Delivered | CM20251024000198 | PCM-20251024-00000444 | TT-20251024-00517 | Reference_EM | Region_2 | RIYD6037 | RIYD6037 |  |  |  | Adham Adham Hassan Farghal | 10/24/2025 08:52:39 | 10/24/2025 14:57:25 | 10/24/2025 14:52:39 | high temprature 32 at RIYD6037-P1-VIP_SRAN @ Sceco | 10/24/2025 08:42:29 | Major | 65102 | high temprature 32 | 10/24/2025 08:42:25 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_EM | [8 empty] | API | 10/24/2025 08:52:39 | 10/24/2025 14:57:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000199 | PCM-20251024-00000446 | TT-20251024-00471 | Reference_telecom | Region_3 | MDN2M8984 | MDN2984 |  |  |  | TAUSEEF ILYAS | 10/24/2025 08:53:05 | 10/24/2025 09:54:10 | 10/24/2025 20:53:05 | Cell RX Channel Interference Noise Power Unbalanced at MDN2M8984-P2-L800 @ Sceco | 10/24/2025 05:15:03 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 05:14:59 | P2 | 4G | madinah | Sceco | 2G NSA | MDN2M8984 | FLM_TE |  |  | PCM-20251024-00000404 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/24/2025 08:53:05 | 10/24/2025 09:54:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000201 | PCM-20251024-00000448 | TT-20251024-00520 | Reference_telecom | Region_6 | JIZ0184 | JIZ0184 |  |  |  | Osama Hadi | 10/24/2025 08:54:11 | 10/24/2025 19:00:48 | 10/24/2025 20:54:11 | ReplaceableUnitProblem observed in JIZ0184_1 towards 10.10.157.66 @ Sceco | 10/23/2025 20:54:42 | Minor |  | ReplaceableUnitProblem | 10/23/2025 20:53:52 | P2 | 2G | jizan | Sceco | TX NSA | JIZ0184 | FLM_TE | [8 empty] | API | 10/24/2025 08:54:11 | 10/24/2025 19:00:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000203 | PCM-20251024-00000457 | TT-20251024-00528 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 08:59:53 | 10/24/2025 12:28:55 | 10/24/2025 14:59:53 | high temprature 40 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/24/2025 08:49:42 | Major | 65103 | high temprature 40 | 10/24/2025 08:49:39 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/24/2025 08:59:53 | 10/24/2025 12:28:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000204 | PCM-20251024-00000458 | TT-20251024-00529 | Reference_telecom | Region_6 | ABH0119 | ABH0119 |  |  |  | Amir Sohail | 10/24/2025 09:00:23 | 10/24/2025 10:41:06 | 10/24/2025 21:00:23 | LossOfSignal observed in ABH0119 towards 10.10.155.45 @ Sceco | 10/23/2025 21:01:50 | Minor |  | LossOfSignal | 10/23/2025 20:59:52 | P2 | 2G | abha | Sceco | TX NSA | ABH0119 | FLM_TE | [8 empty] | API | 10/24/2025 09:00:23 | 10/24/2025 10:41:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000205 | PCM-20251024-00000460 | TT-20251024-00522 | EM | Region_2 | RYQ2M1989 | RYQ0989 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/24/2025 09:02:30 | 10/25/2025 09:03:03 | 10/24/2025 15:02:30 | 1(2G/3G) sites down under RYQ0989-P2/RY1BSCH02 @ Sceco | 10/24/2025 08:55:50 | Major | 21825 | CSL Fault | 10/24/2025 08:55:49 | P2 | 2G | majma | Sceco | 2G_3G SA | RYQ0989-P2 | FLM_EM | RYQ0989 | Results: DOWN SITE HUB RYQ0989-P2 RYQ0989 Summary: Hub: RYQ0989, Down Count: 1, Down Sites: RYQ0989-P2 Alarm Summary: RYQ0989 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 09:02:30 | 10/25/2025 08:57:46 | 10/25/2025 09:02:53 | 10/25/2025 09:02:56 |  | 10/25/2025 09:03:03 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000207 | PCM-20251024-00000465 | TT-20251024-00536 | Telecom | Region_2 | RIYD6037 | RIYD6037 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 09:04:32 | 10/25/2025 10:55:53 | 10/24/2025 21:04:32 | RF Unit Maintenance Link Failure at RIYD6037-DCU2 @ Sceco | 10/24/2025 08:52:17 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 08:59:11 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_TE | [8 empty] | API | 10/24/2025 09:04:32 | 10/25/2025 08:50:15 | 10/25/2025 10:55:30 |  |  | 10/25/2025 10:55:53 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000208 | PCM-20251024-00000467 | TT-20251024-00535 | EM | Region_1 | DJL2M1615 | DJL0615 | Equipment | PMR_Power_Cable_RRU | Replace Outdoor Power Connector | Mahmoud Abdelwanis Massoud Elrashidy | 10/24/2025 09:09:31 | 10/24/2025 10:25:56 | 10/24/2025 15:09:31 | 1(2G/3G/LTE) sites down under DJL0615-P3-USF/SK1BSCH01 @ Generator_SG | 10/24/2025 09:02:43 | Major | 21825 | CSL Fault | 10/24/2025 09:02:41 | P3 | 2G | sakaka | Generator_SG | 2G_3G_LTE SA | DJL0615-P3-USF | FLM_EM | DJL0615 | Results: DOWN SITE HUB DJL0615-P3-USF DJL0615 Summary: Hub: DJL0615, Down Count: 1, Down Sites: DJL0615-P3-USF Alarm Summary: DJL0615 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 09:09:31 | 10/24/2025 10:24:56 | 10/24/2025 10:25:02 | 10/24/2025 10:25:16 | 10/24/2025 10:25:22 | 10/24/2025 10:25:56 |  | Mahmoud Abdelwanis Massoud Elrashidy |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000209 | PCM-20251024-00000469 | TT-20251024-00544 | Telecom | Region_5 | MAK1M9541 | MAK0541 |  |  |  | Husain Hassan Ishag Omer | 10/24/2025 09:11:46 | 10/25/2025 11:01:34 | 10/24/2025 21:11:46 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9541-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/24/2025 09:11:09 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 09:11:04 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9541 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 09:11:46 | 10/25/2025 11:01:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000214 | PCM-20251024-00000475 | TT-20251024-00553 | EM | Region_6 | MKW2344 | MKW2344 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/24/2025 09:17:58 | 10/24/2025 16:11:45 | 10/24/2025 21:17:58 | COMMERCIAL POWER FAILURE at MKW2344-G9-L8-L18-NR2.6-SBTS-P3 @ Generator_SG | 10/24/2025 09:10:03 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/24/2025 09:09:53 | P3 | 2G | Baha | Generator_SG | 2G NSA | MKW2344 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/24/2025 09:17:58 | 10/24/2025 16:11:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000215 | PCM-20251024-00000477 | TT-20251024-00555 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/24/2025 09:21:05 | 10/26/2025 00:11:27 | 10/24/2025 15:21:05 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/24/2025 09:11:04 | Major | 65102 | high temprature 32 | 10/24/2025 09:11:00 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/24/2025 09:21:05 | 10/26/2025 00:11:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000220 | PCM-20251024-00000485 | TT-20251024-00574 | Telecom | Region_1 | JBL6009 | JBL6009 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/24/2025 09:35:33 | 10/24/2025 10:39:17 | 10/24/2025 21:35:33 | RF Unit Maintenance Link Failure at JBL6009-DCU1 @ Sceco | 10/24/2025 09:31:10 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 09:30:06 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL6009 | FLM_TE | [8 empty] | API | 10/24/2025 09:35:33 | 10/24/2025 10:39:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000223 | PCM-20251024-00000495 | TT-20251024-00583 | EM | Region_2 | RY1BSCH02 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/24/2025 09:42:16 | 10/24/2025 09:42:16 | 10/24/2025 13:42:16 | Genset Not in Auto at RY1BSCH02 @ Sceco_STB | 10/24/2025 09:42:02 | Critical | 65345 | Genset Not in Auto | 10/24/2025 09:41:59 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | RY1BSCH02 | FLM_EM | [8 empty] | API | 10/24/2025 09:42:16 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000224 | PCM-20251024-00000496 | TT-20251024-00585 | EM | Region_2 | RY1BSCH02 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/24/2025 09:42:45 | 10/24/2025 09:42:45 | 10/24/2025 13:42:45 | Gen set running SH1 at RY1BSCH02 @ Sceco_STB | 10/24/2025 09:42:30 | Critical | 65344 | Gen set running SH1 | 10/24/2025 09:42:26 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | RY1BSCH02 | FLM_EM | [8 empty] | API | 10/24/2025 09:42:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000226 | PCM-20251024-00000501 | TT-20251024-00588 | Telecom | Region_5 | MAK2709 | MAK2709 |  |  |  | Husain Hassan Ishag Omer | 10/24/2025 09:49:28 | 10/25/2025 11:01:35 | 10/24/2025 15:49:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2709-G9-L8-L18-L21-NR2.6-SBTS @ Sceco | 10/24/2025 09:48:52 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 09:48:41 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2709 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 09:49:28 | 10/25/2025 11:01:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000227 | PCM-20251024-00000502 | TT-20251024-00589 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/24/2025 09:52:04 | 10/24/2025 19:26:41 | 10/24/2025 21:52:04 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/24/2025 09:43:40 | Minor | 7103 | HIGH TEMP | 10/24/2025 09:43:30 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/24/2025 09:52:04 | 10/24/2025 19:26:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000230 | PCM-20251024-00000508 | TT-20251024-00599 | EM | Region_4 | JED2032 | JED2032 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/24/2025 10:01:22 | 10/24/2025 10:01:22 | 10/24/2025 22:01:22 | RECTIFIER MODULE FAILURE at JED2032-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 09:53:16 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/24/2025 09:53:07 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2032 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/24/2025 10:01:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000233 | PCM-20251024-00000513 | TT-20251023-01821 | Telecom | Region_2 | RIY2C8864 | RIY2864 | Equipment | Power Cable_RRU_BTS | Change Port on DCDU | Ejaz Hussain Muhammad Sharif | 10/24/2025 10:06:08 | 10/25/2025 07:47:52 | 10/24/2025 16:06:08 | Cell Unavailable at RIY2C8864-L800-CA-P1-VIP @ Generator_SG | 10/23/2025 18:45:58 | Major | 29240 | Cell Unavailable | 10/23/2025 18:44:23 | P3 | 4G | riyadh | Generator_SG | LTE SA | RIY2C8864 | FLM_TE |  |  | PCM-20251023-00002088 | site down due to TE issue and nO power issue at site | site down due to TE issue and nO power issue at site |  |  |  | API | 10/24/2025 10:06:08 | 10/25/2025 07:44:06 | 10/25/2025 07:47:19 |  |  | 10/25/2025 07:47:52 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000234 | PCM-20251024-00000514 | TT-20251023-01820 | Telecom | Region_2 | RIY2864 | RIY2864 | Equipment | Power Cable_RRU_BTS | Change Port on DCDU | Ejaz Hussain Muhammad Sharif | 10/24/2025 10:07:18 | 10/25/2025 07:46:59 | 10/24/2025 22:07:18 | RF Unit Maintenance Link Failure at RIY2864-P1-VIP_SRAN @ Generator_SG | 10/23/2025 18:46:02 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/23/2025 18:44:19 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2864 | FLM_TE |  |  | PCM-20251023-00002085 | site down due to Te issue and No power issue at site | site down due to Te issue and No power issue at site |  |  |  | API | 10/24/2025 10:07:18 | 10/25/2025 07:44:08 | 10/25/2025 07:44:36 |  |  | 10/25/2025 07:46:59 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000236 | PCM-20251024-00000520 | TT-20251024-00613 | Reference_EM | Region_1 | JBL6009 | JBL6009 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/24/2025 10:14:17 | 10/25/2025 12:53:16 | 10/24/2025 22:14:17 | Air condition 3 failure alarm at JBL6009-P3_SRAN @ Sceco | 10/24/2025 10:04:16 | Minor | 65117 | Air condition 3 failure alarm | 10/24/2025 10:04:00 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL6009 | FLM_EM | [8 empty] | API | 10/24/2025 10:14:17 | 10/25/2025 12:53:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251024000238 | PCM-20251024-00000527 | TT-20251024-00619 | EM | [7 empty] | 10/24/2025 10:17:53 | 10/24/2025 10:17:53 | 10/24/2025 22:17:53 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/24/2025 10:09:34 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/24/2025 10:09:28 | P3 | 4G |  | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | API | 10/24/2025 10:17:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000239 | PCM-20251024-00000539 | TT-20251024-00633 | EM | Region_4 | USF1M7694 | USF0694 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/24/2025 10:25:39 | 10/25/2025 04:36:46 | 10/24/2025 22:25:39 | RECTIFIER MODULE FAILURE at USF1M7694-G9-L8-SBTS-P2-USF @ Sceco | 10/24/2025 10:17:35 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/24/2025 10:17:28 | P3 | 4G | jeddah | Sceco | LTE NSA | USF1M7694 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/24/2025 10:25:39 | 10/25/2025 04:36:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000240 | PCM-20251024-00000544 | TT-20251024-00644 | Telecom | Region_4 | JZMA1M7824 | JZMA0824 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/24/2025 10:32:54 | 10/25/2025 01:15:24 | 10/24/2025 22:32:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at JZMA1M7824-G9-L8-SBTS-P3 @ Sceco | 10/24/2025 10:32:01 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 10:31:51 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JZMA1M7824 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 10:32:54 | 10/25/2025 01:15:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000241 | PCM-20251024-00000546 | TT-20251024-00647 | EM | Region_2 | R2_RY1_HWBSC01 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/24/2025 10:33:54 | 10/24/2025 10:33:54 | 10/24/2025 14:33:54 | Gen set running(SH1) at R2_RY1_HWBSC01 @ Sceco_STB | 10/24/2025 10:33:46 | Critical | 65344 | Gen set running(SH1) | 10/24/2025 10:33:42 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY1_HWBSC01 | FLM_EM | [8 empty] | API | 10/24/2025 10:33:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000242 | PCM-20251024-00000545 | TT-20251024-00646 | EM | Region_2 | R2_RY1_HWBSC01 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/24/2025 10:33:55 | 10/24/2025 10:33:55 | 10/24/2025 14:33:55 | Genset Not in Auto at R2_RY1_HWBSC01 @ Sceco_STB | 10/24/2025 10:33:29 | Critical | 65345 | Genset Not in Auto | 10/24/2025 10:33:25 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY1_HWBSC01 | FLM_EM | [8 empty] | API | 10/24/2025 10:33:55 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000246 | PCM-20251024-00000556 | TT-20251024-00661 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/24/2025 10:40:09 | 10/25/2025 11:20:08 | 10/24/2025 16:40:09 | Board Temperature Unacceptable at RIY2866-P3_SRAN-PC @ Sceco | 10/24/2025 10:31:35 | Major | 26104 | Board Temperature Unacceptable | 10/24/2025 10:30:01 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/24/2025 10:40:09 | 10/25/2025 11:20:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000247 | PCM-20251024-00000560 | TT-20251024-00665 | Reference_telecom | Region_6 | ABH0289 | ABH0289 | Transsmission | MW_HW_stuck | Reset FAN | Muhammad Jamshaid Muhammad Ashraf | 10/24/2025 10:41:39 | 10/24/2025 16:17:44 | 10/24/2025 22:41:39 | FanFailure observed in ABH0289 _01 towards 10.10.154.195 @ Sceco | 10/23/2025 22:41:36 | Minor |  | FanFailure | 10/23/2025 22:41:31 | P3 | 2G | abha | Sceco | TX NSA | ABH0289 | FLM_TE | [8 empty] | API | 10/24/2025 10:41:39 | 10/24/2025 11:36:40 | 10/24/2025 16:17:19 |  |  | 10/24/2025 16:17:44 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000248 | PCM-20251024-00000562 | TT-20251024-00606 | Telecom | Region_2 | SRIY0230 | SRIY0230 |  |  |  | Majid Khan Arsalan Khan | 10/24/2025 10:42:24 | 10/24/2025 10:42:24 | 10/24/2025 14:42:24 | 1(2G) 2(3G) 1(LTE) sites down under SRIY0230-P3,SRIY0231-P1-DIA,RIY0695-P3/R2_RY4_HWBSC01 @ Sceco | 10/24/2025 10:05:03 | Critical | 21825 | CSL Fault | 10/24/2025 10:05:00 | P3 | SRAN | riyadh | Sceco | 2G_3G_LTE SA | RIY0695-P3 2G_LTE,SRIY0230-P3 3G,SRIY0231-P1-DIA 3G | FLM_EM | SRIY0230 | SITES HUB FB RIY0695-P3 RIY0695 suspecting power issue at hub site SRIY0230-P3 SRIY0230 suspecting power issue at hub site SRIY0231-P1-DIA SRIY0230 suspecting power issue at hub site | PCM-20251024-00000519 | SITES HUB FB RIY0695-P3 RIY0695 suspecting power issue at hub site SRIY0230-P3 SRIY0230 suspecting power issue at hub site SRIY0231-P1-DIA SRIY0230 suspecting power issue at hub site | SITES HUB FB RIY0695-P3 RIY0695 suspecting power issue at hub site SRIY0230-P3 SRIY0230 suspecting power issue at hub site SRIY0231-P1-DIA SRIY0230 suspecting power issue at hub site |  | sites down |  | API | 10/24/2025 10:42:24 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000251 | PCM-20251024-00000571 | TT-20251024-00671 | Telecom | Region_4 | JED1MN2689 | JED2689 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 10:47:52 | 10/24/2025 10:47:52 | 10/24/2025 22:47:52 | BASE STATION INFORMATION (No module fan detected) at JED1MN2689-NR2.6-P3 @ Sceco | 10/24/2025 10:39:26 | Minor | 7115 | BASE STATION INFORMATION | 10/24/2025 10:39:19 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN2689 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/24/2025 10:47:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000252 | PCM-20251024-00000573 | TT-20251024-00672 | Telecom | Region_1 | KBR6054 | KBR6054 |  |  |  | Meraj Husain Idd Baksh | 10/24/2025 10:48:24 | 10/24/2025 17:26:16 | 10/24/2025 22:48:24 | RF Unit Maintenance Link Failure at KBR6054-DCU1 @ Sceco | 10/24/2025 10:43:17 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 10:43:14 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6054 | FLM_TE | [8 empty] | API | 10/24/2025 10:48:24 | 10/24/2025 17:26:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000253 | PCM-20251024-00000574 | TT-20251024-00675 | EM | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Gamal Mohamed Farag | 10/24/2025 10:49:55 | 10/26/2025 02:22:14 | 10/24/2025 22:49:55 | HIGH TEMPERATURE 32 DEGREE C at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/24/2025 10:41:45 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/24/2025 10:41:34 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7558 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/24/2025 10:49:55 | 10/26/2025 02:22:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000254 | PCM-20251024-00000575 | TT-20251024-00604 | Reference_telecom | Region_4 | JED2063 | JED2063 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 10:51:14 | 10/24/2025 10:51:14 | 10/24/2025 22:51:14 | BASE STATION SERVICE PROBLEM (Radio Module fail safe mode) at JED2063-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 10:01:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 10:00:52 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2063 | FLM_TE |  |  | PCM-20251024-00000511 | Kindly check the RFM at site and support to make HC | Kindly check the RFM at site and support to make HC |  |  |  | API | 10/24/2025 10:51:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000259 | PCM-20251024-00000585 | TT-20251024-00615 | Telecom | Region_4 | JED1M8555 | JED2555 |  |  |  | MALIK ATIF ZAMAN | 10/24/2025 10:54:53 | 10/24/2025 11:42:24 | 10/24/2025 16:54:53 | BASE STATION SERVICE PROBLEM (RX out of order)at JED1M8555-L800-CA-P1-VVIP-SBTS @ Generator_SG | 10/24/2025 10:12:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 10:12:07 | VIP | 4G | jeddah | Generator_SG | LTE SA | JED1M8555 | FLM_TE |  |  | PCM-20251024-00000564 | As discussed, currently alarm is cleared, if repeats need to check locally | As discussed, currently alarm is cleared, if repeats need to check locally |  |  |  | API | 10/24/2025 10:54:53 | 10/24/2025 11:42:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000262 | PCM-20251024-00000590 | TT-20251024-00686 | Reference_EM | Region_3 | RSP0036 | RSP0036 |  |  |  | Sayed Satoor | 10/24/2025 11:01:18 | 10/25/2025 14:53:21 | 10/24/2025 17:01:18 | high temprature 40 at RSP0036-P1-VIP_SRAN @ Generator_SG | 10/24/2025 10:51:09 | Major | 65103 | high temprature 40 | 10/24/2025 10:51:05 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0036 | FLM_EM | [8 empty] | API | 10/24/2025 11:01:18 | 10/25/2025 14:53:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000264 | PCM-20251024-00000594 | TT-20251024-00688 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 11:07:31 | 10/24/2025 11:07:31 | 10/24/2025 17:07:31 | 1(5G) sites down under JED0035-NR2.6-P2 @ Sceco | 10/24/2025 10:59:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 10:59:09 | P2 | 5G | jeddah | Sceco | 5G SA | JED0035-NR2.6-P2 | FLM_TE | JED0035 | Results: DOWN SITE HUB JED0035-NR2.6-P2 JED0035 Summary: Hub: JED0035, Down Count: 1, Down Sites: JED0035-NR2.6-P2 Alarm Summary: JED0035 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.119.28:8080] [URL:http://10.88.119.28:8080/NE3S/1.0/] | sites down |  | API | 10/24/2025 11:07:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000265 | PCM-20251024-00000596 | TT-20251024-00691 | EM | Region_4 | JED2050 | JED2050 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/24/2025 11:09:03 | 10/24/2025 11:09:03 | 10/24/2025 23:09:03 | AIRCON 1 FAILURE at JED2050-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/24/2025 11:00:50 | Minor | 7103 | AIRCON 1 FAILURE | 10/24/2025 11:00:46 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2050 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/24/2025 11:09:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000267 | PCM-20251024-00000598 | TT-20251024-00692 | EM | Region_4 | RYMK1M7544 | RYMK0544 |  |  |  | Farghal Ashour Hassan Farghal | 10/24/2025 11:10:36 | 10/24/2025 11:10:36 | 10/24/2025 23:10:36 | HIGH TEMPERATURE 32 DEGREE C at RYMK1M7544-L800-P2-USF @ Sceco | 10/24/2025 11:02:39 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/24/2025 11:02:29 | P2 | 4G | taif | Sceco | LTE NSA | RYMK1M7544 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/24/2025 11:10:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000268 | PCM-20251024-00000600 | TT-20251024-00694 | Telecom | Region_2 | RIYA6009 | RIYA6009 |  |  |  | Pawan Virdi Santokh Singh | 10/24/2025 11:11:07 | 10/25/2025 10:05:49 | 10/24/2025 23:11:07 | BBU DC Output Out of Range at RIYA6009-P3_SRAN @ Sceco | 10/24/2025 11:08:24 | Minor | 26112 | BBU DC Output Out of Range | 10/24/2025 11:06:52 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6009 | FLM_TE | [8 empty] | API | 10/24/2025 11:11:07 | 10/25/2025 10:05:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000270 | PCM-20251024-00000601 | TT-20251024-00373 | Reference_telecom | Region_6 | QJF1M7051 | QJF0051 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Zeshan Ali Adnan | 10/24/2025 11:11:17 | 10/24/2025 15:51:55 | 10/24/2025 23:11:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QJF1M7051-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/24/2025 06:12:38 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 02:59:59 | P2 | 4G | baish | Sceco | LTE NSA | QJF1M7051 | FLM_TE |  |  | PCM-20251024-00000322 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/24/2025 11:11:17 | 10/24/2025 15:50:27 | 10/24/2025 15:51:12 |  |  | 10/24/2025 15:51:55 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000277 | PCM-20251024-00000616 | TT-20251024-00586 | Reference_telecom | Region_6 | AQQ0058 | AQQ0058 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/24/2025 11:16:25 | 10/25/2025 16:13:18 | 10/24/2025 17:16:25 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at AQQ0058-P2 @ Sceco | 10/24/2025 09:43:34 | Major | 7607 | TRX OPERATION DEGRADED | 10/24/2025 09:43:31 | P2 | 2G | Albaha | Sceco | 2G_TRX NSA | AQQ0058 | FLM_TE |  |  | PCM-20251024-00000500 | RSSI alarm active at site, kindly check | RSSI alarm active at site, kindly check |  |  |  | API | 10/24/2025 11:16:25 | 10/25/2025 16:06:53 | 10/25/2025 16:13:09 |  |  | 10/25/2025 16:13:18 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000278 | PCM-20251024-00000619 | TT-20251024-00708 | Telecom | Region_2 | RIYA2U6709 | RIYA6009 |  |  |  | Pawan Virdi Santokh Singh | 10/24/2025 11:19:59 | 10/25/2025 10:05:48 | 10/24/2025 17:19:59 | Cell Unavailable at RIYA2U6709-P3 @ Sceco | 10/24/2025 11:17:09 | Major | 29240 | Cell Unavailable | 10/24/2025 11:15:33 | P3 | 4G | riyadh | Sceco | LTE SA | RIYA2U6709 | FLM_TE | [8 empty] | API | 10/24/2025 11:19:59 | 10/25/2025 10:05:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000279 | PCM-20251024-00000626 | TT-20251024-00714 | Reference_telecom | Region_1 | DMJR2266 | DMJR2266 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/24/2025 11:26:37 | 10/24/2025 19:53:01 | 10/24/2025 23:26:37 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR2266-P3-USF_SRAN @ Sceco | 10/24/2025 08:26:11 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/24/2025 08:26:07 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR2266 | FLM_TE | [8 empty] | API | 10/24/2025 11:26:37 | 10/24/2025 19:53:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000281 | PCM-20251024-00000628 | TT-20251024-00361 | Reference_telecom | Region_6 | HSH1M7019 | HSH0019 | Equipment | BSS_HW_fault | Replace RRU | Shahid Ali Roshan Ali | 10/24/2025 11:32:24 | 10/25/2025 01:15:14 | 10/24/2025 17:32:24 | CELL FAULTY (RF Module failure) at HSH1M7019 (Ref:TT-20251023-00993) @ Sceco | 10/24/2025 04:59:06 | Major | 7653 | CELL FAULTY | 10/24/2025 04:58:58 | P3 | 4G | najran | Sceco | 3G_Cell SA | HSH1M7019 | FLM_TE |  |  | PCM-20251024-00000380 | Approved | Approved |  |  |  | API | 10/24/2025 11:32:24 | 10/24/2025 15:07:28 | 10/25/2025 01:14:48 |  |  | 10/25/2025 01:15:14 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000282 | PCM-20251024-00000629 | TT-20251024-00460 | Telecom | Region_4 | JED0415 | JED0415 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 11:32:43 | 10/24/2025 13:01:19 | 10/24/2025 23:32:43 | BASE STATION ANTENNA LINE PROBLEM at JED0415-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 07:51:36 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 07:51:32 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0415 | FLM_TE |  |  | PCM-20251024-00000397 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/24/2025 11:32:43 | 10/24/2025 13:01:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000283 | PCM-20251024-00000630 | TT-20251024-00717 | Telecom | Region_3 | MDN2903 | MDN2903 | Equipment | SW | Issue was solved after softaware configuration | Ibrahim Mohammad AbdulMalik alraee | 10/24/2025 11:35:24 | 10/24/2025 19:04:24 | 10/24/2025 23:35:24 | ALD Maintenance Link Failure at MDN2903-P2_SRAN @ Sceco | 10/24/2025 11:32:48 | Minor | 26541 | ALD Maintenance Link Failure | 10/24/2025 11:31:11 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2903 | FLM_TE | [8 empty] | API | 10/24/2025 11:35:24 | 10/24/2025 14:52:29 | 10/24/2025 19:04:18 |  |  | 10/24/2025 19:04:24 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000284 | PCM-20251024-00000632 | TT-20251024-00190 | Reference_telecom | Region_1 | JBL2394 | JBL2394 | Equipment | BSS_HW_fault | Replace RRU | Rafiq Ahmed Elturifi | 10/24/2025 11:36:59 | 10/25/2025 13:58:18 | 10/24/2025 23:36:59 | RF Unit RX Channel RTWP/RSSI Unbalanced at JBL2394-P2_SRAN @ Sceco | 10/24/2025 00:14:05 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/24/2025 00:14:01 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL2394 | FLM_TE |  |  | PCM-20251024-00000581 | Dear FLM , Approved as per your TS & flapping alarms with below data: Display Board Manufacturing Information --------------------------------------- Type = WD5MIRUDC10 Serial Number = 2102310TQF6TFC400504 Description = RRU3839,WD5MIRUDC10,MRRU | Dear FLM , Approved as per your TS & flapping alarms with below data: Display Board Manufacturing Information --------------------------------------- Type = WD5MIRUDC10 Serial Number = 2102310TQF6TFC400504 Description = RRU3839,WD5MIRUDC10,MRRU |  |  |  | API | 10/24/2025 11:36:59 | 10/24/2025 12:43:36 | 10/25/2025 12:19:56 | 10/25/2025 12:20:22 | 10/25/2025 12:57:29 | 10/25/2025 13:58:18 |  | Rafiq Ahmed Elturifi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000285 | PCM-20251024-00000634 | TT-20251024-00630 | Reference_telecom | Region_1 | DAM2M7648 | DAM0648 | Equipment | BSS_HW_Stuck | Reset RRU | Shakeel Ahmed Hafeez Ameen | 10/24/2025 11:37:48 | 10/25/2025 18:37:57 | 10/24/2025 23:37:48 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M7648-FWA-P1-VIP-L800 @ Sceco | 10/24/2025 07:23:05 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 07:23:03 | P2 | 4G | dammam | Sceco | 2G NSA | DAM2M7648 | FLM_TE |  |  | PCM-20251024-00000534 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/24/2025 11:37:48 | 10/24/2025 12:06:01 | 10/25/2025 17:04:28 | 10/25/2025 17:36:47 | 10/25/2025 17:36:52 | 10/25/2025 18:37:57 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000287 | PCM-20251024-00000636 | TT-20251024-00699 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/24/2025 11:38:56 | 10/24/2025 11:40:47 | 10/24/2025 23:38:56 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/24/2025 11:07:08 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 11:06:59 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251024-00000606 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/24/2025 11:38:56 | 10/24/2025 11:40:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000288 | PCM-20251024-00000638 | TT-20251024-00722 | Telecom | Region_5 | MAK0325 | MAK0325 |  |  |  | Husain Hassan Ishag Omer | 10/24/2025 11:39:01 | 10/25/2025 11:01:36 | 10/24/2025 23:39:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0325-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/24/2025 11:38:19 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 11:38:13 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK0325 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 11:39:01 | 10/25/2025 11:01:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000289 | PCM-20251024-00000639 | TT-20251024-00697 | Reference_telecom | Region_4 | JED2177 | JED2177 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 11:40:32 | 10/24/2025 13:01:19 | 10/24/2025 17:40:32 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED2177-P3 @ Sceco | 10/24/2025 11:06:16 | Major | 7602 | BCF NOTIFICATION | 10/24/2025 11:06:03 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2177 | FLM_TE |  |  | PCM-20251024-00000604 | Site is down, kindly check | Site is down, kindly check |  |  |  | API | 10/24/2025 11:40:32 | 10/24/2025 13:01:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000290 | PCM-20251024-00000640 | TT-20251024-00523 | Reference_telecom | Region_4 | JED0714 | JED0714 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 11:41:13 | 10/24/2025 13:01:20 | 10/24/2025 17:41:13 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED0714-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/24/2025 08:51:31 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 08:51:24 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0714 | FLM_TE |  |  | PCM-20251024-00000453 | Site is down, kindly check | Site is down, kindly check |  |  |  | API | 10/24/2025 11:41:13 | 10/24/2025 13:01:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000292 | PCM-20251024-00000642 | TT-20251024-00524 | Reference_telecom | Region_4 | JED2009 | JED2009 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 11:42:34 | 10/24/2025 13:01:20 | 10/24/2025 23:42:34 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED2009-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/24/2025 08:51:28 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 08:51:22 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2009 | FLM_TE |  |  | PCM-20251024-00000451 | Need to check the anchor site, which is down | Need to check the anchor site, which is down |  |  |  | API | 10/24/2025 11:42:34 | 10/24/2025 13:01:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000293 | PCM-20251024-00000643 | TT-20251024-00726 | Reference_telecom | Region_4 | JED0550 | JED0550 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/24/2025 11:43:09 | 10/24/2025 13:31:30 | 10/24/2025 23:43:09 | Degrade observed in JED0550_02 towards 10.10.147.36 @ Sceco | 10/23/2025 23:42:51 | Minor |  | Degrade | 10/23/2025 23:42:47 | P2 | 2G | jeddah | Sceco | TX NSA | JED0550 | FLM_TE | [8 empty] | API | 10/24/2025 11:43:09 | 10/24/2025 13:31:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000294 | PCM-20251024-00000644 | TT-20251024-00727 | Reference_telecom | Region_4 | JED0958 | JED0958 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/24/2025 11:43:09 | 10/24/2025 13:31:30 | 10/24/2025 23:43:09 | LossOfSignal observed in JED0958 FTK towards 10.10.147.35 @ Sceco | 10/23/2025 23:42:49 | Minor |  | LossOfSignal | 10/23/2025 23:42:45 | P3 | 2G | jeddah | Sceco | TX NSA | JED0958 | FLM_TE | [8 empty] | API | 10/24/2025 11:43:09 | 10/24/2025 13:31:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000296 | PCM-20251024-00000648 | TT-20251024-00731 | Telecom | Region_5 | MAK1M8149 | MAK2149 |  |  |  | Amr Abdulla Ali Othman | 10/24/2025 11:46:15 | 10/24/2025 11:46:15 | 10/24/2025 17:46:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M8149-P3-CA-L800 @ Sceco | 10/24/2025 11:45:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 11:45:32 | P3 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M8149 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 11:46:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000297 | PCM-20251024-00000650 | TT-20251024-00526 | Reference_telecom | Region_6 | BHAB1M8103 | BHAB2103 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/24/2025 11:49:44 | 10/24/2025 13:59:28 | 10/24/2025 23:49:44 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at BHAB1M8103-G9-L8-L18-P3-SBTS @ Generator_DG | 10/24/2025 08:56:59 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/23/2025 20:26:25 | P3 | 4G | Baha | Generator_DG | LTE NSA | BHAB1M8103 | FLM_TE |  |  | PCM-20251024-00000454 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/24/2025 11:49:44 | 10/24/2025 13:58:22 | 10/24/2025 13:59:10 |  |  | 10/24/2025 13:59:28 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000299 | PCM-20251024-00000652 | TT-20251024-00291 | Telecom | Region_5 | MAK6009 | MAK6009 |  |  |  | Mosab Nasr eldeen Mohamed | 10/24/2025 11:51:43 | 10/24/2025 11:51:43 | 10/24/2025 15:51:43 | 1(LTE) sites down under MAK6009-CA-P1-HRM-SBTS @ Sceco | 10/24/2025 04:34:21 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 04:34:18 | P1 | 2G | makkah | Sceco | LTE SA | MAK6009-CA-P1-HRM-SBTS | FLM_TE | MAK6009 | Results: DOWN SITE HUB MAK6009-CA-P1-HRM-SBTS MAK6009 Summary: Hub: MAK6009, Down Count: 1, Down Sites: MAK6009-CA-P1-HRM-SBTS Alarm Summary: MAK6009 No Active Alarm on HUB | PCM-20251024-00000617 | Approved | Approved |  | sites down |  | API | 10/24/2025 11:51:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000300 | PCM-20251024-00000654 | TT-20251024-00732 | Reference_telecom | Region_4 | JED1M7383 | JED0383 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/24/2025 11:52:57 | 10/24/2025 13:31:31 | 10/24/2025 17:52:57 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7383-CA-L900-L800-SBTS @ Sceco | 10/24/2025 11:41:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 11:41:17 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7383 | FLM_TE |  |  | PCM-20251024-00000649 | Kindly check the RFM and make HC at site | Kindly check the RFM and make HC at site |  |  |  | API | 10/24/2025 11:52:57 | 10/24/2025 13:31:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000301 | PCM-20251024-00000655 | TT-20251024-00721 | Reference_telecom | Region_5 | MAK1U6934 | MAK6034 |  |  |  | Atif Javed Javed Hussain | 10/24/2025 11:54:10 | 10/24/2025 11:54:10 | 10/24/2025 17:54:10 | CELL OPERATION DEGRADED (VSWR minor alarm) at MAK1U6934-P3-CA @ Sceco | 10/24/2025 11:31:06 | Major | 7654 | CELL OPERATION DEGRADED | 10/24/2025 11:30:54 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6934 | FLM_TE |  |  | PCM-20251024-00000637 | VSWR alarm active at site | VSWR alarm active at site |  |  |  | API | 10/24/2025 11:54:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000303 | PCM-20251024-00000657 | TT-20251024-00740 | Telecom | Region_4 | JED1M8162 | JED2162 | Equipment | BSS_HW_fault | Replace Controller Card | MALIK ATIF ZAMAN | 10/24/2025 11:55:02 | 10/24/2025 16:47:18 | 10/24/2025 17:55:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8162-P3-L800-CA @ Sceco | 10/24/2025 11:54:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 11:54:17 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8162 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 11:55:02 | 10/24/2025 14:14:30 | 10/24/2025 14:21:18 | 10/24/2025 14:21:55 | 10/24/2025 16:26:58 | 10/24/2025 16:47:18 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000304 | PCM-20251024-00000659 | TT-20251024-00741 | EM | Region_4 | JED1U6729 | JED6029 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/24/2025 11:55:32 | 10/24/2025 11:55:32 | 10/24/2025 23:55:32 | Rectifier Low battery voltage at JED1U6729-G9-L18-L21-SBTS-P3 @ Sceco | 10/24/2025 11:47:25 | Minor | 7103 | Rectifier Low battery voltage | 10/24/2025 11:47:15 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6729 | FLM_EM | [5 empty] | Rectifier Low battery voltage |  |  | API | 10/24/2025 11:55:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000305 | PCM-20251024-00000660 | TT-20251024-00743 | Reference_EM | Region_3 | DBTB2M5269 | DBTB0269 | Equipment | SW | Issue was solved after softaware configuration | Walid Attia Shahata Alim | 10/24/2025 11:56:04 | 10/25/2025 05:00:10 | 10/24/2025 23:56:04 | Mains Failure at DBTB2M5269-P3 @ Generator_DG | 10/24/2025 11:46:20 | Minor | 65109 | Mains Failure | 10/24/2025 11:46:16 | P3 | 2G | tabouk | Generator_DG | 2G NSA | DBTB2M5269 | FLM_EM | [8 empty] | API | 10/24/2025 11:56:04 | 10/24/2025 13:27:07 | 10/25/2025 01:47:34 | 10/25/2025 01:47:39 | 10/25/2025 01:47:41 | 10/25/2025 05:00:10 |  | Walid Attia Shahata Alim |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000307 | PCM-20251024-00000664 | TT-20251024-00736 | EM | Region_6 | DAR0951 | DAR0951 |  |  |  | Muhammad Tayyab | 10/24/2025 11:57:59 | 10/24/2025 13:55:48 | 10/24/2025 15:57:59 | 1(2G/3G/LTE) sites down under DAR0951-P1/DAR0951-P1 @ Sceco | 10/24/2025 11:50:10 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 11:50:06 | P1 | 2G | dair | Sceco | 2G_3G_LTE SA | DAR0951-P1 | FLM_EM | DAR0951 | Results: DOWN SITE HUB DAR0951-P1 DAR0951 Summary: Hub: DAR0951, Down Count: 1, Down Sites: DAR0951-P1 Alarm Summary: DAR0951 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 11:57:59 | 10/24/2025 13:55:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000308 | PCM-20251024-00000665 | TT-20251024-00737 | EM | Region_2 | RIYA2U6109 | RIYA6009 |  |  |  | Pawan Virdi Santokh Singh | 10/24/2025 11:58:01 | 10/25/2025 10:05:48 | 10/24/2025 17:58:01 | 1(2G/LTE) sites down under RIYA6009-P3/R2_RY1_HWBSC01 @ Sceco | 10/24/2025 11:49:54 | Major | 21825 | CSL Fault | 10/24/2025 11:49:50 | P3 | 2G | riyadh | Sceco | 2G_LTE SA | RIYA6009-P3 | FLM_EM | RIYA6009 | Results: DOWN SITE HUB RIYA6009-P3 RIYA6009 Summary: Hub: RIYA6009, Down Count: 1, Down Sites: RIYA6009-P3 Alarm Summary: RIYA6009 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 11:58:01 | 10/25/2025 10:05:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000310 | PCM-20251024-00000670 | TT-20251024-00744 | Telecom | Region_6 | MKW2344 | MKW2344 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/24/2025 12:01:59 | 10/25/2025 02:21:50 | 10/24/2025 18:01:59 | 2(2G/LTE) sites down under MKW2344-P3,MUMA2349-P3 @ Generator_SG | 10/24/2025 11:53:58 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 11:53:54 | P3 | 2G | Baha | Generator_SG | 2G_5G SA | MKW2344-P3 | FLM_EM | MKW2344 | Results: DOWN SITE HUB MKW2344-P3 MKW2344 Summary: Hub: MKW2344, Down Count: 1, Down Sites: MKW2344-P3 Alarm Summary: MKW2344 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 12:01:59 | 10/24/2025 16:11:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000311 | PCM-20251024-00000671 | TT-20251024-00754 | Reference_EM | Region_2 | RYMK2517 | RYMK2517 |  |  |  | Saleem Khan Amir Dost | 10/24/2025 12:03:48 | 10/25/2025 11:35:06 | 10/25/2025 00:03:48 | Mains Failure at RYMK2517-P3_SRAN @ Sceco | 10/24/2025 11:53:59 | Minor | 65109 | Mains Failure | 10/24/2025 11:53:55 | P3 | SRAN | quweyah | Sceco | 2G NSA | RYMK2517 | FLM_EM | [8 empty] | API | 10/24/2025 12:03:48 | 10/25/2025 11:35:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000318 | PCM-20251024-00000687 | TT-20251024-00762 | EM | Region_4 | JED0052 | JED0052 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 12:19:09 | 10/24/2025 14:40:04 | 10/24/2025 16:19:09 | 1(2G/LTE) sites down under JED0052-P1-WDM-FON/JED0052-P1-WDM-FON @ Sceco | 10/24/2025 12:05:39 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 12:05:33 | P1 | 2G | jeddah | Sceco | 2G_LTE SA | JED0052-P1-WDM-FON | FLM_TE | JED0052 | Results: DOWN SITE HUB JED0052-P1-WDM-FON JED0052 Summary: Hub: JED0052, Down Count: 1, Down Sites: JED0052-P1-WDM-FON Alarm Summary: JED0052 No Active Alarm on HUB | PCM-20251024-00000685 | No Power Issue | No Power Issue |  | sites down |  | API | 10/24/2025 12:19:09 | 10/24/2025 14:40:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000319 | PCM-20251024-00000688 | TT-20251024-00770 | Telecom | Region_5 | MAK0540 | MAK0540 |  |  |  | Atif Javed Javed Hussain | 10/24/2025 12:19:50 | 10/24/2025 12:19:50 | 10/24/2025 18:19:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0540-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM @ Sceco | 10/24/2025 12:18:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 12:18:41 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0540 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 12:19:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000321 | PCM-20251024-00000690 | TT-20251024-00772 | Telecom | Region_5 | MAK1M9582 | MAK0582 |  |  |  | Ahmed Mohamed Soliman Mohamed | 10/24/2025 12:23:58 | 10/24/2025 12:23:58 | 10/24/2025 18:23:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9582-P1-HRM-CA-VIP-L800-SBTS @ Sceco | 10/24/2025 12:22:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 12:22:48 | VIP | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9582 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 12:23:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000324 | PCM-20251024-00000695 | TT-20251024-00778 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 12:32:13 | 10/24/2025 12:32:13 | 10/25/2025 00:32:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 12:31:23 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 12:31:16 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0500 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 12:32:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000326 | PCM-20251024-00000699 | TT-20251024-00784 | Reference_telecom | Region_2 | RIYA6009 | RIYA6009 |  |  |  | Pawan Virdi Santokh Singh | 10/24/2025 12:37:23 | 10/25/2025 10:05:49 | 10/25/2025 00:37:23 | POWER_ABNORMAL at RIYA6009/CRIY0015_NE_1/CRIY1041-1 @ Sceco | 10/24/2025 11:07:03 | Minor | 1-412 | POWER_ABNORMAL | 10/24/2025 11:06:52 | P3 | SRAN | riyadh | Sceco | TX NSA | RIYA6009 | FLM_TE | [8 empty] | API | 10/24/2025 12:37:23 | 10/25/2025 10:05:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000327 | PCM-20251024-00000702 | TT-20251024-00787 | Reference_EM | Region_3 | RSP0039 | RSP0039 |  |  |  | Sayed Satoor | 10/24/2025 12:38:57 | 10/25/2025 14:53:21 | 10/24/2025 18:38:57 | Door opening alarm at RSP0039-P1-ARP-VVIP_SRAN @ Sceco | 10/24/2025 12:38:37 | Major | 65101 | Door opening alarm | 10/24/2025 12:38:32 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0039 | FLM_EM | [8 empty] | API | 10/24/2025 12:38:57 | 10/25/2025 14:53:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000330 | PCM-20251024-00000709 | TT-20251024-00791 | EM | Region_5 | MAK2591 | MAK2591 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/24/2025 12:49:30 | 10/24/2025 12:59:45 | 10/24/2025 18:49:30 | 1(2G/5G) sites down under MAK2591-P3/MAK2591-P3 @ Sceco | 10/24/2025 12:41:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 12:41:00 | P3 | 2G | makkah | Sceco | 2G SA | MAK2591-P3 | FLM_TE | MAK2591 | Results: DOWN SITE HUB MAK2591-P3 MAK2591 Summary: Hub: MAK2591, Down Count: 1, Down Sites: MAK2591-P3 Alarm Summary: MAK2591 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 12:49:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000331 | PCM-20251024-00000713 | TT-20251024-00634 | EM | Region_4 | SIR0173 | SIR0173 | Equipment | SFP_BTS | Replace SFP | Asad Ur Rehman | 10/24/2025 12:51:36 | 10/24/2025 14:39:47 | 10/24/2025 18:51:36 | 1(2G/3G/5G) sites down under SIR0173-P2-USF/SIR0173-P2-USF @ Generator_SG | 10/24/2025 10:23:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 10:23:01 | P2 | 2G | adam | Generator_SG | 2G_3G_5G SA | SIR0173-P2-USF | FLM_TE | SIR0173 | Results: DOWN SITE HUB SIR0173-P2-USF SIR0173 Summary: Hub: SIR0173, Down Count: 1, Down Sites: SIR0173-P2-USF Alarm Summary: SIR0173 No Active Alarm on HUB | PCM-20251024-00000543 | No Power Issue | No Power Issue |  | sites down |  | API | 10/24/2025 12:51:36 | 10/24/2025 13:10:39 | 10/24/2025 13:27:56 | 10/24/2025 13:28:12 | 10/24/2025 13:46:29 | 10/24/2025 14:39:47 |  | Asad Ur Rehman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000333 | PCM-20251024-00000715 | TT-20251024-00801 | EM | Region_5 | MK1_CORE | MK1 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/24/2025 12:51:51 | 10/25/2025 12:11:33 | 10/24/2025 18:51:51 | GENRATOR-2 RUNNING at MK1_CORE-P1-VIP @ Sceco_STB | 10/24/2025 12:51:37 | Major | 7103 | GENRATOR-2 RUNNING | 10/24/2025 12:51:32 | P1 | 4G | makkah | Sceco_STB | 2G NSA | MK1_CORE | FLM_EM | [5 empty] | GENRATOR-2 RUNNING |  |  | API | 10/24/2025 12:51:51 | 10/25/2025 12:11:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000334 | PCM-20251024-00000721 | TT-20251024-00807 | Reference_EM | Region_3 | HAL0946 | HAL0946 |  |  |  | Mohamed Hafez Fahim Abdelaziz | 10/24/2025 12:56:00 | 10/25/2025 01:15:36 | 10/25/2025 00:56:00 | Mains Failure at HAL0946-P2_SRAN @ Sceco | 10/24/2025 12:45:50 | Minor | 65109 | Mains Failure | 10/24/2025 12:45:46 | P2 | SRAN | hail | Sceco | 2G NSA | HAL0946 | FLM_EM | [8 empty] | API | 10/24/2025 12:56:00 | 10/25/2025 01:15:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000335 | PCM-20251024-00000719 | TT-20251024-00808 | Reference_telecom | Region_4 | JED0768 | JED0768 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 12:56:00 | 10/24/2025 12:56:00 | 10/25/2025 00:56:00 | BASE STATION SERVICE PROBLEM (TX out of order) at JED0768-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 12:51:20 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 12:51:15 | P2 | 2G | jeddah | Sceco | LTE_Cell SA | JED0768 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/24/2025 12:56:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000336 | PCM-20251024-00000724 | TT-20251024-00812 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/24/2025 12:59:06 | 10/24/2025 17:26:18 | 10/25/2025 00:59:06 | RF Unit Maintenance Link Failure at DAM6027-DCU1 @ Sceco | 10/24/2025 12:53:56 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 12:53:40 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/24/2025 12:59:06 | 10/24/2025 17:26:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000338 | PCM-20251024-00000727 | TT-20251024-00814 | Telecom | Region_1 | DAM2995 | DAM2995 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/24/2025 13:00:08 | 10/24/2025 13:14:24 | 10/25/2025 01:00:08 | RF Unit Temperature Unacceptable at DAM2995-P2_SRAN @ Sceco | 10/24/2025 12:53:23 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/24/2025 12:53:20 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2995 | FLM_TE | [8 empty] | API | 10/24/2025 13:00:08 | 10/24/2025 13:14:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000339 | PCM-20251024-00000728 | TT-20251024-00815 | Telecom | Region_1 | JBL0468 | JBL0468 | Equipment | BSS_HW_fault | Replace Interface Card | Tahir Mahmood Hafiz Yar | 10/24/2025 13:00:38 | 10/24/2025 16:34:44 | 10/25/2025 01:00:38 | RF Unit CPRI Interface Error at JBL0468-P2_SRAN @ Sceco | 10/24/2025 12:55:03 | Minor | 26504 | RF Unit CPRI Interface Error | 10/24/2025 12:53:29 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0468 | FLM_TE | [8 empty] | API | 10/24/2025 13:00:38 | 10/24/2025 13:17:15 | 10/24/2025 15:24:31 | 10/24/2025 15:24:47 | 10/24/2025 15:26:52 | 10/24/2025 16:34:44 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000340 | PCM-20251024-00000729 | TT-20251024-00649 | Telecom | Region_4 | JED0519 | JED0519 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 13:01:35 | 10/24/2025 21:48:32 | 10/24/2025 17:01:35 | 7(2G) 6(5G) sites down under JED2313-P3 @ Generator_SG | 10/24/2025 10:32:32 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 10:32:28 | P2 | 2G | jeddah | Sceco | 2G_5G SA | JED0714-FWA-P1-VIP 2G_5G,JED2177-P3 2G_5G,JED2030-FWA-P1-VIP 2G_5G,JED2313-P3 2G,JED2339-P3 2G,JED2561-P3 2G,JED2263-P3 2G | FLM_TE | JED0519 | Site HUB TRM FB JED2263-P3 JED2263 observing LOS TO AIRSCALE JED2339-P3 JED0519 Suspecting power issue JED2030-FWA-P1-VIP JED0519 Suspecting power issue JED0714-FWA-P1-VIP JED0519 Suspecting power issue JED2561-P3 JED0519 Suspecting power issue JED2177-P3 JED0519 Suspecting power issue JED2313-P3 JED0519 Suspecting power issue JED2717-P1-VIP JED2004 Suspecting power issue | PCM-20251024-00000569 | No Power Issue | No Power Issue |  | sites down |  | API | 10/24/2025 13:01:35 | 10/24/2025 19:24:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000341 | PCM-20251024-00000732 | TT-20251024-00519 | Telecom | Region_4 | JED0519 | JED0519 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 13:01:50 | 10/24/2025 19:24:14 | 10/24/2025 17:01:50 | 7(2G/5G) sites down under JED0519-P2/JED0519-P2 @ Sceco | 10/24/2025 08:50:58 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 08:50:50 | P2 | 2G | jeddah | Sceco | 2G_5G SA | JED0519-P2 | FLM_TE | JED0519 | Results: DOWN SITE HUB JED0519-P2 JED0519 Summary: Hub: JED0519, Down Count: 1, Down Sites: JED0519-P2 Alarm Summary: JED0519 No Active Alarm on HUB | PCM-20251024-00000455 | No Power Issue | No Power Issue |  | sites down |  | API | 10/24/2025 13:01:50 | 10/24/2025 19:24:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000344 | PCM-20251024-00000735 | TT-20251024-00820 | Reference_telecom | Region_6 | KMS0146 | KMS0146 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/24/2025 13:04:16 | 10/24/2025 14:27:36 | 10/25/2025 01:04:16 | ReplaceableUnitProblem observed in KMS0146 towards 10.10.159.134 @ Sceco | 10/24/2025 01:04:18 | Minor |  | ReplaceableUnitProblem | 10/24/2025 01:04:09 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KMS0146 | FLM_TE | [8 empty] | API | 10/24/2025 13:04:16 | 10/24/2025 14:27:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000345 | PCM-20251024-00000737 | TT-20251024-00823 | Telecom | Region_5 | HAJ0270 | HAJ0270 |  |  |  | Muhammad Saleem Iqbal | 10/24/2025 13:07:53 | 10/26/2025 05:13:14 | 10/25/2025 01:07:53 | BD_STATUS at HAJ0270_NE_1_OMB @ Sceco | 10/24/2025 09:07:58 | Minor | 1-119 | BD_STATUS | 10/24/2025 09:07:49 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0270 | FLM_TE | [8 empty] | API | 10/24/2025 13:07:53 | 10/26/2025 05:13:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000347 | PCM-20251024-00000742 | TT-20251024-00828 | Reference_telecom | Region_4 | JED0845 | JED0845 |  |  |  | MALIK ATIF ZAMAN | 10/24/2025 13:10:28 | 10/24/2025 14:03:40 | 10/25/2025 01:10:28 | ReplaceableUnitProblem observed in JED0845_04 towards 10.10.141.236 @ Sceco | 10/24/2025 01:10:02 | Minor |  | ReplaceableUnitProblem | 10/24/2025 01:09:57 | P2 | 2G | jeddah | Sceco | TX NSA | JED0845 | FLM_TE | [8 empty] | API | 10/24/2025 13:10:28 | 10/24/2025 14:03:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000348 | PCM-20251024-00000745 | TT-20251024-00830 | Telecom | Region_4 | JED2028 | JED2028 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 13:14:05 | 10/24/2025 13:14:05 | 10/25/2025 01:14:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2028-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/24/2025 13:13:18 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:13:08 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2028 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 13:14:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000349 | PCM-20251024-00000747 | TT-20251024-00835 | Reference_telecom | Region_6 | SAB0062 | SAB0062 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/24/2025 13:19:15 | 10/24/2025 17:53:00 | 10/25/2025 01:19:15 | LossOfSignal observed in SAB0062 towards 10.10.155.135 @ Sceco | 10/24/2025 01:19:27 | Minor |  | LossOfSignal | 10/24/2025 01:19:03 | P2 | 2G | baish | Sceco | TX NSA | SAB0062 | FLM_TE | [8 empty] | API | 10/24/2025 13:19:15 | 10/24/2025 17:53:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000351 | PCM-20251024-00000752 | TT-20251024-00832 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/24/2025 13:21:59 | 10/24/2025 20:19:28 | 10/24/2025 19:21:59 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/24/2025 13:13:48 | Major | 22214 | NodeB Unavailable | 10/24/2025 13:13:46 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 13:21:59 | 10/24/2025 20:19:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000353 | PCM-20251024-00000756 | TT-20251024-00844 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/24/2025 13:26:59 | 10/24/2025 13:26:59 | 10/24/2025 17:26:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/24/2025 13:26:00 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:25:50 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 13:26:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000354 | PCM-20251024-00000757 | TT-20251024-00848 | Telecom | Region_4 | JED0991 | JED0991 | Equipment | SW | Issue was solved after softaware configuration | BARKAT ALI MAIN HILAL | 10/24/2025 13:30:37 | 10/24/2025 15:47:50 | 10/24/2025 19:30:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0991-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/24/2025 13:30:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:29:54 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0991 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 13:30:37 | 10/24/2025 14:40:04 | 10/24/2025 15:29:12 | 10/24/2025 15:29:16 |  | 10/24/2025 15:47:50 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000356 | PCM-20251024-00000759 | TT-20251024-00850 | Telecom | Region_4 | JED0578 | JED0578 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 13:31:38 | 10/24/2025 13:31:38 | 10/24/2025 19:31:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0578-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/24/2025 13:30:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:30:38 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0578 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 13:31:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000359 | PCM-20251024-00000763 | TT-20251024-00857 | Reference_telecom | [7 empty] | 10/24/2025 13:33:13 | 10/24/2025 13:33:13 | 10/25/2025 01:33:13 | LossOfSignal observed in HAW2897 _01 towards 10.221.247.130 @ Sceco | 10/24/2025 01:34:30 | Minor |  | LossOfSignal | 10/24/2025 01:32:53 | VIP | 2G |  | Sceco | TX NSA | HAW2897 | FLM_TE | [8 empty] | API | 10/24/2025 13:33:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000362 | PCM-20251024-00000767 | TT-20251024-00862 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/24/2025 13:39:24 | 10/24/2025 13:39:24 | 10/25/2025 01:39:24 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/24/2025 13:31:11 | Minor | 7115 | BASE STATION INFORMATION | 10/24/2025 13:31:04 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/24/2025 13:39:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000363 | PCM-20251024-00000770 | TT-20251024-00865 | Telecom | Region_5 | MAK1MN2246 | MAK2246 |  |  |  | Atif Javed Javed Hussain | 10/24/2025 13:40:57 | 10/24/2025 13:40:57 | 10/24/2025 19:40:57 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN2246-NR2.6-P3 @ Sceco | 10/24/2025 13:40:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:40:16 | P3 | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN2246 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 13:40:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000364 | PCM-20251024-00000771 | TT-20251024-00867 | Reference_EM | Region_2 | RIY2824 | RIY2824 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/24/2025 13:43:01 | 10/24/2025 13:47:07 | 10/25/2025 01:43:01 | high temprature 32 at RIY2824-P2_SRAN @ Sceco | 10/24/2025 13:32:56 | Minor | 65102 | high temprature 32 | 10/24/2025 13:32:35 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2824 | FLM_EM | [8 empty] | API | 10/24/2025 13:43:01 | 10/24/2025 13:47:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000366 | PCM-20251024-00000774 | TT-20251024-00866 | Telecom | Region_3 | DBQL2M5264 | DBQL0264 |  |  |  | Hossam Ali Ahmed Ali | 10/24/2025 13:45:59 | 10/24/2025 17:58:02 | 10/24/2025 19:45:59 | 1(2G) sites down under DBQL0264-P3/R3_TB_HWBSC01 @ Generator_SG | 10/24/2025 13:37:45 | Major | 21807 | OML Fault | 10/24/2025 13:37:39 | P3 | 2G | tabouk | Generator_SG | 2G SA | DBQL0264-P3 | FLM_TE |  | Results: DOWN SITE HUB DBQL0264-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/24/2025 13:45:59 | 10/24/2025 17:58:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000373 | PCM-20251024-00000794 | TT-20251024-00891 | Telecom | [7 empty] | 10/24/2025 13:58:32 | 10/24/2025 13:58:32 | 10/24/2025 17:58:32 | ETH_LOS at FRIY0001-1 @ Sceco | 10/24/2025 13:57:28 | Critical | 1-235 | ETH_LOS | 10/24/2025 13:56:53 | P3 | DWDM |  | Sceco | DWDM NSA | FRIY0001 | FLM_TE | [5 empty] | 0-1-C-4-K1EX10-3(Awqaf)-MAC:1 |  |  | API | 10/24/2025 13:58:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000374 | PCM-20251024-00000796 | TT-20251024-00894 | Telecom | Region_1 | HFF6029 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/24/2025 13:59:02 | 10/24/2025 17:48:27 | 10/24/2025 19:59:02 | DCU CPRI Interface Error at HFF6029-DCU1 @ Sceco | 10/24/2025 13:53:03 | Major | 26234 | DCU CPRI Interface Error | 10/24/2025 13:52:04 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/24/2025 13:59:02 | 10/24/2025 14:33:34 | 10/24/2025 17:48:17 |  |  | 10/24/2025 17:48:27 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000376 | PCM-20251024-00000799 | TT-20251024-00889 | EM | Region_4 | JED6029 | JED6029 |  |  |  | Mohamed Farag Abdelbary | 10/24/2025 14:01:59 | 10/25/2025 13:02:19 | 10/24/2025 20:01:59 | 1(2G/LTE) sites down under JED6029-P3/JED6029-P3 @ Sceco | 10/24/2025 13:53:47 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 13:53:41 | P3 | 2G | jeddah | Sceco | 2G SA | JED6029-P3 | FLM_TE | JED6029 | Results: DOWN SITE HUB JED6029-P3 JED6029 Summary: Hub: JED6029, Down Count: 1, Down Sites: JED6029-P3 Alarm Summary: JED6029 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 14:01:59 | 10/25/2025 13:02:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000378 | PCM-20251024-00000801 | TT-20251024-00898 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/24/2025 14:03:40 | 10/24/2025 14:36:34 | 10/25/2025 02:03:40 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/24/2025 13:56:42 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/24/2025 13:56:37 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/24/2025 14:03:40 | 10/24/2025 14:36:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000381 | PCM-20251024-00000805 | TT-20251024-00905 | Telecom | Region_5 | MAK0674 | MAK0674 |  |  |  | Amjad Ali Muhammad Parves | 10/24/2025 14:08:50 | 10/25/2025 12:15:01 | 10/25/2025 02:08:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0674-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/24/2025 14:08:10 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 14:08:04 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0674 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 14:08:50 | 10/25/2025 12:15:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000385 | PCM-20251024-00000813 | TT-20251024-00728 | Reference_telecom | Region_2 | RIY2802 | RIY2802 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Ejaz Hussain Muhammad Sharif | 10/24/2025 14:12:21 | 10/24/2025 18:24:55 | 10/25/2025 02:12:21 | RF Unit RX Channel RTWP/RSSI Unbalanced at RIY2802-P2_SRAN @ Sceco | 10/24/2025 08:43:48 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/24/2025 08:43:45 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2802 | FLM_TE |  |  | PCM-20251024-00000723 | Dear FLM , kindly need the result of HC check & if you Swap the board with another or not? | Dear FLM , kindly need the result of HC check & if you Swap the board with another or not? |  |  |  | API | 10/24/2025 14:12:21 | 10/24/2025 14:50:14 | 10/24/2025 14:53:33 | 10/24/2025 14:53:38 | 10/24/2025 15:59:02 | 10/24/2025 18:24:55 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000386 | PCM-20251024-00000815 | TT-20251024-00777 | Reference_telecom | Region_2 | RIY2M7134 | RIY0134 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | Muhammad Waqas Ashraf Muhammad Ashraf | 10/24/2025 14:13:17 | 10/24/2025 16:55:04 | 10/25/2025 02:13:17 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M7134-P2-L900-L800 @ Sceco | 10/24/2025 09:29:29 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 09:29:24 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M7134 | FLM_TE |  |  | PCM-20251024-00000694 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/24/2025 14:13:17 | 10/24/2025 14:28:45 | 10/24/2025 15:27:20 | 10/24/2025 15:27:23 | 10/24/2025 15:27:25 | 10/24/2025 16:55:04 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000388 | PCM-20251024-00000817 | TT-20251024-00817 | Reference_telecom | Region_3 | MDN2U6702 | MDN6002 |  |  |  | TAUSEEF ILYAS | 10/24/2025 14:14:20 | 10/25/2025 05:00:24 | 10/25/2025 02:14:20 | Cell RX Channel Interference Noise Power Unbalanced at MDN2U6702-P1-VIP @ Sceco | 10/24/2025 10:01:14 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 10:01:09 | VIP | 4G | madinah | Sceco | 2G NSA | MDN2U6702 | FLM_TE |  |  | PCM-20251024-00000731 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/24/2025 14:14:20 | 10/25/2025 05:00:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251024000390 | PCM-20251024-00000819 | TT-20251024-00916 | Telecom | Region_4 | JED0935 | JED0935 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 14:15:03 | 10/25/2025 09:56:37 | 10/25/2025 02:15:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0935-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Generator_SG | 10/24/2025 14:14:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 14:13:56 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0935 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 14:15:03 | 10/24/2025 19:24:14 | 10/25/2025 09:52:31 | 10/25/2025 09:52:33 | 10/25/2025 09:56:37 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000394 | PCM-20251024-00000829 | TT-20251024-00930 | Telecom | Region_4 | MKJD1M9570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/24/2025 14:23:50 | 10/25/2025 12:15:01 | 10/25/2025 02:23:50 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MKJD1M9570-P3-L800-SBTS @ Generator_DG | 10/24/2025 14:15:51 | Minor | 7115 | BASE STATION INFORMATION | 10/24/2025 14:15:45 | P2 | 4G | jeddah | Generator_DG | LTE NSA | MKJD1M9570 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/24/2025 14:23:50 | 10/25/2025 12:15:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000395 | PCM-20251024-00000832 | TT-20251024-00932 | Reference_telecom | Region_5 | MAK0256 | MAK0256 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/24/2025 14:26:56 | 10/24/2025 14:26:56 | 10/25/2025 02:26:56 | ReplaceableUnitProblem observed in MAK0256 towards 10.10.141.196 @ Sceco | 10/24/2025 02:26:54 | Minor |  | ReplaceableUnitProblem | 10/24/2025 02:26:49 | P2 | 2G | makkah | Sceco | TX NSA | MAK0256 | FLM_TE | [8 empty] | API | 10/24/2025 14:26:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000396 | PCM-20251024-00000838 | TT-20251024-00936 | Reference_telecom | Region_4 | JED1M7884 | JED0884 |  |  |  | Mohammed Ramadan A Abu Abid | 10/24/2025 14:31:04 | 10/24/2025 19:24:15 | 10/24/2025 20:31:04 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7884-CA-L900-L800-SBTS @ Sceco | 10/24/2025 14:26:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 14:26:22 | P2 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7884 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/24/2025 14:31:04 | 10/24/2025 19:24:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000397 | PCM-20251024-00000840 | TT-20251024-00931 | EM | Region_4 | MKYL1M3916 | MKYL0916 |  |  |  | Riasat Ali Allah Baksh | 10/24/2025 14:31:31 | 10/24/2025 22:54:31 | 10/24/2025 20:31:31 | 1(2G/3G/5G) sites down under MKYL0916-P3/MKYL1M3916-P3 @ Generator_SG | 10/24/2025 14:23:57 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/24/2025 14:23:16 | P3 | 3G | alaith | Generator_SG | 3G SA | MKYL0916-P3 | FLM_TE | MKYL0916 | Results: DOWN SITE HUB MKYL0916-P3 MKYL0916 Summary: Hub: MKYL0916, Down Count: 1, Down Sites: MKYL0916-P3 Alarm Summary: MKYL0916 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 14:31:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251024000398 | PCM-20251024-00000842 | TT-20251024-00868 | Telecom | Region_1 | QTF0491 | QTF0491 |  |  |  | Meraj Husain Idd Baksh | 10/24/2025 14:35:31 | 10/25/2025 01:42:20 | 10/25/2025 02:35:31 | Inter-System Communication Failure at QTF0491-P2_SRAN @ Generator_SG | 10/24/2025 13:37:55 | Minor | 26270 | Inter-System Communication Failure | 10/24/2025 13:36:22 | P2 | SRAN | dammam | Generator_SG | 2G NSA | QTF0491 | FLM_TE |  |  | PCM-20251024-00000837 | Dear FLM , alarm due to 3G site is down ( all cells are locked ) but site is down & unviable from our side , please check the CO- TX cable between GLN BBU & 3G BBU & check with TX | Dear FLM , alarm due to 3G site is down ( all cells are locked ) but site is down & unviable from our side , please check the CO- TX cable between GLN BBU & 3G BBU & check with TX |  |  |  | API | 10/24/2025 14:35:31 | 10/25/2025 01:42:12 | 10/25/2025 01:42:20 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000399 | PCM-20251024-00000843 | TT-20251024-00941 | Telecom | Region_4 | TAF2405 | TAF2405 |  |  |  | Ahmad Kamal Abdelmawla | 10/24/2025 14:35:42 | 10/24/2025 16:05:10 | 10/25/2025 02:35:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF2405-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 14:35:06 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 14:34:56 | P2 | 2G | taif | Sceco | 5G_Cell SA | TAF2405 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 14:35:42 | 10/24/2025 16:05:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000400 | PCM-20251024-00000847 | TT-20251024-00946 | EM | Region_3 | RUSF9040 | RUSF9040 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/24/2025 14:39:20 | 10/24/2025 14:39:20 | 10/25/2025 02:39:20 | NETECO: Insufficient Redundant Rectifiers at RUSF9040 @ Sceco_STB | 10/24/2025 14:32:58 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/24/2025 14:32:58 | P3 | Repeater | madinah | Sceco_STB | 2G NSA | RUSF9040 | FLM_EM | [8 empty] | API | 10/24/2025 14:39:20 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000403 | PCM-20251024-00000852 | TT-20251024-00952 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/24/2025 14:42:56 | 10/24/2025 14:42:56 | 10/25/2025 02:42:56 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/24/2025 14:34:47 | Minor | 7103 | AIRCON 2 FAILURE | 10/24/2025 14:34:36 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/24/2025 14:42:56 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000406 | PCM-20251024-00000856 | TT-20251024-00957 | Reference_EM | Region_3 | MDN2U6172 | MDN6072 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Tasbeeh Ullah Muhammad Yousaf | 10/24/2025 14:45:32 | 10/25/2025 01:39:10 | 10/25/2025 02:45:32 | Mains Input Out of Range at MDN2U6172-P3 @ Sceco | 10/24/2025 14:35:46 | Minor | 25622 | Mains Input Out of Range | 10/24/2025 14:35:04 | P3 | 2G | madinah | Sceco | 2G NSA | MDN2U6172 | FLM_EM | [8 empty] | API | 10/24/2025 14:45:32 | 10/25/2025 01:38:45 | 10/25/2025 01:39:02 |  |  | 10/25/2025 01:39:10 |  | Tasbeeh Ullah Muhammad Yousaf |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000407 | PCM-20251024-00000858 | TT-20251024-00958 | EM | Region_6 | BSA2296 | BSA2296 |  |  |  | Asad Saddiq | 10/24/2025 14:46:34 | 10/25/2025 00:41:24 | 10/25/2025 02:46:34 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at BSA2296-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/24/2025 14:38:35 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/24/2025 14:38:30 | P3 | 2G | bisha | Generator_SG | 2G NSA | BSA2296 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/24/2025 14:46:34 | 10/25/2025 00:41:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000410 | PCM-20251024-00000864 | TT-20251024-00956 | EM | Region_6 | DAR0954 | DAR0954 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Muhammad Tayyab | 10/24/2025 14:50:29 | 10/24/2025 18:55:15 | 10/24/2025 20:50:29 | 1(2G/3G/5G) sites down under DAR0954-P2/DAR0954-P2 @ Sceco | 10/24/2025 14:42:25 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 14:42:19 | P2 | 2G | dair | Sceco | 2G_3G_5G SA | DAR0954-P2 | FLM_EM | DAR0954 | Results: DOWN SITE HUB DAR0954-P2 DAR0954 Summary: Hub: DAR0954, Down Count: 1, Down Sites: DAR0954-P2 Alarm Summary: DAR0954 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 14:50:29 | 10/24/2025 15:14:35 | 10/24/2025 18:54:25 | 10/24/2025 18:54:27 | 10/24/2025 18:54:31 | 10/24/2025 18:55:15 |  | Muhammad Tayyab |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000411 | PCM-20251024-00000865 | TT-20251024-00962 | Reference_telecom | Region_2 | RIY0289 | RIY0289 |  |  |  | Farmanullah Akbar Jan | 10/24/2025 14:51:44 | 10/25/2025 00:30:36 | 10/25/2025 02:51:44 | BUS_ERR at RIY0289_NE_9_SDB @ Sceco | 10/24/2025 13:51:22 | Minor | 1-377 | BUS_ERR | 10/24/2025 13:51:12 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0289 | FLM_TE | [8 empty] | API | 10/24/2025 14:51:44 | 10/25/2025 00:30:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000413 | PCM-20251024-00000869 | TT-20251024-00966 | Reference_telecom | Region_4 | RYMK0541 | RYMK0541 |  |  |  | Rashid Shafique | 10/24/2025 14:56:22 | 10/24/2025 20:06:16 | 10/25/2025 02:56:22 | LossOfSignal observed in RYMK0541_05 towards 10.221.247.129 @ Sceco_STB | 10/24/2025 02:56:59 | Minor |  | LossOfSignal | 10/24/2025 02:56:13 | P2 | 2G | taif | Sceco_STB | TX NSA | RYMK0541 | FLM_TE | [8 empty] | API | 10/24/2025 14:56:22 | 10/24/2025 20:06:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000414 | PCM-20251024-00000870 | TT-20251024-00967 | EM | Region_4 | HAW0331 | HAW0331 |  |  |  | Farghal Ashour Hassan Farghal | 10/24/2025 14:56:54 | 10/24/2025 14:56:54 | 10/25/2025 02:56:54 | SHELTER DOOR OPEN at HAW0331-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 14:56:20 | Minor | 7103 | SHELTER DOOR OPEN | 10/24/2025 14:56:09 | P2 | 2G | taif | Sceco | 2G NSA | HAW0331 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/24/2025 14:56:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000415 | PCM-20251024-00000871 | TT-20251024-00969 | Telecom | Region_1 | JBL0468 | JBL0468 |  |  |  | Tahir Mahmood Hafiz Yar | 10/24/2025 14:58:58 | 10/24/2025 16:34:50 | 10/25/2025 02:58:58 | RF Unit Maintenance Link Failure at JBL0468-P2_SRAN @ Sceco | 10/24/2025 14:55:30 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 14:53:47 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0468 | FLM_TE | [8 empty] | API | 10/24/2025 14:58:58 | 10/24/2025 16:34:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000426 | PCM-20251024-00000893 | TT-20251024-00982 | EM | Region_3 | MDN2U6172 | MDN6072 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Tasbeeh Ullah Muhammad Yousaf | 10/24/2025 15:14:29 | 10/25/2025 01:39:28 | 10/24/2025 21:14:29 | 1(2G/3G/LTE) sites down under MDN6072-P3/R3_MD_HWBSC02 @ Sceco | 10/24/2025 15:06:19 | Major | 21807 | OML Fault | 10/24/2025 15:06:13 | P3 | 2G | madinah | Sceco | 2G_3G_LTE SA | MDN6072-P3 | FLM_EM | MDN6072 | Results: DOWN SITE HUB MDN6072-P3 MDN6072 Summary: Hub: MDN6072, Down Count: 1, Down Sites: MDN6072-P3 Alarm Summary: MDN6072 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 15:14:29 | 10/25/2025 01:38:46 | 10/25/2025 01:39:20 |  |  | 10/25/2025 01:39:28 |  | Tasbeeh Ullah Muhammad Yousaf |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000427 | PCM-20251024-00000895 | TT-20251024-00994 | EM | Region_6 | BHAB0824 | BHAB0824 |  |  |  | Sohail Nasir Mir Afzal | 10/24/2025 15:18:29 | 10/24/2025 16:07:08 | 10/24/2025 21:18:29 | 1(2G/3G/LTE) sites down under BHAB0824-P2-WBB-G3/BHAB0824-P2-WBB-G3 @ Sceco | 10/24/2025 15:10:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 15:10:43 | P2 | 2G | makhwa | Sceco | 2G_3G_LTE SA | BHAB0824-P2-WBB-G3 | FLM_EM | BHAB0824 | Results: DOWN SITE HUB BHAB0824-P2-WBB-G3 BHAB0824 Summary: Hub: BHAB0824, Down Count: 1, Down Sites: BHAB0824-P2-WBB-G3 Alarm Summary: BHAB0824 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 15:18:29 | 10/24/2025 16:07:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000428 | PCM-20251024-00000898 | TT-20251024-00996 | EM | Region_6 | BHAB2015 | BHAB2015 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/24/2025 15:18:59 | 10/24/2025 17:13:02 | 10/24/2025 21:18:59 | 1(2G/LTE) sites down under BHAB2015-P3/BHAB2015-P3 @ Generator_SG | 10/24/2025 15:10:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 15:10:43 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2015-P3 | FLM_EM | BHAB2015 | Results: DOWN SITE HUB BHAB2015-P3 BHAB2015 Summary: Hub: BHAB2015, Down Count: 1, Down Sites: BHAB2015-P3 Alarm Summary: BHAB2015 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 15:18:59 | 10/24/2025 17:13:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000429 | PCM-20251024-00000900 | TT-20251024-01002 | Telecom | Region_6 | ABDB9019 | ABDB9019 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Amir Sohail | 10/24/2025 15:19:37 | 10/24/2025 20:05:13 | 10/25/2025 03:19:37 | ODU CPU / Cable Open at ABDB9019_2 on 10.154.163.187 @ Sceco_STB | 10/24/2025 15:18:10 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/24/2025 15:18:15 | P1 | Repeater | abha | Sceco_STB | TX NSA | ABDB9019 | FLM_TE | [8 empty] | API | 10/24/2025 15:19:37 | 10/24/2025 16:42:43 | 10/24/2025 20:04:54 |  |  | 10/24/2025 20:05:13 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000430 | PCM-20251024-00000904 | TT-20251024-01010 | EM | Region_6 | NJR0116 | NJR0116 |  |  |  | Habib Ahmed | 10/24/2025 15:23:13 | 10/24/2025 15:25:45 | 10/25/2025 03:23:13 | RECTIFIER MAINS POWER FAILURE at NJR0116-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 15:19:21 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/24/2025 15:15:04 | P2 | 2G | najran | Sceco | 2G NSA | NJR0116 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/24/2025 15:23:13 | 10/24/2025 15:25:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000431 | PCM-20251024-00000905 | TT-20251024-01012 | Reference_telecom | Region_4 | JED2625 | JED2625 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 15:23:45 | 10/24/2025 15:29:53 | 10/25/2025 03:23:45 | Degrade observed in JED2625_01 towards 10.21.75.246 @ Sceco | 10/24/2025 03:23:21 | Minor |  | Degrade | 10/24/2025 03:23:15 | P3 | 2G | jeddah | Sceco | TX NSA | JED2625 | FLM_TE | [8 empty] | API | 10/24/2025 15:23:45 | 10/24/2025 15:29:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000432 | PCM-20251024-00000906 | TT-20251024-01014 | EM | Region_6 | DAR0954 | DAR0954 |  |  |  | Muhammad Tayyab | 10/24/2025 15:24:16 | 10/24/2025 15:26:18 | 10/25/2025 03:24:16 | AIRCON 1 FAILURE;Default System Time at DAR0954-GSM-UMTS-P2 @ Sceco | 10/24/2025 15:22:32 | Minor | 7103 | AIRCON 1 FAILURE;Default System Time | 10/24/2025 15:11:08 | P2 | 2G | dair | Sceco | 2G NSA | DAR0954 | FLM_EM | [5 empty] | AIRCON 1 FAILURE;Default System Time |  |  | API | 10/24/2025 15:24:16 | 10/24/2025 15:26:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000433 | PCM-20251024-00000907 | TT-20251024-00495 | Reference_telecom | Region_1 | ARM2608 | ARM2608 |  |  |  | Imran Ali Yousaf | 10/24/2025 15:24:18 | 10/25/2025 02:33:35 | 10/25/2025 03:24:18 | FAN_FAIL at ARM2608_NE_7_SDB @ Generator_SG | 10/24/2025 07:36:47 | Minor | 1-115 | FAN_FAIL | 10/24/2025 07:36:35 | P3 | SRAN | dammam | Generator_SG | TX NSA | ARM2608 | FLM_TE |  |  | PCM-20251024-00000839 | Approved as per TS steps [NE:ARM2608_NE_7_SDB] [Board:FAN Slot:11] [Board Properties] BoardType=TND1FAN02 BarCode=030LKHN0M1000268 Item=03030LKH | Approved as per TS steps [NE:ARM2608_NE_7_SDB] [Board:FAN Slot:11] [Board Properties] BoardType=TND1FAN02 BarCode=030LKHN0M1000268 Item=03030LKH |  |  |  | API | 10/24/2025 15:24:18 | 10/25/2025 02:33:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000434 | PCM-20251024-00000909 | TT-20251024-01016 | Telecom | Region_4 | JED1M8176 | JED2176 | Equipment | BTS_Cable | Replace CPRI Cable | MALIK ATIF ZAMAN | 10/24/2025 15:25:49 | 10/24/2025 18:35:49 | 10/24/2025 21:25:49 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8176-CA-L1800-L800-P3 @ Sceco | 10/24/2025 15:25:11 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 15:25:00 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8176 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 15:25:49 | 10/24/2025 16:10:07 | 10/24/2025 16:47:33 | 10/24/2025 16:47:49 | 10/24/2025 17:26:50 | 10/24/2025 18:35:49 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000435 | PCM-20251024-00000910 | TT-20251024-01003 | Telecom | Region_3 | HAL2M1943 | HAL0943 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/24/2025 15:25:59 | 10/25/2025 08:15:51 | 10/24/2025 21:25:59 | 1(2G) sites down under HAL0943-P3/R3_HL_HWBSC01 @ Sceco | 10/24/2025 15:17:54 | Major | 21807 | OML Fault | 10/24/2025 15:17:43 | P3 | 2G | hail | Sceco | 2G SA | HAL0943-P3 | FLM_TE | HAL0943 | Results: DOWN SITE HUB HAL0943-P3 HAL0943 Summary: Hub: HAL0943, Down Count: 1, Down Sites: HAL0943-P3 Alarm Summary: HAL0943 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 15:25:59 | 10/25/2025 08:15:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000439 | PCM-20251024-00000919 | TT-20251024-01030 | EM | [7 empty] | 10/24/2025 15:37:11 | 10/24/2025 15:37:11 | 10/25/2025 03:37:11 | RECTIFIER MAINS POWER FAILURE at AQQ1M8426-G9-L8-SBTS-P3 @ Generator_SG | 10/24/2025 15:29:00 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/24/2025 15:28:50 | P3 | 4G |  | Generator_SG | LTE NSA | AQQ1M8426 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/24/2025 15:37:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000440 | PCM-20251024-00000920 | TT-20251024-01031 | Telecom | Region_4 | JED0253 | JED0253 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 15:37:11 | 10/24/2025 15:37:11 | 10/25/2025 03:37:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0253-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 15:36:33 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 15:36:23 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0253 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 15:37:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000442 | PCM-20251024-00000923 | TT-20251024-01034 | EM | Region_6 | BHAB2090 | BHAB2090 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/24/2025 15:41:18 | 10/24/2025 17:13:02 | 10/25/2025 03:41:18 | AIRCON 2 FAILURE at BHAB2090-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/24/2025 15:33:13 | Minor | 7103 | AIRCON 2 FAILURE | 10/24/2025 15:32:52 | P3 | 2G | mohail | Generator_SG | 2G NSA | BHAB2090 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/24/2025 15:41:18 | 10/24/2025 17:13:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000444 | PCM-20251024-00000930 | TT-20251024-01046 | Reference_telecom | Region_1 | KSB0031 | KSB0031 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Zubair Guilzar | 10/24/2025 15:46:30 | 10/26/2025 06:52:34 | 10/25/2025 03:46:30 | RF Unit RX Channel RTWP/RSSI Unbalanced at KSB0031-P3-WDM_SRAN @ Sceco_STB | 10/24/2025 12:46:22 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/24/2025 12:46:18 | P3 | SRAN | arar | Sceco_STB | 2G NSA | KSB0031 | FLM_TE | [8 empty] | API | 10/24/2025 15:46:30 | 10/24/2025 18:16:57 | 10/26/2025 00:26:55 | 10/26/2025 05:01:03 | 10/26/2025 06:03:23 | 10/26/2025 06:52:34 |  | Muhammad Zubair Guilzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000445 | PCM-20251024-00000931 | TT-20251024-01047 | Telecom | Region_4 | TAF0170-ZTa01-CSG-03 | TAF0170 |  |  |  | Ahmad Kamal Abdelmawla | 10/24/2025 15:46:59 | 10/24/2025 16:05:10 | 10/25/2025 03:46:59 | Bad Package Error Rising at TAF0170-ZTa01-CSG-03 @ Sceco_STB | 10/24/2025 15:46:50 | Minor | 101-2501403 | Bad Package Error Rising | 10/24/2025 15:46:43 | P2 | IPRAN | taif | Sceco_STB | IPRAN NSA | TAF0170-ZTa01-CSG-03 | FLM_TE | [8 empty] | API | 10/24/2025 15:46:59 | 10/24/2025 16:05:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000449 | PCM-20251024-00000941 | TT-20251024-01056 | Telecom | Region_4 | HBI1M7353 | HBI0353 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/24/2025 16:04:59 | 10/25/2025 01:15:25 | 10/24/2025 22:04:59 | 1(LTE) sites down under HBI0353-G9-L8-L18-SBTS-P3 @ Sceco | 10/24/2025 15:56:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 15:56:54 | P3 | 4G | qunfuddah | Sceco | LTE SA | HBI0353-G9-L8-L18-SBTS-P3 | FLM_TE | HBI0353 | Results: DOWN SITE HUB HBI0353-G9-L8-L18-SBTS-P3 HBI0353 Summary: Hub: HBI0353, Down Count: 1, Down Sites: HBI0353-G9-L8-L18-SBTS-P3 Alarm Summary: HBI0353 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.98.0.180:8080] [URL:http://10.98.0.180:8080/NE3S/1.0/] | sites down |  | API | 10/24/2025 16:04:59 | 10/25/2025 01:15:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000451 | PCM-20251024-00000947 | TT-20251024-01065 | Telecom | Region_4 | RAB1M3660 | RAB0660 |  |  |  | Khizer Hayat | 10/24/2025 16:08:42 | 10/24/2025 16:08:59 | 10/25/2025 04:08:42 | BASE STATION NOTIFICATION (Fan failure) at RAB1M3660-P2-USF @ Sceco | 10/24/2025 15:38:29 | Minor | 7652 | BASE STATION NOTIFICATION | 10/24/2025 15:38:10 | P2 | 3G | jeddah | Sceco | 3G NSA | RAB1M3660 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/24/2025 16:08:42 | 10/24/2025 16:08:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000453 | PCM-20251024-00000949 | TT-20251024-00975 | Telecom | Region_1 | JBL0468 | JBL0468 |  |  |  | Tahir Mahmood Hafiz Yar | 10/24/2025 16:14:08 | 10/24/2025 16:34:50 | 10/24/2025 22:14:08 | NR Cell Unavailable at JBL0468-P2_SRAN @ Sceco | 10/24/2025 14:55:22 | Major | 29841 | NR Cell Unavailable | 10/24/2025 14:53:50 | P2 | SRAN | jubail | Sceco | 5G SA | JBL0468 | FLM_TE |  |  | PCM-20251024-00000943 | TE team checking | TE team checking |  |  |  | API | 10/24/2025 16:14:08 | 10/24/2025 16:34:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000455 | PCM-20251024-00000955 | TT-20251024-01074 | Telecom | Region_4 | JED1M7683 | JED0683 |  |  |  | Nazeer Mohammed | 10/24/2025 16:19:25 | 10/25/2025 10:31:17 | 10/24/2025 22:19:25 | PT::FLM need to perform HC at JED1M7683-P3-CA-L900-L800-SBTS (Bo request) | 10/24/2025 16:19:10 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/24/2025 16:19:10 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1M7683-P3-CA-L900-L800-SBTS | FLM_TE | [8 empty] | API | 10/24/2025 16:19:25 | 10/25/2025 10:31:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000456 | PCM-20251024-00000957 | TT-20251024-01072 | EM | Region_6 | ARF0186 | ARF0186 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/24/2025 16:21:29 | 10/24/2025 18:25:18 | 10/24/2025 22:21:29 | 1(2G/3G/5G) sites down under ARF0186-P2/ARF0186-P2 @ Sceco | 10/24/2025 16:13:49 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 16:13:45 | P2 | 2G | al harja | Sceco | 2G_3G_5G SA | ARF0186-P2 | FLM_EM | ARF0186 | Results: DOWN SITE HUB ARF0186-P2 ARF0186 Summary: Hub: ARF0186, Down Count: 1, Down Sites: ARF0186-P2 Alarm Summary: ARF0186 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 16:21:29 | 10/24/2025 18:25:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000457 | PCM-20251024-00000959 | TT-20251024-01079 | EM | Region_6 | ARF0186 | ARF0186 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/24/2025 16:26:15 | 10/24/2025 18:25:18 | 10/25/2025 04:26:15 | RECTIFIER MODULE FAILURE at ARF0186-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 16:20:26 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/24/2025 16:17:45 | P2 | 2G | al harja | Sceco | 2G NSA | ARF0186 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/24/2025 16:26:15 | 10/24/2025 18:25:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000458 | PCM-20251024-00000961 | TT-20251024-01084 | Telecom | Region_2 | RIY0134 | RIY0134 | AutoRecovery | Clear_Before_Investigation | Auto Clear | WAQAR AHMED BASHIR AHMED | 10/24/2025 16:28:50 | 10/25/2025 07:57:53 | 10/24/2025 22:28:50 | BBU CPRI Interface Error at RIY0134-P2_SRAN @ Sceco | 10/24/2025 16:24:21 | Major | 26234 | BBU CPRI Interface Error | 10/24/2025 16:21:49 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0134 | FLM_TE | [8 empty] | API | 10/24/2025 16:28:50 | 10/25/2025 07:27:59 | 10/25/2025 07:57:42 |  |  | 10/25/2025 07:57:53 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000459 | PCM-20251024-00000963 | TT-20251024-01086 | Reference_telecom | Region_4 | JDJZ0761 | JDJZ0761 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 16:31:13 | 10/24/2025 17:26:51 | 10/24/2025 20:31:13 | As per BO request NOKIA MW link JDJZ0761-JED0783 | 10/24/2025 16:29:39 | Critical | 113388 | LOF | 10/24/2025 16:29:42 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDJZ0761-JED0783 | FLM_TE | [8 empty] | API | 10/24/2025 16:31:13 | 10/24/2025 17:26:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000460 | PCM-20251024-00000965 | TT-20251024-01083 | EM | [7 empty] | 10/24/2025 16:33:30 | 10/24/2025 16:33:30 | 10/24/2025 22:33:30 | 1(2G/LTE) sites down under SML2426-P3-CAP/R3_HL_HWBSC01 @ Generator_DG | 10/24/2025 16:25:22 | Major | 21825 | CSL Fault | 10/24/2025 16:25:18 | P3 | 2G |  | Generator_DG | 2G_LTE SA | SML2426-P3-CAP | FLM_EM | SML2426 | Results: DOWN SITE HUB SML2426-P3-CAP SML2426 Summary: Hub: SML2426, Down Count: 1, Down Sites: SML2426-P3-CAP Alarm Summary: SML2426 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 16:33:30 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000461 | PCM-20251024-00000971 | TT-20251024-01094 | Telecom | Region_1 | DAM2474 | DAM2474 | Equipment | BSS_HW_Stuck | Reset RRU | Shakeel Ahmed Hafeez Ameen | 10/24/2025 16:43:19 | 10/25/2025 16:57:34 | 10/25/2025 04:43:19 | RF Unit Maintenance Link Failure at DAM2474-P1-SHOP_SRAN @ Sceco | 10/24/2025 16:38:48 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 16:37:50 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2474 | FLM_TE | [8 empty] | API | 10/24/2025 16:43:19 | 10/24/2025 16:43:21 | 10/25/2025 15:30:27 | 10/25/2025 15:35:42 | 10/25/2025 15:46:19 | 10/25/2025 16:57:34 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000462 | PCM-20251024-00000993 | TT-20251024-01118 | Telecom | Region_2 | RIY2M8802 | RIY2802 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Ejaz Hussain Muhammad Sharif | 10/24/2025 16:56:38 | 10/24/2025 18:27:15 | 10/24/2025 22:56:38 | Cell Unavailable at RIY2M8802-P2-L800-L900 @ Sceco | 10/24/2025 16:55:54 | Major | 29240 | Cell Unavailable | 10/24/2025 16:55:42 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M8802 | FLM_TE | [8 empty] | API | 10/24/2025 16:56:38 | 10/24/2025 17:14:31 | 10/24/2025 18:26:37 | 10/24/2025 18:26:40 | 10/24/2025 18:26:43 | 10/24/2025 18:27:15 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000464 | PCM-20251024-00001000 | TT-20251024-01126 | Reference_telecom | Region_5 | BIK0788 | BIK0788 |  |  |  | Hazem Ali Moustafa Ali | 10/24/2025 17:05:07 | 10/24/2025 17:05:07 | 10/24/2025 21:05:07 | AS per BO request NEC MW Link BIK0788-BIK0153 | 10/24/2025 17:03:54 | Critical | 113388 | LOF | 10/24/2025 17:03:57 | P3 | 2G | makkah | Generator_SG | TX NSA | BIK0788-BIK0153 | FLM_TE | [8 empty] | API | 10/24/2025 17:05:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000465 | PCM-20251024-00001002 | TT-20251024-01129 | EM | Region_4 | TURY0688 | TURY0688 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/24/2025 17:11:11 | 10/25/2025 07:08:54 | 10/25/2025 05:11:11 | SHELTER DOOR OPEN at TURY0688-GSM-P3 @ Sceco | 10/24/2025 17:11:04 | Minor | 7103 | SHELTER DOOR OPEN | 10/24/2025 17:10:53 | P3 | 2G | taif | Sceco | 2G NSA | TURY0688 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/24/2025 17:11:11 | 10/25/2025 07:08:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251024000467 | PCM-20251024-00001006 | TT-20251024-01133 | EM | [7 empty] | 10/24/2025 17:13:46 | 10/24/2025 17:13:46 | 10/25/2025 05:13:46 | COMMERCIAL POWER FAILURE at JDJZ1M8181-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/24/2025 17:05:28 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/24/2025 17:05:15 | P3 | 4G |  | Generator_SG | LTE NSA | JDJZ1M8181 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/24/2025 17:13:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000468 | PCM-20251024-00001010 | TT-20251024-01134 | Telecom | Region_3 | HLJF2M5753 | HLJF0753 | Enviroment | SCECO_Failure | SCECO auto restored | Mazin Meshary AlEnzi | 10/24/2025 17:19:30 | 10/24/2025 18:31:33 | 10/24/2025 23:19:30 | 1(2G) sites down under HLJF0753-P3/R3_HL_HWBSC01 @ Generator_SG | 10/24/2025 17:11:31 | Major | 21807 | OML Fault | 10/24/2025 17:11:23 | P3 | 2G | hail | Generator_SG | 2G SA | HLJF0753-P3 | FLM_TE | HLJF0753 | Results: DOWN SITE HUB HLJF0753-P3 HLJF0753 Summary: Hub: HLJF0753, Down Count: 1, Down Sites: HLJF0753-P3 Alarm Summary: HLJF0753 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 17:19:30 | 10/24/2025 18:11:31 | 10/24/2025 18:31:27 |  |  | 10/24/2025 18:31:33 |  | Mazin Meshary AlEnzi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000470 | PCM-20251024-00001014 | TT-20251024-01142 | Telecom | Region_2 | RIYA6168B | RIYA6168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 17:25:39 | 10/25/2025 11:00:55 | 10/25/2025 05:25:39 | RF Unit Maintenance Link Failure at RIYA6168B-P1-VIP_SRAN @ Sceco | 10/24/2025 17:21:49 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 17:20:05 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYA6168B | FLM_TE | [8 empty] | API | 10/24/2025 17:25:39 | 10/25/2025 08:10:42 | 10/25/2025 11:00:40 |  |  | 10/25/2025 11:00:55 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000471 | PCM-20251024-00001015 | TT-20251024-01144 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/24/2025 17:27:12 | 10/24/2025 21:20:36 | 10/24/2025 23:27:12 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/24/2025 17:19:54 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 17:19:48 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/24/2025 17:27:12 | 10/24/2025 21:20:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000472 | PCM-20251024-00001016 | TT-20251024-01145 | Telecom | Region_2 | RIYA6168B | RIYA6168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 17:28:14 | 10/25/2025 11:01:13 | 10/24/2025 23:28:14 | NR Cell Unavailable at RIYA6168B-P1-VIP_SRAN @ Sceco | 10/24/2025 17:21:39 | Major | 29841 | NR Cell Unavailable | 10/24/2025 17:20:06 | VIP | SRAN | riyadh | Sceco | 5G SA | RIYA6168B | FLM_TE | [8 empty] | API | 10/24/2025 17:28:14 | 10/25/2025 08:10:37 | 10/25/2025 11:00:59 |  |  | 10/25/2025 11:01:13 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000473 | PCM-20251024-00001025 | TT-20251024-01157 | Telecom | Region_4 | JED0514 | JED0514 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 17:38:33 | 10/24/2025 17:38:33 | 10/25/2025 05:38:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0514-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/24/2025 17:37:37 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 17:37:28 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0514 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 17:38:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000474 | PCM-20251024-00001026 | TT-20251024-01158 | EM | Region_4 | JDJZ2156 | JDJZ2156 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/24/2025 17:43:45 | 10/24/2025 19:26:41 | 10/25/2025 05:43:45 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JDJZ2156-G9-L8-L18-SBTS-P3 @ Sceco | 10/24/2025 17:35:22 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/24/2025 17:35:13 | P3 | 2G | qunfuddah | Sceco | 2G NSA | JDJZ2156 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/24/2025 17:43:45 | 10/24/2025 19:26:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000478 | PCM-20251024-00001033 | TT-20251024-01166 | Telecom | Region_3 | HHR5-SEC0037 | SEC0037 |  |  |  | Qaiser abbas | 10/24/2025 17:48:09 | 10/24/2025 17:48:09 | 10/24/2025 23:48:09 | IN_PWR_HIGH ALARM AT HHR5-SEC0037 | 10/24/2025 17:41:34 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/24/2025 17:41:34 | P1 | DWDM | madinah | Sceco | DWDM NSA | HHR5-SEC0037 | FLM_TE | [8 empty] | API | 10/24/2025 17:48:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000479 | PCM-20251024-00001036 | TT-20251024-01168 | Telecom | Region_3 | HLJF2M5753 | HLJF0753 |  |  |  | Mazin Meshary AlEnzi | 10/24/2025 17:51:59 | 10/24/2025 18:11:32 | 10/25/2025 05:51:59 | Monitoring Device Maintenance Link Failure at HLJF2M5753-P3 @ Generator_SG | 10/24/2025 17:47:51 | Minor | 25600 | Monitoring Device Maintenance Link Failure | 10/24/2025 17:47:31 | P3 | 2G | hail | Generator_SG | 2G NSA | HLJF2M5753 | FLM_TE | [8 empty] | API | 10/24/2025 17:51:59 | 10/24/2025 18:11:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000480 | PCM-20251024-00001042 | TT-20251024-01138 | Telecom | Region_6 | BHAB2063 | BHAB2063 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/24/2025 17:58:30 | 10/24/2025 21:25:48 | 10/24/2025 23:58:30 | 2(2G) 2(LTE) sites down under BHAB2069-P3,BHAB2063-P3/BHAB2063-P3 @ Generator_SG | 10/24/2025 17:15:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 17:15:43 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2069-P3 2G_LTE,BHAB2063-P3 2G_LTE | FLM_EM | BHAB2063 | Hub: BHAB2063 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251024-00001013 | Hub: BHAB2063 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: BHAB2063 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/24/2025 17:58:30 | 10/24/2025 21:25:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000482 | PCM-20251024-00001049 | TT-20251024-01181 | Reference_telecom | Region_2 | RIY2M8802 | RIY2802 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Ejaz Hussain Muhammad Sharif | 10/24/2025 18:03:52 | 10/24/2025 18:25:44 | 10/25/2025 00:03:52 | RF Out of Service at RIY2M8802-P2-L800-L900 @ Sceco | 10/24/2025 17:57:45 | Major | 29248 | RF Out of Service | 10/24/2025 17:57:22 | P2 | 4G | riyadh | Sceco | 2G SA | RIY2M8802 | FLM_TE | [8 empty] | API | 10/24/2025 18:03:52 | 10/24/2025 18:11:10 | 10/24/2025 18:25:08 | 10/24/2025 18:25:11 | 10/24/2025 18:25:14 | 10/24/2025 18:25:44 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000483 | PCM-20251024-00001050 | TT-20251024-01171 | Telecom | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/24/2025 18:05:01 | 10/24/2025 18:08:31 | 10/25/2025 00:05:01 | 1(2G) 1(LTE) 2(5G) sites down under JED6020-GSM-P3,JED0253-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/24/2025 17:50:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 17:50:08 | P3 | 2G | jeddah | Sceco | 2G_5G SA | JED0253-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 5G,JED6020-GSM-P3 2G | FLM_EM | JED6020 | Scattered sites:JED6020 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0253 observing LOS TO AIRSCALE Kindly update TT under EM, FLM | PCM-20251024-00001043 | Scattered sites:JED6020 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0253 observing LOS TO AIRSCALE Kindly update TT under EM, FLM | Scattered sites:JED6020 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0253 observing LOS TO AIRSCALE Kindly update TT under EM, FLM |  | sites down |  | API | 10/24/2025 18:05:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000484 | PCM-20251024-00001051 | TT-20251024-01183 | Reference_EM | Region_3 | HHR2085 | HHR2085 |  |  |  | Walid Mohamad Fazil | 10/24/2025 18:05:26 | 10/24/2025 18:05:26 | 10/25/2025 06:05:26 | Minor Rec alarm at HHR2085-P3_SRAN @ Generator_SG | 10/24/2025 17:55:06 | Minor | 65108 | Minor Rec alarm | 10/24/2025 17:55:02 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HHR2085 | FLM_EM | [8 empty] | API | 10/24/2025 18:05:26 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000485 | PCM-20251024-00001052 | TT-20251024-01185 | Reference_EM | Region_3 | MDN2366 | MDN2366 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/24/2025 18:08:00 | 10/24/2025 18:08:00 | 10/25/2025 06:08:00 | Door opening alarm at MDN2366-P3_SRAN @ Sceco | 10/24/2025 18:07:39 | Minor | 65101 | Door opening alarm | 10/24/2025 18:07:34 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2366 | FLM_EM | [8 empty] | API | 10/24/2025 18:08:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000486 | PCM-20251024-00001053 | TT-20251024-01184 | EM | Region_3 | MDN2366 | MDN2366 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/24/2025 18:08:00 | 10/24/2025 18:08:00 | 10/25/2025 06:08:00 | NETECO: Door Status Sensor Alarm at MDN2366 @ Sceco | 10/24/2025 18:07:31 | Minor | 5152 | Door Status Sensor Alarm | 10/24/2025 18:07:31 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2366 | FLM_EM | [8 empty] | API | 10/24/2025 18:08:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000488 | PCM-20251024-00001056 | TT-20251024-01188 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 18:09:02 | 10/25/2025 08:50:15 | 10/25/2025 00:09:02 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/24/2025 15:08:51 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/24/2025 15:08:38 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/24/2025 18:09:02 | 10/25/2025 08:50:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000487 | PCM-20251024-00001055 | TT-20251024-01187 | Telecom | Region_2 | RIY2802 | RIY2802 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Ejaz Hussain Muhammad Sharif | 10/24/2025 18:09:02 | 10/24/2025 18:26:27 | 10/25/2025 00:09:02 | BBU CPRI Interface Error at RIY2802-P2_SRAN @ Sceco | 10/24/2025 18:05:09 | Major | 26234 | BBU CPRI Interface Error | 10/24/2025 18:01:53 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2802 | FLM_TE | [8 empty] | API | 10/24/2025 18:09:02 | 10/24/2025 18:10:54 | 10/24/2025 18:25:52 | 10/24/2025 18:25:55 | 10/24/2025 18:25:59 | 10/24/2025 18:26:27 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000489 | PCM-20251024-00001058 | TT-20251024-00917 | Reference_telecom | Region_4 | JED1MN0771 | JED0771 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 18:13:50 | 10/26/2025 10:36:38 | 10/25/2025 00:13:50 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at JED1MN0771-NR2.6-P3 @ Sceco | 10/24/2025 14:11:02 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 14:10:56 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0771 | FLM_TE |  |  | PCM-20251024-00000820 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:13:50 | 10/26/2025 10:36:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000490 | PCM-20251024-00001059 | TT-20251024-00926 | Telecom | Region_4 | JED1MN2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 18:14:09 | 10/24/2025 18:14:09 | 10/24/2025 22:14:09 | BASE STATION HARDWARE PROBLEM (SFP Transceiver temperature too high) at JED1MN2979-NR2.6-P1-VIP @ Generator_SG | 10/24/2025 14:12:13 | Critical | 7100 | BASE STATION HARDWARE PROBLEM | 10/24/2025 14:12:04 | VIP | 5G | jeddah | Generator_SG | 5G NSA | JED1MN2979 | FLM_TE |  |  | PCM-20251024-00000824 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:14:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000491 | PCM-20251024-00001060 | TT-20251024-01204 | Reference_telecom | Region_4 | BHR0783 | BHR0783 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/24/2025 18:14:21 | 10/24/2025 19:23:53 | 10/25/2025 00:14:21 | BCCH MISSING at BHR0783-P2-USF(Ref:TT-20251024-00843) @ Generator_SG | 10/24/2025 17:48:36 | Major | 7767 | BCCH MISSING | 10/24/2025 17:48:31 | P2 | 2G | jeddah | Generator_SG | 2G_Cell SA | BHR0783 | FLM_TE | [5 empty] | 07 |  |  | API | 10/24/2025 18:14:21 | 10/24/2025 19:23:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000492 | PCM-20251024-00001061 | TT-20251024-00965 | Reference_telecom | Region_4 | FAT2363 | FAT2363 |  |  |  | Ahmad Kamal Abdelmawla | 10/24/2025 18:14:22 | 10/24/2025 23:46:49 | 10/25/2025 06:14:22 | Fronthaul loop back connectivity check failure at FAT2363-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/24/2025 14:24:57 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/24/2025 14:24:51 | P2 | 2G | taif | Sceco | 2G NSA | FAT2363 | FLM_TE |  |  | PCM-20251024-00000868 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:14:22 | 10/24/2025 23:46:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000493 | PCM-20251024-00001062 | TT-20251024-00976 | Reference_telecom | Region_4 | JED1MN0187 | JED0187 |  |  |  | MALIK ATIF ZAMAN | 10/24/2025 18:14:44 | 10/24/2025 18:14:44 | 10/25/2025 06:14:44 | Fronthaul loop back connectivity check failure at JED1MN0187-NR2.6-P2 @ Sceco | 10/24/2025 14:32:43 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/24/2025 14:32:34 | P1 | 5G | jeddah | Sceco | 5G NSA | JED1MN0187 | FLM_TE |  |  | PCM-20251024-00000880 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:14:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000494 | PCM-20251024-00001063 | TT-20251024-01091 | Reference_telecom | Region_4 | JED1MN2045 | JED2045 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 18:14:55 | 10/26/2025 10:36:39 | 10/25/2025 06:14:55 | Fronthaul loop back connectivity check failure at JED1MN2045-NR2.6-P3 @ Sceco | 10/24/2025 16:08:34 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/24/2025 16:08:23 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN2045 | FLM_TE |  |  | PCM-20251024-00000967 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:14:55 | 10/26/2025 10:36:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000495 | PCM-20251024-00001064 | TT-20251024-00842 | Reference_telecom | Region_4 | JED1M7035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 18:17:56 | 10/24/2025 18:17:56 | 10/25/2025 00:17:56 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7035-CA-L900-L800-SBTS @ Sceco | 10/24/2025 13:20:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:20:29 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7035 | FLM_TE |  |  | PCM-20251024-00000754 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:17:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000496 | PCM-20251024-00001065 | TT-20251024-00841 | Reference_telecom | Region_4 | JED0024 | JED0024 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 18:18:11 | 10/26/2025 10:36:39 | 10/25/2025 00:18:11 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at JED0024-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/24/2025 13:19:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 13:19:06 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0024 | FLM_TE |  |  | PCM-20251024-00000753 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:18:11 | 10/26/2025 10:36:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000497 | PCM-20251024-00001066 | TT-20251024-01191 | EM | Region_6 | RYAB1M3648 | RYAB0648 | Equipment | SW | Issue was solved after softaware configuration | Umair Abbas Muhammad Abbas | 10/24/2025 18:18:29 | 10/25/2025 17:17:08 | 10/24/2025 22:18:29 | 1(3G/5G) sites down under RYAB0648-P1-HUB-USF/RYAB1M3648-P1-HUB-USF @ Sceco_STB | 10/24/2025 18:11:03 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/24/2025 18:10:23 | P1 | 3G | turaib | Sceco_STB | 3G_5G SA | RYAB0648-P1-HUB-USF | FLM_EM | RYAB0648 | Results: DOWN SITE HUB RYAB0648-P1-HUB-USF RYAB0648 Summary: Hub: RYAB0648, Down Count: 1, Down Sites: RYAB0648-P1-HUB-USF Alarm Summary: RYAB0648 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 18:18:29 | 10/25/2025 16:34:13 | 10/25/2025 17:16:54 |  |  | 10/25/2025 17:17:08 |  | Umair Abbas Muhammad Abbas |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000498 | PCM-20251024-00001067 | TT-20251024-00831 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 |  |  |  | Mohamed Farag Abdelbary | 10/24/2025 18:18:37 | 10/25/2025 13:02:19 | 10/24/2025 22:18:37 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/24/2025 13:07:07 | Critical | 7654 | CELL OPERATION DEGRADED | 10/24/2025 13:07:00 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251024-00000746 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/24/2025 18:18:37 | 10/25/2025 13:02:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000499 | PCM-20251024-00001068 | TT-20251024-01192 | EM | [7 empty] | 10/24/2025 18:18:59 | 10/24/2025 18:23:01 | 10/25/2025 00:18:59 | 1(2G/5G) sites down under HAW2304-P3/HAW2304-P3 @ Generator_SG | 10/24/2025 18:10:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 18:10:44 | P3 | 2G |  | Generator_SG | 2G SA | HAW2304-P3 | FLM_TE | HAW2304 | Results: DOWN SITE HUB HAW2304-P3 HAW2304 Summary: Hub: HAW2304, Down Count: 1, Down Sites: HAW2304-P3 Alarm Summary: HAW2304 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 18:18:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000501 | PCM-20251024-00001070 | TT-20251024-00993 | Reference_telecom | Region_5 | SHD1M3787 | SHD0787 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/24/2025 18:19:17 | 10/24/2025 18:19:17 | 10/25/2025 00:19:17 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at SHD1M3787-P3 @ Sceco | 10/24/2025 15:11:35 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 13:10:34 | P3 | 3G | makkah | Sceco | 3G NSA | SHD1M3787 | FLM_TE |  |  | PCM-20251024-00000891 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:19:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000502 | PCM-20251024-00001071 | TT-20251024-00990 | Reference_telecom | Region_5 | BIK1M4332 | BIK2332 |  |  |  | Hazem Ali Moustafa Ali | 10/24/2025 18:19:42 | 10/24/2025 18:19:42 | 10/25/2025 00:19:42 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at BIK1M4332-USF @ Generator_SG | 10/24/2025 15:10:56 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 13:10:33 | P3 | 3G | makkah | Generator_SG | 3G NSA | BIK1M4332 | FLM_TE |  |  | PCM-20251024-00000888 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:19:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000503 | PCM-20251024-00001072 | TT-20251024-00759 | Reference_telecom | Region_4 | JED1MN2689 | JED2689 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 18:22:38 | 10/24/2025 18:22:38 | 10/25/2025 00:22:38 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at JED1MN2689-NR2.6-P3 @ Sceco | 10/24/2025 12:01:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 12:01:25 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2689 | FLM_TE |  |  | PCM-20251024-00000676 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/24/2025 18:22:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000504 | PCM-20251024-00001073 | TT-20251024-00910 | Reference_telecom | Region_6 | ABBS1M7157 | ABBS0157 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/24/2025 18:23:50 | 10/25/2025 00:36:49 | 10/25/2025 06:23:50 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at ABBS1M7157-L800-SBTS-P3 @ Sceco | 10/24/2025 14:10:58 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 03:05:07 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M7157 | FLM_TE |  |  | PCM-20251024-00000814 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:23:50 | 10/25/2025 00:32:42 | 10/25/2025 00:36:07 |  |  | 10/25/2025 00:36:49 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000506 | PCM-20251024-00001076 | TT-20251024-00755 | Telecom | Region_5 | MAK1M9028 | MAK0028 | Equipment | BSS_HW_fault | Replace MHA | Zakir Hossan | 10/24/2025 18:26:20 | 10/25/2025 20:03:38 | 10/25/2025 00:26:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9028-P2-CA-L800 @ Sceco | 10/24/2025 12:03:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 12:03:02 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9028 | FLM_TE |  |  | PCM-20251024-00000901 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/24/2025 18:26:20 | 10/25/2025 15:14:43 | 10/25/2025 16:52:06 | 10/25/2025 16:52:09 | 10/25/2025 16:52:13 | 10/25/2025 20:03:38 |  | Zakir Hossan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000507 | PCM-20251024-00001078 | TT-20251024-01209 | Reference_telecom | Region_6 | DAR1M4954 | DAR0954 | Equipment | BSS_HW_Stuck | Reset RRU | Muhammad Usman Aslam | 10/24/2025 18:27:32 | 10/25/2025 08:49:20 | 10/25/2025 00:27:32 | RNW O&M SCENARIO FAILURE at DAR1M4954-P2 @ Sceco | 10/24/2025 17:55:21 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/24/2025 17:54:30 | P3 | 3G | dair | Sceco | 3G NSA | DAR1M4954 | FLM_TE |  |  | PCM-20251024-00001074 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:27:32 | 10/25/2025 08:49:20 | [5 empty] | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000509 | PCM-20251024-00001090 | TT-20251024-01225 | Reference_telecom | Region_2 | BUR6002 | BUR6002 |  |  |  | Raise Ahmed Nisar Ahmed | 10/24/2025 18:34:09 | 10/25/2025 13:13:11 | 10/25/2025 00:34:09 | RFC Port Underpower at BUR6002-DCU1 @ Sceco | 10/24/2025 10:42:15 | Major | 29803 | RFC Port Underpower | 10/24/2025 10:42:07 | VIP | SRAN | buraidah | Sceco | 2G NSA | BUR6002 | FLM_TE | [8 empty] | API | 10/24/2025 18:34:09 | 10/25/2025 13:13:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000510 | PCM-20251024-00001091 | TT-20251024-01226 | Reference_EM | Region_3 | MDQS2500 | MDQS2500 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/24/2025 18:35:24 | 10/25/2025 10:20:59 | 10/25/2025 06:35:24 | NETECO: Low Battery Capacity at MDQS2500 @ Generator_DG | 10/24/2025 18:28:56 | Minor | 11357 | Low Battery Capacity | 10/24/2025 18:28:56 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2500 | FLM_EM | [8 empty] | API | 10/24/2025 18:35:24 | 10/25/2025 10:20:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000512 | PCM-20251024-00001095 | TT-20251024-01029 | Telecom | Region_4 | JED1M7683 | JED0683 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/24/2025 18:38:50 | 10/25/2025 10:34:35 | 10/25/2025 00:38:50 | CELL SERVICE PROBLEM(Sleeping Cell Detection Due To Abnormal Antenna RX Power Measurements) at JED1M7683-P3-CA-L900-L800-SBTS @ Sceco | 10/24/2025 15:33:51 | Major | 7114 | CELL SERVICE PROBLEM | 10/24/2025 15:33:45 | P3 | 4G | jeddah | Sceco | LTE SA | JED1M7683 | FLM_TE |  |  | PCM-20251024-00000918 | While checked found, RTWP degraded in LNCEL-10 between two antenna ports & no high user attached on cell. Please perform HC on SFP, Cable connectivity(RMOD-to BBMOD) & HW on RMOD-3. Please secure approval as action is SA.(SPL monitoring site). | While checked found, RTWP degraded in LNCEL-10 between two antenna ports & no high user attached on cell. Please perform HC on SFP, Cable connectivity(RMOD-to BBMOD) & HW on RMOD-3. Please secure approval as action is SA.(SPL monitoring site). |  |  |  | API | 10/24/2025 18:38:50 | 10/25/2025 10:31:17 | 10/25/2025 10:34:30 |  |  | 10/25/2025 10:34:35 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000513 | PCM-20251024-00001097 | TT-20251024-01135 | Reference_telecom | Region_6 | NJR0116 | NJR0116 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 10/24/2025 18:40:03 | 10/25/2025 01:20:47 | 10/25/2025 06:40:03 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0116-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 15:19:20 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 15:15:37 | P2 | 2G | najran | Sceco | 2G NSA | NJR0116 | FLM_TE |  |  | PCM-20251024-00001007 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:40:03 | 10/24/2025 19:39:30 | 10/25/2025 01:12:18 |  |  | 10/25/2025 01:20:47 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000514 | PCM-20251024-00001098 | TT-20251024-01130 | Reference_telecom | Region_6 | BHAB1M8015 | BHAB2015 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/24/2025 18:40:29 | 10/24/2025 19:15:30 | 10/25/2025 06:40:29 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHAB1M8015-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/24/2025 15:20:31 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 15:11:12 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8015 | FLM_TE |  |  | PCM-20251024-00001003 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:40:29 | 10/24/2025 19:14:45 | 10/24/2025 19:14:54 |  |  | 10/24/2025 19:15:30 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000516 | PCM-20251024-00001101 | TT-20251024-01233 | Reference_EM | Region_3 | HLMD2499 | HLMD2499 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/24/2025 18:42:38 | 10/26/2025 09:09:58 | 10/25/2025 06:42:38 | Generator failure at HLMD2499-P3-USF_SRAN @ Generator_SG | 10/24/2025 18:32:18 | Minor | 65114 | Generator failure | 10/24/2025 18:32:13 | P3 | SRAN | hail | Generator_SG | 2G NSA | HLMD2499 | FLM_EM | [8 empty] | API | 10/24/2025 18:42:38 | 10/26/2025 09:09:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000517 | PCM-20251024-00001102 | TT-20251024-01117 | Reference_telecom | Region_6 | NJR1M7019 | NJR0019 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 10/24/2025 18:42:53 | 10/25/2025 01:20:21 | 10/25/2025 06:42:53 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7019-G9-L18-L21-SBTS-P2-HUB @ Sceco | 10/24/2025 15:20:09 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:55:08 | P2 | 4G | najran | Sceco | LTE NSA | NJR1M7019 | FLM_TE |  |  | PCM-20251024-00000992 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:42:53 | 10/24/2025 19:39:31 | 10/25/2025 01:20:08 |  |  | 10/25/2025 01:20:21 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000518 | PCM-20251024-00001103 | TT-20251024-01116 | Reference_telecom | Region_6 | KHN1M7032 | KHN0032 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:43:08 | 10/24/2025 21:26:25 | 10/25/2025 00:43:08 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHN1M7032-P1-CA-L800-SBTS @ Sceco_STB | 10/24/2025 15:19:37 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:55:00 | P1 | 4G | najran | Sceco_STB | LTE NSA | KHN1M7032 | FLM_TE |  |  | PCM-20251024-00000991 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:43:08 | 10/24/2025 18:51:07 | 10/24/2025 21:26:02 |  |  | 10/24/2025 21:26:25 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000519 | PCM-20251024-00001104 | TT-20251024-01113 | Reference_telecom | Region_6 | NJR1M7371 | NJR0371 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:43:34 | 10/24/2025 21:41:44 | 10/25/2025 00:43:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7371-CA-L800-P3 @ Generator_SG | 10/24/2025 15:20:27 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:41 | P3 | 4G | najran | Generator_SG | LTE NSA | NJR1M7371 | FLM_TE |  |  | PCM-20251024-00000988 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:43:34 | 10/24/2025 18:51:08 | 10/24/2025 21:41:30 |  |  | 10/24/2025 21:41:44 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000520 | PCM-20251024-00001105 | TT-20251024-01235 | EM | Region_6 | RYAB0622 | RYAB0622 |  |  |  | Muhammad Bilal Niamat Ali | 10/24/2025 18:43:39 | 10/24/2025 18:53:38 | 10/25/2025 00:43:39 | SHELTER DOOR OPEN at RYAB0622-GSM-UMTS-P1-HUB @ Sceco_STB | 10/24/2025 18:43:05 | Major | 7103 | SHELTER DOOR OPEN | 10/24/2025 18:42:54 | P1 | 2G | sulail | Sceco_STB | 2G NSA | RYAB0622 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/24/2025 18:43:39 | 10/24/2025 18:53:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000521 | PCM-20251024-00001106 | TT-20251024-01115 | Reference_telecom | Region_6 | NJR0213 | NJR0213 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 10/24/2025 18:44:27 | 10/25/2025 01:20:01 | 10/25/2025 06:44:27 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0213-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 15:19:25 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:55:00 | P2 | 2G | najran | Sceco | 2G NSA | NJR0213 | FLM_TE |  |  | PCM-20251024-00000990 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:44:27 | 10/24/2025 19:39:32 | 10/25/2025 01:19:49 |  |  | 10/25/2025 01:20:01 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000522 | PCM-20251024-00001107 | TT-20251024-01236 | Reference_EM | Region_3 | MDQS0454 | MDQS0454 |  |  |  | Ahmed Hassan Waqialla | 10/24/2025 18:45:13 | 10/24/2025 18:49:20 | 10/25/2025 06:45:13 | Door opening alarm at MDQS0454-P2_SRAN @ Generator_SG | 10/24/2025 18:44:55 | Minor | 65101 | Door opening alarm | 10/24/2025 18:44:51 | P2 | SRAN | madinah | Generator_SG | 2G NSA | MDQS0454 | FLM_EM | [8 empty] | API | 10/24/2025 18:45:13 | 10/24/2025 18:49:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000523 | PCM-20251024-00001109 | TT-20251024-01114 | Reference_telecom | Region_6 | RYN1M7030 | RYN0030 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:47:49 | 10/24/2025 21:27:00 | 10/25/2025 00:47:49 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at RYN1M7030-L800-P3 @ Sceco | 10/24/2025 15:19:32 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:46 | P3 | 4G | najran | Sceco | LTE NSA | RYN1M7030 | FLM_TE |  |  | PCM-20251024-00000989 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:47:49 | 10/24/2025 18:51:08 | 10/24/2025 21:26:44 |  |  | 10/24/2025 21:27:00 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000524 | PCM-20251024-00001110 | TT-20251024-01240 | Reference_telecom | Region_5 | MKTF1M7641 | MKTF0641 |  |  |  | Husain Hassan Ishag Omer | 10/24/2025 18:48:59 | 10/25/2025 11:01:36 | 10/25/2025 00:48:59 | BASE STATION HARDWARE PROBLEM(Connection Unstable At 6Gbps) at MKTF1M7641-P2-USF(ref. TT-20251024-00387) | 10/24/2025 07:23:16 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/24/2025 07:23:16 | P2 | 4G | makkah | Sceco | LTE SA | MKTF1M7641-P2-USF | FLM_TE | [8 empty] | API | 10/24/2025 18:48:59 | 10/25/2025 11:01:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251024000527 | PCM-20251024-00001115 | TT-20251024-01216 | Telecom | Region_5 | MKMD0551 | MKMD0551 |  |  |  | Inam ullah | 10/24/2025 18:52:49 | 10/24/2025 19:44:07 | 10/24/2025 22:52:49 | 1(5G) sites down under MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 10/24/2025 18:25:50 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 18:25:47 | P1 | 2G | makkah | Generator_DG | 2G_3G_5G SA | MAK0320-NR2.6-P1-VIP-HAJJ 5G,USMD0711-P2-USF 2G_3G,MKMD0552-P2 2G_3G,MKMD0553-P2-USF 2G_3G,HSN2454-P2-USF 2G,HSN0453-P2-USF 2G | FLM_TE | MKMD0551 | Site HUB TRM FB MAK0320-NR2.6-P1-VIP-HAJJ 5G MAK0320 observing LOS TO AIRSCALE USMD0711-P2-USF 2G_3G MKMD0551 observing LOS TO AIRSCALE MKMD0552-P2 2G_3G MKMD0551 observing LOS TO AIRSCALE MKMD0553-P2-USF 2G_3G MKMD0551 observing LOS TO AIRSCALE HSN2454-P2-USF 2G MKMD0551 observing LOS TO AIRSCALE HSN0453-P2-USF 2G MKMD0551 observing LOS TO AIRSCALE | PCM-20251024-00001089 | Site HUB TRM FB MAK0320-NR2.6-P1-VIP-HAJJ 5G MAK0320 observing LOS TO AIRSCALE USMD0711-P2-USF 2G_3G MKMD0551 observing LOS TO AIRSCALE MKMD0552-P2 2G_3G MKMD0551 observing LOS TO AIRSCALE MKMD0553-P2-USF 2G_3G MKMD0551 observing LOS TO AIRSCALE HSN2454-P2-USF 2G MKMD0551 observing LOS TO AIRSCALE HSN0453-P2-USF 2G MKMD0551 observing LOS TO AIRSCALE | Site HUB TRM FB MAK0320-NR2.6-P1-VIP-HAJJ 5G MAK0320 observing LOS TO AIRSCALE USMD0711-P2-USF 2G_3G MKMD0551 observing LOS TO AIRSCALE MKMD0552-P2 2G_3G MKMD0551 observing LOS TO AIRSCALE MKMD0553-P2-USF 2G_3G MKMD0551 observing LOS TO AIRSCALE HSN2454-P2-USF 2G MKMD0551 observing LOS TO AIRSCALE HSN0453-P2-USF 2G MKMD0551 observing LOS TO AIRSCALE |  | sites down |  | API | 10/24/2025 18:52:49 | 10/24/2025 19:02:52 | 10/24/2025 19:03:39 | 10/24/2025 19:03:43 | 10/24/2025 19:44:07 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000528 | PCM-20251024-00001116 | TT-20251024-01103 | Reference_telecom | Region_6 | NJR1M7265 | NJR0265 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:53:07 | 10/24/2025 21:40:24 | 10/25/2025 00:53:07 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at NJR1M7265-P3-CA @ Sceco | 10/24/2025 15:20:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:19 | P2 | 4G | najran | Sceco | LTE NSA | NJR1M7265 | FLM_TE |  |  | PCM-20251024-00000978 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:53:07 | 10/24/2025 18:53:33 | 10/24/2025 21:40:08 |  |  | 10/24/2025 21:40:24 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000529 | PCM-20251024-00001117 | TT-20251024-01105 | Reference_telecom | Region_6 | NJR2460 | NJR2460 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:53:18 | 10/24/2025 21:41:25 | 10/25/2025 06:53:18 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR2460-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/24/2025 15:19:30 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:29 | P3 | 2G | najran | Sceco | 2G NSA | NJR2460 | FLM_TE |  |  | PCM-20251024-00000980 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:53:18 | 10/24/2025 18:53:33 | 10/24/2025 21:41:09 |  |  | 10/24/2025 21:41:25 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000530 | PCM-20251024-00001118 | TT-20251024-01109 | Reference_telecom | Region_6 | NJR2452 | NJR2452 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:53:30 | 10/24/2025 21:33:44 | 10/25/2025 06:53:30 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at NJR2452-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/24/2025 15:19:24 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:45 | P3 | 2G | najran | Sceco | 2G NSA | NJR2452 | FLM_TE |  |  | PCM-20251024-00000984 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:53:30 | 10/24/2025 18:53:34 | 10/24/2025 21:33:21 |  |  | 10/24/2025 21:33:44 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000531 | PCM-20251024-00001119 | TT-20251024-01107 | Reference_telecom | Region_6 | NJR2046 | NJR2046 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:53:40 | 10/24/2025 21:39:50 | 10/25/2025 00:53:40 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR2046-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/24/2025 15:19:43 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:55:00 | P3 | 2G | najran | Sceco | 2G NSA | NJR2046 | FLM_TE |  |  | PCM-20251024-00000983 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:53:40 | 10/24/2025 18:54:43 | 10/24/2025 21:39:34 |  |  | 10/24/2025 21:39:50 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000532 | PCM-20251024-00001120 | TT-20251024-01110 | Reference_telecom | Region_6 | NJR1M7043 | NJR0043 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:53:50 | 10/24/2025 21:33:09 | 10/25/2025 06:53:50 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7043-P3-NCA-CA-SBTS @ Generator_SG | 10/24/2025 15:19:26 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:54 | P3 | 4G | najran | Generator_SG | LTE NSA | NJR1M7043 | FLM_TE |  |  | PCM-20251024-00000985 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:53:50 | 10/24/2025 18:54:44 | 10/24/2025 21:32:52 |  |  | 10/24/2025 21:33:09 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000533 | PCM-20251024-00001121 | TT-20251024-01112 | Reference_telecom | Region_6 | NJR1M7266 | NJR0266 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 10/24/2025 18:54:01 | 10/25/2025 01:19:43 | 10/25/2025 00:54:01 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7266-P2 @ Generator_SG | 10/24/2025 15:19:57 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:49 | P2 | 4G | najran | Generator_SG | LTE NSA | NJR1M7266 | FLM_TE |  |  | PCM-20251024-00000987 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:54:01 | 10/24/2025 19:39:32 | 10/25/2025 01:19:30 |  |  | 10/25/2025 01:19:43 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000534 | PCM-20251024-00001123 | TT-20251024-01108 | Reference_telecom | Region_6 | NJR1M8044 | NJR2044 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:57:12 | 10/24/2025 21:32:41 | 10/25/2025 06:57:12 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M8044-G9-L8-L18-L21-SBTS-P3 @ Generator_DG | 10/24/2025 15:20:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:48 | P3 | 4G | najran | Generator_DG | LTE NSA | NJR1M8044 | FLM_TE |  |  | PCM-20251024-00000982 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:57:12 | 10/24/2025 18:57:29 | 10/24/2025 21:32:23 |  |  | 10/24/2025 21:32:41 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000535 | PCM-20251024-00001124 | TT-20251024-01106 | Reference_telecom | Region_6 | NJR2450 | NJR2450 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:57:24 | 10/24/2025 21:32:10 | 10/25/2025 00:57:24 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR2450-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/24/2025 15:19:34 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:55:06 | P3 | 2G | najran | Sceco | 2G NSA | NJR2450 | FLM_TE |  |  | PCM-20251024-00000981 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:57:24 | 10/24/2025 18:57:30 | 10/24/2025 21:31:53 |  |  | 10/24/2025 21:32:10 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000536 | PCM-20251024-00001125 | TT-20251024-01102 | Reference_telecom | Region_6 | NJR0262 | NJR0262 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:57:34 | 10/24/2025 21:31:38 | 10/25/2025 00:57:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0262-CA-L800-NR2.6-SBTS-PI-VIP-ARP @ Generator_SG | 10/24/2025 15:20:08 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:31 | VIP | 2G | najran | Generator_SG | 2G NSA | NJR0262 | FLM_TE |  |  | PCM-20251024-00000977 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:57:34 | 10/24/2025 18:57:36 | 10/24/2025 21:31:17 |  |  | 10/24/2025 21:31:38 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000537 | PCM-20251024-00001126 | TT-20251024-01246 | Reference_telecom | Region_4 | JED2054 | JED2054 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 18:57:36 | 10/24/2025 18:57:36 | 10/25/2025 06:57:36 | LagPortDown observed in JED2054 towards 10.1.225.66 @ Sceco | 10/24/2025 06:58:29 | Minor |  | LagPortDown | 10/24/2025 06:57:30 | P2 | 2G | jeddah | Sceco | TX NSA | JED2054 | FLM_TE | [8 empty] | API | 10/24/2025 18:57:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000538 | PCM-20251024-00001127 | TT-20251024-01247 | Reference_telecom | Region_4 | JED0332 | JED0332 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 18:57:36 | 10/24/2025 18:57:36 | 10/25/2025 06:57:36 | Degrade observed in JED0332 -8 towards 10.1.225.65 @ Sceco | 10/24/2025 06:58:31 | Minor |  | Degrade | 10/24/2025 06:57:30 | P1 | 2G | jeddah | Sceco | TX NSA | JED0332 | FLM_TE | [8 empty] | API | 10/24/2025 18:57:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000539 | PCM-20251024-00001128 | TT-20251024-01104 | Reference_telecom | Region_6 | NJR1M7777 | NJR0777 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:57:44 | 10/24/2025 21:31:02 | 10/25/2025 06:57:44 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7777-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/24/2025 15:19:51 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:10 | P3 | 4G | najran | Sceco | LTE NSA | NJR1M7777 | FLM_TE |  |  | PCM-20251024-00000979 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:57:44 | 10/24/2025 18:57:48 | 10/24/2025 21:30:46 |  |  | 10/24/2025 21:31:02 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000540 | PCM-20251024-00001129 | TT-20251024-01067 | Reference_telecom | Region_6 | NJR2458 | NJR2458 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:57:55 | 10/24/2025 21:27:55 | 10/25/2025 00:57:55 | CELL SERVICE PROBLEM (Phase error exceeds the interference limit) at NJR2458-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/24/2025 15:19:26 | Major | 7114 | CELL SERVICE PROBLEM | 10/24/2025 15:09:50 | P3 | 2G | najran | Sceco | 5G_Cell SA | NJR2458 | FLM_TE |  |  | PCM-20251024-00000954 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:57:55 | 10/24/2025 18:59:20 | 10/24/2025 21:27:38 |  |  | 10/24/2025 21:27:55 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000541 | PCM-20251024-00001130 | TT-20251024-01068 | Reference_telecom | Region_6 | NJR2458 | NJR2458 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 18:58:08 | 10/24/2025 21:28:22 | 10/25/2025 00:58:08 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at NJR2458-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/24/2025 15:44:46 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 15:44:37 | P3 | 2G | najran | Sceco | 2G NSA | NJR2458 | FLM_TE |  |  | PCM-20251024-00000950 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 18:58:08 | 10/24/2025 18:59:21 | 10/24/2025 21:28:06 |  |  | 10/24/2025 21:28:22 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000542 | PCM-20251024-00001132 | TT-20251024-01248 | EM | Region_4 | JED0846 | JED0846 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/24/2025 18:59:09 | 10/24/2025 18:59:09 | 10/25/2025 06:59:09 | SHELTER DOOR OPENED at JED0846-GSM-P3 @ Sceco | 10/24/2025 18:58:54 | Minor | 7103 | SHELTER DOOR OPENED | 10/24/2025 18:58:47 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0846 | FLM_EM | [5 empty] | SHELTER DOOR OPENED |  |  | API | 10/24/2025 18:59:09 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000543 | PCM-20251024-00001133 | TT-20251024-01242 | Reference_telecom | Region_4 | JED0687 | JED0687 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/24/2025 18:59:21 | 10/25/2025 10:34:50 | 10/25/2025 06:59:21 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0687-G9-L18-NR2.6-SBTS-P3 @ Generator_SG | 10/24/2025 18:46:11 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 18:45:57 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0687 | FLM_TE |  |  | PCM-20251024-00001111 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/24/2025 18:59:21 | 10/25/2025 10:31:18 | 10/25/2025 10:34:43 |  |  | 10/25/2025 10:34:50 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000545 | PCM-20251024-00001136 | TT-20251024-01111 | Reference_telecom | Region_6 | NJR2453 | NJR2453 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 19:00:41 | 10/24/2025 21:30:34 | 10/25/2025 07:00:41 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR2453-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/24/2025 15:19:39 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 14:54:39 | P3 | 2G | najran | Sceco | 2G NSA | NJR2453 | FLM_TE |  |  | PCM-20251024-00000986 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/24/2025 19:00:41 | 10/24/2025 19:00:42 | 10/24/2025 21:30:17 |  |  | 10/24/2025 21:30:34 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000546 | PCM-20251024-00001137 | TT-20251024-01250 | Reference_telecom | Region_4 | JED0789 | JED0789 | Transsmission | MW_HW_stuck | Reset Control Card | Moustafa Mahmoud Ahmed Fathelbab | 10/24/2025 19:01:13 | 10/25/2025 14:18:09 | 10/25/2025 07:01:13 | ReplaceableUnitProblem observed in JED0789 towards 10.10.147.50 @ Sceco | 10/24/2025 07:02:47 | Minor |  | ReplaceableUnitProblem | 10/24/2025 07:00:43 | P2 | 2G | jeddah | Sceco | TX NSA | JED0789 | FLM_TE | [8 empty] | API | 10/24/2025 19:01:13 | 10/24/2025 19:23:54 | 10/25/2025 14:17:58 |  |  | 10/25/2025 14:18:09 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000547 | PCM-20251024-00001140 | TT-20251024-01252 | Telecom | Region_2 | RIY0359 | RIY0359 |  |  |  | Asad Ali Nadiq Khan | 10/24/2025 19:03:17 | 10/24/2025 19:03:17 | 10/25/2025 01:03:17 | BBU CPRI Interface Error at RIY0359-P1_SRAN @ Sceco | 10/24/2025 19:00:18 | Major | 26234 | BBU CPRI Interface Error | 10/24/2025 18:57:43 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0359 | FLM_TE | [8 empty] | API | 10/24/2025 19:03:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000549 | PCM-20251024-00001144 | TT-20251024-01256 | Telecom | Region_2 | RIY0359 | RIY0359 |  |  |  | Asad Ali Nadiq Khan | 10/24/2025 19:06:24 | 10/24/2025 19:06:24 | 10/25/2025 01:06:24 | NR Cell Unavailable at RIY0359-P1_SRAN @ Sceco | 10/24/2025 18:59:25 | Major | 29841 | NR Cell Unavailable | 10/24/2025 18:57:52 | P1 | SRAN | riyadh | Sceco | 5G SA | RIY0359 | FLM_TE | [8 empty] | API | 10/24/2025 19:06:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000550 | PCM-20251024-00001146 | TT-20251024-00873 | EM | Region_6 | NJR0777 | NJR0777 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 19:14:40 | 10/24/2025 21:18:49 | 10/25/2025 01:14:40 | 1(2G/LTE) sites down under NJR0777-P3/NJR0777-P3 @ Sceco | 10/24/2025 13:44:36 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 13:44:31 | P3 | 2G | najran | Sceco | 2G_LTE SA | NJR0777-P3 | FLM_TE | NJR0777 | Results: DOWN SITE HUB NJR0777-P3 NJR0777 Summary: Hub: NJR0777, Down Count: 1, Down Sites: NJR0777-P3 Alarm Summary: NJR0777 No Active Alarm on HUB | PCM-20251024-00001114 | Thanks to check locally HUB site NJR0777 | Thanks to check locally HUB site NJR0777 |  | sites down |  | API | 10/24/2025 19:14:40 | 10/24/2025 19:30:21 | 10/24/2025 21:15:56 |  |  | 10/24/2025 21:18:49 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000552 | PCM-20251024-00001148 | TT-20251024-01264 | Reference_EM | Region_1 | RSK2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/24/2025 19:16:35 | 10/25/2025 08:06:01 | 10/25/2025 07:16:35 | high temprature 40 at RSK2086-P2_SRAN @ Sceco | 10/24/2025 19:06:20 | Minor | 65103 | high temprature 40 | 10/24/2025 19:06:17 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2086 | FLM_EM | [8 empty] | API | 10/24/2025 19:16:35 | 10/25/2025 08:06:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000553 | PCM-20251024-00001149 | TT-20251024-01257 | Reference_telecom | Region_5 | MAK0763 | MAK0763 | Equipment | BTS_Cable | Reconnect Fiber Cable | IJAZ ALI | 10/24/2025 19:16:46 | 10/24/2025 23:20:47 | 10/24/2025 23:16:46 | 1(2G) Site down under MAK0763-P1-VIP-HRM(ref. TT-20251024-01165) | 10/24/2025 17:44:46 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 17:44:46 | VIP | 2G | makkah | Sceco | 2G_3G_LTE SA | MAK0763 | FLM_TE | MAK0763 | Results: DOWN SITE HUB MAK0763 MAK0763 Summary: Hub: MAK0763, Down Count: 1, Down Sites: MAK0763 Alarm Summary: MAK0763 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/24/2025 19:16:46 | 10/24/2025 19:26:07 | 10/24/2025 23:20:35 |  |  | 10/24/2025 23:20:47 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000554 | PCM-20251024-00001151 | TT-20251024-01259 | EM | [7 empty] | 10/24/2025 19:18:56 | 10/24/2025 19:18:56 | 10/25/2025 01:18:56 | 1(2G/LTE) sites down under AQQ2426-P3/AQQ2426-P3 @ Generator_SG | 10/24/2025 19:09:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 19:09:27 | P3 | 2G |  | Generator_SG | 2G_LTE SA | AQQ2426-P3 | FLM_EM | AQQ2426 | Results: DOWN SITE HUB AQQ2426-P3 AQQ2426 Summary: Hub: AQQ2426, Down Count: 1, Down Sites: AQQ2426-P3 Alarm Summary: AQQ2426 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 19:18:56 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000559 | PCM-20251024-00001159 | TT-20251024-01274 | Telecom | Region_4 | JED1M8243 | JED2243 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 19:27:03 | 10/24/2025 19:27:03 | 10/25/2025 07:27:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8243-L800-CA-SBTS-P3 @ Sceco | 10/24/2025 19:26:19 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 19:26:10 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8243 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 19:27:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000560 | PCM-20251024-00001160 | TT-20251024-01275 | EM | Region_4 | KHY1M8251 | KHY2251 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/24/2025 19:27:58 | 10/25/2025 16:29:34 | 10/25/2025 07:27:58 | GENERATOR LOW FULE ALARM at KHY1M8251-G9-L8-SBTS-P3 @ Generator_SG | 10/24/2025 19:19:30 | Minor | 7103 | GENERATOR LOW FULE ALARM | 10/24/2025 19:19:24 | P3 | 4G | jeddah | Generator_SG | LTE NSA | KHY1M8251 | FLM_EM | [5 empty] | GENERATOR LOW FULE ALARM |  |  | API | 10/24/2025 19:27:58 | 10/25/2025 16:29:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000563 | PCM-20251024-00001176 | TT-20251024-01297 | EM | Region_3 | BDR2108 | BDR2108 |  |  |  | Muhammad Imran Muhammad Aslam | 10/24/2025 19:41:53 | 10/25/2025 03:18:52 | 10/25/2025 07:41:53 | NETECO: Communication Failure at BDR2108 @ Generator_SG | 10/24/2025 19:35:27 | Minor | 17451 | Communication Failure | 10/24/2025 19:35:27 | P3 | SRAN | yanbu | Generator_SG | 2G NSA | BDR2108 | FLM_EM | [8 empty] | API | 10/24/2025 19:41:53 | 10/25/2025 03:18:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000564 | PCM-20251024-00001178 | TT-20251024-01299 | Reference_telecom | Region_3 | MDN6072 | MDN6072 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/24/2025 19:42:27 | 10/24/2025 21:53:28 | 10/25/2025 01:42:27 | RFC Port Underpower at MDN6072-Sector C-DCU @ Sceco | 10/24/2025 15:34:08 | Major | 29803 | RFC Port Underpower | 10/24/2025 15:37:46 | P3 | SRAN | madinah | Sceco | 2G SA | MDN6072 | FLM_TE | [8 empty] | API | 10/24/2025 19:42:27 | 10/24/2025 21:53:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000566 | PCM-20251024-00001188 | TT-20251024-01308 | EM | Region_6 | BLC0054 | BLC0054 |  |  |  | Sohail Nasir Mir Afzal | 10/24/2025 19:56:30 | 10/24/2025 21:21:33 | 10/25/2025 01:56:30 | 1(2G/3G/LTE) sites down under BLC0054-P3-WBB-G3/BLC0054-P3-WBB-G3 @ Sceco | 10/24/2025 19:48:24 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 19:48:20 | P3 | 2G | Albaha | Sceco | 2G_3G_LTE SA | BLC0054-P3-WBB-G3 | FLM_EM |  | Results: DOWN SITE HUB BLC0054-P3-WBB-G3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/24/2025 19:56:30 | 10/24/2025 21:21:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000567 | PCM-20251024-00001191 | TT-20251024-01239 | Telecom | Region_5 | MKMD0551 | MKMD0551 | Transsmission | MW_HW_fault | Replace IDU | Jawad Ali Bakht Sher Khan | 10/24/2025 20:04:21 | 10/25/2025 04:18:51 | 10/25/2025 00:04:21 | 6(2G) 4(3G) 6(LTE) 2(5G) sites down under SHSN0900-USF-P3 @ Sceco | 10/24/2025 18:43:21 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 18:43:17 | P1 | 2G | makkah | Generator_DG | LTE SA | SHSN0900-USF-P3 | FLM_TE | MKMD0551 | Hub:MKMD0551 We are observing LOS TO AIRSCALE kindly send team to check locally | PCM-20251024-00001164 | Hub:MKMD0551 We are observing LOS TO AIRSCALE kindly send team to check locally | Hub:MKMD0551 We are observing LOS TO AIRSCALE kindly send team to check locally |  | sites down |  | API | 10/24/2025 20:04:21 | 10/25/2025 01:36:34 | 10/25/2025 01:37:20 | 10/25/2025 01:37:24 | 10/25/2025 02:03:05 | 10/25/2025 04:18:51 |  | Jawad Ali Bakht Sher Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000569 | PCM-20251024-00001194 | TT-20251024-01318 | Reference_telecom | Region_5 | HAJ2M1153 | HAJ0153 |  |  |  | Muhammad Saleem Iqbal | 10/24/2025 20:06:09 | 10/26/2025 05:13:14 | 10/25/2025 02:06:09 | GSM Cell out of Service at HAJ2M1153-P3 (REF"TT-20251024-01180) @ Sceco | 10/24/2025 19:54:24 | Major | 21801 | GSM Cell out of Service | 10/24/2025 19:54:21 | P3 | 2G | makkah | Sceco | 2G SA | HAJ2M1153 | FLM_TE | [8 empty] | API | 10/24/2025 20:06:09 | 10/26/2025 05:13:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000574 | PCM-20251024-00001213 | TT-20251024-01337 | Telecom | Region_4 | JED1MN2004 | JED2004 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 20:25:13 | 10/24/2025 20:25:13 | 10/25/2025 02:25:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2004-NR2.6-P2 @ Sceco | 10/24/2025 20:24:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 20:24:11 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2004 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 20:25:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000577 | PCM-20251024-00001220 | TT-20251024-01343 | Telecom | Region_4 | JED1MC2037 | JED2037 |  |  |  | MALIK ATIF ZAMAN | 10/24/2025 20:30:24 | 10/24/2025 20:30:24 | 10/25/2025 02:30:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MC2037-NR3.5-P2 @ Sceco | 10/24/2025 20:29:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 20:29:41 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MC2037 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 20:30:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000583 | PCM-20251024-00001229 | TT-20251024-01355 | EM | [7 empty] | 10/24/2025 20:50:32 | 10/24/2025 20:50:32 | 10/25/2025 08:50:32 | NETECO: Maintenance Reminder at SML2426 @ Generator_DG | 10/24/2025 20:44:28 | Minor | 40563 | Maintenance Reminder | 10/24/2025 20:44:28 | P3 | SRAN |  | Generator_DG | 2G NSA | SML2426 | FLM_EM | [8 empty] | API | 10/24/2025 20:50:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000584 | PCM-20251024-00001230 | TT-20251024-01357 | Telecom | Region_4 | JED2126 | JED2126 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/24/2025 20:54:10 | 10/25/2025 21:03:57 | 10/25/2025 08:54:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/24/2025 20:53:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 20:53:10 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2126 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 20:54:10 | 10/24/2025 23:12:15 | 10/25/2025 19:02:20 | 10/25/2025 19:02:32 | 10/25/2025 19:05:27 | 10/25/2025 21:03:57 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000585 | PCM-20251024-00001233 | TT-20251024-01359 | Telecom | Region_2 | RIYA6168C | RIYA6168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 20:58:17 | 10/25/2025 10:59:46 | 10/25/2025 08:58:17 | RF Unit Maintenance Link Failure at RIYA6168C-P1-VIP_SRAN @ Sceco | 10/24/2025 20:54:36 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 20:52:54 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYA6168C | FLM_TE | [8 empty] | API | 10/24/2025 20:58:17 | 10/25/2025 08:10:57 | 10/25/2025 10:59:34 |  |  | 10/25/2025 10:59:46 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000586 | PCM-20251024-00001235 | TT-20251024-01363 | Telecom | Region_2 | RIYA6168C | RIYA6168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 21:01:24 | 10/25/2025 11:00:05 | 10/25/2025 09:01:24 | NR DU Cell TRP Unavailable at RIYA6168C-P1-VIP_SRAN @ Sceco | 10/24/2025 20:54:29 | Minor | 29870 | NR DU Cell TRP Unavailable | 10/24/2025 20:52:56 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYA6168C | FLM_TE | [8 empty] | API | 10/24/2025 21:01:24 | 10/25/2025 08:10:52 | 10/25/2025 10:59:51 |  |  | 10/25/2025 11:00:05 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000587 | PCM-20251024-00001236 | TT-20251024-01358 | Telecom | Region_2 | RIYA6168C | RIYA6168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 21:01:30 | 10/25/2025 11:00:19 | 10/25/2025 01:01:30 | 1(5G) sites down under RIYA6168C-P1-VIP_SRAN @ Sceco | 10/24/2025 20:54:30 | Critical | 29840 | gNodeB Out of Service | 10/24/2025 20:52:57 | VIP | SRAN | riyadh | Sceco | 5G SA | RIYA6168C-P1-VIP_SRAN | FLM_TE | RIYA6168C | Results: DOWN SITE HUB RIYA6168C-P1-VIP_SRAN RIYA6168C Summary: Hub: RIYA6168C, Down Count: 1, Down Sites: RIYA6168C-P1-VIP_SRAN Alarm Summary: RIYA6168C No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 21:01:30 | 10/25/2025 08:10:47 | 10/25/2025 11:00:09 |  |  | 10/25/2025 11:00:19 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000588 | PCM-20251024-00001240 | TT-20251023-01657 | MW_HC | Region_6 | JDS0803 | JDS0803 |  |  |  | Osama Hadi | 10/24/2025 21:06:21 | 10/25/2025 05:49:09 | 10/25/2025 09:06:21 | As per bo request Nokia MW HC observing link JDS0803-JDS0802 | 10/23/2025 17:14:09 | Minor | 321339 | Demodulator Fail | 10/23/2025 17:14:06 | P1 | 2G | jizan | Sceco | TX NSA | link JDS0803-JDS0802 | FLM_TE |  | Thanks to check modems 5,6&7&8 at JDS0802 still counting error | PCM-20251023-00001823 | Thanks to check modems 5,6&7&8 at JDS0802 still counting error | Thanks to check modems 5,6&7&8 at JDS0802 still counting error |  |  |  | API | 10/24/2025 21:06:21 | 10/25/2025 05:49:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000589 | PCM-20251024-00001241 | TT-20251024-01302 | EM | Region_5 | MLK0699 | MLK0699 |  |  |  | Hassan Ezzelarab Ali Mohamed | 10/24/2025 21:08:13 | 10/24/2025 21:08:13 | 10/25/2025 03:08:13 | 1(2G/5G) sites down under MLK0699-P2-USF/MLK0699-P2-USF @ Generator_SG | 10/24/2025 19:44:19 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 19:44:14 | P2 | 2G | makkah | Generator_SG | 2G_5G SA | MLK0699-P2-USF | FLM_TE | MLK0699 | Results: DOWN SITE HUB MLK0699-P2-USF MLK0699 Summary: Hub: MLK0699, Down Count: 1, Down Sites: MLK0699-P2-USF Alarm Summary: MLK0699 No Active Alarm on HUB | PCM-20251024-00001184 | No Power Issue | No Power Issue |  | sites down |  | API | 10/24/2025 21:08:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251024000590 | PCM-20251024-00001242 | TT-20251024-01314 | Telecom | Region_4 | TAF0281 | TAF0281 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/24/2025 21:08:59 | 10/24/2025 23:39:08 | 10/25/2025 01:08:59 | 2(2G) 1(3G) 2(5G) sites down under TAF2127-P3,TAF0281-P1-HUB/TAF0281-P1-HUB @ Sceco | 10/24/2025 19:57:03 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 19:57:00 | P1 | 2G | taif | Sceco | 2G_3G SA | TAF0281-P1-HUB 2G_3G,TAF2127-P3 2G | FLM_TE | TAF0281 | Results: DOWN SITE HUB TAF0281-P1-HUB TAF0281 TAF2127-P3 TAF0281 Summary: Hub: TAF0281, Down Count: 2, Down Sites: TAF0281-P1-HUB, TAF2127-P3 Alarm Summary: TAF0281 Alarm Active on HUB | PCM-20251024-00001208 | No Power Issue | No Power Issue |  | sites down |  | API | 10/24/2025 21:08:59 | 10/24/2025 21:43:52 | 10/24/2025 21:43:56 | 10/24/2025 21:44:11 | 10/24/2025 21:45:28 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000592 | PCM-20251024-00001244 | TT-20251024-01368 | Telecom | Region_4 | JED0134 | JED0134 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/24/2025 21:09:39 | 10/25/2025 10:12:06 | 10/25/2025 01:09:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0134-G9-L8-L18-L21-NR2.6-NR3.5-P1-HUB-WDM-FON @ Sceco_STB | 10/24/2025 21:08:35 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 21:08:27 | P1 | 2G | jeddah | Sceco_STB | 5G_Cell SA | JED0134 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 21:09:39 | 10/25/2025 10:12:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000595 | PCM-20251024-00001248 | TT-20251024-01361 | Telecom | [7 empty] | 10/24/2025 21:17:08 | 10/25/2025 11:05:02 | 10/25/2025 03:17:08 | 3(2G) 3(LTE) sites down under TBL2319-P3,TBL2284-P3,TBL2286-P3/TBL2286-P3 @ Generator_SG | 10/24/2025 20:56:43 | Major | 7706 | BTS O&M LINK FAILURE | 10/24/2025 20:56:40 | P3 | 2G |  | Generator_SG | 2G_LTE SA | TBL2284-P3 2G_LTE,TBL2286-P3 2G_LTE,TBL2319-P3 2G_LTE | FLM_EM | TBL2284 | Results: DOWN SITE HUB TBL2284-P3 TBL2284 TBL2286-P3 TBL2286 TBL2319-P3 TBL2319 Summary: Hub: TBL2284, Down Count: 1, Down Sites: TBL2284-P3 Hub: TBL2286, Down Count: 1, Down Sites: TBL2286-P3 Hub: TBL2319, Down Count: 1, Down Sites: TBL2319-P3 Alarm Summary: TBL2284 Alarm Active on HUB TBL2286 Alarm Active on HUB TBL2319 Alarm Active on HUB | PCM-20251024-00001238 | TBL2284 | TBL2284 |  | sites down |  | API | 10/24/2025 21:17:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000597 | PCM-20251024-00001254 | TT-20251024-01378 | Telecom | Region_4 | JED0053 | JED0053 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 21:27:13 | 10/26/2025 10:36:39 | 10/25/2025 03:27:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0053-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-SHOP @ Sceco | 10/24/2025 21:26:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 21:26:21 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0053 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 21:27:13 | 10/26/2025 10:36:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000598 | PCM-20251024-00001259 | TT-20251024-01387 | Reference_telecom | Region_1 | SMN0850 | SMN0850 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/24/2025 21:34:27 | 10/25/2025 11:22:28 | 10/25/2025 03:34:27 | RF Unit VSWR Threshold Crossed at SMN0850-P2-USF_SRAN @ Generator_DG | 10/24/2025 18:34:15 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/24/2025 18:34:02 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0850 | FLM_TE | [8 empty] | API | 10/24/2025 21:34:27 | 10/25/2025 11:22:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000600 | PCM-20251024-00001263 | TT-20251024-01390 | Telecom | Region_4 | JED1M7278 | JED0278 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 21:37:33 | 10/24/2025 21:37:33 | 10/25/2025 03:37:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7278-CA-L900-L800-SBTS @ Sceco | 10/24/2025 21:36:48 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 21:36:40 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7278 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 21:37:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000601 | PCM-20251024-00001265 | TT-20251024-01385 | Reference_telecom | Region_2 | RIYB2U6725 | RIYB6025 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/24/2025 21:42:00 | 10/25/2025 08:50:16 | 10/25/2025 09:42:00 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6725-CA-P2 @ Sceco | 10/24/2025 18:32:50 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 18:32:46 | P2 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6725 | FLM_TE |  | Dears Kindly check HW | PCM-20251024-00001258 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/24/2025 21:42:00 | 10/25/2025 08:50:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000602 | PCM-20251024-00001271 | TT-20251024-01393 | Telecom | Region_4 | JED0519 | JED0519 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Mohammed Ramadan A Abu Abid | 10/24/2025 21:53:31 | 10/25/2025 21:04:18 | 10/25/2025 01:53:31 | 7(2G/5G) sites down under JED0519-P2/JED0519-P2 @ Sceco | 10/24/2025 21:45:05 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 21:45:02 | P2 | 2G | jeddah | Sceco | 2G SA | JED0519-P2 | FLM_TE | JED0519 | Results: DOWN SITE HUB JED0519-P2 JED0519 Summary: Hub: JED0519, Down Count: 1, Down Sites: JED0519-P2 Alarm Summary: JED0519 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 21:53:31 | 10/24/2025 23:12:16 | 10/25/2025 10:59:37 | 10/25/2025 10:59:46 | 10/25/2025 11:34:11 | 10/25/2025 21:04:18 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000604 | PCM-20251024-00001275 | TT-20251024-01403 | Telecom | Region_4 | JED1M8609 | JED2609 |  |  |  | BARKAT ALI MAIN HILAL | 10/24/2025 21:57:10 | 10/26/2025 10:36:40 | 10/25/2025 03:57:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8609-P3-L800-CA @ Sceco | 10/24/2025 21:56:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 21:56:06 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8609 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 21:57:10 | 10/26/2025 10:36:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000605 | PCM-20251024-00001276 | TT-20251024-01404 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/24/2025 21:58:12 | 10/24/2025 21:58:12 | 10/25/2025 09:58:12 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/24/2025 21:57:31 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 21:57:26 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 21:58:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000609 | PCM-20251024-00001281 | TT-20251024-01415 | Telecom | Region_3 | MDN2986 | MDN2986 |  |  |  | Junaid Eisa | 10/24/2025 22:01:50 | 10/25/2025 17:36:33 | 10/25/2025 10:01:50 | RF Unit Maintenance Link Failure at MDN2986-P1-WDM_SRAN-FON @ Sceco | 10/24/2025 21:58:17 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 21:56:34 | P1 | SRAN | madinah | Sceco | 2G NSA | MDN2986 | FLM_TE | [8 empty] | API | 10/24/2025 22:01:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251024000612 | PCM-20251024-00001285 | TT-20251024-01421 | Telecom | [7 empty] | 10/24/2025 22:04:24 | 10/24/2025 22:04:24 | 10/25/2025 04:04:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6006-G9-L18-L21-NR3.5-SBTS-MMM @ Sceco | 10/24/2025 22:03:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:03:28 | P3 | 2G |  | Sceco | 5G_Cell SA | JED6006 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 22:04:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000611 | PCM-20251024-00001284 | TT-20251024-01420 | Telecom | Region_3 | MDN2986 | MDN2986 |  |  |  | Junaid Eisa | 10/24/2025 22:04:24 | 10/25/2025 17:36:17 | 10/25/2025 04:04:24 | BBU CPRI Interface Error at MDN2986-P1-WDM_SRAN-FON @ Sceco | 10/24/2025 22:00:09 | Major | 26234 | BBU CPRI Interface Error | 10/24/2025 21:57:35 | P1 | SRAN | madinah | Sceco | 2G NSA | MDN2986 | FLM_TE | [8 empty] | API | 10/24/2025 22:04:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000614 | PCM-20251024-00001288 | TT-20251024-01402 | Reference_telecom | Region_2 | RIYA2U6835 | RIYA6135 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/24/2025 22:05:20 | 10/25/2025 19:14:42 | 10/25/2025 10:05:20 | Cell RX Channel Interference Noise Power Unbalanced at RIYA2U6835-P3-CA @ Sceco | 10/24/2025 18:56:14 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 18:56:11 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYA2U6835 | FLM_TE |  | Dears Kindly check HW | PCM-20251024-00001274 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/24/2025 22:05:20 | 10/25/2025 19:14:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000616 | PCM-20251024-00001291 | TT-20251024-01426 | Telecom | Region_5 | MAK0055 | MAK0055 | Equipment | PMR_Power_Cable_RRU | Replace Power Cable | Mohamed Ramadan abdelmawla Zarie | 10/24/2025 22:05:58 | 10/25/2025 07:02:36 | 10/25/2025 10:05:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0055-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/24/2025 22:05:21 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:05:13 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0055 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 22:05:58 | 10/25/2025 05:24:11 | 10/25/2025 06:20:20 | 10/25/2025 06:20:26 | 10/25/2025 06:20:33 | 10/25/2025 07:02:36 |  | Mohamed Ramadan abdelmawla Zarie |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000617 | PCM-20251024-00001298 | TT-20251024-01423 | Telecom | Region_3 | MDN2986 | MDN2986 |  |  |  | Junaid Eisa | 10/24/2025 22:09:59 | 10/25/2025 17:35:54 | 10/25/2025 02:09:59 | 1(5G) sites down under MDN2986-P1-WDM_SRAN-FON @ Sceco | 10/24/2025 22:03:20 | Critical | 29840 | gNodeB Out of Service | 10/24/2025 22:01:47 | P1 | SRAN | madinah | Sceco | 5G SA | MDN2986-P1-WDM_SRAN-FON | FLM_TE | MDN2986 | Results: DOWN SITE HUB MDN2986-P1-WDM_SRAN-FON MDN2986 Summary: Hub: MDN2986, Down Count: 1, Down Sites: MDN2986-P1-WDM_SRAN-FON Alarm Summary: MDN2986 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 22:09:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000618 | PCM-20251024-00001299 | TT-20251024-01428 | Reference_telecom | Region_3 | YNB0656 | YNB0656 |  |  |  | Muhammad Sajjad R3 | 10/24/2025 22:10:01 | 10/25/2025 14:49:37 | 10/25/2025 10:10:01 | External Clock Reference Problem at YNB0656-P2_SRAN @ Sceco | 10/24/2025 19:07:30 | Minor | 26262 | External Clock Reference Problem | 10/24/2025 19:07:16 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB0656 | FLM_TE |  | Dears Kindly check GNSS | PCM-20251024-00001295 | Dears Kindly check GNSS | Dears Kindly check GNSS |  |  |  | API | 10/24/2025 22:10:01 | 10/25/2025 14:49:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000620 | PCM-20251024-00001308 | TT-20251024-01440 | Telecom | Region_5 | MAK1M9619 | MAK0619 |  |  |  | Husain Hassan Ishag Omer | 10/24/2025 22:15:15 | 10/25/2025 11:01:36 | 10/25/2025 10:15:15 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MAK1M9619-P2-CA-L800-SBTS @ Sceco | 10/24/2025 22:07:14 | Minor | 7115 | BASE STATION INFORMATION | 10/24/2025 22:07:07 | P2 | 4G | makkah | Sceco | LTE NSA | MAK1M9619 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/24/2025 22:15:15 | 10/25/2025 11:01:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000623 | PCM-20251024-00001312 | TT-20251024-01444 | Telecom | Region_4 | HBI1M7353 | HBI0353 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/24/2025 22:17:51 | 10/25/2025 01:15:26 | 10/25/2025 10:17:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at HBI1M7353-G9-L8-L18-SBTS-P3 @ Sceco | 10/24/2025 22:16:59 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:16:49 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | HBI1M7353 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 22:17:51 | 10/25/2025 01:15:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000624 | PCM-20251024-00001313 | TT-20251024-01445 | Telecom | Region_2 | HBT0531 | HBT0531 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Hakim Ullah Raif Ullah Jan | 10/24/2025 22:18:52 | 10/25/2025 00:36:19 | 10/25/2025 10:18:52 | RF Unit Maintenance Link Failure at HBT0531-P1-SHOP_SRAN @ Sceco | 10/24/2025 22:14:13 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 22:13:27 | P1 | SRAN | al kharj | Sceco | 2G NSA | HBT0531 | FLM_TE | [8 empty] | API | 10/24/2025 22:18:52 | 10/24/2025 22:39:11 | 10/24/2025 22:39:18 | 10/24/2025 22:39:20 | 10/25/2025 00:00:11 | 10/25/2025 00:36:19 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000625 | PCM-20251024-00001317 | TT-20251024-01449 | Telecom | Region_2 | HBT2M7531 | HBT0531 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Hakim Ullah Raif Ullah Jan | 10/24/2025 22:21:00 | 10/25/2025 00:36:57 | 10/25/2025 04:21:00 | Cell Unavailable at HBT2M7531-P1-SHOP-L800 @ Sceco | 10/24/2025 22:20:26 | Major | 29240 | Cell Unavailable | 10/24/2025 22:19:50 | P1 | 4G | al kharj | Sceco | LTE SA | HBT2M7531 | FLM_TE | [8 empty] | API | 10/24/2025 22:21:00 | 10/24/2025 22:39:12 | 10/25/2025 00:36:26 | 10/25/2025 00:36:28 | 10/25/2025 00:36:31 | 10/25/2025 00:36:57 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000628 | PCM-20251024-00001320 | TT-20251024-01432 | Reference_telecom | Region_3 | YNB0291 | YNB0291 |  |  |  | Muhammad Sajjad R3 | 10/24/2025 22:23:45 | 10/25/2025 14:49:38 | 10/25/2025 10:23:45 | External Clock Reference Problem at YNB0291-P2_SRAN @ Generator_SG | 10/24/2025 19:14:14 | Minor | 26262 | External Clock Reference Problem | 10/24/2025 19:10:51 | P2 | SRAN | yanbu | Generator_SG | 2G NSA | YNB0291 | FLM_TE |  | Dears Kindly check GNSS | PCM-20251024-00001302 | Dears Kindly check GNSS | Dears Kindly check GNSS |  |  |  | API | 10/24/2025 22:23:45 | 10/25/2025 14:49:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000630 | PCM-20251024-00001325 | TT-20251024-01455 | Telecom | Region_5 | MAK1MN0054 | MAK0054 |  |  |  | Muhammad Shabbir Muhammad | 10/24/2025 22:26:07 | 10/24/2025 22:26:07 | 10/25/2025 02:26:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0054-NR2.6-P1 @ Sceco_STB | 10/24/2025 22:25:25 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:25:14 | P1 | 5G | makkah | Sceco_STB | 5G_Cell SA | MAK1MN0054 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 22:26:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000633 | PCM-20251024-00001330 | TT-20251024-01462 | EM | Region_4 | HBI1M8412 | HBI2412 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/24/2025 22:30:46 | 10/24/2025 22:30:46 | 10/25/2025 10:30:46 | RECTIFIER MODULE FAILURE at HBI1M8412-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/24/2025 22:22:50 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/24/2025 22:22:40 | P3 | 4G | jeddah | Generator_DG | LTE NSA | HBI1M8412 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/24/2025 22:30:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000634 | PCM-20251024-00001332 | TT-20251024-01460 | Reference_telecom | Region_1 | JBKH2M7111 | JBKH0111 |  |  |  | Mohamed Abdelaziz | 10/24/2025 22:30:56 | 10/24/2025 22:34:48 | 10/25/2025 10:30:56 | Cell RX Channel Interference Noise Power Unbalanced at JBKH2M7111-L800-P1 @ Generator_SG | 10/24/2025 19:28:50 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 19:28:47 | P1 | 4G | jubail | Generator_SG | 2G NSA | JBKH2M7111 | FLM_TE |  | Dears Kindly check HW | PCM-20251024-00001329 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/24/2025 22:30:56 | 10/24/2025 22:34:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000635 | PCM-20251024-00001333 | TT-20251024-01458 | EM | Region_1 | KFKM2M5788 | KFKM0788 | Equipment | SW | Issue was solved after softaware configuration | Mahmoud Youssef Mohamed Ahmed | 10/24/2025 22:33:00 | 10/25/2025 00:52:42 | 10/25/2025 04:33:00 | 1(2G/LTE) sites down under KFKM0788-P3/HB1BSCH01 @ Generator_SG | 10/24/2025 22:24:40 | Major | 21825 | CSL Fault | 10/24/2025 22:24:38 | P3 | 2G | hafr | Generator_SG | 2G_LTE SA | KFKM0788-P3 | FLM_EM | KFKM0788 | Results: DOWN SITE HUB KFKM0788-P3 KFKM0788 Summary: Hub: KFKM0788, Down Count: 1, Down Sites: KFKM0788-P3 Alarm Summary: KFKM0788 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 22:33:00 | 10/24/2025 22:43:31 | 10/25/2025 00:26:28 | 10/25/2025 00:26:39 | 10/25/2025 00:26:46 | 10/25/2025 00:52:42 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251024000636 | PCM-20251024-00001334 | TT-20251024-01466 | Reference_EM | Region_3 | MDN2367 | MDN2367 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/24/2025 22:34:53 | 10/24/2025 22:34:53 | 10/25/2025 10:34:53 | Mains Failure at MDN2367-P3_SRAN @ Generator_SG | 10/24/2025 22:25:02 | Minor | 65109 | Mains Failure | 10/24/2025 22:24:56 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDN2367 | FLM_EM | [8 empty] | API | 10/24/2025 22:34:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000639 | PCM-20251024-00001339 | TT-20251024-01471 | Reference_telecom | Region_5 | MAK0654 | MAK0654 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Husain Hassan Ishag Omer | 10/24/2025 22:43:40 | 10/25/2025 15:16:32 | 10/25/2025 10:43:40 | DemXpicLOS observed in MAK0654_04 towards 10.3.227.10 @ Sceco | 10/24/2025 10:44:10 | Minor |  | DemXpicLOS | 10/24/2025 10:43:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0654 | FLM_TE | [8 empty] | API | 10/24/2025 22:43:40 | 10/25/2025 12:57:29 | 10/25/2025 12:57:35 | 10/25/2025 12:57:38 | 10/25/2025 12:57:40 | 10/25/2025 15:16:32 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000640 | PCM-20251024-00001340 | TT-20251024-01472 | EM | Region_3 | RUSF9023 | RUSF9023 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/24/2025 22:46:15 | 10/25/2025 10:47:08 | 10/25/2025 10:46:15 | NETECO: Communication Failure at RUSF9023 @ Generator_DG | 10/24/2025 22:40:08 | Minor | 17451 | Communication Failure | 10/24/2025 22:40:08 | P3 | Repeater | hail | Generator_DG | 2G NSA | RUSF9023 | FLM_EM | [8 empty] | API | 10/24/2025 22:46:15 | 10/25/2025 10:47:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000641 | PCM-20251024-00001341 | TT-20251024-01475 | Reference_EM | Region_1 | ARM2M1709 | ARM0709 | Enviroment | Genset failure_High Temperature | Change Generator radiator | Ahmed Hassan Ahmed Hassanin | 10/24/2025 22:50:54 | 10/25/2025 15:14:14 | 10/25/2025 10:50:54 | Mains Failure at ARM2M1709-P3 @ Generator_SG | 10/24/2025 22:41:05 | Minor | 65109 | Mains Failure | 10/24/2025 22:41:02 | P3 | 2G | jubail | Generator_SG | 2G NSA | ARM2M1709 | FLM_EM | [8 empty] | API | 10/24/2025 22:50:54 | 10/25/2025 05:50:03 | 10/25/2025 15:14:08 |  |  | 10/25/2025 15:14:14 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000642 | PCM-20251024-00001342 | TT-20251024-01476 | Reference_EM | Region_3 | HNK2274 | HNK2274 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/24/2025 22:51:25 | 10/25/2025 10:21:00 | 10/25/2025 10:51:25 | NETECO: AC Failure at HNK2274 @ Generator_SG | 10/24/2025 22:45:05 | Minor | 10202 | AC Failure | 10/24/2025 22:45:05 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HNK2274 | FLM_EM | [8 empty] | API | 10/24/2025 22:51:25 | 10/25/2025 10:21:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000643 | PCM-20251024-00001344 | TT-20251024-01480 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/24/2025 22:52:59 | 10/25/2025 07:39:08 | 10/25/2025 10:52:59 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/24/2025 22:44:40 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/24/2025 22:44:31 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/24/2025 22:52:59 | 10/25/2025 07:39:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000646 | PCM-20251024-00001349 | TT-20251024-01483 | Reference_EM | Region_3 | HNK2274 | HNK2274 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/24/2025 22:55:03 | 10/25/2025 10:21:00 | 10/25/2025 10:55:03 | Mains Failure at HNK2274-P3-USF_SRAN @ Generator_SG | 10/24/2025 22:45:11 | Minor | 65109 | Mains Failure | 10/24/2025 22:45:08 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HNK2274 | FLM_EM | [8 empty] | API | 10/24/2025 22:55:03 | 10/25/2025 10:21:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000650 | PCM-20251024-00001358 | TT-20251024-01489 | EM | Region_6 | RYAB0631 | RYAB0631 | Equipment | SFP_BTS | Clean SFP | Ahmed Mamdouh Helal Helal | 10/24/2025 23:06:59 | 10/25/2025 00:33:17 | 10/25/2025 03:06:59 | 1(2G/3G/5G) sites down under RYAB0631-P1-HUB-USF/RYAB0631-P1-HUB-USF @ Generator_SG | 10/24/2025 22:58:50 | Critical | 7706 | BTS O&M LINK FAILURE | 10/24/2025 22:58:46 | P1 | 2G | wadi dawasar | Generator_SG | 2G_5G SA | RYAB0631-P1-HUB-USF | FLM_EM | RYAB0631 | Results: DOWN SITE HUB RYAB0631-P1-HUB-USF RYAB0631 Summary: Hub: RYAB0631, Down Count: 1, Down Sites: RYAB0631-P1-HUB-USF Alarm Summary: RYAB0631 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/24/2025 23:06:59 | 10/24/2025 23:30:26 | 10/25/2025 00:16:26 | 10/25/2025 00:16:30 | 10/25/2025 00:16:34 | 10/25/2025 00:33:17 |  | Ahmed Mamdouh Helal Helal |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251024000653 | PCM-20251024-00001362 | TT-20251024-01495 | Telecom | Region_5 | SMAK1S9027 | SMAK0027 |  |  |  | Husain Hassan Ishag Omer | 10/24/2025 23:12:58 | 10/25/2025 11:01:37 | 10/25/2025 05:12:58 | 1(LTE) sites down under SMAK0027-P3 @ Sceco | 10/24/2025 23:04:51 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/24/2025 23:04:48 | P3 | 4G | makkah | Sceco | LTE SA | SMAK0027-P3 | FLM_TE | SMAK0027 | Results: DOWN SITE HUB SMAK0027-P3 SMAK0027 Summary: Hub: SMAK0027, Down Count: 1, Down Sites: SMAK0027-P3 Alarm Summary: SMAK0027 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.99.56.92:8080] [URL:http://10.99.56.92:8080/NE3S/1.0/] | sites down |  | API | 10/24/2025 23:12:58 | 10/25/2025 11:01:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000655 | PCM-20251024-00001367 | TT-20251024-01509 | Reference_EM | Region_3 | YBDB2292 | YBDB2292 | Enviroment | Circuit Breaker/Rectifier | Change rectifier main breaker | Eid Fawzi Sayed Ali | 10/24/2025 23:20:53 | 10/25/2025 08:04:19 | 10/25/2025 05:20:53 | Fire Fighting system alarm at YBDB2292-P1-HUB_SRAN @ Generator_DG | 10/24/2025 23:10:39 | Major | 65111 | Fire Fighting system alarm | 10/24/2025 23:10:32 | P1 | SRAN | tabouk | Generator_DG | 2G NSA | YBDB2292 | FLM_EM | [8 empty] | API | 10/24/2025 23:20:53 | 10/25/2025 08:01:11 | 10/25/2025 08:03:47 |  |  | 10/25/2025 08:04:19 |  | Eid Fawzi Sayed Ali |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251024000656 | PCM-20251024-00001369 | TT-20251024-01511 | Telecom | Region_4 | JED1M8042 | JED2042 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/24/2025 23:21:55 | 10/25/2025 06:15:39 | 10/25/2025 05:21:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8042-P1-VIP-CA-L900-L800-SBTS @ Generator_SG | 10/24/2025 23:21:09 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 23:21:02 | VIP | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8042 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/24/2025 23:21:55 | 10/25/2025 06:15:11 | 10/25/2025 06:15:28 | 10/25/2025 06:15:32 | 10/25/2025 06:15:39 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000659 | PCM-20251024-00001372 | TT-20251024-01512 | EM | Region_1 | ARM2M1709 | ARM0709 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Hassan Ahmed Hassanin | 10/24/2025 23:31:59 | 10/25/2025 15:13:32 | 10/25/2025 05:31:59 | 1(2G/3G/LTE) sites down under ARM0709-P3/R1_JB_HWBSC01 @ Generator_SG | 10/24/2025 23:24:52 | Major | 21807 | OML Fault | 10/24/2025 23:24:44 | P3 | 2G | jubail | Generator_SG | 2G_3G_LTE SA | ARM0709-P3 | FLM_EM | ARM0709 | Results: DOWN SITE HUB ARM0709-P3 ARM0709 Summary: Hub: ARM0709, Down Count: 1, Down Sites: ARM0709-P3 Alarm Summary: ARM0709 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/24/2025 23:31:59 | 10/25/2025 05:50:04 | 10/25/2025 15:13:23 | 10/25/2025 15:13:25 |  | 10/25/2025 15:13:32 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000660 | PCM-20251024-00001374 | TT-20251024-01004 | Reference_telecom | Region_6 | NJR2458 | NJR2458 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/24/2025 23:32:13 | 10/25/2025 01:15:27 | 10/25/2025 05:32:13 | BASE STATION SERVICE PROBLEM (Unit synchronization failed) at NJR2458-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/24/2025 15:19:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 15:08:52 | P3 | 2G | najran | Sceco | 5G_Cell SA | NJR2458 | FLM_TE |  |  | PCM-20251024-00000902 | HW alarm active at site, kindly check | HW alarm active at site, kindly check |  |  |  | API | 10/24/2025 23:32:13 | 10/24/2025 23:35:56 | 10/25/2025 01:15:11 |  |  | 10/25/2025 01:15:27 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000664 | PCM-20251024-00001380 | TT-20251024-01312 | Reference_telecom | Region_6 | ZFR1M3035 | ZFR0035 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/24/2025 23:41:27 | 10/25/2025 16:07:21 | 10/25/2025 05:41:27 | CELL FAULTY (Failure in optical RP3 interface) at ZFR1M3035-P3 @ Sceco | 10/24/2025 19:50:51 | Major | 7653 | CELL FAULTY | 10/24/2025 19:50:34 | P3 | 3G | makhwa | Sceco | LTE_Cell SA | ZFR1M3035 | FLM_TE |  |  | PCM-20251024-00001187 | Kindly check the Fiber optical cable at site. | Kindly check the Fiber optical cable at site. |  |  |  | API | 10/24/2025 23:41:27 | 10/25/2025 16:06:55 | 10/25/2025 16:07:12 |  |  | 10/25/2025 16:07:21 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251024000665 | PCM-20251024-00001382 | TT-20251024-01301 | Reference_telecom | Region_4 | JED2864 | JED2864 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/24/2025 23:43:23 | 10/25/2025 04:50:26 | 10/25/2025 05:43:23 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED2864-P3 @ Sceco | 10/24/2025 19:38:46 | Major | 7602 | BCF NOTIFICATION | 10/24/2025 19:38:33 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2864 | FLM_TE |  |  | PCM-20251024-00001179 | 5G tech is having HW alarm active at site, kindly check | 5G tech is having HW alarm active at site, kindly check |  |  |  | API | 10/24/2025 23:43:23 | 10/25/2025 04:49:49 | 10/25/2025 04:50:12 | 10/25/2025 04:50:23 | 10/25/2025 04:50:26 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000666 | PCM-20251024-00001383 | TT-20251024-01298 | Telecom | Region_5 | MAK1M9254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/24/2025 23:43:39 | 10/24/2025 23:43:39 | 10/25/2025 05:43:39 | BASE STATION ANTENNA LINE PROBLEM at MAK1M9254-P1-SHOP-CA-L800-SBTS @ Sceco | 10/24/2025 19:34:55 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 19:34:45 | P1 | 4G | makkah | Sceco | LTE NSA | MAK1M9254 | FLM_TE |  |  | PCM-20251024-00001177 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/24/2025 23:43:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000667 | PCM-20251024-00001384 | TT-20251024-01523 | Telecom | Region_5 | HAJ0011 | HAJ0011 | Equipment | SFP_BTS | Clean SFP | Zakir Hossan | 10/24/2025 23:44:09 | 10/25/2025 15:22:59 | 10/25/2025 11:44:09 | RF Unit CPRI Interface Error at HAJ0011-P3_SRAN @ Sceco | 10/24/2025 23:38:28 | Minor | 26504 | RF Unit CPRI Interface Error | 10/24/2025 23:37:09 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ0011 | FLM_TE | [8 empty] | API | 10/24/2025 23:44:09 | 10/25/2025 12:38:42 | 10/25/2025 13:34:55 | 10/25/2025 13:34:58 | 10/25/2025 13:35:02 | 10/25/2025 15:22:59 |  | Zakir Hossan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000668 | PCM-20251024-00001385 | TT-20251024-01320 | Reference_telecom | Region_6 | ZFR1M3035 | ZFR0035 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/24/2025 23:47:24 | 10/25/2025 16:07:39 | 10/25/2025 05:47:24 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at ZFR1M3035-P3 @ Sceco | 10/24/2025 19:42:33 | Major | 7771 | WCDMA CELL OUT OF USE | 10/24/2025 19:40:23 | P3 | 3G | makhwa | Sceco | 3G SA | ZFR1M3035 | FLM_TE |  |  | PCM-20251024-00001197 | Kindly check the site locally as cells are down due to degraded connectivity | Kindly check the site locally as cells are down due to degraded connectivity |  |  |  | API | 10/24/2025 23:47:24 | 10/25/2025 16:06:55 | 10/25/2025 16:07:32 |  |  | 10/25/2025 16:07:39 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000670 | PCM-20251024-00001387 | TT-20251024-01329 | Telecom | Region_4 | JED0539 | JED0539 | Equipment | FAN Cleaning | Reset FAN | Abdullah Ahmad Mohammad Abdelsheekh | 10/24/2025 23:48:13 | 10/25/2025 18:43:44 | 10/25/2025 11:48:13 | BASE STATION ANTENNA LINE PROBLEM at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/24/2025 20:10:37 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 20:10:28 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0539 | FLM_TE |  |  | PCM-20251024-00001207 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/24/2025 23:48:13 | 10/25/2025 18:14:31 | 10/25/2025 18:27:43 | 10/25/2025 18:28:18 | 10/25/2025 18:28:41 | 10/25/2025 18:43:44 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000671 | PCM-20251024-00001389 | TT-20251024-01338 | Telecom | Region_6 | JIZ1U6797 | JIZ6097 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/24/2025 23:48:31 | 10/25/2025 06:13:59 | 10/25/2025 05:48:31 | BASE STATION ANTENNA LINE PROBLEM at JIZ1U6797-G9-L18-SBTS-P1-VIP-SHOP @ Sceco | 10/24/2025 20:19:28 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 20:19:19 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1U6797 | FLM_TE |  |  | PCM-20251024-00001214 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/24/2025 23:48:31 | 10/25/2025 05:49:10 | 10/25/2025 06:13:52 |  |  | 10/25/2025 06:13:59 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000672 | PCM-20251024-00001390 | TT-20251024-01526 | Telecom | Region_1 | JBRK2M3924 | JBRK0924 |  |  |  | Rafiq Ahmed Elturifi | 10/24/2025 23:48:34 | 10/26/2025 09:36:24 | 10/25/2025 05:48:34 | UMTS Cell Unavailable at JBRK2M3924-P2 @ Sceco | 10/24/2025 23:47:20 | Major | 22202 | UMTS Cell Unavailable | 10/24/2025 23:47:16 | P2 | 3G | jubail | Sceco | 3G SA | JBRK2M3924 | FLM_TE | [8 empty] | API | 10/24/2025 23:48:34 | 10/26/2025 09:36:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000673 | PCM-20251024-00001391 | TT-20251024-01528 | Telecom | Region_3 | RSP0001-MDC-NE8K-M14-02 | RSP0001 |  |  |  | Hossam Ali Ahmed Ali | 10/24/2025 23:51:53 | 10/25/2025 10:12:22 | 10/25/2025 11:51:53 | Bad Package Error Rising at RSP0001-MDC-NE8K-M14-02 @ Sceco | 10/24/2025 23:51:41 | Minor | 101-2501403 | Bad Package Error Rising | 10/24/2025 23:51:34 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | RSP0001-MDC-NE8K-M14-02 | FLM_TE | [8 empty] | API | 10/24/2025 23:51:53 | 10/25/2025 10:12:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000675 | PCM-20251024-00001394 | TT-20251024-01513 | EM | Region_1 | ARM0709 | ARM0709 | Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator | Ahmed Hassan Ahmed Hassanin | 10/24/2025 23:54:36 | 10/25/2025 15:13:12 | 10/25/2025 05:54:36 | 1(2G/3G/LTE) sites down under ARM2771-P3/R1_JB_HWBSC01 @ Sceco | 10/24/2025 23:25:00 | Major | 21825 | CSL Fault | 10/24/2025 23:24:57 | P3 | SRAN | jubail | Generator_SG | 2G_3G_LTE SA | ARM2771-P3 | FLM_EM | ARM0709 | Dear Team, Hub:- ARM0709 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251024-00001388 | Dear Team, Hub:- ARM0709 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- ARM0709 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/24/2025 23:54:36 | 10/25/2025 05:50:05 | 10/25/2025 05:50:30 | 10/25/2025 05:50:33 | 10/25/2025 06:44:02 | 10/25/2025 15:13:12 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251024000676 | PCM-20251024-00001395 | TT-20251024-01529 | Reference_telecom | Region_6 | MKW2344 | MKW2344 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 10/24/2025 23:54:59 | 10/25/2025 08:14:08 | 10/25/2025 11:54:59 | LossOfSignal observed in MKW2344_01 towards 10.221.244.214 @ Generator_SG | 10/24/2025 11:55:57 | Minor |  | LossOfSignal | 10/24/2025 11:54:43 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2344 | FLM_TE | [8 empty] | API | 10/24/2025 23:54:59 | 10/25/2025 01:48:27 | 10/25/2025 08:13:39 |  |  | 10/25/2025 08:14:08 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000677 | PCM-20251024-00001398 | TT-20251024-01346 | Reference_telecom | Region_4 | JED0695 | JED0695 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/24/2025 23:55:47 | 10/24/2025 23:55:47 | 10/25/2025 03:55:47 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0695-P1-HUB @ Sceco | 10/24/2025 20:26:27 | Critical | 7602 | BCF NOTIFICATION | 10/24/2025 20:26:14 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0695 | FLM_TE |  |  | PCM-20251024-00001222 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/24/2025 23:55:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000678 | PCM-20251024-00001399 | TT-20251024-01371 | Reference_telecom | Region_4 | JED1U6831 | JED6131 |  |  |  | Mohamed Farag Abdelbary | 10/24/2025 23:56:40 | 10/25/2025 13:02:20 | 10/25/2025 05:56:40 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/24/2025 21:08:17 | Major | 7654 | CELL OPERATION DEGRADED | 10/24/2025 21:08:06 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251024-00001247 | VSWR alarm active at site, kindly check | VSWR alarm active at site, kindly check |  |  |  | API | 10/24/2025 23:56:40 | 10/25/2025 13:02:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251024000679 | PCM-20251024-00001400 | TT-20251024-01377 | Telecom | Region_4 | JED1U6739 | JED6039 |  |  |  | Mohamed Farag Abdelbary | 10/24/2025 23:57:28 | 10/25/2025 13:02:20 | 10/25/2025 05:57:28 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/24/2025 21:20:13 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 21:20:04 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251024-00001253 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/24/2025 23:57:28 | 10/25/2025 13:02:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251024000680 | PCM-20251024-00001402 | TT-20251024-01531 | Reference_telecom | Region_5 | MAK0989 | MAK0989 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/24/2025 23:59:06 | 10/24/2025 23:59:06 | 10/25/2025 11:59:06 | DemFail observed in MAK0989 towards 10.3.227.11 @ Sceco | 10/24/2025 12:00:42 | Minor |  | DemFail | 10/24/2025 11:58:47 | P3 | 2G | makkah | Sceco | TX NSA | MAK0989 | FLM_TE | [8 empty] | API | 10/24/2025 23:59:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000002 | PCM-20251025-00000006 | TT-20251025-00007 | EM | Region_6 | RYAB0646 | RYAB0646 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Javad Qadir Bukhsh | 10/25/2025 00:03:14 | 10/25/2025 01:32:54 | 10/25/2025 12:03:14 | SHELTER DOOR OPEN at RYAB0646-GSM-UMTS-P3-USF @ Sceco_STB | 10/25/2025 00:03:01 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 00:02:52 | P3 | 2G | turaib | Sceco_STB | 2G NSA | RYAB0646 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 00:03:14 | 10/25/2025 01:10:49 | 10/25/2025 01:28:51 | 10/25/2025 01:28:53 | 10/25/2025 01:29:09 | 10/25/2025 01:32:54 |  | Javad Qadir Bukhsh |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000004 | PCM-20251025-00000009 | TT-20251025-00009 | EM | Region_1 | R1_HF_HWBSC01 | HF1 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/25/2025 00:05:18 | 10/25/2025 08:06:29 | 10/25/2025 04:05:18 | Intruder Alarm(SH1) at R1_HF_HWBSC01 @ Sceco_STB | 10/25/2025 00:04:51 | Critical | 65334 | Intruder Alarm(SH1) | 10/25/2025 00:04:45 | P1 | BSC | hafouf | Sceco_STB | 2G NSA | R1_HF_HWBSC01 | FLM_EM | [8 empty] | API | 10/25/2025 00:05:18 | 10/25/2025 08:05:34 | 10/25/2025 08:06:22 |  |  | 10/25/2025 08:06:29 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000006 | PCM-20251025-00000012 | TT-20251024-01533 | Reference_telecom | Region_3 | YNB2962 | YNB2962 |  |  |  | Muhammad Sajjad R3 | 10/25/2025 00:05:58 | 10/25/2025 14:49:38 | 10/25/2025 12:05:58 | External Clock Reference Problem at YNB2962-P2_SRAN @ Sceco | 10/24/2025 21:03:16 | Minor | 26262 | External Clock Reference Problem | 10/24/2025 20:59:53 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB2962 | FLM_TE |  | Dears Kindly check GNSS | PCM-20251024-00001403 | Dears Kindly check GNSS | Dears Kindly check GNSS |  |  |  | API | 10/25/2025 00:05:58 | 10/25/2025 14:49:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000008 | PCM-20251025-00000013 | TT-20251021-01356 | Telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | BSS_HW_fault | Replace RF Module | Fawad Khan | 10/25/2025 00:06:12 | 10/25/2025 00:38:41 | 10/25/2025 12:06:12 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/21/2025 12:23:41 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 12:23:29 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251024-00001296 | Currently site is clear, if repeats, kindly check the GPS and its location, try to relocate the GPS to lower position. | Currently site is clear, if repeats, kindly check the GPS and its location, try to relocate the GPS to lower position. |  |  |  | API | 10/25/2025 00:06:12 | 10/25/2025 00:32:46 | 10/25/2025 00:37:51 |  |  | 10/25/2025 00:38:41 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000010 | PCM-20251025-00000015 | TT-20251024-01446 | Reference_telecom | Region_4 | JED2179 | JED2179 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 00:08:14 | 10/25/2025 00:08:14 | 10/25/2025 12:08:14 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED2179-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/24/2025 22:14:59 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:14:54 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2179 | FLM_TE |  |  | PCM-20251024-00001315 | RSSI alarm active at site, kindly check and clear | RSSI alarm active at site, kindly check and clear |  |  |  | API | 10/25/2025 00:08:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000012 | PCM-20251025-00000020 | TT-20251025-00011 | EM | Region_2 | ZRN2M1247 | ZRN0247 | Enviroment | Genset failure_AVR | Change Generator AVR | Gul Rahman Gul ZADA | 10/25/2025 00:11:29 | 10/25/2025 04:44:53 | 10/25/2025 06:11:29 | 1(2G/3G/LTE) sites down under ZRN0247-P3/RY1BSCH02 @ Generator_SG | 10/25/2025 00:04:33 | Major | 21825 | CSL Fault | 10/25/2025 00:04:32 | P3 | 2G | rumah | Generator_SG | 2G_3G_LTE SA | ZRN0247-P3 | FLM_EM | ZRN0247 | Results: DOWN SITE HUB ZRN0247-P3 ZRN0247 Summary: Hub: ZRN0247, Down Count: 1, Down Sites: ZRN0247-P3 Alarm Summary: ZRN0247 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 00:11:29 | 10/25/2025 00:25:03 | 10/25/2025 04:44:41 |  |  | 10/25/2025 04:44:53 |  | Gul Rahman Gul ZADA |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000013 | PCM-20251025-00000023 | TT-20251025-00008 | Reference_telecom | Region_2 | RIYB2U6786 | RIYB6086 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/25/2025 00:12:07 | 10/25/2025 19:14:42 | 10/25/2025 12:12:07 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6786-L1800-CA-P3 @ Sceco | 10/24/2025 21:04:23 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/24/2025 21:04:21 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6786 | FLM_TE |  | Dears Kindly check HW | PCM-20251025-00000008 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/25/2025 00:12:07 | 10/25/2025 19:14:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000014 | PCM-20251025-00000025 | TT-20251025-00013 | Telecom | Region_4 | JED0500 | JED0500 | Equipment | BSS_HW_fault | Replace Air Scale | Khaled Mohammad Abdallah | 10/25/2025 00:13:59 | 10/25/2025 23:21:09 | 10/25/2025 06:13:59 | 1(5G) sites down under JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 00:05:42 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 00:05:39 | P2 | 2G | jeddah | Sceco | 5G SA | JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | JED0500 | Results: DOWN SITE HUB JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 JED0500 Summary: Hub: JED0500, Down Count: 1, Down Sites: JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 Alarm Summary: JED0500 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.104.124:8080] [URL:http://10.96.104.124:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 00:13:59 | 10/25/2025 21:38:47 | 10/25/2025 22:05:35 | 10/25/2025 22:06:09 | 10/25/2025 22:06:12 | 10/25/2025 23:21:09 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000015 | PCM-20251025-00000026 | TT-20251024-00542 | Telecom | Region_6 | HUS1M7076 | HUS0076 | Equipment | BSS_HW_fault | Replace RRU | Ansir Iqbal Muhammad Iqbal | 10/25/2025 00:15:25 | 10/25/2025 02:26:48 | 10/25/2025 12:15:25 | BASE STATION ANTENNA LINE PROBLEM at HUS1M7076-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/24/2025 09:03:32 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/24/2025 09:03:25 | P2 | 4G | baish | Sceco | LTE NSA | HUS1M7076 | FLM_TE |  |  | PCM-20251024-00001346 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/25/2025 00:15:25 | 10/25/2025 02:25:50 | 10/25/2025 02:26:22 |  |  | 10/25/2025 02:26:48 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000016 | PCM-20251025-00000027 | TT-20251024-01456 | Reference_telecom | Region_5 | MAK1MN0156 | MAK0156 | Equipment | BSS_HW_fault | Replace Antenna | MOHAMMED JASEEL ARAYIL | 10/25/2025 00:17:15 | 10/25/2025 19:41:33 | 10/25/2025 06:17:15 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at MAK1MN0156-NR2.6-P2 @ Sceco | 10/24/2025 22:21:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:21:29 | P1 | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0156 | FLM_TE |  |  | PCM-20251024-00001324 | Kindly check the RFM at site and perform HC | Kindly check the RFM at site and perform HC |  |  |  | API | 10/25/2025 00:17:15 | 10/25/2025 14:10:20 | 10/25/2025 16:08:28 | 10/25/2025 16:08:30 | 10/25/2025 16:14:11 | 10/25/2025 19:41:33 |  | MOHAMMED JASEEL ARAYIL |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000019 | PCM-20251025-00000031 | TT-20251025-00020 | Reference_telecom | Region_6 | MKW2340 | MKW2340 | Transsmission | MW_HW_stuck | Reset IDU | SHAH KHALID | 10/25/2025 00:19:46 | 10/25/2025 08:15:05 | 10/25/2025 12:19:46 | LossOfSignal observed in MKW2340_02 towards 10.221.244.213 @ Generator_SG | 10/24/2025 12:21:19 | Minor |  | LossOfSignal | 10/24/2025 12:19:26 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2340 | FLM_TE | [8 empty] | API | 10/25/2025 00:19:46 | 10/25/2025 01:48:28 | 10/25/2025 08:14:45 |  |  | 10/25/2025 08:15:05 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000021 | PCM-20251025-00000033 | TT-20251025-00027 | Reference_EM | Region_3 | DBTB2M5269 | DBTB0269 |  |  |  | Walid Attia Shahata Alim | 10/25/2025 00:28:34 | 10/25/2025 06:52:33 | 10/25/2025 12:28:34 | Mains Failure at DBTB2M5269-P3 @ Generator_DG | 10/25/2025 00:18:42 | Minor | 65109 | Mains Failure | 10/25/2025 00:18:37 | P3 | 2G | tabouk | Generator_DG | 2G NSA | DBTB2M5269 | FLM_EM | [8 empty] | API | 10/25/2025 00:28:34 | 10/25/2025 06:52:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000022 | PCM-20251025-00000034 | TT-20251024-01484 | Reference_telecom | Region_5 | MAK0732 | MAK0732 | Equipment | BSS_HW_fault | Replace Antenna | KAMRAN AAMIR | 10/25/2025 00:28:54 | 10/26/2025 10:38:56 | 10/25/2025 12:28:54 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at MAK0732-G9-L800-L1800-L21-NR2.6-SBTS-P2 @ Sceco | 10/24/2025 22:51:52 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:51:44 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0732 | FLM_TE |  |  | PCM-20251024-00001352 | Kindly check and perform HC at site | Kindly check and perform HC at site |  |  |  | API | 10/25/2025 00:28:54 |  | 10/26/2025 10:03:33 | 10/26/2025 10:03:37 | 10/26/2025 10:38:56 |  |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000024 | PCM-20251025-00000037 | TT-20251025-00031 | Telecom | Region_4 | JD1 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/25/2025 00:31:13 | 10/25/2025 00:31:13 | 10/25/2025 06:31:13 | Request for support | 10/25/2025 00:31:05 | Major | 4205 | The interface traffic exceeds the threshold | 10/25/2025 00:31:05 | P1 | BSC | jeddah | Sceco_STB | IPBB NSA | Request for support | FLM_TE | [5 empty] | Request for support |  |  | API | 10/25/2025 00:31:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000025 | PCM-20251025-00000046 | TT-20251025-00029 | EM | Region_4 | JED2050 | JED2050 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Gamal Mohamed Farag | 10/25/2025 00:34:59 | 10/25/2025 05:24:53 | 10/25/2025 06:34:59 | 1(2G/5G) sites down under JED2050-P2/JED2050-P2 @ Sceco | 10/25/2025 00:26:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 00:26:41 | P2 | 2G | jeddah | Sceco | 2G SA | JED2050-P2 | FLM_TE | JED2050 | Results: DOWN SITE HUB JED2050-P2 JED2050 Summary: Hub: JED2050, Down Count: 1, Down Sites: JED2050-P2 Alarm Summary: JED2050 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 00:34:59 | 10/25/2025 02:17:21 | 10/25/2025 03:02:58 | 10/25/2025 03:03:01 | 10/25/2025 03:03:03 | 10/25/2025 05:24:53 |  | Ahmed Gamal Mohamed Farag |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000026 | PCM-20251025-00000048 | TT-20251025-00041 | EM | Region_3 | MDTB2547 | MDTB2547 |  |  |  | Mohammed Sadeq Nawaz | 10/25/2025 00:43:01 | 10/25/2025 00:43:01 | 10/25/2025 12:43:01 | NETECO: Communication Fail at MDTB2547 @ Generator_DG | 10/25/2025 00:36:44 | Minor | 20001 | Communication Fail | 10/25/2025 00:36:44 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDTB2547 | FLM_EM | [8 empty] | API | 10/25/2025 00:43:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000031 | PCM-20251025-00000057 | TT-20251023-00069 | MW_HC | Region_6 | QIS0267 | QIS0267 |  |  |  | Muhammad Ali | 10/25/2025 00:59:02 | 10/25/2025 01:40:05 | 10/25/2025 12:59:02 | As BO Requested MW Nokia Observing ACM Degraded on MW Link QIS0267-QIS0031 | 10/23/2025 00:48:44 | Minor | 113388 | LOF | 10/23/2025 00:48:46 | P3 | 2G | jizan | Sceco | TX NSA | QIS0267-QIS0031 | FLM_TE |  | HW approved thanks to share after HC completed | PCM-20251024-00001392 | HW approved thanks to share after HC completed | HW approved thanks to share after HC completed |  |  |  | API | 10/25/2025 00:59:02 | 10/25/2025 01:40:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000032 | PCM-20251025-00000059 | TT-20251025-00054 | EM | Region_4 | NNL0139 | NNL0139 | Equipment | FAN Cleaning | Reset FAN | Basyouni Kotb Basyouni Eldabsha | 10/25/2025 01:02:29 | 10/25/2025 09:09:28 | 10/25/2025 07:02:29 | 1(2G/3G) sites down under NNL0139-P3/NNL0139-P3 @ Generator_SG | 10/25/2025 00:54:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 00:54:26 | P3 | 2G | qunfuddah | Generator_SG | 2G_3G SA | NNL0139-P3 | FLM_EM | NNL0139 | Results: DOWN SITE HUB NNL0139-P3 NNL0139 Summary: Hub: NNL0139, Down Count: 1, Down Sites: NNL0139-P3 Alarm Summary: NNL0139 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 01:02:29 | 10/25/2025 09:08:58 | 10/25/2025 09:09:03 | 10/25/2025 09:09:14 | 10/25/2025 09:09:17 | 10/25/2025 09:09:28 |  | Basyouni Kotb Basyouni Eldabsha |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000035 | PCM-20251025-00000065 | TT-20251025-00062 | EM | Region_6 | BHAB0836 | BHAB0836 |  |  |  | Zia Ur Rahamn | 10/25/2025 01:05:15 | 10/25/2025 15:51:54 | 10/25/2025 13:05:15 | AIRCON 1 FAILURE at BHAB0836-GSM-UMTS-P3 @ Sceco | 10/25/2025 00:57:02 | Minor | 7103 | AIRCON 1 FAILURE | 10/25/2025 00:56:56 | P3 | 2G | mohail | Sceco | 2G NSA | BHAB0836 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/25/2025 01:05:15 | 10/25/2025 08:10:27 | 10/25/2025 15:51:35 | 10/25/2025 15:51:38 | 10/25/2025 15:51:54 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000037 | PCM-20251025-00000069 | TT-20251024-01530 | Reference_telecom | Region_4 | HAW1M8355 | HAW2355 |  |  |  | Rashid Shafique | 10/25/2025 01:08:52 | 10/25/2025 12:02:16 | 10/25/2025 13:08:52 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at HAW1M8355-G9-L18-L21-SBTS-P3 @ Sceco | 10/24/2025 23:53:54 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 05:19:15 | P3 | 4G | taif | Sceco | LTE NSA | HAW1M8355 | FLM_TE |  | Thanks to check HAW2355-HAW0333 | PCM-20251025-00000022 | Thanks to check HAW2355-HAW0333 | Thanks to check HAW2355-HAW0333 |  |  |  | API | 10/25/2025 01:08:52 | 10/25/2025 12:02:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000040 | PCM-20251025-00000074 | TT-20251025-00069 | Telecom | Region_2 | RIYB2U6104 | RIYB6004 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/25/2025 01:17:59 | 10/25/2025 19:14:43 | 10/25/2025 07:17:59 | 1(2G) sites down under RIYB6004-P3/R2_RY4_HWBSC01 @ Sceco | 10/25/2025 01:09:37 | Major | 21825 | CSL Fault | 10/25/2025 01:09:34 | P3 | 2G | riyadh | Sceco | 2G SA | RIYB6004-P3 | FLM_TE | RIYB6004 | Results: DOWN SITE HUB RIYB6004-P3 RIYB6004 Summary: Hub: RIYB6004, Down Count: 1, Down Sites: RIYB6004-P3 Alarm Summary: RIYB6004 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 01:17:59 | 10/25/2025 19:14:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000041 | PCM-20251025-00000076 | TT-20251025-00071 | EM | Region_6 | MHL0124 | MHL0124 |  |  |  | Zia Ur Rahamn | 10/25/2025 01:21:29 | 10/25/2025 08:10:27 | 10/25/2025 07:21:29 | 1(2G/3G/5G) sites down under MHL0124-P2/MHL0124-P2 @ Sceco | 10/25/2025 01:13:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 01:13:44 | P2 | 2G | mohail | Sceco | 2G_3G_5G SA | MHL0124-P2 | FLM_EM | MHL0124 | Results: DOWN SITE HUB MHL0124-P2 MHL0124 Summary: Hub: MHL0124, Down Count: 1, Down Sites: MHL0124-P2 Alarm Summary: MHL0124 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 01:21:29 | 10/25/2025 08:10:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000045 | PCM-20251025-00000084 | TT-20251025-00081 | Telecom | Region_1 | HFF6028 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 01:24:53 | 10/25/2025 20:22:37 | 10/25/2025 13:24:53 | RF Unit Maintenance Link Failure at HFF6028-DCU1 @ Sceco | 10/25/2025 01:11:42 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 01:19:31 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/25/2025 01:24:53 | 10/25/2025 08:43:39 | 10/25/2025 20:22:26 |  |  | 10/25/2025 20:22:37 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000048 | PCM-20251025-00000087 | TT-20251025-00078 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace CB on Rectifier | DILSHAD ALI ABDUL HAMEED | 10/25/2025 01:28:29 | 10/26/2025 07:11:29 | 10/25/2025 05:28:29 | 1(5G) sites down under RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/25/2025 01:20:31 | Critical | 29840 | gNodeB Out of Service | 10/25/2025 01:20:20 | VIP | SRAN | riyadh | Sceco | 5G SA | RIY0964-P1-PNU-VIP_SRAN | FLM_TE | RIY0964 | Results: DOWN SITE HUB RIY0964-P1-PNU-VIP_SRAN RIY0964 Summary: Hub: RIY0964, Down Count: 1, Down Sites: RIY0964-P1-PNU-VIP_SRAN Alarm Summary: RIY0964 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 01:28:29 | 10/26/2025 07:08:31 | 10/26/2025 07:10:20 |  |  | 10/26/2025 07:11:29 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000049 | PCM-20251025-00000090 | TT-20251025-00093 | Reference_telecom | Region_4 | JED2069 | JED2069 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 01:38:18 | 10/25/2025 01:38:18 | 10/25/2025 13:38:18 | LagPortDown observed in JED2069 towards 10.1.230.52 @ Generator_SG | 10/24/2025 13:38:46 | Minor |  | LagPortDown | 10/24/2025 13:37:59 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2069 | FLM_TE | [8 empty] | API | 10/25/2025 01:38:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000050 | PCM-20251025-00000094 | TT-20251025-00092 | Telecom | Region_1 | UQR2M1681 | UQR0681 |  |  |  | Mohamed Magdy Fouad Zayed | 10/25/2025 01:41:29 | 10/25/2025 17:36:59 | 10/25/2025 07:41:29 | 1(2G) sites down under UQR0681-P3-USF/R1_DM_HWBSC01 @ Power Cube | 10/25/2025 01:33:14 | Major | 21825 | CSL Fault | 10/25/2025 01:33:12 | P3 | 2G | hafouf | Power Cube | 2G SA | UQR0681-P3-USF | FLM_TE | UQR0681 | Results: DOWN SITE HUB UQR0681-P3-USF UQR0681 Summary: Hub: UQR0681, Down Count: 1, Down Sites: UQR0681-P3-USF Alarm Summary: UQR0681 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 01:41:29 | 10/25/2025 17:36:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000052 | PCM-20251025-00000098 | TT-20251025-00101 | EM | Region_5 | HHR0428 | HHR0428 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/25/2025 01:50:42 | 10/25/2025 02:35:32 | 10/25/2025 13:50:42 | RECTIFIER MAINS POWER FAILURE at HHR0428-G9-L8-L18-NR2.6-SBTS-P3 @ Generator_SG | 10/25/2025 01:42:27 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 01:42:21 | P3 | 2G | makkah | Generator_SG | 2G NSA | HHR0428 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 01:50:42 | 10/25/2025 02:35:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000053 | PCM-20251025-00000099 | TT-20251025-00102 | Reference_telecom | Region_4 | JED0791 | JED0791 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 01:53:48 | 10/25/2025 01:53:48 | 10/25/2025 13:53:48 | Degrade observed in JED0791 towards 10.10.180.7 @ Sceco | 10/24/2025 13:54:14 | Minor |  | Degrade | 10/24/2025 13:53:25 | P2 | 2G | jeddah | Sceco | TX NSA | JED0791 | FLM_TE | [8 empty] | API | 10/25/2025 01:53:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000056 | PCM-20251025-00000104 | TT-20251025-00104 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to SCECO failure, was auto restored | Waseem Shahzad Ghulam Rasool | 10/25/2025 02:06:59 | 10/25/2025 12:36:44 | 10/25/2025 06:06:59 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/25/2025 01:58:53 | Critical | 301 | NE Is Disconnected | 10/25/2025 01:58:50 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 02:06:59 | 10/25/2025 12:36:14 | 10/25/2025 12:36:21 |  |  | 10/25/2025 12:36:44 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000057 | PCM-20251025-00000111 | TT-20251025-00117 | EM | Region_3 | RUSF9012 | RUSF9012 |  |  |  | Muhammad Imran Muhammad Aslam | 10/25/2025 02:15:30 | 10/25/2025 03:18:52 | 10/25/2025 14:15:30 | NETECO: Communication Fail at RUSF9012 @ Generator_SG | 10/25/2025 02:09:25 | Minor | 20001 | Communication Fail | 10/25/2025 02:09:25 | P3 | Repeater | madinah | Generator_SG | 2G NSA | RUSF9012 | FLM_EM | [8 empty] | API | 10/25/2025 02:15:30 | 10/25/2025 03:18:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000062 | PCM-20251025-00000123 | TT-20251025-00124 | Telecom | Region_4 | JED0053 | JED0053 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 02:26:31 | 10/26/2025 10:36:40 | 10/25/2025 06:26:31 | 1(2G) sites down under JED0053-P1-SHOP/JED0053-P1-SHOP @ Sceco | 10/25/2025 02:18:27 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 02:18:20 | P1 | 2G | jeddah | Sceco | 2G SA | JED0053-P1-SHOP | FLM_TE | JED0053 | Results: DOWN SITE HUB JED0053-P1-SHOP JED0053 Summary: Hub: JED0053, Down Count: 1, Down Sites: JED0053-P1-SHOP Alarm Summary: JED0053 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 02:26:31 | 10/26/2025 10:36:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000064 | PCM-20251025-00000126 | TT-20251025-00132 | EM | Region_2 | QSDH2M1714 | QSDH0714 |  |  |  | Moustafa Elzaafarany Abdellah | 10/25/2025 02:32:29 | 10/25/2025 05:02:28 | 10/25/2025 08:32:29 | 1(2G/3G) sites down under QSDH0714-P2/R2_BR1_HWBSC01 @ Sceco | 10/25/2025 02:25:12 | Major | 21807 | OML Fault | 10/25/2025 02:25:06 | P2 | 2G | dawadmi | Sceco | 2G_3G SA | QSDH0714-P2 | FLM_EM | QSDH0714 | Results: DOWN SITE HUB QSDH0714-P2 QSDH0714 Summary: Hub: QSDH0714, Down Count: 1, Down Sites: QSDH0714-P2 Alarm Summary: QSDH0714 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 02:32:29 | 10/25/2025 05:02:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000067 | PCM-20251025-00000132 | TT-20251025-00147 | Telecom | Region_5 | MAK2208 | MAK2208 | Equipment | BSS_HW_fault | Replace Antenna | KAMRAN AAMIR | 10/25/2025 02:36:41 | 10/25/2025 13:57:43 | 10/25/2025 14:36:41 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2208-G9-NL8-NL18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/25/2025 02:35:48 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 02:35:43 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2208 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 02:36:41 | 10/25/2025 11:05:33 | 10/25/2025 11:41:22 | 10/25/2025 11:41:27 | 10/25/2025 12:06:35 | 10/25/2025 13:57:43 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000071 | PCM-20251025-00000139 | TT-20251025-00151 | EM | Region_3 | HLUL2M2300 | HLUL2300 |  |  |  | Muhamed Ismail Muhamed Daoud | 10/25/2025 02:48:59 | 10/25/2025 02:48:59 | 10/25/2025 08:48:59 | 1(2G/3G) sites down under HLUL2300-P2/R3_TB_HWBSC01 @ Generator_SG | 10/25/2025 02:41:45 | Major | 21825 | CSL Fault | 10/25/2025 02:41:40 | P2 | 2G | hail | Generator_SG | 2G_3G SA | HLUL2300-P2 | FLM_EM | HLUL2300 | Results: DOWN SITE HUB HLUL2300-P2 HLUL2300 Summary: Hub: HLUL2300, Down Count: 1, Down Sites: HLUL2300-P2 Alarm Summary: HLUL2300 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 02:48:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000073 | PCM-20251025-00000141 | TT-20251025-00157 | Reference_telecom | Region_4 | JED0637 | JED0637 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 02:51:09 | 10/25/2025 02:51:09 | 10/25/2025 14:51:09 | DemFail observed in JED0637_02 towards 10.10.183.195 @ Sceco | 10/24/2025 14:51:27 | Minor |  | DemFail | 10/24/2025 14:50:50 | VIP | 2G | jeddah | Sceco | TX NSA | JED0637 | FLM_TE | [8 empty] | API | 10/25/2025 02:51:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000075 | PCM-20251025-00000148 | TT-20251025-00166 | Reference_EM | Region_2 | QSDH2M5891 | QSDH0891 | Equipment | FAN Cleaning | Clean FAN | Moustafa Elzaafarany Abdellah | 10/25/2025 02:56:49 | 10/25/2025 06:24:36 | 10/25/2025 14:56:49 | Minor Rec. alarm at QSDH2M5891-P3 @ Generator_SG | 10/25/2025 02:46:23 | Minor | 65108 | Minor Rec. alarm | 10/25/2025 02:46:21 | P3 | 2G | dawadmi | Generator_SG | 2G NSA | QSDH2M5891 | FLM_EM | [8 empty] | API | 10/25/2025 02:56:49 | 10/25/2025 05:02:29 | 10/25/2025 05:39:39 | 10/25/2025 05:39:42 | 10/25/2025 05:40:04 | 10/25/2025 06:24:36 |  | Moustafa Elzaafarany Abdellah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251023000983 | PCM-20251023-00002141 | TT-20251023-02137 | Reference_EM | Region_2 | RIY2115 | RIY2115 |  |  |  | Pawan Virdi Santokh Singh | 10/23/2025 22:56:41 | 10/25/2025 10:05:48 | 10/24/2025 10:56:41 | Mains Failure at RIY2115-P3_SRAN @ Sceco | 10/23/2025 22:46:34 | Minor | 65109 | Mains Failure | 10/23/2025 22:46:30 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2115 | FLM_EM | [8 empty] | API | 10/23/2025 22:56:41 | 10/25/2025 10:05:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251023000997 | PCM-20251023-00002164 | TT-20251023-02160 | Reference_EM | Region_2 | RIY2058 | RIY2058 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/23/2025 23:18:26 | 10/24/2025 12:28:53 | 10/24/2025 11:18:26 | Low battery voltage at RIY2058-P2_SRAN @ Sceco | 10/23/2025 23:07:54 | Minor | 65110 | Low battery voltage | 10/23/2025 23:07:52 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2058 | FLM_EM | [8 empty] | API | 10/23/2025 23:18:26 | 10/24/2025 12:28:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000005 | PCM-20251024-00000010 | TT-20251024-00014 | Reference_EM | Region_2 | RIY0809 | RIY0809 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 00:11:36 | 10/24/2025 12:28:53 | 10/24/2025 12:11:36 | Minor Rec alarm at RIY0809-P2_SRAN @ Sceco | 10/24/2025 00:01:07 | Minor | 65108 | Minor Rec alarm | 10/24/2025 00:01:05 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0809 | FLM_EM | [8 empty] | API | 10/24/2025 00:11:36 | 10/24/2025 12:28:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000012 | PCM-20251024-00000030 | TT-20251024-00034 | Reference_EM | Region_2 | RIY2323 | RIY2323 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 00:31:46 | 10/24/2025 12:28:54 | 10/24/2025 12:31:46 | Air condition 1 failure alarm at RIY2323-P2_SRAN-PC @ Sceco | 10/24/2025 00:21:06 | Minor | 65104 | Air condition 1 failure alarm | 10/24/2025 00:21:02 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2323 | FLM_EM | [8 empty] | API | 10/24/2025 00:31:46 | 10/24/2025 12:28:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000053 | PCM-20251024-00000116 | TT-20251024-00134 | Reference_EM | Region_2 | HIL2471 | HIL2471 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Farman Ullah Muhammad Nazir | 10/24/2025 02:16:06 | 10/26/2025 02:20:52 | 10/24/2025 14:16:06 | Door opening alarm at HIL2471-P2_SRAN @ Sceco | 10/24/2025 02:15:40 | Minor | 65101 | Door opening alarm | 10/24/2025 02:15:37 | P2 | SRAN | al rass | Sceco | 2G NSA | HIL2471 | FLM_EM | [8 empty] | API | 10/24/2025 02:16:06 | 10/25/2025 07:59:04 | 10/26/2025 01:41:57 | 10/26/2025 01:42:01 | 10/26/2025 01:42:03 | 10/26/2025 02:20:52 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000054 | PCM-20251024-00000117 | TT-20251024-00135 | Reference_EM | Region_2 | RIY0405 | RIY0405 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/24/2025 02:16:07 | 10/24/2025 22:02:13 | 10/24/2025 14:16:07 | Air condition 1 failure alarm at RIY0405-P2_SRAN @ Sceco | 10/24/2025 02:14:17 | Minor | 65104 | Air condition 1 failure alarm | 10/24/2025 01:33:33 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0405 | FLM_EM | [8 empty] | API | 10/24/2025 02:16:07 | 10/24/2025 22:02:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000061 | PCM-20251024-00000149 | TT-20251024-00171 | Reference_EM | Region_1 | SMN0806 | SMN0806 |  |  |  | Rahman Ullah Said Halim | 10/24/2025 03:00:36 | 10/25/2025 11:32:58 | 10/24/2025 15:00:36 | low fuel alarm at SMN0806-P2_SRAN @ Generator_DG | 10/24/2025 02:50:09 | Minor | 65115 | low fuel alarm | 10/24/2025 02:50:06 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/24/2025 03:00:36 | 10/25/2025 11:32:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251024000074 | PCM-20251024-00000191 | TT-20251024-00224 | EM | Region_2 | RIY0202 | RIY0202 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 03:44:31 | 10/24/2025 12:28:55 | 10/24/2025 07:44:31 | ACU FAILURE at RIY0202_OCS @ Sceco | 10/24/2025 03:42:42 | Critical | 1-12307 | ACU FAILURE | 10/24/2025 03:42:33 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0202 | FLM_EM | [5 empty] | 0-TO RIY0041(1-A)-72-E1EFI-ACU FAILURE:2 |  |  | API | 10/24/2025 03:44:31 | 10/24/2025 12:28:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251024000093 | PCM-20251024-00000246 | TT-20251024-00293 | Reference_EM | Region_2 | KHJ0995 | KHJ0995 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Fritz Ian Generale | 10/24/2025 04:39:16 | 10/24/2025 20:48:09 | 10/24/2025 16:39:16 | Generator failure at KHJ0995-P2-USF_SRAN-PC @ Sceco | 10/24/2025 04:28:44 | Minor | 65114 | Generator failure | 10/24/2025 04:28:41 | P2 | SRAN | al kharj | Sceco | 2G NSA | KHJ0995 | FLM_EM | [8 empty] | API | 10/24/2025 04:39:16 | 10/24/2025 20:47:40 | 10/24/2025 20:47:55 |  |  | 10/24/2025 20:48:09 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000127 | PCM-20251024-00000305 | TT-20251024-00346 | Reference_EM | Region_2 | RIY0657 | RIY0657 |  |  |  | Moin Uddin | 10/24/2025 05:42:16 | 10/25/2025 12:16:17 | 10/24/2025 17:42:16 | Air condition 1 failure alarm at RIY0657-P2_SRAN @ Sceco | 10/24/2025 05:31:58 | Minor | 65104 | Air condition 1 failure alarm | 10/24/2025 05:31:56 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0657 | FLM_EM | [8 empty] | API | 10/24/2025 05:42:16 | 10/25/2025 12:16:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000163 | PCM-20251024-00000388 | TT-20251024-00452 | Reference_EM | Region_2 | RIY0385 | RIY0385 | Enviroment | SCECO_Failure | SCECO auto restored | Vignesh Sivakumar Sivakumar | 10/24/2025 07:45:41 | 10/24/2025 20:04:53 | 10/24/2025 13:45:41 | Mains Failure at RIY0385-P1-HUB_SRAN-VIP-FON @ Sceco | 10/24/2025 07:35:39 | Major | 65109 | Mains Failure | 10/24/2025 07:35:35 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0385 | FLM_EM | [8 empty] | API | 10/24/2025 07:45:41 | 10/24/2025 13:37:14 | 10/24/2025 13:45:44 | 10/24/2025 13:45:51 | 10/24/2025 13:45:56 | 10/24/2025 20:04:53 |  | Vignesh Sivakumar Sivakumar |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251024000169 | PCM-20251024-00000396 | TT-20251024-00459 | Reference_EM | Region_2 | RIY2251 | RIY2251 |  |  |  | Vignesh Sivakumar Sivakumar | 10/24/2025 07:58:35 | 10/24/2025 13:37:14 | 10/24/2025 19:58:35 | Major Rec alarm at RIY2251-P2_SRAN @ Sceco | 10/24/2025 07:48:02 | Minor | 65107 | Major Rec alarm | 10/24/2025 07:47:59 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2251 | FLM_EM | [8 empty] | API | 10/24/2025 07:58:35 | 10/24/2025 13:37:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000181 | PCM-20251024-00000412 | TT-20251024-00481 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Mohamed Samir Farahat Allam | 10/24/2025 08:26:01 | 10/25/2025 13:27:21 | 10/24/2025 20:26:01 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/24/2025 08:15:28 | Minor | 65102 | high temprature 32 | 10/24/2025 08:15:25 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/24/2025 08:26:01 | 10/25/2025 13:27:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000185 | PCM-20251024-00000421 | TT-20251024-00489 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/24/2025 08:34:46 | 10/24/2025 17:14:36 | 10/24/2025 20:34:46 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/24/2025 08:24:16 | Minor | 65107 | Major Rec alarm | 10/24/2025 08:24:12 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/24/2025 08:34:46 | 10/24/2025 17:14:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000186 | PCM-20251024-00000422 | TT-20251024-00492 | EM | Region_1 | KBR0163 | KBR0163 | Enviroment | Air Condition | Change Fan | Yasser Mohamed Abdelnabi Ibrahim | 10/24/2025 08:35:22 | 10/26/2025 04:34:21 | 10/24/2025 12:35:22 | high temprature 32 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/24/2025 08:33:17 | Critical | 65102 | high temprature 32 | 10/24/2025 08:33:13 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/24/2025 08:35:22 | 10/24/2025 15:07:45 | 10/26/2025 04:34:13 |  |  | 10/26/2025 04:34:21 |  | Yasser Mohamed Abdelnabi Ibrahim | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251024000189 | PCM-20251024-00000427 | TT-20251024-00501 | Reference_EM | Region_2 | RIY2087 | RIY2087 |  |  |  | Vignesh Sivakumar Sivakumar | 10/24/2025 08:39:56 | 10/24/2025 13:37:15 | 10/24/2025 20:39:56 | Mains Failure at RIY2087-P2_SRAN @ Sceco | 10/24/2025 08:29:39 | Minor | 65109 | Mains Failure | 10/24/2025 08:29:36 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2087 | FLM_EM | [8 empty] | API | 10/24/2025 08:39:56 | 10/24/2025 13:37:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000196 | PCM-20251024-00000440 | TT-20251024-00511 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/24/2025 08:48:15 | 10/24/2025 17:14:37 | 10/24/2025 20:48:15 | high temprature 32 at RIY0349-P2_SRAN @ Sceco | 10/24/2025 08:37:34 | Minor | 65102 | high temprature 32 | 10/24/2025 08:37:30 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/24/2025 08:48:15 | 10/24/2025 17:14:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251024000206 | PCM-20251024-00000459 | TT-20251024-00530 | Reference_EM | Region_2 | KHJ0469 | KHJ0469 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/24/2025 09:02:41 | 10/24/2025 09:02:41 | 10/24/2025 21:02:41 | High temperature 32C alarm at KHJ2M1469-P3 @ Sceco | 10/24/2025 08:52:18 | Minor | 65102 | High temperature 32C alarm | 10/24/2025 08:52:15 | P3 | 2G | al kharj | Sceco | 2G NSA | KHJ2M1469 | FLM_EM | [8 empty] | API | 10/24/2025 09:02:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000210 | PCM-20251024-00000470 | TT-20251024-00545 | Reference_EM | Region_2 | AFF0521 | AFF0521 |  |  |  | Moustafa Elzaafarany Abdellah | 10/24/2025 09:12:31 | 10/24/2025 14:29:16 | 10/24/2025 21:12:31 | Major Rec alarm at AFF0521-P2_SRAN @ Sceco | 10/24/2025 09:02:17 | Minor | 65107 | Major Rec alarm | 10/24/2025 09:02:13 | P2 | SRAN | dawadmi | Sceco | 2G NSA | AFF0521 | FLM_EM | [8 empty] | API | 10/24/2025 09:12:31 | 10/24/2025 14:29:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000222 | PCM-20251024-00000493 | TT-20251024-00582 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/24/2025 09:41:26 | 10/24/2025 13:11:52 | 10/24/2025 21:41:26 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/24/2025 09:30:46 | Minor | 65102 | high temprature 32 | 10/24/2025 09:30:41 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/24/2025 09:41:26 | 10/24/2025 13:11:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251024000229 | PCM-20251024-00000507 | TT-20251024-00596 | Reference_EM | Region_2 | RIY2447 | RIY2447 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 10:00:05 | 10/24/2025 12:28:56 | 10/24/2025 22:00:05 | Air condition 1 failure alarm at RIY2447-P2_SRAN @ Sceco | 10/24/2025 09:50:08 | Minor | 65104 | Air condition 1 failure alarm | 10/24/2025 09:49:15 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2447 | FLM_EM | [8 empty] | API | 10/24/2025 10:00:05 | 10/24/2025 12:28:56 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251024000232 | PCM-20251024-00000510 | TT-20251024-00601 | Reference_EM | Region_2 | DLM0485 | DLM0485 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/24/2025 10:04:41 | 10/24/2025 10:04:41 | 10/24/2025 22:04:41 | high temprature 32 at DLM0485-P2_SRAN @ Sceco | 10/24/2025 09:54:00 | Minor | 65102 | high temprature 32 | 10/24/2025 09:53:56 | P2 | SRAN | al kharj | Sceco | 2G NSA | DLM0485 | FLM_EM | [8 empty] | API | 10/24/2025 10:04:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000249 | PCM-20251024-00000563 | TT-20251024-00651 | Telecom | Region_2 | BUR0053 | BUR0053 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Farman Ullah Muhammad Nazir | 10/24/2025 10:43:01 | 10/25/2025 13:44:53 | 10/24/2025 16:43:01 | BBU CPRI Interface Error at BUR0053-P2_SRAN @ Sceco | 10/24/2025 10:32:33 | Major | 26234 | BBU CPRI Interface Error | 10/24/2025 10:29:58 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0053 | FLM_EM |  |  | PCM-20251024-00000550 | power issue at site | power issue at site |  |  |  | API | 10/24/2025 10:43:01 | 10/25/2025 07:59:05 | 10/25/2025 13:44:42 |  |  | 10/25/2025 13:44:53 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000261 | PCM-20251024-00000588 | TT-20251024-00683 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/24/2025 10:59:25 | 10/25/2025 13:35:41 | 10/24/2025 14:59:25 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/24/2025 10:57:23 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/24/2025 10:57:16 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 2-TO HFR0502(2-A) |  |  | API | 10/24/2025 10:59:25 | 10/24/2025 13:49:34 | 10/25/2025 13:35:15 |  |  | 10/25/2025 13:35:41 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251024000272 | PCM-20251024-00000603 | TT-20251024-00695 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/24/2025 11:12:21 | 10/24/2025 12:55:58 | 10/24/2025 17:12:21 | high temprature 40 at DAM2066-P1-HUB_SRAN @ Sceco | 10/24/2025 11:01:41 | Major | 65103 | high temprature 40 | 10/24/2025 11:01:37 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/24/2025 11:12:21 | 10/24/2025 12:55:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000276 | PCM-20251024-00000613 | TT-20251024-00703 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/24/2025 11:15:32 | 10/26/2025 09:13:39 | 10/24/2025 23:15:32 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/24/2025 11:09:01 | Minor | 40564 | Genset Fault | 10/24/2025 11:09:01 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/24/2025 11:15:32 | 10/24/2025 15:20:14 | 10/26/2025 09:13:28 |  |  | 10/26/2025 09:13:39 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251024000298 | PCM-20251024-00000651 | TT-20251024-00735 | Reference_EM | Region_2 | RIY0164 | RIY0164 |  |  |  | Kadri Jalal Mohammed Asmail | 10/24/2025 11:51:06 | 10/24/2025 12:26:59 | 10/24/2025 23:51:06 | Air condition 1 failure alarm at RIY0164-P2_SRAN @ Sceco | 10/24/2025 11:44:54 | Minor | 65104 | Air condition 1 failure alarm | 10/24/2025 11:40:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0164 | FLM_EM | [8 empty] | API | 10/24/2025 11:51:06 | 10/24/2025 12:26:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000313 | PCM-20251024-00000673 | TT-20251024-00756 | Reference_EM | Region_2 | AFL0090 | AFL0090 | Enviroment | Genset failure_AVR | Change Generator AVR | Saeed Ud Din Muhammad Yousaf | 10/24/2025 12:05:06 | 10/24/2025 15:32:07 | 10/25/2025 00:05:06 | Generator failure at AFL0090-P3-USF_SRAN-PC @ Power Cube | 10/24/2025 11:54:47 | Minor | 65114 | Generator failure | 10/24/2025 11:54:42 | P3 | SRAN | aflaj | Power Cube | 2G NSA | AFL0090 | FLM_EM | [8 empty] | API | 10/24/2025 12:05:06 | 10/24/2025 15:23:08 | 10/24/2025 15:31:32 | 10/24/2025 15:31:35 | 10/24/2025 15:31:42 | 10/24/2025 15:32:07 |  | Saeed Ud Din Muhammad Yousaf |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251024000322 | PCM-20251024-00000691 | TT-20251024-00773 | Reference_EM | Region_2 | HIR0543 | HIR0543 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/24/2025 12:24:41 | 10/24/2025 17:14:37 | 10/25/2025 00:24:41 | high temprature 32 at HIR0543-P2_SRAN @ Sceco | 10/24/2025 12:14:27 | Minor | 65102 | high temprature 32 | 10/24/2025 12:14:23 | P2 | SRAN | riyadh | Sceco | 2G NSA | HIR0543 | FLM_EM | [8 empty] | API | 10/24/2025 12:24:41 | 10/24/2025 17:14:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000325 | PCM-20251024-00000698 | TT-20251024-00783 | Reference_EM | Region_2 | RYD0938 | RYD0938 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/24/2025 12:37:06 | 10/24/2025 13:47:05 | 10/25/2025 00:37:06 | Minor Rec alarm at RYD0938-P2_SRAN @ Sceco | 10/24/2025 12:26:50 | Minor | 65108 | Minor Rec alarm | 10/24/2025 12:26:47 | P2 | SRAN | riyadh | Sceco | 2G NSA | RYD0938 | FLM_EM | [8 empty] | API | 10/24/2025 12:37:06 | 10/24/2025 13:47:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251024000329 | PCM-20251024-00000707 | TT-20251024-00795 | Reference_EM | Region_2 | RIY2642 | RIY2642 | Enviroment | Genset failure_High Temperature | Change Generator radiator | Amr Abbas Zaghloul Abbas | 10/24/2025 12:49:01 | 10/24/2025 15:16:11 | 10/24/2025 18:49:01 | Generator failure at RIY2642-P1-VIP_SRAN @ Generator_DG | 10/24/2025 12:38:43 | Major | 65114 | Generator failure | 10/24/2025 12:38:40 | VIP | SRAN | riyadh | Generator_DG | 2G NSA | RIY2642 | FLM_EM | [8 empty] | API | 10/24/2025 12:49:01 | 10/24/2025 13:14:07 | 10/24/2025 13:14:30 | 10/24/2025 13:14:57 | 10/24/2025 13:49:12 | 10/24/2025 15:16:11 |  | Amr Abbas Zaghloul Abbas |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000337 | PCM-20251024-00000726 | TT-20251024-00813 | Reference_EM | Region_2 | RIY0250 | RIY0250 | Enviroment | Air Condition | Welding pipes & adding freon | Ahmed Mohamed Ibrahim Elnagar | 10/24/2025 12:59:50 | 10/24/2025 14:54:12 | 10/24/2025 18:59:50 | high temprature 32 at RIY0250-P1-HUB_SRAN-FON @ Sceco | 10/24/2025 12:44:38 | Major | 65102 | high temprature 32 | 10/24/2025 12:49:21 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0250 | FLM_EM | [8 empty] | API | 10/24/2025 12:59:50 | 10/24/2025 13:47:05 | 10/24/2025 13:47:15 | 10/24/2025 13:47:25 | 10/24/2025 13:47:34 | 10/24/2025 14:54:12 |  | Ahmed Mohamed Ibrahim Elnagar |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251024000350 | PCM-20251024-00000748 | TT-20251024-00836 | Reference_EM | Region_2 | RIY0259 | RIY0259 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 13:20:01 | 10/25/2025 06:29:10 | 10/25/2025 01:20:01 | high temprature 32 at RIY0259-P2_SRAN @ Sceco | 10/24/2025 13:09:32 | Minor | 65102 | high temprature 32 | 10/24/2025 13:09:28 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0259 | FLM_EM | [8 empty] | API | 10/24/2025 13:20:01 | 10/25/2025 06:29:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000357 | PCM-20251024-00000761 | TT-20251024-00854 | Reference_EM | Region_2 | RIY2506 | RIY2506 |  |  |  | Kadri Jalal Mohammed Asmail | 10/24/2025 13:32:26 | 10/25/2025 11:24:35 | 10/25/2025 01:32:26 | Minor Rec alarm at RIY2506-P2_SRAN @ Sceco | 10/24/2025 13:22:01 | Minor | 65108 | Minor Rec alarm | 10/24/2025 13:21:59 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2506 | FLM_EM | [8 empty] | API | 10/24/2025 13:32:26 | 10/25/2025 11:24:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000358 | PCM-20251024-00000762 | TT-20251024-00855 | Reference_EM | Region_2 | RIY0289 | RIY0289 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 13:32:55 | 10/25/2025 06:29:10 | 10/25/2025 01:32:55 | Door opening alarm at RIY0289-P2_SRAN @ Sceco | 10/24/2025 13:32:25 | Minor | 65101 | Door opening alarm | 10/24/2025 09:30:55 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0289 | FLM_EM | [8 empty] | API | 10/24/2025 13:32:55 | 10/25/2025 06:29:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000360 | PCM-20251024-00000765 | TT-20251024-00861 | Reference_EM | Region_2 | RIY0289 | RIY0289 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 13:37:01 | 10/25/2025 06:29:10 | 10/25/2025 01:37:01 | Air condition 2 failure alarm at RIY0289-P2_SRAN @ Sceco | 10/24/2025 13:32:58 | Minor | 65105 | Air condition 2 failure alarm | 10/24/2025 13:26:43 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0289 | FLM_EM | [8 empty] | API | 10/24/2025 13:37:01 | 10/25/2025 06:29:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000365 | PCM-20251024-00000773 | TT-20251024-00869 | Reference_EM | Region_2 | RIY0518 | RIY0518 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/24/2025 13:45:21 | 10/24/2025 17:14:38 | 10/25/2025 01:45:21 | Minor Rec alarm at RIY0518-P2_SRAN @ Sceco | 10/24/2025 13:34:52 | Minor | 65108 | Minor Rec alarm | 10/24/2025 13:34:46 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0518 | FLM_EM | [8 empty] | API | 10/24/2025 13:45:21 | 10/24/2025 17:14:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000367 | PCM-20251024-00000775 | TT-20251024-00871 | Reference_EM | Region_2 | RIY0264 | RIY0264 |  |  |  | Vignesh Sivakumar Sivakumar | 10/24/2025 13:46:51 | 10/24/2025 20:04:59 | 10/25/2025 01:46:51 | high temprature 32 at RIY0264-P2_SRAN @ Sceco | 10/24/2025 13:36:11 | Minor | 65102 | high temprature 32 | 10/24/2025 13:36:09 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0264 | FLM_EM | [8 empty] | API | 10/24/2025 13:46:51 | 10/24/2025 20:04:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000370 | PCM-20251024-00000785 | TT-20251024-00884 | Reference_EM | Region_2 | RIY0033 | RIY0033 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/24/2025 13:52:01 | 10/24/2025 22:02:14 | 10/24/2025 19:52:01 | high temprature 32 at RIY0033-P1-DIA_SRAN @ Sceco | 10/24/2025 13:41:21 | Major | 65102 | high temprature 32 | 10/24/2025 13:41:18 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0033 | FLM_EM | [8 empty] | API | 10/24/2025 13:52:01 | 10/24/2025 22:02:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000371 | PCM-20251024-00000790 | TT-20251024-00881 | Telecom | Region_2 | RIY0153 | RIY0153 |  |  |  | Adham Adham Hassan Farghal | 10/24/2025 13:55:40 | 10/24/2025 14:57:26 | 10/25/2025 01:55:40 | RF Unit Maintenance Link Failure at RIY0153-P2_SRAN @ Sceco | 10/24/2025 13:45:39 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 13:45:27 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0153 | FLM_EM |  |  | PCM-20251024-00000784 | power issue at site // Power alarm REPORTED | power issue at site // Power alarm REPORTED |  |  |  | API | 10/24/2025 13:55:40 | 10/24/2025 14:57:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000380 | PCM-20251024-00000804 | TT-20251024-00904 | Reference_EM | Region_2 | KHJ0842 | KHJ0842 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Fritz Ian Generale | 10/24/2025 14:08:31 | 10/24/2025 20:48:37 | 10/25/2025 02:08:31 | Door opening alarm at KHJ0842-P2_SRAN @ Generator_SG | 10/24/2025 14:08:06 | Minor | 65101 | Door opening alarm | 10/24/2025 14:08:03 | P2 | SRAN | al kharj | Generator_SG | 2G NSA | KHJ0842 | FLM_EM | [8 empty] | API | 10/24/2025 14:08:31 | 10/24/2025 20:47:40 | 10/24/2025 20:48:22 |  |  | 10/24/2025 20:48:37 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000387 | PCM-20251024-00000816 | TT-20251024-00912 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/24/2025 14:14:16 | 10/24/2025 14:57:27 | 10/24/2025 20:14:16 | high temprature 40 at RIY0232-P1_SRAN @ Sceco | 10/24/2025 14:03:52 | Major | 65103 | high temprature 40 | 10/24/2025 14:03:49 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/24/2025 14:14:16 | 10/24/2025 14:57:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000404 | PCM-20251024-00000853 | TT-20251024-00953 | Reference_EM | Region_2 | RIY0446 | RIY0446 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/24/2025 14:43:40 | 10/24/2025 17:14:38 | 10/25/2025 02:43:40 | high temprature 40 at RIY0446-P2_SRAN @ Sceco | 10/24/2025 14:33:18 | Minor | 65103 | high temprature 40 | 10/24/2025 14:33:16 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0446 | FLM_EM | [8 empty] | API | 10/24/2025 14:43:40 | 10/24/2025 17:14:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000408 | PCM-20251024-00000860 | TT-20251024-00960 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/24/2025 14:48:21 | 10/25/2025 13:21:15 | 10/25/2025 02:48:21 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/24/2025 14:37:46 | Minor | 65102 | High temperature 32C alarm | 10/24/2025 14:37:43 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/24/2025 14:48:21 | 10/25/2025 13:21:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000463 | PCM-20251024-00000997 | TT-20251024-01123 | Reference_EM | Region_2 | HRQ0222 | HRQ0222 | Enviroment | Fire Alarm | Reset Fire Pannel | ABUZAR Ahmed Humida Mustafa | 10/24/2025 17:03:11 | 10/24/2025 17:40:30 | 10/25/2025 05:03:11 | Generator failure at HRQ0222-P3-USF_SRAN-PC @ Power Cube | 10/24/2025 16:52:50 | Minor | 65114 | Generator failure | 10/24/2025 16:52:47 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HRQ0222 | FLM_EM | [8 empty] | API | 10/24/2025 17:03:11 | 10/24/2025 17:39:56 | 10/24/2025 17:40:12 |  |  | 10/24/2025 17:40:30 |  | ABUZAR Ahmed Humida Mustafa |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000466 | PCM-20251024-00001004 | TT-20251024-01132 | Reference_EM | Region_2 | RIY0199 | RIY0199 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/24/2025 17:13:31 | 10/24/2025 17:14:39 | 10/24/2025 23:13:31 | Mains Failure at RIY0199-P1-VIP_SRAN @ Sceco | 10/24/2025 17:03:28 | Major | 65109 | Mains Failure | 10/24/2025 17:03:24 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0199 | FLM_EM | [8 empty] | API | 10/24/2025 17:13:31 | 10/24/2025 17:14:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000477 | PCM-20251024-00001031 | TT-20251024-01162 | EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 17:47:36 | 10/25/2025 06:29:11 | 10/25/2025 05:47:36 | NETECO: Communication Failure at RIY2431 @ Sceco | 10/24/2025 17:41:04 | Minor | 13750 | Communication Failure | 10/24/2025 17:41:04 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/24/2025 17:47:36 | 10/25/2025 06:29:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000556 | PCM-20251024-00001154 | TT-20251024-01270 | Reference_EM | Region_2 | RIY0272 | RIY0272 |  |  |  | Vignesh Sivakumar Sivakumar | 10/24/2025 19:23:46 | 10/24/2025 20:04:59 | 10/25/2025 07:23:46 | high temprature 32 at RIY0272-P2_SRAN @ Sceco | 10/24/2025 19:13:06 | Minor | 65102 | high temprature 32 | 10/24/2025 19:13:03 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0272 | FLM_EM | [8 empty] | API | 10/24/2025 19:23:46 | 10/24/2025 20:04:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251024000558 | PCM-20251024-00001157 | TT-20251024-01273 | Reference_EM | Region_2 | HRHT0135 | HRHT0135 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Fritz Ian Generale | 10/24/2025 19:26:55 | 10/24/2025 21:06:00 | 10/25/2025 07:26:55 | Generator failure at HRHT0135-P2_SRAN-PC @ Power Cube | 10/24/2025 19:16:11 | Minor | 65114 | Generator failure | 10/24/2025 19:16:08 | P2 | SRAN | riyadh | Power Cube | 2G NSA | HRHT0135 | FLM_EM | [8 empty] | API | 10/24/2025 19:26:55 | 10/24/2025 20:47:41 | 10/24/2025 20:48:45 | 10/24/2025 20:48:53 | 10/24/2025 20:48:56 | 10/24/2025 21:06:00 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000562 | PCM-20251024-00001170 | TT-20251024-01293 | Reference_EM | Region_2 | FAM0021 | FAM0021 |  |  |  | Moustafa Elzaafarany Abdellah | 10/24/2025 19:36:55 | 10/24/2025 20:03:39 | 10/25/2025 07:36:55 | Major Rec. alarm at FAM2M1021-P3 @ Sceco | 10/24/2025 19:26:37 | Minor | 65107 | Major Rec. alarm | 10/24/2025 19:26:33 | P3 | 2G | dawadmi | Sceco | 2G NSA | FAM2M1021 | FLM_EM | [8 empty] | API | 10/24/2025 19:36:55 | 10/24/2025 20:03:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000576 | PCM-20251024-00001218 | TT-20251024-01341 | Reference_EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/24/2025 20:29:35 | 10/25/2025 06:29:11 | 10/25/2025 08:29:35 | Low battery voltage at RIY2431-P2_SRAN @ Sceco | 10/24/2025 20:19:19 | Minor | 65110 | Low battery voltage | 10/24/2025 20:19:13 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/24/2025 20:29:35 | 10/25/2025 06:29:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251024000580 | PCM-20251024-00001224 | TT-20251024-01322 | Telecom | Region_2 | RIY0272 | RIY0272 |  |  |  | Vignesh Sivakumar Sivakumar | 10/24/2025 20:42:11 | 10/24/2025 20:42:11 | 10/25/2025 08:42:11 | RF Unit Maintenance Link Failure at RIY0272-P2_SRAN @ Sceco | 10/24/2025 20:09:36 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 20:07:53 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0272 | FLM_EM |  |  | PCM-20251024-00001199 | power issue at site | power issue at site |  |  |  | API | 10/24/2025 20:42:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000591 | PCM-20251024-00001243 | TT-20251024-01367 | Reference_EM | Region_2 | RIY0772 | RIY0772 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/24/2025 21:09:20 | 10/25/2025 08:41:14 | 10/25/2025 09:09:20 | Mains Failure at RIY0772-P2_SRAN @ Sceco | 10/24/2025 20:59:05 | Minor | 65109 | Mains Failure | 10/24/2025 20:59:01 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0772 | FLM_EM | [8 empty] | API | 10/24/2025 21:09:20 | 10/25/2025 08:41:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251024000615 | PCM-20251024-00001289 | TT-20251024-01424 | Reference_EM | Region_2 | RIY0883 | RIY0883 |  |  |  | Ahmed Khalifa Amin Aboueltaher | 10/24/2025 22:05:40 | 10/24/2025 23:04:44 | 10/25/2025 10:05:40 | high temprature 32 at RIY0883-P2_SRAN @ Sceco | 10/24/2025 21:55:10 | Minor | 65102 | high temprature 32 | 10/24/2025 21:55:06 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0883 | FLM_EM | [8 empty] | API | 10/24/2025 22:05:40 | 10/24/2025 23:03:52 | 10/24/2025 23:04:34 | 10/24/2025 23:04:37 | 10/24/2025 23:04:44 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251024000637 | PCM-20251024-00001335 | TT-20251024-01467 | Reference_EM | Region_2 | RIY0272 | RIY0272 |  |  |  | Vignesh Sivakumar Sivakumar | 10/24/2025 22:35:41 | 10/24/2025 22:35:41 | 10/25/2025 10:35:41 | Door opening alarm at RIY0272-P2_SRAN @ Sceco | 10/24/2025 22:34:55 | Minor | 65101 | Door opening alarm | 10/24/2025 22:32:45 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0272 | FLM_EM | [8 empty] | API | 10/24/2025 22:35:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251024000638 | PCM-20251024-00001338 | TT-20251024-01071 | Reference_telecom | Region_2 | RIY2521 | RIY2521 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 10/24/2025 22:43:26 | 10/25/2025 06:28:17 | 10/25/2025 10:43:26 | External Clock Reference Problem at RIY2521-P2_SRAN @ Generator_SG | 10/24/2025 13:30:41 | Minor | 26262 | External Clock Reference Problem | 10/24/2025 13:16:17 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2521 | FLM_EM |  | Dear Team , We observing PLA_MEMBER _DOWN_EXT Alarm at RIY2521 , kindly visit the site and check this issue | PCM-20251024-00001327 | Dear Team , We observing PLA_MEMBER _DOWN_EXT Alarm at RIY2521 , kindly visit the site and check this issue | Dear Team , We observing PLA_MEMBER _DOWN_EXT Alarm at RIY2521 , kindly visit the site and check this issue |  |  |  | API | 10/24/2025 22:43:26 | 10/25/2025 06:28:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000027 | PCM-20251025-00000049 | TT-20251025-00046 | Reference_EM | Region_2 | AFL0018 | AFL0018 | Enviroment | Genset failure_AVR | Change Generator AVR | Fritz Ian Generale | 10/25/2025 00:47:56 | 10/25/2025 13:49:10 | 10/25/2025 12:47:56 | Generator failure at AFL0018-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 00:37:30 | Minor | 65114 | Generator failure | 10/25/2025 00:37:26 | P3 | SRAN | al kharj | Power Cube | 2G NSA | AFL0018 | FLM_EM | [8 empty] | API | 10/25/2025 00:47:56 | 10/25/2025 02:10:25 | 10/25/2025 02:10:45 | 10/25/2025 02:10:49 | 10/25/2025 02:10:54 | 10/25/2025 13:49:10 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000038 | PCM-20251025-00000072 | TT-20251025-00068 | Reference_EM | Region_2 | RIY0460 | RIY0460 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/25/2025 01:13:11 | 10/26/2025 00:11:28 | 10/25/2025 13:13:11 | Door opening alarm at RIY0460-P3_SRAN @ Generator_SG | 10/25/2025 01:12:51 | Minor | 65101 | Door opening alarm | 10/25/2025 01:12:47 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0460 | FLM_EM | [8 empty] | API | 10/25/2025 01:13:11 | 10/26/2025 00:11:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000039 | PCM-20251025-00000073 | TT-20251025-00072 | Reference_EM | Region_1 | HFF2397 | HFF2397 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/25/2025 01:16:51 | 10/25/2025 10:41:16 | 10/25/2025 13:16:51 | Mains Failure at HFF2397-P3_SRAN @ Sceco | 10/25/2025 01:06:29 | Minor | 65109 | Mains Failure | 10/25/2025 01:06:26 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF2397 | FLM_EM | [8 empty] | API | 10/25/2025 01:16:51 | 10/25/2025 10:41:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000046 | PCM-20251025-00000083 | TT-20251025-00080 | Reference_EM | Region_2 | HTM0016 | HTM0016 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | Fritz Ian Generale | 10/25/2025 01:25:05 | 10/26/2025 10:39:38 | 10/25/2025 13:25:05 | Generator failure at HTM0016-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 01:14:49 | Minor | 65114 | Generator failure | 10/25/2025 01:14:45 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HTM0016 | FLM_EM | [8 empty] | API | 10/25/2025 01:25:05 | 10/25/2025 02:10:26 | 10/26/2025 10:39:28 |  |  | 10/26/2025 10:39:38 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000055 | PCM-20251025-00000103 | TT-20251025-00109 | Reference_EM | Region_2 | DUB0015 | DUB0015 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Fritz Ian Generale | 10/25/2025 02:06:26 | 10/26/2025 10:35:19 | 10/25/2025 14:06:26 | Generator failure at DUB0015-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 01:55:45 | Minor | 65114 | Generator failure | 10/25/2025 01:55:43 | P3 | SRAN | al kharj | Power Cube | 2G NSA | DUB0015 | FLM_EM | [8 empty] | API | 10/25/2025 02:06:26 | 10/25/2025 02:10:27 | 10/26/2025 10:35:00 |  |  | 10/26/2025 10:35:19 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000063 | PCM-20251025-00000124 | TT-20251025-00134 | Reference_EM | Region_2 | RIY0357 | RIY0357 |  |  |  | Kadri Jalal Mohammed Asmail | 10/25/2025 02:32:16 | 10/25/2025 11:24:35 | 10/25/2025 14:32:16 | Door opening alarm at RIY0357-P2_SRAN @ Sceco | 10/25/2025 02:31:44 | Minor | 65101 | Door opening alarm | 10/25/2025 02:31:39 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0357 | FLM_EM | [8 empty] | API | 10/25/2025 02:32:16 | 10/25/2025 11:24:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000074 | PCM-20251025-00000142 | TT-20251025-00158 | Reference_EM | Region_2 | HTM0016 | HTM0016 | Enviroment | SCECO_Failure | SCECO auto restored | Irfan Yousaf | 10/25/2025 02:52:27 | 10/25/2025 06:58:05 | 10/25/2025 14:52:27 | Door opening alarm at HTM0016-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 02:51:50 | Minor | 65101 | Door opening alarm | 10/25/2025 02:51:46 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HTM0016 | FLM_EM | [8 empty] | API | 10/25/2025 02:52:27 | 10/25/2025 06:04:26 | 10/25/2025 06:57:38 |  |  | 10/25/2025 06:58:05 |  | Irfan Yousaf |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251025000076 | PCM-20251025-00000150 | TT-20251025-00167 | Reference_telecom | Region_4 | JED2623 | JED2623 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/25/2025 02:57:50 | 10/25/2025 16:27:03 | 10/25/2025 14:57:50 | InternalCommunicationProblem observed in JED2623_01 towards 10.10.183.196 @ Sceco | 10/24/2025 14:57:23 | Minor |  | InternalCommunicationProblem | 10/24/2025 14:57:18 | P3 | 2G | jeddah | Sceco | TX NSA | JED2623 | FLM_TE | [8 empty] | API | 10/25/2025 02:57:50 | 10/25/2025 16:20:35 | 10/25/2025 16:26:59 | 10/25/2025 16:27:01 | 10/25/2025 16:27:03 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000077 | PCM-20251025-00000151 | TT-20251025-00168 | Reference_telecom | Region_4 | JED2635 | JED2635 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 02:58:22 | 10/25/2025 02:58:22 | 10/25/2025 14:58:22 | LossOfSignal observed in JED2635_01 towards 10.3.233.169 @ Sceco | 10/24/2025 15:00:27 | Minor |  | LossOfSignal | 10/24/2025 14:58:10 | P3 | 2G | jeddah | Sceco | TX NSA | JED2635 | FLM_TE | [8 empty] | API | 10/25/2025 02:58:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000080 | PCM-20251025-00000164 | TT-20251025-00114 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 03:14:06 | 10/25/2025 03:14:06 | 10/25/2025 09:14:06 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/25/2025 02:06:47 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 02:06:40 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251025-00000108 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 03:14:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000083 | PCM-20251025-00000170 | TT-20251025-00058 | Reference_telecom | Region_6 | BCH0080 | BCH0080 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/25/2025 03:20:15 | 10/25/2025 16:08:49 | 10/25/2025 15:20:15 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at BCH0080-G9-NL8-L9-NL18-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 00:56:06 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 00:55:59 | P3 | 2G | Albaha | Sceco | 5G_Cell SA | BCH0080 | FLM_TE |  |  | PCM-20251025-00000058 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 03:20:15 | 10/25/2025 16:06:56 | 10/25/2025 16:08:40 |  |  | 10/25/2025 16:08:49 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000085 | PCM-20251025-00000172 | TT-20251025-00064 | Reference_telecom | Region_4 | JED0310 | JED0310 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 03:21:01 | 10/25/2025 08:51:41 | 10/25/2025 09:21:01 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Generator_SG | 10/24/2025 21:08:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 21:08:21 | VIP | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0310 | FLM_TE |  |  | PCM-20251025-00000068 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 03:21:01 | 10/25/2025 08:51:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000086 | PCM-20251025-00000174 | TT-20251025-00165 | Reference_telecom | Region_5 | MAK1MN0320 | MAK0320 |  |  |  | Atif Javed Javed Hussain | 10/25/2025 03:22:02 | 10/25/2025 03:22:02 | 10/25/2025 07:22:02 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 10/24/2025 22:54:52 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:54:47 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0320 | FLM_TE |  |  | PCM-20251025-00000147 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 03:22:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000087 | PCM-20251025-00000175 | TT-20251025-00016 | Reference_telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/25/2025 03:22:49 | 10/25/2025 03:22:49 | 10/25/2025 07:22:49 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/24/2025 20:12:47 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 20:12:43 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE |  |  | PCM-20251025-00000024 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 03:22:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000089 | PCM-20251025-00000177 | TT-20251025-00145 | Telecom | Region_1 | JBKH2M3603 | JBKH0603 | Equipment | BSS_HW_fault | Replace RFU | AbdalHafiz Sirageldin Mohamed Yasin | 10/25/2025 03:24:24 | 10/25/2025 08:52:52 | 10/25/2025 09:24:24 | Local Cell Capability Decline at JBKH2M3603-P2 @ Sceco | 10/25/2025 02:33:17 | Major | 28206 | Local Cell Capability Decline | 10/25/2025 02:31:38 | P2 | 3G | dammam | Sceco | 2G NSA | JBKH2M3603 | FLM_TE |  | Dears Kindly check HW | PCM-20251025-00000131 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/25/2025 03:24:24 | 10/25/2025 04:49:06 | 10/25/2025 06:45:15 | 10/25/2025 06:45:19 | 10/25/2025 08:30:38 | 10/25/2025 08:52:52 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000090 | PCM-20251025-00000178 | TT-20251025-00175 | Reference_telecom | Region_4 | JED1M7223 | JED0223 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/25/2025 03:24:49 | 10/25/2025 10:35:18 | 10/25/2025 09:24:49 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M7223-P1-HUB-CA-L900-L800-SBTS @ Sceco_STB | 10/25/2025 03:00:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 03:00:23 | P1 | 4G | jeddah | Sceco_STB | 5G_Cell SA | JED1M7223 | FLM_TE |  |  | PCM-20251025-00000157 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 03:24:49 | 10/25/2025 10:31:18 | 10/25/2025 10:35:13 |  |  | 10/25/2025 10:35:18 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000095 | PCM-20251025-00000196 | TT-20251025-00209 | Telecom | Region_3 | RSP2M2801 | RSP2801 |  |  |  | Muhammad Sajjad R3 | 10/25/2025 03:40:48 | 10/25/2025 14:49:39 | 10/25/2025 07:40:48 | CSL Fault at RSP2M2801-P1-VIP @ Sceco | 10/25/2025 03:35:11 | Critical | 21825 | CSL Fault | 10/25/2025 03:35:09 | VIP | 2G | yanbu | Sceco | 2G SA | RSP2M2801 | FLM_TE | RSP2M2801 | Results: DOWN SITE HUB RSP2M2801 RSP2M2801 Summary: Hub: RSP2M2801, Down Count: 1, Down Sites: RSP2M2801 Alarm Summary: RSP2M2801 No Active Alarm on HUB | [6 empty] | API | 10/25/2025 03:40:48 | 10/25/2025 14:49:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000096 | PCM-20251025-00000198 | TT-20251025-00219 | Reference_EM | Region_3 | HHR2076 | HHR2076 |  |  |  | Muhammad arshad Anwar | 10/25/2025 03:42:48 | 10/25/2025 05:07:28 | 10/25/2025 15:42:48 | Mains Failure at HHR2076-P3_SRAN-PC @ Generator_SG | 10/25/2025 03:32:44 | Minor | 65109 | Mains Failure | 10/25/2025 03:32:41 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HHR2076 | FLM_EM | [8 empty] | API | 10/25/2025 03:42:48 | 10/25/2025 05:07:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000100 | PCM-20251025-00000209 | TT-20251025-00224 | Telecom | Region_1 | HMBY2M8501 | HMBY2501 |  |  |  | Imran Ali Yousaf | 10/25/2025 03:50:40 | 10/25/2025 12:44:00 | 10/25/2025 09:50:40 | Cell Unavailable at HMBY2M8501-P3-L800 @ Sceco | 10/25/2025 03:49:17 | Major | 29240 | Cell Unavailable | 10/25/2025 03:49:08 | P3 | 4G | dammam | Sceco | LTE SA | HMBY2M8501 | FLM_TE | [8 empty] | API | 10/25/2025 03:50:40 | 10/25/2025 12:44:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000101 | PCM-20251025-00000210 | TT-20251025-00226 | Reference_EM | Region_3 | MDTB0345 | MDTB0345 |  |  |  | Muhamed Ismail Muhamed Daoud | 10/25/2025 03:53:07 | 10/25/2025 03:53:07 | 10/25/2025 15:53:07 | high temprature 32 at MDTB0345-P2_SRAN @ Sceco | 10/25/2025 03:42:58 | Minor | 65102 | high temprature 32 | 10/25/2025 03:42:55 | P3 | SRAN | tabouk | Sceco | 2G NSA | MDTB0345 | FLM_EM | [8 empty] | API | 10/25/2025 03:53:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000102 | PCM-20251025-00000211 | TT-20251025-00227 | Reference_telecom | Region_4 | JED2995 | JED2995 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 03:53:38 | 10/25/2025 10:12:07 | 10/25/2025 15:53:38 | Degrade observed in JED2995 towards 10.21.76.102 @ Generator_SG | 10/24/2025 15:53:38 | Minor |  | Degrade | 10/24/2025 15:53:33 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2995 | FLM_TE | [8 empty] | API | 10/25/2025 03:53:38 | 10/25/2025 10:12:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000103 | PCM-20251025-00000212 | TT-20251025-00228 | Reference_telecom | Region_4 | JED0833 | JED0833 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 03:54:09 | 10/25/2025 08:51:42 | 10/25/2025 15:54:09 | LossOfSignal observed in JED0833_2 towards 10.21.76.101 @ Generator_SG | 10/24/2025 15:53:48 | Minor |  | LossOfSignal | 10/24/2025 15:53:44 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0833 | FLM_TE | [8 empty] | API | 10/25/2025 03:54:09 | 10/25/2025 08:51:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000104 | PCM-20251025-00000213 | TT-20251025-00229 | Telecom | Region_1 | HMBY2501 | HMBY2501 |  |  |  | Imran Ali Yousaf | 10/25/2025 03:54:10 | 10/25/2025 12:44:01 | 10/25/2025 15:54:10 | RF Unit Maintenance Link Failure at HMBY2501-P3_SRAN @ Sceco | 10/25/2025 03:49:36 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 03:49:03 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2501 | FLM_TE | [8 empty] | API | 10/25/2025 03:54:10 | 10/25/2025 12:44:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251025000105 | PCM-20251025-00000218 | TT-20251024-01496 | Telecom | Region_1 | JBKH2M3603 | JBKH0603 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 03:59:18 | 10/25/2025 09:02:22 | 10/25/2025 15:59:18 | RF Unit Maintenance Link Failure at JBKH2M3603-P2 @ Sceco | 10/24/2025 23:05:06 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/24/2025 23:03:23 | P2 | 3G | dammam | Sceco | 2G NSA | JBKH2M3603 | FLM_TE |  |  | PCM-20251025-00000180 | Dear FLM, Approved referenced to below shared troubleshooting steps & results details. | Dear FLM, Approved referenced to below shared troubleshooting steps & results details. |  |  |  | API | 10/25/2025 03:59:18 | 10/25/2025 09:01:34 | 10/25/2025 09:02:22 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000106 | PCM-20251025-00000219 | TT-20251025-00236 | Reference_telecom | Region_5 | MAK2084 | MAK2084 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 03:59:20 | 10/25/2025 03:59:20 | 10/25/2025 15:59:20 | LagPortDown observed in MAK2084 towards 10.10.187.227 @ Sceco | 10/24/2025 15:58:58 | Minor |  | LagPortDown | 10/24/2025 15:58:53 | P3 | 2G | makkah | Sceco | TX NSA | MAK2084 | FLM_TE | [8 empty] | API | 10/25/2025 03:59:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000107 | PCM-20251025-00000220 | TT-20251025-00239 | Reference_telecom | Region_5 | MAK0078 | MAK0078 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/25/2025 04:03:28 | 10/25/2025 04:03:28 | 10/25/2025 16:03:28 | LagPortDown observed in MAK0078 towards 10.10.187.226 @ Sceco_STB | 10/24/2025 16:03:22 | Minor |  | LagPortDown | 10/24/2025 16:03:06 | P1 | 2G | makkah | Sceco_STB | TX NSA | MAK0078 | FLM_TE | [8 empty] | API | 10/25/2025 04:03:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000108 | PCM-20251025-00000225 | TT-20251025-00238 | EM | Region_3 | HHR2M2076 | HHR2076 |  |  |  | Muhammad arshad Anwar | 10/25/2025 04:08:00 | 10/25/2025 05:07:30 | 10/25/2025 10:08:00 | 1(2G/3G/LTE) sites down under HHR2076-P3/R3_MD_HWBSC01 @ Generator_SG | 10/25/2025 04:00:56 | Major | 21825 | CSL Fault | 10/25/2025 04:00:53 | P3 | 2G | madinah | Generator_SG | 2G_3G_LTE SA | HHR2076-P3 | FLM_EM | HHR2076 | Results: DOWN SITE HUB HHR2076-P3 HHR2076 Summary: Hub: HHR2076, Down Count: 1, Down Sites: HHR2076-P3 Alarm Summary: HHR2076 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 04:08:00 | 10/25/2025 05:07:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000109 | PCM-20251025-00000227 | TT-20251025-00246 | EM | Region_5 | HHR1M7436 | HHR0436 | Enviroment | Air Condition | Change compressor | AYMAN SAEED ELSAYED ALBAGORY | 10/25/2025 04:09:08 | 10/25/2025 05:12:54 | 10/25/2025 10:09:08 | AIRCON 1 FAILURE at HHR1M7436-G9-L8-NL18-NL21-SBTS-P1-VIP-HHR @ Sceco | 10/25/2025 04:01:00 | Major | 7103 | AIRCON 1 FAILURE | 10/25/2025 04:00:49 | VIP | 4G | makkah | Sceco | LTE NSA | HHR1M7436 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/25/2025 04:09:08 |  | 10/25/2025 04:44:50 | 10/25/2025 04:44:53 | 10/25/2025 04:44:55 | 10/25/2025 05:12:54 |  | AYMAN SAEED ELSAYED ALBAGORY |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000110 | PCM-20251025-00000229 | TT-20251025-00216 | Telecom | Region_3 | RSP2801 | RSP2801 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Sayed Satoor | 10/25/2025 04:11:33 | 10/25/2025 16:49:15 | 10/25/2025 08:11:33 | 1(2G) 2(LTE) sites down under RSP2801-P1-VIP_SRAN,RSP2800-P1-VIP/YB1MBSCH01 @ Sceco | 10/25/2025 03:35:32 | Critical | 21825 | CSL Fault | 10/25/2025 03:35:30 | VIP | SRAN | yanbu | Sceco | 2G_LTE SA | RSP2800-P1-VIP 2G_LTE,RSP2801-P1-VIP_SRAN LTE | FLM_EM | RSP2801 | Dear Team, Hub:- RSP2801 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM Need to check Summary: Alarm Summary: HUB site not found | PCM-20251025-00000200 | Dear Team, Hub:- RSP2801 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- RSP2801 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/25/2025 04:11:33 | 10/25/2025 14:53:22 | 10/25/2025 16:49:04 |  |  | 10/25/2025 16:49:15 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000111 | PCM-20251025-00000230 | TT-20251025-00248 | Telecom | Region_5 | MAK1MN0111 | MAK0111 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/25/2025 04:12:15 | 10/25/2025 04:12:15 | 10/25/2025 10:12:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0111-NR2.6-P2 @ Sceco | 10/25/2025 04:11:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 04:11:23 | P2 | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0111 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 04:12:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000115 | PCM-20251025-00000242 | TT-20251025-00263 | Reference_EM | Region_3 | ULA2749 | ULA2749 |  |  |  | Muhamed Ismail Muhamed Daoud | 10/25/2025 04:24:07 | 10/25/2025 04:24:07 | 10/25/2025 16:24:07 | Mains Failure at ULA2749-P3_SRAN @ Sceco | 10/25/2025 04:14:14 | Minor | 65109 | Mains Failure | 10/25/2025 04:14:11 | P3 | SRAN | madinah | Sceco | 2G NSA | ULA2749 | FLM_EM | [8 empty] | API | 10/25/2025 04:24:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000116 | PCM-20251025-00000243 | TT-20251025-00264 | Telecom | Region_1 | HMBY2M8501 | HMBY2501 | Equipment | BSS_HW_Stuck | Reset RFU | AbdalHafiz Sirageldin Mohamed Yasin | 10/25/2025 04:24:46 | 10/25/2025 07:32:16 | 10/25/2025 10:24:46 | Cell Unavailable at HMBY2M8501-P3-L800 @ Sceco | 10/25/2025 04:19:00 | Major | 29240 | Cell Unavailable | 10/25/2025 04:18:23 | P3 | 4G | dammam | Sceco | LTE SA | HMBY2M8501 | FLM_TE | [8 empty] | API | 10/25/2025 04:24:46 | 10/25/2025 06:14:30 | 10/25/2025 06:45:22 | 10/25/2025 06:45:25 | 10/25/2025 07:11:58 | 10/25/2025 07:32:16 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000118 | PCM-20251025-00000246 | TT-20251025-00265 | Reference_telecom | Region_5 | HAJ0102 | HAJ0102 |  |  |  | Muhammad Saleem Iqbal | 10/25/2025 04:27:04 | 10/26/2025 05:13:15 | 10/25/2025 16:27:04 | (As per BO Request) Huawei MW HC PM error observed At HAJ0102-HAJ0110 | 10/25/2025 04:24:06 | Minor | 1-631 | MW_LOF | 10/25/2025 04:24:06 | P1 | SRAN | makkah | Sceco | TX NSA | HAJ0102-HAJ0110 | FLM_TE | [5 empty] | (As per BO Request) Huawei MW HC PM error observed At HAJ0102-HAJ0110 |  |  | API | 10/25/2025 04:27:04 | 10/26/2025 05:13:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000119 | PCM-20251025-00000247 | TT-20251025-00256 | EM | Region_2 | RIY2164 | RIY2164 | Equipment | PMR_Power_Cable_RRU | Replace Outdoor Power Connector | WAQAR AHMED BASHIR AHMED | 10/25/2025 04:32:34 | 10/25/2025 07:00:25 | 10/25/2025 16:32:34 | RF Unit External Power Supply Insufficient at RIY2164-P1-VIP-SRAN @ Generator_SG | 10/25/2025 04:08:27 | Minor | 26546 | RF Unit External Power Supply Insufficient | 10/25/2025 04:07:53 | P1 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2164 | FLM_TE |  |  | PCM-20251025-00000235 | under telecom issue | under telecom issue |  |  |  | API | 10/25/2025 04:32:34 | 10/25/2025 06:00:04 | 10/25/2025 06:00:12 | 10/25/2025 06:00:14 | 10/25/2025 06:00:17 | 10/25/2025 07:00:25 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000120 | PCM-20251025-00000249 | TT-20251025-00267 | EM | Region_6 | NJR0040 | NJR0040 | Equipment | CB_BTS | Replace CB on Rectifier | TALEH MUHAMMAD | 10/25/2025 04:33:02 | 10/25/2025 05:11:47 | 10/25/2025 10:33:02 | 1(2G/3G/5G) sites down under NJR0040-P2/NJR0040-P2 @ Sceco | 10/25/2025 04:25:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 04:25:05 | P2 | 2G | najran | Sceco | 2G_3G_5G SA | NJR0040-P2 | FLM_EM | NJR0040 | Results: DOWN SITE HUB NJR0040-P2 NJR0040 Summary: Hub: NJR0040, Down Count: 1, Down Sites: NJR0040-P2 Alarm Summary: NJR0040 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 04:33:02 |  | 10/25/2025 04:49:32 | 10/25/2025 04:49:35 | 10/25/2025 04:52:23 | 10/25/2025 05:11:47 |  | TALEH MUHAMMAD |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000124 | PCM-20251025-00000256 | TT-20251025-00288 | EM | Region_6 | BHAQ1M8435 | BHAQ2435 |  |  |  | Muhammad Tayyab | 10/25/2025 04:59:45 | 10/25/2025 11:44:38 | 10/25/2025 16:59:45 | Genset Running at BHAQ1M8435-P3 -G900-L800-SBTS @ Generator_DG | 10/25/2025 04:51:37 | Minor | 7103 | Genset Running | 10/25/2025 04:51:21 | P3 | 4G | Albaha | Generator_DG | LTE NSA | BHAQ1M8435 | FLM_EM | [5 empty] | Genset Running |  |  | API | 10/25/2025 04:59:45 | 10/25/2025 11:44:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000125 | PCM-20251025-00000259 | TT-20251025-00291 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 05:01:20 | 10/25/2025 05:01:20 | 10/25/2025 11:01:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/25/2025 05:00:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 05:00:32 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 05:01:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000127 | PCM-20251025-00000261 | TT-20251025-00293 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/25/2025 05:03:22 | 10/25/2025 05:03:22 | 10/25/2025 17:03:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/25/2025 05:02:48 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 05:02:36 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 05:03:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000128 | PCM-20251025-00000265 | TT-20251025-00302 | Reference_telecom | Region_2 | QSRY2735 | QSRY2735 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/25/2025 05:10:06 | 10/25/2025 10:36:24 | 10/25/2025 17:10:06 | MW_LOF at QSRY2735_NE_4 @ Generator_SG | 10/25/2025 03:46:51 | Minor | 1-631 | MW_LOF | 10/25/2025 03:46:39 | P2 | SRAN | muzamiah | Generator_SG | TX NSA | QSRY2735 | FLM_TE | [8 empty] | API | 10/25/2025 05:10:06 | 10/25/2025 10:36:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000129 | PCM-20251025-00000270 | TT-20251025-00307 | Telecom | Region_4 | JED1MN2910 | JED2910 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 05:27:40 | 10/26/2025 10:36:41 | 10/25/2025 11:27:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/25/2025 05:27:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 05:26:56 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 05:27:40 | 10/26/2025 10:36:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000131 | PCM-20251025-00000273 | TT-20251025-00313 | Reference_telecom | Region_1 | HMBY2M8501 | HMBY2501 |  |  |  | Imran Ali Yousaf | 10/25/2025 05:39:27 | 10/25/2025 12:44:01 | 10/25/2025 11:39:27 | Cell Unavailable at HMBY2M8501-P3-L800 (REF:TT-20251025-00229) @ Sceco | 10/25/2025 05:24:45 | Major | 29240 | Cell Unavailable | 10/25/2025 05:24:14 | P3 | 4G | dammam | Sceco | LTE SA | HMBY2M8501 | FLM_TE | [8 empty] | API | 10/25/2025 05:39:27 | 10/25/2025 12:44:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000135 | PCM-20251025-00000280 | TT-20251025-00296 | Telecom | Region_5 | HHR1M7436 | HHR0436 | Equipment | BSS_HW_fault | Replace Interface Card | Amjad Ali Muhammad Parves | 10/25/2025 05:42:49 | 10/25/2025 16:02:11 | 10/25/2025 11:42:49 | BASE STATION HARDWARE PROBLEM (Ethernet link unstable) at HHR1M7436-G9-L8-NL18-NL21-SBTS-P1-VIP-HHR @ Sceco | 10/25/2025 05:00:27 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/25/2025 05:00:23 | VIP | 4G | makkah | Sceco | LTE NSA | HHR1M7436 | FLM_TE |  |  | PCM-20251025-00000262 | Please check and close | Please check and close |  |  |  | API | 10/25/2025 05:42:49 | 10/25/2025 12:15:02 | 10/25/2025 12:25:52 | 10/25/2025 12:25:55 | 10/25/2025 13:19:27 | 10/25/2025 16:02:11 |  | Amjad Ali Muhammad Parves |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000136 | PCM-20251025-00000281 | TT-20251025-00262 | Reference_telecom | Region_4 | JED1M8205 | JED2205 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 05:43:38 | 10/25/2025 05:43:38 | 10/25/2025 17:43:38 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M8205-L2100-L1800-L800-P3-SBTS @ Sceco | 10/25/2025 04:18:44 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 04:18:34 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8205 | FLM_TE |  |  | PCM-20251025-00000241 | Please check RSSI at the site | Please check RSSI at the site |  |  |  | API | 10/25/2025 05:43:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000138 | PCM-20251025-00000283 | TT-20251025-00335 | Telecom | Region_2 | RIY2164 | RIY2164 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | WAQAR AHMED BASHIR AHMED | 10/25/2025 05:44:43 | 10/25/2025 07:01:48 | 10/25/2025 11:44:43 | NR Cell Unavailable at RIY2164-P1-VIP-SRAN @ Generator_SG | 10/25/2025 05:37:44 | Major | 29841 | NR Cell Unavailable | 10/25/2025 05:36:11 | P1 | SRAN | riyadh | Generator_SG | 5G SA | RIY2164 | FLM_TE | [8 empty] | API | 10/25/2025 05:44:43 | 10/25/2025 06:02:18 | 10/25/2025 07:00:52 | 10/25/2025 07:00:58 | 10/25/2025 07:01:00 | 10/25/2025 07:01:48 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251025000140 | PCM-20251025-00000285 | TT-20251025-00244 | Reference_telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 05:46:13 | 10/26/2025 10:59:15 | 10/25/2025 11:46:13 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/25/2025 04:00:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 04:00:03 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251025-00000222 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 05:46:13 | 10/25/2025 11:30:47 | 10/26/2025 10:59:15 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000141 | PCM-20251025-00000288 | TT-20251025-00301 | Telecom | Region_4 | JED1U6781 | JED6081 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 05:49:01 | 10/25/2025 13:02:24 | 10/25/2025 11:49:01 | BASE STATION ANTENNA LINE PROBLEM at JED1U6781-G9-L18-L21-P3-CA @ Sceco | 10/25/2025 05:02:36 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 05:02:28 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6781 | FLM_TE |  |  | PCM-20251025-00000264 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 05:49:01 | 10/25/2025 13:02:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000142 | PCM-20251025-00000290 | TT-20251025-00260 | Telecom | Region_6 | KMS0599 | KMS0599 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/25/2025 05:49:47 | 10/25/2025 12:33:07 | 10/25/2025 17:49:47 | BASE STATION ANTENNA LINE PROBLEM at KMS0599-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 04:14:13 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 04:14:08 | P3 | 2G | khamis mushyet | Sceco | 2G NSA | KMS0599 | FLM_TE |  |  | PCM-20251025-00000239 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 05:49:47 | 10/25/2025 12:31:47 | 10/25/2025 12:32:47 |  |  | 10/25/2025 12:33:07 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000143 | PCM-20251025-00000291 | TT-20251025-00341 | Reference_telecom | Region_6 | BHAB0883 | BHAB0883 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/25/2025 05:49:52 | 10/25/2025 11:05:46 | 10/25/2025 17:49:52 | LossOfSignal observed in BHAB0883_03 towards 10.221.242.150 @ Sceco | 10/24/2025 17:50:22 | Minor |  | LossOfSignal | 10/24/2025 17:49:31 | P3 | 2G | makhwa | Sceco | TX NSA | BHAB0883 | FLM_TE | [8 empty] | API | 10/25/2025 05:49:52 | 10/25/2025 11:05:14 | 10/25/2025 11:05:33 |  |  | 10/25/2025 11:05:46 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000145 | PCM-20251025-00000295 | TT-20251025-00339 | EM | Region_1 | JBL2M1488 | JBL0488 |  |  |  | Hamid Bilal Bashir Ahmed | 10/25/2025 05:51:59 | 10/25/2025 06:02:56 | 10/25/2025 11:51:59 | 1(2G/3G/LTE) sites down under JBL0488-P2/R1_JB_HWBSC01 @ Sceco | 10/25/2025 05:44:52 | Major | 21825 | CSL Fault | 10/25/2025 05:44:48 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | JBL0488-P2 | FLM_EM | JBL0488 | Results: DOWN SITE HUB JBL0488-P2 JBL0488 Summary: Hub: JBL0488, Down Count: 1, Down Sites: JBL0488-P2 Alarm Summary: JBL0488 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 05:51:59 | 10/25/2025 06:02:56 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000146 | PCM-20251025-00000296 | TT-20251025-00344 | Telecom | Region_2 | RIY2164 | RIY2164 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | WAQAR AHMED BASHIR AHMED | 10/25/2025 05:52:28 | 10/25/2025 07:00:47 | 10/25/2025 11:52:28 | BBU CPRI Interface Error at RIY2164-P1-VIP-SRAN @ Generator_SG | 10/25/2025 05:49:53 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 05:47:19 | P1 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2164 | FLM_TE | [8 empty] | API | 10/25/2025 05:52:28 | 10/25/2025 06:00:17 | 10/25/2025 07:00:32 | 10/25/2025 07:00:34 | 10/25/2025 07:00:36 | 10/25/2025 07:00:47 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000147 | PCM-20251025-00000297 | TT-20251025-00345 | EM | Region_6 | BHAB1M8015 | BHAB2015 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 05:55:03 | 10/25/2025 07:39:10 | 10/25/2025 17:55:03 | H/E ALARM at BHAB1M8015-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/25/2025 05:46:36 | Minor | 7103 | H/E ALARM | 10/25/2025 05:46:31 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8015 | FLM_EM | [5 empty] | H/E ALARM |  |  | API | 10/25/2025 05:55:03 | 10/25/2025 07:39:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000148 | PCM-20251025-00000298 | TT-20251025-00331 | Telecom | Region_3 | HHR2076 | HHR2076 |  |  |  | Muhammad arshad Anwar | 10/25/2025 05:56:14 | 10/25/2025 06:11:13 | 10/25/2025 09:56:14 | 6(2G) 6(LTE) sites down under R3_MD_HWBSC01 @ Generator_SG | 10/25/2025 05:40:41 | Critical | 21825 | CSL Fault | 10/25/2025 05:40:36 | P3 | SRAN | madinah | Generator_SG | 2G_LTE SA | MKMD2092-P3-CAP_SRAN LTE,MDN2270-P3-USF 2G_LTE,MDN2132-P3 2G_LTE,MDN2269-P3 2G_LTE,MDN2268-P3 2G_LTE,WFR2279-P3 2G_LTE,MDN2217-P3-CAP 2G | FLM_EM | HHR2076 | Dear Team, Hub:- HHR2076 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251025-00000287 | Dear Team, Hub:- HHR2076 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- HHR2076 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/25/2025 05:56:14 | 10/25/2025 06:11:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000149 | PCM-20251025-00000302 | TT-20251025-00317 | Telecom | Region_3 | HHR2076 | HHR2076 |  |  |  | Muhammad arshad Anwar | 10/25/2025 05:59:34 | 10/25/2025 06:11:13 | 10/25/2025 09:59:34 | 9(2G) 5(3G) 9(LTE) sites down under R3_MD_HWBSC01 @ Generator_SG | 10/25/2025 05:40:43 | Critical | 21825 | CSL Fault | 10/25/2025 05:40:38 | P3 | SRAN | madinah | Generator_SG | 2G_3G_LTE SA | MKMD2657-P3 2G_LTE,HHR2074-P3 2G_3G_LTE,WFR2321-P3 2G_LTE,WFR2280-P3 2G_LTE,HHR2073-P3 2G_3G_LTE,MKMD2538-P3 2G_LTE,HHR2075-P3 2G_3G_LTE,HHR2071-P3 2G_3G_LTE,HHR2072-P3 2G_3G_LTE | FLM_EM | HHR2076 | Dear Team, Hub:- HHR2076 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251025-00000286 | Dear Team, Hub:- HHR2076 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- HHR2076 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/25/2025 05:59:34 | 10/25/2025 06:11:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000150 | PCM-20251025-00000303 | TT-20251025-00348 | Reference_EM | Region_1 | HFBD2M5008 | HFBD0008 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/25/2025 05:59:42 | 10/25/2025 05:59:42 | 10/25/2025 11:59:42 | Door opening alarm at HFBD2M5008-P1-HUB @ Generator_SG | 10/25/2025 05:59:09 | Major | 65101 | Door opening alarm | 10/25/2025 05:59:06 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5008 | FLM_EM | [8 empty] | API | 10/25/2025 05:59:42 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000151 | PCM-20251025-00000308 | TT-20251025-00355 | Telecom | Region_1 | HFF0490 | HFF0490 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 06:01:14 | 10/25/2025 08:43:39 | 10/25/2025 18:01:14 | RF Unit Maintenance Link Failure at HFF0490-P2_SRAN @ Sceco | 10/25/2025 00:54:46 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:53:03 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0490 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:14 | 10/25/2025 08:43:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000152 | PCM-20251025-00000307 | TT-20251025-00354 | Telecom | Region_1 | DAM0306 | DAM0306 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/25/2025 06:01:14 | 10/25/2025 08:16:37 | 10/25/2025 12:01:14 | BBU CPRI Interface Error at DAM0306-P2_SRAN @ Sceco | 10/25/2025 04:25:14 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 04:22:40 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0306 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:14 | 10/25/2025 08:16:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000153 | PCM-20251025-00000305 | TT-20251025-00352 | Telecom | Region_3 | MDN0593 | MDN0593 |  |  |  | TAUSEEF ILYAS | 10/25/2025 06:01:15 | 10/25/2025 07:08:56 | 10/25/2025 18:01:15 | RF Unit Maintenance Link Failure at MDN0593-P3_SRAN-PC @ Sceco | 10/25/2025 00:50:38 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:48:56 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN0593 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:15 | 10/25/2025 07:08:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000154 | PCM-20251025-00000311 | TT-20251025-00358 | Telecom | Region_3 | HAL2945 | HAL2945 |  |  |  | Atif Shahzad Muhammad Ajaib | 10/25/2025 06:01:16 | 10/25/2025 09:06:06 | 10/25/2025 18:01:16 | RF Unit Maintenance Link Failure at HAL2945-P3_SRAN @ Generator_SG | 10/25/2025 00:50:38 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:48:55 | P3 | SRAN | hail | Generator_SG | 2G NSA | HAL2945 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:16 | 10/25/2025 09:06:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000155 | PCM-20251025-00000309 | TT-20251025-00357 | Telecom | Region_2 | BUR0011 | BUR0011 |  |  |  | Raise Ahmed Nisar Ahmed | 10/25/2025 06:01:16 | 10/25/2025 13:13:15 | 10/25/2025 18:01:16 | RF Unit Maintenance Link Failure at BUR0011-P2_SRAN @ Sceco | 10/25/2025 00:54:46 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:53:03 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0011 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:16 | 10/25/2025 13:13:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000156 | PCM-20251025-00000310 | TT-20251025-00356 | Telecom | Region_3 | HAL2945 | HAL2945 |  |  |  | Atif Shahzad Muhammad Ajaib | 10/25/2025 06:01:16 | 10/25/2025 09:06:06 | 10/25/2025 12:01:16 | BBU CPRI Interface Error at HAL2945-P3_SRAN @ Generator_SG | 10/25/2025 02:18:19 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 02:15:47 | P3 | SRAN | hail | Generator_SG | 2G NSA | HAL2945 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:16 | 10/25/2025 09:06:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000157 | PCM-20251025-00000313 | TT-20251025-00360 | Telecom | Region_1 | DAM0306 | DAM0306 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/25/2025 06:01:18 | 10/25/2025 08:16:38 | 10/25/2025 18:01:18 | RF Unit Maintenance Link Failure at DAM0306-P2_SRAN @ Sceco | 10/25/2025 03:34:28 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 03:32:36 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0306 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:18 | 10/25/2025 08:16:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000158 | PCM-20251025-00000315 | TT-20251025-00362 | Telecom | Region_1 | HFF0224 | HFF0224 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 06:01:18 | 10/25/2025 13:51:15 | 10/25/2025 18:01:18 | RF Unit Maintenance Link Failure at HFF0224-P3_SRAN @ Generator_SG | 10/25/2025 01:20:58 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:53:03 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | HFF0224 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:18 | 10/25/2025 08:43:40 | 10/25/2025 13:39:12 | 10/25/2025 13:39:20 | 10/25/2025 13:39:23 | 10/25/2025 13:51:15 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000159 | PCM-20251025-00000314 | TT-20251025-00361 | Telecom | Region_2 | RIY0669 | RIY0669 |  |  |  | Mubashar Farooq Abdul Majeed | 10/25/2025 06:01:20 | 10/25/2025 08:54:28 | 10/25/2025 18:01:20 | RF Unit Maintenance Link Failure at RIY0669-P2_SRAN @ Sceco | 10/25/2025 00:51:51 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:50:07 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0669 | FLM_TE | [8 empty] | API | 10/25/2025 06:01:20 | 10/25/2025 08:54:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000162 | PCM-20251025-00000321 | TT-20251025-00374 | Reference_telecom | Region_4 | TAF0156 | TAF0156 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 06:11:03 | 10/25/2025 11:30:48 | 10/25/2025 18:11:03 | FanFailure observed in TAF0156 towards 10.10.187.178 @ Sceco | 10/24/2025 18:11:09 | Minor |  | FanFailure | 10/24/2025 18:10:52 | VIP | 2G | taif | Sceco | TX NSA | TAF0156 | FLM_TE | [8 empty] | API | 10/25/2025 06:11:03 | 10/25/2025 11:30:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000163 | PCM-20251025-00000322 | TT-20251025-00375 | Reference_EM | Region_1 | HFBD2M5008 | HFBD0008 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/25/2025 06:11:34 | 10/25/2025 06:11:34 | 10/25/2025 12:11:34 | Air-condition #1 failure alarm at HFBD2M5008-P1-HUB @ Generator_SG | 10/25/2025 06:01:11 | Major | 65104 | Air-condition #1 failure alarm | 10/25/2025 06:01:08 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5008 | FLM_EM | [8 empty] | API | 10/25/2025 06:11:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000164 | PCM-20251025-00000328 | TT-20251025-00378 | EM | Region_4 | JED6077 | JED6077 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/25/2025 06:15:41 | 10/25/2025 06:15:41 | 10/25/2025 18:15:41 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V;Default System Time at JED6077-GSM-P3 @ Sceco | 10/25/2025 06:13:54 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V;Default System Time | 10/25/2025 03:01:24 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6077 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V;Default System Time |  |  | API | 10/25/2025 06:15:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000167 | PCM-20251025-00000333 | TT-20251025-00380 | Reference_EM | Region_3 | HHR2076 | HHR2076 |  |  |  | Muhammad arshad Anwar | 10/25/2025 06:22:25 | 10/25/2025 06:22:25 | 10/25/2025 18:22:25 | Door opening alarm at HHR2076-P3_SRAN-PC @ Generator_SG | 10/25/2025 06:22:12 | Minor | 65101 | Door opening alarm | 10/25/2025 06:22:10 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HHR2076 | FLM_EM | [8 empty] | API | 10/25/2025 06:22:25 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000168 | PCM-20251025-00000334 | TT-20251025-00303 | Telecom | Region_4 | YLM0756 | YLM0756 |  |  |  | Riasat Ali Allah Baksh | 10/25/2025 06:23:22 | 10/25/2025 06:25:30 | 10/25/2025 10:23:22 | 8(3G) 1(LTE) 2(5G) sites down under YLM1M3756-P1 @ Generator_DG | 10/25/2025 05:10:20 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/25/2025 05:09:40 | P1 | 2G | alaith | Generator_DG | 3G_LTE_5G SA | YLM0756-P1 3G_5G,YLM0789-P3 3G_LTE,MLJI0744-P3 3G,YLM0735-P3 3G,YLM0746-P3 3G,YLM0768-P3 3G,YLM2368-P3 3G,YLM0745-P3 3G | FLM_TE | YLM0756 | Results: DOWN SITE HUB YLM0756-P1 YLM0756 YLM0789-P3 YLM0756 MLJI0744-P3 MLJI0744 YLM0735-P3 YLM0756 YLM0746-P3 YLM0756 YLM0768-P3 YLM0756 YLM2368-P3 YLM0756 YLM0745-P3 YLM0756 Summary: Hub: YLM0756, Down Count: 7, Down Sites: YLM0756-P1, YLM0789-P3, YLM0735-P3, YLM0746-P3, YLM0768-P3, YLM2368-P3, YLM0745-P3 Hub: MLJI0744, Down Count: 1, Down Sites: MLJI0744-P3 Alarm Summary: YLM0756 No Active Alarm on HUB MLJI0744 No Active Alarm on HUB | PCM-20251025-00000268 | Hub: YLM0756 We are observing PM error alarm flapped from our end at the outage time kindly send the FLM, EM to check the site YLM0756- YLM0876 | Hub: YLM0756 We are observing PM error alarm flapped from our end at the outage time kindly send the FLM, EM to check the site YLM0756- YLM0876 |  | sites down |  | API | 10/25/2025 06:23:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000169 | PCM-20251025-00000336 | TT-20251025-00379 | EM | Region_1 | HFR2M2377 | HFR2377 |  |  |  | Reda Mohammed Mohamed Hassanein | 10/25/2025 06:25:59 | 10/25/2025 09:13:48 | 10/25/2025 12:25:59 | 1(2G/3G/LTE) sites down under HFR2377-P2/HB1BSCH01 @ Sceco | 10/25/2025 06:19:11 | Major | 21825 | CSL Fault | 10/25/2025 06:19:09 | P2 | 2G | hafr | Sceco | 2G_3G_LTE SA | HFR2377-P2 | FLM_EM | HFR2377 | Results: DOWN SITE HUB HFR2377-P2 HFR2377 Summary: Hub: HFR2377, Down Count: 1, Down Sites: HFR2377-P2 Alarm Summary: HFR2377 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 06:25:59 | 10/25/2025 09:13:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000170 | PCM-20251025-00000338 | TT-20251007-02278 | Reference_telecom | Region_4 | GMK0442 | GMK0442 |  |  |  | Riasat Ali Allah Baksh | 10/25/2025 06:26:31 | 10/25/2025 06:26:31 | 10/25/2025 18:26:31 | ReplaceableUnitMissing observed in GMK0442 towards 10.3.234.210 @ Sceco | 10/07/2025 09:54:19 | Minor |  | ReplaceableUnitMissing | 10/07/2025 09:54:02 | P2 | 2G | qunfuddah | Sceco | TX NSA | GMK0442 | FLM_TE |  | Approved | PCM-20251025-00000325 | Approved | Approved |  |  |  | API | 10/25/2025 06:26:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000171 | PCM-20251025-00000339 | TT-20251021-01424 | MW_HC | Region_4 | JED2273 | JED2273 | Transsmission | MW_HW_fault | Replace ODU | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 06:28:33 | 10/25/2025 15:38:49 | 10/25/2025 18:28:33 | Nokia MW HC_P1 Observing Performance Issue at JED2273_FTK-JED0978 FTK | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2273_FTK-JED0978 FTK | FLM_TE |  | Approved | PCM-20251025-00000326 | Approved | Approved |  |  |  | API | 10/25/2025 06:28:33 | 10/25/2025 10:12:07 | 10/25/2025 13:14:38 | 10/25/2025 13:25:32 | 10/25/2025 13:25:55 | 10/25/2025 15:38:49 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000172 | PCM-20251025-00000340 | TT-20251025-00269 | Telecom | Region_4 | HAW1M8411 | HAW2411 | Equipment | BTS_Cable | Replace Fiber Cable | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 06:31:13 | 10/25/2025 15:34:35 | 10/25/2025 18:31:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAW1M8411-P3-CA-L800-SBTS @ Generator_SG | 10/25/2025 04:39:36 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 04:39:32 | P2 | 4G | taif | Generator_SG | 5G_Cell SA | HAW1M8411 | FLM_TE |  |  | PCM-20251025-00000300 | No Power Issue | No Power Issue |  |  |  | API | 10/25/2025 06:31:13 | 10/25/2025 11:30:49 | 10/25/2025 11:30:59 | 10/25/2025 11:31:06 | 10/25/2025 11:39:34 | 10/25/2025 15:34:35 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000173 | PCM-20251025-00000341 | TT-20251025-00383 | Telecom | Region_3 | MDV2M1072 | MDV0072 |  |  |  | TAUSEEF ILYAS | 10/25/2025 06:36:00 | 10/25/2025 07:08:56 | 10/25/2025 12:36:00 | 1(2G) sites down under MDV0072-P2-Rehome/R2_RY2_HWBSC01 @ Sceco | 10/25/2025 06:27:56 | Major | 21807 | OML Fault | 10/25/2025 06:27:47 | P2 | 2G | madinah | Sceco | 2G SA | MDV0072-P2-Rehome | FLM_TE | MDV0072 | Results: DOWN SITE HUB MDV0072-P2-Rehome MDV0072 Summary: Hub: MDV0072, Down Count: 1, Down Sites: MDV0072-P2-Rehome Alarm Summary: MDV0072 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 06:36:00 | 10/25/2025 07:08:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000174 | PCM-20251025-00000343 | TT-20251025-00384 | EM | Region_1 | R1_JB_HWBSC01 | JB1 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/25/2025 06:40:30 | 10/25/2025 12:53:17 | 10/25/2025 10:40:30 | Intruder Alarm(SH1) at R1_JB_HWBSC01 @ Sceco_STB | 10/25/2025 06:39:51 | Critical | 65334 | Intruder Alarm(SH1) | 10/25/2025 06:39:46 | P1 | BSC | jubail | Sceco_STB | 2G NSA | R1_JB_HWBSC01 | FLM_EM | [8 empty] | API | 10/25/2025 06:40:30 | 10/25/2025 12:53:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000175 | PCM-20251025-00000344 | TT-20251025-00388 | Telecom | Region_1 | HFF6028 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 06:42:33 | 10/25/2025 20:22:58 | 10/25/2025 18:42:33 | RF Unit CPRI Interface Error at HFF6028-DCU1 @ Sceco | 10/25/2025 06:28:13 | Minor | 26504 | RF Unit CPRI Interface Error | 10/25/2025 06:35:48 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/25/2025 06:42:33 | 10/25/2025 08:43:40 | 10/25/2025 20:22:47 |  |  | 10/25/2025 20:22:58 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251025000178 | PCM-20251025-00000350 | TT-20251025-00395 | Reference_telecom | Region_1 | JBKH2M3603 | JBKH0603 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 06:48:43 | 10/25/2025 09:03:35 | 10/25/2025 12:48:43 | Local Cell Unusable at JBKH2M3603-P2(ref:TT-20251024-01496) @ Sceco | 10/25/2025 05:02:44 | Major | 28203 | Local Cell Unusable | 10/25/2025 05:01:04 | P2 | 3G | dammam | Sceco | 3G SA | JBKH2M3603 | FLM_TE | [8 empty] | API | 10/25/2025 06:48:43 | 10/25/2025 09:01:34 | 10/25/2025 09:03:35 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000179 | PCM-20251025-00000354 | TT-20251025-00392 | EM | Region_1 | KBR2U6137 | KBR6037 |  |  |  | Mohamed Samir Farahat Allam | 10/25/2025 06:50:29 | 10/25/2025 13:27:22 | 10/25/2025 12:50:29 | 1(2G/3G) sites down under KBR6037-P3/DM1MBSCH01 @ Sceco | 10/25/2025 06:42:32 | Major | 21807 | OML Fault | 10/25/2025 06:42:30 | P3 | 2G | dammam | Sceco | 2G_3G SA | KBR6037-P3 | FLM_EM | KBR6037 | Results: DOWN SITE HUB KBR6037-P3 KBR6037 Summary: Hub: KBR6037, Down Count: 1, Down Sites: KBR6037-P3 Alarm Summary: KBR6037 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 06:50:29 | 10/25/2025 13:27:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000181 | PCM-20251025-00000368 | TT-20251025-00414 | Telecom | Region_3 | YBDB0291 | YBDB0291 |  |  |  | Waqas Shah | 10/25/2025 07:10:26 | 10/25/2025 11:16:09 | 10/25/2025 13:10:26 | COMMUN_FAIL at YBDB0291_OCS @ Generator_DG | 10/25/2025 07:06:43 | Major | 1-199 | COMMUN_FAIL | 10/25/2025 07:06:32 | P1 | DWDM | yanbu | Generator_DG | DWDM NSA | YBDB0291 | FLM_TE | [5 empty] | 1-LOCAL-2(1-A)-1-G2TMD20-OTHER |  |  | API | 10/25/2025 07:10:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000183 | PCM-20251025-00000370 | TT-20251025-00417 | Reference_EM | Region_1 | HFF6022 | HFF6022 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/25/2025 07:13:00 | 10/25/2025 08:06:42 | 10/25/2025 19:13:00 | Door opening alarm at HFF6022-P3_SRAN @ Sceco | 10/25/2025 07:12:30 | Minor | 65101 | Door opening alarm | 10/25/2025 07:12:29 | P3 | SRAN | hafr | Sceco | 2G NSA | HFF6022 | FLM_EM | [8 empty] | API | 10/25/2025 07:13:00 | 10/25/2025 08:05:34 | 10/25/2025 08:06:36 |  |  | 10/25/2025 08:06:42 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000184 | PCM-20251025-00000373 | TT-20251025-00419 | Reference_EM | Region_1 | HFBD2M5010 | HFBD0010 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/25/2025 07:14:34 | 10/25/2025 07:14:34 | 10/25/2025 13:14:34 | Door opening alarm at HFBD2M5010-P1-HUB @ Generator_SG | 10/25/2025 07:14:08 | Major | 65101 | Door opening alarm | 10/25/2025 07:14:04 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5010 | FLM_EM | [8 empty] | API | 10/25/2025 07:14:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000189 | PCM-20251025-00000379 | TT-20251025-00423 | Reference_telecom | Region_1 | DRN2M3114 | DRN0114 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/25/2025 07:19:04 | 10/25/2025 15:13:31 | 10/25/2025 13:19:04 | Inter-Board CANBUS Communication Failure at DRN2M3114-P3 @ Sceco | 10/25/2025 05:22:16 | Major | 26101 | Inter-Board CANBUS Communication Failure | 10/25/2025 05:20:42 | P3 | 3G | dammam | Sceco | 2G NSA | DRN2M3114 | FLM_TE |  | Dears kindly check HW | PCM-20251025-00000375 | Dears kindly check HW | Dears kindly check HW |  |  |  | API | 10/25/2025 07:19:04 | 10/25/2025 15:13:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000190 | PCM-20251025-00000381 | TT-20251025-00421 | EM | Region_4 | JED0294 | JED0294 |  |  |  | Nazeer Mohammed | 10/25/2025 07:21:03 | 10/26/2025 06:01:01 | 10/25/2025 13:21:03 | 1(2G/LTE/5G) sites down under JED0294-P3 @ Generator_SG | 10/25/2025 07:13:02 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 07:12:59 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5347630 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 07:21:03 | 10/25/2025 10:31:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000192 | PCM-20251025-00000384 | TT-20251025-00427 | Reference_EM | Region_1 | HFF6022 | HFF6022 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/25/2025 07:22:50 | 10/25/2025 08:06:53 | 10/25/2025 19:22:50 | Air condition 2 failure alarm at HFF6022-P3_SRAN @ Sceco | 10/25/2025 07:12:30 | Minor | 65105 | Air condition 2 failure alarm | 10/25/2025 07:12:26 | P3 | SRAN | hafr | Sceco | 2G NSA | HFF6022 | FLM_EM | [8 empty] | API | 10/25/2025 07:22:50 | 10/25/2025 08:05:35 | 10/25/2025 08:06:47 |  |  | 10/25/2025 08:06:53 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000193 | PCM-20251025-00000385 | TT-20251025-00432 | Reference_EM | Region_1 | HFBD2M5010 | HFBD0010 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/25/2025 07:26:27 | 10/25/2025 07:26:27 | 10/25/2025 13:26:27 | Major Rec. alarm at HFBD2M5010-P1-HUB @ Generator_SG | 10/25/2025 07:16:11 | Major | 65107 | Major Rec. alarm | 10/25/2025 07:16:07 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5010 | FLM_EM | [8 empty] | API | 10/25/2025 07:26:27 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000194 | PCM-20251025-00000387 | TT-20251025-00434 | Reference_telecom | Region_5 | MAK0207 | MAK0207 | Equipment | SFP_BTS | Clean SFP | MOHAMMED JASEEL ARAYIL | 10/25/2025 07:26:58 | 10/25/2025 11:43:56 | 10/25/2025 19:26:58 | BASE STATION SERVICE PROBLEM (TX out of order) at MAK0207-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 07:22:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 07:22:10 | P2 | 2G | makkah | Sceco | LTE_Cell SA | MAK0207 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/25/2025 07:26:58 | 10/25/2025 09:19:21 | 10/25/2025 09:19:54 | 10/25/2025 09:50:15 | 10/25/2025 09:57:58 | 10/25/2025 11:43:56 |  | MOHAMMED JASEEL ARAYIL |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000195 | PCM-20251025-00000388 | TT-20251025-00435 | EM | Region_6 | JEC0377 | JEC0377 |  |  |  | Fizan Ahmed | 10/25/2025 07:27:28 | 10/25/2025 07:27:28 | 10/25/2025 13:27:28 | RECTIFIER MAINS POWER FAILURE at JEC0377-GSM-P1-VIP @ Generator_SG | 10/25/2025 07:19:33 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 07:19:24 | VIP | 2G | baish | Generator_SG | 2G NSA | JEC0377 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 07:27:28 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000196 | PCM-20251025-00000390 | TT-20251025-00436 | EM | Region_6 | JZ1_CORE | JZ1 | Enviroment | SCECO_Failure | SCECO auto restored | Adnan Nadeem Abdul Ghaffar | 10/25/2025 07:27:29 | 10/25/2025 09:20:20 | 10/25/2025 13:27:29 | BSC Shelter A/C 1 Fail at JZ1_CORE-P1-VIP @ Sceco_STB | 10/25/2025 07:26:52 | Major | 7103 | BSC Shelter A/C 1 Fail | 10/25/2025 07:26:45 | P1 | 4G | jizan | Sceco_STB | 2G NSA | JZ1_CORE | FLM_EM | [5 empty] | BSC Shelter A/C 1 Fail |  |  | API | 10/25/2025 07:27:29 | 10/25/2025 08:24:50 | 10/25/2025 08:24:55 | 10/25/2025 08:24:59 | 10/25/2025 08:29:58 | 10/25/2025 09:20:20 |  | Adnan Nadeem Abdul Ghaffar |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000200 | PCM-20251025-00000397 | TT-20251025-00442 | EM | Region_6 | DAR0951 | DAR0951 |  |  |  | Muhammad Tayyab | 10/25/2025 07:36:29 | 10/25/2025 08:50:04 | 10/25/2025 11:36:29 | 1(2G/3G/LTE) sites down under DAR0951-P1/DAR0951-P1 @ Sceco | 10/25/2025 07:28:31 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 07:28:24 | P1 | 2G | dair | Sceco | 2G_3G_LTE SA | DAR0951-P1 | FLM_EM | DAR0951 | Results: DOWN SITE HUB DAR0951-P1 DAR0951 Summary: Hub: DAR0951, Down Count: 1, Down Sites: DAR0951-P1 Alarm Summary: DAR0951 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 07:36:29 | 10/25/2025 08:50:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251025000201 | PCM-20251025-00000398 | TT-20251025-00456 | EM | [7 empty] | 10/25/2025 07:37:17 | 10/25/2025 07:37:17 | 10/25/2025 19:37:17 | SHELTER DOOR OPEN;Default System Time at TBL1M8284-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/25/2025 07:37:00 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/24/2025 03:01:05 | P3 | 4G |  | Generator_SG | LTE NSA | TBL1M8284 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/25/2025 07:37:17 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000205 | PCM-20251025-00000409 | TT-20251025-00426 | Telecom | Region_1 | HMBY2501 | HMBY2501 | Equipment | BSS_HW_fault | Replace RFU | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 07:44:45 | 10/25/2025 10:23:59 | 10/25/2025 13:44:45 | BBU CPRI Interface Error at HMBY2501-P3_SRAN @ Sceco | 10/25/2025 07:17:05 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 07:14:33 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2501 | FLM_TE |  | Approved as per your TS | PCM-20251025-00000407 | Approved as per your TS | Approved as per your TS |  |  |  | API | 10/25/2025 07:44:45 | 10/25/2025 08:43:41 | 10/25/2025 09:47:38 | 10/25/2025 09:47:43 | 10/25/2025 09:55:15 | 10/25/2025 10:23:59 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000207 | PCM-20251025-00000414 | TT-20251025-00478 | Telecom | Region_4 | JD1 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/25/2025 07:47:18 | 10/25/2025 07:47:18 | 10/25/2025 13:47:18 | Observing Link Down Flapped and restored On JED1-PE Connected to Router ¦ JED1-PE-01 ¦ 400GE6/1/0 | 10/25/2025 07:45:01 | Major | 5000003 | Link Down | 10/25/2025 07:45:01 | P1 | BSC | jeddah | Sceco_STB | IPBB NSA | Observing Link Down Flapped and restored On JED1-PE Connected to Router ¦ JED1-PE-01 ¦ 400GE6/1/0 | FLM_TE | [5 empty] | Observing Link Down Flapped and restored On JED1-PE Connected to Router ¦ JED1-PE-01 ¦ 400GE6/1/0 |  |  | API | 10/25/2025 07:47:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000209 | PCM-20251025-00000419 | TT-20251025-00484 | EM | Region_3 | MDN2564 | MDN2564 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/25/2025 07:50:44 | 10/25/2025 07:50:44 | 10/25/2025 19:50:44 | NETECO: Insufficient Redundant Rectifiers at MDN2564 @ Generator_DG | 10/25/2025 07:44:37 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/25/2025 07:44:37 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDN2564 | FLM_EM | [8 empty] | API | 10/25/2025 07:50:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000210 | PCM-20251025-00000422 | TT-20251025-00486 | Telecom | Region_2 | RIY2176 | RIY2176 | Equipment | BTS_Cable | Replace CPRI Cable | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/25/2025 07:52:48 | 10/25/2025 16:27:28 | 10/25/2025 13:52:48 | BBU CPRI Interface Error at RIY2176-P1-DIA_SRAN @ Sceco | 10/25/2025 07:50:07 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 07:47:34 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2176 | FLM_TE | [8 empty] | API | 10/25/2025 07:52:48 | 10/25/2025 16:23:55 | 10/25/2025 16:26:20 |  |  | 10/25/2025 16:27:28 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000211 | PCM-20251025-00000428 | TT-20251025-00483 | EM | Region_2 | BUR2M2038 | BUR2038 | Enviroment | SCECO_Failure | SCECO auto restored | Farman Ullah Muhammad Nazir | 10/25/2025 07:55:29 | 10/25/2025 13:44:03 | 10/25/2025 13:55:29 | 1(2G/3G/LTE) sites down under BUR2038-P2/R2_BR1_HWBSC01 @ Sceco | 10/25/2025 07:48:36 | Major | 21825 | CSL Fault | 10/25/2025 07:48:32 | P2 | 2G | buraidah | Sceco | 2G_3G_LTE SA | BUR2038-P2 | FLM_EM | BUR2038 | Results: DOWN SITE HUB BUR2038-P2 BUR2038 Summary: Hub: BUR2038, Down Count: 1, Down Sites: BUR2038-P2 Alarm Summary: BUR2038 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 07:55:29 | 10/25/2025 07:59:05 | 10/25/2025 13:43:56 |  |  | 10/25/2025 13:44:03 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000212 | PCM-20251025-00000429 | TT-20251025-00493 | Telecom | Region_2 | RIY2176 | RIY2176 | Equipment | BTS_Cable | Replace CPRI Cable | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/25/2025 07:55:54 | 10/25/2025 16:26:11 | 10/25/2025 13:55:54 | NR Cell Unavailable at RIY2176-P1-DIA_SRAN @ Sceco | 10/25/2025 07:49:12 | Major | 29841 | NR Cell Unavailable | 10/25/2025 07:47:37 | P1 | SRAN | riyadh | Sceco | 5G SA | RIY2176 | FLM_TE | [8 empty] | API | 10/25/2025 07:55:54 | 10/25/2025 16:23:54 | 10/25/2025 16:25:14 |  |  | 10/25/2025 16:26:11 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000213 | PCM-20251025-00000431 | TT-20251025-00495 | Reference_telecom | Region_4 | TAF0281 | TAF0281 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 07:56:55 | 10/25/2025 11:30:53 | 10/25/2025 19:56:55 | LagPortDown observed in TAF0281 towards 10.1.233.82 @ Sceco | 10/24/2025 19:58:24 | Minor |  | LagPortDown | 10/24/2025 19:56:26 | P1 | 2G | taif | Sceco | TX NSA | TAF0281 | FLM_TE | [8 empty] | API | 10/25/2025 07:56:55 | 10/25/2025 11:30:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000217 | PCM-20251025-00000441 | TT-20251025-00506 | Reference_EM | Region_2 | RIYA6147 | RIYA6147 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/25/2025 08:01:05 | 10/25/2025 17:04:17 | 10/25/2025 20:01:05 | Minor Rec alarm at RIYA6147-P3_SRAN @ Sceco | 10/25/2025 07:50:38 | Minor | 65108 | Minor Rec alarm | 10/25/2025 07:50:33 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6147 | FLM_EM | [8 empty] | API | 10/25/2025 08:01:05 | 10/25/2025 17:04:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000219 | PCM-20251025-00000444 | TT-20251025-00510 | Telecom | Region_4 | RYMK0528-LL-CSG | RYMK0528 | Transsmission | Fiber CUT | Mobily LL cut | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 08:02:38 | 10/25/2025 21:48:38 | 10/25/2025 12:02:38 | The Device is offline at RYMK0528-LL-CSG @ Generator_SG | 10/25/2025 08:02:01 | Critical | 101-7 | The Device is offline | 10/25/2025 08:01:59 | P1 | IPRAN | taif | Generator_SG | IPRAN SA | RYMK0528-LL-CSG | FLM_TE | [8 empty] | API | 10/25/2025 08:02:38 | 10/25/2025 11:30:53 | 10/25/2025 21:48:30 |  |  | 10/25/2025 21:48:38 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000221 | PCM-20251025-00000452 | TT-20251025-00511 | Telecom | Region_4 | RYMK0528 | RYMK0528 | Transsmission | Fiber CUT | Mobily LL cut | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 08:11:51 | 10/25/2025 21:51:50 | 10/25/2025 12:11:51 | 2(2G) 2(3G) 1(LTE) sites down under RYMK0665-P3,RYMK0528-P1/RYMK0528-P1 @ Generator_SG | 10/25/2025 08:00:36 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 08:00:29 | P1 | 2G | taif | Generator_SG | 2G_3G_LTE SA | RYMK0665-P3 2G_3G_LTE,RYMK0528-P1 2G_3G | FLM_TE | RYMK0528 | Hub: RYMK0528 We are observing no alarm flapped from our end at the outage time kindly send the FLM, EM to check the site | PCM-20251025-00000450 | Hub: RYMK0528 We are observing no alarm flapped from our end at the outage time kindly send the FLM, EM to check the site | Hub: RYMK0528 We are observing no alarm flapped from our end at the outage time kindly send the FLM, EM to check the site |  | sites down |  | API | 10/25/2025 08:11:51 | 10/25/2025 11:30:54 | 10/25/2025 21:51:43 |  |  | 10/25/2025 21:51:50 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000224 | PCM-20251025-00000463 | TT-20251025-00534 | Reference_telecom | Region_3 | MDN2U6915 | MDN6015 |  |  |  | TAUSEEF ILYAS | 10/25/2025 08:20:11 | 10/25/2025 11:03:57 | 10/25/2025 14:20:11 | RF Out of Service at MDN2U6915-P1-HRMCST @ Sceco | 10/25/2025 08:15:31 | Major | 29248 | RF Out of Service | 10/25/2025 08:13:58 | P1 | 4G | madinah | Sceco | 2G SA | MDN2U6915 | FLM_TE | [8 empty] | API | 10/25/2025 08:20:11 | 10/25/2025 11:03:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000225 | PCM-20251025-00000464 | TT-20251025-00537 | Telecom | Region_1 | DAM1-P | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/25/2025 08:22:46 | 10/25/2025 08:22:46 | 10/25/2025 20:22:46 | Chassis Fail at DAM1-P @ Sceco_STB | 10/25/2025 08:22:08 | Minor | 101-2505202 | Chassis Fail | 10/25/2025 08:22:03 | P1 | IPBB | dammam | Sceco_STB | IPRAN NSA | DAM1-P | FLM_TE | [8 empty] | API | 10/25/2025 08:22:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000226 | PCM-20251025-00000465 | TT-20251025-00539 | Telecom | Region_2 | RIYC6038 | RIYC6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/25/2025 08:23:47 | 10/25/2025 08:50:16 | 10/25/2025 20:23:47 | RF Unit Maintenance Link Failure at RIYC6038-DCU1 @ Sceco | 10/25/2025 08:22:09 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 08:13:09 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYC6038 | FLM_TE | [8 empty] | API | 10/25/2025 08:23:47 | 10/25/2025 08:50:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000227 | PCM-20251025-00000467 | TT-20251025-00544 | Reference_EM | Region_1 | HFBD2M5015 | HFBD0015 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/25/2025 08:25:50 | 10/25/2025 08:25:50 | 10/25/2025 14:25:50 | Door opening alarm at HFBD2M5015-P1-HUB @ Generator_DG | 10/25/2025 08:25:38 | Major | 65101 | Door opening alarm | 10/25/2025 08:25:34 | P1 | 2G | hafouf | Generator_DG | 2G NSA | HFBD2M5015 | FLM_EM | [8 empty] | API | 10/25/2025 08:25:50 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000228 | PCM-20251025-00000472 | TT-20251025-00546 | Reference_EM | Region_3 | HAL2M1941 | HAL0941 |  |  |  | Mohamed Hafez Fahim Abdelaziz | 10/25/2025 08:29:27 | 10/25/2025 09:53:02 | 10/25/2025 20:29:27 | Mains Failure at HAL2M1941-P3 @ Sceco | 10/25/2025 08:19:35 | Minor | 65109 | Mains Failure | 10/25/2025 08:19:28 | P3 | 2G | hail | Sceco | 2G NSA | HAL2M1941 | FLM_EM | [8 empty] | API | 10/25/2025 08:29:27 | 10/25/2025 09:53:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000231 | PCM-20251025-00000477 | TT-20251025-00555 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/25/2025 08:39:48 | 10/25/2025 17:48:03 | 10/25/2025 20:39:48 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/25/2025 08:33:38 | Minor | 1589 | AC Overfrequency | 10/25/2025 08:33:38 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/25/2025 08:39:48 | 10/25/2025 09:23:05 | 10/25/2025 17:47:54 |  |  | 10/25/2025 17:48:03 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000234 | PCM-20251025-00000482 | TT-20251025-00556 | Telecom | Region_2 | RIYA2U6174c | RIYA6074 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 08:44:59 | 10/25/2025 08:58:08 | 10/25/2025 14:44:59 | 1(2G) sites down under RIYA6074-P3/R2_RY1_HWBSC01 @ Sceco | 10/25/2025 08:36:34 | Major | 21807 | OML Fault | 10/25/2025 08:36:27 | P3 | 2G | riyadh | Sceco | 2G SA | RIYA6074-P3 | FLM_TE | RIYA6074 | Results: DOWN SITE HUB RIYA6074-P3 RIYA6074 Summary: Hub: RIYA6074, Down Count: 1, Down Sites: RIYA6074-P3 Alarm Summary: RIYA6074 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 08:44:59 | 10/25/2025 08:58:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000235 | PCM-20251025-00000488 | TT-20251025-00562 | Telecom | Region_4 | JED0519 | JED0519 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 08:50:38 | 10/25/2025 08:51:42 | 10/25/2025 20:50:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0519-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/25/2025 08:49:36 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 08:49:30 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0519 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 08:50:38 | 10/25/2025 08:51:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000237 | PCM-20251025-00000495 | TT-20251025-00577 | Reference_EM | Region_3 | FQR0998 | FQR0998 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Shafique Ahmad Sardar Ali | 10/25/2025 08:59:25 | 10/25/2025 11:56:23 | 10/25/2025 20:59:25 | Mains Failure at FQR0998-P2_SRAN @ Sceco | 10/25/2025 08:49:16 | Minor | 65109 | Mains Failure | 10/25/2025 08:49:14 | P2 | SRAN | madinah | Sceco | 2G NSA | FQR0998 | FLM_EM | [8 empty] | API | 10/25/2025 08:59:25 | 10/25/2025 09:17:20 | 10/25/2025 10:06:17 | 10/25/2025 10:06:19 | 10/25/2025 11:22:23 | 10/25/2025 11:56:23 |  | Shafique Ahmad Sardar Ali |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000239 | PCM-20251025-00000499 | TT-20251025-00580 | Reference_EM | Region_3 | HHR2084 | HHR2084 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Shafique Ahmad Sardar Ali | 10/25/2025 09:00:27 | 10/25/2025 17:37:11 | 10/25/2025 21:00:27 | Mains Failure at HHR2084-P3_SRAN-PC @ Generator_SG | 10/25/2025 08:50:20 | Minor | 65109 | Mains Failure | 10/25/2025 08:50:17 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HHR2084 | FLM_EM | [8 empty] | API | 10/25/2025 09:00:27 | 10/25/2025 09:18:03 | 10/25/2025 17:37:00 |  |  | 10/25/2025 17:37:11 |  | Shafique Ahmad Sardar Ali |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000248 | PCM-20251025-00000519 | TT-20251025-00606 | Telecom | Region_1 | DAM6095 | DAM6095 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 09:09:46 | 10/25/2025 11:06:53 | 10/25/2025 21:09:46 | RF Unit Maintenance Link Failure at DAM6095-P3_SRAN @ Sceco | 10/25/2025 09:06:26 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 09:04:42 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6095 | FLM_TE | [8 empty] | API | 10/25/2025 09:09:46 | 10/25/2025 11:06:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000250 | PCM-20251025-00000529 | TT-20251025-00611 | Telecom | Region_2 | WMZH0002 | WMZH0002 |  |  |  | Nawaz Sharif Muhammad Iqbal | 10/25/2025 09:17:26 | 10/25/2025 11:03:08 | 10/25/2025 21:17:26 | WMZH0002 Complete Down | 10/25/2025 09:05:49 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/25/2025 09:05:49 | P3 | WIFI | quweyah | Sceco | Wifi SA | WMZH0002 | FLM_TE |  | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally | PCM-20251025-00000524 | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally |  |  |  | API | 10/25/2025 09:17:26 | 10/25/2025 11:03:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000252 | PCM-20251025-00000536 | TT-20251025-00623 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/25/2025 09:21:07 | 10/26/2025 00:11:29 | 10/25/2025 15:21:07 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/25/2025 09:10:59 | Major | 65102 | high temprature 32 | 10/25/2025 09:10:56 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/25/2025 09:21:07 | 10/26/2025 00:11:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251025000253 | PCM-20251025-00000538 | TT-20251025-00624 | EM | [7 empty] | 10/25/2025 09:21:38 | 10/25/2025 09:21:38 | 10/25/2025 21:21:38 | SHELTER DOOR OPEN at AQQ1M8426-G9-L8-SBTS-P3 @ Generator_SG | 10/25/2025 09:21:21 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 09:21:11 | P3 | 4G |  | Generator_SG | LTE NSA | AQQ1M8426 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 09:21:38 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000254 | PCM-20251025-00000540 | TT-20251025-00609 | Reference_telecom | Region_2 | RIYC2U6725 | RIYC6025 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/25/2025 09:22:43 | 10/25/2025 19:14:43 | 10/25/2025 21:22:43 | Cell RX Channel Interference Noise Power Unbalanced at RIYC2U6725-L800-CA-P3 @ Sceco | 10/25/2025 06:12:12 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 06:12:08 | P2 | 4G | riyadh | Sceco | 2G NSA | RIYC2U6725 | FLM_TE |  |  | PCM-20251025-00000523 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/25/2025 09:22:43 | 10/25/2025 19:14:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000255 | PCM-20251025-00000542 | TT-20251025-00628 | EM | [7 empty] | 10/25/2025 09:25:15 | 10/25/2025 09:25:15 | 10/25/2025 21:25:15 | RECTIFIER MODULE FAILURE at AQQ1M8426-G9-L8-SBTS-P3 @ Generator_SG | 10/25/2025 09:18:27 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/25/2025 09:16:44 | P3 | 4G |  | Generator_SG | LTE NSA | AQQ1M8426 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/25/2025 09:25:15 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000256 | PCM-20251025-00000549 | TT-20251025-00329 | Reference_telecom | Region_3 | HLUL2300 | HLUL2300 |  |  |  | Muhamed Ismail Muhamed Daoud | 10/25/2025 09:34:45 | 10/25/2025 09:34:45 | 10/25/2025 21:34:45 | External Clock Reference Problem at HLUL2300-P2_SRAN @ Generator_SG | 10/25/2025 02:49:26 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 02:42:10 | P2 | SRAN | hail | Generator_SG | 2G NSA | HLUL2300 | FLM_EM |  | Dear TX Team kindly check as IP CLK unavailable Link No. = 0 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.153.163.238 VRF Index = 0 Server IPv4 = 10.161.136.169 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = ON Clock Server Description = NULL Link No. = 1 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.153.163.238 VRF Index = 0 Server IPv4 = 10.161.137.169 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = ON Clock Server Description = NULL (Number of results = 2) | PCM-20251025-00000421 | We are observing RSL -90 at hub site HLUL2300 ,Suspected power issue, Dear EM FLM please check issue and solve | We are observing RSL -90 at hub site HLUL2300 ,Suspected power issue, Dear EM FLM please check issue and solve |  |  |  | API | 10/25/2025 09:34:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000261 | PCM-20251025-00000567 | TT-20251025-00656 | EM | Region_6 | QLW1M8374 | QLW2374 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 09:46:27 | 10/25/2025 13:52:43 | 10/25/2025 21:46:27 | SHELTER DOOR OPEN at QLW1M8374-G9-L8-L18-SBTS-P3-P3 @ Generator_SG | 10/25/2025 09:45:54 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 09:45:50 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8374 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 09:46:27 | 10/25/2025 13:52:43 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000263 | PCM-20251025-00000585 | TT-20251025-00674 | Telecom | Region_4 | JED1MN2140 | JED2140 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 09:54:43 | 10/25/2025 09:54:43 | 10/25/2025 15:54:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2140-NR2.6-P2 @ Sceco | 10/25/2025 09:53:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 09:53:52 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2140 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 09:54:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000265 | PCM-20251025-00000592 | TT-20251025-00679 | EM | Region_1 | TRAP2M2982 | TRAP2982 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Bashir Sahib Rahman | 10/25/2025 10:02:30 | 10/25/2025 16:40:39 | 10/25/2025 16:02:30 | 1(2G/3G) sites down under TRAP2982-P3/AR1BSCH01 @ Sceco | 10/25/2025 09:55:24 | Major | 21825 | CSL Fault | 10/25/2025 09:55:22 | P1 | 2G | quriyat | Sceco | 2G_3G SA | TRAP2982-P3 | FLM_EM | TRAP2982 | Results: DOWN SITE HUB TRAP2982-P3 TRAP2982 Summary: Hub: TRAP2982, Down Count: 1, Down Sites: TRAP2982-P3 Alarm Summary: TRAP2982 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 10:02:30 | 10/25/2025 12:55:57 | 10/25/2025 16:40:26 |  |  | 10/25/2025 16:40:39 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000266 | PCM-20251025-00000593 | TT-20251025-00587 | Telecom | Region_1 | TRF0988 | TRF0988 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/25/2025 10:03:19 | 10/25/2025 10:28:50 | 10/25/2025 16:03:19 | NR Cell Unavailable at TRF0988-FWA-P1-VIP-HUB-WDM_SRAN @ Sceco_STB | 10/25/2025 08:55:42 | Major | 29841 | NR Cell Unavailable | 10/25/2025 08:55:20 | VIP | SRAN | arar | Sceco_STB | 5G SA | TRF0988 | FLM_TE |  |  | PCM-20251025-00000509 | after EM team visit site found 5G down due to equipment CB trip | after EM team visit site found 5G down due to equipment CB trip |  |  |  | API | 10/25/2025 10:03:19 | 10/25/2025 10:28:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000267 | PCM-20251025-00000594 | TT-20251025-00683 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/25/2025 10:03:30 | 10/25/2025 21:15:34 | 10/25/2025 22:03:30 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/25/2025 09:55:16 | Minor | 7103 | HIGH TEMP | 10/25/2025 09:55:12 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/25/2025 10:03:30 | 10/25/2025 21:15:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000268 | PCM-20251025-00000599 | TT-20251025-00690 | Reference_EM | Region_2 | RIY2051 | RIY2051 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Tanveer Ahmad Fateh Muhammad | 10/25/2025 10:09:42 | 10/25/2025 13:04:39 | 10/25/2025 16:09:42 | Mains Failure at RIY2051-P1-VIP_SRAN @ Sceco | 10/25/2025 09:59:34 | Major | 65109 | Mains Failure | 10/25/2025 09:59:31 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2051 | FLM_EM | [8 empty] | API | 10/25/2025 10:09:42 | 10/25/2025 11:20:09 | 10/25/2025 11:20:17 | 10/25/2025 11:20:21 | 10/25/2025 11:20:23 | 10/25/2025 13:04:39 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000269 | PCM-20251025-00000604 | TT-20251025-00694 | Telecom | Region_1 | HMBY2M8501 | HMBY2501 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 10:11:45 | 10/25/2025 10:15:52 | 10/25/2025 16:11:45 | Cell Unavailable at HMBY2M8501-P3-L800 @ Sceco | 10/25/2025 10:08:53 | Major | 29240 | Cell Unavailable | 10/25/2025 10:07:20 | P3 | 4G | dammam | Sceco | LTE SA | HMBY2M8501 | FLM_TE | [8 empty] | API | 10/25/2025 10:11:45 | 10/25/2025 10:15:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000270 | PCM-20251025-00000606 | TT-20251025-00695 | Telecom | Region_2 | RAS2248 | RAS2248 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Syed Sibtain Naqvi SyedManzoor | 10/25/2025 10:12:47 | 10/25/2025 15:03:50 | 10/25/2025 22:12:47 | ALD Maintenance Link Failure at RAS2248-FWA-P1-VIP_SRAN @ Sceco | 10/25/2025 10:10:15 | Minor | 26541 | ALD Maintenance Link Failure | 10/25/2025 10:08:40 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS2248 | FLM_TE | [8 empty] | API | 10/25/2025 10:12:47 | 10/25/2025 13:49:38 | 10/25/2025 13:49:43 | 10/25/2025 13:54:13 | 10/25/2025 14:18:10 | 10/25/2025 15:03:50 |  | Syed Sibtain Naqvi SyedManzoor |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000271 | PCM-20251025-00000605 | TT-20251025-00697 | Reference_EM | Region_2 | RIYD6037 | RIYD6037 |  |  |  | Adham Adham Hassan Farghal | 10/25/2025 10:12:48 | 10/25/2025 12:17:22 | 10/25/2025 16:12:48 | high temprature 32 at RIYD6037-P1-VIP_SRAN @ Sceco | 10/25/2025 10:02:27 | Major | 65102 | high temprature 32 | 10/25/2025 10:02:23 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_EM | [8 empty] | API | 10/25/2025 10:12:48 | 10/25/2025 12:17:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000273 | PCM-20251025-00000609 | TT-20251025-00689 | Telecom | Region_2 | DWD2113 | DWD2113 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Zakir Muhammad Yar Muhammad | 10/25/2025 10:13:29 | 10/26/2025 03:56:58 | 10/25/2025 16:13:29 | 1(5G) sites down under DWD2113-P3_SRAN @ Sceco | 10/25/2025 10:06:57 | Major | 29840 | gNodeB Out of Service | 10/25/2025 10:05:23 | P3 | SRAN | dawadmi | Sceco | 5G SA | DWD2113-P3_SRAN | FLM_TE | DWD2113 | Results: DOWN SITE HUB DWD2113-P3_SRAN DWD2113 Summary: Hub: DWD2113, Down Count: 1, Down Sites: DWD2113-P3_SRAN Alarm Summary: DWD2113 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 10:13:29 | 10/25/2025 15:51:33 | 10/26/2025 03:56:28 |  |  | 10/26/2025 03:56:58 |  | Zakir Muhammad Yar Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000274 | PCM-20251025-00000610 | TT-20251025-00700 | Telecom | Region_1 | JBL0422 | JBL0422 |  |  |  | Tahir Mahmood Hafiz Yar | 10/25/2025 10:14:21 | 10/25/2025 10:29:13 | 10/25/2025 22:14:21 | RF Unit Maintenance Link Failure at JBL0422-P2_SRAN @ Sceco | 10/25/2025 00:54:46 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 00:53:03 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0422 | FLM_TE | [8 empty] | API | 10/25/2025 10:14:21 | 10/25/2025 10:29:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000275 | PCM-20251025-00000612 | TT-20251025-00702 | Reference_telecom | Region_6 | SMT0063 | SMT0063 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | Mohammed Sideag Mohammed Ali | 10/25/2025 10:15:22 | 10/25/2025 19:13:13 | 10/25/2025 22:15:22 | Degrade observed in SMT0063 _3 towards 10.3.226.41 @ Sceco | 10/24/2025 22:17:03 | Minor |  | Degrade | 10/24/2025 22:15:06 | P1 | 2G | jizan | Sceco | TX NSA | SMT0063 | FLM_TE | [8 empty] | API | 10/25/2025 10:15:22 | 10/25/2025 13:35:31 | 10/25/2025 19:00:12 | 10/25/2025 19:00:24 | 10/25/2025 19:00:32 | 10/25/2025 19:13:13 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000278 | PCM-20251025-00000617 | TT-20251025-00706 | EM | Region_3 | RUSF9069 | RUSF9069 |  |  |  | Muhamad Hanif Ahmad | 10/25/2025 10:16:24 | 10/25/2025 16:23:15 | 10/25/2025 14:16:24 | RELAY_ALARM_CRITICAL at RUSF9069_NE_2 @ Generator_SG | 10/25/2025 10:15:46 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/25/2025 10:15:33 | P3 | Repeater | madinah | Generator_SG | TX NSA | RUSF9069 | FLM_EM | [8 empty] | API | 10/25/2025 10:16:24 | 10/25/2025 16:23:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000279 | PCM-20251025-00000618 | TT-20251025-00709 | EM | Region_3 | RUSF9069 | RUSF9069 |  |  |  | Muhamad Hanif Ahmad | 10/25/2025 10:17:58 | 10/25/2025 16:23:16 | 10/25/2025 14:17:58 | RELAY_ALARM_MAJOR at RUSF9069_NE_2 @ Generator_SG | 10/25/2025 10:16:06 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/25/2025 10:15:54 | P3 | Repeater | madinah | Generator_SG | TX NSA | RUSF9069 | FLM_EM | [8 empty] | API | 10/25/2025 10:17:58 | 10/25/2025 16:23:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000280 | PCM-20251025-00000620 | TT-20251025-00680 | Telecom | Region_6 | TBL2295 | TBL2295 |  |  |  | Abdul Rauf Muhammad Aslam | 10/25/2025 10:18:15 | 10/25/2025 11:48:21 | 10/25/2025 16:18:15 | 3(2G) 3(LTE) sites down under TBL2328-P3,TBL2295-P3,TBL2324-P3/TBL2324-P3 @ Generator_DG | 10/25/2025 09:55:51 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 09:55:48 | P3 | 2G | bisha | Generator_DG | 2G_LTE SA | TBL2324-P3 2G_LTE,TBL2328-P3 2G_LTE,TBL2295-P3 2G_LTE | FLM_EM | TBL2295 | Hub:TBL2295 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251025-00000595 | Hub:TBL2295 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub:TBL2295 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/25/2025 10:18:15 | 10/25/2025 11:48:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000281 | PCM-20251025-00000621 | TT-20251024-00518 | Telecom | Region_5 | MAK1M9982 | MAK0982 | Equipment | BTS_Cable | Replace CPRI Cable | KAMRAN AAMIR | 10/25/2025 10:18:28 | 10/25/2025 10:59:19 | 10/25/2025 16:18:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9982-P2-CA-L800 @ Sceco | 10/24/2025 08:52:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 08:52:05 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9982 | FLM_TE |  |  | PCM-20251024-00000570 | No Power Issue | No Power Issue |  |  |  | API | 10/25/2025 10:18:28 |  | 10/25/2025 10:53:00 | 10/25/2025 10:53:06 | 10/25/2025 10:57:56 | 10/25/2025 10:59:19 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000283 | PCM-20251025-00000627 | TT-20251025-00626 | Telecom | Region_4 | JED0219 | JED0219 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 10:21:56 | 10/25/2025 10:21:56 | 10/25/2025 16:21:56 | 2(2G) 1(LTE) 2(5G) sites down under JED0219-P2,JED2561-P3/JED2561-P3 @ Sceco | 10/25/2025 09:19:17 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 09:19:14 | P2 | 2G | jeddah | Sceco | 2G_5G SA | JED0219-P2 2G_5G,JED2561-P3 2G | FLM_TE | JED0219 | Scattered sites:JED0519 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0219 observing LOS TO AIRSCALE Kindly update TT under EM, FLM | PCM-20251025-00000544 | Scattered sites:JED0519 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0219 observing LOS TO AIRSCALE Kindly update TT under EM, FLM | Scattered sites:JED0519 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0219 observing LOS TO AIRSCALE Kindly update TT under EM, FLM |  | sites down |  | API | 10/25/2025 10:21:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000284 | PCM-20251025-00000631 | TT-20251025-00717 | Telecom | Region_2 | RIYD6037 | RIYD6037 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/25/2025 10:22:06 | 10/25/2025 10:55:23 | 10/25/2025 22:22:06 | RF Unit Maintenance Link Failure at RIYD6037-DCU2 @ Sceco | 10/25/2025 10:09:56 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 10:16:49 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_TE | [8 empty] | API | 10/25/2025 10:22:06 | 10/25/2025 10:50:41 | 10/25/2025 10:54:30 |  |  | 10/25/2025 10:55:23 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000286 | PCM-20251025-00000632 | TT-20251025-00719 | Reference_EM | Region_3 | AHT2339 | AHT2339 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 10:22:36 | 10/25/2025 10:47:08 | 10/25/2025 22:22:36 | Mains Failure at AHT2339-P3-USF_SRAN @ Sceco | 10/25/2025 10:12:45 | Minor | 65109 | Mains Failure | 10/25/2025 10:12:41 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2339 | FLM_EM | [8 empty] | API | 10/25/2025 10:22:36 | 10/25/2025 10:47:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000289 | PCM-20251025-00000636 | TT-20251025-00723 | EM | Region_6 | MTB1M8377 | MTB2377 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 10:23:07 | 10/25/2025 11:26:02 | 10/25/2025 22:23:07 | COMMERCIAL POWER FAILURE at MTB1M8377-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/25/2025 10:14:51 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/25/2025 10:14:45 | P2 | 4G | Baha | Sceco | LTE NSA | MTB1M8377 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/25/2025 10:23:07 | 10/25/2025 11:26:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000293 | PCM-20251025-00000646 | TT-20251025-00707 | Telecom | Region_6 | TLM2223 | TLM2223 |  |  |  | Zia Ur Rahamn | 10/25/2025 10:28:26 | 10/25/2025 10:37:54 | 10/25/2025 16:28:26 | 3(2G) 2(LTE) sites down under TLM2223-P3,TNM0724-P3,TLM2248-P3/TLM2248-P3 @ Sceco | 10/25/2025 10:13:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 10:13:39 | P3 | 2G | mohail | Generator_SG | 2G_LTE SA | TLM2223-P3 2G_LTE,TLM2248-P3 2G_LTE,TNM0724-P3 2G | FLM_EM | TLM2223 | Hub: TLM2223 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. TNM0720 observing visibility down Kindly update TT under EM, FLM | PCM-20251025-00000628 | Hub: TLM2223 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. TNM0720 observing visibility down Kindly update TT under EM, FLM | Hub: TLM2223 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. TNM0720 observing visibility down Kindly update TT under EM, FLM |  | sites down |  | API | 10/25/2025 10:28:26 | 10/25/2025 10:37:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000297 | PCM-20251025-00000650 | TT-20251025-00743 | EM | Region_6 | BHS1M8367 | BHS2367 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 10:30:22 | 10/25/2025 11:26:02 | 10/25/2025 22:30:22 | SHELTER DOOR OPEN at BHS1M8367-G9-L8-L18-SBTS @ Sceco | 10/25/2025 10:30:01 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 10:29:55 | P3 | 4G | Baha | Sceco | LTE NSA | BHS1M8367 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 10:30:22 | 10/25/2025 11:26:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000298 | PCM-20251025-00000651 | TT-20251025-00744 | Telecom | Region_4 | JED1M8208 | JED2208 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 10:30:22 | 10/25/2025 11:34:24 | 10/25/2025 16:30:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8208-CA-L800-P3 @ | 10/25/2025 10:29:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 10:29:35 | P3 | 4G | jeddah |  | 5G_Cell SA | JED1M8208 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 10:30:22 | 10/25/2025 11:34:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000301 | PCM-20251025-00000655 | TT-20251025-00634 | EM | Region_6 | MKW0037 | MKW0037 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/25/2025 10:32:28 | 10/25/2025 16:10:29 | 10/25/2025 16:32:28 | 1(3G/5G) sites down under MKW0037-P3-WBB-G3/MKW1M3037-P3-WBB-G3 @ Sceco | 10/25/2025 09:28:10 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/25/2025 09:27:31 | P3 | 2G | makhwa | Sceco | 3G_5G SA | MKW0037-P3-WBB-G3 | FLM_TE | MKW0037 | Hub: MKW0037 We are observing Demodulator failure, unavailable time, RDI, PPP failure, CLK failure at site kindly send team to check locally | PCM-20251025-00000560 | Hub: MKW0037 We are observing Demodulator failure, unavailable time, RDI, PPP failure, CLK failure at site kindly send team to check locally | Hub: MKW0037 We are observing Demodulator failure, unavailable time, RDI, PPP failure, CLK failure at site kindly send team to check locally |  | sites down |  | API | 10/25/2025 10:32:28 | 10/25/2025 16:06:58 | 10/25/2025 16:10:21 |  |  | 10/25/2025 16:10:29 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000303 | PCM-20251025-00000657 | TT-20251025-00747 | Reference_EM | Region_3 | RSP0814 | RSP0814 | Enviroment | SCECO_Failure | SCECO auto restored | Sayed Satoor | 10/25/2025 10:33:58 | 10/25/2025 16:50:34 | 10/25/2025 22:33:58 | Mains Failure at RSP0814-P3_SRAN @ Generator_SG | 10/25/2025 10:24:04 | Minor | 65109 | Mains Failure | 10/25/2025 10:23:59 | P3 | SRAN | Deba | Generator_SG | 2G NSA | RSP0814 | FLM_EM | [8 empty] | API | 10/25/2025 10:33:58 | 10/25/2025 14:53:22 | 10/25/2025 16:50:21 |  |  | 10/25/2025 16:50:34 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000306 | PCM-20251025-00000663 | TT-20251025-00750 | Telecom | Region_5 | MAK1M9982 | MAK0982 |  |  |  | Husain Hassan Ishag Omer | 10/25/2025 10:36:03 | 10/25/2025 11:01:39 | 10/25/2025 16:36:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9982-P2-CA-L800 @ Sceco | 10/25/2025 10:35:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 10:35:16 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9982 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 10:36:03 | 10/25/2025 11:01:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000308 | PCM-20251025-00000670 | TT-20251025-00756 | Telecom | Region_4 | JED2063 | JED2063 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 10:39:08 | 10/25/2025 10:39:08 | 10/25/2025 22:39:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2063-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 10:38:06 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 10:37:53 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2063 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 10:39:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000309 | PCM-20251025-00000671 | TT-20251025-00757 | EM | Region_6 | JDJZ1M7790 | JDJZ0790 |  |  |  | Khurram Nawaz Muhammad Akram | 10/25/2025 10:39:09 | 10/26/2025 10:52:42 | 10/25/2025 22:39:09 | SHELTER DOOR OPEN;Default System Time at JDJZ1M7790-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/25/2025 10:38:39 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/25/2025 03:01:30 | P2 | 4G | jizan | Sceco | LTE NSA | JDJZ1M7790 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/25/2025 10:39:09 | 10/26/2025 10:52:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000310 | PCM-20251025-00000673 | TT-20251025-00748 | EM | Region_6 | JDJZ0790 | JDJZ0790 |  |  |  | Khurram Nawaz Muhammad Akram | 10/25/2025 10:39:59 | 10/26/2025 10:52:43 | 10/25/2025 16:39:59 | 1(2G/3G/LTE) sites down under JDJZ0790-P2/JDJZ0790-P2 @ Sceco | 10/25/2025 10:32:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 10:32:09 | P2 | 2G | jizan | Sceco | 2G_3G_LTE SA | JDJZ0790-P2 | FLM_EM | JDJZ0790 | Results: DOWN SITE HUB JDJZ0790-P2 JDJZ0790 Summary: Hub: JDJZ0790, Down Count: 1, Down Sites: JDJZ0790-P2 Alarm Summary: JDJZ0790 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 10:39:59 | 10/26/2025 10:52:43 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000313 | PCM-20251025-00000677 | TT-20251025-00751 | Telecom | Region_3 | TBK2M3104 | TBK0104 |  |  |  | Mehsan Bin Sayeed | 10/25/2025 10:41:30 | 10/25/2025 10:49:47 | 10/25/2025 16:41:30 | 1(3G) sites down under TBK0104-P3/TB1RNCH01 @ Sceco | 10/25/2025 10:33:05 | Major | 22214 | NodeB Unavailable | 10/25/2025 10:33:01 | P3 | 3G | tabouk | Sceco | 3G SA | TBK0104-P3 | FLM_TE | TBK0104 | Results: DOWN SITE HUB TBK0104-P3 TBK0104 Summary: Hub: TBK0104, Down Count: 1, Down Sites: TBK0104-P3 Alarm Summary: TBK0104 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 10:41:30 | 10/25/2025 10:49:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000315 | PCM-20251025-00000680 | TT-20251025-00763 | EM | Region_6 | MTB1M8377 | MTB2377 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 10:42:46 | 10/25/2025 11:26:03 | 10/25/2025 22:42:46 | SHELTER DOOR OPEN at MTB1M8377-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/25/2025 10:42:10 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 10:42:04 | P2 | 4G | Baha | Sceco | LTE NSA | MTB1M8377 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 10:42:46 | 10/25/2025 11:26:03 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000316 | PCM-20251025-00000679 | TT-20251025-00762 | Reference_EM | Region_3 | HNK2272 | HNK2272 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/25/2025 10:42:46 | 10/25/2025 11:59:25 | 10/25/2025 22:42:46 | Mains Failure at HNK2272-P3_SRAN @ Sceco | 10/25/2025 10:32:46 | Minor | 65109 | Mains Failure | 10/25/2025 10:32:43 | P3 | SRAN | madinah | Sceco | 2G NSA | HNK2272 | FLM_EM | [8 empty] | API | 10/25/2025 10:42:46 | 10/25/2025 11:59:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000317 | PCM-20251025-00000682 | TT-20251025-00766 | Telecom | Region_4 | JED2721 | JED2721 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 10:43:16 | 10/25/2025 18:10:09 | 10/25/2025 16:43:16 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2721-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/25/2025 10:42:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 10:42:21 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2721 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 10:43:16 | 10/25/2025 17:56:30 | 10/25/2025 18:02:40 | 10/25/2025 18:02:42 | 10/25/2025 18:10:09 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000319 | PCM-20251025-00000685 | TT-20251025-00759 | EM | Region_4 | JED1M8596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 10:44:59 | 10/25/2025 11:40:04 | 10/25/2025 14:44:59 | 1(2G/LTE/5G) sites down under JED2596-P1 @ Sceco | 10/25/2025 10:36:56 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 10:36:54 | P1 | 4G | jeddah | Sceco | LTE SA | JED2596-P1-CA-L800 | FLM_TE | JED2596 | Results: DOWN SITE HUB JED2596-P1-CA-L800 JED2596 Summary: Hub: JED2596, Down Count: 1, Down Sites: JED2596-P1-CA-L800 Alarm Summary: JED2596 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.97.88.52:8080] [URL:http://10.97.88.52:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 10:44:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000320 | PCM-20251025-00000687 | TT-20251025-00770 | EM | Region_6 | BHS1M8367 | BHS2367 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 10:47:25 | 10/25/2025 11:26:04 | 10/25/2025 22:47:25 | RECTIFIER MAINS POWER FAILURE at BHS1M8367-G9-L8-L18-SBTS @ Sceco | 10/25/2025 10:39:06 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 10:39:01 | P3 | 4G | Baha | Sceco | LTE NSA | BHS1M8367 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 10:47:25 | 10/25/2025 11:26:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000321 | PCM-20251025-00000688 | TT-20251025-00771 | EM | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Gamal Mohamed Farag | 10/25/2025 10:47:25 | 10/26/2025 02:22:15 | 10/25/2025 22:47:25 | HIGH TEMPERATURE 32 DEGREE C at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/25/2025 10:39:23 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/25/2025 10:39:14 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7558 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/25/2025 10:47:25 | 10/26/2025 02:22:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000322 | PCM-20251025-00000690 | TT-20251025-00774 | EM | Region_6 | JDJZ1M7790 | JDJZ0790 |  |  |  | Khurram Nawaz Muhammad Akram | 10/25/2025 10:48:28 | 10/26/2025 10:52:43 | 10/25/2025 22:48:28 | AIRCON 1 FAILURE at JDJZ1M7790-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/25/2025 10:40:24 | Minor | 7103 | AIRCON 1 FAILURE | 10/25/2025 10:40:20 | P2 | 4G | jizan | Sceco | LTE NSA | JDJZ1M7790 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/25/2025 10:48:28 | 10/26/2025 10:52:43 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000323 | PCM-20251025-00000691 | TT-20251025-00776 | Telecom | Region_2 | RIY2M8965 | RIY2965 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Khan zeb Shah nawaz | 10/25/2025 10:52:52 | 10/25/2025 12:10:23 | 10/25/2025 16:52:52 | Cell Unavailable at RIY2M8965-L800-L1800-CA-P3 @ Generator_SG | 10/25/2025 10:52:10 | Major | 29240 | Cell Unavailable | 10/25/2025 10:50:37 | P3 | 4G | riyadh | Generator_SG | LTE SA | RIY2M8965 | FLM_TE | [8 empty] | API | 10/25/2025 10:52:52 | 10/25/2025 11:08:38 | 10/25/2025 12:10:04 |  |  | 10/25/2025 12:10:23 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000324 | PCM-20251025-00000692 | TT-20251025-00778 | Telecom | Region_1 | ARR2U6702 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 10/25/2025 10:53:08 | 10/25/2025 12:22:55 | 10/25/2025 16:53:08 | Cell Unavailable at ARR2U6702-P3 @ Sceco | 10/25/2025 10:49:42 | Major | 29240 | Cell Unavailable | 10/25/2025 10:48:07 | P3 | 4G | arar | Sceco | LTE SA | ARR2U6702 | FLM_TE | [8 empty] | API | 10/25/2025 10:53:08 | 10/25/2025 12:22:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000325 | PCM-20251025-00000693 | TT-20251025-00779 | Telecom | Region_1 | ARR6002 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 10/25/2025 10:53:37 | 10/25/2025 12:22:56 | 10/25/2025 22:53:37 | RF Unit Maintenance Link Failure at ARR6002-P3_SRAN @ Sceco | 10/25/2025 10:49:46 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 10:48:05 | P3 | SRAN | arar | Sceco | 2G NSA | ARR6002 | FLM_TE | [8 empty] | API | 10/25/2025 10:53:37 | 10/25/2025 12:22:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000326 | PCM-20251025-00000695 | TT-20251025-00781 | Telecom | Region_1 | ARR6002 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 10/25/2025 10:55:09 | 10/25/2025 12:22:57 | 10/25/2025 16:55:09 | BBU CPRI Interface Error at ARR6002-P3_SRAN @ Sceco | 10/25/2025 10:50:41 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 10:48:00 | P3 | SRAN | arar | Sceco | 2G NSA | ARR6002 | FLM_TE | [8 empty] | API | 10/25/2025 10:55:09 | 10/25/2025 12:22:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000328 | PCM-20251025-00000710 | TT-20251025-00485 | EM | Region_6 | BSA0446 | BSA0446 | Transsmission | SFP_Transmission | Replace SFP | Hamid Ullah Muhammad Alam Khan | 10/25/2025 11:03:32 | 10/25/2025 17:23:48 | 10/25/2025 17:03:32 | 1(2G/3G/5G) sites down under BSA0446-P3/BSA0446-P3 @ Sceco | 10/25/2025 07:49:38 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 07:49:34 | P3 | 2G | bisha | Sceco | 2G_3G_5G SA | BSA0446-P3 | FLM_TE | BSA0446 | Results: DOWN SITE HUB BSA0446-P3 BSA0446 Summary: Hub: BSA0446, Down Count: 1, Down Sites: BSA0446-P3 Alarm Summary: BSA0446 No Active Alarm on HUB | PCM-20251025-00000432 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 11:03:32 | 10/25/2025 11:40:38 | 10/25/2025 17:23:26 |  |  | 10/25/2025 17:23:48 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000332 | PCM-20251025-00000719 | TT-20251024-01430 | Telecom | Region_5 | MAK1MC0856 | MAK0856 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 11:08:43 | 10/25/2025 11:08:43 | 10/25/2025 17:08:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MC0856-NR3.5-P3 @ Sceco | 10/24/2025 22:09:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 22:09:09 | P3 | 5G | makkah | Sceco | 5G_Cell SA | MAK1MC0856 | FLM_TE |  |  | PCM-20251025-00000674 | No Power Issue | No Power Issue |  |  |  | API | 10/25/2025 11:08:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000333 | PCM-20251025-00000725 | TT-20251025-00805 | Telecom | Region_4 | JED1M8256 | JED2256 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/25/2025 11:11:42 | 10/25/2025 17:42:20 | 10/25/2025 17:11:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8256-CA-L800-P1-VIP-SBTS @ Generator_SG | 10/25/2025 11:10:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:10:34 | VIP | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8256 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 11:11:42 | 10/25/2025 17:00:09 | 10/25/2025 17:42:14 |  |  | 10/25/2025 17:42:20 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000334 | PCM-20251025-00000727 | TT-20251025-00807 | Reference_telecom | Region_1 | ARR2U6702 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 10/25/2025 11:13:46 | 10/25/2025 12:22:58 | 10/25/2025 17:13:46 | RF Out of Service at ARR2U6702-P3 @ Sceco | 10/25/2025 11:08:51 | Major | 29248 | RF Out of Service | 10/25/2025 11:07:17 | P3 | 4G | arar | Sceco | 2G SA | ARR2U6702 | FLM_TE | [8 empty] | API | 10/25/2025 11:13:46 | 10/25/2025 12:22:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000335 | PCM-20251025-00000728 | TT-20251025-00602 | Telecom | Region_1 | DAM2U6195 | DAM6095 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 11:14:42 | 10/25/2025 15:09:28 | 10/25/2025 17:14:42 | GSM Local Cell Unusable at DAM2U6195-P3 @ Sceco | 10/25/2025 09:06:28 | Major | 28016 | GSM Local Cell Unusable | 10/25/2025 09:04:54 | P3 | 2G | dammam | Sceco | 2G SA | DAM2U6195 | FLM_TE |  |  | PCM-20251025-00000724 | H.W alarm check locally | H.W alarm check locally |  |  |  | API | 10/25/2025 11:14:42 | 10/25/2025 15:09:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000338 | PCM-20251025-00000740 | TT-20251025-00819 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/25/2025 11:19:27 | 10/25/2025 11:20:10 | 10/25/2025 17:19:27 | Board Temperature Unacceptable at RIY2866-P3_SRAN-PC @ Sceco | 10/25/2025 11:10:37 | Major | 26104 | Board Temperature Unacceptable | 10/25/2025 11:09:11 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/25/2025 11:19:27 | 10/25/2025 11:20:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000340 | PCM-20251025-00000744 | TT-20251025-00448 | Telecom | Region_4 | JED0202 | JED0202 | Equipment | BSS_HW_Stuck | Reset FAN | Abdullah Ahmad Mohammad Abdelsheekh | 10/25/2025 11:23:26 | 10/25/2025 12:54:59 | 10/25/2025 17:23:26 | 3(2G) 2(LTE) 2(5G) sites down under JED0202-P2,JED2056-P3,JED0746-P2/JED0746-P2 @ Sceco | 10/25/2025 07:31:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 07:30:59 | P2 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED0202-P2 2G_LTE,JED0746-P2 2G_5G,JED2056-P3 2G | FLM_TE | JED0202 | Results: DOWN SITE HUB JED0202-P2 JED0202 JED0746-P2 JED0202 JED2056-P3 JED0202 Summary: Hub: JED0202, Down Count: 3, Down Sites: JED0202-P2, JED0746-P2, JED2056-P3 Alarm Summary: JED0202 Alarm Active on HUB | PCM-20251025-00000408 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 11:23:26 | 10/25/2025 12:21:16 | 10/25/2025 12:23:42 | 10/25/2025 12:23:44 | 10/25/2025 12:23:48 | 10/25/2025 12:54:59 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000341 | PCM-20251025-00000747 | TT-20251025-00825 | Reference_telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 11:24:37 | 10/25/2025 11:24:37 | 10/25/2025 17:24:37 | BASE STATION SERVICE PROBLEM (RX out of order) at JED1M8061-CA-L800-SBTS @ Sceco | 10/25/2025 11:19:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:19:51 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M8061 | FLM_TE | [5 empty] | RX out of order |  |  | API | 10/25/2025 11:24:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000344 | PCM-20251025-00000753 | TT-20251025-00830 | Telecom | Region_4 | MLJI0089 | MLJI0089 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/25/2025 11:26:40 | 10/25/2025 18:07:10 | 10/25/2025 17:26:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at MLJI0089-GSM-UMTS-P3 @ Generator_SG | 10/25/2025 11:25:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:25:47 | P3 | 2G | qunfuddah | Generator_SG | 5G_Cell SA | MLJI0089 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 11:26:40 | 10/25/2025 18:07:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000345 | PCM-20251025-00000754 | TT-20251025-00822 | Telecom | Region_4 | JED0177 | JED0177 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 11:27:59 | 10/25/2025 11:27:59 | 10/25/2025 17:27:59 | 1(2G) sites down under JED0177-P2/JED0177-P2 @ Sceco | 10/25/2025 11:19:37 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 11:19:32 | P2 | 2G | jeddah | Sceco | 2G SA | JED0177-P2 | FLM_TE | JED0177 | Results: DOWN SITE HUB JED0177-P2 JED0177 Summary: Hub: JED0177, Down Count: 1, Down Sites: JED0177-P2 Alarm Summary: JED0177 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 11:27:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000346 | PCM-20251025-00000755 | TT-20251025-00831 | EM | Region_6 | UKHA1M8371 | UKHA2371 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 11:28:13 | 10/25/2025 11:28:50 | 10/25/2025 23:28:13 | SHELTER DOOR OPEN at UKHA1M8371-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/25/2025 11:27:44 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 11:27:33 | P3 | 4G | Baha | Generator_DG | LTE NSA | UKHA1M8371 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 11:28:13 | 10/25/2025 11:28:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000347 | PCM-20251025-00000757 | TT-20251025-00548 | Telecom | Region_6 | BHAB9038 | BHAB9038 | Transsmission | MW_HW_stuck | Reset IDU | Fawad Khan | 10/25/2025 11:28:46 | 10/26/2025 10:24:44 | 10/25/2025 17:28:46 | 6(2G) 4(3G) 5(LTE) sites down under BHAB0826-P2/BHAB0826-P2 @ Sceco | 10/25/2025 08:29:35 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 08:29:25 | P1 | Repeater | namas | Generator_SG | 2G_3G_LTE SA | THR0181-G9-L8-L18-L21-SBTS-P3-WBB-G3 LTE,BHAB0901-G9-U9-L8-L18-L21-SBTS-P3 LTE,BHAB0826-P2 2G_3G | FLM_TE | BHAB9038 | Hub:BHAB9038 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251025-00000487 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 11:28:46 | 10/25/2025 11:55:16 | 10/25/2025 14:50:03 |  |  | 10/25/2025 14:51:23 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000348 | PCM-20251025-00000758 | TT-20251025-00787 | Telecom | [7 empty] | 10/25/2025 11:30:11 | 10/25/2025 11:30:11 | 10/25/2025 17:30:11 | 2(2G) 2(LTE) sites down under BDR2243-P3-CAP,BDR2244-P3-CAP/R3_MD_HWBSC01 @ Sceco | 10/25/2025 10:55:50 | Major | 21825 | CSL Fault | 10/25/2025 10:55:49 | P3 | SRAN |  | Sceco | 2G_LTE SA | BDR2244-P3-CAP 2G_LTE,BDR2243-P3-CAP 2G_LTE | FLM_EM | BDR2244 | Dear Team, Hub: RUSF9078 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251025-00000711 | Dear Team, Hub: RUSF9078 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: RUSF9078 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/25/2025 11:30:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000352 | PCM-20251025-00000768 | TT-20251025-00843 | Reference_telecom | Region_4 | JED1M7357 | JED0357 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 11:35:58 | 10/25/2025 11:35:58 | 10/25/2025 23:35:58 | BASE STATION SERVICE PROBLEM (RX out of order) at JED1M7357-P2-CA-L900-L800-SBTS @ Sceco | 10/25/2025 11:31:24 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:31:13 | P2 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7357 | FLM_TE | [5 empty] | RX out of order |  |  | API | 10/25/2025 11:35:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000353 | PCM-20251025-00000771 | TT-20251025-00845 | EM | Region_5 | MKTF1M9796 | MKTF0796 |  |  |  | Muhammad Shabbir Muhammad | 10/25/2025 11:37:29 | 10/25/2025 11:37:29 | 10/25/2025 23:37:29 | SHELTER DOOR OPEN at MKTF1M9796-G9-NL8-L21-SBTS-P2-USF @ Generator_SG | 10/25/2025 11:37:03 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 11:36:53 | P3 | 4G | makkah | Generator_SG | LTE NSA | MKTF1M9796 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 11:37:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000354 | PCM-20251025-00000773 | TT-20251025-00846 | EM | Region_4 | ASQ0343 | ASQ0343 |  |  |  | Ibrahim Fawzy Mohamed Elbers | 10/25/2025 11:38:00 | 10/25/2025 11:38:00 | 10/25/2025 17:38:00 | RECTIFIER MAINS POWER FAILURE at ASQ0343-GSM-UMTS-P1-HUB-USF @ Sceco | 10/25/2025 11:29:49 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 11:29:42 | P1 | 2G | adam | Sceco | 2G NSA | ASQ0343 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 11:38:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000356 | PCM-20251025-00000776 | TT-20251025-00842 | EM | Region_5 | MAK0989 | MAK0989 | Equipment | BTS_Cable | Reconnect Fiber Cable | Muhammad Saleem Iqbal | 10/25/2025 11:38:59 | 10/26/2025 07:10:17 | 10/25/2025 17:38:59 | 1(2G/5G) sites down under MAK0989-P3 @ Sceco | 10/25/2025 11:30:51 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 11:30:48 | P3 | 2G | makkah | Sceco | 5G SA | MAK0989-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 | FLM_TE | MAK0989 | Results: DOWN SITE HUB MAK0989-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 MAK0989 Summary: Hub: MAK0989, Down Count: 1, Down Sites: MAK0989-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 Alarm Summary: MAK0989 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.98.176.52:8080] [URL:http://10.98.176.52:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 11:38:59 | 10/26/2025 04:49:18 | 10/26/2025 05:13:17 | 10/26/2025 05:13:24 | 10/26/2025 06:03:28 | 10/26/2025 07:10:17 |  | Muhammad Saleem Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000357 | PCM-20251025-00000777 | TT-20251025-00850 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 11:39:33 | 10/25/2025 15:09:29 | 10/25/2025 23:39:33 | RF Unit CPRI Interface Error at DAM6027-DCU1 @ Sceco | 10/25/2025 11:32:52 | Minor | 26504 | RF Unit CPRI Interface Error | 10/25/2025 11:32:22 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/25/2025 11:39:33 | 10/25/2025 15:09:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000359 | PCM-20251025-00000780 | TT-20251025-00856 | EM | Region_3 | RUSF9004 | RUSF9004 |  |  |  | Muhamad Hanif Ahmad | 10/25/2025 11:41:06 | 10/25/2025 16:23:16 | 10/25/2025 15:41:06 | RELAY_ALARM_MAJOR at RUSF9004_NE_1 @ Sceco | 10/25/2025 11:39:45 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/25/2025 11:39:33 | P3 | Repeater | madinah | Sceco | TX NSA | RUSF9004 | FLM_EM | [8 empty] | API | 10/25/2025 11:41:06 | 10/25/2025 16:23:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000362 | PCM-20251025-00000784 | TT-20251025-00829 | Reference_telecom | Region_2 | RIY2M8796 | RIY2796 | AutoRecovery | Clear_Before_Investigation | Auto Clear | WAQAR AHMED BASHIR AHMED | 10/25/2025 11:44:24 | 10/26/2025 10:43:55 | 10/25/2025 23:44:24 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8796-P2-L900-L800 @ Sceco | 10/25/2025 08:25:58 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 08:25:55 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M8796 | FLM_TE |  |  | PCM-20251025-00000751 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/25/2025 11:44:24 | 10/26/2025 09:59:56 | 10/26/2025 10:01:26 | 10/26/2025 10:01:28 | 10/26/2025 10:43:55 |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000363 | PCM-20251025-00000785 | TT-20251025-00851 | EM | Region_1 | HFF2U6122 | HFF6022 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/25/2025 11:44:59 | 10/26/2025 05:12:10 | 10/25/2025 17:44:59 | 1(2G/3G/LTE) sites down under HFF6022-P3/R1_HF_HWBSC01 @ Sceco | 10/25/2025 11:38:12 | Major | 21825 | CSL Fault | 10/25/2025 11:38:11 | P3 | 2G | hafr | Sceco | 2G_3G_LTE SA | HFF6022-P3 | FLM_EM | HFF6022 | Results: DOWN SITE HUB HFF6022-P3 HFF6022 Summary: Hub: HFF6022, Down Count: 1, Down Sites: HFF6022-P3 Alarm Summary: HFF6022 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 11:44:59 | 10/25/2025 20:48:15 | 10/26/2025 05:12:03 |  |  | 10/26/2025 05:12:10 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000364 | PCM-20251025-00000789 | TT-20251025-00853 | Telecom | Region_2 | RIYA2U6153 | RIYA6053 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/25/2025 11:45:28 | 10/25/2025 11:55:15 | 10/25/2025 17:45:28 | 1(2G) sites down under RIYA6053-P3/R2_RY1_HWBSC01 @ Sceco | 10/25/2025 11:37:20 | Major | 21825 | CSL Fault | 10/25/2025 11:37:17 | P3 | 2G | riyadh | Sceco | 2G SA | RIYA6053-P3 | FLM_TE | RIYA6053 | Results: DOWN SITE HUB RIYA6053-P3 RIYA6053 Summary: Hub: RIYA6053, Down Count: 1, Down Sites: RIYA6053-P3 Alarm Summary: RIYA6053 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 11:45:28 | 10/25/2025 11:55:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000365 | PCM-20251025-00000790 | TT-20251025-00855 | EM | Region_4 | JED2170 | JED2170 | Equipment | BSS_HW_Stuck | Reset System Module | Khaled Mohammad Abdallah | 10/25/2025 11:45:59 | 10/26/2025 02:19:46 | 10/25/2025 17:45:59 | 1(2G/LTE/5G) sites down under JED2170-P3/JED2170-P3 @ Sceco | 10/25/2025 11:37:42 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 11:37:38 | P3 | 2G | jeddah | Sceco | 2G SA | JED2170-P3 | FLM_TE | JED2170 | Results: DOWN SITE HUB JED2170-P3 JED2170 Summary: Hub: JED2170, Down Count: 1, Down Sites: JED2170-P3 Alarm Summary: JED2170 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 11:45:59 |  | 10/26/2025 01:18:57 | 10/26/2025 01:18:59 | 10/26/2025 01:19:01 | 10/26/2025 02:19:46 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000367 | PCM-20251025-00000793 | TT-20251025-00865 | EM | Region_4 | HHR0459 | HHR0459 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/25/2025 11:49:53 | 10/25/2025 11:49:53 | 10/25/2025 17:49:53 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at HHR0459-P1-VIP @ Sceco | 10/25/2025 11:41:43 | Major | 7404 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/25/2025 11:41:40 | VIP | 2G | jeddah | Sceco | 2G NSA | HHR0459 | FLM_EM | [8 empty] | API | 10/25/2025 11:49:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000368 | PCM-20251025-00000795 | TT-20251025-00867 | EM | Region_4 | USF1M7694 | USF0694 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/25/2025 11:51:27 | 10/25/2025 11:51:27 | 10/25/2025 23:51:27 | RECTIFIER MODULE FAILURE at USF1M7694-G9-L8-SBTS-P2-USF @ Sceco | 10/25/2025 11:43:03 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/25/2025 11:42:54 | P3 | 4G | jeddah | Sceco | LTE NSA | USF1M7694 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/25/2025 11:51:27 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000369 | PCM-20251025-00000799 | TT-20251025-00873 | Reference_EM | Region_4 | TF1_CORE | TF1 |  |  |  | Farghal Ashour Hassan Farghal | 10/25/2025 11:55:34 | 10/25/2025 12:26:28 | 10/25/2025 17:55:34 | DOOR OPEN ALARM at TF1_CORE-P1-VIP(Violation of no RFC) | 10/25/2025 11:55:14 | Major | 7103 | DOOR OPEN ALARM | 10/25/2025 11:55:09 | P1 | BSC | taif | Sceco_STB | 2G NSA | TF1_CORE | FLM_EM | [5 empty] | DOOR OPEN ALARM |  |  | API | 10/25/2025 11:55:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000370 | PCM-20251025-00000800 | TT-20251025-00875 | Reference_EM | Region_2 | RIY2138 | RIY2138 |  |  |  | Moin Uddin | 10/25/2025 11:56:05 | 10/25/2025 12:16:22 | 10/25/2025 23:56:05 | Air condition 1 failure alarm at RIY2138-P2_SRAN @ Sceco | 10/25/2025 11:45:51 | Minor | 65104 | Air condition 1 failure alarm | 10/25/2025 11:45:47 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY2138 | FLM_EM | [8 empty] | API | 10/25/2025 11:56:05 | 10/25/2025 12:16:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000372 | PCM-20251025-00000803 | TT-20251025-00878 | Telecom | Region_4 | JED1M8170 | JED2170 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 11:56:37 | 10/25/2025 12:20:30 | 10/25/2025 23:56:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8170-CA-L1800-L800-P3-SBTS @ Sceco | 10/25/2025 11:55:31 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:55:42 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8170 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 11:56:37 | 10/25/2025 12:20:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000373 | PCM-20251025-00000804 | TT-20251025-00879 | EM | Region_5 | MINA_HWBSC01 | HM1 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/25/2025 11:57:07 | 10/25/2025 12:11:34 | 10/25/2025 15:57:07 | LG AC FAULT ALARM EQUIPMENT ROOM at MINA_HWBSC01 @ Sceco_STB | 10/25/2025 11:56:32 | Critical | 65346 | LG AC FAULT ALARM EQUIPMENT ROOM | 10/25/2025 11:56:26 | P1 | BSC | makkah | Sceco_STB | 2G NSA | MINA_HWBSC01 | FLM_EM | [8 empty] | API | 10/25/2025 11:57:07 | 10/25/2025 12:11:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000374 | PCM-20251025-00000805 | TT-20251025-00880 | EM | Region_5 | MINA_HWBSC01 | HM1 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/25/2025 11:57:08 | 10/25/2025 12:11:34 | 10/25/2025 15:57:08 | AIRCONDITION #2 FAULT ALARM EQUIPMENT ROOM at MINA_HWBSC01 @ Sceco_STB | 10/25/2025 11:56:32 | Critical | 65349 | AIRCONDITION #2 FAULT ALARM EQUIPMENT ROOM | 10/25/2025 11:56:26 | P1 | BSC | makkah | Sceco_STB | 2G NSA | MINA_HWBSC01 | FLM_EM | [8 empty] | API | 10/25/2025 11:57:08 | 10/25/2025 12:11:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000375 | PCM-20251025-00000806 | TT-20251025-00881 | Telecom | Region_4 | JED1MN2689 | JED2689 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 11:58:10 | 10/25/2025 11:58:10 | 10/25/2025 23:58:10 | BASE STATION INFORMATION (No module fan detected) at JED1MN2689-NR2.6-P3 @ Sceco | 10/25/2025 11:50:08 | Minor | 7115 | BASE STATION INFORMATION | 10/25/2025 11:49:58 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN2689 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/25/2025 11:58:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000377 | PCM-20251025-00000814 | TT-20251025-00889 | EM | [7 empty] | 10/25/2025 12:00:46 | 10/25/2025 12:00:46 | 10/26/2025 00:00:46 | NETECO: Door Status Sensor Alarm at BDR2111 @ Generator_SG | 10/25/2025 12:00:38 | Minor | 5152 | Door Status Sensor Alarm | 10/25/2025 12:00:38 | P3 | SRAN |  | Generator_SG | 2G NSA | BDR2111 | FLM_EM | [8 empty] | API | 10/25/2025 12:00:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000379 | PCM-20251025-00000815 | TT-20251025-00874 | EM | Region_4 | JED2380 | JED2380 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 12:01:02 | 10/26/2025 10:36:41 | 10/25/2025 18:01:02 | 1(2G/5G) sites down under JED2380-P3/JED2380-P3 @ Sceco | 10/25/2025 11:52:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 11:52:27 | P3 | 2G | jeddah | Sceco | 2G SA | JED2380-P3 | FLM_TE | JED2380 | Results: DOWN SITE HUB JED2380-P3 JED2380 Summary: Hub: JED2380, Down Count: 1, Down Sites: JED2380-P3 Alarm Summary: JED2380 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 12:01:02 | 10/26/2025 10:36:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000383 | PCM-20251025-00000821 | TT-20251025-00897 | EM | Region_5 | HM1 | HM1 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Aly Abdelkarim Abdel Rahman | 10/25/2025 12:03:51 | 10/25/2025 13:26:03 | 10/25/2025 18:03:51 | AIRCONDITION #2 FAULT ALARM EQUIPMENT 2nd ROOM at HM1-ENV Alarm BBU-Core-P1 @ Sceco_STB | 10/25/2025 11:56:30 | Major | 65173 | AIRCONDITION #2 FAULT ALARM EQUIPMENT 2nd ROOM | 10/25/2025 11:56:25 | P1 | BSC | makkah | Sceco_STB | 2G NSA | HM1 | FLM_EM | [8 empty] | API | 10/25/2025 12:03:51 | 10/25/2025 12:11:35 | 10/25/2025 12:12:03 | 10/25/2025 12:16:52 | 10/25/2025 12:30:38 | 10/25/2025 13:26:03 |  | Mohamed Aly Abdelkarim Abdel Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000384 | PCM-20251025-00000822 | TT-20251025-00898 | Reference_EM | Region_1 | DAM0118 | DAM0118 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/25/2025 12:05:24 | 10/25/2025 12:05:24 | 10/26/2025 00:05:24 | Door opening alarm at DAM0118-P3_SRAN @ Sceco | 10/25/2025 12:04:46 | Minor | 65101 | Door opening alarm | 10/25/2025 12:04:43 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM0118 | FLM_EM | [8 empty] | API | 10/25/2025 12:05:24 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000385 | PCM-20251025-00000827 | TT-20251025-00893 | Telecom | Region_4 | MLJI1M3187 | MLJI0187 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/25/2025 12:07:59 | 10/25/2025 18:07:12 | 10/25/2025 18:07:59 | 1(3G) sites down under MLJI0187-P2-USF/MLJI1M3187-P2-USF @ Sceco | 10/25/2025 12:00:13 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/25/2025 11:59:32 | P2 | 3G | alaith | Sceco | 3G SA | MLJI0187-P2-USF | FLM_TE | MLJI0187 | Results: DOWN SITE HUB MLJI0187-P2-USF MLJI0187 Summary: Hub: MLJI0187, Down Count: 1, Down Sites: MLJI0187-P2-USF Alarm Summary: MLJI0187 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 12:07:59 | 10/25/2025 18:07:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000386 | PCM-20251025-00000833 | TT-20251025-00907 | EM | Region_4 | BHMF1M8373 | BHMF2373 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/25/2025 12:09:31 | 10/25/2025 21:15:35 | 10/26/2025 00:09:31 | SHELTER DOOR OPEN at BHMF1M8373-G9-L8-SBTS-P3 @ Generator_SG | 10/25/2025 12:08:54 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 12:08:52 | P3 | 4G | jeddah | Generator_SG | LTE NSA | BHMF1M8373 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 12:09:31 | 10/25/2025 21:15:35 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000387 | PCM-20251025-00000835 | TT-20251025-00909 | Reference_EM | Region_3 | AHT2339 | AHT2339 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 12:10:34 | 10/25/2025 12:10:34 | 10/26/2025 00:10:34 | Door opening alarm at AHT2339-P3-USF_SRAN @ Sceco | 10/25/2025 12:10:27 | Minor | 65101 | Door opening alarm | 10/25/2025 12:10:24 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2339 | FLM_EM | [8 empty] | API | 10/25/2025 12:10:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000388 | PCM-20251025-00000838 | TT-20251025-00903 | EM | Region_5 | MAK0432 | MAK0432 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/25/2025 12:12:29 | 10/25/2025 12:20:01 | 10/25/2025 18:12:29 | 1(2G/5G) sites down under MAK0432-P2/MAK0432-P2 @ Sceco | 10/25/2025 12:04:15 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 12:04:13 | P2 | 2G | makkah | Sceco | 2G SA | MAK0432-P2 | FLM_TE | MAK0432 | Results: DOWN SITE HUB MAK0432-P2 MAK0432 Summary: Hub: MAK0432, Down Count: 1, Down Sites: MAK0432-P2 Alarm Summary: MAK0432 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 12:12:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000389 | PCM-20251025-00000839 | TT-20251025-00912 | Telecom | Region_4 | JED1M8039 | JED2039 | Equipment | SFP_BTS | Re-Plug SFP | Mohammed Ramadan A Abu Abid | 10/25/2025 12:12:37 | 10/25/2025 21:04:35 | 10/25/2025 18:12:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8039-CA-L900-L800-SBTS @ Sceco | 10/25/2025 12:12:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 12:11:50 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8039 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 12:12:37 | 10/25/2025 12:43:17 | 10/25/2025 13:17:02 | 10/25/2025 13:17:06 | 10/25/2025 13:17:08 | 10/25/2025 21:04:35 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000391 | PCM-20251025-00000844 | TT-20251025-00882 | Reference_telecom | Region_2 | RIYC2U6721 | RIYC6021 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/25/2025 12:16:24 | 10/25/2025 19:14:44 | 10/26/2025 00:16:24 | Cell RX Channel Interference Noise Power Unbalanced at RIYC2U6721-L800-CA-P3 @ Sceco | 10/25/2025 08:58:36 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 08:58:34 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYC2U6721 | FLM_TE |  |  | PCM-20251025-00000808 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/25/2025 12:16:24 | 10/25/2025 19:14:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000394 | PCM-20251025-00000847 | TT-20251025-00799 | Reference_telecom | Region_3 | MDHL2M5384 | MDHL0384 |  |  |  | Mohamed Naveed | 10/25/2025 12:18:05 | 10/25/2025 12:30:43 | 10/26/2025 00:18:05 | External Clock Reference Problem at MDHL2M5384-P3 @ Sceco | 10/25/2025 08:05:59 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 08:05:32 | P3 | 2G | hail | Sceco | 2G NSA | MDHL2M5384 | FLM_TE |  |  | PCM-20251025-00000720 | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/25/2025 12:18:05 | 10/25/2025 12:30:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000395 | PCM-20251025-00000848 | TT-20251025-00785 | Reference_telecom | Region_3 | MDHL2M5379 | MDHL0379 |  |  |  | Mohamed Naveed | 10/25/2025 12:18:17 | 10/25/2025 12:30:43 | 10/26/2025 00:18:17 | External Clock Reference Problem at MDHL2M5379-P1-HUB @ Sceco_STB | 10/25/2025 07:59:23 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 07:55:58 | P1 | 2G | hail | Sceco_STB | 2G NSA | MDHL2M5379 | FLM_TE |  |  | PCM-20251025-00000704 | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/25/2025 12:18:17 | 10/25/2025 12:30:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000397 | PCM-20251025-00000852 | TT-20251025-00791 | Reference_telecom | Region_3 | MDHL2M5380 | MDHL0380 |  |  |  | Mohamed Naveed | 10/25/2025 12:18:46 | 10/25/2025 12:30:44 | 10/26/2025 00:18:46 | External Clock Reference Problem at MDHL2M5380-P1-HUB @ Sceco_STB | 10/25/2025 08:03:11 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 08:00:49 | P1 | 2G | hail | Sceco_STB | 2G NSA | MDHL2M5380 | FLM_TE |  |  | PCM-20251025-00000709 | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/25/2025 12:18:46 | 10/25/2025 12:30:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000398 | PCM-20251025-00000855 | TT-20251025-00946 | Telecom | Region_3 | MDN2929 | MDN2929 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Hamayo Din Jalal | 10/25/2025 12:22:26 | 10/25/2025 14:49:52 | 10/25/2025 18:22:26 | BBU CPRI Interface Error at MDN2929-P2_SRAN @ Sceco | 10/25/2025 12:19:22 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 12:16:49 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2929 | FLM_TE | [8 empty] | API | 10/25/2025 12:22:26 | 10/25/2025 14:13:57 | 10/25/2025 14:20:34 | 10/25/2025 14:20:42 | 10/25/2025 14:20:48 | 10/25/2025 14:49:52 |  | Hamayo Din Jalal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000399 | PCM-20251025-00000856 | TT-20251025-00949 | EM | Region_6 | BLQ1M8192 | BLQ2192 |  |  |  | Muhammad Naeem Taj Din | 10/25/2025 12:22:58 | 10/26/2025 03:03:07 | 10/26/2025 00:22:58 | SHELTER DOOR OPEN at BLQ1M8192-G9-L8- L18- L21-SBTS-P3 @ Generator_SG | 10/25/2025 12:22:36 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 12:22:32 | P3 | 4G | namas | Generator_SG | LTE NSA | BLQ1M8192 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 12:22:58 | 10/26/2025 03:03:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000400 | PCM-20251025-00000860 | TT-20251025-00953 | EM | Region_4 | HBI1M8412 | HBI2412 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/25/2025 12:23:59 | 10/25/2025 12:23:59 | 10/26/2025 00:23:59 | RECTIFIER MODULE FAILURE at HBI1M8412-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/25/2025 12:15:46 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/25/2025 12:15:40 | P3 | 4G | jeddah | Generator_DG | LTE NSA | HBI1M8412 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/25/2025 12:23:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000401 | PCM-20251025-00000862 | TT-20251025-00960 | EM | Region_5 | MAK1M9611 | MAK0611 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 12:27:06 | 10/25/2025 12:27:06 | 10/26/2025 00:27:06 | SHELTER DOOR OPEN at MAK1M9611-P2-CA-L800 @ Sceco | 10/25/2025 12:26:51 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 12:26:38 | P2 | 4G | makkah | Sceco | LTE NSA | MAK1M9611 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 12:27:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000402 | PCM-20251025-00000865 | TT-20251025-00965 | Reference_EM | Region_1 | JBKH0110 | JBKH0110 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/25/2025 12:29:09 | 10/26/2025 10:24:37 | 10/25/2025 18:29:09 | high temprature 32 at JBKH0110-P1-HUB_SRAN @ Generator_SG | 10/25/2025 12:18:53 | Major | 65102 | high temprature 32 | 10/25/2025 12:18:49 | P1 | SRAN | jubail | Generator_SG | 2G NSA | JBKH0110 | FLM_EM | [8 empty] | API | 10/25/2025 12:29:09 | 10/26/2025 10:24:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000404 | PCM-20251025-00000871 | TT-20251025-00958 | Telecom | Region_4 | JED2886 | JED2886 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 12:31:29 | 10/26/2025 10:36:42 | 10/25/2025 18:31:29 | 1(2G) sites down under JED2886-P3/JED2886-P3 @ Generator_SG | 10/25/2025 12:23:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 12:23:08 | P3 | 2G | jeddah | Generator_SG | 2G SA | JED2886-P3 | FLM_TE | JED2886 | Results: DOWN SITE HUB JED2886-P3 JED2886 Summary: Hub: JED2886, Down Count: 1, Down Sites: JED2886-P3 Alarm Summary: JED2886 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 12:31:29 | 10/26/2025 10:36:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000405 | PCM-20251025-00000876 | TT-20251025-00973 | Telecom | Region_3 | MDN2903 | MDN2903 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/25/2025 12:34:20 | 10/25/2025 13:27:29 | 10/26/2025 00:34:20 | ALD Maintenance Link Failure at MDN2903-P2_SRAN @ Sceco | 10/25/2025 12:31:41 | Minor | 26541 | ALD Maintenance Link Failure | 10/25/2025 12:30:06 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2903 | FLM_TE | [8 empty] | API | 10/25/2025 12:34:20 | 10/25/2025 13:27:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000407 | PCM-20251025-00000883 | TT-20251025-00980 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/25/2025 12:37:57 | 10/25/2025 12:37:57 | 10/26/2025 00:37:57 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/25/2025 12:29:53 | Minor | 7103 | AIRCON 1 FAILURE | 10/25/2025 12:29:47 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/25/2025 12:37:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000408 | PCM-20251025-00000884 | TT-20251025-00981 | EM | Region_6 | BHAB1M8103 | BHAB2103 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 12:38:27 | 10/25/2025 12:51:12 | 10/26/2025 00:38:27 | AIRCON 1 FAILURE at BHAB1M8103-G9-L8-L18-P3-SBTS @ Generator_DG | 10/25/2025 12:30:16 | Minor | 7103 | AIRCON 1 FAILURE | 10/25/2025 12:30:08 | P3 | 4G | Baha | Generator_DG | LTE NSA | BHAB1M8103 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/25/2025 12:38:27 | 10/25/2025 12:51:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000409 | PCM-20251025-00000886 | TT-20251025-00982 | Reference_EM | Region_3 | RSP0039 | RSP0039 | Enviroment | SCECO_Failure | SCECO auto restored | Sayed Satoor | 10/25/2025 12:38:59 | 10/25/2025 16:50:12 | 10/25/2025 18:38:59 | Door opening alarm at RSP0039-P1-ARP-VVIP_SRAN @ Sceco | 10/25/2025 12:38:47 | Major | 65101 | Door opening alarm | 10/25/2025 12:38:44 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0039 | FLM_EM | [8 empty] | API | 10/25/2025 12:38:59 | 10/25/2025 14:53:23 | 10/25/2025 16:49:58 |  |  | 10/25/2025 16:50:12 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000410 | PCM-20251025-00000887 | TT-20251025-00983 | Reference_telecom | Region_4 | JED0177 | JED0177 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/25/2025 12:40:00 | 10/26/2025 09:44:51 | 10/26/2025 00:40:00 | BASE STATION SERVICE PROBLEM (TX out of order) at JED0177-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 12:35:25 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 12:35:12 | P2 | 2G | jeddah | Sceco | LTE_Cell SA | JED0177 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/25/2025 12:40:00 | 10/26/2025 09:38:55 | 10/26/2025 09:44:46 | 10/26/2025 09:44:48 | 10/26/2025 09:44:51 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000411 | PCM-20251025-00000888 | TT-20251025-00967 | Telecom | Region_2 | RIY2M8965 | RIY2965 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Khan zeb Shah nawaz | 10/25/2025 12:40:25 | 10/25/2025 12:54:24 | 10/26/2025 00:40:25 | Cell Capability Degraded at RIY2M8965-L800-L1800-CA-P3 @ Generator_SG | 10/25/2025 12:25:01 | Minor | 29243 | Cell Capability Degraded | 10/25/2025 12:23:27 | P3 | 4G | riyadh | Generator_SG | 2G NSA | RIY2M8965 | FLM_TE |  |  | PCM-20251025-00000868 | check h.w alarm | check h.w alarm |  |  |  | API | 10/25/2025 12:40:25 | 10/25/2025 12:50:22 | 10/25/2025 12:54:00 |  |  | 10/25/2025 12:54:24 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000412 | PCM-20251025-00000892 | TT-20251025-00987 | Telecom | Region_6 | JEC1M7377 | JEC0377 | Equipment | BSS_HW_fault | Replace Interface Card | Ansir Iqbal Muhammad Iqbal | 10/25/2025 12:41:34 | 10/25/2025 17:19:57 | 10/25/2025 18:41:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at JEC1M7377-VIP-P3-CA-L800 @ Generator_SG | 10/25/2025 12:40:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 12:40:26 | VIP | 4G | baish | Generator_SG | 5G_Cell SA | JEC1M7377 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 12:41:34 | 10/25/2025 14:11:08 | 10/25/2025 15:20:48 | 10/25/2025 15:25:32 |  | 10/25/2025 17:19:57 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000417 | PCM-20251025-00000898 | TT-20251025-00994 | EM | Region_4 | RYMK1M7544 | RYMK0544 |  |  |  | Farghal Ashour Hassan Farghal | 10/25/2025 12:44:39 | 10/25/2025 12:44:39 | 10/26/2025 00:44:39 | HIGH TEMPERATURE 32 DEGREE C at RYMK1M7544-L800-P2-USF @ Sceco | 10/25/2025 12:36:23 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/25/2025 12:36:14 | P2 | 4G | taif | Sceco | LTE NSA | RYMK1M7544 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/25/2025 12:44:39 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000418 | PCM-20251025-00000899 | TT-20251025-00995 | Telecom | Region_6 | JEC1M7331 | JEC0331 | Equipment | SFP_BTS | Replace SFP | Ansir Iqbal Muhammad Iqbal | 10/25/2025 12:45:10 | 10/25/2025 15:20:15 | 10/25/2025 16:45:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JEC1M7331-CA-P1-L800-VIP @ Generator_SG | 10/25/2025 12:44:23 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 12:44:10 | VIP | 4G | baish | Generator_SG | 5G_Cell SA | JEC1M7331 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 12:45:10 | 10/25/2025 14:11:09 | 10/25/2025 15:19:59 |  |  | 10/25/2025 15:20:15 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000421 | PCM-20251025-00000903 | TT-20251025-00998 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/25/2025 12:47:14 | 10/26/2025 10:11:51 | 10/25/2025 16:47:14 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/25/2025 12:46:59 | Critical | 65334 | Door open Alarm Equipment room | 10/25/2025 12:46:54 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/25/2025 12:47:14 | 10/26/2025 10:11:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000422 | PCM-20251025-00000905 | TT-20251025-01000 | Telecom | Region_4 | JZMA1M7824 | JZMA0824 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/25/2025 12:47:45 | 10/25/2025 14:50:00 | 10/26/2025 00:47:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at JZMA1M7824-G9-L8-SBTS-P3 @ Sceco | 10/25/2025 12:47:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 12:45:36 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JZMA1M7824 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 12:47:45 | 10/25/2025 14:50:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000423 | PCM-20251025-00000908 | TT-20251025-00993 | EM | Region_4 | JDAP0940 | JDAP0940 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 12:49:29 | 10/25/2025 13:51:01 | 10/25/2025 16:49:29 | 1(2G/LTE) sites down under JDAP0940-P1-VIP-ARP/JDAP0940-P1-VIP-ARP @ Sceco | 10/25/2025 12:41:09 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 12:41:05 | VIP | 2G | jeddah | Sceco | 2G SA | JDAP0940-P1-VIP-ARP | FLM_TE | [6 empty] | sites down |  | API | 10/25/2025 12:49:29 | 10/25/2025 13:02:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000424 | PCM-20251025-00000909 | TT-20251025-01001 | Reference_EM | Region_3 | MDN2358 | MDN2358 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/25/2025 12:49:49 | 10/25/2025 12:49:49 | 10/26/2025 00:49:49 | Mains Failure at MDN2358-P3_SRAN @ Sceco | 10/25/2025 12:40:08 | Minor | 65109 | Mains Failure | 10/25/2025 12:40:04 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2358 | FLM_EM | [8 empty] | API | 10/25/2025 12:49:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000425 | PCM-20251025-00000910 | TT-20251025-01003 | EM | Region_4 | JDAP1M7940 | JDAP0940 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/25/2025 12:51:22 | 10/25/2025 12:51:22 | 10/25/2025 18:51:22 | RECTIFIER MODULE FAILURE at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/25/2025 12:46:06 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/25/2025 12:43:10 | VIP | 4G | jeddah | Sceco | LTE NSA | JDAP1M7940 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/25/2025 12:51:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000426 | PCM-20251025-00000911 | TT-20251025-00999 | EM | Region_6 | JEC0377 | JEC0377 |  |  |  | Fizan Ahmed | 10/25/2025 12:52:29 | 10/25/2025 12:52:29 | 10/25/2025 16:52:29 | 1(2G/3G/LTE/5G) sites down under JEC0377-P1-VIP/JEC0377-P1-VIP @ Generator_SG | 10/25/2025 12:44:38 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 12:44:34 | VIP | 2G | baish | Generator_SG | 2G_3G_LTE_5G SA | JEC0377-P1-VIP | FLM_EM | JEC0377 | Results: DOWN SITE HUB JEC0377-P1-VIP JEC0377 Summary: Hub: JEC0377, Down Count: 1, Down Sites: JEC0377-P1-VIP Alarm Summary: JEC0377 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 12:52:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000429 | PCM-20251025-00000916 | TT-20251025-01002 | Telecom | Region_4 | HAW2423 | HAW2423 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 12:55:59 | 10/25/2025 21:45:58 | 10/25/2025 18:55:59 | 1(5G) sites down under HAW2423-GSM-P3 @ Sceco | 10/25/2025 12:47:40 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 12:47:38 | P3 | 2G | taif | Sceco | 5G SA | HAW2423-GSM-P3 | FLM_TE | HAW2423 | Results: DOWN SITE HUB HAW2423-GSM-P3 HAW2423 Summary: Hub: HAW2423, Down Count: 1, Down Sites: HAW2423-GSM-P3 Alarm Summary: HAW2423 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-4388459 [ACTIVE] [URL:http://10.98.74.228:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 12:55:59 | 10/25/2025 21:45:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000430 | PCM-20251025-00000917 | TT-20251025-01012 | Telecom | Region_6 | BHAB9035 | BHAB9035 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Fawad Khan | 10/25/2025 12:57:34 | 10/25/2025 18:40:32 | 10/26/2025 00:57:34 | ODU CPU / Cable Open at BHAB9035-BLH0118 on 10.154.163.165 @ Sceco_STB | 10/25/2025 12:56:50 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/25/2025 12:43:14 | P1 | Repeater | namas | Sceco_STB | TX NSA | BHAB9035 | FLM_TE | [8 empty] | API | 10/25/2025 12:57:34 | 10/25/2025 14:51:41 | 10/25/2025 18:40:08 |  |  | 10/25/2025 18:40:32 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000432 | PCM-20251025-00000920 | TT-20251025-01006 | EM | [7 empty] | 10/25/2025 12:58:25 | 10/25/2025 12:58:25 | 10/26/2025 00:58:25 | NETECO: Under Fuel Level at BDR2111 @ Generator_SG | 10/25/2025 12:47:04 | Minor | 301 | Under Fuel Level | 10/25/2025 12:47:04 | P3 | SRAN |  | Generator_SG | 2G NSA | BDR2111 | FLM_EM | BDR2111 | Results: DOWN SITE HUB BDR2111 BDR2111 Summary: Hub: BDR2111, Down Count: 1, Down Sites: BDR2111 Alarm Summary: BDR2111 No Active Alarm on HUB | [6 empty] | API | 10/25/2025 12:58:25 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000433 | PCM-20251025-00000922 | TT-20251025-01017 | Telecom | Region_2 | UMA0561 | UMA0561 | Equipment | BTS_Cable | Re-Tightened Outdoor Feeder cable Connector | Waseem Shahzad Ghulam Rasool | 10/25/2025 12:59:58 | 10/25/2025 17:01:59 | 10/26/2025 00:59:58 | HC::: FLM need to do HC under UMA0561 | 10/25/2025 12:53:12 | Minor | 676767672 | Health Check-WO to TE FME | 10/25/2025 12:53:13 | P2 | SRAN | riyadh | Sceco | 2G_3G_LTE_5G NSA | UMA0561 | FLM_TE | [8 empty] | API | 10/25/2025 12:59:58 | 10/25/2025 13:45:46 | 10/25/2025 15:34:47 | 10/25/2025 15:35:03 | 10/25/2025 15:35:07 | 10/25/2025 17:01:59 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000437 | PCM-20251025-00000930 | TT-20251025-01022 | EM | Region_4 | TURY0685 | TURY0685 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/25/2025 13:04:17 | 10/25/2025 16:46:15 | 10/25/2025 19:04:17 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at TURY0685-GSM-P1-HUB @ Sceco | 10/25/2025 12:56:20 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/25/2025 12:56:09 | P1 | 2G | taif | Sceco | 2G NSA | TURY0685 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/25/2025 13:04:17 | 10/25/2025 16:46:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000438 | PCM-20251025-00000932 | TT-20251025-01025 | Reference_EM | Region_2 | RIY2936 | RIY2936 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/25/2025 13:04:17 | 10/25/2025 14:50:30 | 10/26/2025 01:04:17 | Door opening alarm at RIY2936-P3_SRAN @ Sceco | 10/25/2025 13:03:53 | Minor | 65101 | Door opening alarm | 10/25/2025 13:03:48 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2936 | FLM_EM | [8 empty] | API | 10/25/2025 13:04:17 | 10/25/2025 14:50:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000439 | PCM-20251025-00000933 | TT-20251025-01024 | Reference_EM | Region_3 | YNB2M1672 | YNB0672 |  |  |  | Muhammad Imran Muhammad Aslam | 10/25/2025 13:04:17 | 10/25/2025 13:38:00 | 10/26/2025 01:04:17 | High temperature 32? alarm at YNB2M1672-P3 @ Sceco | 10/25/2025 12:54:11 | Minor | 65102 | High temperature 32? alarm | 10/25/2025 12:54:09 | P3 | 2G | yanbu | Sceco | 2G NSA | YNB2M1672 | FLM_EM | [8 empty] | API | 10/25/2025 13:04:17 | 10/25/2025 13:38:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000441 | PCM-20251025-00000935 | TT-20251025-01029 | EM | Region_6 | JEC0377 | JEC0377 |  |  |  | Fizan Ahmed | 10/25/2025 13:05:18 | 10/25/2025 13:05:18 | 10/25/2025 19:05:18 | SHELTER DOOR OPEN;Default System Time at JEC0377-GSM-P1-VIP @ Generator_SG | 10/25/2025 13:04:43 | Major | 7103 | SHELTER DOOR OPEN;Default System Time | 10/25/2025 03:01:18 | VIP | 2G | baish | Generator_SG | 2G NSA | JEC0377 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/25/2025 13:05:18 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000442 | PCM-20251025-00000936 | TT-20251025-01030 | Reference_EM | Region_1 | HFBD2M5009 | HFBD0009 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/25/2025 13:05:18 | 10/25/2025 13:05:18 | 10/25/2025 19:05:18 | Door opening alarm at HFBD2M5009-P1-HUB @ Generator_SG | 10/25/2025 13:05:03 | Major | 65101 | Door opening alarm | 10/25/2025 13:05:00 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5009 | FLM_EM | [8 empty] | API | 10/25/2025 13:05:18 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000444 | PCM-20251025-00000938 | TT-20251025-01032 | Reference_EM | Region_3 | HLHD0714 | HLHD0714 |  |  |  | Mohamed Hafez Fahim Abdelaziz | 10/25/2025 13:06:51 | 10/25/2025 13:06:51 | 10/26/2025 01:06:51 | NETECO: AC Failure at HLHD0714 @ Sceco | 10/25/2025 13:00:40 | Minor | 10202 | AC Failure | 10/25/2025 13:00:40 | P3 | SRAN | hail | Sceco | 2G NSA | HLHD0714 | FLM_EM | [8 empty] | API | 10/25/2025 13:06:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000448 | PCM-20251025-00000943 | TT-20251025-01036 | Reference_EM | Region_3 | HLHD0714 | HLHD0714 |  |  |  | Mohamed Hafez Fahim Abdelaziz | 10/25/2025 13:10:28 | 10/25/2025 13:10:28 | 10/26/2025 01:10:28 | Mains Failure at HLHD0714-P3_SRAN @ Sceco | 10/25/2025 13:00:44 | Minor | 65109 | Mains Failure | 10/25/2025 13:00:40 | P3 | SRAN | hail | Sceco | 2G NSA | HLHD0714 | FLM_EM | [8 empty] | API | 10/25/2025 13:10:28 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000449 | PCM-20251025-00000944 | TT-20251025-01037 | Reference_EM | Region_3 | HAL2M1947 | HAL0947 |  |  |  | Mohamed Hafez Fahim Abdelaziz | 10/25/2025 13:10:29 | 10/25/2025 13:10:29 | 10/25/2025 19:10:29 | Mains Failure at HAL2M1947-P1-HUB @ Sceco | 10/25/2025 13:00:49 | Major | 65109 | Mains Failure | 10/25/2025 13:00:44 | P1 | 2G | hail | Sceco | 2G NSA | HAL2M1947 | FLM_EM | [8 empty] | API | 10/25/2025 13:10:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000450 | PCM-20251025-00000945 | TT-20251025-01038 | Telecom | Region_1 | DAM6001 | DAM6001 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 13:11:31 | 10/25/2025 15:09:29 | 10/26/2025 01:11:31 | ALC Controlling Threshold Crossing (Minor) at DAM6001-DCU2 @ Sceco | 10/25/2025 13:05:44 | Minor | 29804 | ALC Controlling Threshold Crossing (Minor) | 10/25/2025 13:07:01 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6001 | FLM_TE | [8 empty] | API | 10/25/2025 13:11:31 | 10/25/2025 15:09:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000452 | PCM-20251025-00000948 | TT-20251025-01034 | EM | Region_2 | ZLH2M1217 | ZLH0217 |  |  |  | Mohamed Moustafa Aboelmagd Hefny | 10/25/2025 13:13:29 | 10/25/2025 14:04:59 | 10/25/2025 19:13:29 | 1(2G/3G/LTE) sites down under ZLH0217-P3/RY1BSCH02 @ Sceco | 10/25/2025 13:06:30 | Major | 21825 | CSL Fault | 10/25/2025 13:06:29 | P3 | 2G | majma | Sceco | 2G_3G_LTE SA | ZLH0217-P3 | FLM_EM | ZLH0217 | Results: DOWN SITE HUB ZLH0217-P3 ZLH0217 Summary: Hub: ZLH0217, Down Count: 1, Down Sites: ZLH0217-P3 Alarm Summary: ZLH0217 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 13:13:29 | 10/25/2025 14:04:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000454 | PCM-20251025-00000959 | TT-20251025-01048 | Telecom | Region_3 | RSP2M7814 | RSP0814 |  |  |  | Hossam Ali Ahmed Ali | 10/25/2025 13:17:24 | 10/25/2025 19:33:20 | 10/25/2025 19:17:24 | Cell Unavailable at RSP2M7814-CA-L800-P3 @ Generator_SG | 10/25/2025 13:12:58 | Major | 29240 | Cell Unavailable | 10/25/2025 13:11:24 | P3 | 4G | Deba | Generator_SG | LTE SA | RSP2M7814 | FLM_TE | [8 empty] | API | 10/25/2025 13:17:24 | 10/25/2025 19:33:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000456 | PCM-20251025-00000961 | TT-20251025-01050 | Reference_EM | Region_3 | AHT2153 | AHT2153 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 13:17:42 | 10/25/2025 13:17:42 | 10/26/2025 01:17:42 | Mains Failure at AHT2153-P3_SRAN @ Sceco | 10/25/2025 13:07:48 | Minor | 65109 | Mains Failure | 10/25/2025 13:07:45 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2153 | FLM_EM | [8 empty] | API | 10/25/2025 13:17:42 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000457 | PCM-20251025-00000962 | TT-20251025-01051 | Reference_telecom | Region_3 | MDYB0462 | MDYB0462 |  |  |  | Muhammad Sajjad R3 | 10/25/2025 13:17:43 | 10/25/2025 14:49:39 | 10/26/2025 01:17:43 | HARD_BAD at MDYB0462_NE_1 @ Sceco_STB | 10/25/2025 12:17:19 | Minor | 1-236 | HARD_BAD | 10/25/2025 12:17:10 | P1 | SRAN | madinah | Sceco_STB | TX NSA | MDYB0462 | FLM_TE | [8 empty] | API | 10/25/2025 13:17:43 | 10/25/2025 14:49:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000458 | PCM-20251025-00000967 | TT-20251025-01053 | Reference_EM | Region_3 | MDN2348 | MDN2348 |  |  |  | Zarshad Ali Hassan Gul | 10/25/2025 13:18:13 | 10/25/2025 23:09:20 | 10/26/2025 01:18:13 | Mains Failure at MDN2348-P3_SRAN @ Generator_SG | 10/25/2025 13:08:17 | Minor | 65109 | Mains Failure | 10/25/2025 13:08:13 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDN2348 | FLM_EM | [8 empty] | API | 10/25/2025 13:18:13 | 10/25/2025 23:09:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000459 | PCM-20251025-00000968 | TT-20251025-01054 | Telecom | Region_4 | JED1M8602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 13:18:14 | 10/25/2025 13:18:14 | 10/25/2025 19:18:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8602-CA-L800-P3 @ Sceco | 10/25/2025 13:17:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 13:17:09 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8602 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 13:18:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000460 | PCM-20251025-00000969 | TT-20251025-01055 | Reference_EM | Region_1 | HFBD2M5009 | HFBD0009 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/25/2025 13:18:44 | 10/25/2025 13:18:44 | 10/25/2025 19:18:44 | Mains Failure at HFBD2M5009-P1-HUB @ Generator_SG | 10/25/2025 13:08:40 | Major | 65109 | Mains Failure | 10/25/2025 13:08:37 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5009 | FLM_EM | [8 empty] | API | 10/25/2025 13:18:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000462 | PCM-20251025-00000979 | TT-20251025-01078 | EM | Region_6 | BHAB1M8940 | BHAB2940 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 13:26:30 | 10/25/2025 13:52:44 | 10/26/2025 01:26:30 | COMMERCIAL POWER FAILURE at BHAB1M8940-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/25/2025 13:18:11 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/25/2025 13:18:05 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8940 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/25/2025 13:26:30 | 10/25/2025 13:52:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000463 | PCM-20251025-00000981 | TT-20251025-01081 | Reference_EM | Region_3 | AHT2153 | AHT2153 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 13:28:03 | 10/25/2025 13:28:03 | 10/26/2025 01:28:03 | Door opening alarm at AHT2153-P3_SRAN @ Sceco | 10/25/2025 13:27:26 | Minor | 65101 | Door opening alarm | 10/25/2025 13:27:23 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2153 | FLM_EM | [8 empty] | API | 10/25/2025 13:28:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000464 | PCM-20251025-00000983 | TT-20251025-01083 | Telecom | Region_5 | MAK0992 | MAK0992 |  |  |  | Atif Javed Javed Hussain | 10/25/2025 13:28:04 | 10/25/2025 13:28:04 | 10/25/2025 19:28:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0992-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM @ Sceco | 10/25/2025 13:27:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 13:27:12 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0992 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 13:28:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000465 | PCM-20251025-00000985 | TT-20251025-01072 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/25/2025 13:28:32 | 10/25/2025 17:37:00 | 10/25/2025 19:28:32 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/25/2025 13:20:04 | Major | 22214 | NodeB Unavailable | 10/25/2025 13:20:01 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 13:28:32 | 10/25/2025 17:37:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000467 | PCM-20251025-00000994 | TT-20251025-01090 | Reference_EM | Region_1 | JBL0478 | JBL0478 | Enviroment | Genset failure_High Temperature | Change Generator radiator | Ahmed Hassan Ahmed Hassanin | 10/25/2025 13:31:39 | 10/25/2025 15:13:53 | 10/26/2025 01:31:39 | Mains Failure at JBL0478-P2_SRAN @ Generator_SG | 10/25/2025 13:26:00 | Minor | 65109 | Mains Failure | 10/25/2025 13:21:56 | P2 | SRAN | jubail | Generator_SG | 2G NSA | JBL0478 | FLM_EM | [8 empty] | API | 10/25/2025 13:31:39 | 10/25/2025 15:13:19 | 10/25/2025 15:13:46 |  |  | 10/25/2025 15:13:53 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000469 | PCM-20251025-00000998 | TT-20251025-01092 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 13:32:10 | 10/26/2025 09:20:14 | 10/25/2025 19:32:10 | high temprature 32 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/25/2025 13:21:46 | Major | 65102 | high temprature 32 | 10/25/2025 13:21:43 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/25/2025 13:32:10 | 10/26/2025 09:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000470 | PCM-20251025-00001003 | TT-20251025-01096 | EM | Region_6 | TLT0722 | TLT0722 |  |  |  | Muhammad Gomaa | 10/25/2025 13:33:43 | 10/25/2025 17:12:31 | 10/26/2025 01:33:43 | SHELTER DOOR OPEN at TLT0722-GSM-P3 @ Sceco | 10/25/2025 13:33:12 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 13:33:08 | P3 | 2G | tathleeth | Sceco | 2G NSA | TLT0722 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 13:33:43 | 10/25/2025 17:12:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000471 | PCM-20251025-00001007 | TT-20251025-01088 | Telecom | Region_4 | JED0024 | JED0024 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 13:35:36 | 10/26/2025 10:36:42 | 10/25/2025 17:35:36 | 1(2G) sites down under JED0024-P1-DIA/JED0024-P1-DIA @ Sceco | 10/25/2025 13:27:33 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 13:27:30 | P1 | 2G | jeddah | Sceco | 2G SA | JED0024-P1-DIA | FLM_TE | JED0024 | Results: DOWN SITE HUB JED0024-P1-DIA JED0024 Summary: Hub: JED0024, Down Count: 1, Down Sites: JED0024-P1-DIA Alarm Summary: JED0024 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 13:35:36 | 10/26/2025 10:36:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000472 | PCM-20251025-00001008 | TT-20251025-01103 | Telecom | Region_1 | JBL2394 | JBL2394 | Equipment | BSS_HW_fault | Replace RRU | Rafiq Ahmed Elturifi | 10/25/2025 13:35:39 | 10/26/2025 09:56:19 | 10/25/2025 19:35:39 | Local Cell Unusable at JBL2394-P2_SRAN @ Sceco | 10/25/2025 13:33:43 | Major | 28203 | Local Cell Unusable | 10/25/2025 13:32:20 | P2 | SRAN | jubail | Sceco | 3G SA | JBL2394 | FLM_TE | [8 empty] | API | 10/25/2025 13:35:39 | 10/26/2025 09:36:25 | 10/26/2025 09:37:39 |  |  | 10/26/2025 09:56:19 |  | Rafiq Ahmed Elturifi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000474 | PCM-20251025-00001015 | TT-20251025-01108 | Reference_EM | Region_3 | RSP0091 | RSP0091 |  |  |  | Sayed Satoor | 10/25/2025 13:38:23 | 10/25/2025 14:53:24 | 10/25/2025 19:38:23 | high temprature 40 at RSP0091-P1-VIP_SRAN @ Generator_SG | 10/25/2025 13:28:23 | Major | 65103 | high temprature 40 | 10/25/2025 13:28:19 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0091 | FLM_EM | [8 empty] | API | 10/25/2025 13:38:23 | 10/25/2025 14:53:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000475 | PCM-20251025-00001017 | TT-20251025-01109 | EM | Region_6 | DRB1M7953 | DRB0953 |  |  |  | Aziz Ul Haq Umar Gul | 10/25/2025 13:39:55 | 10/25/2025 21:26:26 | 10/26/2025 01:39:55 | SHELTER DOOR OPEN;Default System Time at DRB1M7953-NCA-L800 @ Sceco | 10/25/2025 13:39:47 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/25/2025 03:01:31 | P3 | 4G | derb | Sceco | LTE NSA | DRB1M7953 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/25/2025 13:39:55 | 10/25/2025 21:26:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000478 | PCM-20251025-00001022 | TT-20251025-01102 | EM | Region_3 | RSP2M1814 | RSP0814 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Sayed Satoor | 10/25/2025 13:40:31 | 10/25/2025 16:48:03 | 10/25/2025 19:40:31 | 1(2G/LTE) sites down under RSP0814-P3/YB1MBSCH01 @ Generator_SG | 10/25/2025 13:32:27 | Major | 21825 | CSL Fault | 10/25/2025 13:32:25 | P1 | 2G | Deba | Generator_SG | 2G_LTE SA | RSP0814-P3 | FLM_EM | RSP0814 | Results: DOWN SITE HUB RSP0814-P3 RSP0814 Summary: Hub: RSP0814, Down Count: 1, Down Sites: RSP0814-P3 Alarm Summary: RSP0814 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 13:40:31 | 10/25/2025 14:53:24 | 10/25/2025 16:47:50 |  |  | 10/25/2025 16:48:03 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000479 | PCM-20251025-00001023 | TT-20251025-01095 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 13:40:57 | 10/25/2025 14:51:53 | 10/25/2025 19:40:57 | 2(2G) 2(LTE) sites down under BHAB2091-P3,BHAB2103-P3/BHAB2103-P3 @ Generator_DG | 10/25/2025 13:30:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 13:29:56 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2103-P3 2G_LTE,BHAB2091-P3 2G_LTE | FLM_EM | BHAB2091 | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251025-00001014 | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/25/2025 13:40:57 | 10/25/2025 14:51:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000481 | PCM-20251025-00001026 | TT-20251025-01113 | Telecom | Region_4 | JED1-PE-01 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/25/2025 13:42:00 | 10/25/2025 13:42:00 | 10/26/2025 01:42:00 | Bad Package Error Rising at JED1-PE-01 @ Sceco_STB | 10/25/2025 13:41:34 | Minor | 101-2501403 | Bad Package Error Rising | 10/25/2025 13:41:25 | P1 | IPBB | jeddah | Sceco_STB | IPRAN NSA | JED1-PE-01 | FLM_TE | [8 empty] | API | 10/25/2025 13:42:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000484 | PCM-20251025-00001031 | TT-20251025-01071 | Telecom | Region_1 | JBL0478 | JBL0478 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Hassan Ahmed Hassanin | 10/25/2025 13:43:51 | 10/25/2025 15:13:43 | 10/25/2025 17:43:51 | 4(2G) 4(3G) sites down under JBL2937-P3,JBL2110-P1-HUB,JBL0478-P2,JBL0896-P3/R1_JB_HWBSC01 @ Generator_DG | 10/25/2025 13:21:13 | Critical | 21807 | OML Fault | 10/25/2025 13:21:06 | P2 | SRAN | jubail | Generator_SG | 2G_3G SA | JBL2937-P3 2G_3G,JBL2110-P1-HUB 2G_3G,JBL0478-P2 2G_3G,JBL0896-P3 2G_3G | FLM_EM | JBL0478 | Dear Team, Hub: JBL0478 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251025-00000984 | Dear Team, Hub: JBL0478 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: JBL0478 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/25/2025 13:43:51 | 10/25/2025 15:13:20 | 10/25/2025 15:13:37 |  |  | 10/25/2025 15:13:43 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000485 | PCM-20251025-00001036 | TT-20251025-00508 | EM | Region_4 | BIK0168 | BIK0168 |  |  |  | Riasat Ali Allah Baksh | 10/25/2025 13:45:30 | 10/25/2025 13:45:30 | 10/25/2025 19:45:30 | 1(2G/3G/5G) sites down under BIK0168-P3/BIK0168-P3 @ Sceco | 10/25/2025 07:58:24 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 07:58:21 | P3 | 2G | alaith | Sceco | 2G_3G SA | BIK0168-P3 | FLM_TE | BIK0168 | Results: DOWN SITE HUB BIK0168-P3 BIK0168 Summary: Hub: BIK0168, Down Count: 1, Down Sites: BIK0168-P3 Alarm Summary: BIK0168 No Active Alarm on HUB | PCM-20251025-00000447 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 13:45:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000487 | PCM-20251025-00001042 | TT-20251025-01028 | Telecom | Region_2 | QSDH0891 | QSDH0891 |  |  |  | Moustafa Elzaafarany Abdellah | 10/25/2025 13:47:56 | 10/25/2025 22:34:33 | 10/25/2025 19:47:56 | 3(2G) sites down under QSDH0891-P3,QSDH0713-P3,QSDH0715-P3/R2_BR1_HWBSC01 @ Generator_SG | 10/25/2025 13:01:36 | Major | 21807 | OML Fault | 10/25/2025 13:01:30 | P3 | SRAN | dawadmi | Generator_SG | 2G SA | QSDH0891-P3 | FLM_EM | QSDH0891 | Dear Team, Hub: QSDH0891 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251025-00001034 | Dear Team, Hub: QSDH0891 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: QSDH0891 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/25/2025 13:47:56 | 10/25/2025 22:34:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000490 | PCM-20251025-00001048 | TT-20251025-01129 | EM | Region_6 | DRB1M7953 | DRB0953 |  |  |  | Aziz Ul Haq Umar Gul | 10/25/2025 13:49:13 | 10/25/2025 21:26:27 | 10/26/2025 01:49:13 | AIRCON 1 FAILURE at DRB1M7953-NCA-L800 @ Sceco | 10/25/2025 13:40:56 | Minor | 7103 | AIRCON 1 FAILURE | 10/25/2025 13:40:45 | P3 | 4G | derb | Sceco | LTE NSA | DRB1M7953 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/25/2025 13:49:13 | 10/25/2025 21:26:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000491 | PCM-20251025-00001051 | TT-20251025-01130 | EM | Region_6 | TBL1M8324 | TBL2324 |  |  |  | Abdul Rauf Muhammad Aslam | 10/25/2025 13:49:44 | 10/25/2025 14:21:07 | 10/26/2025 01:49:44 | SHELTER DOOR OPEN at TBL1M8324-G9-L8-SBTS-P3 @ Generator_DG | 10/25/2025 13:49:12 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 11:31:27 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8324 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 13:49:44 | 10/25/2025 14:21:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000496 | PCM-20251025-00001066 | TT-20251025-01142 | EM | Region_6 | BLQ1M8192 | BLQ2192 |  |  |  | Muhammad Naeem Taj Din | 10/25/2025 13:55:25 | 10/26/2025 03:03:07 | 10/26/2025 01:55:25 | GENS RUNING at BLQ1M8192-G9-L8- L18- L21-SBTS-P3 @ Generator_SG | 10/25/2025 13:47:25 | Minor | 7103 | GENS RUNING | 10/25/2025 13:47:15 | P3 | 4G | namas | Generator_SG | LTE NSA | BLQ1M8192 | FLM_EM | [5 empty] | GENS RUNING |  |  | API | 10/25/2025 13:55:25 | 10/26/2025 03:03:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000498 | PCM-20251025-00001070 | TT-20251025-00514 | Reference_telecom | Region_4 | DKA1M3347 | DKA0347 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/25/2025 13:58:56 | 10/25/2025 14:50:00 | 10/25/2025 19:58:56 | WCDMA CELL OUT OF USE at DKA1M3347-P3 @ Sceco | 10/25/2025 08:02:13 | Major | 7771 | WCDMA CELL OUT OF USE | 10/25/2025 08:00:00 | P3 | 3G | qunfuddah | Sceco | 3G SA | DKA1M3347 | FLM_TE |  |  | PCM-20251025-00000449 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 13:58:56 | 10/25/2025 14:50:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000500 | PCM-20251025-00001073 | TT-20251025-01149 | Reference_EM | Region_1 | HLHD0705 | HLHD0705 |  |  |  | Ibrahim Khaled Shendy Khaled | 10/25/2025 14:00:06 | 10/25/2025 15:42:25 | 10/26/2025 02:00:06 | NETECO: AC Failure at HLHD0705 @ Generator_SG | 10/25/2025 13:53:39 | Minor | 10202 | AC Failure | 10/25/2025 13:53:39 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0705 | FLM_EM | [8 empty] | API | 10/25/2025 14:00:06 | 10/25/2025 15:42:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000502 | PCM-20251025-00001077 | TT-20251025-00215 | Reference_telecom | Region_4 | NNL1M3139 | NNL0139 |  |  |  | Riasat Ali Allah Baksh | 10/25/2025 14:01:32 | 10/25/2025 14:01:32 | 10/25/2025 20:01:32 | RNW O&M SCENARIO FAILURE at NNL1M3139-P3 @ Generator_SG | 10/25/2025 03:08:33 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/25/2025 03:07:41 | P3 | 3G | qunfuddah | Generator_SG | 3G NSA | NNL1M3139 | FLM_TE |  |  | PCM-20251025-00000194 | Please check O&M at the site | Please check O&M at the site |  |  |  | API | 10/25/2025 14:01:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000503 | PCM-20251025-00001078 | TT-20251025-01152 | Telecom | Region_4 | MLJI0206 | MLJI0206 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/25/2025 14:03:10 | 10/25/2025 18:07:14 | 10/25/2025 20:03:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at MLJI0206-GSM-UMTS-P3 @ Generator_SG | 10/25/2025 14:02:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 14:02:30 | P3 | 2G | adam | Generator_SG | 5G_Cell SA | MLJI0206 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 14:03:10 | 10/25/2025 18:07:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000504 | PCM-20251025-00001079 | TT-20251025-01153 | Reference_EM | Region_1 | HLHD0705 | HLHD0705 |  |  |  | Ibrahim Khaled Shendy Khaled | 10/25/2025 14:03:41 | 10/25/2025 15:42:26 | 10/26/2025 02:03:41 | Mains Failure at HLHD0705-P3_SRAN @ Generator_SG | 10/25/2025 13:53:43 | Minor | 65109 | Mains Failure | 10/25/2025 13:53:41 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0705 | FLM_EM | [8 empty] | API | 10/25/2025 14:03:41 | 10/25/2025 15:42:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251025000505 | PCM-20251025-00001081 | TT-20251025-01156 | Reference_EM | [7 empty] | 10/25/2025 14:04:13 | 10/25/2025 14:04:13 | 10/26/2025 02:04:13 | Mains Failure at AWJ2395-P3_SRAN @ Generator_SG | 10/25/2025 13:54:25 | Minor | 65109 | Mains Failure | 10/25/2025 13:54:22 | P3 | SRAN |  | Generator_SG | 2G NSA | AWJ2395 | FLM_EM | [8 empty] | API | 10/25/2025 14:04:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000506 | PCM-20251025-00001083 | TT-20251025-01158 | EM | Region_4 | RYMK1M7538 | RYMK0538 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Waheed Ullah Said Haleem | 10/25/2025 14:04:44 | 10/25/2025 15:10:21 | 10/25/2025 20:04:44 | GENERATOR1 + GENERATOR 2 FAILURE at RYMK1M7538-L800-SBTS-P1-HUB @ Generator_DG | 10/25/2025 13:56:34 | Major | 7103 | GENERATOR1 + GENERATOR 2 FAILURE | 10/25/2025 13:56:26 | P1 | 4G | taif | Generator_DG | LTE NSA | RYMK1M7538 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR 2 FAILURE |  |  | API | 10/25/2025 14:04:44 | 10/25/2025 15:09:50 | 10/25/2025 15:09:58 | 10/25/2025 15:10:00 | 10/25/2025 15:10:04 | 10/25/2025 15:10:21 |  | Waheed Ullah Said Haleem |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000507 | PCM-20251025-00001084 | TT-20251025-01159 | Reference_EM | Region_3 | AHT2155 | AHT2155 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 14:05:16 | 10/25/2025 14:05:16 | 10/26/2025 02:05:16 | Mains Failure at AHT2155-P3_SRAN @ Sceco | 10/25/2025 13:55:24 | Minor | 65109 | Mains Failure | 10/25/2025 13:55:21 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2155 | FLM_EM | [8 empty] | API | 10/25/2025 14:05:16 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000508 | PCM-20251025-00001091 | TT-20251025-00906 | Reference_telecom | Region_4 | JED0600 | JED0600 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 14:07:01 | 10/25/2025 14:07:01 | 10/26/2025 02:07:01 | Fronthaul loop back connectivity check failure at JED0600-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/25/2025 11:38:53 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/25/2025 11:38:45 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0600 | FLM_TE |  |  | PCM-20251025-00000831 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 14:07:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000509 | PCM-20251025-00001094 | TT-20251025-01169 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/25/2025 14:09:22 | 10/25/2025 15:21:04 | 10/26/2025 02:09:22 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/25/2025 14:02:12 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/25/2025 14:02:10 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/25/2025 14:09:22 | 10/25/2025 15:21:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000510 | PCM-20251025-00001095 | TT-20251025-01171 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 14:09:23 | 10/25/2025 14:51:53 | 10/26/2025 02:09:23 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/25/2025 14:01:04 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 14:00:53 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 14:09:23 | 10/25/2025 14:51:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000511 | PCM-20251025-00001096 | TT-20251025-01023 | Reference_telecom | Region_4 | JED0063 | JED0063 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 14:10:04 | 10/25/2025 14:10:04 | 10/26/2025 02:10:04 | Fronthaul loop back connectivity check failure at JED0063-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 12:34:05 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/25/2025 12:33:54 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0063 | FLM_TE |  |  | PCM-20251025-00000931 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 14:10:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000512 | PCM-20251025-00001099 | TT-20251012-01968 | MW_HC | Region_1 | SLW0915 | SLW0915 |  |  |  | Mohamed Magdy Fouad Zayed | 10/25/2025 14:13:57 | 10/25/2025 17:37:00 | 10/26/2025 02:13:57 | Huawei MW HC_P2 Observing Errors at SLW0915-SLW0921 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | hafouf | Power Cube | TX NSA | SLW0915-SLW0921 | FLM_TE |  | kindly share correct clearance time what is 00:60? | PCM-20251025-00001069 | kindly share correct clearance time what is 00:60? | kindly share correct clearance time what is 00:60? |  |  |  | API | 10/25/2025 14:13:57 | 10/25/2025 17:37:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000513 | PCM-20251025-00001100 | TT-20251025-01173 | Reference_EM | Region_3 | AHT2155 | AHT2155 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 14:14:33 | 10/25/2025 14:14:33 | 10/26/2025 02:14:33 | Door opening alarm at AHT2155-P3_SRAN @ Sceco | 10/25/2025 14:14:07 | Minor | 65101 | Door opening alarm | 10/25/2025 14:14:04 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2155 | FLM_EM | [8 empty] | API | 10/25/2025 14:14:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000514 | PCM-20251025-00001104 | TT-20251025-01178 | Telecom | Region_4 | JED2042 | JED2042 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 14:17:19 | 10/25/2025 14:54:15 | 10/25/2025 20:17:19 | D-CHANNEL FAILURE at JED2042-P1-VIP @ Generator_SG | 10/25/2025 14:14:30 | Major | 7705 | D-CHANNEL FAILURE | 10/25/2025 14:13:25 | VIP | 2G | jeddah | Generator_SG | 2G_Cell SA | JED2042 | FLM_TE | [8 empty] | API | 10/25/2025 14:17:19 | 10/25/2025 14:54:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000515 | PCM-20251025-00001105 | TT-20251025-01181 | Telecom | Region_3 | MDN0720-ZMad02-CSG-01 | MDN0720 |  |  |  | TAUSEEF ILYAS | 10/25/2025 14:18:10 | 10/25/2025 14:51:17 | 10/26/2025 02:18:10 | Bad Package Error Rising at MDN0720-ZMad02-CSG-01 @ Sceco | 10/25/2025 14:17:41 | Minor | 101-2501403 | Bad Package Error Rising | 10/25/2025 14:17:31 | P1 | IPRAN | madinah | Sceco | IPRAN NSA | MDN0720-ZMad02-CSG-01 | FLM_TE | [8 empty] | API | 10/25/2025 14:18:10 | 10/25/2025 14:51:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000516 | PCM-20251025-00001106 | TT-20251025-01183 | Reference_EM | Region_1 | HFBD2M5660 | HFBD0660 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/25/2025 14:19:11 | 10/25/2025 14:19:11 | 10/25/2025 20:19:11 | Door opening alarm at HFBD2M5660-P1-HUB @ Generator_SG | 10/25/2025 14:18:36 | Major | 65101 | Door opening alarm | 10/25/2025 14:18:32 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5660 | FLM_EM | [8 empty] | API | 10/25/2025 14:19:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000517 | PCM-20251025-00001109 | TT-20251025-01144 | Telecom | Region_5 | HHR0436 | HHR0436 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 14:19:14 | 10/26/2025 01:12:01 | 10/25/2025 18:19:14 | 2(2G) 1(LTE) 1(5G) sites down under MAK0764-P1-HRM,HHR0436-P1-VIP-HHR/HHR0436-P1-VIP-HHR @ Sceco | 10/25/2025 13:53:21 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 13:53:15 | VIP | 2G | makkah | Sceco | 2G_LTE SA | HHR0436-P1-VIP-HHR 2G_LTE,MAK0764-P1-HRM 2G | FLM_TE | HHR0436 | Scattered sites:MAK0764 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. HHR0436 observing ETH LOS and Lan Link Kindly update TT under EM, FLM | PCM-20251025-00001076 | Scattered sites:MAK0764 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. HHR0436 observing ETH LOS and Lan Link Kindly update TT under EM, FLM | Scattered sites:MAK0764 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. HHR0436 observing ETH LOS and Lan Link Kindly update TT under EM, FLM |  | sites down |  | API | 10/25/2025 14:19:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000519 | PCM-20251025-00001112 | TT-20251025-01188 | EM | Region_5 | HHR1M7436 | HHR0436 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 14:21:46 | 10/25/2025 14:21:46 | 10/25/2025 20:21:46 | SHELTER DOOR OPEN;Default System Time at HHR1M7436-G9-L8-NL18-NL21-SBTS-P1-VIP-HHR @ Sceco | 10/25/2025 14:21:31 | Major | 7103 | SHELTER DOOR OPEN;Default System Time | 10/25/2025 14:12:32 | VIP | 4G | makkah | Sceco | LTE NSA | HHR1M7436 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/25/2025 14:21:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000520 | PCM-20251025-00001114 | TT-20251025-00837 | Telecom | Region_4 | JED1M7238 | JED0238 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 14:23:19 | 10/26/2025 10:46:12 | 10/25/2025 20:23:19 | BASE STATION ANTENNA LINE PROBLEM at JED1M7238-P1-WDM-CA-L900-NL800-SBTS @ Sceco | 10/25/2025 11:24:59 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 11:24:49 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7238 | FLM_TE |  |  | PCM-20251025-00000762 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 14:23:19 | 10/26/2025 10:36:42 | 10/26/2025 10:39:02 | 10/26/2025 10:39:05 | 10/26/2025 10:46:12 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000521 | PCM-20251025-00001116 | TT-20251025-01182 | EM | Region_6 | BHAB2090 | BHAB2090 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/25/2025 14:23:59 | 10/25/2025 14:51:54 | 10/25/2025 20:23:59 | 1(2G/5G) sites down under BHAB2090-P3/BHAB2090-P3 @ Generator_SG | 10/25/2025 14:15:55 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 14:15:53 | P3 | 2G | mohail | Generator_SG | 2G_5G SA | BHAB2090-P3 | FLM_EM | BHAB2090 | Results: DOWN SITE HUB BHAB2090-P3 BHAB2090 Summary: Hub: BHAB2090, Down Count: 1, Down Sites: BHAB2090-P3 Alarm Summary: BHAB2090 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 14:23:59 | 10/25/2025 14:51:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000522 | PCM-20251025-00001118 | TT-20251025-01191 | Reference_EM | Region_2 | RIY2056 | RIY2056 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 14:24:21 | 10/26/2025 09:20:15 | 10/25/2025 20:24:21 | Door opening alarm at RIY2056-P1-VIP_SRAN @ Sceco | 10/25/2025 14:23:53 | Major | 65101 | Door opening alarm | 10/25/2025 14:23:49 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2056 | FLM_EM | [8 empty] | API | 10/25/2025 14:24:21 | 10/26/2025 09:20:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000523 | PCM-20251025-00001119 | TT-20251025-01105 | Telecom | Region_6 | KMS1M7304 | KMS0304 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/25/2025 14:24:22 | 10/25/2025 20:18:35 | 10/25/2025 20:24:22 | BASE STATION ANTENNA LINE PROBLEM at KMS1M7304-P3-CA-L800 @ Sceco | 10/25/2025 13:29:03 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 13:28:59 | P2 | 4G | abha | Sceco | LTE NSA | KMS1M7304 | FLM_TE |  |  | PCM-20251025-00001011 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 14:24:22 | 10/25/2025 17:53:08 | 10/25/2025 20:17:58 | 10/25/2025 20:18:01 |  | 10/25/2025 20:18:35 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000524 | PCM-20251025-00001120 | TT-20251025-01192 | Reference_EM | [7 empty] | 10/25/2025 14:24:52 | 10/25/2025 14:24:52 | 10/26/2025 02:24:52 | Major Rec alarm at RIYA6131-P3_SRAN @ Sceco | 10/25/2025 14:14:40 | Minor | 65107 | Major Rec alarm | 10/25/2025 14:14:35 | P3 | SRAN |  | Sceco | 2G NSA | RIYA6131 | FLM_EM | [8 empty] | API | 10/25/2025 14:24:52 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000528 | PCM-20251025-00001131 | TT-20251008-01738 | MW_HC | Region_1 | SLW0915 | SLW0915 |  |  |  | Mohamed Magdy Fouad Zayed | 10/25/2025 14:30:32 | 10/25/2025 17:37:01 | 10/26/2025 02:30:32 | Huawei MW HC_P2 Observing Errors at SLW0915-SLW0913 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | hafouf | Power Cube | TX NSA | SLW0915-SLW0913 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251025-00001113 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/25/2025 14:30:32 | 10/25/2025 17:37:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000529 | PCM-20251025-00001132 | TT-20251025-01205 | EM | Region_6 | MKW1M8400 | MKW2400 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 14:30:34 | 10/25/2025 17:36:47 | 10/26/2025 02:30:34 | H/E Alarm at MKW1M8400-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/25/2025 14:22:26 | Minor | 7103 | H/E Alarm | 10/25/2025 14:22:19 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8400 | FLM_EM | [5 empty] | H/E Alarm |  |  | API | 10/25/2025 14:30:34 | 10/25/2025 17:36:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000530 | PCM-20251025-00001135 | TT-20251025-01207 | Telecom | Region_1 | HFF6029 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 14:31:04 | 10/25/2025 20:23:23 | 10/25/2025 20:31:04 | DCU CPRI Interface Error at HFF6029-DCU1 @ Sceco | 10/25/2025 14:24:50 | Major | 26234 | DCU CPRI Interface Error | 10/25/2025 14:24:10 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/25/2025 14:31:04 | 10/25/2025 14:49:31 | 10/25/2025 20:23:09 |  |  | 10/25/2025 20:23:23 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000531 | PCM-20251025-00001138 | TT-20251025-01079 | EM | Region_6 | JIZ0093 | JIZ0093 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/25/2025 14:32:20 | 10/25/2025 17:08:51 | 10/25/2025 18:32:20 | 1(2G/3G/LTE) sites down under JIZ0093-P1-HUB/JIZ0093-P1-HUB @ Sceco_STB | 10/25/2025 13:23:29 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 13:23:23 | P1 | 2G | jizan | Sceco_STB | 2G_3G_LTE SA | JIZ0093-P1-HUB | FLM_TE | JIZ0093 | Results: DOWN SITE HUB JIZ0093-P1-HUB JIZ0093 Summary: Hub: JIZ0093, Down Count: 1, Down Sites: JIZ0093-P1-HUB Alarm Summary: JIZ0093 No Active Alarm on HUB | PCM-20251025-00000993 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 14:32:20 | 10/25/2025 17:06:31 | 10/25/2025 17:08:37 |  |  | 10/25/2025 17:08:51 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000532 | PCM-20251025-00001141 | TT-20251025-01212 | Telecom | Region_2 | RIY0948 | RIY0948 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Waseem Shahzad Ghulam Rasool | 10/25/2025 14:34:10 | 10/25/2025 17:33:02 | 10/25/2025 20:34:10 | BBU CPRI Interface Error at RIY0948-P1-VIP_SRAN-FON @ Sceco | 10/25/2025 14:31:06 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 14:28:34 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0948 | FLM_TE | [8 empty] | API | 10/25/2025 14:34:10 | 10/25/2025 15:34:48 | 10/25/2025 17:32:57 |  |  | 10/25/2025 17:33:02 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000533 | PCM-20251025-00001150 | TT-20251025-01218 | Telecom | Region_2 | RIY0948 | RIY0948 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Waseem Shahzad Ghulam Rasool | 10/25/2025 14:36:45 | 10/25/2025 17:33:16 | 10/25/2025 20:36:45 | NR Cell Unavailable at RIY0948-P1-VIP_SRAN-FON @ Sceco | 10/25/2025 14:30:15 | Major | 29841 | NR Cell Unavailable | 10/25/2025 14:28:43 | VIP | SRAN | riyadh | Sceco | 5G SA | RIY0948 | FLM_TE | [8 empty] | API | 10/25/2025 14:36:45 | 10/25/2025 15:34:48 | 10/25/2025 17:33:10 |  |  | 10/25/2025 17:33:16 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000534 | PCM-20251025-00001151 | TT-20251025-01219 | Telecom | Region_4 | MKMD1M7557 | MKMD0557 |  |  |  | Khizer Hayat | 10/25/2025 14:36:45 | 10/26/2025 08:36:43 | 10/25/2025 20:36:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKMD1M7557-L800-SBTS @ Sceco_STB | 10/25/2025 14:36:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 14:35:56 | P2 | 4G | jeddah | Sceco_STB | 5G_Cell SA | MKMD1M7557 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 14:36:45 | 10/26/2025 08:36:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000535 | PCM-20251025-00001153 | TT-20251025-01166 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/25/2025 14:39:45 | 10/26/2025 08:36:44 | 10/26/2025 02:39:45 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/25/2025 14:00:09 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 14:00:01 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251025-00001092 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 14:39:45 | 10/26/2025 08:36:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000536 | PCM-20251025-00001155 | TT-20251025-01224 | Telecom | Region_4 | UKZ0164 | UKZ0164 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/25/2025 14:39:52 | 10/25/2025 18:07:15 | 10/25/2025 20:39:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at UKZ0164-GSM-UMTS-P2-USF @ Generator_SG | 10/25/2025 14:39:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 14:38:52 | P2 | 2G | adam | Generator_SG | 5G_Cell SA | UKZ0164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 14:39:52 | 10/25/2025 18:07:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000537 | PCM-20251025-00001157 | TT-20251025-01227 | Telecom | Region_4 | JED2028 | JED2028 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 14:40:22 | 10/25/2025 14:40:22 | 10/26/2025 02:40:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2028-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/25/2025 14:39:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 14:39:34 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2028 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 14:40:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000538 | PCM-20251025-00001159 | TT-20251025-01229 | Reference_EM | Region_1 | HFBD2M5660 | HFBD0660 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/25/2025 14:40:23 | 10/25/2025 14:40:23 | 10/25/2025 20:40:23 | Mains Failure at HFBD2M5660-P1-HUB @ Generator_SG | 10/25/2025 14:30:22 | Major | 65109 | Mains Failure | 10/25/2025 14:30:15 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5660 | FLM_EM | [8 empty] | API | 10/25/2025 14:40:23 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000540 | PCM-20251025-00001160 | TT-20251025-01157 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 14:42:06 | 10/25/2025 14:42:06 | 10/25/2025 18:42:06 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/25/2025 13:56:30 | Critical | 7654 | CELL OPERATION DEGRADED | 10/25/2025 13:56:18 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251025-00001082 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 14:42:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000543 | PCM-20251025-00001165 | TT-20251025-00839 | Reference_telecom | Region_4 | HHR1M7459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 14:44:52 | 10/25/2025 14:44:52 | 10/25/2025 18:44:52 | CELL NOTIFICATION (Temperature alarm) at HHR1M7459-L800-P1-VIP @ Sceco | 10/25/2025 11:24:50 | Critical | 7655 | CELL NOTIFICATION | 10/25/2025 11:24:39 | VIP | 4G | jeddah | Sceco | LTE NSA | HHR1M7459 | FLM_TE |  |  | PCM-20251025-00000764 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 14:44:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000545 | PCM-20251025-00001169 | TT-20251025-01230 | Telecom | Region_4 | JZMA1M7824 | JZMA0824 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/25/2025 14:45:29 | 10/25/2025 14:50:01 | 10/25/2025 20:45:29 | 1(LTE) sites down under JZMA0824-G9-L8-SBTS-P3 @ Sceco | 10/25/2025 14:37:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 14:37:09 | P3 | 4G | qunfuddah | Sceco | LTE SA | JZMA0824-G9-L8-SBTS-P3 | FLM_TE | JZMA0824 | Results: DOWN SITE HUB JZMA0824-G9-L8-SBTS-P3 JZMA0824 Summary: Hub: JZMA0824, Down Count: 1, Down Sites: JZMA0824-G9-L8-SBTS-P3 Alarm Summary: JZMA0824 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.0.100:8080] [URL:http://10.98.0.100:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 14:45:29 | 10/25/2025 14:50:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000546 | PCM-20251025-00001181 | TT-20251025-01253 | Telecom | Region_6 | TFBH0887-LL-CSG-01 | TFBH0887 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/25/2025 14:49:40 | 10/25/2025 16:18:21 | 10/26/2025 02:49:40 | Bad Package Error Rising at TFBH0887-LL-CSG-01 @ Sceco_STB | 10/25/2025 14:49:12 | Minor | 101-2501403 | Bad Package Error Rising | 10/25/2025 14:49:05 | P3 | IPRAN | makhwa | Sceco_STB | IPRAN NSA | TFBH0887-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/25/2025 14:49:40 | 10/25/2025 15:12:13 | 10/25/2025 16:17:54 |  |  | 10/25/2025 16:18:21 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000547 | PCM-20251025-00001185 | TT-20251025-01254 | Telecom | Region_6 | JIZ0011 | JIZ0011 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/25/2025 14:50:42 | 10/25/2025 17:06:55 | 10/25/2025 20:50:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ0011-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB @ Sceco | 10/25/2025 14:49:48 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 14:49:38 | P1 | 2G | jizan | Sceco | 5G_Cell SA | JIZ0011 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 14:50:42 | 10/25/2025 17:06:32 | 10/25/2025 17:06:42 |  |  | 10/25/2025 17:06:55 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000550 | PCM-20251025-00001195 | TT-20251025-01259 | EM | Region_6 | BLQ1M8059 | BLQ2059 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 14:53:49 | 10/25/2025 17:36:47 | 10/26/2025 02:53:49 | SHELTER DOOR OPEN at BLQ1M8059-G9-L8-L18-L21-SBTS @ Generator_SG | 10/25/2025 14:53:25 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 14:53:15 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BLQ1M8059 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 14:53:49 | 10/25/2025 17:36:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000552 | PCM-20251025-00001199 | TT-20251025-01262 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 14:55:21 | 10/25/2025 15:09:29 | 10/26/2025 02:55:21 | RF Unit Maintenance Link Failure at DAM6027-DCU1 @ Sceco | 10/25/2025 14:50:10 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 14:49:54 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/25/2025 14:55:21 | 10/25/2025 15:09:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000553 | PCM-20251025-00001201 | TT-20251025-01245 | Telecom | Region_4 | JED0712 | JED0712 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/25/2025 14:55:35 | 10/25/2025 14:55:35 | 10/25/2025 20:55:35 | 2(2G) 2(LTE) 1(5G) sites down under JED0712-P2,JDMK2401 -P3/JDMK2401-P3 @ Generator_SG | 10/25/2025 14:45:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 14:44:57 | P2 | 2G | jeddah | Generator_SG | 2G_LTE SA | JDMK2401 -P3 2G_LTE,JED0712-P2 2G_LTE | FLM_EM | JED0712 | Hub: JED0712 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251025-00001193 | Hub: JED0712 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: JED0712 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/25/2025 14:55:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000554 | PCM-20251025-00001203 | TT-20251025-01255 | Reference_telecom | Region_6 | BRQ1M3084 | BRQ0084 | Equipment | CB_BTS | Replace DCDU Fuse | Muhammad Jamal Khan Abbas Ali | 10/25/2025 14:56:31 | 10/25/2025 18:51:22 | 10/25/2025 20:56:31 | CELL OPERATION DEGRADED (Failure in optical RP3 interface) at BRQ1M3084-P2-WBB-G3 @ Sceco | 10/25/2025 14:42:35 | Major | 7654 | CELL OPERATION DEGRADED | 10/25/2025 14:42:18 | P1 | 3G | mohail | Sceco | LTE_Cell SA | BRQ1M3084 | FLM_TE |  |  | PCM-20251025-00001186 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 14:56:31 | 10/25/2025 17:52:59 | 10/25/2025 18:07:54 | 10/25/2025 18:07:58 | 10/25/2025 18:34:29 | 10/25/2025 18:51:22 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000558 | PCM-20251025-00001212 | TT-20251025-01269 | EM | Region_6 | ABBS1M8247 | ABBS2247 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/25/2025 14:59:29 | 10/25/2025 14:59:29 | 10/26/2025 02:59:29 | SHELTER DOOR OPEN at ABBS1M8247-L800-P3-SBTS-WBB-G3 @ Sceco | 10/25/2025 14:58:53 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 14:58:46 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M8247 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 14:59:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000559 | PCM-20251025-00001213 | TT-20251025-01271 | Telecom | Region_6 | TNM1M8720 | TNM2720 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/25/2025 14:59:30 | 10/25/2025 17:52:59 | 10/26/2025 02:59:30 | BASE STATION INFORMATION (Fan vendor not detected) at TNM1M8720-CA-L1800-L800-P3 @ Generator_SG | 10/25/2025 14:51:22 | Minor | 7115 | BASE STATION INFORMATION | 10/25/2025 14:51:11 | P3 | 4G | mohail | Generator_SG | LTE NSA | TNM1M8720 | FLM_TE | [5 empty] | Fan vendor not detected |  |  | API | 10/25/2025 14:59:30 | 10/25/2025 17:52:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000561 | PCM-20251025-00001214 | TT-20251025-01089 | Reference_telecom | Region_4 | KHL1M7471 | KHL0471 |  |  |  | Nazeer Mohammed | 10/25/2025 14:59:56 | 10/25/2025 17:00:10 | 10/25/2025 20:59:56 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at KHL1M7471-P3-CA-L800 @ Sceco | 10/25/2025 13:26:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 13:26:15 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | KHL1M7471 | FLM_TE |  |  | PCM-20251025-00000992 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 14:59:56 | 10/25/2025 17:00:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000562 | PCM-20251025-00001215 | TT-20251025-01239 | Telecom | Region_1 | HLHD0705 | HLHD0705 |  |  |  | Ibrahim Khaled Shendy Khaled | 10/25/2025 15:00:12 | 10/25/2025 17:34:33 | 10/25/2025 21:00:12 | 3(2G) 1(3G) 3(LTE) sites down under HLHD0707-P3,HLHD0705-P3,RAF2584-P3-USF/HB1BSCH01 @ Generator_SG | 10/25/2025 14:44:09 | Major | 21825 | CSL Fault | 10/25/2025 14:44:07 | P3 | SRAN | rafha | Generator_SG | 2G_3G_LTE SA | RAF2584-P3-USF 2G_3G_LTE,HLHD0707-P3 2G_LTE,HLHD0705-P3 2G_LTE | FLM_EM | HLHD0705 | Dear Team, Hub: HLHD0705 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251025-00001188 | Dear Team, Hub: HLHD0705 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: HLHD0705 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/25/2025 15:00:12 | 10/25/2025 15:42:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000563 | PCM-20251025-00001216 | TT-20251025-01272 | Telecom | Region_6 | KMS1M7460 | KMS0460 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/25/2025 15:01:34 | 10/25/2025 22:14:25 | 10/26/2025 03:01:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS1M7460-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/25/2025 15:00:37 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:00:32 | P3 | 4G | khamis mushyet | Sceco | 5G_Cell SA | KMS1M7460 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:01:34 | 10/25/2025 17:25:30 | 10/25/2025 22:14:12 |  |  | 10/25/2025 22:14:25 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000564 | PCM-20251025-00001217 | TT-20251025-01250 | Reference_telecom | Region_4 | JED1M7712 | JED0712 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 15:02:20 | 10/25/2025 15:02:20 | 10/25/2025 21:02:20 | CELL FAULTY (Failure in optical interface) at JED1M7712-CA-L900-P3 @ Generator_SG | 10/25/2025 14:44:21 | Major | 7653 | CELL FAULTY | 10/25/2025 14:44:13 | P2 | 4G | jeddah | Generator_SG | LTE_Cell SA | JED1M7712 | FLM_TE |  |  | PCM-20251025-00001178 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 15:02:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000566 | PCM-20251025-00001219 | TT-20251025-01107 | Telecom | Region_4 | JED0024 | JED0024 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 15:03:30 | 10/26/2025 10:36:43 | 10/25/2025 21:03:30 | BASE STATION HARDWARE PROBLEM (RX Power too low) at JED0024-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/25/2025 13:32:27 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/25/2025 13:30:33 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0024 | FLM_TE |  |  | PCM-20251025-00001013 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 15:03:30 | 10/26/2025 10:36:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000567 | PCM-20251025-00001220 | TT-20251025-01277 | Telecom | Region_6 | ABBS1M8096 | ABBS2096 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/25/2025 15:04:39 | 10/25/2025 16:18:50 | 10/26/2025 03:04:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABBS1M8096-P3-L800-SBTS-WBB-G3 @ Sceco | 10/25/2025 15:04:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:03:52 | P3 | 4G | Albaha | Sceco | 5G_Cell SA | ABBS1M8096 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:04:39 | 10/25/2025 15:12:14 | 10/25/2025 16:18:39 |  |  | 10/25/2025 16:18:50 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000569 | PCM-20251025-00001226 | TT-20251025-01280 | Reference_EM | Region_3 | MDN2367 | MDN2367 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/25/2025 15:05:41 | 10/25/2025 15:05:41 | 10/26/2025 03:05:41 | Mains Failure at MDN2367-P3_SRAN @ Generator_SG | 10/25/2025 14:55:43 | Minor | 65109 | Mains Failure | 10/25/2025 14:55:37 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDN2367 | FLM_EM | [8 empty] | API | 10/25/2025 15:05:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000570 | PCM-20251025-00001227 | TT-20251025-00884 | Reference_telecom | Region_6 | BHAB1M7819 | BHAB0819 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/25/2025 15:05:53 | 10/25/2025 16:17:38 | 10/26/2025 03:05:53 | BASE STATION SERVICE PROBLEM (Not able to synchronize baseband bus) at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/25/2025 11:54:30 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:54:22 | P3 | 4G | makhwa | Sceco | 5G_Cell SA | BHAB1M7819 | FLM_TE |  |  | PCM-20251025-00000809 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 15:05:53 | 10/25/2025 15:12:14 | 10/25/2025 16:17:24 |  |  | 10/25/2025 16:17:38 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000571 | PCM-20251025-00001228 | TT-20251025-01281 | EM | Region_6 | BLQ1M8059 | BLQ2059 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 15:06:12 | 10/25/2025 17:36:48 | 10/26/2025 03:06:12 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at BLQ1M8059-G9-L8-L18-L21-SBTS @ Generator_SG | 10/25/2025 14:57:49 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/25/2025 14:57:43 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BLQ1M8059 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/25/2025 15:06:12 | 10/25/2025 17:36:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000572 | PCM-20251025-00001230 | TT-20251025-01283 | Reference_telecom | Region_4 | JED2215 | JED2215 |  |  |  | Nazeer Mohammed | 10/25/2025 15:06:43 | 10/25/2025 17:00:10 | 10/26/2025 03:06:43 | LossOfSignal observed in JED2215 towards 10.21.74.163 @ Sceco | 10/25/2025 03:06:20 | Minor |  | LossOfSignal | 10/25/2025 03:06:16 | P3 | 2G | jeddah | Sceco | TX NSA | JED2215 | FLM_TE | [8 empty] | API | 10/25/2025 15:06:43 | 10/25/2025 17:00:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000573 | PCM-20251025-00001231 | TT-20251025-01284 | Reference_telecom | Region_4 | JED2288 | JED2288 |  |  |  | Nazeer Mohammed | 10/25/2025 15:06:44 | 10/25/2025 17:00:10 | 10/26/2025 03:06:44 | LagPortDown observed in JED2288 towards 10.21.74.162 @ Sceco | 10/25/2025 03:06:22 | Minor |  | LagPortDown | 10/25/2025 03:06:17 | P3 | 2G | jeddah | Sceco | TX NSA | JED2288 | FLM_TE | [8 empty] | API | 10/25/2025 15:06:44 | 10/25/2025 17:00:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000577 | PCM-20251025-00001236 | TT-20251025-01279 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 15:07:32 | 10/25/2025 15:07:32 | 10/25/2025 21:07:32 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/25/2025 15:00:12 | Major | 7114 | CELL SERVICE PROBLEM | 10/25/2025 15:00:07 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251025-00001224 | Please check with TRM team | Please check with TRM team |  |  |  | API | 10/25/2025 15:07:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251025000579 | PCM-20251025-00001241 | TT-20251025-01293 | Reference_telecom | Region_4 | JED0882 | JED0882 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/25/2025 15:11:09 | 10/25/2025 18:05:30 | 10/26/2025 03:11:09 | AS per BO request NOKIA MW link JED0882-JED0679 | 10/25/2025 15:08:57 | Minor | 113388 | LOF | 10/25/2025 15:09:00 | P2 | 2G | jeddah | Sceco | TX NSA | JED0882-JED0679 | FLM_TE | [8 empty] | API | 10/25/2025 15:11:09 | 10/25/2025 18:04:42 | 10/25/2025 18:05:04 | 10/25/2025 18:05:07 | 10/25/2025 18:05:30 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000581 | PCM-20251025-00001248 | TT-20251025-01290 | Reference_telecom | Region_3 | MDN2U6702 | MDN6002 |  |  |  | TAUSEEF ILYAS | 10/25/2025 15:14:10 | 10/25/2025 18:56:49 | 10/26/2025 03:14:10 | Cell RX Channel Interference Noise Power Unbalanced at MDN2U6702-P1-VIP @ Sceco | 10/25/2025 12:07:53 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 12:07:49 | VIP | 4G | madinah | Sceco | 2G NSA | MDN2U6702 | FLM_TE |  |  | PCM-20251025-00001238 | Need FLM to make RF path HC for RRU 71 | Need FLM to make RF path HC for RRU 71 |  |  |  | API | 10/25/2025 15:14:10 | 10/25/2025 18:56:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000584 | PCM-20251025-00001251 | TT-20251025-01296 | EM | Region_6 | FIF0150 | FIF0150 |  |  |  | Muhammad Tayyab | 10/25/2025 15:17:01 | 10/25/2025 20:16:07 | 10/25/2025 21:17:01 | 1(2G/3G/LTE) sites down under FIF0150-P2/FIF0150-P2 @ Sceco | 10/25/2025 15:09:23 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 15:09:20 | P2 | 2G | dair | Sceco | 2G_3G_LTE SA | FIF0150-P2 | FLM_EM | FIF0150 | Results: DOWN SITE HUB FIF0150-P2 FIF0150 Summary: Hub: FIF0150, Down Count: 1, Down Sites: FIF0150-P2 Alarm Summary: FIF0150 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 15:17:01 | 10/25/2025 20:16:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000586 | PCM-20251025-00001254 | TT-20251025-01305 | Telecom | Region_4 | JED2480 | JED2480 |  |  |  | Nazeer Mohammed | 10/25/2025 15:18:36 | 10/25/2025 17:00:11 | 10/26/2025 03:18:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2480-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 15:17:42 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:17:35 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2480 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:18:36 | 10/25/2025 17:00:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000587 | PCM-20251025-00001255 | TT-20251025-01304 | EM | Region_6 | BSA2045 | BSA2045 |  |  |  | Asad Saddiq | 10/25/2025 15:18:37 | 10/26/2025 07:20:13 | 10/26/2025 03:18:37 | RECTIFIER MAINS POWER FAILURE at BSA2045-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 15:10:21 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 15:10:17 | P3 | 2G | bisha | Sceco | 2G NSA | BSA2045 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 15:18:37 | 10/26/2025 07:20:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000591 | PCM-20251025-00001260 | TT-20251025-01310 | EM | Region_6 | BHAB1M7827 | BHAB0827 |  |  |  | Zia Ur Rahamn | 10/25/2025 15:20:40 | 10/26/2025 07:35:58 | 10/25/2025 21:20:40 | SHELTER DOOR OPEN at BHAB1M7827-G9-L8-L18-L21-SBTS-P1-HUB @ Sceco_STB | 10/25/2025 15:20:24 | Major | 7103 | SHELTER DOOR OPEN | 10/25/2025 15:20:17 | P1 | 4G | makhwa | Sceco_STB | LTE NSA | BHAB1M7827 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 15:20:40 | 10/26/2025 07:35:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000592 | PCM-20251025-00001263 | TT-20251025-01312 | EM | Region_6 | AQQ1M8424 | AQQ2424 |  |  |  | Sohail Nasir Mir Afzal | 10/25/2025 15:21:42 | 10/25/2025 21:20:58 | 10/26/2025 03:21:42 | RECTIFIER MAINS POWER FAILURE at AQQ1M8424-G9-L8-L18-SBTS @ Generator_SG | 10/25/2025 15:13:45 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/25/2025 15:13:39 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8424 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/25/2025 15:21:42 | 10/25/2025 21:20:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000593 | PCM-20251025-00001265 | TT-20251025-01315 | Telecom | Region_4 | JD1-OSN7500-SWAP | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/25/2025 15:24:54 | 10/25/2025 15:24:54 | 10/25/2025 21:24:54 | R_LOF Active alarm at JD1-OSN7500-SWAP 8-N1SLO16-1(RY1JD1-STM16-02)-SPI:1 | 10/25/2025 15:19:40 | Major | 8 | R_LOF | 10/25/2025 15:19:40 | P3 | TX | jeddah | Sceco_STB | TX NSA | JD1-OSN7500-SWAP | FLM_TE | [5 empty] | RR_LOF Active alarm at JD1-OSN7500-SWAP 8-N1SLO16-1(RY1JD1-STM16-02)-SPI:1 |  |  | API | 10/25/2025 15:24:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000595 | PCM-20251025-00001268 | TT-20251025-01320 | Telecom | Region_6 | BAH0009 | BAH0009 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/25/2025 15:25:50 | 10/25/2025 16:10:09 | 10/26/2025 03:25:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at BAH0009-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 15:25:17 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:25:07 | P3 | 2G | Albaha | Sceco | 5G_Cell SA | BAH0009 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:25:50 | 10/25/2025 16:06:58 | 10/25/2025 16:10:01 |  |  | 10/25/2025 16:10:09 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000597 | PCM-20251025-00001273 | TT-20251025-01316 | EM | Region_2 | QRA2M2855 | QRA2855 |  |  |  | Farman Ullah Muhammad Nazir | 10/25/2025 15:29:59 | 10/25/2025 15:29:59 | 10/25/2025 21:29:59 | 1(2G/3G/LTE) sites down under QRA2855-P2/R2_BR1_HWBSC01 @ Sceco | 10/25/2025 15:23:17 | Major | 21825 | CSL Fault | 10/25/2025 15:23:16 | P2 | 2G | buraidah | Sceco | 2G_3G_LTE SA | QRA2855-P2 | FLM_EM | QRA2855 | Results: DOWN SITE HUB QRA2855-P2 QRA2855 Summary: Hub: QRA2855, Down Count: 1, Down Sites: QRA2855-P2 Alarm Summary: QRA2855 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 15:29:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000598 | PCM-20251025-00001275 | TT-20251025-01329 | Telecom | Region_4 | JED1M8178 | JED2178 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 15:31:01 | 10/25/2025 15:31:01 | 10/25/2025 21:31:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8178-P3-CA-L800 @ Sceco | 10/25/2025 15:30:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:30:17 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8178 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:31:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000601 | PCM-20251025-00001282 | TT-20251025-01342 | EM | Region_6 | MKW2335 | MKW2335 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 15:34:37 | 10/25/2025 17:36:49 | 10/26/2025 03:34:37 | COMERCIAL POWER at MKW2335-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/25/2025 15:26:31 | Minor | 7103 | COMERCIAL POWER | 10/25/2025 15:26:20 | P3 | 2G | Albaha | Generator_SG | 2G NSA | MKW2335 | FLM_EM | [5 empty] | COMERCIAL POWER |  |  | API | 10/25/2025 15:34:37 | 10/25/2025 17:36:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000603 | PCM-20251025-00001285 | TT-20251025-01226 | EM | Region_6 | NJR0777 | NJR0777 |  |  |  | TALEH MUHAMMAD | 10/25/2025 15:36:22 | 10/25/2025 16:09:38 | 10/25/2025 21:36:22 | 1(2G/LTE) sites down under NJR0777-P3/NJR0777-P3 @ Sceco | 10/25/2025 14:36:37 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 14:36:33 | P3 | 2G | najran | Sceco | 2G_LTE SA | NJR0777-P3 | FLM_TE | NJR0777 | Results: DOWN SITE HUB NJR0777-P3 NJR0777 Summary: Hub: NJR0777, Down Count: 1, Down Sites: NJR0777-P3 Alarm Summary: NJR0777 Alarm Active on HUB | PCM-20251025-00001167 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 15:36:22 | 10/25/2025 16:09:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000605 | PCM-20251025-00001290 | TT-20251025-01349 | Reference_EM | Region_3 | MDN2338 | MDN2338 |  |  |  | Usman Khan Fazal Manan | 10/25/2025 15:40:49 | 10/25/2025 15:46:26 | 10/26/2025 03:40:49 | Genset not in auto mode at MDN2338-P3_SRAN @ Generator_DG | 10/25/2025 15:30:25 | Minor | 65113 | Genset not in auto mode | 10/25/2025 15:30:22 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDN2338 | FLM_EM | [8 empty] | API | 10/25/2025 15:40:49 | 10/25/2025 15:46:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000606 | PCM-20251025-00001292 | TT-20251025-01352 | Reference_EM | Region_3 | YBDB9002 | YBDB9002 | Enviroment | SCECO_Failure | SCECO auto restored | Sayed Satoor | 10/25/2025 15:42:23 | 10/25/2025 16:47:39 | 10/26/2025 03:42:23 | NETECO: AC Failure at YBDB9002 @ Sceco | 10/25/2025 15:36:04 | Minor | 10202 | AC Failure | 10/25/2025 15:36:04 | P3 | Repeater | yanbu | Sceco | 2G NSA | YBDB9002 | FLM_EM | [8 empty] | API | 10/25/2025 15:42:23 | 10/25/2025 16:43:47 | 10/25/2025 16:47:26 |  |  | 10/25/2025 16:47:39 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000608 | PCM-20251025-00001296 | TT-20251025-01357 | Telecom | Region_4 | TAF1M8995 | TAF2995 |  |  |  | Rashid Shafique | 10/25/2025 15:44:27 | 10/25/2025 15:44:27 | 10/25/2025 21:44:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF1M8995-P3-CA-L800 @ Sceco | 10/25/2025 15:43:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:43:26 | P3 | 4G | taif | Sceco | 5G_Cell SA | TAF1M8995 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:44:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000610 | PCM-20251025-00001298 | TT-20251025-01359 | Telecom | Region_6 | ABH1M7361 | ABH0361 | Equipment | BSS_HW_fault | Replace RF Module | Amir Sohail | 10/25/2025 15:45:28 | 10/25/2025 18:01:19 | 10/26/2025 03:45:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH1M7361-CA-L800-SBTS-P3 @ Sceco | 10/25/2025 15:44:25 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:44:15 | P3 | 4G | abha | Sceco | 5G_Cell SA | ABH1M7361 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:45:28 | 10/25/2025 15:50:17 | 10/25/2025 15:50:26 | 10/25/2025 15:50:29 | 10/25/2025 16:13:24 | 10/25/2025 18:01:19 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000611 | PCM-20251025-00001299 | TT-20251025-01360 | Reference_EM | Region_3 | YBDB9002 | YBDB9002 | Enviroment | SCECO_Failure | SCECO auto restored | Sayed Satoor | 10/25/2025 15:45:59 | 10/25/2025 16:47:20 | 10/26/2025 03:45:59 | Mains Failure at YBDB9002-P3 @ Sceco | 10/25/2025 15:36:09 | Minor | 65109 | Mains Failure | 10/25/2025 15:36:05 | P3 | Repeater | yanbu | Sceco | 2G NSA | YBDB9002 | FLM_EM | [8 empty] | API | 10/25/2025 15:45:59 | 10/25/2025 16:43:47 | 10/25/2025 16:47:05 |  |  | 10/25/2025 16:47:20 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000612 | PCM-20251025-00001300 | TT-20251025-01361 | Telecom | Region_1 | JBL0468 | JBL0468 |  |  |  | Tahir Mahmood Hafiz Yar | 10/25/2025 15:46:00 | 10/25/2025 16:18:29 | 10/26/2025 03:46:00 | RF Unit Maintenance Link Failure at JBL0468-P2_SRAN @ Sceco | 10/25/2025 15:42:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 15:40:48 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0468 | FLM_TE | [8 empty] | API | 10/25/2025 15:46:00 | 10/25/2025 16:18:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000613 | PCM-20251025-00001301 | TT-20251025-01362 | Reference_EM | Region_1 | HFBD2M5012 | HFBD0012 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/25/2025 15:46:30 | 10/25/2025 15:46:30 | 10/25/2025 21:46:30 | Door opening alarm at HFBD2M5012-P1-HUB @ Generator_SG | 10/25/2025 15:46:09 | Major | 65101 | Door opening alarm | 10/25/2025 15:46:05 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5012 | FLM_EM | [8 empty] | API | 10/25/2025 15:46:30 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000614 | PCM-20251025-00001306 | TT-20251025-01368 | Reference_EM | Region_3 | MDN2348 | MDN2348 |  |  |  | Zarshad Ali Hassan Gul | 10/25/2025 15:48:34 | 10/25/2025 23:09:21 | 10/26/2025 03:48:34 | Door opening alarm at MDN2348-P3_SRAN @ Generator_SG | 10/25/2025 15:48:10 | Minor | 65101 | Door opening alarm | 10/25/2025 15:48:05 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDN2348 | FLM_EM | [8 empty] | API | 10/25/2025 15:48:34 | 10/25/2025 23:09:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000615 | PCM-20251025-00001308 | TT-20251025-01370 | Telecom | Region_1 | JBL0468 | JBL0468 | Equipment | SFP_BTS | Replace SFP | Tahir Mahmood Hafiz Yar | 10/25/2025 15:49:06 | 10/25/2025 16:55:17 | 10/25/2025 21:49:06 | NR Cell Unavailable at JBL0468-P2_SRAN @ Sceco | 10/25/2025 15:42:23 | Major | 29841 | NR Cell Unavailable | 10/25/2025 15:40:50 | P2 | SRAN | jubail | Sceco | 5G SA | JBL0468 | FLM_TE | [8 empty] | API | 10/25/2025 15:49:06 | 10/25/2025 16:18:29 | 10/25/2025 16:19:17 | 10/25/2025 16:19:19 | 10/25/2025 16:19:23 | 10/25/2025 16:55:17 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000616 | PCM-20251025-00001310 | TT-20251025-01372 | Telecom | Region_6 | ABH1M7188 | ABH0188 | Equipment | CB_BTS | Replace CB on Rectifier | Muhammad Jamshaid Muhammad Ashraf | 10/25/2025 15:49:36 | 10/26/2025 00:51:50 | 10/25/2025 21:49:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH1M7188-P3-L800 @ Sceco | 10/25/2025 15:48:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:48:34 | P3 | 4G | abha | Sceco | 5G_Cell SA | ABH1M7188 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 15:49:36 | 10/25/2025 20:47:07 | 10/26/2025 00:51:35 |  |  | 10/26/2025 00:51:50 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000617 | PCM-20251025-00001312 | TT-20251025-01375 | Telecom | Region_1 | DAM2M8474 | DAM2474 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | AbdalHafiz Sirageldin Mohamed Yasin | 10/25/2025 15:50:56 | 10/26/2025 09:00:06 | 10/25/2025 21:50:56 | Cell Unavailable at DAM2M8474-P1-SHOP-L800 @ Sceco | 10/25/2025 15:50:15 | Major | 29240 | Cell Unavailable | 10/25/2025 15:48:42 | P1 | 4G | dammam | Sceco | LTE SA | DAM2M8474 | FLM_TE | [8 empty] | API | 10/25/2025 15:50:56 | 10/26/2025 05:03:01 | 10/26/2025 05:05:18 | 10/26/2025 05:05:22 | 10/26/2025 08:58:32 | 10/26/2025 09:00:06 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000618 | PCM-20251025-00001318 | TT-20251025-01382 | Telecom | Region_1 | DAM2474 | DAM2474 | Equipment | PMR_Power_Cable_RRU | Replace Outdoor Power Connector | Shakeel Ahmed Hafeez Ameen | 10/25/2025 15:55:48 | 10/26/2025 10:31:10 | 10/25/2025 21:55:48 | BBU CPRI Interface Error at DAM2474-P1-SHOP_SRAN @ Sceco | 10/25/2025 15:51:10 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 15:48:37 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2474 | FLM_TE | [8 empty] | API | 10/25/2025 15:55:48 | 10/25/2025 16:57:50 | 10/26/2025 10:30:57 |  |  | 10/26/2025 10:31:10 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000621 | PCM-20251025-00001323 | TT-20251025-01387 | Reference_telecom | Region_5 | MAK0755 | MAK0755 | Transsmission | MW_HW_fault | Replace FAN | Muhammad Saleem Iqbal | 10/25/2025 16:00:28 | 10/26/2025 00:06:35 | 10/26/2025 04:00:28 | FanFailure observed in MAK0755 towards 10.1.239.35 @ Sceco | 10/25/2025 04:01:36 | Minor |  | FanFailure | 10/25/2025 04:00:02 | P3 | 2G | makkah | Sceco | TX NSA | MAK0755 | FLM_TE | [8 empty] | API | 10/25/2025 16:00:28 | 10/25/2025 22:05:58 | 10/25/2025 22:29:18 | 10/25/2025 22:29:22 | 10/25/2025 22:46:57 | 10/26/2025 00:06:35 |  | Muhammad Saleem Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000622 | PCM-20251025-00001327 | TT-20251025-01391 | Reference_EM | Region_1 | HFBD2M5012 | HFBD0012 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/25/2025 16:03:03 | 10/25/2025 16:03:03 | 10/25/2025 22:03:03 | Mains Failure at HFBD2M5012-P1-HUB @ Generator_SG | 10/25/2025 15:53:01 | Major | 65109 | Mains Failure | 10/25/2025 15:52:57 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5012 | FLM_EM | [8 empty] | API | 10/25/2025 16:03:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000623 | PCM-20251025-00001329 | TT-20251025-01300 | Telecom | Region_4 | JED1MN2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 16:04:34 | 10/25/2025 16:04:34 | 10/25/2025 20:04:34 | BASE STATION HARDWARE PROBLEM (SFP Transceiver temperature too high) at JED1MN2979-NR2.6-P1-VIP @ Generator_SG | 10/25/2025 15:06:38 | Critical | 7100 | BASE STATION HARDWARE PROBLEM | 10/25/2025 15:06:28 | VIP | 5G | jeddah | Generator_SG | 5G NSA | JED1MN2979 | FLM_TE |  |  | PCM-20251025-00001247 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 16:04:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000624 | PCM-20251025-00001330 | TT-20251025-01393 | Telecom | Region_4 | JED1M8859 | JED2859 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 16:04:36 | 10/25/2025 16:04:36 | 10/25/2025 22:04:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8859-P3-CA-L800 @ Sceco | 10/25/2025 16:03:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 16:03:32 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8859 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 16:04:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000626 | PCM-20251025-00001334 | TT-20251025-01332 | Reference_telecom | Region_4 | JED1M8256 | JED2256 |  |  |  | Nazeer Mohammed | 10/25/2025 16:05:39 | 10/25/2025 17:00:12 | 10/25/2025 22:05:39 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1M8256-CA-L800-P1-VIP-SBTS @ Generator_SG | 10/25/2025 11:32:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:32:10 | VIP | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8256 | FLM_TE |  |  | PCM-20251025-00001279 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/25/2025 16:05:39 | 10/25/2025 17:00:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000628 | PCM-20251025-00001337 | TT-20251025-01398 | Reference_EM | Region_3 | HNK2274 | HNK2274 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/25/2025 16:06:40 | 10/25/2025 16:06:40 | 10/26/2025 04:06:40 | Mains Failure at HNK2274-P3-USF_SRAN @ Generator_SG | 10/25/2025 15:56:35 | Minor | 65109 | Mains Failure | 10/25/2025 15:56:30 | P3 | SRAN | madinah | Generator_SG | 2G NSA | HNK2274 | FLM_EM | [8 empty] | API | 10/25/2025 16:06:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000629 | PCM-20251025-00001338 | TT-20251025-01292 | Reference_telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 16:06:41 | 10/25/2025 18:51:01 | 10/26/2025 04:06:41 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/25/2025 15:05:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:05:38 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251025-00001240 | Please check RSSI at the site | Please check RSSI at the site |  |  |  | API | 10/25/2025 16:06:41 | 10/25/2025 18:51:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000630 | PCM-20251025-00001339 | TT-20251023-00571 | Reference_telecom | Region_4 | JED6058 | JED6058 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 16:08:06 | 10/25/2025 16:08:06 | 10/25/2025 22:08:06 | BCCH MISSING at JED6058-P3 (REF_TT-20251023-00315) @ Sceco | 10/23/2025 03:27:35 | Major | 7767 | BCCH MISSING | 10/23/2025 03:27:31 | P3 | 2G | jeddah | Sceco | 2G_Cell SA | JED6058 | FLM_TE |  |  | PCM-20251025-00000958 | Please check the site locally | Please check the site locally |  |  |  | API | 10/25/2025 16:08:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000632 | PCM-20251025-00001341 | TT-20251023-00567 | Reference_telecom | Region_4 | JED6175 | JED6075 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 16:09:00 | 10/25/2025 16:09:00 | 10/25/2025 22:09:00 | BCCH MISSING at JED6175-P3 (REF_TT-20251023-00337) @ Sceco | 10/23/2025 03:33:20 | Major | 7767 | BCCH MISSING | 10/23/2025 03:33:16 | P3 | 2G | jeddah | Sceco | 2G_Cell SA | JED6175 | FLM_TE |  |  | PCM-20251025-00000963 | Please check the site locally | Please check the site locally |  |  |  | API | 10/25/2025 16:09:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000633 | PCM-20251025-00001343 | TT-20251025-01341 | Telecom | Region_4 | JDRS0758 | JDRS0758 |  |  |  | Khizer Hayat | 10/25/2025 16:09:32 | 10/26/2025 08:36:45 | 10/25/2025 22:09:32 | 1(2G) site down under JED2619-P3 @ Sceco | 10/25/2025 15:32:43 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 15:32:39 | P3 | 2G | jeddah | Generator_DG | 2G_5G SA | JDRS0758-GSM-P3-USF 5G,JED2619-P3 2G | FLM_TE | JDRS0758 | Scattered sites: JDRS0758 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED2619 observing LOS TO AIRSCALE Kindly update TT under EM, FLM | PCM-20251025-00001293 | No Power Issue | No Power Issue |  | site down |  | API | 10/25/2025 16:09:32 | 10/26/2025 08:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000635 | PCM-20251025-00001350 | TT-20251019-02105 | MW_HC | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/25/2025 16:12:24 | 10/25/2025 16:13:43 | 10/26/2025 04:12:24 | NEC MW HC_P1 Observing Performance Issue at DMH0104(10.159.105.138)--DMH0606(10.159.105.140) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104(10.159.105.138)--DMH0606(10.159.105.140) | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251025-00001315 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/25/2025 16:12:24 | 10/25/2025 16:13:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000636 | PCM-20251025-00001352 | TT-20251025-01411 | EM | Region_6 | TNM1M8221 | TNM2221 |  |  |  | Zia Ur Rahamn | 10/25/2025 16:13:54 | 10/26/2025 07:35:59 | 10/26/2025 04:13:54 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at TNM1M8221-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/25/2025 16:05:47 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/25/2025 16:05:40 | P3 | 4G | mohail | Generator_SG | LTE NSA | TNM1M8221 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/25/2025 16:13:54 | 10/26/2025 07:35:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000638 | PCM-20251025-00001356 | TT-20251008-02013 | MW_HC | Region_3 | WHAL0002 | WHAL0002 |  |  |  | Mazin Meshary AlEnzi | 10/25/2025 16:15:53 | 10/25/2025 17:43:31 | 10/26/2025 04:15:53 | Nokia MW HC_P2 Observing Performance Issue at WHAL0002-HAL0117 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | WIFI | hail | Sceco | TX NSA | WHAL0002-HAL0117 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251025-00001354 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/25/2025 16:15:53 | 10/25/2025 17:43:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000641 | PCM-20251025-00001360 | TT-20251025-01417 | Telecom | Region_6 | KMS1M7050 | KMS0050 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/25/2025 16:18:01 | 10/25/2025 23:07:40 | 10/26/2025 04:18:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS1M7050-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/25/2025 16:17:26 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 16:17:22 | P3 | 4G | khamis mushyet | Sceco | 5G_Cell SA | KMS1M7050 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 16:18:01 | 10/25/2025 17:53:09 | 10/25/2025 20:16:57 | 10/25/2025 20:17:00 | 10/25/2025 21:25:39 | 10/25/2025 23:07:40 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000642 | PCM-20251025-00001361 | TT-20251025-00177 | Telecom | Region_4 | JED1MN0007 | JED0007 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 16:18:09 | 10/25/2025 18:51:02 | 10/25/2025 22:18:09 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1MN0007-NR2.6-P2 @ Sceco | 10/25/2025 03:03:42 | Major | 7114 | CELL SERVICE PROBLEM | 10/25/2025 03:03:31 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0007 | FLM_TE |  |  | PCM-20251025-00000159 | Alarm is cleared, please close as HW stuck | Alarm is cleared, please close as HW stuck |  |  |  | API | 10/25/2025 16:18:09 | 10/25/2025 18:51:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000646 | PCM-20251025-00001374 | TT-20251025-01424 | EM | [7 empty] | 10/25/2025 16:25:03 | 10/25/2025 16:25:03 | 10/25/2025 22:25:03 | 1(2G/LTE) sites down under MDN2352-P3-CAP/R3_MD_HWBSC01 @ Sceco | 10/25/2025 16:16:38 | Major | 21825 | CSL Fault | 10/25/2025 16:16:34 | P3 | 2G |  | Sceco | 2G_LTE SA | MDN2352-P3-CAP | FLM_EM | MDN2352 | Results: DOWN SITE HUB MDN2352-P3-CAP MDN2352 Summary: Hub: MDN2352, Down Count: 1, Down Sites: MDN2352-P3-CAP Alarm Summary: MDN2352 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 16:25:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000647 | PCM-20251025-00001381 | TT-20251025-01433 | Telecom | Region_4 | KHY1M3227 | KHY0227 |  |  |  | Khizer Hayat | 10/25/2025 16:31:00 | 10/26/2025 08:36:45 | 10/25/2025 22:31:00 | 1(3G) sites down under KHY0227-P2-USF/KHY1M3227-P2-USF @ Generator_SG | 10/25/2025 16:23:18 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/25/2025 16:22:37 | P2 | 3G | jeddah | Generator_SG | 3G SA | KHY0227-P2-USF | FLM_TE | KHY0227 | Results: DOWN SITE HUB KHY0227-P2-USF KHY0227 Summary: Hub: KHY0227, Down Count: 1, Down Sites: KHY0227-P2-USF Alarm Summary: KHY0227 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 16:31:00 | 10/26/2025 08:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000649 | PCM-20251025-00001387 | TT-20251025-01449 | Reference_EM | [7 empty] | 10/25/2025 16:35:04 | 10/25/2025 16:35:04 | 10/26/2025 04:35:04 | Genset not in auto mode at HLMD2456-P3-CAP_SRAN @ Generator_DG | 10/25/2025 16:24:43 | Minor | 65113 | Genset not in auto mode | 10/25/2025 16:24:39 | P3 | SRAN |  | Generator_DG | 2G NSA | HLMD2456 | FLM_EM | [8 empty] | API | 10/25/2025 16:35:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251025000651 | PCM-20251025-00001390 | TT-20251025-01423 | Telecom | [7 empty] | 10/25/2025 16:36:57 | 10/25/2025 16:36:57 | 10/25/2025 22:36:57 | 3(2G) 2(LTE) sites down under BDR2108-P3,BDR2111-900,BDR2246-P3/R3_MD_HWBSC01 @ Sceco | 10/25/2025 16:16:37 | Major | 21825 | CSL Fault | 10/25/2025 16:16:34 | P3 | Repeater |  | Sceco | 2G_LTE SA | BDR2108-P3 2G_LTE,BDR2246-P3 2G_LTE,BDR2111-900 2G | FLM_EM | RUSF9045 | Dear Team, Hub: RUSF9045 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251025-00001373 | Dear Team, Hub: RUSF9045 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: RUSF9045 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/25/2025 16:36:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000653 | PCM-20251025-00001395 | TT-20251025-01098 | EM | Region_5 | MLK0705 | MLK0705 |  |  |  | Hassan Ezzelarab Ali Mohamed | 10/25/2025 16:42:54 | 10/25/2025 16:42:54 | 10/25/2025 22:42:54 | 1(2G/3G/5G) sites down under MLK0705-P2-USF/MLK0705-P2-USF @ Generator_SG | 10/25/2025 13:31:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 13:31:07 | P2 | 2G | makkah | Generator_SG | 2G_3G SA | MLK0705-P2-USF | FLM_TE | MLK0705 | Results: DOWN SITE HUB MLK0705-P2-USF MLK0705 Summary: Hub: MLK0705, Down Count: 1, Down Sites: MLK0705-P2-USF Alarm Summary: MLK0705 No Active Alarm on HUB | PCM-20251025-00001016 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 16:42:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000654 | PCM-20251025-00001397 | TT-20251025-01459 | Reference_EM | Region_1 | JBL0478 | JBL0478 | Enviroment | Air Condition | Change Fan | Islam Elsawi Mohamed Elsawi | 10/25/2025 16:43:51 | 10/25/2025 23:24:33 | 10/26/2025 04:43:51 | Door opening alarm at JBL0478-P2_SRAN @ Generator_SG | 10/25/2025 16:43:28 | Minor | 65101 | Door opening alarm | 10/25/2025 16:39:31 | P2 | SRAN | jubail | Generator_SG | 2G NSA | JBL0478 | FLM_EM | [8 empty] | API | 10/25/2025 16:43:51 | 10/25/2025 22:21:28 | 10/25/2025 22:23:36 | 10/25/2025 22:23:39 | 10/25/2025 22:50:47 | 10/25/2025 23:24:33 |  | Islam Elsawi Mohamed Elsawi |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000655 | PCM-20251025-00001398 | TT-20251025-01460 | Telecom | Region_3 | TBK2M2642 | TBK2642 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Mehsan Bin Sayeed | 10/25/2025 16:45:09 | 10/25/2025 16:58:41 | 10/25/2025 22:45:09 | GSM Local Cell Unusable at TBK2M2642-FWA-P1-VIP @ Sceco | 10/25/2025 16:40:00 | Major | 28016 | GSM Local Cell Unusable | 10/25/2025 16:38:28 | P2 | 2G | tabouk | Sceco | 2G SA | TBK2M2642 | FLM_TE | [8 empty] | API | 10/25/2025 16:45:09 | 10/25/2025 16:57:15 | 10/25/2025 16:57:26 | 10/25/2025 16:57:28 | 10/25/2025 16:57:30 | 10/25/2025 16:58:41 |  | Mehsan Bin Sayeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000657 | PCM-20251025-00001402 | TT-20251025-01464 | Telecom | Region_6 | KHS1M7693 | KHS0693 | Equipment | BSS_HW_Stuck | Reset RRU | Ahmed Abdelaziz Hamid Abdelrahman | 10/25/2025 16:45:56 | 10/25/2025 22:14:00 | 10/26/2025 04:45:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at KHS1M7693-G9-L9-L18-SBTS-P2 @ Generator_SG | 10/25/2025 16:45:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 16:45:04 | P2 | 4G | khamis mushyet | Generator_SG | 5G_Cell SA | KHS1M7693 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 16:45:56 | 10/25/2025 17:25:30 | 10/25/2025 22:13:49 |  |  | 10/25/2025 22:14:00 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000659 | PCM-20251025-00001410 | TT-20251025-01472 | Telecom | Region_5 | MAK1U6993 | MAK6093 |  |  |  | Muhammad Sajjad | 10/25/2025 16:53:59 | 10/25/2025 16:53:59 | 10/25/2025 20:53:59 | 1(LTE) sites down under MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM @ Sceco | 10/25/2025 16:45:50 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 16:45:48 | VIP | 4G | makkah | Sceco | LTE SA | MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM | FLM_TE | MAK6093 | Results: DOWN SITE HUB MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM MAK6093 Summary: Hub: MAK6093, Down Count: 1, Down Sites: MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM Alarm Summary: MAK6093 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.248.20:8080] [URL:http://10.98.248.20:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 16:53:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000660 | PCM-20251025-00001414 | TT-20251025-00180 | Reference_telecom | Region_4 | SJED1S7018 | SJED0018 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 16:56:53 | 10/25/2025 16:56:53 | 10/25/2025 20:56:53 | BASE STATION OPERATION DEGRADED (BTS reference clock missing: GPS receiver alarm: not tracking satellites) at SJED1S7018-CA-P1-ARP-HAJJ-VIP @ Sceco | 10/25/2025 03:09:51 | Critical | 7651 | BASE STATION OPERATION DEGRADED | 10/25/2025 02:59:48 | VIP | 4G | jeddah | Sceco | LTE NSA | SJED1S7018 | FLM_TE |  |  | PCM-20251025-00000163 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/25/2025 16:56:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000661 | PCM-20251025-00001415 | TT-20251025-01483 | Telecom | Region_4 | TAF1MN0323 | TAF0323 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/25/2025 16:57:17 | 10/25/2025 21:45:59 | 10/25/2025 22:57:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF1MN0323-NR2.6-P2 @ Sceco | 10/25/2025 16:56:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 16:56:19 | P2 | 5G | taif | Sceco | 5G_Cell SA | TAF1MN0323 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 16:57:17 | 10/25/2025 21:45:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000662 | PCM-20251025-00001419 | TT-20251025-01493 | EM | [7 empty] | 10/25/2025 17:02:59 | 10/25/2025 17:02:59 | 10/26/2025 05:02:59 | NETECO: Door Open Alarm at HLMD2456 @ Generator_DG | 10/25/2025 17:02:38 | Minor | 5152 | Door Open Alarm | 10/25/2025 17:02:38 | P3 | SRAN |  | Generator_DG | 2G NSA | HLMD2456 | FLM_EM | [8 empty] | API | 10/25/2025 17:02:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251025000663 | PCM-20251025-00001420 | TT-20251025-01494 | Reference_EM | [7 empty] | 10/25/2025 17:02:59 | 10/25/2025 17:02:59 | 10/26/2025 05:02:59 | Door opening alarm at HLMD2456-P3-CAP_SRAN @ Generator_DG | 10/25/2025 17:02:44 | Minor | 65101 | Door opening alarm | 10/25/2025 17:02:40 | P3 | SRAN |  | Generator_DG | 2G NSA | HLMD2456 | FLM_EM | [8 empty] | API | 10/25/2025 17:02:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000664 | PCM-20251025-00001424 | TT-20251025-01491 | Telecom | Region_4 | JED1MN2685 | JED2685 |  |  |  | Nazeer Mohammed | 10/25/2025 17:05:29 | 10/25/2025 17:44:10 | 10/25/2025 23:05:29 | 1(5G) sites down under JED2685-NR2.6-P3 @ Sceco | 10/25/2025 16:57:02 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 16:56:59 | P3 | 5G | jeddah | Sceco | 5G SA | JED2685-NR2.6-P3 | FLM_TE | JED2685 | Results: DOWN SITE HUB JED2685-NR2.6-P3 JED2685 Summary: Hub: JED2685, Down Count: 1, Down Sites: JED2685-NR2.6-P3 Alarm Summary: JED2685 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.97.52.124:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 17:05:29 | 10/25/2025 17:44:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000665 | PCM-20251025-00001426 | TT-20251025-01501 | Reference_telecom | Region_2 | RIYB6038 | RIYB6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/25/2025 17:09:10 | 10/25/2025 23:18:00 | 10/25/2025 23:09:10 | RF Unit VSWR Threshold Crossed at RIYB6038-P3_SRAN @ Sceco | 10/25/2025 14:08:58 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/25/2025 14:08:46 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6038 | FLM_TE | [8 empty] | API | 10/25/2025 17:09:10 | 10/25/2025 23:18:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000669 | PCM-20251025-00001440 | TT-20251025-01515 | EM | Region_6 | AQQ1M8431 | AQQ2431 |  |  |  | Sohail Nasir Mir Afzal | 10/25/2025 17:17:26 | 10/25/2025 21:20:59 | 10/26/2025 05:17:26 | RECTIFIER MODULE FAILURE at AQQ1M8431-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/25/2025 17:09:00 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/25/2025 17:08:53 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8431 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/25/2025 17:17:26 | 10/25/2025 21:20:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251025000670 | PCM-20251025-00001447 | TT-20251025-01504 | Reference_telecom | Region_2 | RIY2M8440 | RIY2440 |  |  |  | Waseem Shahzad Ghulam Rasool | 10/25/2025 17:19:55 | 10/26/2025 10:47:35 | 10/26/2025 05:19:55 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8440-P3-L800 @ Sceco | 10/25/2025 14:10:05 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 14:10:04 | P3 | 4G | riyadh | Sceco | 2G NSA | RIY2M8440 | FLM_TE |  |  | PCM-20251025-00001428 | Need FLM to make RF path HC for RRU 121 | Need FLM to make RF path HC for RRU 121 |  |  |  | API | 10/25/2025 17:19:55 | 10/26/2025 10:23:04 | 10/26/2025 10:47:26 | 10/26/2025 10:47:28 | 10/26/2025 10:47:35 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000672 | PCM-20251025-00001448 | TT-20251025-01520 | EM | Region_3 | MDHL9054 | MDHL9054 |  |  |  | Sami Mohammed Jad Shahatah | 10/25/2025 17:20:01 | 10/25/2025 17:20:01 | 10/25/2025 21:20:01 | INTRUDER Alarm (Input-1) at MDHL9054-MDHL0384 on 10.21.222.210 @ Generator_DG | 10/25/2025 17:15:41 | Critical | INTRUDER Alarm (Input-1) | INTRUDER Alarm (Input-1) | 10/25/2025 17:14:31 | P3 | Repeater | hail | Generator_DG | TX NSA | MDHL9054 | FLM_EM | [8 empty] | API | 10/25/2025 17:20:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000674 | PCM-20251025-00001451 | TT-20251025-01523 | Reference_telecom | Region_5 | MAK0676 | MAK0676 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 17:22:37 | 10/25/2025 17:22:37 | 10/26/2025 05:22:37 | FanFailure observed in MAK0676 towards 10.10.149.34 @ Sceco | 10/25/2025 05:23:40 | Minor |  | FanFailure | 10/25/2025 05:22:29 | P3 | 2G | makkah | Sceco | TX NSA | MAK0676 | FLM_TE | [8 empty] | API | 10/25/2025 17:22:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000676 | PCM-20251025-00001454 | TT-20251025-01524 | Telecom | Region_5 | MAK1M9028 | MAK0028 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/25/2025 17:23:07 | 10/25/2025 17:23:07 | 10/25/2025 23:23:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9028-P2-CA-L800 @ Sceco | 10/25/2025 17:22:31 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 17:22:24 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9028 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 17:23:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000677 | PCM-20251025-00001458 | TT-20251025-01530 | Telecom | Region_4 | JED0914 | JED0914 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 17:26:44 | 10/25/2025 17:26:44 | 10/26/2025 05:26:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0914-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 17:25:50 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 17:25:38 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0914 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 17:26:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000679 | PCM-20251025-00001464 | TT-20251025-01543 | EM | Region_6 | TBL1M8328 | TBL2328 |  |  |  | Abdul Rauf Muhammad Aslam | 10/25/2025 17:30:21 | 10/26/2025 10:25:06 | 10/26/2025 05:30:21 | SHELTER DOOR OPEN at TBL1M8328-G9-L8-SBTS-P3 @ Generator_DG | 10/25/2025 17:30:09 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 17:20:46 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8328 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 17:30:21 | 10/26/2025 10:25:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000680 | PCM-20251025-00001465 | TT-20251025-01544 | Telecom | Region_4 | JED2671 | JED2671 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 17:30:52 | 10/25/2025 18:51:02 | 10/25/2025 23:30:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2671-G9-L8-L18-L21-NR2.6-P3 @ Generator_SG | 10/25/2025 17:30:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 17:29:57 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED2671 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 17:30:52 | 10/25/2025 18:51:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000681 | PCM-20251025-00001466 | TT-20251025-01545 | Telecom | Region_4 | JED0271 | JED0271 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 17:30:52 | 10/25/2025 17:31:24 | 10/26/2025 05:30:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 17:29:55 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 17:29:47 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 17:30:52 | 10/25/2025 17:31:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251025000683 | PCM-20251025-00001469 | TT-20251025-01547 | Reference_EM | [7 empty] | 10/25/2025 17:32:57 | 10/25/2025 17:32:57 | 10/26/2025 05:32:57 | Door opening alarm at AWJ2395-P3_SRAN @ Generator_SG | 10/25/2025 17:32:49 | Minor | 65101 | Door opening alarm | 10/25/2025 17:32:44 | P3 | SRAN |  | Generator_SG | 2G NSA | AWJ2395 | FLM_EM | [8 empty] | API | 10/25/2025 17:32:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000685 | PCM-20251025-00001475 | TT-20251025-01552 | Reference_EM | Region_1 | JDNR2M5771 | JDNR0771 |  |  |  | Muhammed Asif Riaz Riaz Hussain Akhgar | 10/25/2025 17:35:32 | 10/25/2025 17:35:32 | 10/26/2025 05:35:32 | Door opening alarm at JDNR2M5771-P2 @ Generator_SG | 10/25/2025 17:35:11 | Minor | 65101 | Door opening alarm | 10/25/2025 17:35:07 | P2 | 2G | dammam | Generator_SG | 2G NSA | JDNR2M5771 | FLM_EM | [8 empty] | API | 10/25/2025 17:35:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000686 | PCM-20251025-00001479 | TT-20251025-01554 | Reference_EM | Region_3 | WFR2279 | WFR2279 |  |  |  | Walid Mohamad Fazil | 10/25/2025 17:36:33 | 10/25/2025 17:36:33 | 10/26/2025 05:36:33 | Mains Failure at WFR2279-P3_SRAN @ Generator_SG | 10/25/2025 17:26:25 | Minor | 65109 | Mains Failure | 10/25/2025 17:26:20 | P3 | SRAN | madinah | Generator_SG | 2G NSA | WFR2279 | FLM_EM | [8 empty] | API | 10/25/2025 17:36:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000687 | PCM-20251025-00001480 | TT-20251025-01555 | Telecom | Region_4 | JED-BDR-02 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/25/2025 17:37:05 | 10/25/2025 17:37:05 | 10/26/2025 05:37:05 | Bad Package Error Rising at JED-BDR-02 @ Sceco_STB | 10/25/2025 17:36:32 | Minor | 101-2501403 | Bad Package Error Rising | 10/25/2025 17:36:23 | P1 | IPBB | jeddah | Sceco_STB | IPRAN NSA | JED-BDR-02 | FLM_TE | [8 empty] | API | 10/25/2025 17:37:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000690 | PCM-20251025-00001488 | TT-20251025-01559 | EM | Region_3 | MDQS2437 | MDQS2437 |  |  |  | Ayman Mohamed Sayed Ahmed | 10/25/2025 17:42:14 | 10/26/2025 04:12:37 | 10/26/2025 05:42:14 | NETECO: Water Alarm at MDQS2437 @ Generator_DG | 10/25/2025 17:35:48 | Minor | 5250 | Water Alarm | 10/25/2025 17:35:48 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2437 | FLM_EM | [8 empty] | API | 10/25/2025 17:42:14 | 10/26/2025 04:12:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000692 | PCM-20251025-00001501 | TT-20251025-01299 | Telecom | Region_4 | JDRS0758 | JDRS0758 |  |  |  | Khizer Hayat | 10/25/2025 17:46:25 | 10/26/2025 08:36:46 | 10/25/2025 19:46:25 | 14(2G) 2(LTE) 1(5G) sites down under JDRS0759-L800-CA-P3 | 10/25/2025 15:10:29 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/25/2025 15:10:25 | P3 | 2G | jeddah | Generator_DG | 2G_LTE SA | JDRS0759-L800-CA-P3 LTE,MAS0653-P1-DIA-CA-L800 LTE,MAS0033-GSM-UMTS-P2-USF 5G,JED2178-P3 2G | FLM_TE | JDRS0758 | Hub: JDRS0758 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED2178 scattered site observing LOS TO AIRSCALE Kindly update TT under EM, FLM | PCM-20251025-00001496 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 17:46:25 | 10/26/2025 08:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000693 | PCM-20251025-00001502 | TT-20251025-01561 | Telecom | Region_4 | JED2671 | JED2671 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 17:47:59 | 10/25/2025 18:51:03 | 10/25/2025 23:47:59 | 1(2G) sites down under JED2671-P3/JED2671-P3 @ Generator_SG | 10/25/2025 17:39:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 17:39:29 | P3 | 2G | jeddah | Generator_SG | 2G SA | JED2671-P3 | FLM_TE | JED2671 | Results: DOWN SITE HUB JED2671-P3 JED2671 Summary: Hub: JED2671, Down Count: 1, Down Sites: JED2671-P3 Alarm Summary: JED2671 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 17:47:59 | 10/25/2025 18:51:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000694 | PCM-20251025-00001504 | TT-20251025-01575 | Telecom | Region_1 | DAM2M7648 | DAM0648 | Equipment | BSS_HW_Stuck | Reset RRU | Shakeel Ahmed Hafeez Ameen | 10/25/2025 17:50:54 | 10/25/2025 20:15:20 | 10/25/2025 23:50:54 | Cell Unavailable at DAM2M7648-FWA-P1-VIP-L800 @ Sceco | 10/25/2025 17:47:47 | Major | 29240 | Cell Unavailable | 10/25/2025 17:46:15 | P2 | 4G | dammam | Sceco | LTE SA | DAM2M7648 | FLM_TE | [8 empty] | API | 10/25/2025 17:50:54 | 10/25/2025 18:57:48 | 10/25/2025 20:15:12 |  |  | 10/25/2025 20:15:20 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000695 | PCM-20251025-00001508 | TT-20251025-01572 | Telecom | Region_2 | SRIY0230 | SRIY0230 | Enviroment | SCECO_Failure | SCECO auto restored | DILSHAD ALI ABDUL HAMEED | 10/25/2025 17:53:00 | 10/26/2025 07:20:05 | 10/25/2025 21:53:00 | 2(3G) sites down under SRIY0230-P3,SRIY0231-P1-DIA/RY1RNCH05 @ Sceco | 10/25/2025 17:43:25 | Critical | 22214 | NodeB Unavailable | 10/25/2025 17:43:24 | P3 | SRAN | riyadh | Sceco | 3G SA | SRIY0231-P1-DIA 3G,SRIY0230-P3 3G | FLM_EM | SRIY0230 | Dear Team, Hub: SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251025-00001505 | Dear Team, Hub: SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/25/2025 17:53:00 | 10/26/2025 07:18:42 | 10/26/2025 07:19:36 |  |  | 10/26/2025 07:20:05 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000696 | PCM-20251025-00001509 | TT-20251025-01578 | Telecom | Region_1 | DAM0648 | DAM0648 | Equipment | BSS_HW_Stuck | Reset RRU | Shakeel Ahmed Hafeez Ameen | 10/25/2025 17:53:05 | 10/25/2025 20:15:01 | 10/25/2025 23:53:05 | BBU CPRI Interface Error at DAM0648-FWA-P1-VIP_SRAN @ Sceco | 10/25/2025 17:48:27 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 17:45:55 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0648 | FLM_TE | [8 empty] | API | 10/25/2025 17:53:05 | 10/25/2025 18:57:49 | 10/25/2025 20:14:36 |  |  | 10/25/2025 20:15:01 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000697 | PCM-20251025-00001513 | TT-20251025-01582 | Telecom | Region_3 | YNB2M7291 | YNB0291 |  |  |  | Muhammad Sajjad R3 | 10/25/2025 17:53:45 | 10/25/2025 17:53:45 | 10/25/2025 23:53:45 | Cell Unavailable at YNB2M7291-P2 @ Generator_SG | 10/25/2025 17:53:26 | Major | 29240 | Cell Unavailable | 10/25/2025 17:53:22 | P2 | 4G | yanbu | Generator_SG | LTE SA | YNB2M7291 | FLM_TE | [8 empty] | API | 10/25/2025 17:53:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000699 | PCM-20251025-00001517 | TT-20251025-01584 | EM | Region_1 | R1_DM_HWBSC01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/25/2025 17:56:11 | 10/26/2025 10:11:52 | 10/25/2025 21:56:11 | Gen set running(SH1) at R1_DM_HWBSC01 @ Sceco_STB | 10/25/2025 17:55:49 | Critical | 65344 | Gen set running(SH1) | 10/25/2025 17:55:44 | P1 | BSC | dammam | Sceco_STB | 2G NSA | R1_DM_HWBSC01 | FLM_EM | [8 empty] | API | 10/25/2025 17:56:11 | 10/26/2025 10:11:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000706 | PCM-20251025-00001527 | TT-20251025-00804 | Reference_telecom | Region_3 | MDHL2M5381 | MDHL0381 |  |  |  | Mohamed Naveed | 10/25/2025 18:09:14 | 10/25/2025 18:59:47 | 10/26/2025 06:09:14 | External Clock Reference Problem at MDHL2M5381-P1-HUB @ Sceco_STB | 10/25/2025 08:10:04 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 08:09:40 | P1 | 2G | hail | Sceco_STB | 2G NSA | MDHL2M5381 | FLM_TE |  |  | PCM-20251025-00001000 | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/25/2025 18:09:14 | 10/25/2025 18:59:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000707 | PCM-20251025-00001528 | TT-20251025-00786 | Reference_telecom | Region_3 | MDHL2M5382 | MDHL0382 |  |  |  | Mohamed Naveed | 10/25/2025 18:09:30 | 10/25/2025 18:59:47 | 10/26/2025 06:09:30 | External Clock Reference Problem at MDHL2M5382-P1-HUB @ Sceco_STB | 10/25/2025 07:59:25 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 07:56:01 | P1 | 2G | hail | Sceco_STB | 2G NSA | MDHL2M5382 | FLM_TE |  |  | PCM-20251025-00000996 | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on MDHL9054-MDHL0385 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/25/2025 18:09:30 | 10/25/2025 18:59:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000708 | PCM-20251025-00001531 | TT-20251025-01043 | Telecom | Region_3 | HLV2M2198 | HLV2198 |  |  |  | Mazin Meshary AlEnzi | 10/25/2025 18:12:04 | 10/25/2025 19:38:46 | 10/26/2025 06:12:04 | MAC Excessive Frame Error Rate at HLV2M2198-P1-HUB @ Sceco_STB | 10/25/2025 13:11:46 | Minor | 25881 | MAC Excessive Frame Error Rate | 10/25/2025 13:11:20 | P1 | 2G | hail | Sceco_STB | 2G NSA | HLV2M2198 | FLM_TE |  |  | PCM-20251025-00000953 | plz check B2B with SRAN port | plz check B2B with SRAN port |  |  |  | API | 10/25/2025 18:12:04 | 10/25/2025 19:38:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000709 | PCM-20251025-00001532 | TT-20251025-01597 | Telecom | Region_6 | ARF0186 | ARF0186 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/25/2025 18:12:12 | 10/25/2025 23:05:40 | 10/26/2025 06:12:12 | BASE STATION SERVICE PROBLEM (No connection to unit) at ARF0186-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 18:11:30 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 18:11:21 | P2 | 2G | al harja | Sceco | 5G_Cell SA | ARF0186 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 18:12:12 | 10/25/2025 20:19:58 | 10/25/2025 23:04:22 | 10/25/2025 23:04:25 |  | 10/25/2025 23:05:40 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000710 | PCM-20251025-00001533 | TT-20251025-01598 | EM | Region_3 | MDN2366 | MDN2366 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/25/2025 18:12:43 | 10/25/2025 18:12:43 | 10/26/2025 06:12:43 | NETECO: Door Status Sensor Alarm at MDN2366 @ Sceco | 10/25/2025 18:12:36 | Minor | 5152 | Door Status Sensor Alarm | 10/25/2025 18:12:36 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2366 | FLM_EM | [8 empty] | API | 10/25/2025 18:12:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000711 | PCM-20251025-00001534 | TT-20251025-01599 | Reference_EM | Region_3 | MDN2366 | MDN2366 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/25/2025 18:13:14 | 10/25/2025 18:13:14 | 10/26/2025 06:13:14 | Door opening alarm at MDN2366-P3_SRAN @ Sceco | 10/25/2025 18:12:45 | Minor | 65101 | Door opening alarm | 10/25/2025 18:12:39 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2366 | FLM_EM | [8 empty] | API | 10/25/2025 18:13:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000712 | PCM-20251025-00001537 | TT-20251025-01595 | EM | Region_6 | RYAB1M3648 | RYAB0648 |  |  |  | Amir Arif Ali | 10/25/2025 18:15:59 | 10/25/2025 18:15:59 | 10/25/2025 22:15:59 | 1(3G/5G) sites down under RYAB0648-P1-HUB-USF/RYAB1M3648-P1-HUB-USF @ Sceco_STB | 10/25/2025 18:08:23 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/25/2025 18:07:45 | P1 | 3G | turaib | Sceco_STB | 3G_5G SA | RYAB0648-P1-HUB-USF | FLM_EM | RYAB0648 | Results: DOWN SITE HUB RYAB0648-P1-HUB-USF RYAB0648 Summary: Hub: RYAB0648, Down Count: 1, Down Sites: RYAB0648-P1-HUB-USF Alarm Summary: RYAB0648 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 18:15:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000713 | PCM-20251025-00001540 | TT-20251025-01618 | Telecom | Region_5 | MAK0721 | MAK0721 | Equipment | CB_BTS | Replace CB on Rectifier | Amjad Ali Muhammad Parves | 10/25/2025 18:18:24 | 10/26/2025 10:29:21 | 10/26/2025 06:18:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0721-G9-L8-L18-L21-NR2.6-SBTS-P2-NEW @ Generator_SG | 10/25/2025 18:17:44 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 18:17:39 | P2 | 2G | makkah | Generator_SG | 5G_Cell SA | MAK0721 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 18:18:24 | 10/25/2025 18:30:30 | 10/25/2025 18:32:49 | 10/25/2025 18:32:52 | 10/25/2025 20:35:16 | 10/26/2025 10:29:21 |  | Amjad Ali Muhammad Parves |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000714 | PCM-20251025-00001541 | TT-20251025-01620 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/25/2025 18:18:55 | 10/25/2025 23:18:01 | 10/26/2025 00:18:55 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/25/2025 15:18:51 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/25/2025 15:18:39 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/25/2025 18:18:55 | 10/25/2025 23:18:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000715 | PCM-20251025-00001543 | TT-20251025-01623 | Telecom | Region_4 | JED0413 | JED0413 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 18:20:29 | 10/25/2025 18:20:29 | 10/26/2025 06:20:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0413-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 18:19:54 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 18:19:50 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0413 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 18:20:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251025000716 | PCM-20251025-00001544 | TT-20251025-01615 | EM | Region_1 | JBRK2M1914 | JBRK0914 |  |  |  | Dileesh Muringothil Devarajan | 10/25/2025 18:20:59 | 10/25/2025 20:12:52 | 10/26/2025 00:20:59 | 1(2G/3G/LTE) sites down under JBRK0914-P2/R1_JB_HWBSC01 @ Sceco | 10/25/2025 18:14:08 | Major | 21825 | CSL Fault | 10/25/2025 18:14:06 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | JBRK0914-P2 | FLM_EM | JBRK0914 | Results: DOWN SITE HUB JBRK0914-P2 JBRK0914 Summary: Hub: JBRK0914, Down Count: 1, Down Sites: JBRK0914-P2 Alarm Summary: JBRK0914 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 18:20:59 | 10/25/2025 20:12:24 | 10/25/2025 20:12:29 | 10/25/2025 20:12:34 | 10/25/2025 20:12:52 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000717 | PCM-20251025-00001547 | TT-20251025-01621 | Telecom | Region_2 | RAS0761 | RAS0761 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/25/2025 18:23:59 | 10/25/2025 18:37:17 | 10/26/2025 00:23:59 | 1(5G) sites down under RAS0761-P3_SRAN @ Sceco | 10/25/2025 18:15:56 | Major | 29840 | gNodeB Out of Service | 10/25/2025 18:15:30 | P3 | SRAN | al rass | Sceco | 5G SA | RAS0761-P3_SRAN | FLM_TE | RAS0761 | Results: DOWN SITE HUB RAS0761-P3_SRAN RAS0761 Summary: Hub: RAS0761, Down Count: 1, Down Sites: RAS0761-P3_SRAN Alarm Summary: RAS0761 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 18:23:59 | 10/25/2025 18:37:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000718 | PCM-20251025-00001549 | TT-20251025-01626 | EM | Region_5 | JDMK2406 | JDMK2406 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/25/2025 18:29:30 | 10/25/2025 18:33:31 | 10/26/2025 00:29:30 | 1(2G/LTE) sites down under JDMK2406-P3/JDMK2406-P3 @ Generator_SG | 10/25/2025 18:21:20 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 18:21:16 | P3 | 2G | makkah | Generator_SG | 2G SA | JDMK2406-P3 | FLM_TE | JDMK2406 | Results: DOWN SITE HUB JDMK2406-P3 JDMK2406 Summary: Hub: JDMK2406, Down Count: 1, Down Sites: JDMK2406-P3 Alarm Summary: JDMK2406 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/25/2025 18:29:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000719 | PCM-20251025-00001554 | TT-20251025-01636 | Telecom | Region_4 | JED1MN2417 | JED2417 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 18:38:03 | 10/25/2025 21:02:45 | 10/26/2025 00:38:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2417-NR2.6-P3 @ Sceco | 10/25/2025 18:37:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 18:37:03 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2417 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 18:38:03 | 10/25/2025 21:02:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000723 | PCM-20251025-00001562 | TT-20251025-01645 | Telecom | Region_4 | TAF0170-ZTa01-CSG-03 | TAF0170 |  |  |  | Ahmad Kamal Abdelmawla | 10/25/2025 18:55:06 | 10/26/2025 09:33:52 | 10/26/2025 06:55:06 | Bad Package Error Rising at TAF0170-ZTa01-CSG-03 @ Sceco_STB | 10/25/2025 18:54:38 | Minor | 101-2501403 | Bad Package Error Rising | 10/25/2025 18:54:32 | P2 | IPRAN | taif | Sceco_STB | IPRAN NSA | TAF0170-ZTa01-CSG-03 | FLM_TE | [8 empty] | API | 10/25/2025 18:55:06 | 10/26/2025 09:33:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000724 | PCM-20251025-00001563 | TT-20251025-01639 | Reference_telecom | Region_2 | RIY2M8295 | RIY2295 |  |  |  | Khan zeb Shah nawaz | 10/25/2025 18:55:58 | 10/26/2025 09:37:22 | 10/26/2025 06:55:58 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8295-P3-L800-CA @ Generator_SG | 10/25/2025 15:42:49 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 15:42:45 | P3 | 4G | riyadh | Generator_SG | 2G NSA | RIY2M8295 | FLM_TE |  |  | PCM-20251025-00001557 | Need FLM to make RF path HC for RRU 71 | Need FLM to make RF path HC for RRU 71 |  |  |  | API | 10/25/2025 18:55:58 | 10/26/2025 09:37:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000725 | PCM-20251025-00001564 | TT-20251025-01642 | Reference_telecom | Region_3 | MDN2M8887 | MDN2887 |  |  |  | TAUSEEF ILYAS | 10/25/2025 18:56:35 | 10/25/2025 18:56:50 | 10/26/2025 06:56:35 | Cell RX Channel Interference Noise Power Unbalanced at MDN2M8887-P2-L800 @ Sceco | 10/25/2025 15:47:39 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 15:47:35 | P2 | 4G | madinah | Sceco | 2G NSA | MDN2M8887 | FLM_TE |  |  | PCM-20251025-00001559 | Need FLM to make RF path HC for MRFU 0 4 0 | Need FLM to make RF path HC for MRFU 0 4 0 |  |  |  | API | 10/25/2025 18:56:35 | 10/25/2025 18:56:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000726 | PCM-20251025-00001566 | TT-20251025-01644 | Telecom | Region_4 | JED1M8864 | JED2864 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 18:57:29 | 10/25/2025 18:57:29 | 10/26/2025 00:57:29 | 1(LTE) sites down under JED2864-CA-L800-P3 @ Sceco | 10/25/2025 18:49:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 18:49:09 | P3 | 4G | jeddah | Sceco | LTE SA | JED2864-CA-L800-P3 | FLM_TE | JED2864 | Results: DOWN SITE HUB JED2864-CA-L800-P3 JED2864 Summary: Hub: JED2864, Down Count: 1, Down Sites: JED2864-CA-L800-P3 Alarm Summary: JED2864 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.48.12:8080] [URL:http://10.97.48.12:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 18:57:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000727 | PCM-20251025-00001567 | TT-20251025-01648 | EM | Region_3 | MDQS2430 | MDQS2430 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/25/2025 18:57:40 | 10/25/2025 18:57:40 | 10/26/2025 06:57:40 | NETECO: Genset Generator Fault at MDQS2430 @ Generator_DG | 10/25/2025 18:51:19 | Minor | 40564 | Genset Generator Fault | 10/25/2025 18:51:19 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2430 | FLM_EM | [8 empty] | API | 10/25/2025 18:57:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000728 | PCM-20251025-00001569 | TT-20251025-01649 | EM | Region_6 | SRA1M8356 | SRA2356 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/25/2025 18:58:43 | 10/25/2025 21:00:01 | 10/26/2025 06:58:43 | RECTIFIER MODULE FAILURE at SRA1M8356-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/25/2025 18:50:43 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/25/2025 18:50:35 | P3 | 4G | Albaha | Generator_SG | LTE NSA | SRA1M8356 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/25/2025 18:58:43 | 10/25/2025 21:00:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000730 | PCM-20251025-00001573 | TT-20251025-01654 | Telecom | Region_6 | KMS1M7216 | KMS0216 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/25/2025 19:03:54 | 10/25/2025 23:07:09 | 10/26/2025 01:03:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS1M7216- CA-L800-SBTS @ Sceco | 10/25/2025 19:03:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:03:11 | P3 | 4G | khamis mushyet | Sceco | 5G_Cell SA | KMS1M7216 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:03:54 | 10/25/2025 20:19:59 | 10/25/2025 23:06:30 | 10/25/2025 23:06:33 |  | 10/25/2025 23:07:09 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000736 | PCM-20251025-00001593 | TT-20251025-01674 | Telecom | Region_6 | SAB1M7096 | SAB0096 | Equipment | SFP_BTS | Replace SFP | Ansir Iqbal Muhammad Iqbal | 10/25/2025 19:21:58 | 10/25/2025 23:11:02 | 10/26/2025 01:21:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at SAB1M7096-P2-CA-L800 @ Generator_SG | 10/25/2025 19:21:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:21:01 | P2 | 4G | baish | Generator_SG | 5G_Cell SA | SAB1M7096 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:21:58 | 10/25/2025 23:07:17 | 10/25/2025 23:09:29 |  |  | 10/25/2025 23:11:02 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000737 | PCM-20251025-00001594 | TT-20251025-01675 | Telecom | Region_4 | JED0135 | JED0135 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 19:23:32 | 10/26/2025 09:43:23 | 10/26/2025 07:23:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0135-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/25/2025 19:22:33 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:22:23 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0135 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:23:32 | 10/26/2025 09:43:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000739 | PCM-20251025-00001597 | TT-20251025-01679 | Telecom | Region_6 | MKW0037 | MKW0037 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/25/2025 19:25:35 | 10/26/2025 10:53:43 | 10/26/2025 07:25:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKW0037-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 19:24:50 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:24:46 | P3 | 2G | makhwa | Sceco | 5G_Cell SA | MKW0037 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:25:35 | 10/26/2025 10:52:37 | 10/26/2025 10:53:29 |  |  | 10/26/2025 10:53:43 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000740 | PCM-20251025-00001598 | TT-20251025-01680 | Telecom | Region_4 | JED0514 | JED0514 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 19:26:06 | 10/25/2025 19:26:06 | 10/26/2025 07:26:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0514-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/25/2025 19:24:53 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:25:19 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0514 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:26:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000741 | PCM-20251025-00001599 | TT-20251025-01673 | Telecom | Region_4 | SJED1S7664 | SJED0664 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 19:26:29 | 10/25/2025 19:26:29 | 10/26/2025 01:26:29 | 1(LTE) sites down under SJED0664-CA-P3 @ Sceco | 10/25/2025 19:18:27 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 19:18:24 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0664-CA-P3 | FLM_TE | SJED0664 | Results: DOWN SITE HUB SJED0664-CA-P3 SJED0664 Summary: Hub: SJED0664, Down Count: 1, Down Sites: SJED0664-CA-P3 Alarm Summary: SJED0664 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.99.235.244:8080] [URL:http://10.99.235.244:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 19:26:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000744 | PCM-20251025-00001603 | TT-20251025-01685 | Telecom | Region_4 | JED0756 | JED0756 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/25/2025 19:28:40 | 10/26/2025 09:43:24 | 10/26/2025 07:28:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0756-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 19:27:37 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:27:28 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0756 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:28:40 | 10/26/2025 09:43:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000746 | PCM-20251025-00001605 | TT-20251025-01655 | EM | Region_4 | JED2069 | JED2069 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 19:29:56 | 10/25/2025 19:29:56 | 10/26/2025 01:29:56 | 1(2G/5G) sites down under JED2069-P3/JED2069-P3 @ Generator_SG | 10/25/2025 19:01:15 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 19:01:10 | P3 | 2G | jeddah | Generator_SG | 2G_5G SA | JED2069-P3 | FLM_TE | JED2069 | Results: DOWN SITE HUB JED2069-P3 JED2069 Summary: Hub: JED2069, Down Count: 1, Down Sites: JED2069-P3 Alarm Summary: JED2069 Alarm Active on HUB | PCM-20251025-00001577 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 19:29:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000747 | PCM-20251025-00001607 | TT-20251025-01687 | Reference_telecom | Region_4 | JED0202 | JED0202 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 19:30:45 | 10/25/2025 19:30:45 | 10/26/2025 07:30:45 | Degrade observed in JED0202 towards 10.10.150.162 @ Sceco | 10/25/2025 07:33:19 | Minor |  | Degrade | 10/25/2025 07:30:30 | P2 | 2G | jeddah | Sceco | TX NSA | JED0202 | FLM_TE | [8 empty] | API | 10/25/2025 19:30:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000749 | PCM-20251025-00001611 | TT-20251025-01695 | Reference_telecom | Region_4 | JED0097 | JED0097 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 19:36:56 | 10/25/2025 19:36:56 | 10/26/2025 07:36:56 | DemFail observed in JED0097_01 towards 10.10.150.161 @ Sceco | 10/25/2025 07:42:01 | Minor |  | DemFail | 10/25/2025 07:36:51 | P1 | 2G | jeddah | Sceco | TX NSA | JED0097 | FLM_TE | [8 empty] | API | 10/25/2025 19:36:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000751 | PCM-20251025-00001613 | TT-20251025-01697 | Telecom | Region_6 | AQQ1M7039 | AQQ0039 |  |  |  | Manzoor Ahmed | 10/25/2025 19:37:27 | 10/26/2025 10:52:37 | 10/26/2025 07:37:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at AQQ1M7039-G9-NL8-L18-NL21-SBTS-P3 @ Sceco | 10/25/2025 19:36:52 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:36:45 | P3 | 4G | Albaha | Sceco | 5G_Cell SA | AQQ1M7039 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:37:27 | 10/26/2025 10:52:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000753 | PCM-20251025-00001616 | TT-20251025-01699 | EM | Region_6 | DH-JANUB-SEC0013 | SEC0013 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/25/2025 19:41:36 | 10/25/2025 22:45:41 | 10/26/2025 01:41:36 | AMBIENT_TEMP_FLUCT ALARM AT DH-JANUB-SEC0013 | 10/25/2025 19:35:35 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/25/2025 19:35:35 | P1 | DWDM | al harja | Sceco_STB_Rental | DWDM NSA | DH-JANUB-SEC0013 | FLM_EM | [8 empty] | API | 10/25/2025 19:41:36 | 10/25/2025 19:58:05 | 10/25/2025 22:24:13 | 10/25/2025 22:24:19 | 10/25/2025 22:24:24 | 10/25/2025 22:45:41 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Stuck | CM20251025000754 | PCM-20251025-00001618 | TT-20251025-01701 | Reference_telecom | [7 empty] | 10/25/2025 19:44:10 | 10/25/2025 19:44:10 | 10/26/2025 07:44:10 | ReplaceableUnitProblem observed in TBL2284_01 towards 10.221.246.2 @ Generator_SG | 10/25/2025 07:43:45 | Minor |  | ReplaceableUnitProblem | 10/25/2025 07:43:39 | P3 | 2G |  | Generator_SG | TX NSA | TBL2284 | FLM_TE | [8 empty] | API | 10/25/2025 19:44:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000755 | PCM-20251025-00001622 | TT-20251025-01705 | Reference_telecom | Region_5 | MAK0654 | MAK0654 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 19:46:45 | 10/25/2025 19:46:45 | 10/26/2025 07:46:45 | ReplaceableUnitProblem observed in MAK0654_02 towards 10.3.227.5 @ Sceco | 10/25/2025 07:47:24 | Minor |  | ReplaceableUnitProblem | 10/25/2025 07:46:16 | P2 | 2G | makkah | Sceco | TX NSA | MAK0654 | FLM_TE | [8 empty] | API | 10/25/2025 19:46:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000757 | PCM-20251025-00001626 | TT-20251025-01713 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/25/2025 19:53:59 | 10/25/2025 19:53:59 | 10/26/2025 07:53:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/25/2025 19:53:12 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:53:01 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 19:53:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000759 | PCM-20251025-00001633 | TT-20251025-01712 | EM | Region_6 | BHAB1M3819 | BHAB0819 |  |  |  | Arif Ullah Shah | 10/25/2025 19:58:29 | 10/26/2025 02:45:53 | 10/26/2025 01:58:29 | 1(3G/LTE) sites down under BHAB0819-P3/BHAB1M3819-P3 @ Sceco | 10/25/2025 19:50:49 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/25/2025 19:50:08 | P3 | 3G | makhwa | Sceco | 3G_LTE SA | BHAB0819-P3 | FLM_EM | BHAB0819 | Results: DOWN SITE HUB BHAB0819-P3 BHAB0819 Summary: Hub: BHAB0819, Down Count: 1, Down Sites: BHAB0819-P3 Alarm Summary: BHAB0819 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 19:58:29 | 10/26/2025 02:45:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000760 | PCM-20251025-00001636 | TT-20251025-01722 | EM | Region_6 | BHAB1M7819 | BHAB0819 |  |  |  | Arif Ullah Shah | 10/25/2025 20:00:42 | 10/26/2025 02:45:53 | 10/26/2025 08:00:42 | COMMERCIAL POWER FAILURE at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/25/2025 19:54:47 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/25/2025 19:52:08 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7819 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/25/2025 20:00:42 | 10/26/2025 02:45:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000761 | PCM-20251025-00001637 | TT-20251025-01723 | Telecom | Region_4 | JED1MN0775 | JED0775 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 20:00:42 | 10/25/2025 20:00:42 | 10/26/2025 02:00:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0775-NR2.6-P2 @ Sceco | 10/25/2025 19:59:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 19:59:39 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0775 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 20:00:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000764 | PCM-20251025-00001648 | TT-20251025-00082 | MW_HC | Region_4 | RYMK9003 | RYMK9003 |  |  |  | Rashid Shafique | 10/25/2025 20:10:58 | 10/25/2025 20:10:58 | 10/26/2025 08:10:58 | As per bo request Nokia MW HC As per bo request Nokia MW HC RYMK9003-RYMK0542 as H system stuck without any alarm flapping. | 10/25/2025 01:23:59 | Minor | 113388 | LOF | 10/25/2025 01:23:56 | P1 | Repeater | taif | Generator_DG | TX NSA | RYMK9003-RYMK0542 | FLM_TE |  |  | PCM-20251025-00001344 | Please share the RCA plus start & end time of action | Please share the RCA plus start & end time of action |  |  |  | API | 10/25/2025 20:10:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000765 | PCM-20251025-00001649 | TT-20251025-01706 | Reference_telecom | Region_1 | SAK0585 | SAK0585 |  |  |  | Syed Fawad Ali | 10/25/2025 20:11:26 | 10/25/2025 21:02:34 | 10/26/2025 08:11:26 | MW Link down at DJL0553-ASG-01 To SAK0585-PE01 REF:TT-20251012-01042 | 10/25/2025 15:22:23 | Minor | 15269 | LOS | 10/25/2025 15:22:23 | P1 | SRAN | sakaka | Sceco | IPRAN NSA | MW Link down at DJL0553-ASG-01 To SAK0585-PE01 REF:TT-20251012-01042 | FLM_TE | SAK0585 | Dear Team , We observing AM_DOWNSHIFT ALARM AT SAK0974 DIR SAK0585 , kindly visit the site and check the issue | PCM-20251025-00001623 | Dear Team , We observing AM_DOWNSHIFT ALARM AT SAK0974 DIR SAK0585 , kindly visit the site and check the issue | Dear Team , We observing AM_DOWNSHIFT ALARM AT SAK0974 DIR SAK0585 , kindly visit the site and check the issue |  |  |  | API | 10/25/2025 20:11:26 | 10/25/2025 21:02:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000766 | PCM-20251025-00001650 | TT-20251025-00179 | MW_HC | Region_4 | JED0783 | JED0783 |  |  |  | BARKAT ALI MAIN HILAL | 10/25/2025 20:11:27 | 10/26/2025 10:36:43 | 10/26/2025 08:11:27 | As per bo request Nokia MW HC observing JED0783-JDJZ0761 | 10/25/2025 03:09:11 | Minor | 113388 | LOF | 10/25/2025 03:09:01 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0783-JDJZ0761 | FLM_TE | JED0783 | dear team,Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251025-00001349 | dear team,Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | dear team,Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/25/2025 20:11:27 | 10/26/2025 10:36:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000768 | PCM-20251025-00001652 | TT-20251025-00701 | Reference_telecom | Region_6 | SMT0064 | SMT0064 |  |  |  | Zeshan Ali Adnan | 10/25/2025 20:15:25 | 10/25/2025 23:06:04 | 10/26/2025 08:15:25 | LossOfSignal observed in SMT0064 towards 10.3.226.42 @ Sceco | 10/24/2025 22:17:03 | Minor |  | LossOfSignal | 10/24/2025 22:15:06 | P2 | 2G | jizan | Sceco | TX NSA | SMT0064 | FLM_TE |  |  | PCM-20251025-00001574 | Dear FLM, Approved for UBT replacement as per TS & tracking it | Dear FLM, Approved for UBT replacement as per TS & tracking it |  |  |  | API | 10/25/2025 20:15:25 | 10/25/2025 23:06:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000769 | PCM-20251025-00001653 | TT-20251023-01788 | MW_HC | Region_6 | QIS0267 | QIS0267 |  |  |  | Muhammad Ali | 10/25/2025 20:15:35 | 10/25/2025 22:26:02 | 10/26/2025 08:15:35 | As per bo request Nokia MW HC - QIS0267-QIS0031 | 10/23/2025 18:23:04 | Minor | 321339 | Demodulator Fail | 10/23/2025 18:23:02 | P3 | 2G | jizan | Sceco | TX NSA | - QIS0267-QIS0031 | FLM_TE |  | HW approved thanks to share after HC completed | PCM-20251025-00001047 | Approved | Approved |  |  |  | API | 10/25/2025 20:15:35 | 10/25/2025 22:26:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000771 | PCM-20251025-00001656 | TT-20251025-00497 | Telecom | Region_6 | DAR0916 | DAR0916 | Equipment | SFP_BTS | Replace SFP | Muhammad Ali | 10/25/2025 20:16:54 | 10/26/2025 00:30:41 | 10/26/2025 02:16:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR0916-GSM-UMTS-P2 @ Sceco | 10/25/2025 07:57:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 07:56:53 | P2 | 2G | dair | Sceco | 5G_Cell SA | DAR0916 | FLM_TE |  |  | PCM-20251025-00001515 | check locally | check locally |  |  |  | API | 10/25/2025 20:16:54 | 10/25/2025 22:26:02 | 10/26/2025 00:30:30 |  |  | 10/26/2025 00:30:41 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000772 | PCM-20251025-00001661 | TT-20251025-01737 | Telecom | Region_5 | OMQ0633 | OMQ0633 |  |  |  | Amjad Ali Muhammad Parves | 10/25/2025 20:31:11 | 10/26/2025 10:29:29 | 10/26/2025 02:31:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at OMQ0633-GSM-P2-USF @ Generator_SG | 10/25/2025 20:30:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 20:30:08 | P2 | 2G | makkah | Generator_SG | 5G_Cell SA | OMQ0633 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 20:31:11 | 10/26/2025 10:29:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000775 | PCM-20251025-00001669 | TT-20251025-01731 | Telecom | Region_4 | HBI2008 | HBI2008 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/25/2025 20:38:30 | 10/26/2025 04:38:02 | 10/26/2025 02:38:30 | 1(2G) 1(3G) 1(LTE) sites down under GMK0350-P2-USF,HBI2008-P3/HBI2008-P3 @ Generator_SG | 10/25/2025 20:16:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 20:16:43 | P3 | 2G | jeddah | Generator_SG | 2G_3G_LTE SA | HBI2008-P3 2G_LTE,GMK0350-P2-USF 3G | FLM_TE | HBI2008 | Results: DOWN SITE HUB HBI2008-P3 HBI2008 GMK0350-P2-USF GMK0350 Summary: Hub: HBI2008, Down Count: 1, Down Sites: HBI2008-P3 Hub: GMK0350, Down Count: 1, Down Sites: GMK0350-P2-USF Alarm Summary: HBI2008 No Active Alarm on HUB GMK0350 No Active Alarm on HUB | PCM-20251025-00001659 | HBI2008 | HBI2008 |  | sites down |  | API | 10/25/2025 20:38:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000776 | PCM-20251025-00001670 | TT-20251025-01748 | Telecom | Region_6 | SHF1M7273 | SHF0273 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Amir Sohail | 10/25/2025 20:40:29 | 10/26/2025 00:51:54 | 10/26/2025 08:40:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at SHF1M7273-G9-L8-L9-SBTS-P2-USF @ Sceco | 10/25/2025 20:39:34 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 20:39:24 | P2 | 4G | al harja | Sceco | 5G_Cell SA | SHF1M7273 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 20:40:29 | 10/25/2025 21:40:51 | 10/26/2025 00:51:46 |  |  | 10/26/2025 00:51:54 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000778 | PCM-20251025-00001676 | TT-20251025-01744 | EM | Region_4 | TFSH0675 | TFSH0675 |  |  |  | Walid Magdy Tawfik Elbana | 10/25/2025 20:43:59 | 10/25/2025 20:50:46 | 10/26/2025 02:43:59 | 1(2G/3G/5G) sites down under TFSH0675-P3/TFSH0675-P3 @ Sceco | 10/25/2025 20:35:52 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 20:35:50 | P3 | 2G | taif | Sceco | 2G_3G SA | TFSH0675-P3 | FLM_EM |  | Results: DOWN SITE HUB TFSH0675-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/25/2025 20:43:59 | 10/25/2025 20:50:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000780 | PCM-20251025-00001680 | TT-20251025-01757 | Telecom | Region_4 | JED0930 | JED0930 |  |  |  | Nazeer Mohammed | 10/25/2025 20:47:11 | 10/25/2025 20:47:11 | 10/26/2025 02:47:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0930-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/25/2025 20:46:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 20:46:15 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0930 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 20:47:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000781 | PCM-20251025-00001683 | TT-20251025-01739 | Telecom | Region_3 | HLV0570 | HLV0570 |  |  |  | Mohamed Naveed | 10/25/2025 20:48:44 | 10/25/2025 20:49:40 | 10/26/2025 02:48:44 | GSM Cell out of Service at HLV2M5570-P3 @ Sceco | 10/25/2025 20:32:55 | Major | 21801 | GSM Cell out of Service | 10/25/2025 20:32:52 | P3 | SRAN | hail | Sceco | 2G SA | HLV2M5570 | FLM_TE | HLV0570 | Dear FLM Team, hub site is HLV0570 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM | PCM-20251025-00001671 | Dear FLM Team, hub site is HLV0570 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM | Dear FLM Team, hub site is HLV0570 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM |  |  |  | API | 10/25/2025 20:48:44 | 10/25/2025 20:49:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251025000783 | PCM-20251025-00001693 | TT-20251025-01781 | Telecom | Region_4 | JED2126 | JED2126 |  |  |  | Mohammed Ramadan A Abu Abid | 10/25/2025 21:08:22 | 10/26/2025 09:37:27 | 10/26/2025 09:08:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/25/2025 21:07:41 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 21:07:30 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2126 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 21:08:22 | 10/25/2025 23:21:48 | 10/26/2025 09:33:42 | 10/26/2025 09:34:09 | 10/26/2025 09:37:27 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000784 | PCM-20251025-00001696 | TT-20251025-01773 | Telecom | Region_6 | BHMF0856 | BHMF0856 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/25/2025 21:12:17 | 10/25/2025 21:33:30 | 10/26/2025 01:12:17 | 9(2G) 1(LTE) sites down under BHMF0856-P3 @ Sceco | 10/25/2025 20:56:26 | Critical | 7706 | BTS O&M LINK FAILURE | 10/25/2025 20:56:18 | P3 | 2G | makhwa | Sceco | 2G_LTE SA | BHMF0856-P3 2G_LTE,MKW2368-P3 2G,QLW2352-P3 2G,MKW2039-P3-WBB-G3 2G,MKW2351-P3 2G,MKW0036-P3 2G,QLW0062-P2 2G,SRA2356-P3 2G,QLW2354-P3 2G | FLM_TE | BHMF0856 | Results: DOWN SITE HUB BHMF0856-P3 BHMF0856 MKW2368-P3 MKW2368 QLW2352-P3 QLW2352 MKW2039-P3-WBB-G3 MKW2039 MKW2351-P3 MKW2351 MKW0036-P3 Need to check QLW0062-P2 Need to check SRA2356-P3 SRA2356 QLW2354-P3 QLW2354 Summary: Hub: BHMF0856, Down Count: 1, Down Sites: BHMF0856-P3 Hub: MKW2368, Down Count: 1, Down Sites: MKW2368-P3 Hub: QLW2352, Down Count: 1, Down Sites: QLW2352-P3 Hub: MKW2039, Down Count: 1, Down Sites: MKW2039-P3-WBB-G3 Hub: MKW2351, Down Count: 1, Down Sites: MKW2351-P3 Hub: SRA2356, Down Count: 1, Down Sites: SRA2356-P3 Hub: QLW2354, Down Count: 1, Down Sites: QLW2354-P3 Alarm Summary: BHMF0856 Alarm Active on HUB MKW2368 No Active Alarm on HUB QLW2352 No Active Alarm on HUB MKW2039 No Active Alarm on HUB MKW2351 No Active Alarm on HUB HUB site not found SRA2356 No Active Alarm on HUB QLW2354 No Active Alarm on HUB | PCM-20251025-00001689 | BHMF0856 | BHMF0856 |  | sites down |  | API | 10/25/2025 21:12:17 | 10/25/2025 21:32:55 | 10/25/2025 21:33:19 |  |  | 10/25/2025 21:33:30 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000785 | PCM-20251025-00001697 | TT-20251025-01780 | EM | Region_1 | JBRK2M3924 | JBRK0924 |  |  |  | Rafiq Ahmed Elturifi | 10/25/2025 21:12:30 | 10/26/2025 09:36:26 | 10/26/2025 03:12:30 | 1(3G/LTE) sites down under JBRK0924-P2/JB1RNCH01 @ Sceco | 10/25/2025 21:04:09 | Major | 22214 | NodeB Unavailable | 10/25/2025 21:04:05 | P2 | 3G | jubail | Sceco | 3G SA | JBRK0924-P2 | FLM_TE | JBRK0924 | Results: DOWN SITE HUB JBRK0924-P2 JBRK0924 Summary: Hub: JBRK0924, Down Count: 1, Down Sites: JBRK0924-P2 Alarm Summary: JBRK0924 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 21:12:30 | 10/26/2025 09:36:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000786 | PCM-20251025-00001707 | TT-20251020-00429 | Reference_telecom | Region_5 | MAK0686 | MAK0686 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/25/2025 21:17:29 | 10/25/2025 21:17:29 | 10/26/2025 09:17:29 | ReplaceableUnitProblem observed in MAK0686 towards 10.10.143.200 @ Sceco | 10/19/2025 16:51:20 | Minor |  | ReplaceableUnitProblem | 10/19/2025 16:50:32 | P2 | 2G | makkah | Sceco | TX NSA | MAK0686 | FLM_TE |  |  | PCM-20251025-00001663 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/25/2025 21:17:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000788 | PCM-20251025-00001723 | TT-20251025-01802 | Telecom | Region_1 | ABQ2M4889 | ABQ2889 |  |  |  | Imran Ali Yousaf | 10/25/2025 21:25:00 | 10/26/2025 01:09:13 | 10/26/2025 03:25:00 | 1(3G) sites down under ABQ2889-P2/HF1RNCH01 @ Sceco | 10/25/2025 21:16:34 | Major | 22214 | NodeB Unavailable | 10/25/2025 21:16:31 | P2 | 3G | dammam | Sceco | 3G SA | ABQ2889-P2 | FLM_TE | ABQ2889 | Results: DOWN SITE HUB ABQ2889-P2 ABQ2889 Summary: Hub: ABQ2889, Down Count: 1, Down Sites: ABQ2889-P2 Alarm Summary: ABQ2889 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 21:25:00 | 10/26/2025 01:09:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000789 | PCM-20251025-00001729 | TT-20251025-01779 | Reference_telecom | Region_1 | KBR2U6710 | KBR6010 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 21:25:59 | 10/25/2025 21:41:19 | 10/26/2025 09:25:59 | Cell RX Channel Interference Noise Power Unbalanced at KBR2U6710-P3-L1800-CA @ Sceco | 10/25/2025 18:07:20 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 18:07:15 | P3 | 4G | dammam | Sceco | 2G NSA | KBR2U6710 | FLM_TE |  |  | PCM-20251025-00001692 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/25/2025 21:25:59 | 10/25/2025 21:41:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000790 | PCM-20251025-00001731 | TT-20251025-01809 | Telecom | Region_5 | MAK1M8089 | MAK2089 |  |  |  | Amjad Ali Muhammad Parves | 10/25/2025 21:27:30 | 10/26/2025 10:29:30 | 10/26/2025 03:27:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M8089-CA-L800-SBTS @ Sceco | 10/25/2025 21:26:44 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 21:26:33 | P3 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M8089 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 21:27:30 | 10/26/2025 10:29:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000791 | PCM-20251025-00001736 | TT-20251025-01811 | Reference_telecom | Region_4 | JED0551 | JED0551 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 21:30:35 | 10/25/2025 21:30:35 | 10/26/2025 09:30:35 | ReplaceableUnitMissing observed in JED0551 towards 10.1.229.227 @ Sceco | 10/25/2025 09:31:03 | Minor |  | ReplaceableUnitMissing | 10/25/2025 09:30:03 | P2 | 2G | jeddah | Sceco | TX NSA | JED0551 | FLM_TE | [8 empty] | API | 10/25/2025 21:30:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000792 | PCM-20251025-00001739 | TT-20251025-01812 | Reference_EM | Region_3 | WFR2279 | WFR2279 |  |  |  | Walid Mohamad Fazil | 10/25/2025 21:33:10 | 10/25/2025 21:33:10 | 10/26/2025 09:33:10 | Door opening alarm at WFR2279-P3_SRAN @ Generator_SG | 10/25/2025 21:32:35 | Minor | 65101 | Door opening alarm | 10/25/2025 21:32:31 | P3 | SRAN | madinah | Generator_SG | 2G NSA | WFR2279 | FLM_EM | [8 empty] | API | 10/25/2025 21:33:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251025000794 | PCM-20251025-00001742 | TT-20251025-01816 | Telecom | Region_4 | RAB1M7482 | RAB0482 |  |  |  | Khizer Hayat | 10/25/2025 21:38:52 | 10/26/2025 08:36:46 | 10/26/2025 09:38:52 | BASE STATION ANTENNA LINE PROBLEM at RAB1M7482-G9-L18-SBTS-P2 @ Generator_DG | 10/25/2025 21:31:43 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 21:31:35 | P2 | 4G | jeddah | Generator_DG | LTE NSA | RAB1M7482 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/25/2025 21:38:52 | 10/26/2025 08:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000795 | PCM-20251025-00001745 | TT-20251025-01813 | Telecom | Region_1 | DMAP2M8155 | DMAP2155 |  |  |  | Meraj Husain Idd Baksh | 10/25/2025 21:40:30 | 10/25/2025 21:41:20 | 10/26/2025 01:40:30 | 1(LTE) sites down under DMAP2155-L800-CA-P1-VIP @ Generator_SG | 10/25/2025 21:33:09 | Critical | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/25/2025 21:32:16 | VIP | 4G | dammam | Generator_SG | LTE SA | DMAP2155-L800-CA-P1-VIP | FLM_TE | DMAP2155 | Results: DOWN SITE HUB DMAP2155-L800-CA-P1-VIP DMAP2155 Summary: Hub: DMAP2155, Down Count: 1, Down Sites: DMAP2155-L800-CA-P1-VIP Alarm Summary: DMAP2155 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 21:40:30 | 10/25/2025 21:41:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000797 | PCM-20251025-00001747 | TT-20251025-01743 | Reference_telecom | Region_1 | HLHD0705 | HLHD0705 |  |  |  | Almmoez Almmoez | 10/25/2025 21:41:32 | 10/26/2025 00:43:45 | 10/26/2025 09:41:32 | External Clock Reference Problem at HLHD0705-P3_SRAN @ Generator_SG | 10/25/2025 17:39:48 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 17:37:21 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0705 | FLM_TE |  |  | PCM-20251025-00001701 | Kindly need to check link HLHD0733-HLHD0705 as suspected power issue exist during this time | Kindly need to check link HLHD0733-HLHD0705 as suspected power issue exist during this time |  |  |  | API | 10/25/2025 21:41:32 | 10/26/2025 00:43:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000798 | PCM-20251025-00001748 | TT-20251025-01647 | Reference_telecom | Region_1 | HLHD0707 | HLHD0707 |  |  |  | Almmoez Almmoez | 10/25/2025 21:41:53 | 10/26/2025 00:43:46 | 10/26/2025 09:41:53 | External Clock Reference Problem at HLHD0707-P3_SRAN @ Generator_SG | 10/25/2025 16:57:49 | Minor | 26262 | External Clock Reference Problem | 10/25/2025 15:56:45 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0707 | FLM_TE |  |  | PCM-20251025-00001572 | Kindly need to check link HLHD0733-HLHD0705 as suspected power issue exist during this time | Kindly need to check link HLHD0733-HLHD0705 as suspected power issue exist during this time |  |  |  | API | 10/25/2025 21:41:53 | 10/26/2025 00:43:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000799 | PCM-20251025-00001750 | TT-20251025-01820 | Telecom | Region_6 | DMD2032 | DMD2032 | Equipment | SFP_BTS | Replace SFP | Ansir Iqbal Muhammad Iqbal | 10/25/2025 21:45:03 | 10/25/2025 23:08:31 | 10/26/2025 09:45:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at DMD2032-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/25/2025 21:44:18 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 21:44:10 | P3 | 2G | bisha | Generator_SG | 5G_Cell SA | DMD2032 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 21:45:03 | 10/25/2025 23:07:18 | 10/25/2025 23:07:59 |  |  | 10/25/2025 23:08:31 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000800 | PCM-20251025-00001751 | TT-20251025-01769 | Reference_telecom | Region_4 | JED1M7839 | JED0839 |  |  |  | Nazeer Mohammed | 10/25/2025 21:46:31 | 10/25/2025 21:46:31 | 10/26/2025 01:46:31 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1M7839-CA-L900-P1-VIP @ Sceco | 10/25/2025 20:49:07 | Critical | 7654 | CELL OPERATION DEGRADED | 10/25/2025 20:48:57 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7839 | FLM_TE |  |  | PCM-20251025-00001686 | cell reset taken | cell reset taken |  |  |  | API | 10/25/2025 21:46:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000801 | PCM-20251025-00001753 | TT-20251025-01810 | Telecom | Region_4 | JED6135 | JED6135 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 21:47:42 | 10/25/2025 21:47:42 | 10/26/2025 09:47:42 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/25/2025 21:24:21 | Minor | 7114 | CELL SERVICE PROBLEM | 10/25/2025 21:24:12 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251025-00001733 | cell reset taken | cell reset taken |  |  |  | API | 10/25/2025 21:47:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000802 | PCM-20251025-00001755 | TT-20251025-01794 | Telecom | Region_4 | HAW2310 | HAW2310 |  |  |  | Rashid Shafique | 10/25/2025 21:48:37 | 10/25/2025 21:48:37 | 10/26/2025 03:48:37 | 2(5G) sites down under HAW2424-G9-L8-L18-L21-NR2.6-SBTS-P2,HAW2310-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/25/2025 21:14:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 21:14:09 | P2 | 2G | taif | Sceco | 5G SA | HAW2310-G9-L8-L18-L21-NR2.6-SBTS-P2 5G,HAW2424-G9-L8-L18-L21-NR2.6-SBTS-P2 5G | FLM_TE | HAW2310 | Results: DOWN SITE HUB HAW2310-G9-L8-L18-L21-NR2.6-SBTS-P2 HAW2310 HAW2424-G9-L8-L18-L21-NR2.6-SBTS-P2 HAW2310 Summary: Hub: HAW2310, Down Count: 2, Down Sites: HAW2310-G9-L8-L18-L21-NR2.6-SBTS-P2, HAW2424-G9-L8-L18-L21-NR2.6-SBTS-P2 Alarm Summary: HAW2310 No Active Alarm on HUB | PCM-20251025-00001718 | HAW2310 | HAW2310 |  | sites down |  | API | 10/25/2025 21:48:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000803 | PCM-20251025-00001758 | TT-20251025-01764 | Telecom | Region_5 | MAK0721 | MAK0721 |  |  |  | Amr Abdulla Ali Othman | 10/25/2025 21:49:38 | 10/25/2025 21:49:38 | 10/26/2025 03:49:38 | 2(2G) 1(3G) 1(LTE) 1(5G) sites down under MAK0721-P2-NEW,BIK0153-P3,MAK0730-P2-USF/MAK0730-P2-USF @ Generator_SG | 10/25/2025 20:47:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 20:47:28 | P2 | 2G | makkah | Generator_SG | 2G_3G_LTE SA | MAK0730-P2-USF 2G_LTE,BIK0153-P3 3G,MAK0721-P2-NEW 2G | FLM_TE | MAK0721 | Results: DOWN SITE HUB MAK0730-P2-USF MAK0721 BIK0153-P3 BIK0153 MAK0721-P2-NEW MAK0721 Summary: Hub: MAK0721, Down Count: 2, Down Sites: MAK0730-P2-USF, MAK0721-P2-NEW Hub: BIK0153, Down Count: 1, Down Sites: BIK0153-P3 Alarm Summary: MAK0721 No Active Alarm on HUB BIK0153 No Active Alarm on HUB | PCM-20251025-00001730 | No Power Issue | No Power Issue |  | sites down |  | API | 10/25/2025 21:49:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000078 | PCM-20251025-00000161 | TT-20251025-00178 | Reference_EM | Region_1 | JBKH2338 | JBKH2338 |  |  |  | Dileesh Muringothil Devarajan | 10/25/2025 03:09:27 | 10/25/2025 08:06:02 | 10/25/2025 09:09:27 | Mains Failure at JBKH2338-P1-VIP_ARP_SRAN @ Sceco | 10/25/2025 02:59:25 | Major | 65109 | Mains Failure | 10/25/2025 02:59:22 | VIP | SRAN | khafji | Sceco | 2G NSA | JBKH2338 | FLM_EM | [8 empty] | API | 10/25/2025 03:09:27 | 10/25/2025 08:06:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000088 | PCM-20251025-00000176 | TT-20251025-00189 | Reference_EM | Region_2 | RUM0042 | RUM0042 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | Gul Rahman Gul ZADA | 10/25/2025 03:23:26 | 10/25/2025 06:50:01 | 10/25/2025 15:23:26 | Generator failure at RUM0042-P3_SRAN @ Generator_DG | 10/25/2025 03:13:01 | Minor | 65114 | Generator failure | 10/25/2025 03:12:57 | P3 | SRAN | riyadh | Generator_DG | 2G NSA | RUM0042 | FLM_EM | [8 empty] | API | 10/25/2025 03:23:26 | 10/25/2025 04:44:34 | 10/25/2025 06:49:53 |  |  | 10/25/2025 06:50:01 |  | Gul Rahman Gul ZADA |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000091 | PCM-20251025-00000182 | TT-20251025-00191 | Reference_EM | Region_2 | HRQ0032 | HRQ0032 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | ABUZAR Ahmed Humida Mustafa | 10/25/2025 03:27:01 | 10/25/2025 05:35:24 | 10/25/2025 15:27:01 | Generator failure at HRQ0032-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 03:16:41 | Minor | 65114 | Generator failure | 10/25/2025 03:16:39 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HRQ0032 | FLM_EM | [8 empty] | API | 10/25/2025 03:27:01 | 10/25/2025 04:23:33 | 10/25/2025 04:23:38 | 10/25/2025 04:23:42 | 10/25/2025 04:58:46 | 10/25/2025 05:35:24 |  | ABUZAR Ahmed Humida Mustafa |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000126 | PCM-20251025-00000260 | TT-20251025-00292 | Reference_EM | Region_1 | RYHR0117 | RYHR0117 | Enviroment | Genset failure_High Temperature | Change Radiator fan | Essam Salah Marsa Hassan | 10/25/2025 05:03:06 | 10/25/2025 12:23:49 | 10/25/2025 17:03:06 | Generator failure at RYHR0117-P3_SRAN @ Generator_SG | 10/25/2025 04:52:37 | Minor | 65114 | Generator failure | 10/25/2025 04:52:33 | P3 | SRAN | hafr | Generator_SG | 2G NSA | RYHR0117 | FLM_EM | [8 empty] | API | 10/25/2025 05:03:06 | 10/25/2025 11:02:23 | 10/25/2025 12:02:13 | 10/25/2025 12:02:15 | 10/25/2025 12:02:20 | 10/25/2025 12:23:49 |  | Essam Salah Marsa Hassan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000130 | PCM-20251025-00000272 | TT-20251025-00309 | Reference_EM | Region_1 | DAM0306 | DAM0306 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/25/2025 05:32:01 | 10/25/2025 12:49:13 | 10/25/2025 17:32:01 | Air condition 1 failure alarm at DAM0306-P2_SRAN @ Sceco | 10/25/2025 05:21:44 | Minor | 65104 | Air condition 1 failure alarm | 10/25/2025 05:21:40 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0306 | FLM_EM | [8 empty] | API | 10/25/2025 05:32:01 | 10/25/2025 12:49:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000132 | PCM-20251025-00000274 | TT-20251025-00314 | Reference_EM | Region_1 | TRF2507 | TRF2507 |  |  |  | Ragab Farg Abdel Nabi Bekhatro | 10/25/2025 05:39:46 | 10/25/2025 07:11:26 | 10/25/2025 17:39:46 | Low battery voltage at TRF2507-P2-USF_SRAN @ Generator_SG | 10/25/2025 05:29:17 | Minor | 65110 | Low battery voltage | 10/25/2025 05:29:13 | P2 | SRAN | arar | Generator_SG | 2G NSA | TRF2507 | FLM_EM | [8 empty] | API | 10/25/2025 05:39:46 | 10/25/2025 07:11:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000160 | PCM-20251025-00000317 | TT-20251025-00364 | Reference_EM | Region_1 | DMJ9917 | DMJ9917 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 06:03:01 | 10/26/2025 09:15:26 | 10/25/2025 18:03:01 | Door opening alarm at DMJ9917-RPT @ Generator_SG | 10/25/2025 06:02:24 | Minor | 65101 | Door opening alarm | 10/25/2025 06:02:20 | P3 | Repeater | hafr | Generator_SG | 3G NSA | DMJ9917 | FLM_EM | [8 empty] | API | 10/25/2025 06:03:01 | 10/25/2025 19:08:16 | 10/26/2025 09:15:10 |  |  | 10/26/2025 09:15:26 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000180 | PCM-20251025-00000361 | TT-20251025-00408 | Reference_EM | Region_1 | ARR0909 | ARR0909 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Ahmed Goda | 10/25/2025 07:02:55 | 10/25/2025 22:16:36 | 10/25/2025 19:02:55 | Door opening alarm at ARR0909-P2-USF_SRAN @ Generator_DG | 10/25/2025 07:02:25 | Minor | 65101 | Door opening alarm | 10/25/2025 07:02:21 | P2 | SRAN | arar | Generator_DG | 2G NSA | ARR0909 | FLM_EM | [8 empty] | API | 10/25/2025 07:02:55 | 10/25/2025 20:39:46 | 10/25/2025 22:16:25 |  |  | 10/25/2025 22:16:36 |  | Mohamed Ahmed Goda |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000185 | PCM-20251025-00000372 | TT-20251025-00418 | EM | Region_2 | AFL9004 | AFL9004 |  |  |  | Sher Zamin Nasib Muhammad | 10/25/2025 07:14:45 | 10/25/2025 19:27:48 | 10/25/2025 11:14:45 | RELAY_ALARM_CRITICAL at AFL9004_NE_1 @ Power Cube | 10/25/2025 07:13:49 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/25/2025 07:13:38 | P3 | Repeater | aflaj | Power Cube | TX NSA | AFL9004 | FLM_EM | [8 empty] | API | 10/25/2025 07:14:45 | 10/25/2025 19:27:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000187 | PCM-20251025-00000378 | TT-20251025-00425 | Reference_EM | Region_1 | NRY0584 | NRY0584 |  |  |  | Dileesh Muringothil Devarajan | 10/25/2025 07:18:26 | 10/25/2025 08:06:02 | 10/25/2025 19:18:26 | Mains Failure at NRY0584-P2-USF_SRAN-PC @ Sceco | 10/25/2025 07:08:20 | Minor | 65109 | Mains Failure | 10/25/2025 07:08:15 | P2 | SRAN | jubail | Sceco | 2G NSA | NRY0584 | FLM_EM | [8 empty] | API | 10/25/2025 07:18:26 | 10/25/2025 08:06:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000188 | PCM-20251025-00000377 | TT-20251025-00424 | Reference_EM | Region_1 | NRY0574 | NRY0574 |  |  |  | Dileesh Muringothil Devarajan | 10/25/2025 07:18:26 | 10/25/2025 08:06:02 | 10/25/2025 19:18:26 | Mains Failure at NRY0574-P3-USF_SRAN-PC @ Sceco | 10/25/2025 07:08:20 | Minor | 65109 | Mains Failure | 10/25/2025 07:08:16 | P3 | SRAN | jubail | Sceco | 2G NSA | NRY0574 | FLM_EM | [8 empty] | API | 10/25/2025 07:18:26 | 10/25/2025 08:06:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000199 | PCM-20251025-00000396 | TT-20251025-00452 | Reference_EM | Region_1 | DMJR2263 | DMJR2263 | Equipment | BSS_HW_Stuck | Reset RRU | Mahmoud Youssef Mohamed Ahmed | 10/25/2025 07:35:26 | 10/25/2025 09:29:30 | 10/25/2025 19:35:26 | Door opening alarm at DMJR2263-P3-USF_SRAN @ Generator_DG | 10/25/2025 07:34:38 | Minor | 65101 | Door opening alarm | 10/25/2025 07:34:35 | P3 | SRAN | hafr | Generator_DG | 2G NSA | DMJR2263 | FLM_EM | [8 empty] | API | 10/25/2025 07:35:26 | 10/25/2025 08:25:45 | 10/25/2025 09:10:47 | 10/25/2025 09:10:59 | 10/25/2025 09:11:03 | 10/25/2025 09:29:30 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000202 | PCM-20251025-00000399 | TT-20251025-00457 | EM | Region_2 | RIY0202 | RIY0202 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 07:38:01 | 10/26/2025 09:20:13 | 10/25/2025 11:38:01 | ACU FAILURE at RIY0202_OCS @ Sceco | 10/25/2025 07:35:58 | Critical | 1-12307 | ACU FAILURE | 10/25/2025 07:35:46 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0202 | FLM_EM | [5 empty] | 0-TO RIY0041(1-A)-72-E1EFI-ACU FAILURE:2 |  |  | API | 10/25/2025 07:38:01 | 10/26/2025 09:20:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251025000216 | PCM-20251025-00000438 | TT-20251025-00502 | EM | Region_2 | AFL9003 | AFL9003 |  |  |  | Sher Zamin Nasib Muhammad | 10/25/2025 07:59:45 | 10/25/2025 19:27:49 | 10/25/2025 11:59:45 | RELAY_ALARM_CRITICAL at AFL9003_NE_2 @ Power Cube | 10/25/2025 07:58:45 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/25/2025 07:58:34 | P3 | Repeater | aflaj | Power Cube | TX NSA | AFL9003 | FLM_EM | [8 empty] | API | 10/25/2025 07:59:45 | 10/25/2025 19:27:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000223 | PCM-20251025-00000462 | TT-20251025-00532 | Reference_EM | Region_2 | WDS9016 | WDS9016 |  |  |  | Sher Zamin Nasib Muhammad | 10/25/2025 08:19:21 | 10/25/2025 19:27:50 | 10/25/2025 20:19:21 | NETECO: Battery Undervoltage at WDS9016 @ Power Cube | 10/25/2025 08:12:36 | Minor | 8901 | Battery Undervoltage | 10/25/2025 08:12:36 | P1 | Repeater | aflaj | Power Cube | 2G NSA | WDS9016 | FLM_EM | [8 empty] | API | 10/25/2025 08:19:21 | 10/25/2025 19:27:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000236 | PCM-20251025-00000490 | TT-20251025-00570 | EM | Region_1 | TRF0988 | TRF0988 | Enviroment | SCECO_Failure | SCECO auto restored | Elsayed Moustafa Elsayed Khodir | 10/25/2025 08:55:31 | 10/25/2025 11:05:02 | 10/25/2025 12:55:31 | Mains Failure at TRF0988-FWA-P1-VIP-HUB-WDM_SRAN @ Sceco_STB | 10/25/2025 08:53:30 | Critical | 65109 | Mains Failure | 10/25/2025 08:53:26 | VIP | SRAN | arar | Sceco_STB | 2G NSA | TRF0988 | FLM_EM | [8 empty] | API | 10/25/2025 08:55:31 | 10/25/2025 09:08:57 | 10/25/2025 09:21:42 | 10/25/2025 09:21:46 | 10/25/2025 09:21:49 | 10/25/2025 11:05:02 |  | Elsayed Moustafa Elsayed Khodir |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251025000243 | PCM-20251025-00000505 | TT-20251025-00586 | Reference_EM | Region_1 | SMN0793 | SMN0793 |  |  |  | Samir Elzain Abdu Gumaa | 10/25/2025 09:03:45 | 10/25/2025 09:03:45 | 10/25/2025 15:03:45 | Door opening alarm at SMN0793-P1-USF-HUB_SRAN @ Sceco_STB | 10/25/2025 09:03:18 | Major | 65101 | Door opening alarm | 10/25/2025 09:03:13 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | SMN0793 | FLM_EM | [8 empty] | API | 10/25/2025 09:03:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Preparation | CM20251025000246 | PCM-20251025-00000514 | TT-20251025-00597 | Reference_EM | Region_1 | HMBY2429 | HMBY2429 |  |  |  | Khaled Mohamed Abdulla Wahba | 10/25/2025 09:06:20 | 10/25/2025 10:03:03 | 10/25/2025 15:06:20 | Mains Failure at HMBY2429-P1-VIP_SRAN @ Generator_SG | 10/25/2025 08:56:21 | Major | 65109 | Mains Failure | 10/25/2025 08:56:16 | VIP | SRAN | dammam | Generator_SG | 2G NSA | HMBY2429 | FLM_EM | [8 empty] | API | 10/25/2025 09:06:20 | 10/25/2025 09:23:06 | 10/25/2025 09:26:45 | 10/25/2025 09:28:12 | 10/25/2025 10:03:03 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000258 | PCM-20251025-00000552 | TT-20251025-00643 | Reference_EM | Region_2 | AFF0521 | AFF0521 |  |  |  | Moustafa Elzaafarany Abdellah | 10/25/2025 09:37:51 | 10/25/2025 22:34:32 | 10/25/2025 21:37:51 | Major Rec alarm at AFF0521-P2_SRAN @ Sceco | 10/25/2025 09:27:11 | Minor | 65107 | Major Rec alarm | 10/25/2025 09:27:08 | P2 | SRAN | dawadmi | Sceco | 2G NSA | AFF0521 | FLM_EM | [8 empty] | API | 10/25/2025 09:37:51 | 10/25/2025 22:34:32 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000260 | PCM-20251025-00000562 | TT-20251025-00650 | Reference_EM | Region_2 | HRHT0132 | HRHT0132 |  |  |  | ABUZAR Ahmed Humida Mustafa | 10/25/2025 09:44:37 | 10/25/2025 15:56:52 | 10/25/2025 21:44:37 | Door opening alarm at HRHT0132-P3_SRAN-PC @ Power Cube | 10/25/2025 09:44:15 | Minor | 65101 | Door opening alarm | 10/25/2025 09:44:12 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HRHT0132 | FLM_EM | [8 empty] | API | 10/25/2025 09:44:37 | 10/25/2025 15:56:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000282 | PCM-20251025-00000624 | TT-20251025-00714 | Reference_EM | Region_2 | DLM0485 | DLM0485 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/25/2025 10:19:46 | 10/25/2025 10:19:46 | 10/25/2025 22:19:46 | high temprature 32 at DLM0485-P2_SRAN @ Sceco | 10/25/2025 10:09:16 | Minor | 65102 | high temprature 32 | 10/25/2025 10:09:13 | P2 | SRAN | al kharj | Sceco | 2G NSA | DLM0485 | FLM_EM | [8 empty] | API | 10/25/2025 10:19:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000285 | PCM-20251025-00000630 | TT-20251025-00716 | Reference_EM | Region_1 | HFBD2014 | HFBD2014 |  |  |  | Montasir Awadalla Abdalla Bala | 10/25/2025 10:22:21 | 10/25/2025 13:07:58 | 10/25/2025 16:22:21 | Major Rec alarm at HFBD2014-P1-HUB_SRAN @ Generator_SG | 10/25/2025 10:11:52 | Major | 65107 | Major Rec alarm | 10/25/2025 10:11:49 | P1 | SRAN | hafouf | Generator_SG | 2G NSA | HFBD2014 | FLM_EM | [8 empty] | API | 10/25/2025 10:22:21 | 10/25/2025 13:07:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000287 | PCM-20251025-00000633 | TT-20251025-00720 | EM | Region_1 | QRY2130 | QRY2130 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Bashir Sahib Rahman | 10/25/2025 10:22:50 | 10/25/2025 16:40:11 | 10/25/2025 22:22:50 | NETECO: Door Alarm at QRY2130 @ Sceco | 10/25/2025 10:22:01 | Minor | 10217 | Door Alarm | 10/25/2025 10:22:01 | P3 | SRAN | quriyat | Sceco | 2G NSA | QRY2130 | FLM_EM | [8 empty] | API | 10/25/2025 10:22:50 | 10/25/2025 12:55:58 | 10/25/2025 16:40:02 |  |  | 10/25/2025 16:40:11 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000288 | PCM-20251025-00000634 | TT-20251025-00721 | Reference_EM | Region_1 | QRY2130 | QRY2130 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Bashir Sahib Rahman | 10/25/2025 10:22:51 | 10/25/2025 16:39:50 | 10/25/2025 22:22:51 | Door opening alarm at QRY2130-P3_SRAN @ Sceco | 10/25/2025 10:22:08 | Minor | 65101 | Door opening alarm | 10/25/2025 10:22:04 | P3 | SRAN | quriyat | Sceco | 2G NSA | QRY2130 | FLM_EM | [8 empty] | API | 10/25/2025 10:22:51 | 10/25/2025 12:55:58 | 10/25/2025 16:39:40 |  |  | 10/25/2025 16:39:50 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000294 | PCM-20251025-00000644 | TT-20251025-00735 | Reference_EM | Region_2 | RIY2072 | RIY2072 |  |  |  | Kadri Jalal Mohammed Asmail | 10/25/2025 10:28:31 | 10/25/2025 11:24:36 | 10/25/2025 22:28:31 | Door opening alarm at RIY2072-P2_SRAN @ Sceco | 10/25/2025 10:27:58 | Minor | 65101 | Door opening alarm | 10/25/2025 10:27:55 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2072 | FLM_EM | [8 empty] | API | 10/25/2025 10:28:31 | 10/25/2025 11:24:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000295 | PCM-20251025-00000647 | TT-20251025-00739 | EM | Region_1 | QRY2130 | QRY2130 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Bashir Sahib Rahman | 10/25/2025 10:29:00 | 10/25/2025 16:38:30 | 10/25/2025 22:29:00 | NETECO: Battery Fuse Break at QRY2130 @ Sceco | 10/25/2025 10:22:15 | Minor | 903 | Battery Fuse Break | 10/25/2025 10:22:15 | P3 | SRAN | quriyat | Sceco | 2G NSA | QRY2130 | FLM_EM | [8 empty] | API | 10/25/2025 10:29:00 | 10/25/2025 12:55:59 | 10/25/2025 16:38:18 |  |  | 10/25/2025 16:38:30 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000296 | PCM-20251025-00000648 | TT-20251025-00740 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 10:29:36 | 10/25/2025 11:14:25 | 10/25/2025 22:29:36 | high temprature 40 at RIY0349-P2_SRAN @ Sceco | 10/25/2025 10:19:01 | Minor | 65103 | high temprature 40 | 10/25/2025 10:18:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/25/2025 10:29:36 | 10/25/2025 11:14:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000311 | PCM-20251025-00000675 | TT-20251025-00760 | Reference_EM | Region_1 | DMAP0404 | DMAP0404 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/25/2025 10:40:55 | 10/25/2025 17:18:53 | 10/25/2025 16:40:55 | Door opening alarm at DMAP2M3404-P1-VIP @ Generator_SG | 10/25/2025 10:40:12 | Major | 65101 | Door opening alarm | 10/25/2025 10:40:07 | VIP | 3G | dammam | Generator_SG | 3G NSA | DMAP2M3404 | FLM_EM | [8 empty] | API | 10/25/2025 10:40:55 | 10/25/2025 11:25:27 | 10/25/2025 17:18:45 |  |  | 10/25/2025 17:18:53 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000318 | PCM-20251025-00000684 | TT-20251025-00761 | Telecom | Region_2 | BUR0053 | BUR0053 |  |  |  | Farman Ullah Muhammad Nazir | 10/25/2025 10:44:30 | 10/25/2025 13:44:59 | 10/25/2025 16:44:30 | BBU Board Maintenance Link Failure at BUR0053-P2_SRAN @ Sceco | 10/25/2025 10:38:58 | Major | 26205 | BBU Board Maintenance Link Failure | 10/25/2025 10:37:24 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0053 | FLM_EM |  |  | PCM-20251025-00000678 | power issue at site | power issue at site |  |  |  | API | 10/25/2025 10:44:30 | 10/25/2025 13:44:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000327 | PCM-20251025-00000706 | TT-20251025-00792 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/25/2025 11:02:06 | 10/25/2025 22:36:06 | 10/25/2025 23:02:06 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/25/2025 10:51:36 | Minor | 65102 | high temprature 32 | 10/25/2025 10:51:32 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/25/2025 11:02:06 | 10/25/2025 22:36:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000329 | PCM-20251025-00000713 | TT-20251025-00798 | Reference_EM | Region_2 | RIY2965 | RIY2965 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 11:05:46 | 10/26/2025 09:20:14 | 10/25/2025 23:05:46 | Door opening alarm at RIY2965-P3_SRAN @ Generator_SG | 10/25/2025 11:05:01 | Minor | 65101 | Door opening alarm | 10/25/2025 11:04:57 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2965 | FLM_EM | [8 empty] | API | 10/25/2025 11:05:46 | 10/26/2025 09:20:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000331 | PCM-20251025-00000717 | TT-20251025-00800 | Reference_EM | Region_2 | MZH0999 | MZH0999 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Ahmed Hamada Mohamed Awad Abouhatab | 10/25/2025 11:08:21 | 10/25/2025 12:06:27 | 10/25/2025 23:08:21 | Generator failure at MZH0999-P2-USF_SRAN-PC @ Power Cube | 10/25/2025 10:58:05 | Minor | 65114 | Generator failure | 10/25/2025 10:58:01 | P2 | SRAN | muzamiah | Power Cube | 2G NSA | MZH0999 | FLM_EM | [8 empty] | API | 10/25/2025 11:08:21 | 10/25/2025 11:42:27 | 10/25/2025 11:42:31 | 10/25/2025 11:42:35 | 10/25/2025 11:42:36 | 10/25/2025 12:06:27 |  | Ahmed Hamada Mohamed Awad Abouhatab |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000336 | PCM-20251025-00000731 | TT-20251025-00812 | Reference_EM | Region_2 | RIY2127 | RIY2127 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 11:17:06 | 10/25/2025 12:10:07 | 10/25/2025 17:17:06 | Major Rec alarm at RIY2127-P1_SRAN @ Sceco | 10/25/2025 11:06:24 | Major | 65107 | Major Rec alarm | 10/25/2025 11:06:20 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2127 | FLM_EM | [8 empty] | API | 10/25/2025 11:17:06 | 10/25/2025 12:10:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251025000339 | PCM-20251025-00000739 | TT-20251025-00818 | Reference_EM | Region_1 | JBKH2114 | JBKH2114 |  |  |  | Abu Sufyan Mehfooz Ali | 10/25/2025 11:19:40 | 10/25/2025 11:19:40 | 10/25/2025 23:19:40 | Generator failure at JBKH2114-P3_SRAN @ Generator_DG | 10/25/2025 11:09:10 | Minor | 65114 | Generator failure | 10/25/2025 11:09:07 | P3 | SRAN | khafji | Generator_DG | 2G NSA | JBKH2114 | FLM_EM | [8 empty] | API | 10/25/2025 11:19:40 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000343 | PCM-20251025-00000752 | TT-20251025-00828 | EM | Region_1 | DMJR0137 | DMJR0137 |  |  |  | Emad Mahmoud Ahmed Mohamed | 10/25/2025 11:26:27 | 10/25/2025 13:34:47 | 10/25/2025 15:26:27 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/25/2025 11:24:34 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/25/2025 11:24:29 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 2-TO HFR0502(2-A) |  |  | API | 10/25/2025 11:26:27 | 10/25/2025 13:34:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251025000349 | PCM-20251025-00000760 | TT-20251025-00835 | Reference_EM | Region_1 | RYHR9915 | RYHR9915 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 11:31:35 | 10/26/2025 09:14:56 | 10/25/2025 23:31:35 | Door opening alarm at RYHR9915-RPT @ Generator_SG | 10/25/2025 11:31:01 | Minor | 65101 | Door opening alarm | 10/25/2025 11:31:00 | P3 | Repeater | hafr | Generator_SG | 3G NSA | RYHR9915 | FLM_EM | [8 empty] | API | 10/25/2025 11:31:35 | 10/25/2025 19:08:17 | 10/26/2025 09:14:48 |  |  | 10/26/2025 09:14:56 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000350 | PCM-20251025-00000759 | TT-20251025-00834 | EM | Region_1 | RYHR9915 | RYHR9915 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 11:31:37 | 10/26/2025 09:14:44 | 10/25/2025 23:31:37 | NETECO: Door Open Alarm at RYHR9915 @ Generator_SG | 10/25/2025 11:30:57 | Minor | 5152 | Door Open Alarm | 10/25/2025 11:30:57 | P3 | Repeater | hafr | Generator_SG | 2G NSA | RYHR9915 | FLM_EM | [8 empty] | API | 10/25/2025 11:31:37 | 10/25/2025 19:08:17 | 10/26/2025 09:14:36 |  |  | 10/26/2025 09:14:44 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000358 | PCM-20251025-00000779 | TT-20251025-00854 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/25/2025 11:40:50 | 10/25/2025 11:40:50 | 10/25/2025 23:40:50 | high temprature 40 at RYHF2036-P2_SRAN @ Generator_SG | 10/25/2025 11:30:16 | Minor | 65103 | high temprature 40 | 10/25/2025 11:30:13 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/25/2025 11:40:50 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000361 | PCM-20251025-00000782 | TT-20251025-00857 | Reference_EM | Region_1 | RYHR9915 | RYHR9915 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 11:43:55 | 10/26/2025 09:14:26 | 10/25/2025 23:43:55 | Generator failure at RYHR9915-RPT @ Generator_SG | 10/25/2025 11:33:15 | Minor | 65114 | Generator failure | 10/25/2025 11:33:11 | P3 | Repeater | hafr | Generator_SG | 3G NSA | RYHR9915 | FLM_EM | [8 empty] | API | 10/25/2025 11:43:55 | 10/25/2025 19:08:18 | 10/26/2025 09:14:10 |  |  | 10/26/2025 09:14:26 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251025000366 | PCM-20251025-00000792 | TT-20251025-00864 | Reference_EM | Region_2 | RYD0935 | RYD0935 |  |  |  | Pawan Virdi Santokh Singh | 10/25/2025 11:49:05 | 10/25/2025 13:38:09 | 10/25/2025 17:49:05 | Board Temperature Unacceptable at RYD0935-P3_SRAN @ Sceco | 10/25/2025 11:39:54 | Major | 26104 | Board Temperature Unacceptable | 10/25/2025 11:38:22 | P3 | SRAN | rumah | Sceco | 2G NSA | RYD0935 | FLM_EM | [8 empty] | API | 10/25/2025 11:49:05 | 10/25/2025 13:37:56 | 10/25/2025 13:38:01 | 10/25/2025 13:38:04 | 10/25/2025 13:38:09 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000371 | PCM-20251025-00000801 | TT-20251025-00876 | EM | Region_1 | JBL0469 | JBL0469 | Enviroment | Genset failure_ATS | Adjust loos power cable connection at ATS | Ahmed Salah Abdalgadir Ahmed | 10/25/2025 11:56:21 | 10/26/2025 07:00:15 | 10/25/2025 15:56:21 | low fuel alarm at JBL0469-P1-HUB-WDM_SRAN-FON @ Sceco_STB | 10/25/2025 11:54:10 | Critical | 65115 | low fuel alarm | 10/25/2025 11:54:07 | P1 | SRAN | jubail | Sceco_STB | 2G NSA | JBL0469 | FLM_EM | [8 empty] | API | 10/25/2025 11:56:21 | 10/25/2025 16:10:14 | 10/26/2025 06:59:04 |  |  | 10/26/2025 07:00:15 |  | Ahmed Salah Abdalgadir Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251025000376 | PCM-20251025-00000810 | TT-20251025-00885 | Reference_EM | Region_2 | RIY0044 | RIY0044 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 12:00:26 | 10/25/2025 13:13:33 | 10/25/2025 18:00:26 | Minor Rec alarm at RIY0044-P1-DIA_SRAN @ Sceco | 10/25/2025 11:49:50 | Major | 65108 | Minor Rec alarm | 10/25/2025 11:49:46 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0044 | FLM_EM | [8 empty] | API | 10/25/2025 12:00:26 | 10/25/2025 12:10:07 | 10/25/2025 12:14:30 | 10/25/2025 12:14:33 | 10/25/2025 12:52:03 | 10/25/2025 13:13:33 |  | Tanveer Ahmad Muhammad Ishaq |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000378 | PCM-20251025-00000813 | TT-20251025-00888 | Reference_EM | Region_2 | RIY0424 | RIY0424 | Enviroment | Air Condition | Change Fan | Ahmed Mohamed Ibrahim Elnagar | 10/25/2025 12:01:00 | 10/25/2025 14:50:23 | 10/26/2025 00:01:00 | Air condition 1 failure alarm at RIY0424-P2_SRAN-FON @ Sceco | 10/25/2025 11:50:34 | Minor | 65104 | Air condition 1 failure alarm | 10/25/2025 11:50:31 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0424 | FLM_EM | [8 empty] | API | 10/25/2025 12:01:00 | 10/25/2025 14:12:20 | 10/25/2025 14:13:35 | 10/25/2025 14:13:39 | 10/25/2025 14:13:58 | 10/25/2025 14:50:23 |  | Ahmed Mohamed Ibrahim Elnagar |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251025000381 | PCM-20251025-00000820 | TT-20251025-00896 | Reference_EM | Region_2 | QSHB0199 | QSHB0199 |  |  |  | Mohamed Alfatih Mohamed Eltayeb Mohamed | 10/25/2025 12:03:36 | 10/25/2025 12:03:36 | 10/26/2025 00:03:36 | Mains Failure at QSHB0199-P3_SRAN @ Sceco | 10/25/2025 11:53:15 | Minor | 65109 | Mains Failure | 10/25/2025 11:53:12 | P3 | SRAN | al rass | Sceco | 2G NSA | QSHB0199 | FLM_EM | [8 empty] | API | 10/25/2025 12:03:36 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000382 | PCM-20251025-00000819 | TT-20251025-00895 | Reference_EM | Region_1 | SMRY0812 | SMRY0812 |  |  |  | Samir Elzain Abdu Gumaa | 10/25/2025 12:03:36 | 10/25/2025 12:03:36 | 10/26/2025 00:03:36 | Door opening alarm at SMRY0812-P3_SRAN @ Generator_SG | 10/25/2025 12:02:50 | Minor | 65101 | Door opening alarm | 10/25/2025 12:02:45 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0812 | FLM_EM | [8 empty] | API | 10/25/2025 12:03:36 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000390 | PCM-20251025-00000840 | TT-20251025-00914 | EM | Region_1 | HFF2172 | HFF2172 | Enviroment | Air Condition | Change Fan | Moustafa Mohamed Saleh Saif | 10/25/2025 12:14:25 | 10/26/2025 10:59:10 | 10/25/2025 16:14:25 | high temprature 32 at HFF2172-P1-WDM_SRAN-FON @ Sceco | 10/25/2025 12:12:17 | Critical | 65102 | high temprature 32 | 10/25/2025 12:12:12 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFF2172 | FLM_EM | [8 empty] | API | 10/25/2025 12:14:25 | 10/25/2025 12:47:37 | 10/25/2025 13:05:52 | 10/25/2025 13:05:57 | 10/25/2025 13:12:30 | 10/26/2025 10:59:10 |  | Moustafa Mohamed Saleh Saif |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251025000392 | PCM-20251025-00000843 | TT-20251025-00922 | Reference_EM | Region_1 | SMRY0812 | SMRY0812 |  |  |  | Samir Elzain Abdu Gumaa | 10/25/2025 12:16:26 | 10/25/2025 12:16:26 | 10/26/2025 00:16:26 | Mains Failure at SMRY0812-P3_SRAN @ Generator_SG | 10/25/2025 12:06:07 | Minor | 65109 | Mains Failure | 10/25/2025 12:06:04 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0812 | FLM_EM | [8 empty] | API | 10/25/2025 12:16:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000406 | PCM-20251025-00000880 | TT-20251025-00977 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/25/2025 12:35:36 | 10/25/2025 13:21:19 | 10/25/2025 18:35:36 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/25/2025 12:25:21 | Major | 65110 | Low battery voltage | 10/25/2025 12:25:18 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/25/2025 12:35:36 | 10/25/2025 13:21:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000413 | PCM-20251025-00000891 | TT-20251025-00986 | Reference_EM | Region_2 | RIY0785 | RIY0785 | Enviroment | Air Condition | Welding condenser & adding Freon | Kadri Jalal Mohammed Asmail | 10/25/2025 12:41:45 | 10/25/2025 13:17:05 | 10/26/2025 00:41:45 | Door opening alarm at RIY0785-P2_SRAN @ Sceco | 10/25/2025 12:41:26 | Minor | 65101 | Door opening alarm | 10/25/2025 12:41:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0785 | FLM_EM | [8 empty] | API | 10/25/2025 12:41:45 | 10/25/2025 13:16:09 | 10/25/2025 13:16:44 | 10/25/2025 13:16:47 | 10/25/2025 13:16:50 | 10/25/2025 13:17:05 |  | Kadri Jalal Mohammed Asmail |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000414 | PCM-20251025-00000894 | TT-20251025-00988 | Reference_EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/25/2025 12:42:50 | 10/25/2025 14:00:54 | 10/26/2025 00:42:50 | Door opening alarm at SMN0805-P3_SRAN @ Generator_DG | 10/25/2025 12:42:19 | Minor | 65101 | Door opening alarm | 10/25/2025 12:42:15 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/25/2025 12:42:50 | 10/25/2025 14:00:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000415 | PCM-20251025-00000896 | TT-20251025-00991 | Reference_EM | Region_2 | RIY0785 | RIY0785 | Enviroment | Air Condition | Welding condenser & adding Freon | Kadri Jalal Mohammed Asmail | 10/25/2025 12:43:50 | 10/25/2025 13:16:38 | 10/26/2025 00:43:50 | Fire Alarm at RIY0785-P2_SRAN @ Sceco | 10/25/2025 12:33:31 | Minor | 65119 | Fire Alarm | 10/25/2025 12:33:27 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0785 | FLM_EM | [8 empty] | API | 10/25/2025 12:43:50 | 10/25/2025 13:16:10 | 10/25/2025 13:16:16 | 10/25/2025 13:16:20 | 10/25/2025 13:16:23 | 10/25/2025 13:16:38 |  | Kadri Jalal Mohammed Asmail |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000416 | PCM-20251025-00000897 | TT-20251025-00992 | EM | Region_1 | ARR9807 | ARR9807 |  |  |  | Ismail Salah Ismail Elbery | 10/25/2025 12:44:20 | 10/25/2025 12:44:20 | 10/26/2025 00:44:20 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/25/2025 12:37:58 | Minor | 40564 | Genset Fault | 10/25/2025 12:37:58 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/25/2025 12:44:20 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000427 | PCM-20251025-00000912 | TT-20251025-01004 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Mohamed Samir Farahat Allam | 10/25/2025 12:53:11 | 10/25/2025 13:27:23 | 10/26/2025 00:53:11 | high temprature 40 at KBR2223-P3_SRAN @ Sceco | 10/25/2025 12:42:50 | Minor | 65103 | high temprature 40 | 10/25/2025 12:42:46 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/25/2025 12:53:11 | 10/25/2025 13:27:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000435 | PCM-20251025-00000923 | TT-20251025-01018 | Reference_EM | Region_1 | DMH0105 | DMH0105 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | Mahmoud Youssef Mohamed Ahmed | 10/25/2025 13:00:55 | 10/25/2025 15:23:59 | 10/25/2025 19:00:55 | Air condition 2 failure alarm at DMH0105-P1-HUB_SRAN @ Generator_SG | 10/25/2025 12:50:12 | Major | 65105 | Air condition 2 failure alarm | 10/25/2025 12:50:07 | P1 | SRAN | hafr | Generator_SG | 2G NSA | DMH0105 | FLM_EM | [8 empty] | API | 10/25/2025 13:00:55 | 10/25/2025 14:27:42 | 10/25/2025 14:27:47 | 10/25/2025 14:27:50 | 10/25/2025 14:27:53 | 10/25/2025 15:23:59 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251025000451 | PCM-20251025-00000947 | TT-20251025-01040 | Reference_EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/25/2025 13:13:15 | 10/25/2025 14:00:55 | 10/26/2025 01:13:15 | Mains Failure at SMN0805-P3_SRAN @ Generator_DG | 10/25/2025 13:03:08 | Minor | 65109 | Mains Failure | 10/25/2025 13:03:04 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/25/2025 13:13:15 | 10/25/2025 14:00:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000473 | PCM-20251025-00001012 | TT-20251025-01106 | Reference_EM | Region_2 | RIY2506 | RIY2506 |  |  |  | Kadri Jalal Mohammed Asmail | 10/25/2025 13:37:35 | 10/25/2025 16:32:51 | 10/26/2025 01:37:35 | Minor Rec alarm at RIY2506-P2_SRAN @ Sceco | 10/25/2025 13:27:01 | Minor | 65108 | Minor Rec alarm | 10/25/2025 13:26:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2506 | FLM_EM | [8 empty] | API | 10/25/2025 13:37:35 | 10/25/2025 16:32:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000476 | PCM-20251025-00001018 | TT-20251025-01110 | Reference_EM | Region_2 | KHJ0007 | KHJ0007 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Fritz Ian Generale | 10/25/2025 13:40:11 | 10/25/2025 15:16:02 | 10/26/2025 01:40:11 | Generator failure at KHJ0007-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 13:29:40 | Minor | 65114 | Generator failure | 10/25/2025 13:29:37 | P3 | SRAN | al kharj | Power Cube | 2G NSA | KHJ0007 | FLM_EM | [8 empty] | API | 10/25/2025 13:40:11 | 10/25/2025 15:02:44 | 10/25/2025 15:02:49 | 10/25/2025 15:02:52 | 10/25/2025 15:02:58 | 10/25/2025 15:16:02 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000488 | PCM-20251025-00001043 | TT-20251025-01125 | Reference_EM | Region_2 | RIY0112 | RIY0112 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/25/2025 13:48:25 | 10/25/2025 14:50:31 | 10/25/2025 19:48:25 | high temprature 32 at RIY0112-P1-DIA_SRAN @ Sceco | 10/25/2025 13:37:43 | Major | 65102 | high temprature 32 | 10/25/2025 13:37:39 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0112 | FLM_EM | [8 empty] | API | 10/25/2025 13:48:25 | 10/25/2025 14:50:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000492 | PCM-20251025-00001052 | TT-20251025-01131 | Reference_EM | Region_2 | ZLHB0873 | ZLHB0873 |  |  |  | Mohamed Moustafa Aboelmagd Hefny | 10/25/2025 13:50:00 | 10/25/2025 14:05:00 | 10/26/2025 01:50:00 | Mains Failure at ZLHB0873-P3_SRAN @ Sceco | 10/25/2025 13:39:37 | Minor | 65109 | Mains Failure | 10/25/2025 13:39:33 | P3 | SRAN | majma | Sceco | 2G NSA | ZLHB0873 | FLM_EM | [8 empty] | API | 10/25/2025 13:50:00 | 10/25/2025 14:05:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000493 | PCM-20251025-00001053 | TT-20251025-01132 | Reference_EM | Region_2 | SAR0308 | SAR0308 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/25/2025 13:50:02 | 10/25/2025 16:16:00 | 10/25/2025 19:50:02 | Mains Failure at SAR0308-P1-HUB_SRAN @ Sceco | 10/25/2025 13:39:38 | Major | 65109 | Mains Failure | 10/25/2025 13:39:35 | P1 | SRAN | rumah | Sceco | 2G NSA | SAR0308 | FLM_EM | [8 empty] | API | 10/25/2025 13:50:02 | 10/25/2025 14:05:00 | 10/25/2025 16:15:15 | 10/25/2025 16:15:18 | 10/25/2025 16:15:43 | 10/25/2025 16:16:00 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Preparation | CM20251025000497 | PCM-20251025-00001068 | TT-20251025-01146 | Reference_EM | Region_2 | RIY0737 | RIY0737 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 13:57:10 | 10/25/2025 14:39:07 | 10/26/2025 01:57:10 | high temprature 40 at RIY0737-P2_SRAN-FON @ Sceco | 10/25/2025 13:46:39 | Minor | 65103 | high temprature 40 | 10/25/2025 13:46:36 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0737 | FLM_EM | [8 empty] | API | 10/25/2025 13:57:10 | 10/25/2025 14:01:28 | 10/25/2025 14:19:38 | 10/25/2025 14:19:42 | 10/25/2025 14:39:07 | [6 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251025000499 | PCM-20251025-00001071 | TT-20251025-01148 | Reference_EM | Region_2 | RIY0175 | RIY0175 | Enviroment | SCECO_Failure | SCECO auto restored | Adel Abdelaziz Mohamed Ayedi | 10/25/2025 13:59:46 | 10/25/2025 17:44:03 | 10/25/2025 19:59:46 | Door opening alarm at RIY0175-P1-VIP_SRAN @ Sceco | 10/25/2025 13:59:26 | Major | 65101 | Door opening alarm | 10/25/2025 13:59:22 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0175 | FLM_EM | [8 empty] | API | 10/25/2025 13:59:46 | 10/25/2025 17:04:17 | 10/25/2025 17:34:39 | 10/25/2025 17:34:42 | 10/25/2025 17:34:45 | 10/25/2025 17:44:03 |  | Adel Abdelaziz Mohamed Ayedi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000518 | PCM-20251025-00001108 | TT-20251025-01185 | Reference_EM | Region_2 | RIY0264 | RIY0264 |  |  |  | Vignesh Sivakumar Sivakumar | 10/25/2025 14:19:26 | 10/25/2025 14:19:26 | 10/26/2025 02:19:26 | high temprature 40 at RIY0264-P2_SRAN @ Sceco | 10/25/2025 14:09:04 | Minor | 65103 | high temprature 40 | 10/25/2025 14:09:01 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0264 | FLM_EM | [8 empty] | API | 10/25/2025 14:19:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000526 | PCM-20251025-00001128 | TT-20251025-01194 | Telecom | Region_2 | LIQ0551 | LIQ0551 |  |  |  | Mohamed Moustafa Aboelmagd Hefny | 10/25/2025 14:29:01 | 10/25/2025 14:45:16 | 10/26/2025 02:29:01 | RF Unit Maintenance Link Failure at LIQ0551-P2_SRAN @ Sceco | 10/25/2025 14:21:45 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 14:21:21 | P2 | SRAN | buraidah | Sceco | 2G NSA | LIQ0551 | FLM_EM |  |  | PCM-20251025-00001123 | power issue at site // Power alarm REPORTED | power issue at site // Power alarm REPORTED |  |  |  | API | 10/25/2025 14:29:01 | 10/25/2025 14:45:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000539 | PCM-20251025-00001158 | TT-20251025-01228 | Reference_EM | Region_2 | QDY2810 | QDY2810 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Ahmed Hamada Mohamed Awad Abouhatab | 10/25/2025 14:40:35 | 10/25/2025 19:00:49 | 10/26/2025 02:40:35 | Door opening alarm at QDY2810-P3_SRAN @ Sceco | 10/25/2025 14:40:00 | Minor | 65101 | Door opening alarm | 10/25/2025 14:39:57 | P3 | SRAN | muzamiah | Sceco | 2G NSA | QDY2810 | FLM_EM | [8 empty] | API | 10/25/2025 14:40:35 | 10/25/2025 18:32:24 | 10/25/2025 18:32:32 | 10/25/2025 18:32:34 | 10/25/2025 18:32:36 | 10/25/2025 19:00:49 |  | Ahmed Hamada Mohamed Awad Abouhatab |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000542 | PCM-20251025-00001161 | TT-20251025-01233 | Reference_EM | Region_2 | RYQ0990 | RYQ0990 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/25/2025 14:43:40 | 10/25/2025 15:18:03 | 10/26/2025 02:43:40 | Door opening alarm at RYQ0990-P3_SRAN @ Sceco | 10/25/2025 14:43:16 | Minor | 65101 | Door opening alarm | 10/25/2025 14:43:12 | P3 | SRAN | rumah | Sceco | 2G NSA | RYQ0990 | FLM_EM | [8 empty] | API | 10/25/2025 14:43:40 | 10/25/2025 14:45:16 | 10/25/2025 14:45:22 | 10/25/2025 14:45:25 | 10/25/2025 14:45:28 | 10/25/2025 15:18:03 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000555 | PCM-20251025-00001202 | TT-20251025-01264 | Reference_EM | Region_1 | KBR0195 | KBR0195 |  |  |  | Abdul Malik Shaik | 10/25/2025 14:56:35 | 10/25/2025 22:36:06 | 10/25/2025 20:56:35 | Door opening alarm at KBR0195-P1-SHOP_SRAN @ Sceco | 10/25/2025 14:55:55 | Major | 65101 | Door opening alarm | 10/25/2025 14:55:51 | P1 | SRAN | dammam | Sceco | 2G NSA | KBR0195 | FLM_EM | [8 empty] | API | 10/25/2025 14:56:35 | 10/25/2025 22:36:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251025000574 | PCM-20251025-00001229 | TT-20251025-01282 | Reference_EM | Region_2 | BUR0064 | BUR0064 |  |  |  | Farman Ullah Muhammad Nazir | 10/25/2025 15:06:56 | 10/25/2025 15:06:56 | 10/26/2025 03:06:56 | Air condition 1 failure alarm at BUR0064-P3_SRAN-FON @ Sceco | 10/25/2025 14:56:26 | Minor | 65104 | Air condition 1 failure alarm | 10/25/2025 14:56:22 | P3 | SRAN | buraidah | Sceco | 2G NSA | BUR0064 | FLM_EM | [8 empty] | API | 10/25/2025 15:06:56 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251025000576 | PCM-20251025-00001234 | TT-20251025-01286 | Reference_EM | Region_2 | RIY2749 | RIY2749 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/25/2025 15:07:30 | 10/25/2025 15:22:40 | 10/26/2025 03:07:30 | Door opening alarm at RIY2749-P3_SRAN @ Sceco | 10/25/2025 15:06:51 | Minor | 65101 | Door opening alarm | 10/25/2025 15:06:48 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2749 | FLM_EM | [8 empty] | API | 10/25/2025 15:07:30 | 10/25/2025 15:22:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000582 | PCM-20251025-00001249 | TT-20251025-01301 | EM | Region_2 | RIY2755 | RIY2755 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/25/2025 15:15:21 | 10/25/2025 17:02:04 | 10/25/2025 19:15:21 | Door opening alarm at RIY2755-P1-VVVIP-WDM_SRAN-FON @ Sceco | 10/25/2025 15:14:42 | Critical | 65101 | Door opening alarm | 10/25/2025 15:14:38 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2755 | FLM_EM | [8 empty] | API | 10/25/2025 15:15:21 | 10/25/2025 17:02:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251025000594 | PCM-20251025-00001267 | TT-20251025-01319 | Reference_EM | Region_1 | RAF0511 | RAF0511 |  |  |  | Murtada Awad AbdElwahab Ahmed | 10/25/2025 15:25:37 | 10/25/2025 15:25:37 | 10/26/2025 03:25:37 | Door opening alarm at RAF0511-P2-USF_SRAN @ Sceco | 10/25/2025 15:24:43 | Minor | 65101 | Door opening alarm | 10/25/2025 15:24:40 | P2 | SRAN | rafha | Sceco | 2G NSA | RAF0511 | FLM_EM | [8 empty] | API | 10/25/2025 15:25:37 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000599 | PCM-20251025-00001280 | TT-20251025-01333 | Reference_EM | Region_1 | RFH0268 | RFH0268 | Enviroment | Air Condition | Change Fan | Ahmed Bashir Sahib Rahman | 10/25/2025 15:33:51 | 10/25/2025 16:39:32 | 10/26/2025 03:33:51 | Door opening at RFH2M7268-P3-PC @ Power Cube | 10/25/2025 15:33:03 | Minor | 65101 | Door opening | 10/25/2025 15:32:59 | P3 | 4G | quriyat | Power Cube | 2G NSA | RFH2M7268 | FLM_EM | [8 empty] | API | 10/25/2025 15:33:51 | 10/25/2025 16:38:37 | 10/25/2025 16:39:21 |  |  | 10/25/2025 16:39:32 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000607 | PCM-20251025-00001294 | TT-20251025-01355 | Reference_EM | Region_2 | RIY0797 | RIY0797 | Enviroment | Air Condition | Change Fan | Tanveer Ahmad Fateh Muhammad | 10/25/2025 15:43:35 | 10/25/2025 17:51:09 | 10/26/2025 03:43:35 | Air condition 1 failure alarm at RIY0797-P2_SRAN @ Sceco | 10/25/2025 15:35:47 | Minor | 65104 | Air condition 1 failure alarm | 10/25/2025 15:33:17 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0797 | FLM_EM | [8 empty] | API | 10/25/2025 15:43:35 | 10/25/2025 17:02:04 | 10/25/2025 17:38:10 | 10/25/2025 17:38:12 | 10/25/2025 17:38:13 | 10/25/2025 17:51:09 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000619 | PCM-20251025-00001319 | TT-20251025-01383 | Reference_EM | Region_1 | RFH0268 | RFH0268 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Bashir Sahib Rahman | 10/25/2025 15:56:31 | 10/25/2025 16:39:09 | 10/26/2025 03:56:31 | Air-Condition #1 FA(SH2) at RFH2M7268-P3-PC @ Power Cube | 10/25/2025 15:45:52 | Minor | 65052 | Air-Condition #1 FA(SH2) | 10/25/2025 15:45:48 | P3 | 4G | quriyat | Power Cube | 2G NSA | RFH2M7268 | FLM_EM | [8 empty] | API | 10/25/2025 15:56:31 | 10/25/2025 16:38:37 | 10/25/2025 16:38:56 |  |  | 10/25/2025 16:39:09 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000620 | PCM-20251025-00001321 | TT-20251025-01386 | Reference_EM | Region_1 | HFAP2035 | HFAP2035 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/25/2025 15:59:11 | 10/25/2025 15:59:11 | 10/25/2025 21:59:11 | Door opening alarm at HFAP2035-P1-HUB_SRAN @ Sceco | 10/25/2025 15:58:19 | Major | 65101 | Door opening alarm | 10/25/2025 15:58:15 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFAP2035 | FLM_EM | [8 empty] | API | 10/25/2025 15:59:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000625 | PCM-20251025-00001332 | TT-20251025-01395 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 16:05:21 | 10/26/2025 10:21:02 | 10/26/2025 04:05:21 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/25/2025 15:55:04 | Minor | 65107 | Major Rec alarm | 10/25/2025 15:55:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/25/2025 16:05:21 | 10/26/2025 10:21:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000627 | PCM-20251025-00001335 | TT-20251025-01397 | Reference_EM | Region_1 | DAM2474 | DAM2474 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/25/2025 16:06:21 | 10/25/2025 22:23:51 | 10/25/2025 22:06:21 | Low battery voltage at DAM2474-P1-SHOP_SRAN @ Sceco | 10/25/2025 15:55:49 | Major | 65110 | Low battery voltage | 10/25/2025 15:55:45 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2474 | FLM_EM | [8 empty] | API | 10/25/2025 16:06:21 | 10/25/2025 22:23:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000645 | PCM-20251025-00001369 | TT-20251025-01430 | Reference_EM | Region_1 | HFAP2035 | HFAP2035 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/25/2025 16:23:56 | 10/25/2025 16:23:56 | 10/25/2025 22:23:56 | Major Rec alarm at HFAP2035-P1-HUB_SRAN @ Sceco | 10/25/2025 16:13:39 | Major | 65107 | Major Rec alarm | 10/25/2025 16:13:36 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFAP2035 | FLM_EM | [8 empty] | API | 10/25/2025 16:23:56 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251025000648 | PCM-20251025-00001382 | TT-20251025-01442 | Reference_EM | Region_2 | RAS2248 | RAS2248 |  |  |  | Mohamed Alfatih Mohamed Eltayeb Mohamed | 10/25/2025 16:31:41 | 10/25/2025 16:31:41 | 10/25/2025 22:31:41 | Air condition 1 failure alarm at RAS2248-FWA-P1-VIP_SRAN @ Sceco | 10/25/2025 16:21:04 | Major | 65104 | Air condition 1 failure alarm | 10/25/2025 16:20:59 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS2248 | FLM_EM | [8 empty] | API | 10/25/2025 16:31:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000658 | PCM-20251025-00001404 | TT-20251025-01466 | Reference_EM | Region_2 | RIY2761 | RIY2761 |  |  |  | Adham Adham Hassan Farghal | 10/25/2025 16:46:41 | 10/26/2025 09:36:34 | 10/26/2025 04:46:41 | Mains Failure at RIY2761-P2_SRAN @ Sceco | 10/25/2025 16:36:35 | Minor | 65109 | Mains Failure | 10/25/2025 16:36:32 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2761 | FLM_EM | [8 empty] | API | 10/25/2025 16:46:41 | 10/26/2025 09:36:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000666 | PCM-20251025-00001431 | TT-20251025-01506 | Reference_EM | Region_2 | RIY0446 | RIY0446 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 17:10:55 | 10/26/2025 10:21:03 | 10/26/2025 05:10:55 | Minor Rec alarm at RIY0446-P2_SRAN @ Sceco | 10/25/2025 17:00:39 | Minor | 65108 | Minor Rec alarm | 10/25/2025 17:00:34 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0446 | FLM_EM | [8 empty] | API | 10/25/2025 17:10:55 | 10/26/2025 10:21:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000667 | PCM-20251025-00001432 | TT-20251025-01508 | Reference_EM | Region_1 | SAK0567 | SAK0567 |  |  |  | Mohamed Amjad Muhammad | 10/25/2025 17:13:01 | 10/26/2025 10:24:00 | 10/26/2025 05:13:01 | Door opening alarm at SAK0567-P2_SRAN @ Sceco | 10/25/2025 17:12:20 | Minor | 65101 | Door opening alarm | 10/25/2025 17:12:17 | P2 | SRAN | sakaka | Sceco | 2G NSA | SAK0567 | FLM_EM | [8 empty] | API | 10/25/2025 17:13:01 | 10/26/2025 10:24:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000668 | PCM-20251025-00001433 | TT-20251025-01510 | Reference_EM | Region_1 | DAM0440 | DAM0440 |  |  |  | Mohamed Abdalgader farah Rahmtalla | 10/25/2025 17:13:31 | 10/25/2025 17:16:07 | 10/26/2025 05:13:31 | high temprature 40 at DAM0440-P2_SRAN @ Sceco | 10/25/2025 17:03:13 | Minor | 65103 | high temprature 40 | 10/25/2025 17:03:09 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0440 | FLM_EM | [8 empty] | API | 10/25/2025 17:13:31 | 10/25/2025 17:16:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000671 | PCM-20251025-00001446 | TT-20251025-01344 | Telecom | Region_1 | HMBY2429 | HMBY2429 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/25/2025 17:19:56 | 10/25/2025 17:48:27 | 10/26/2025 05:19:56 | Transmission Optical Interface Error at HMBY2429-P1-VIP_SRAN @ Generator_SG | 10/25/2025 15:32:43 | Minor | 26222 | Transmission Optical Interface Error | 10/25/2025 15:31:09 | VIP | SRAN | dammam | Generator_SG | 2G NSA | HMBY2429 | FLM_EM |  |  | PCM-20251025-00001284 | power issue at site | power issue at site |  |  |  | API | 10/25/2025 17:19:56 | 10/25/2025 17:46:04 | 10/25/2025 17:48:15 |  |  | 10/25/2025 17:48:27 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251025000678 | PCM-20251025-00001459 | TT-20251025-01531 | Reference_EM | Region_1 | ABQ0530 | ABQ0530 |  |  |  | Ahmed AbdELmoaz Ibrahim | 10/25/2025 17:27:01 | 10/25/2025 17:27:01 | 10/25/2025 23:27:01 | Door opening alarm at ABQ0530-P1-USF-HUB_SRAN-PC @ Power Cube | 10/25/2025 17:26:10 | Major | 65101 | Door opening alarm | 10/25/2025 17:26:06 | P1 | SRAN | dammam | Power Cube | 2G NSA | ABQ0530 | FLM_EM | [8 empty] | API | 10/25/2025 17:27:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000691 | PCM-20251025-00001493 | TT-20251025-01562 | Reference_EM | Region_1 | ABQ0530 | ABQ0530 |  |  |  | Ahmed AbdELmoaz Ibrahim | 10/25/2025 17:43:26 | 10/25/2025 17:43:26 | 10/25/2025 23:43:26 | Generator failure at ABQ0530-P1-USF-HUB_SRAN-PC @ Power Cube | 10/25/2025 17:33:05 | Major | 65114 | Generator failure | 10/25/2025 17:33:01 | P1 | SRAN | dammam | Power Cube | 2G NSA | ABQ0530 | FLM_EM | [8 empty] | API | 10/25/2025 17:43:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000702 | PCM-20251025-00001522 | TT-20251025-01588 | Reference_EM | Region_2 | HYN0067 | HYN0067 |  |  |  | Kazi Jalil Allimiya | 10/25/2025 18:00:06 | 10/26/2025 10:16:37 | 10/26/2025 06:00:06 | Door opening alarm at HYN0067-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 17:59:26 | Minor | 65101 | Door opening alarm | 10/25/2025 17:52:35 | P3 | SRAN | aflaj | Power Cube | 2G NSA | HYN0067 | FLM_EM | [8 empty] | API | 10/25/2025 18:00:06 | 10/26/2025 10:16:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000705 | PCM-20251025-00001526 | TT-20251025-01593 | Reference_EM | Region_2 | RIY0395 | RIY0395 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 10/25/2025 18:08:51 | 10/25/2025 18:08:51 | 10/26/2025 06:08:51 | Door opening alarm at RIY0395-P2_SRAN @ Generator_SG | 10/25/2025 18:08:08 | Minor | 65101 | Door opening alarm | 10/25/2025 18:08:03 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0395 | FLM_EM | [8 empty] | API | 10/25/2025 18:08:51 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000721 | PCM-20251025-00001556 | TT-20251025-01638 | EM | Region_1 | RYHR9915 | RYHR9915 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 18:42:56 | 10/26/2025 09:14:03 | 10/26/2025 06:42:56 | NETECO: Genset Work Abnormal at RYHR9915 @ Generator_SG | 10/25/2025 18:36:27 | Minor | 40561 | Genset Work Abnormal | 10/25/2025 18:36:27 | P3 | Repeater | hafr | Generator_SG | 2G NSA | RYHR9915 | FLM_EM | [8 empty] | API | 10/25/2025 18:42:56 | 10/25/2025 19:08:19 | 10/26/2025 09:13:55 |  |  | 10/26/2025 09:14:03 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000729 | PCM-20251025-00001571 | TT-20251025-01652 | EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 19:02:00 | 10/26/2025 09:20:15 | 10/26/2025 07:02:00 | NETECO: Communication Failure at RIY2431 @ Sceco | 10/25/2025 18:55:32 | Minor | 13750 | Communication Failure | 10/25/2025 18:55:32 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/25/2025 19:02:00 | 10/26/2025 09:20:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000734 | PCM-20251025-00001591 | TT-20251025-01671 | EM | Region_2 | RIY0041 | RIY0041 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 19:21:11 | 10/26/2025 09:20:16 | 10/25/2025 23:21:11 | Mains Failure at RIY0041-P1-DIA-WDM_SRAN @ Sceco | 10/25/2025 19:19:11 | Critical | 65109 | Mains Failure | 10/25/2025 19:19:07 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0041 | FLM_EM | [8 empty] | API | 10/25/2025 19:21:11 | 10/26/2025 09:20:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251025000735 | PCM-20251025-00001592 | TT-20251025-01672 | EM | Region_2 | RIY0041 | RIY0041 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 19:21:40 | 10/26/2025 09:20:16 | 10/25/2025 23:21:40 | ACU FAILURE at RIY0041_HYB @ Sceco | 10/25/2025 19:19:45 | Critical | 1-12307 | ACU FAILURE | 10/25/2025 19:19:35 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0041 | FLM_EM | [5 empty] | 0-TO RIY0202(1-A)-72-E1EFI-ACU FAILURE:2 |  |  | API | 10/25/2025 19:21:40 | 10/26/2025 09:20:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251025000738 | PCM-20251025-00001596 | TT-20251025-01676 | EM | Region_1 | DAM0440 | DAM0440 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/25/2025 19:24:16 | 10/26/2025 11:03:39 | 10/26/2025 07:24:16 | TEMP_ALARM at DAM0440_NE_1_SDB @ Sceco | 10/25/2025 19:18:45 | Minor | 1-166 | TEMP_ALARM | 10/25/2025 19:18:35 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0440 | FLM_EM | [8 empty] | API | 10/25/2025 19:24:16 | 10/25/2025 19:59:22 | 10/26/2025 10:30:48 | 10/26/2025 10:30:51 | 10/26/2025 10:30:54 | 10/26/2025 11:03:39 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000748 | PCM-20251025-00001608 | TT-20251025-01691 | Reference_EM | Region_2 | RIY0518 | RIY0518 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 19:33:35 | 10/26/2025 10:21:03 | 10/26/2025 07:33:35 | Minor Rec alarm at RIY0518-P2_SRAN @ Sceco | 10/25/2025 19:23:01 | Minor | 65108 | Minor Rec alarm | 10/25/2025 19:22:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0518 | FLM_EM | [8 empty] | API | 10/25/2025 19:33:35 | 10/26/2025 10:21:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000750 | PCM-20251025-00001610 | TT-20251025-01694 | Reference_EM | Region_2 | UNK0183 | UNK0183 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Omar Fathy Mahmoud Elsayed | 10/25/2025 19:37:10 | 10/25/2025 22:57:04 | 10/26/2025 07:37:10 | Door opening alarm at UNK2M5183-P3 @ Generator_SG | 10/25/2025 19:36:47 | Minor | 65101 | Door opening alarm | 10/25/2025 19:36:43 | P3 | 2G | buraidah | Generator_SG | 2G NSA | UNK2M5183 | FLM_EM | [8 empty] | API | 10/25/2025 19:37:10 | 10/25/2025 22:14:48 | 10/25/2025 22:15:31 | 10/25/2025 22:15:55 | 10/25/2025 22:16:12 | 10/25/2025 22:57:04 |  | Omar Fathy Mahmoud Elsayed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000752 | PCM-20251025-00001614 | TT-20251025-01698 | Reference_EM | Region_1 | ARM0879 | ARM0879 |  |  |  | Nazar Mohammed Siddig Abdalla | 10/25/2025 19:39:46 | 10/25/2025 19:39:46 | 10/26/2025 07:39:46 | Low battery voltage at ARM0879-P3_SRAN-PC @ Power Cube | 10/25/2025 19:35:16 | Minor | 65110 | Low battery voltage | 10/25/2025 19:29:10 | P3 | SRAN | hafouf | Power Cube | 2G NSA | ARM0879 | FLM_EM | [8 empty] | API | 10/25/2025 19:39:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000758 | PCM-20251025-00001632 | TT-20251025-01721 | Reference_EM | Region_1 | HFF0224 | HFF0224 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/25/2025 19:58:21 | 10/25/2025 19:58:21 | 10/26/2025 07:58:21 | high temprature 40 at HFF0224-P3_SRAN @ Generator_SG | 10/25/2025 19:47:41 | Minor | 65103 | high temprature 40 | 10/25/2025 19:47:37 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | HFF0224 | FLM_EM | [8 empty] | API | 10/25/2025 19:58:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000762 | PCM-20251025-00001638 | TT-20251025-01724 | Reference_EM | Region_1 | HFF0015 | HFF0015 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/25/2025 20:01:56 | 10/25/2025 21:13:40 | 10/26/2025 08:01:56 | Door opening alarm at HFF0015-P2_SRAN @ Sceco | 10/25/2025 20:01:24 | Minor | 65101 | Door opening alarm | 10/25/2025 20:01:21 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0015 | FLM_EM | [8 empty] | API | 10/25/2025 20:01:56 | 10/25/2025 20:48:15 | 10/25/2025 21:07:50 | 10/25/2025 21:07:57 | 10/25/2025 21:08:17 | 10/25/2025 21:13:40 |  | Shahid Khan Dilawar Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000773 | PCM-20251025-00001662 | TT-20251025-01738 | Reference_EM | Region_1 | RAF2521 | RAF2521 |  |  |  | Murtada Awad AbdElwahab Ahmed | 10/25/2025 20:32:26 | 10/25/2025 20:32:26 | 10/26/2025 08:32:26 | Mains Failure at RAF2521-P2-USF_SRAN @ Sceco | 10/25/2025 20:22:10 | Minor | 65109 | Mains Failure | 10/25/2025 20:22:05 | P2 | SRAN | rafha | Sceco | 2G NSA | RAF2521 | FLM_EM | [8 empty] | API | 10/25/2025 20:32:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000779 | PCM-20251025-00001678 | TT-20251025-01756 | Reference_EM | Region_1 | DMJ9917 | DMJ9917 |  |  |  | Imran Qamar Ghulam Qamar | 10/25/2025 20:46:26 | 10/25/2025 20:51:02 | 10/26/2025 08:46:26 | Low fuel alarm at DMJ9917-RPT @ Generator_SG | 10/25/2025 20:35:51 | Minor | 65115 | Low fuel alarm | 10/25/2025 20:35:48 | P3 | Repeater | hafr | Generator_SG | 3G NSA | DMJ9917 | FLM_EM | [8 empty] | API | 10/25/2025 20:46:26 | 10/25/2025 20:51:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000805 | PCM-20251025-00001766 | TT-20251025-01826 | Telecom | Region_2 | RIY2529 | RIY2529 | Equipment | Power Cable_RRU_BTS | Change Port on DCDU | Ejaz Hussain Muhammad Sharif | 10/25/2025 21:57:27 | 10/26/2025 07:14:46 | 10/26/2025 03:57:27 | NR Cell Unavailable at RIY2529-P2_SRAN @ Sceco | 10/25/2025 21:49:42 | Major | 29841 | NR Cell Unavailable | 10/25/2025 21:49:18 | P2 | SRAN | riyadh | Sceco | 5G SA | RIY2529 | FLM_TE | [8 empty] | API | 10/25/2025 21:57:27 | 10/26/2025 07:13:27 | 10/26/2025 07:14:19 |  |  | 10/26/2025 07:14:46 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000807 | PCM-20251025-00001772 | TT-20251025-01832 | Telecom | Region_2 | RIY2529 | RIY2529 | Equipment | Power Cable_RRU_BTS | Change Port on DCDU | Ejaz Hussain Muhammad Sharif | 10/25/2025 22:00:02 | 10/26/2025 07:15:17 | 10/26/2025 04:00:02 | BBU CPRI Interface Error at RIY2529-P2_SRAN @ Sceco | 10/25/2025 21:55:33 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 21:53:01 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2529 | FLM_TE | [8 empty] | API | 10/25/2025 22:00:02 | 10/26/2025 07:13:26 | 10/26/2025 07:14:56 |  |  | 10/26/2025 07:15:17 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000811 | PCM-20251025-00001786 | TT-20251025-01850 | Telecom | Region_4 | JED0765 | JED0765 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 22:18:38 | 10/25/2025 22:18:38 | 10/26/2025 10:18:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0765-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 22:17:34 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:17:26 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0765 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 22:18:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000812 | PCM-20251025-00001787 | TT-20251025-01841 | Telecom | Region_1 | HFS2026 | HFS2026 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 22:22:10 | 10/26/2025 09:34:40 | 10/26/2025 04:22:10 | 2(3G) 1(LTE) sites down under BTA0696-P3,HFS2535-P3-USF/HF1RNCH01 @ Power Cube | 10/25/2025 22:08:37 | Major | 22214 | NodeB Unavailable | 10/25/2025 22:08:34 | P3 | SRAN | hafouf | Generator_SG | 3G SA | HFS2535-P3-USF 3G,BTA0696-P3 3G | FLM_TE | HFS2026 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SLW0899 DIR HFS2026 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM | PCM-20251025-00001783 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SLW0899 DIR HFS2026 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SLW0899 DIR HFS2026 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM |  | sites down |  | API | 10/25/2025 22:22:10 | 10/26/2025 09:34:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000816 | PCM-20251025-00001799 | TT-20251025-01863 | Telecom | Region_5 | MAK2215 | MAK2215 |  |  |  | Atif Javed Javed Hussain | 10/25/2025 22:35:10 | 10/25/2025 22:35:10 | 10/26/2025 10:35:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2215-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/25/2025 22:34:27 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:34:20 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2215 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 22:35:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000817 | PCM-20251025-00001801 | TT-20251025-01788 | Reference_telecom | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 22:36:21 | 10/25/2025 22:36:21 | 10/26/2025 04:36:21 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/25/2025 21:08:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 21:08:47 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7558 | FLM_TE |  |  | PCM-20251025-00001699 | perform HC | perform HC |  |  |  | API | 10/25/2025 22:36:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000818 | PCM-20251025-00001802 | TT-20251025-01858 | Reference_telecom | Region_6 | KMS2462 | KMS2462 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Muhammad shafiq Muhammad Rasheed | 10/25/2025 22:36:36 | 10/26/2025 00:53:12 | 10/26/2025 04:36:36 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at KMS2462-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Generator_SG | 10/25/2025 22:23:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:23:43 | P3 | 2G | Khamis Mushait | Generator_SG | 5G_Cell SA | KMS2462 | FLM_TE |  |  | PCM-20251025-00001790 | perform HC | perform HC |  |  |  | API | 10/25/2025 22:36:36 | 10/25/2025 23:07:56 | 10/25/2025 23:10:35 | 10/25/2025 23:10:39 | 10/25/2025 23:39:30 | 10/26/2025 00:53:12 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000819 | PCM-20251025-00001803 | TT-20251025-01751 | Telecom | Region_5 | MAK1M9254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/25/2025 22:38:42 | 10/25/2025 22:38:42 | 10/26/2025 04:38:42 | BASE STATION ANTENNA LINE PROBLEM at MAK1M9254-P1-SHOP-CA-L800-SBTS @ Sceco | 10/25/2025 20:35:12 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 20:35:00 | P1 | 4G | makkah | Sceco | LTE NSA | MAK1M9254 | FLM_TE |  |  | PCM-20251025-00001674 | Perform HC | Perform HC |  |  |  | API | 10/25/2025 22:38:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000820 | PCM-20251025-00001805 | TT-20251025-01864 | Telecom | Region_4 | JED1U6739 | JED6039 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 22:39:03 | 10/25/2025 22:39:03 | 10/26/2025 04:39:03 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/25/2025 22:29:01 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 22:28:54 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251025-00001800 | cleared | cleared |  |  |  | API | 10/25/2025 22:39:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000821 | PCM-20251025-00001810 | TT-20251025-01873 | Reference_telecom | Region_4 | JED6154 | JED6154 |  |  |  | Mohamed Farag Abdelbary | 10/25/2025 22:44:27 | 10/25/2025 22:44:27 | 10/26/2025 10:44:27 | LossOfSignal observed in JED6154 towards 10.10.150.116 @ Sceco | 10/25/2025 10:45:03 | Minor |  | LossOfSignal | 10/25/2025 10:44:07 | P3 | 2G | jeddah | Sceco | TX NSA | JED6154 | FLM_TE | [8 empty] | API | 10/25/2025 22:44:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000822 | PCM-20251025-00001812 | TT-20251025-01875 | Telecom | Region_5 | HHR0429 | HHR0429 |  |  |  | Amjad Ali Muhammad Parves | 10/25/2025 22:45:29 | 10/26/2025 10:29:31 | 10/26/2025 04:45:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at HHR0429-G9-L8-L18-L21-NNR2.6-SBTS-P1-VIP-HHR @ Generator_SG | 10/25/2025 22:44:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:44:27 | VIP | 2G | makkah | Generator_SG | 5G_Cell SA | HHR0429 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 22:45:29 | 10/26/2025 10:29:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000823 | PCM-20251025-00001813 | TT-20251025-01877 | EM | Region_3 | RUSF9023 | RUSF9023 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/25/2025 22:46:31 | 10/25/2025 22:46:31 | 10/26/2025 10:46:31 | NETECO: Communication Failure at RUSF9023 @ Generator_DG | 10/25/2025 22:40:07 | Minor | 17451 | Communication Failure | 10/25/2025 22:40:07 | P3 | Repeater | hail | Generator_DG | 2G NSA | RUSF9023 | FLM_EM | [8 empty] | API | 10/25/2025 22:46:31 | [10 empty] | EM | Zain |  | Running |  | OWS
Departed | CM20251025000824 | PCM-20251025-00001814 | TT-20251025-01867 | Reference_telecom | Region_5 | MAK0676 | MAK0676 |  |  |  | Amjad Ali Muhammad Parves | 10/25/2025 22:48:32 | 10/26/2025 10:29:44 | 10/26/2025 10:48:32 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at MAK0676-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 22:34:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:34:00 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK0676 | FLM_TE |  |  | PCM-20251025-00001804 | cleared | cleared |  |  |  | API | 10/25/2025 22:48:32 | 10/26/2025 09:58:41 | 10/26/2025 10:29:41 | 10/26/2025 10:29:44 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000825 | PCM-20251025-00001815 | TT-20251025-01878 | Reference_EM | Region_1 | SKJF0199 | SKJF0199 | Enviroment | Circuit Breaker/Owner | Change MDB main breaker | Ahmed Bashir Sahib Rahman | 10/25/2025 22:50:07 | 10/26/2025 01:51:15 | 10/26/2025 04:50:07 | Mains Failure at SKJF0199-P1-HUB_SRAN @ Sceco | 10/25/2025 22:40:21 | Major | 65109 | Mains Failure | 10/25/2025 22:40:18 | P1 | SRAN | quriyat | Sceco | 2G NSA | SKJF0199 | FLM_EM | [8 empty] | API | 10/25/2025 22:50:07 | 10/25/2025 22:52:33 | 10/26/2025 01:50:45 |  |  | 10/26/2025 01:51:15 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000826 | PCM-20251025-00001816 | TT-20251025-01879 | Telecom | Region_4 | JED1MN0217 | JED0217 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/25/2025 22:50:07 | 10/25/2025 22:50:07 | 10/26/2025 02:50:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0217-NR2.6-P1 @ Sceco | 10/25/2025 22:49:15 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:49:02 | P1 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0217 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 22:50:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000827 | PCM-20251025-00001818 | TT-20251025-01521 | Reference_telecom | Region_4 | TURY0692 | TURY0692 |  |  |  | Ahmad Kamal Abdelmawla | 10/25/2025 22:51:44 | 10/26/2025 09:33:52 | 10/26/2025 04:51:44 | BCF NOTIFICATION (FF FF FF FF FF FF) at TURY0692-P3 @ Generator_SG | 10/25/2025 17:14:19 | Major | 7602 | BCF NOTIFICATION | 10/25/2025 17:14:06 | P3 | 2G | taif | Generator_SG | 2G NSA | TURY0692 | FLM_TE |  |  | PCM-20251025-00001450 | cleared | cleared |  |  |  | API | 10/25/2025 22:51:44 | 10/26/2025 09:33:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000828 | PCM-20251025-00001820 | TT-20251025-01881 | Reference_telecom | Region_2 | RIY2M8278 | RIY2278 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Farmanullah Akbar Jan | 10/25/2025 22:57:22 | 10/26/2025 11:00:27 | 10/26/2025 10:57:22 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8278-P3-CA-L800 @ Sceco | 10/25/2025 19:55:47 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 19:55:44 | P3 | 4G | riyadh | Sceco | 2G NSA | RIY2M8278 | FLM_TE |  |  | PCM-20251025-00001819 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/25/2025 22:57:22 | 10/26/2025 09:26:35 | 10/26/2025 09:28:13 | 10/26/2025 09:28:21 | 10/26/2025 09:47:03 | 10/26/2025 11:00:27 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000829 | PCM-20251025-00001822 | TT-20251025-01882 | Telecom | Region_5 | MAK1M9376 | MAK0376 |  |  |  | Atif Javed Javed Hussain | 10/25/2025 22:58:23 | 10/25/2025 22:58:23 | 10/26/2025 04:58:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9376-P1-VIP-HAJJ-HRM-L800-SBTS @ Sceco | 10/25/2025 22:57:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:57:48 | VIP | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9376 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 22:58:23 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000831 | PCM-20251025-00001835 | TT-20251025-01890 | EM | Region_6 | BHAB1M7819 | BHAB0819 |  |  |  | Arif Ullah Shah | 10/25/2025 23:05:38 | 10/26/2025 02:45:54 | 10/26/2025 11:05:38 | SHELTER DOOR OPEN at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/25/2025 23:05:23 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 23:05:16 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7819 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 23:05:38 | 10/26/2025 02:45:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251025000837 | PCM-20251025-00001849 | TT-20251025-01904 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/25/2025 23:30:26 | 10/25/2025 23:30:26 | 10/26/2025 11:30:26 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/25/2025 23:29:39 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 23:29:29 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 23:30:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000838 | PCM-20251025-00001852 | TT-20251025-01906 | Reference_EM | Region_3 | YBDB2292 | YBDB2292 |  |  |  | Eid Fawzi Sayed Ali | 10/25/2025 23:32:31 | 10/26/2025 09:51:37 | 10/26/2025 05:32:31 | Fire Fighting system alarm at YBDB2292-P1-HUB_SRAN @ Generator_DG | 10/25/2025 23:22:23 | Major | 65111 | Fire Fighting system alarm | 10/25/2025 23:22:19 | P1 | SRAN | tabouk | Generator_DG | 2G NSA | YBDB2292 | FLM_EM | [8 empty] | API | 10/25/2025 23:32:31 | 10/26/2025 09:51:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000840 | PCM-20251025-00001858 | TT-20251025-01912 | Telecom | Region_6 | JEC1M7286 | JEC0286 | Equipment | SFP_BTS | Replace SFP | Ansir Iqbal Muhammad Iqbal | 10/25/2025 23:35:05 | 10/26/2025 09:02:05 | 10/26/2025 11:35:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JEC1M7286-G9-L8-L18-L21-SBTS-P2 @ Generator_SG | 10/25/2025 23:34:17 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 23:34:12 | VIP | 4G | baish | Generator_SG | 5G_Cell SA | JEC1M7286 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/25/2025 23:35:05 | 10/26/2025 04:00:36 | 10/26/2025 09:01:44 |  |  | 10/26/2025 09:02:05 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251025000841 | PCM-20251025-00001863 | TT-20251025-01915 | Reference_telecom | Region_2 | BUR0019 | BUR0019 |  |  |  | Raise Ahmed Nisar Ahmed | 10/25/2025 23:42:19 | 10/26/2025 03:15:18 | 10/26/2025 03:42:19 | Violation TT ¦¦ SALAM : LINK DOWN B/W QSHL0737-LH-BUR0019-LH ¦¦ CRQ000000158105 | 10/25/2025 23:41:48 | Critical | 1-14579 | POWER_JITTER | 10/25/2025 23:41:35 | P1 | SRAN | buraidah | Sceco_STB | DWDM NSA | BUR0019 | FLM_TE | [5 empty] | 0-TO QSHL0737(1-A)-2-G6WDAPXF-11(LINEIN/LINEOUT(TO QSHL0737_OCS-TNG6WDAPXF(1-D02)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/25/2025 23:42:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000843 | PCM-20251025-00001865 | TT-20251025-01918 | EM | Region_6 | ABH0280 | ABH0280 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/25/2025 23:44:24 | 10/26/2025 09:37:17 | 10/26/2025 11:44:24 | SHELTER DOOR OPEN at ABH0280-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/25/2025 23:44:08 | Minor | 7103 | SHELTER DOOR OPEN | 10/25/2025 23:43:57 | P2 | 2G | abha | Sceco | 2G NSA | ABH0280 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/25/2025 23:44:24 | 10/26/2025 09:37:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000848 | PCM-20251025-00001874 | TT-20251025-01922 | Telecom | Region_2 | DWD2113 | DWD2113 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Zakir Muhammad Yar Muhammad | 10/25/2025 23:50:35 | 10/26/2025 04:00:08 | 10/26/2025 05:50:35 | BBU Board Maintenance Link Failure at DWD2113-P3_SRAN @ Sceco | 10/25/2025 23:47:48 | Major | 26205 | BBU Board Maintenance Link Failure | 10/25/2025 23:46:15 | P3 | SRAN | dawadmi | Sceco | 2G NSA | DWD2113 | FLM_TE | [8 empty] | API | 10/25/2025 23:50:35 | 10/26/2025 00:55:54 | 10/26/2025 03:59:45 |  |  | 10/26/2025 04:00:08 |  | Zakir Muhammad Yar Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000849 | PCM-20251025-00001875 | TT-20251025-01923 | Telecom | Region_2 | DWD2113 | DWD2113 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Zakir Muhammad Yar Muhammad | 10/25/2025 23:51:37 | 10/26/2025 04:00:42 | 10/26/2025 11:51:37 | RF Unit Maintenance Link Failure at DWD2113-P3_SRAN @ Sceco | 10/25/2025 23:48:06 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 23:46:22 | P3 | SRAN | dawadmi | Sceco | 2G NSA | DWD2113 | FLM_TE | [8 empty] | API | 10/25/2025 23:51:37 | 10/26/2025 00:55:55 | 10/26/2025 04:00:18 |  |  | 10/26/2025 04:00:42 |  | Zakir Muhammad Yar Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000850 | PCM-20251025-00001876 | TT-20251025-01927 | Telecom | Region_1 | HFF0224 | HFF0224 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 23:56:15 | 10/26/2025 09:34:40 | 10/26/2025 05:56:15 | BBU CPRI Interface Error at HFF0224-P3_SRAN @ Generator_SG | 10/25/2025 22:08:46 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 22:06:13 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | HFF0224 | FLM_TE | [8 empty] | API | 10/25/2025 23:56:15 | 10/26/2025 09:34:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000851 | PCM-20251025-00001878 | TT-20251025-01925 | Telecom | Region_6 | RYNJ0205 | RYNJ0205 | Transsmission | MW_RSL_fading | Fading issue | Saif Muhammad | 10/25/2025 23:58:01 | 10/26/2025 01:43:35 | 10/26/2025 05:58:01 | 1(5G) sites down under RYNJ0205-GSM-P3-HUB @ Generator_SG | 10/25/2025 23:49:59 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 23:49:56 | P1 | 2G | wadi dawasar | Generator_SG | 5G SA | RYNJ0205-GSM-P3-HUB | FLM_TE | RYNJ0205 | Results: DOWN SITE HUB RYNJ0205-GSM-P3-HUB RYNJ0205 Summary: Hub: RYNJ0205, Down Count: 1, Down Sites: RYNJ0205-GSM-P3-HUB Alarm Summary: RYNJ0205 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.102.77.84:8080] [URL:http://10.102.77.84:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 23:58:01 | 10/26/2025 01:42:34 | 10/26/2025 01:43:04 |  |  | 10/26/2025 01:43:35 |  | Saif Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000853 | PCM-20251025-00001881 | TT-20251025-01926 | EM | Region_4 | JED2178 | JED2178 | Equipment | BSS_HW_fault | Replace RF Module | Khaled Mohammad Abdallah | 10/25/2025 23:59:58 | 10/26/2025 08:15:14 | 10/26/2025 05:59:58 | 1(2G/LTE) sites down under JED2178-P3/JED2178-P3 @ Sceco | 10/25/2025 23:51:51 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 23:51:47 | P3 | 2G | jeddah | Sceco | 2G SA | JED2178-P3 | FLM_TE | JED2178 | Results: DOWN SITE HUB JED2178-P3 JED2178 Summary: Hub: JED2178, Down Count: 1, Down Sites: JED2178-P3 Alarm Summary: JED2178 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 23:59:58 |  | 10/26/2025 06:10:47 | 10/26/2025 06:10:49 | 10/26/2025 06:10:51 | 10/26/2025 08:15:14 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000001 | PCM-20251026-00000002 | TT-20251026-00001 | Telecom | Region_6 | KMS0168 | KMS0168 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/26/2025 00:04:01 | 10/26/2025 01:03:02 | 10/26/2025 12:04:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS0168-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 00:03:22 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 00:03:14 | P3 | 2G | khamis mushyet | Sceco | 5G_Cell SA | KMS0168 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 00:04:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000002 | PCM-20251026-00000003 | TT-20251026-00002 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 00:04:31 | 10/26/2025 10:00:13 | 10/26/2025 06:04:31 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/25/2025 21:02:52 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/25/2025 21:03:59 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/26/2025 00:04:31 | 10/26/2025 10:00:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000003 | PCM-20251026-00000005 | TT-20251025-01883 | Telecom | Region_6 | JIZ1U6797 | JIZ6097 |  |  |  | Osama Hadi | 10/26/2025 00:05:10 | 10/26/2025 03:25:21 | 10/26/2025 06:05:10 | BASE STATION ANTENNA LINE PROBLEM at JIZ1U6797-G9-L18-SBTS-P1-VIP-SHOP @ Sceco | 10/25/2025 22:52:14 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 22:52:03 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1U6797 | FLM_TE |  |  | PCM-20251025-00001823 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 00:05:10 | 10/26/2025 03:25:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000004 | PCM-20251026-00000006 | TT-20251026-00003 | Telecom | Region_1 | HFR6002 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 00:07:06 | 10/26/2025 00:30:02 | 10/26/2025 06:07:06 | BBU CPRI Interface Error at HFR6002-P3_SRAN @ Sceco | 10/26/2025 00:02:29 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 00:00:13 | P3 | SRAN | hafr | Sceco | 2G NSA | HFR6002 | FLM_TE | [8 empty] | API | 10/26/2025 00:07:06 | 10/26/2025 00:30:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000005 | PCM-20251026-00000008 | TT-20251026-00006 | EM | Region_3 | YBDB2291 | YBDB2291 | Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue | Sayed Satoor | 10/26/2025 00:07:38 | 10/26/2025 03:41:53 | 10/26/2025 04:07:38 | Mains Failure at YBDB2291-P1-WDM-HUB_SRAN @ Generator_DG | 10/26/2025 00:06:06 | Critical | 65109 | Mains Failure | 10/26/2025 00:06:03 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | YBDB2291 | FLM_EM | [8 empty] | API | 10/26/2025 00:07:38 | 10/26/2025 03:41:05 | 10/26/2025 03:41:34 |  |  | 10/26/2025 03:41:53 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000009 | PCM-20251026-00000014 | TT-20251026-00013 | EM | Region_5 | MKYL1M7910 | MKYL0910 | Enviroment | Air Condition | Change Fan | Muhammad Wahab Tahir Muhammad Afzal | 10/26/2025 00:14:52 | 10/26/2025 02:47:39 | 10/26/2025 06:14:52 | High TEAMPRATURE at MKYL1M7910-G9-L8-L18-L21-SBTS-P1-HUB-USF @ Generator_DG | 10/26/2025 00:06:50 | Major | 7103 | High TEAMPRATURE | 10/26/2025 00:06:41 | P1 | 4G | makkah | Generator_DG | LTE NSA | MKYL1M7910 | FLM_EM | [5 empty] | High TEAMPRATURE |  |  | API | 10/26/2025 00:14:52 | 10/26/2025 01:10:30 | 10/26/2025 01:11:50 | 10/26/2025 01:11:52 | 10/26/2025 01:30:31 | 10/26/2025 02:47:39 |  | Muhammad Wahab Tahir Muhammad Afzal |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000010 | PCM-20251026-00000017 | TT-20251026-00016 | EM | Region_4 | HLA1M8439 | HLA2439 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/26/2025 00:16:55 | 10/26/2025 00:16:55 | 10/26/2025 12:16:55 | LOW FUEL at HLA1M8439-G9-L8-L18-L21-SBTS @ Sceco | 10/26/2025 00:08:50 | Minor | 7103 | LOW FUEL | 10/26/2025 00:08:40 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8439 | FLM_EM | [5 empty] | LOW FUEL |  |  | API | 10/26/2025 00:16:55 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000013 | PCM-20251026-00000023 | TT-20251025-00691 | Reference_telecom | Region_4 | JED1U6720 | JED6020 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 00:19:16 | 10/26/2025 00:19:16 | 10/26/2025 06:19:16 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/25/2025 10:03:17 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/25/2025 10:03:05 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251025-00000600 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/26/2025 00:19:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000015 | PCM-20251026-00000025 | TT-20251026-00023 | Telecom | Region_3 | TBK0232 | TBK0232 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Tahir Abbas Fateh Khan | 10/26/2025 00:20:02 | 10/26/2025 01:21:25 | 10/26/2025 12:20:02 | RF Unit Maintenance Link Failure at TBK0232-P2_SRAN @ Sceco | 10/26/2025 00:15:43 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 00:14:58 | P2 | SRAN | tabouk | Sceco | 2G NSA | TBK0232 | FLM_TE | [8 empty] | API | 10/26/2025 00:20:02 | 10/26/2025 00:22:41 | 10/26/2025 00:42:37 | 10/26/2025 00:42:40 | 10/26/2025 01:04:21 | 10/26/2025 01:21:25 |  | Tahir Abbas Fateh Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000016 | PCM-20251026-00000026 | TT-20251025-01887 | Reference_telecom | Region_4 | JED2040 | JED2040 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 00:20:12 | 10/26/2025 00:20:12 | 10/26/2025 12:20:12 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED2040-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 22:59:09 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:59:02 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2040 | FLM_TE |  |  | PCM-20251025-00001832 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 00:20:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000017 | PCM-20251026-00000028 | TT-20251026-00005 | Reference_telecom | Region_2 | RIY2M8123 | RIY2123 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 00:21:21 | 10/26/2025 09:10:46 | 10/26/2025 12:21:21 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8123-P3-L800 @ Sceco | 10/25/2025 21:07:25 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 21:07:21 | P3 | 4G | riyadh | Sceco | 2G NSA | RIY2M8123 | FLM_TE |  |  | PCM-20251026-00000007 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/26/2025 00:21:21 | 10/26/2025 09:10:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000020 | PCM-20251026-00000043 | TT-20251026-00026 | EM | Region_6 | SDA0322 | SDA0322 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/26/2025 00:27:29 | 10/26/2025 09:37:17 | 10/26/2025 06:27:29 | 1(2G/LTE) sites down under SDA0322-P3/SDA0322-P3 @ Sceco | 10/26/2025 00:19:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 00:19:08 | P3 | 2G | abha | Sceco | 2G_LTE SA | SDA0322-P3 | FLM_EM | SDA0322 | Results: DOWN SITE HUB SDA0322-P3 SDA0322 Summary: Hub: SDA0322, Down Count: 1, Down Sites: SDA0322-P3 Alarm Summary: SDA0322 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 00:27:29 | 10/26/2025 09:37:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000021 | PCM-20251026-00000052 | TT-20251026-00039 | Telecom | Region_2 | RIY0716 | RIY0716 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | DILSHAD ALI ABDUL HAMEED | 10/26/2025 00:32:25 | 10/26/2025 07:06:26 | 10/26/2025 12:32:25 | BBU DC Output Out of Range at RIY0716-P2_SRAN @ Sceco | 10/26/2025 00:29:03 | Minor | 26112 | BBU DC Output Out of Range | 10/26/2025 00:27:55 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0716 | FLM_TE | [8 empty] | API | 10/26/2025 00:32:25 | 10/26/2025 07:05:18 | 10/26/2025 07:06:04 |  |  | 10/26/2025 07:06:26 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000024 | PCM-20251026-00000061 | TT-20251026-00045 | Telecom | Region_3 | RSP0001-MDC-NE8K-M14-02 | RSP0001 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 00:36:03 | 10/26/2025 00:46:03 | 10/26/2025 12:36:03 | Bad Package Error Rising at RSP0001-MDC-NE8K-M14-02 @ Sceco | 10/26/2025 00:35:48 | Minor | 101-2501403 | Bad Package Error Rising | 10/26/2025 00:35:40 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | RSP0001-MDC-NE8K-M14-02 | FLM_TE | [8 empty] | API | 10/26/2025 00:36:03 | 10/26/2025 00:46:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000026 | PCM-20251026-00000066 | TT-20251026-00044 | Telecom | Region_5 | MDQ0354 | MDQ0354 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/26/2025 00:43:10 | 10/26/2025 00:43:10 | 10/26/2025 06:43:10 | 2(5G) sites down under MDQ2344-GSM-UMTS-P2-USF,MDQ0354-GSM-UMTS-P2-USF @ Generator_SG | 10/26/2025 00:32:05 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 00:32:03 | P2 | 2G | makkah | Generator_SG | 5G SA | MDQ0354-GSM-UMTS-P2-USF 5G,MDQ2344-GSM-UMTS-P2-USF 5G | FLM_TE |  | Results: DOWN SITE HUB MDQ0354-GSM-UMTS-P2-USF Need to check MDQ2344-GSM-UMTS-P2-USF Need to check Summary: Alarm Summary: HUB site not found | PCM-20251026-00000063 | MDQ0354 | MDQ0354 |  | sites down |  | API | 10/26/2025 00:43:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000027 | PCM-20251026-00000068 | TT-20251026-00047 | EM | Region_4 | JED0316 | JED0316 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 00:43:29 | 10/26/2025 10:36:44 | 10/26/2025 06:43:29 | 1(2G/LTE/5G) sites down under JED0316-P2/JED0316-P2 @ Sceco | 10/26/2025 00:35:26 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 00:35:18 | P2 | 2G | jeddah | Sceco | 2G SA | JED0316-P2 | FLM_TE | JED0316 | Results: DOWN SITE HUB JED0316-P2 JED0316 Summary: Hub: JED0316, Down Count: 1, Down Sites: JED0316-P2 Alarm Summary: JED0316 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 00:43:29 | 10/26/2025 10:36:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000030 | PCM-20251026-00000074 | TT-20251025-00297 | Reference_telecom | Region_4 | NSH1M7165 | NSH0165 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 00:51:00 | 10/26/2025 09:54:22 | 10/26/2025 12:51:00 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NSH1M7165-G9-L9-L18-SBTS-P3 @ Generator_SG | 10/25/2025 03:09:05 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 03:07:29 | P3 | 4G | adam | Generator_SG | LTE NSA | NSH1M7165 | FLM_TE |  |  | PCM-20251025-00000263 | Please close site is clear | Please close site is clear |  |  |  | API | 10/26/2025 00:51:00 | 10/26/2025 09:54:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000033 | PCM-20251026-00000078 | TT-20251025-01824 | Reference_telecom | Region_6 | KHS1M7565 | KHS0565 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 00:55:20 | 10/26/2025 03:55:04 | 10/26/2025 06:55:20 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHS1M7565-P2-USF-L900 @ Sceco | 10/25/2025 21:17:03 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 19:51:59 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7565 | FLM_TE |  |  | PCM-20251025-00001761 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:55:20 | 10/26/2025 01:43:42 | 10/26/2025 02:48:56 |  |  | 10/26/2025 03:55:04 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000034 | PCM-20251026-00000079 | TT-20251025-01821 | Reference_telecom | Region_6 | KHS1M7657 | KHS0657 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 00:55:58 | 10/26/2025 03:54:53 | 10/26/2025 06:55:58 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHS1M7657-P3-L900 @ Generator_SG | 10/25/2025 21:17:14 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 19:46:49 | P3 | 4G | turaib | Generator_SG | LTE NSA | KHS1M7657 | FLM_TE |  |  | PCM-20251025-00001752 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:55:58 | 10/26/2025 01:43:43 | 10/26/2025 02:49:00 |  |  | 10/26/2025 03:54:53 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000035 | PCM-20251026-00000080 | TT-20251025-01823 | Reference_telecom | Region_6 | KHS1M7992 | KHS0992 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 00:56:15 | 10/26/2025 03:54:40 | 10/26/2025 06:56:15 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHS1M7992-P2-USF-L900 @ Sceco | 10/25/2025 21:21:18 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 19:51:25 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7992 | FLM_TE |  |  | PCM-20251025-00001760 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:15 | 10/26/2025 01:43:43 | 10/26/2025 02:49:05 |  |  | 10/26/2025 03:54:40 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000036 | PCM-20251026-00000081 | TT-20251025-01123 | Reference_telecom | Region_6 | NJR0020 | NJR0020 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/26/2025 00:56:26 | 10/26/2025 02:21:19 | 10/26/2025 12:56:26 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0020-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/25/2025 11:48:15 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 11:46:37 | P2 | 2G | najran | Sceco | 2G NSA | NJR0020 | FLM_TE |  |  | PCM-20251025-00001038 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:26 | 10/26/2025 01:33:53 | 10/26/2025 02:20:38 |  |  | 10/26/2025 02:21:19 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000037 | PCM-20251026-00000082 | TT-20251025-01431 | Reference_telecom | Region_6 | NJR1M7042 | NJR0042 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/26/2025 00:56:34 | 10/26/2025 02:22:06 | 10/26/2025 12:56:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7042-P2-NCA-L800-SBTS @ Sceco | 10/25/2025 14:59:40 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 14:23:38 | P2 | 4G | najran | Sceco | LTE NSA | NJR1M7042 | FLM_TE |  |  | PCM-20251025-00001370 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:34 | 10/26/2025 01:33:54 | 10/26/2025 02:21:25 |  |  | 10/26/2025 02:22:06 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000038 | PCM-20251026-00000083 | TT-20251026-00063 | Telecom | Region_4 | JED0151 | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 00:56:41 | 10/26/2025 00:56:41 | 10/26/2025 06:56:41 | LOCAL_FAULT at JED0151 (JD1)_ELC @ Sceco_STB | 10/26/2025 00:53:11 | Major | 1-12545 | LOCAL_FAULT | 10/26/2025 00:52:58 | VIP | 2G | jeddah | Sceco_STB | DWDM NSA | JED0151 | FLM_TE | [5 empty] | 5-ELC(3-E)-13-G1M520S-4(RX2/TX2(ISP_PCLS0001JD1-100GE-03))-CLIENT:1 |  |  | API | 10/26/2025 00:56:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000039 | PCM-20251026-00000084 | TT-20251025-00917 | Reference_telecom | Region_6 | TLM1M8248 | TLM2248 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/26/2025 00:56:51 | 10/26/2025 08:39:30 | 10/26/2025 12:56:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TLM1M8248-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/25/2025 10:38:59 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 10:13:55 | P3 | 4G | mohail | Sceco | LTE NSA | TLM1M8248 | FLM_TE |  |  | PCM-20251025-00000841 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:51 | 10/26/2025 08:33:21 | 10/26/2025 08:39:17 |  |  | 10/26/2025 08:39:30 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000040 | PCM-20251026-00000085 | TT-20251025-00490 | Reference_telecom | Region_6 | MKW2344 | MKW2344 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/26/2025 00:57:02 | 10/26/2025 10:21:19 | 10/26/2025 12:57:02 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at MKW2344-G9-L8-L18-NR2.6-SBTS-P3 @ Generator_SG | 10/25/2025 07:52:19 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 09:11:31 | P3 | 2G | Baha | Generator_SG | 2G NSA | MKW2344 | FLM_TE |  |  | PCM-20251025-00000426 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:57:02 | 10/26/2025 10:20:12 | 10/26/2025 10:20:57 |  |  | 10/26/2025 10:21:19 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000041 | PCM-20251026-00000087 | TT-20251026-00065 | Telecom | Region_2 | RIYB6029-CSG-01 | RIYB6029 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/26/2025 00:58:15 | 10/26/2025 00:58:15 | 10/26/2025 12:58:15 | Crc error alarm notification at RIYB6029-CSG-01 @ Sceco | 10/26/2025 00:57:39 | Minor | 101-1103100 | Crc error alarm notification | 10/26/2025 00:57:20 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6029-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 00:58:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000042 | PCM-20251026-00000088 | TT-20251025-01311 | Reference_telecom | Region_6 | QFL1M7033 | QFL0033 | Equipment | BSS_HW_Stuck | Reset Air Scale | Mohammed Sideag Mohammed Ali | 10/26/2025 00:58:16 | 10/26/2025 01:06:31 | 10/26/2025 12:58:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at QFL1M7033-P2-CA-L800-SBTS @ Sceco | 10/25/2025 15:19:19 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 06:42:05 | P2 | 4G | jizan | Sceco | LTE NSA | QFL1M7033 | FLM_TE |  |  | PCM-20251025-00001262 | Please close the site is clear | Please close the site is clear |  |  |  | API | 10/26/2025 00:58:16 | 10/26/2025 01:05:53 | 10/26/2025 01:06:15 |  |  | 10/26/2025 01:06:31 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000043 | PCM-20251026-00000089 | TT-20251026-00066 | EM | Region_5 | MAK6028 | MAK6028 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 00:58:45 | 10/26/2025 00:58:45 | 10/26/2025 12:58:45 | AIRCON 2 FAILURE at MAK6028-GSM-P3 @ Sceco | 10/26/2025 00:50:31 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 00:50:25 | P3 | 2G | makkah | Sceco | 2G NSA | MAK6028 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 00:58:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000044 | PCM-20251026-00000090 | TT-20251026-00048 | Telecom | Region_3 | WFR2279 | WFR2279 |  |  |  | Walid Mohamad Fazil | 10/26/2025 00:58:45 | 10/26/2025 01:33:14 | 10/26/2025 06:58:45 | 4(2G) 4(LTE) sites down under R3_MD_HWBSC01 @ Sceco | 10/26/2025 00:36:19 | Major | 21825 | CSL Fault | 10/26/2025 00:36:13 | P3 | SRAN | madinah | Generator_SG | 2G_LTE SA | WFR2321-P3 2G_LTE,WFR2280-P3 2G_LTE | FLM_EM | WFR2279 | Dear Team, Hub:- WFR2279 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251026-00000069 | Dear Team, Hub:- WFR2279 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- WFR2279 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/26/2025 00:58:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000045 | PCM-20251026-00000093 | TT-20251025-00100 | Reference_telecom | Region_4 | NSH1M7128 | NSH0128 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 00:59:46 | 10/26/2025 00:59:46 | 10/26/2025 12:59:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NSH1M7128-G9-NL8-L18-SBTS-P2-USF @ Generator_DG | 10/24/2025 23:49:35 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 23:49:25 | P2 | 4G | adam | Generator_DG | LTE NSA | NSH1M7128 | FLM_TE |  |  | PCM-20251025-00000097 | Please close the site is clear | Please close the site is clear |  |  |  | API | 10/26/2025 00:59:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000046 | PCM-20251026-00000095 | TT-20251026-00068 | Reference_telecom | Region_5 | MAK0628 | MAK0628 | Equipment | SFP_BTS | Replace SFP | Inam ullah | 10/26/2025 01:01:59 | 10/26/2025 10:54:01 | 10/26/2025 13:01:59 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at MAK0628-G9-NL8-NL18-L21-NR2.6-SBTS-P3-NEW @ Sceco | 10/26/2025 00:55:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 00:55:36 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK0628 | FLM_TE |  |  | PCM-20251026-00000094 | kindly support to perform HC,check sfp cable connector connected RMOD | kindly support to perform HC,check sfp cable connector connected RMOD |  |  |  | API | 10/26/2025 01:01:59 | 10/26/2025 09:57:41 | 10/26/2025 09:58:07 | 10/26/2025 09:58:12 | 10/26/2025 10:20:43 | 10/26/2025 10:54:01 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000047 | PCM-20251026-00000097 | TT-20251026-00070 | EM | Region_6 | BSA1M8308 | BSA2308 |  |  |  | Asad Saddiq | 10/26/2025 01:02:22 | 10/26/2025 07:20:14 | 10/26/2025 13:02:22 | RECTIFIER MODULE FAILURE at BSA1M8308-G9-L800-L1800-L2100-SBTS-P3 @ Generator_SG | 10/26/2025 00:53:59 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 00:53:51 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8308 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 01:02:22 | 10/26/2025 07:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000052 | PCM-20251026-00000105 | TT-20251026-00073 | Reference_EM | Region_1 | SKJF0199 | SKJF0199 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Bashir Sahib Rahman | 10/26/2025 01:07:02 | 10/26/2025 01:51:57 | 10/26/2025 07:07:02 | Door opening alarm at SKJF0199-P1-HUB_SRAN @ Sceco | 10/26/2025 01:06:47 | Major | 65101 | Door opening alarm | 10/26/2025 01:06:43 | P1 | SRAN | quriyat | Sceco | 2G NSA | SKJF0199 | FLM_EM | [8 empty] | API | 10/26/2025 01:07:02 | 10/26/2025 01:51:23 | 10/26/2025 01:51:36 |  |  | 10/26/2025 01:51:57 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000053 | PCM-20251026-00000109 | TT-20251026-00074 | Reference_EM | Region_1 | DMJR0132 | DMJR0132 |  |  |  | Elsaid Adel Mohamed Abouhegara | 10/26/2025 01:10:07 | 10/26/2025 01:10:07 | 10/26/2025 13:10:07 | Mains Failure at DMJR0132-P3_SRAN @ Generator_SG | 10/26/2025 01:00:13 | Minor | 65109 | Mains Failure | 10/26/2025 01:00:08 | P3 | SRAN | quriyat | Generator_SG | 2G NSA | DMJR0132 | FLM_EM | [8 empty] | API | 10/26/2025 01:10:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000056 | PCM-20251026-00000120 | TT-20251026-00088 | Reference_telecom | Region_4 | JED0207 | JED0207 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 01:20:59 | 10/26/2025 10:36:44 | 10/26/2025 13:20:59 | LossOfSignal observed in JED0207 towards 10.3.227.85 @ Sceco | 10/25/2025 13:22:03 | Minor |  | LossOfSignal | 10/25/2025 13:20:50 | P2 | 2G | jeddah | Sceco | TX NSA | JED0207 | FLM_TE | [8 empty] | API | 10/26/2025 01:20:59 | 10/26/2025 10:36:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000057 | PCM-20251026-00000125 | TT-20251026-00037 | Reference_telecom | Region_5 | MAK1M8091 | MAK2091 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 01:22:41 | 10/26/2025 01:22:41 | 10/26/2025 07:22:41 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at MAK1M8091-CA-L800-P3 @ Sceco | 10/26/2025 00:22:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 00:21:30 | P3 | 4G | makkah | Sceco | LTE NSA | MAK1M8091 | FLM_TE |  |  | PCM-20251026-00000045 | Please check the HW issue | Please check the HW issue |  |  |  | API | 10/26/2025 01:22:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20251026000058 | PCM-20251026-00000127 | TT-20251025-01256 | Telecom | Region_1 | DJL0553-LH | DJL0553 |  |  |  | Syed Fawad Ali | 10/26/2025 01:25:32 | 10/26/2025 05:24:12 | 10/26/2025 07:25:32 | IN_PWR_HIGH ALARM AT DJL0553-LH | 10/25/2025 14:49:09 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/25/2025 14:49:09 | P1 | DWDM | sakaka | Sceco_STB_Rental | DWDM NSA | DJL0553-LH | FLM_TE |  |  | PCM-20251025-00001393 | we observing high power from IP side , so we will check if can we add atteunatour in MW or need SA RFC | we observing high power from IP side , so we will check if can we add atteunatour in MW or need SA RFC |  |  |  | API | 10/26/2025 01:25:32 | 10/26/2025 04:57:49 | 10/26/2025 04:58:00 | 10/26/2025 04:58:03 | 10/26/2025 04:58:07 | 10/26/2025 05:24:12 |  | Syed Fawad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000059 | PCM-20251026-00000129 | TT-20251023-01756 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 01:29:09 | 10/26/2025 01:29:09 | 10/26/2025 07:29:09 | LOCAL_FAULT at YBDB2655_ELC @ Sceco_STB | 10/23/2025 17:44:42 | Major | 1-12545 | LOCAL_FAULT | 10/23/2025 17:44:30 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE |  |  | PCM-20251023-00001807 | you can ignore for now as ports still no in use and still not migrated | you can ignore for now as ports still no in use and still not migrated |  |  |  | API | 10/26/2025 01:29:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000060 | PCM-20251026-00000130 | TT-20251025-01308 | Telecom | Region_4 | JD2 | JD2 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/26/2025 01:30:33 | 10/26/2025 01:30:33 | 10/26/2025 05:30:33 | SCECO :: LINK DOWN B/W HHR1-SEC0039-JD2_LH | 10/25/2025 15:19:35 | Critical | 1-12843 | OSC_LOS | 10/25/2025 15:19:23 | P1 | DWDM | jeddah | Sceco_STB | DWDM NSA | JD2 | FLM_TE |  |  | PCM-20251025-00001477 | will check after SEC team restore link between HHR1-SEC0039-JD2 | will check after SEC team restore link between HHR1-SEC0039-JD2 |  |  |  | API | 10/26/2025 01:30:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000061 | PCM-20251026-00000131 | TT-20251026-00093 | Reference_telecom | Region_6 | TNM0727 | TNM0727 |  |  |  | Fawad Khan | 10/26/2025 01:30:47 | 10/26/2025 08:41:48 | 10/26/2025 13:30:47 | ReplaceableUnitMissing observed in TNM0727_01 towards 10.221.247.84 @ Sceco | 10/25/2025 13:32:00 | Minor |  | ReplaceableUnitMissing | 10/25/2025 13:30:36 | P2 | 2G | mohail | Sceco | TX NSA | TNM0727 | FLM_TE | [8 empty] | API | 10/26/2025 01:30:47 | 10/26/2025 08:41:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000062 | PCM-20251026-00000132 | TT-20251025-01236 | Telecom | Region_2 | RIY2474 | RIY2474 | AutoRecovery | Clear_Before_Investigation | Auto Clear | DILSHAD ALI ABDUL HAMEED | 10/26/2025 01:32:06 | 10/26/2025 02:06:04 | 10/26/2025 07:32:06 | IN_PWR_HIGH ALARM AT RIY2474 | 10/25/2025 14:36:38 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/25/2025 14:36:38 | P2 | SRAN | riyadh | Sceco | DWDM NSA | RIY2474 | FLM_TE |  |  | PCM-20251025-00001506 | alarm stable cleared from long time , no need actions . | alarm stable cleared from long time , no need actions . |  |  |  | API | 10/26/2025 01:32:06 | 10/26/2025 01:49:39 | 10/26/2025 02:05:40 |  |  | 10/26/2025 02:06:04 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000064 | PCM-20251026-00000138 | TT-20251024-00648 | Telecom | Region_4 | JED0151(JD1) | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 01:37:29 | 10/26/2025 01:37:29 | 10/26/2025 07:37:29 | IN_PWR_LOW ALARM AT JED0151(JD1) | 10/24/2025 10:30:43 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/24/2025 10:30:43 | P1 | DWDM | jeddah | Sceco_STB_Rental | DWDM NSA | JED0151 | FLM_TE |  |  | PCM-20251024-00000592 | site now clear , no need actions from FLM side . | site now clear , no need actions from FLM side . |  |  |  | API | 10/26/2025 01:37:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000065 | PCM-20251026-00000148 | TT-20251026-00101 | EM | Region_4 | DGB2169 | DGB2169 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 01:43:58 | 10/26/2025 03:34:31 | 10/26/2025 07:43:58 | 1(2G/5G) sites down under DGB2169-P3/DGB2169-P3 @ Sceco | 10/26/2025 01:35:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 01:35:43 | P3 | 2G | alaith | Sceco | 2G SA | DGB2169-P3 | FLM_TE | DGB2169 | Results: DOWN SITE HUB DGB2169-P3 DGB2169 Summary: Hub: DGB2169, Down Count: 1, Down Sites: DGB2169-P3 Alarm Summary: DGB2169 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 01:43:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251026000066 | PCM-20251026-00000150 | TT-20251026-00080 | EM | Region_3 | HAL0045 | HAL0045 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 01:46:13 | 10/26/2025 09:41:04 | 10/26/2025 07:46:13 | 1(2G/3G) sites down under HAL0045-P3/R3_HL_HWBSC01 @ Generator_SG | 10/26/2025 01:09:32 | Major | 21825 | CSL Fault | 10/26/2025 01:09:28 | P3 | SRAN | hail | Generator_SG | 2G_3G SA | HAL0045-P3 | FLM_TE | HAL0045 | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20251026-00000141 | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally |  | sites down |  | API | 10/26/2025 01:46:13 | 10/26/2025 09:34:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000067 | PCM-20251026-00000151 | TT-20251026-00111 | Reference_telecom | Region_6 | KMS0473 | KMS0473 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 01:49:54 | 10/26/2025 03:55:18 | 10/26/2025 13:49:54 | Degrade observed in KMS0473 towards 10.10.159.35 @ Sceco | 10/25/2025 13:51:33 | Minor |  | Degrade | 10/25/2025 13:49:27 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0473 | FLM_TE | [8 empty] | API | 10/26/2025 01:49:54 | 10/26/2025 03:55:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000068 | PCM-20251026-00000153 | TT-20251026-00112 | Reference_telecom | Region_6 | KMS0064 | KMS0064 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 01:49:54 | 10/26/2025 10:36:06 | 10/26/2025 13:49:54 | ReplaceableUnitMissing observed in KMS0064 towards 10.10.159.34 @ Sceco | 10/25/2025 13:51:34 | Minor |  | ReplaceableUnitMissing | 10/25/2025 13:49:27 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KMS0064 | FLM_TE | [8 empty] | API | 10/26/2025 01:49:54 | 10/26/2025 10:36:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000070 | PCM-20251026-00000160 | TT-20251026-00121 | Reference_telecom | Region_2 | RIY2M7399 | RIY0399 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 01:55:29 | 10/26/2025 09:03:24 | 10/26/2025 07:55:29 | RFC Violation of Exceeding down time ¦¦ Cell Unavailable at RIY2M7399-P2-L900-L800 @ Sceco ¦¦ Refrance : CRQ000000539455 | 10/26/2025 01:54:01 | Major | 29240 | Cell Unavailable | 10/26/2025 01:51:46 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7399 | FLM_TE | [8 empty] | API | 10/26/2025 01:55:29 | 10/26/2025 09:03:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000071 | PCM-20251026-00000161 | TT-20251026-00122 | EM | Region_2 | RIY0298 | RIY0298 |  |  |  | Farhat Saeed Pirzada | 10/26/2025 01:56:05 | 10/26/2025 01:56:05 | 10/26/2025 05:56:05 | Door opening alarm at RIY0298-P1-Core-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 01:55:55 | Critical | 65101 | Door opening alarm | 10/26/2025 01:55:52 | P1 | SRAN | riyadh | Sceco_STB | 2G NSA | RIY0298 | FLM_EM | [8 empty] | API | 10/26/2025 01:56:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000072 | PCM-20251026-00000162 | TT-20251026-00123 | Telecom | Region_2 | RIY0399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Asad Ali Nadiq Khan | 10/26/2025 01:56:36 | 10/26/2025 10:54:28 | 10/26/2025 13:56:36 | RF Unit Maintenance Link Failure at RIY0399-P2_SRAN @ Sceco | 10/26/2025 01:54:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 01:51:19 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0399 | FLM_TE | [8 empty] | API | 10/26/2025 01:56:36 | 10/26/2025 08:12:29 | 10/26/2025 10:06:44 | 10/26/2025 10:07:03 | 10/26/2025 10:07:23 | 10/26/2025 10:54:28 |  | Asad Ali Nadiq Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000074 | PCM-20251026-00000166 | TT-20251025-01389 | Reference_telecom | Region_6 | JIZ0007 | JIZ0007 |  |  |  | Osama Hadi | 10/26/2025 01:58:26 | 10/26/2025 03:25:21 | 10/26/2025 13:58:26 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0007-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 14:04:11 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 14:02:22 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0007 | FLM_TE |  |  | PCM-20251026-00000116 | Observed node rebooted @ the same time of alarm occurrence | Observed node rebooted @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 01:58:26 | 10/26/2025 03:25:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000075 | PCM-20251026-00000169 | TT-20251025-00002 | Reference_telecom | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 02:01:10 | 10/26/2025 10:36:45 | 10/26/2025 14:01:10 | BASE STATION CONNECTIVITY PROBLEM (NR GTP-U Path Failure) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/24/2025 23:53:40 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 23:53:30 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2259 | FLM_TE |  |  | PCM-20251026-00000110 | Observed related uplink was flapping & currently cleared | Observed related uplink was flapping & currently cleared |  |  |  | API | 10/26/2025 02:01:10 | 10/26/2025 10:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000076 | PCM-20251026-00000170 | TT-20251026-00131 | Reference_EM | Region_1 | KB2 | KB2 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/26/2025 02:01:46 | 10/26/2025 10:11:53 | 10/26/2025 08:01:46 | Door opening alarm at KB2-Main Shelter-Core-P1 @ Sceco_STB | 10/26/2025 02:01:35 | Major | 65101 | Door opening alarm | 10/26/2025 02:01:33 | P1 | DWDM | dammam | Sceco_STB | 2G NSA | KB2 | FLM_EM | [8 empty] | API | 10/26/2025 02:01:46 | 10/26/2025 10:11:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000077 | PCM-20251026-00000171 | TT-20251025-00340 | Reference_telecom | Region_4 | JED1M7783 | JED0783 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 02:01:46 | 10/26/2025 10:36:45 | 10/26/2025 08:01:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED1M7783-CA-L900-L800-SBTS @ Generator_SG | 10/25/2025 03:49:09 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 03:48:55 | P2 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7783 | FLM_TE |  |  | PCM-20251026-00000117 | Observed related uplink was flapping & currently cleared | Observed related uplink was flapping & currently cleared |  |  |  | API | 10/26/2025 02:01:46 | 10/26/2025 10:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000078 | PCM-20251026-00000172 | TT-20251026-00132 | EM | Region_4 | JZMA1M8202 | JZMA2202 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 02:02:51 | 10/26/2025 09:29:23 | 10/26/2025 14:02:51 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JZMA1M8202-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 01:54:34 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/26/2025 01:54:29 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8202 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/26/2025 02:02:51 | 10/26/2025 09:29:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000081 | PCM-20251026-00000175 | TT-20251025-01702 | Reference_telecom | Region_6 | JIZ1MT0168 | JIZ0168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/26/2025 02:04:19 | 10/26/2025 03:30:42 | 10/26/2025 08:04:19 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1MT0168-P3 @ Sceco | 10/25/2025 17:51:56 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 17:45:16 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1MT0168 | FLM_TE |  |  | PCM-20251026-00000122 | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 02:04:19 | 10/26/2025 03:29:29 | 10/26/2025 03:30:29 |  |  | 10/26/2025 03:30:42 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000082 | PCM-20251026-00000176 | TT-20251026-00136 | Telecom | Region_1 | HFF6028 | HFF6028 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 02:04:21 | 10/26/2025 09:34:41 | 10/26/2025 14:04:21 | RF Unit Maintenance Link Failure at HFF6028-DCU1 @ Sceco | 10/26/2025 01:51:10 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 01:59:00 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/26/2025 02:04:21 | 10/26/2025 09:34:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000083 | PCM-20251026-00000177 | TT-20251025-01703 | Reference_telecom | Region_6 | JIZ1MT0244 | JIZ0244 |  |  |  | Zeshan Ali Adnan | 10/26/2025 02:05:03 | 10/26/2025 02:05:03 | 10/26/2025 06:05:03 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1MT0244-P1 @ Sceco | 10/25/2025 17:52:22 | Critical | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 17:45:32 | P1 | 4G | jizan | Sceco | LTE NSA | JIZ1MT0244 | FLM_TE |  |  | PCM-20251026-00000123 | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 02:05:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000084 | PCM-20251026-00000178 | TT-20251026-00137 | Telecom | Region_2 | RIY0399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Asad Ali Nadiq Khan | 10/26/2025 02:05:54 | 10/26/2025 10:57:41 | 10/26/2025 08:05:54 | BBU CPRI Interface Error at RIY0399-P2_SRAN @ Sceco | 10/26/2025 02:01:27 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 01:58:53 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0399 | FLM_TE | [8 empty] | API | 10/26/2025 02:05:54 | 10/26/2025 08:12:29 | 10/26/2025 10:57:09 | 10/26/2025 10:57:12 | 10/26/2025 10:57:15 | 10/26/2025 10:57:41 |  | Asad Ali Nadiq Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000085 | PCM-20251026-00000179 | TT-20251025-00108 | Reference_telecom | Region_6 | JIZ0296 | JIZ0296 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/26/2025 02:06:31 | 10/26/2025 03:30:03 | 10/26/2025 14:06:31 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0296-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 01:08:24 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 00:03:17 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0296 | FLM_TE |  |  | PCM-20251026-00000121 | Observed node rebooted @ FE JIZ0100 @ the same time of alarm occurrence | Observed node rebooted @ FE JIZ0100 @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 02:06:31 | 10/26/2025 03:29:30 | 10/26/2025 03:29:51 |  |  | 10/26/2025 03:30:03 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000086 | PCM-20251026-00000180 | TT-20251026-00140 | Reference_EM | Region_3 | SML2332 | SML2332 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 02:07:59 | 10/26/2025 02:07:59 | 10/26/2025 14:07:59 | Mains Failure at SML2332-P3-USF_SRAN @ Generator_SG | 10/26/2025 01:58:17 | Minor | 65109 | Mains Failure | 10/26/2025 01:58:12 | P3 | SRAN | hail | Generator_SG | 2G NSA | SML2332 | FLM_EM | [8 empty] | API | 10/26/2025 02:07:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000089 | PCM-20251026-00000184 | TT-20251026-00144 | Telecom | [7 empty] | 10/26/2025 02:11:36 | 10/26/2025 02:11:36 | 10/26/2025 14:11:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2608-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Generator_SG | 10/26/2025 02:10:46 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 02:10:38 | P3 | 2G |  | Generator_SG | 5G_Cell SA | JED2608 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 02:11:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000090 | PCM-20251026-00000185 | TT-20251026-00138 | Telecom | Region_4 | HHR0874 | HHR0874 |  |  |  | Khizer Hayat | 10/26/2025 02:11:59 | 10/26/2025 08:36:48 | 10/26/2025 06:11:59 | 1(5G) sites down under HHR0874-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/26/2025 02:03:32 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 02:03:30 | VIP | 2G | jeddah | Generator_SG | 5G SA | HHR0874-GSM-UMTS-P1-VIP-HHR | FLM_TE | HHR0874 | Results: DOWN SITE HUB HHR0874-GSM-UMTS-P1-VIP-HHR HHR0874 Summary: Hub: HHR0874, Down Count: 1, Down Sites: HHR0874-GSM-UMTS-P1-VIP-HHR Alarm Summary: HHR0874 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5443531 [ACTIVE] [URL:http://10.96.146.244:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 02:11:59 | 10/26/2025 08:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000091 | PCM-20251026-00000186 | TT-20251025-00488 | Reference_telecom | Region_5 | JDMK1M8406 | JDMK2406 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/26/2025 02:12:17 | 10/26/2025 02:12:17 | 10/26/2025 08:12:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JDMK1M8406-CA-P3 @ Generator_SG | 10/25/2025 05:53:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 05:53:15 | P3 | 4G | makkah | Generator_SG | LTE NSA | JDMK1M8406 | FLM_TE |  |  | PCM-20251026-00000118 | Observed node rebooted @ JDMK2406 @ the sane time of alarm occurrence | Observed node rebooted @ JDMK2406 @ the sane time of alarm occurrence |  |  |  | API | 10/26/2025 02:12:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000093 | PCM-20251026-00000188 | TT-20251026-00147 | Telecom | Region_1 | JBL-3459-NE40E-X3-P&PE-01 | JBL0459 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 02:13:09 | 10/26/2025 02:28:03 | 10/26/2025 06:13:09 | The Device is offline at JBL-3459-NE40E-X3-P&PE-01 @ Generator_DG | 10/26/2025 02:12:57 | Critical | 101-7 | The Device is offline | 10/26/2025 02:12:54 | P1 | IPRAN | jubail | Generator_DG | IPRAN SA | JBL-3459-NE40E-X3-P&PE-01 | FLM_TE | [8 empty] | API | 10/26/2025 02:13:09 | 10/26/2025 02:28:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000094 | PCM-20251026-00000191 | TT-20251025-00487 | Reference_telecom | Region_5 | MKJD1M9565 | MKJD0565 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 02:14:35 | 10/26/2025 02:14:35 | 10/26/2025 14:14:35 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MKJD1M9565-G9-L8-L18-L21-SBTS-P2 @ Generator_SG | 10/25/2025 05:53:21 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 05:53:11 | P2 | 4G | makkah | Generator_SG | LTE NSA | MKJD1M9565 | FLM_TE |  |  | PCM-20251026-00000124 | Observed node rebooted @ MKJD0565 @ the sane time of alarm occurrence | Observed node rebooted @ MKJD0565 @ the sane time of alarm occurrence |  |  |  | API | 10/26/2025 02:14:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000096 | PCM-20251026-00000193 | TT-20251026-00142 | EM | Region_4 | JZMA2202 | JZMA2202 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 02:14:59 | 10/26/2025 09:29:24 | 10/26/2025 08:14:59 | 1(2G/LTE) sites down under JZMA2202-P3/JZMA2202-P3 @ Generator_SG | 10/26/2025 02:07:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:07:02 | P3 | 2G | jeddah | Generator_SG | 2G_LTE SA | JZMA2202-P3 | FLM_EM | JZMA2202 | Results: DOWN SITE HUB JZMA2202-P3 JZMA2202 Summary: Hub: JZMA2202, Down Count: 1, Down Sites: JZMA2202-P3 Alarm Summary: JZMA2202 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:14:59 | 10/26/2025 09:29:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000097 | PCM-20251026-00000194 | TT-20251025-01625 | Reference_telecom | Region_6 | BHMF1M7856 | BHMF0856 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/26/2025 02:16:41 | 10/26/2025 10:22:04 | 10/26/2025 14:16:41 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHMF1M7856-G9-L8-L18-SBTS-P3 @ Sceco | 10/25/2025 16:27:29 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 16:22:27 | P3 | 4G | makhwa | Sceco | LTE NSA | BHMF1M7856 | FLM_TE |  |  | PCM-20251026-00000114 | Thanks to rectify related link BHMF0856-BHMF0859 | Thanks to rectify related link BHMF0856-BHMF0859 |  |  |  | API | 10/26/2025 02:16:41 | 10/26/2025 10:20:13 | 10/26/2025 10:21:41 |  |  | 10/26/2025 10:22:04 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000098 | PCM-20251026-00000196 | TT-20251026-00157 | EM | Region_2 | R2_RY4_HWBSC01 | RY4 |  |  |  | Farhat Saeed Pirzada | 10/26/2025 02:18:20 | 10/26/2025 02:18:20 | 10/26/2025 06:18:20 | Intruder Alarm SH1 EQ R at R2_RY4_HWBSC01 @ Sceco_STB | 10/26/2025 02:17:53 | Critical | 65349 | Intruder Alarm SH1 EQ R | 10/26/2025 02:17:48 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY4_HWBSC01 | FLM_EM | [8 empty] | API | 10/26/2025 02:18:20 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000099 | PCM-20251026-00000197 | TT-20251026-00159 | EM | Region_3 | MDTB2547 | MDTB2547 |  |  |  | Mohammed Sadeq Nawaz | 10/26/2025 02:21:55 | 10/26/2025 02:21:55 | 10/26/2025 14:21:55 | NETECO: Communication Fail at MDTB2547 @ Generator_DG | 10/26/2025 02:15:47 | Minor | 20001 | Communication Fail | 10/26/2025 02:15:47 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDTB2547 | FLM_EM | [8 empty] | API | 10/26/2025 02:21:55 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000102 | PCM-20251026-00000204 | TT-20251026-00126 | Reference_telecom | Region_4 | JED1M8986 | JED2986 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 02:25:31 | 10/26/2025 10:36:45 | 10/26/2025 08:25:31 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at JED1M8986-CA-L800-P3 @ Generator_SG | 10/26/2025 01:56:29 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 03:04:31 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8986 | FLM_TE |  |  | PCM-20251026-00000165 | Please close the alarm during site down | Please close the alarm during site down |  |  |  | API | 10/26/2025 02:25:31 | 10/26/2025 10:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000103 | PCM-20251026-00000205 | TT-20251026-00114 | Reference_telecom | Region_4 | HAW0300 | HAW0300 |  |  |  | Rashid Shafique | 10/26/2025 02:26:25 | 10/26/2025 02:26:25 | 10/26/2025 14:26:25 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at HAW0300-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/26/2025 01:46:32 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 01:46:23 | P2 | 2G | taif | Generator_SG | 5G_Cell SA | HAW0300 | FLM_TE |  |  | PCM-20251026-00000155 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/26/2025 02:26:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000104 | PCM-20251026-00000208 | TT-20251026-00167 | Telecom | Region_4 | JED1M7312 | JED0312 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 02:28:19 | 10/26/2025 06:09:03 | 10/26/2025 08:28:19 | BASE STATION ANTENNA LINE PROBLEM at JED1M7312-CA-L900-L800-SBTS @ Sceco | 10/26/2025 02:19:48 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 02:19:44 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7312 | FLM_TE |  |  | PCM-20251026-00000207 | kindly support to perform HC,check sfp cable connector connected RMOD | kindly support to perform HC,check sfp cable connector connected RMOD |  |  |  | API | 10/26/2025 02:28:19 | 10/26/2025 06:09:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000105 | PCM-20251026-00000214 | TT-20251026-00181 | Reference_telecom | Region_4 | MKMD0563 | MKMD0563 |  |  |  | Khizer Hayat | 10/26/2025 02:36:23 | 10/26/2025 08:36:49 | 10/26/2025 14:36:23 | DemFail observed in MKMD0563_02 towards 10.3.235.3 @ Sceco_STB | 10/25/2025 14:38:12 | Minor |  | DemFail | 10/25/2025 14:36:05 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKMD0563 | FLM_TE | [8 empty] | API | 10/26/2025 02:36:23 | 10/26/2025 08:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000106 | PCM-20251026-00000215 | TT-20251026-00173 | EM | Region_4 | MKYL0913 | MKYL0913 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/26/2025 02:37:59 | 10/26/2025 02:40:01 | 10/26/2025 08:37:59 | 1(2G/3G/5G) sites down under MKYL0913-P2/MKYL0913-P2 @ Generator_SG | 10/26/2025 02:30:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:30:07 | P2 | 2G | alaith | Generator_SG | 2G_3G SA | MKYL0913-P2 | FLM_EM | MKYL0913 | Results: DOWN SITE HUB MKYL0913-P2 MKYL0913 Summary: Hub: MKYL0913, Down Count: 1, Down Sites: MKYL0913-P2 Alarm Summary: MKYL0913 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:37:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000107 | PCM-20251026-00000216 | TT-20251026-00174 | EM | Region_4 | MKYL0912 | MKYL0912 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/26/2025 02:38:01 | 10/26/2025 02:38:01 | 10/26/2025 08:38:01 | 1(2G/3G) sites down under MKYL0912-P2/MKYL0912-P2 @ Generator_SG | 10/26/2025 02:30:13 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:30:06 | P2 | 2G | makkah | Generator_SG | 2G_3G SA | MKYL0912-P2 | FLM_EM | MKYL0912 | Results: DOWN SITE HUB MKYL0912-P2 MKYL0912 Summary: Hub: MKYL0912, Down Count: 1, Down Sites: MKYL0912-P2 Alarm Summary: MKYL0912 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:38:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000108 | PCM-20251026-00000217 | TT-20251026-00116 | Reference_telecom | Region_4 | MLJI1M3205 | MLJI0205 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 02:38:15 | 10/26/2025 09:54:23 | 10/26/2025 08:38:15 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at MLJI1M3205-P2-USF @ Generator_SG | 10/26/2025 01:23:13 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 01:21:02 | P2 | 3G | alaith | Generator_SG | 3G SA | MLJI1M3205 | FLM_TE |  |  | PCM-20251026-00000154 | Please check the site is down | Please check the site is down |  |  |  | API | 10/26/2025 02:38:15 | 10/26/2025 09:54:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000109 | PCM-20251026-00000218 | TT-20251026-00182 | Telecom | Region_4 | JZMA2421 | JZMA2421 |  |  |  | Khizer Hayat | 10/26/2025 02:42:29 | 10/26/2025 08:36:49 | 10/26/2025 08:42:29 | 1(2G) sites down under JZMA2421-P3/JZMA2421-P3 @ Generator_SG | 10/26/2025 02:34:06 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:34:01 | P3 | 2G | jeddah | Generator_SG | 2G SA | JZMA2421-P3 | FLM_TE | JZMA2421 | Results: DOWN SITE HUB JZMA2421-P3 JZMA2421 Summary: Hub: JZMA2421, Down Count: 1, Down Sites: JZMA2421-P3 Alarm Summary: JZMA2421 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:42:29 | 10/26/2025 08:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000110 | PCM-20251026-00000220 | TT-20251026-00185 | Telecom | Region_5 | HAJ0011 | HAJ0011 |  |  |  | Muhammad Saleem Iqbal | 10/26/2025 02:44:08 | 10/26/2025 05:13:16 | 10/26/2025 14:44:08 | RF Unit CPRI Interface Error at HAJ0011-P3_SRAN @ Sceco | 10/26/2025 02:38:46 | Minor | 26504 | RF Unit CPRI Interface Error | 10/26/2025 02:37:12 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ0011 | FLM_TE | [8 empty] | API | 10/26/2025 02:44:08 | 10/26/2025 05:13:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000112 | PCM-20251026-00000223 | TT-20251026-00189 | Reference_telecom | Region_4 | MKMD0557 | MKMD0557 |  |  |  | Khizer Hayat | 10/26/2025 02:49:18 | 10/26/2025 08:36:50 | 10/26/2025 14:49:18 | ReplaceableUnitProblem observed in MKMD0557 towards 10.3.235.4 @ Sceco_STB | 10/25/2025 14:49:37 | Minor |  | ReplaceableUnitProblem | 10/25/2025 14:49:11 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKMD0557 | FLM_TE | [8 empty] | API | 10/26/2025 02:49:18 | 10/26/2025 08:36:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000113 | PCM-20251026-00000225 | TT-20251026-00191 | Telecom | Region_6 | JIZ1M7092 | JIZ0092 | Equipment | BSS_HW_Stuck | Reset Air Scale | Osama Hadi | 10/26/2025 02:49:19 | 10/26/2025 05:12:05 | 10/26/2025 08:49:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ1M7092-G9-L8-L18-L21-SBTS-P1-HUB @ Sceco_STB | 10/26/2025 02:48:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 02:48:13 | P1 | 4G | jizan | Sceco_STB | 5G_Cell SA | JIZ1M7092 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 02:49:19 | 10/26/2025 03:25:22 | 10/26/2025 05:02:19 |  |  | 10/26/2025 05:12:05 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000116 | PCM-20251026-00000233 | TT-20251026-00201 | Telecom | Region_4 | JED2001 | JED2001 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 03:02:45 | 10/26/2025 03:02:45 | 10/26/2025 15:02:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2001-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/26/2025 03:02:08 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:01:58 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2001 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 03:02:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000118 | PCM-20251026-00000239 | TT-20251026-00204 | Telecom | Region_6 | BSA2308 | BSA2308 |  |  |  | Asad Saddiq | 10/26/2025 03:13:00 | 10/26/2025 07:20:14 | 10/26/2025 09:13:00 | 4(2G/LTE) sites down under BSA2308-P3,BSA2303-P3,BSA2305-P3,BSA2315-P3 @ Generator_SG | 10/26/2025 03:04:35 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:04:28 | P3 | 2G | bisha | Generator_SG | 2G_LTE SA | BSA2308-P3 | FLM_EM | BSA2308 | Results: DOWN SITE HUB BSA2308-P3 BSA2308 Summary: Hub: BSA2308, Down Count: 1, Down Sites: BSA2308-P3 Alarm Summary: BSA2308 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 03:13:00 | 10/26/2025 07:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000119 | PCM-20251026-00000241 | TT-20251026-00216 | Telecom | Region_4 | JED1-PE | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/26/2025 03:17:13 | 10/26/2025 03:17:13 | 10/26/2025 15:17:13 | Chassis Fail at JED1-PE @ Sceco_STB | 10/26/2025 03:16:37 | Minor | 101-2505202 | Chassis Fail | 10/26/2025 03:16:33 | P1 | IPBB | jeddah | Sceco_STB | IPRAN NSA | JED1-PE | FLM_TE | [8 empty] | API | 10/26/2025 03:17:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000120 | PCM-20251026-00000243 | TT-20251026-00220 | Telecom | Region_5 | MAK1M8523 | MAK2523 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 03:19:17 | 10/26/2025 03:19:17 | 10/26/2025 09:19:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M8523-CA-L800-P3 @ Sceco | 10/26/2025 03:18:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:18:10 | P3 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M8523 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 03:19:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000122 | PCM-20251026-00000245 | TT-20251026-00221 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace CB on Rectifier | DILSHAD ALI ABDUL HAMEED | 10/26/2025 03:20:50 | 10/26/2025 07:12:04 | 10/26/2025 15:20:50 | RF Unit Maintenance Link Failure at RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 03:17:00 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 03:15:17 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0964 | FLM_TE | [8 empty] | API | 10/26/2025 03:20:50 | 10/26/2025 07:08:06 | 10/26/2025 07:11:33 |  |  | 10/26/2025 07:12:04 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000123 | PCM-20251026-00000248 | TT-20251026-00226 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace CB on Rectifier | DILSHAD ALI ABDUL HAMEED | 10/26/2025 03:23:25 | 10/26/2025 07:12:37 | 10/26/2025 15:23:25 | NR DU Cell TRP Unavailable at RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 03:16:51 | Minor | 29870 | NR DU Cell TRP Unavailable | 10/26/2025 03:15:19 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0964 | FLM_TE | [8 empty] | API | 10/26/2025 03:23:25 | 10/26/2025 07:07:55 | 10/26/2025 07:12:10 |  |  | 10/26/2025 07:12:37 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000124 | PCM-20251026-00000249 | TT-20251026-00217 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace DCDU Fuse | DILSHAD ALI ABDUL HAMEED | 10/26/2025 03:23:29 | 10/26/2025 06:20:06 | 10/26/2025 07:23:29 | 1(5G) sites down under RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 03:16:51 | Critical | 29840 | gNodeB Out of Service | 10/26/2025 03:15:19 | VIP | SRAN | riyadh | Sceco | 5G SA | RIY0964-P1-PNU-VIP_SRAN | FLM_TE | RIY0964 | Results: DOWN SITE HUB RIY0964-P1-PNU-VIP_SRAN RIY0964 Summary: Hub: RIY0964, Down Count: 1, Down Sites: RIY0964-P1-PNU-VIP_SRAN Alarm Summary: RIY0964 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 03:23:29 | 10/26/2025 05:23:30 | 10/26/2025 05:30:45 | 10/26/2025 05:30:48 | 10/26/2025 06:00:20 | 10/26/2025 06:20:06 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000126 | PCM-20251026-00000255 | TT-20251026-00233 | EM | Region_3 | RUSF9013 | RUSF9013 |  |  |  | Yasser Mohamed Mohamed Yousef | 10/26/2025 03:25:58 | 10/26/2025 03:25:58 | 10/26/2025 07:25:58 | RELAY_ALARM_MAJOR at RUSF9013_NE_1 @ Generator_SG | 10/26/2025 03:24:14 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/26/2025 03:24:02 | P3 | Repeater | yanbu | Generator_SG | TX NSA | RUSF9013 | FLM_EM | [8 empty] | API | 10/26/2025 03:25:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000127 | PCM-20251026-00000256 | TT-20251026-00234 | Reference_telecom | Region_4 | JED1M7564 | JED0564 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 03:25:59 | 10/26/2025 03:25:59 | 10/26/2025 09:25:59 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7564-P1-VIP-CA-L900-L800-SBTS @ Generator_SG | 10/26/2025 03:21:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:21:07 | VIP | 4G | jeddah | Generator_SG | LTE_Cell SA | JED1M7564 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/26/2025 03:25:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000129 | PCM-20251026-00000260 | TT-20251026-00238 | Telecom | Region_2 | RIY0785 | RIY0785 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/26/2025 03:28:34 | 10/26/2025 06:22:55 | 10/26/2025 15:28:34 | RF Unit Maintenance Link Failure at RIY0785-P2_SRAN @ Sceco | 10/26/2025 03:23:41 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 03:23:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0785 | FLM_TE | [8 empty] | API | 10/26/2025 03:28:34 | 10/26/2025 06:22:17 | 10/26/2025 06:22:25 | 10/26/2025 06:22:27 | 10/26/2025 06:22:29 | 10/26/2025 06:22:55 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000130 | PCM-20251026-00000261 | TT-20251026-00239 | Telecom | Region_2 | RIY2M7785 | RIY0785 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/26/2025 03:28:46 | 10/26/2025 06:17:42 | 10/26/2025 09:28:46 | Cell Unavailable at RIY2M7785-P2-L800-L900 @ Sceco | 10/26/2025 03:26:07 | Major | 29240 | Cell Unavailable | 10/26/2025 03:25:41 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7785 | FLM_TE | [8 empty] | API | 10/26/2025 03:28:46 | 10/26/2025 05:24:28 | 10/26/2025 05:27:04 | 10/26/2025 05:50:40 | 10/26/2025 05:53:02 | 10/26/2025 06:17:42 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000131 | PCM-20251026-00000262 | TT-20251026-00194 | Reference_telecom | Region_4 | JED1M7572 | JED0572 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 03:29:12 | 10/26/2025 03:29:12 | 10/26/2025 15:29:12 | Fronthaul loop back connectivity check failure at JED1M7572-P1-DIA-CA-L900-L800-SBTS @ Sceco | 10/26/2025 02:24:06 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/26/2025 02:23:59 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7572 | FLM_TE |  |  | PCM-20251026-00000228 | kindly support to perform HC,check sfp cable connector connected RMOD | kindly support to perform HC,check sfp cable connector connected RMOD |  |  |  | API | 10/26/2025 03:29:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000132 | PCM-20251026-00000263 | TT-20251026-00232 | EM | Region_2 | RYQS2M2575 | RYQS2575 |  |  |  | Asim Mushtaq Mushtaq Ahmad | 10/26/2025 03:29:29 | 10/26/2025 03:29:29 | 10/26/2025 09:29:29 | 1(2G/3G/LTE) sites down under RYQS2575-P2/RY1BSCH02 @ Generator_SG | 10/26/2025 03:22:28 | Major | 21825 | CSL Fault | 10/26/2025 03:22:27 | P2 | 2G | rumah | Generator_SG | 2G_3G_LTE SA | RYQS2575-P2 | FLM_EM | RYQS2575 | Results: DOWN SITE HUB RYQS2575-P2 RYQS2575 Summary: Hub: RYQS2575, Down Count: 1, Down Sites: RYQS2575-P2 Alarm Summary: RYQS2575 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 03:29:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000133 | PCM-20251026-00000264 | TT-20251026-00186 | Reference_telecom | Region_6 | BCH0080 | BCH0080 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 03:30:44 | 10/26/2025 10:54:42 | 10/26/2025 15:30:44 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at BCH0080-G9-NL8-L9-NL18-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 02:41:10 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 02:41:01 | P3 | 2G | Albaha | Sceco | 5G_Cell SA | BCH0080 | FLM_TE |  |  | PCM-20251026-00000221 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 03:30:44 | 10/26/2025 10:52:38 | 10/26/2025 10:54:28 |  |  | 10/26/2025 10:54:42 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000134 | PCM-20251026-00000270 | TT-20251026-00249 | Reference_EM | Region_2 | RIY2977 | RIY2977 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 03:33:14 | 10/26/2025 09:36:34 | 10/26/2025 15:33:14 | Minor Rec alarm at RIY2977-P3_SRAN-PC @ Sceco | 10/26/2025 03:23:12 | Minor | 65108 | Minor Rec alarm | 10/26/2025 03:23:09 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2977 | FLM_EM | [8 empty] | API | 10/26/2025 03:33:14 | 10/26/2025 09:36:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000135 | PCM-20251026-00000271 | TT-20251026-00180 | Reference_telecom | Region_6 | WDS2498 | WDS2498 |  |  |  | Ahmed Mamdouh Helal Helal | 10/26/2025 03:33:31 | 10/26/2025 03:33:31 | 10/26/2025 15:33:31 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at WDS2498-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Generator_SG | 10/26/2025 02:05:49 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 02:05:42 | P3 | 2G | wadi dawasar | Generator_SG | 2G NSA | WDS2498 | FLM_TE |  |  | PCM-20251026-00000213 | HW alarm flapping at site,FLM need to restore | HW alarm flapping at site,FLM need to restore |  |  |  | API | 10/26/2025 03:33:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000136 | PCM-20251026-00000272 | TT-20251026-00253 | EM | Region_6 | HJR1M7027 | HJR0027 |  |  |  | Arif Ullah Shah | 10/26/2025 03:36:19 | 10/26/2025 03:49:05 | 10/26/2025 15:36:19 | AIRCON 2 FAILURE at HJR1M7027-P3-L800 @ Sceco | 10/26/2025 03:28:21 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 03:28:15 | P3 | 4G | makhwa | Sceco | LTE NSA | HJR1M7027 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 03:36:19 | 10/26/2025 03:49:05 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000137 | PCM-20251026-00000275 | TT-20251026-00254 | EM | Region_6 | UKHA1M8363 | UKHA2363 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 03:37:21 | 10/26/2025 06:55:22 | 10/26/2025 15:37:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at UKHA1M8363-G9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 03:28:59 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/26/2025 03:28:53 | P3 | 4G | Baha | Sceco | LTE NSA | UKHA1M8363 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/26/2025 03:37:21 | 10/26/2025 06:55:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000138 | PCM-20251026-00000276 | TT-20251026-00251 | Telecom | Region_4 | YLM1M7876 | YLM0876 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 03:39:29 | 10/26/2025 03:39:29 | 10/26/2025 07:39:29 | 1(LTE) sites down under YLM0876-L800-SBTS-P1 @ Generator_DG | 10/26/2025 03:31:27 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 03:31:24 | P1 | 4G | alaith | Generator_DG | LTE SA | YLM0876-L800-SBTS-P1 | FLM_TE |  | Results: DOWN SITE HUB YLM0876-L800-SBTS-P1 Need to check Summary: Alarm Summary: HUB site not found |  |  |  | Timeout connecting to [/10.88.39.44:8080] [URL:http://10.88.39.44:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 03:39:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000139 | PCM-20251026-00000278 | TT-20251026-00255 | Reference_EM | [7 empty] | 10/26/2025 03:40:26 | 10/26/2025 03:40:26 | 10/26/2025 15:40:26 | Mains Failure at RIYB6055-P3_SRAN @ Sceco | 10/26/2025 03:33:18 | Minor | 65109 | Mains Failure | 10/26/2025 03:30:35 | P3 | SRAN |  | Sceco | 2G NSA | RIYB6055 | FLM_EM | [8 empty] | API | 10/26/2025 03:40:26 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000141 | PCM-20251026-00000280 | TT-20251026-00245 | Telecom | Region_6 | SRA2359 | SRA2359 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 03:42:30 | 10/26/2025 09:44:44 | 10/26/2025 09:42:30 | 4(2G) 4(LTE) sites down under SRA2355-P3,MTB2377-P3,SRA2359-P3,QLW2372-P3/QLW2372-P3 @ Generator_SG | 10/26/2025 03:28:53 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:28:50 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2355-P3 2G_LTE,MTB2377-P3 2G_LTE,SRA2359-P3 2G_LTE,QLW2372-P3 2G_LTE | FLM_EM | SRA2359 | Results: DOWN SITE HUB SRA2355-P3 SRA2355 MTB2377-P3 MTB2377 SRA2359-P3 SRA2359 QLW2372-P3 QLW2372 Summary: Hub: SRA2355, Down Count: 1, Down Sites: SRA2355-P3 Hub: MTB2377, Down Count: 1, Down Sites: MTB2377-P3 Hub: SRA2359, Down Count: 1, Down Sites: SRA2359-P3 Hub: QLW2372, Down Count: 1, Down Sites: QLW2372-P3 Alarm Summary: SRA2355 No Active Alarm on HUB MTB2377 No Active Alarm on HUB SRA2359 Alarm Active on HUB QLW2372 Alarm Active on HUB | PCM-20251026-00000274 | SRA2359 | SRA2359 |  | sites down |  | API | 10/26/2025 03:42:30 | 10/26/2025 09:44:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000143 | PCM-20251026-00000284 | TT-20251025-01891 | Telecom | Region_1 | ARM2759 | ARM2759 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 03:45:10 | 10/26/2025 05:10:59 | 10/26/2025 07:45:10 | 1(LTE) sites down under ARM2759-P1_SRAN-PC @ Power Cube | 10/25/2025 23:07:25 | Critical | 301 | NE Is Disconnected | 10/25/2025 23:07:22 | P1 | SRAN | jubail | Power Cube | LTE SA | ARM2759-P1_SRAN-PC | FLM_TE | ARM2759 | Results: DOWN SITE HUB ARM2759-P1_SRAN-PC ARM2759 Summary: Hub: ARM2759, Down Count: 1, Down Sites: ARM2759-P1_SRAN-PC Alarm Summary: ARM2759 No Active Alarm on HUB | PCM-20251026-00000106 | Kindly need HC on link JBKH0095-ARM2759 as bad performance ,RSL degradation exist during this time | Kindly need HC on link JBKH0095-ARM2759 as bad performance ,RSL degradation exist during this time |  | sites down |  | API | 10/26/2025 03:45:10 | 10/26/2025 05:10:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000144 | PCM-20251026-00000285 | TT-20251026-00163 | Telecom | Region_6 | TNM0176 | TNM0176 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Fawad Khan | 10/26/2025 03:46:16 | 10/26/2025 08:54:37 | 10/26/2025 15:46:16 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at TNM0176-G9-L8-L18-NL21-NNR2.6-SBTS-P3 @ Sceco | 10/26/2025 02:19:06 | Minor | 7114 | CELL SERVICE PROBLEM | 10/26/2025 02:19:01 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNM0176 | FLM_TE |  |  | PCM-20251026-00000200 | Please perform the HC for Cell-B and C have sleeping cell issue | Please perform the HC for Cell-B and C have sleeping cell issue |  |  |  | API | 10/26/2025 03:46:16 | 10/26/2025 08:41:49 | 10/26/2025 08:53:57 |  |  | 10/26/2025 08:54:37 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000145 | PCM-20251026-00000287 | TT-20251026-00260 | EM | Region_3 | RUSF9012 | RUSF9012 |  |  |  | Muhammad Imran Muhammad Aslam | 10/26/2025 03:48:43 | 10/26/2025 03:48:43 | 10/26/2025 15:48:43 | NETECO: Communication Fail at RUSF9012 @ Generator_SG | 10/26/2025 03:42:19 | Minor | 20001 | Communication Fail | 10/26/2025 03:42:19 | P3 | Repeater | madinah | Generator_SG | 2G NSA | RUSF9012 | FLM_EM | [8 empty] | API | 10/26/2025 03:48:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000146 | PCM-20251026-00000290 | TT-20251026-00055 | Reference_telecom | Region_6 | KHNJ1M8241 | KHNJ2241 |  |  |  | Bilal Anwar Khurshid Anwar | 10/26/2025 03:53:59 | 10/26/2025 04:02:32 | 10/26/2025 15:53:59 | BASE STATION SERVICE PROBLEM (TX out of order) at KHNJ1M8241-CA-L800-P3-SBTS @ Sceco | 10/26/2025 00:45:18 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 00:45:08 | P3 | 4G | al harja | Sceco | LTE_Cell SA | KHNJ1M8241 | FLM_TE |  |  | PCM-20251026-00000269 | Please update once change the HW | Please update once change the HW |  |  |  | API | 10/26/2025 03:53:59 | 10/26/2025 04:02:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000147 | PCM-20251026-00000292 | TT-20251026-00261 | Telecom | Region_4 | SDY0763 | SDY0763 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 03:54:59 | 10/26/2025 03:54:59 | 10/26/2025 09:54:59 | 1(5G) sites down under SDY0763-GSM-UMTS-P3 @ Generator_DG | 10/26/2025 03:46:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 03:46:54 | P3 | 2G | alaith | Generator_DG | 5G SA | SDY0763-GSM-UMTS-P3 | FLM_TE | SDY0763 | Results: DOWN SITE HUB SDY0763-GSM-UMTS-P3 SDY0763 Summary: Hub: SDY0763, Down Count: 1, Down Sites: SDY0763-GSM-UMTS-P3 Alarm Summary: SDY0763 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.9.44:8080] [URL:http://10.88.9.44:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 03:54:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000148 | PCM-20251026-00000294 | TT-20251026-00218 | Telecom | Region_5 | MAK2706 | MAK2706 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/26/2025 03:56:31 | 10/26/2025 03:56:31 | 10/26/2025 09:56:31 | 1(2G) sites down under MAK2706-P3/MAK2706-P3 @ Generator_SG | 10/26/2025 03:15:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:15:40 | P3 | 2G | makkah | Generator_SG | 2G SA | MAK2706-P3 | FLM_TE | MAK2706 | Results: DOWN SITE HUB MAK2706-P3 MAK2706 Summary: Hub: MAK2706, Down Count: 1, Down Sites: MAK2706-P3 Alarm Summary: MAK2706 No Active Alarm on HUB | PCM-20251026-00000258 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 03:56:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000149 | PCM-20251026-00000295 | TT-20251026-00267 | EM | Region_3 | R3_MD_HWBSC02 | MD2 | Equipment | BSS_HW_Stuck | Reset Air Scale | Essam Aboulfadil | 10/26/2025 03:57:30 | 10/26/2025 04:48:27 | 10/26/2025 07:57:30 | Air-Condition #2 FA(SH2) at R3_MD_HWBSC02 @ Sceco_STB | 10/26/2025 03:57:16 | Critical | 65353 | Air-Condition #2 FA(SH2) | 10/26/2025 03:57:11 | P1 | BSC | madinah | Sceco_STB | 2G NSA | R3_MD_HWBSC02 | FLM_EM | [8 empty] | API | 10/26/2025 03:57:30 | 10/26/2025 04:14:41 | 10/26/2025 04:14:51 | 10/26/2025 04:14:54 | 10/26/2025 04:18:26 | 10/26/2025 04:48:27 |  | Essam Aboulfadil |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000151 | PCM-20251026-00000297 | TT-20251026-00193 | Reference_telecom | Region_4 | SDY1M3738 | SDY0738 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 03:59:09 | 10/26/2025 03:59:09 | 10/26/2025 09:59:09 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at SDY1M3738-P3 @ Sceco_STB | 10/26/2025 02:25:09 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 02:22:59 | P3 | 3G | alaith | Sceco_STB | 3G SA | SDY1M3738 | FLM_TE |  |  | PCM-20251026-00000226 | Please perform the multiple HW issue | Please perform the multiple HW issue |  |  |  | API | 10/26/2025 03:59:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000156 | PCM-20251026-00000314 | TT-20251026-00288 | Reference_EM | Region_3 | SML2332 | SML2332 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 04:22:47 | 10/26/2025 04:22:47 | 10/26/2025 16:22:47 | Door opening alarm at SML2332-P3-USF_SRAN @ Generator_SG | 10/26/2025 04:22:29 | Minor | 65101 | Door opening alarm | 10/26/2025 04:22:27 | P3 | SRAN | hail | Generator_SG | 2G NSA | SML2332 | FLM_EM | [8 empty] | API | 10/26/2025 04:22:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000157 | PCM-20251026-00000318 | TT-20251026-00258 | Telecom | Region_4 | KMMD0722 | KMMD0722 |  |  |  | Nazeer Mohammed | 10/26/2025 04:24:28 | 10/26/2025 04:24:28 | 10/26/2025 08:24:28 | 5(5G) sites down under KMMD0639-GSM-P2 @ Sceco | 10/26/2025 03:41:26 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 03:41:24 | P1 | 2G | jeddah | Sceco_STB | 5G SA | KMMD0639-GSM-P2 5G,KMMD0754-GSM-P3 5G,KMMD0726-GSM-P3 5G,KMMD0722-GSM-P1-HUB 5G,KMMD0637-GSM-P3 5G | FLM_TE | KMMD0722 | Results: DOWN SITE HUB KMMD0639-GSM-P2 KMMD0639 KMMD0754-GSM-P3 KMMD0754 KMMD0726-GSM-P3 Need to check KMMD0722-GSM-P1-HUB Need to check KMMD0637-GSM-P3 Need to check Summary: Hub: KMMD0639, Down Count: 1, Down Sites: KMMD0639-GSM-P2 Hub: KMMD0754, Down Count: 1, Down Sites: KMMD0754-GSM-P3 Alarm Summary: KMMD0639 No Active Alarm on HUB KMMD0754 No Active Alarm on HUB HUB site not found | PCM-20251026-00000307 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 04:24:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000158 | PCM-20251026-00000321 | TT-20251026-00296 | Reference_telecom | Region_4 | JED0056 | JED0056 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | 10/26/2025 16:25:22 | LossOfSignal observed in JED0056 towards 10.10.146.248 @ Sceco | 10/25/2025 16:26:25 | Minor |  | LossOfSignal | 10/25/2025 16:25:03 | P3 | 2G | jeddah | Sceco | TX NSA | JED0056 | FLM_TE | [8 empty] | API | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000159 | PCM-20251026-00000320 | TT-20251026-00295 | Reference_telecom | Region_4 | JED0899 | JED0899 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | 10/26/2025 16:25:22 | Degrade observed in JED0899_SH04 towards 10.10.146.247 @ Generator_SG | 10/25/2025 16:26:25 | Minor |  | Degrade | 10/25/2025 16:25:02 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0899 | FLM_TE | [8 empty] | API | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000160 | PCM-20251026-00000323 | TT-20251026-00299 | Reference_telecom | Region_3 | WFR2279 | WFR2279 |  |  |  | TAUSEEF ILYAS | 10/26/2025 04:27:27 | 10/26/2025 04:59:42 | 10/26/2025 16:27:27 | ETH_LOS at WFR2279_NE_1 @ Generator_SG | 10/26/2025 00:27:11 | Minor | 1-235 | ETH_LOS | 10/26/2025 00:27:01 | P3 | SRAN | madinah | Generator_SG | TX NSA | WFR2279 | FLM_TE | [8 empty] | API | 10/26/2025 04:27:27 | 10/26/2025 04:59:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000161 | PCM-20251026-00000324 | TT-20251026-00298 | Telecom | Region_6 | BSH1M7201 | BSH0201 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 04:31:29 | 10/26/2025 11:04:25 | 10/26/2025 10:31:29 | 1(LTE) sites down under BSH0201-P3-CA-L800 @ Sceco | 10/26/2025 04:23:28 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 04:23:25 | P3 | 4G | baish | Sceco | LTE SA | BSH0201-P3-CA-L800 | FLM_TE | BSH0201 | Results: DOWN SITE HUB BSH0201-P3-CA-L800 BSH0201 Summary: Hub: BSH0201, Down Count: 1, Down Sites: BSH0201-P3-CA-L800 Alarm Summary: BSH0201 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.103.47.228:8080] [URL:http://10.103.47.228:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 04:31:29 | 10/26/2025 11:04:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000162 | PCM-20251026-00000325 | TT-20251026-00278 | Reference_telecom | Region_4 | JED1U6771 | JED6071 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 04:31:57 | 10/26/2025 04:31:57 | 10/26/2025 10:31:57 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1U6771-G9-L18-SBTS-P1-SHOP @ Sceco | 10/26/2025 04:11:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 04:11:26 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1U6771 | FLM_TE |  |  | PCM-20251026-00000310 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/26/2025 04:31:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000163 | PCM-20251026-00000326 | TT-20251026-00305 | Telecom | Region_1 | JBL0468 | JBL0468 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 04:32:06 | 10/26/2025 05:10:59 | 10/26/2025 16:32:06 | RF Unit CPRI Interface Error at JBL0468-P2_SRAN @ Sceco | 10/26/2025 04:26:47 | Minor | 26504 | RF Unit CPRI Interface Error | 10/26/2025 04:25:16 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0468 | FLM_TE | [8 empty] | API | 10/26/2025 04:32:06 | 10/26/2025 05:10:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000165 | PCM-20251026-00000329 | TT-20251026-00313 | Reference_telecom | Region_3 | MKMD2538 | MKMD2538 |  |  |  | TAUSEEF ILYAS | 10/26/2025 04:34:40 | 10/26/2025 04:59:42 | 10/26/2025 16:34:40 | MW_LOF at MKMD2538_NE_1 @ Generator_SG | 10/26/2025 00:34:22 | Minor | 1-631 | MW_LOF | 10/26/2025 00:34:13 | P3 | SRAN | madinah | Generator_SG | TX NSA | MKMD2538 | FLM_TE | [8 empty] | API | 10/26/2025 04:34:40 | 10/26/2025 04:59:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000167 | PCM-20251026-00000341 | TT-20251026-00320 | Telecom | Region_6 | BHAB2253 | BHAB2253 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/26/2025 04:50:29 | 10/26/2025 08:38:54 | 10/26/2025 10:50:29 | 1(2G) sites down under BHAB2253-P3/BHAB2253-P3 @ Generator_SG | 10/26/2025 04:42:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 04:41:59 | P3 | 2G | Albaha | Generator_SG | 2G SA | BHAB2253-P3 | FLM_TE | BHAB2253 | Results: DOWN SITE HUB BHAB2253-P3 BHAB2253 Summary: Hub: BHAB2253, Down Count: 1, Down Sites: BHAB2253-P3 Alarm Summary: BHAB2253 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 04:50:29 | 10/26/2025 08:33:22 | 10/26/2025 08:38:27 |  |  | 10/26/2025 08:38:54 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000168 | PCM-20251026-00000344 | TT-20251026-00324 | Telecom | Region_4 | JED0723 | JED0723 |  |  |  | Nazeer Mohammed | 10/26/2025 04:51:44 | 10/26/2025 04:51:44 | 10/26/2025 10:51:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0723-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB-WDM @ Sceco | 10/26/2025 04:50:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 04:50:50 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0723 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 04:51:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000169 | PCM-20251026-00000345 | TT-20251026-00321 | EM | Region_4 | JED0723 | JED0723 |  |  |  | Nazeer Mohammed | 10/26/2025 04:51:59 | 10/26/2025 05:57:07 | 10/26/2025 08:51:59 | 1(2G/5G) sites down under JED0723-P1-HUB-WDM-FON @ Sceco | 10/26/2025 04:43:56 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 04:43:54 | P1 | 2G | jeddah | Sceco | 5G SA | JED0723-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB-WDM | FLM_TE | JED0723 | Results: DOWN SITE HUB JED0723-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB-WDM JED0723 Summary: Hub: JED0723, Down Count: 1, Down Sites: JED0723-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB-WDM Alarm Summary: JED0723 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.68.76:8080] [URL:http://10.97.68.76:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 04:51:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000170 | PCM-20251026-00000348 | TT-20251026-00327 | Telecom | Region_1 | DJL0551 | DJL0551 |  |  |  | Syed Fawad Ali | 10/26/2025 04:56:52 | 10/26/2025 04:57:50 | 10/26/2025 16:56:52 | SFP Removed at DJL0551-5 on 10.147.4.50 @ Sceco_STB | 10/26/2025 02:45:13 | Minor | SFP Removed | SFP Removed | 10/26/2025 02:52:38 | P2 | SRAN | sakaka | Sceco_STB | TX NSA | DJL0551 | FLM_TE | [8 empty] | API | 10/26/2025 04:56:52 | 10/26/2025 04:57:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000172 | PCM-20251026-00000351 | TT-20251026-00332 | Telecom | Region_6 | DAR0918 | DAR0918 |  |  |  | Muhammad Ali | 10/26/2025 05:02:32 | 10/26/2025 05:08:31 | 10/26/2025 11:02:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR0918-GSM-UMTS-P2 @ Sceco | 10/26/2025 05:01:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 05:01:35 | P2 | 2G | dair | Sceco | 5G_Cell SA | DAR0918 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 05:02:32 | 10/26/2025 05:08:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000173 | PCM-20251026-00000352 | TT-20251026-00329 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:02:59 | 10/26/2025 05:02:59 | 10/26/2025 11:02:59 | 1(2G) sites down under MKYL0914-P3/MKYL0914-P3 @ Sceco | 10/26/2025 04:54:39 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 04:54:36 | P3 | 2G | alaith | Sceco | 2G SA | MKYL0914-P3 | FLM_TE | MKYL0914 | Results: DOWN SITE HUB MKYL0914-P3 MKYL0914 Summary: Hub: MKYL0914, Down Count: 1, Down Sites: MKYL0914-P3 Alarm Summary: MKYL0914 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 05:02:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000174 | PCM-20251026-00000354 | TT-20251026-00334 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 05:05:08 | 10/26/2025 06:55:23 | 10/26/2025 17:05:08 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/26/2025 04:56:48 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 04:56:38 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 05:05:08 | 10/26/2025 06:55:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000175 | PCM-20251026-00000356 | TT-20251026-00331 | EM | Region_6 | JIZ1M7092 | JIZ0092 |  |  |  | Osama Hadi | 10/26/2025 05:06:59 | 10/26/2025 06:41:01 | 10/26/2025 09:06:59 | 1(3G/LTE) sites down under JIZ0092-P1-HUB @ Sceco_STB | 10/26/2025 04:58:34 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 04:58:30 | P1 | 4G | jizan | Sceco_STB | LTE SA | JIZ0092-G9-L8-L18-L21-SBTS-P1-HUB | FLM_TE | JIZ0092 | Results: DOWN SITE HUB JIZ0092-G9-L8-L18-L21-SBTS-P1-HUB JIZ0092 Summary: Hub: JIZ0092, Down Count: 1, Down Sites: JIZ0092-G9-L8-L18-L21-SBTS-P1-HUB Alarm Summary: JIZ0092 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.103.39.84:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 05:06:59 | 10/26/2025 05:12:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000176 | PCM-20251026-00000361 | TT-20251026-00317 | Telecom | Region_6 | JDJZ0885 | JDJZ0885 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 05:08:20 | 10/26/2025 11:04:26 | 10/26/2025 09:08:20 | 6(2G) 7(3G) 2(5G) sites down under JDJZ0895-P3 @ Sceco_STB | 10/26/2025 04:35:36 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 04:35:32 | P1 | 2G | derb | Sceco_STB | 2G_3G_5G SA | JDJZ0895-P3 2G_3G_5G,JDJZ0780-P3 2G_3G_5G,JDJZ0782-P3 2G_3G,JDJZ0781-P2 3G,JDJZ0783-P2 2G_3G,QEH0142-P2 2G_3G,JDJZ0885-P1-HUB 3G,HRD0778-P1-VIP 2G | FLM_TE | JDJZ0885 | Results: DOWN SITE HUB JDJZ0895-P3 JDJZ0885 JDJZ0780-P3 JDJZ0885 JDJZ0782-P3 JDJZ0885 JDJZ0781-P2 JDJZ0885 JDJZ0783-P2 JDJZ0885 QEH0142-P2 JDJZ0885 JDJZ0885-P1-HUB JDJZ0885 HRD0778-P1-VIP JDJZ0885 Summary: Hub: JDJZ0885, Down Count: 8, Down Sites: JDJZ0895-P3, JDJZ0780-P3, JDJZ0782-P3, JDJZ0781-P2, JDJZ0783-P2, QEH0142-P2, JDJZ0885-P1-HUB, HRD0778-P1-VIP Alarm Summary: JDJZ0885 No Active Alarm on HUB | PCM-20251026-00000339 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 05:08:20 | 10/26/2025 11:04:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000177 | PCM-20251026-00000362 | TT-20251026-00270 | Reference_telecom | Region_4 | JED1M7223 | JED0223 |  |  |  | Nazeer Mohammed | 10/26/2025 05:11:48 | 10/26/2025 05:11:48 | 10/26/2025 11:11:48 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M7223-P1-HUB-CA-L900-L800-SBTS @ Sceco_STB | 10/26/2025 03:56:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:56:31 | P1 | 4G | jeddah | Sceco_STB | 5G_Cell SA | JED1M7223 | FLM_TE |  |  | PCM-20251026-00000299 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/26/2025 05:11:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000178 | PCM-20251026-00000364 | TT-20251026-00325 | Reference_telecom | Region_4 | JED1M8928 | JED2928 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 05:14:27 | 10/26/2025 05:14:27 | 10/26/2025 11:14:27 | BASE STATION CONNECTIVITY PROBLEM (OMU signaling connection failure in Abis interface;Default System Time) at JED1M8928-USF-P3 @ Sceco | 10/26/2025 04:50:23 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 07/16/2024 13:20:41 | P3 | 4G | qunfuddah | Sceco | LTE NSA | JED1M8928 | FLM_TE |  |  | PCM-20251026-00000346 | Please check the multiple HW issue | Please check the multiple HW issue |  |  |  | API | 10/26/2025 05:14:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000179 | PCM-20251026-00000366 | TT-20251026-00314 | Reference_telecom | Region_6 | BHAB1M8253 | BHAB2253 | Equipment | BTS_Cable | Replace CPRI Cable | Muhammad Jamal Khan Abbas Ali | 10/26/2025 05:15:15 | 10/26/2025 08:44:24 | 10/26/2025 17:15:15 | BASE STATION CONNECTIVITY PROBLEM (S1 SCTP path failure) at BHAB1M8253-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 04:27:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 04:27:11 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8253 | FLM_TE |  |  | PCM-20251026-00000330 | Please check the site down | Please check the site down |  |  |  | API | 10/26/2025 05:15:15 | 10/26/2025 08:33:22 | 10/26/2025 08:44:07 |  |  | 10/26/2025 08:44:24 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000181 | PCM-20251026-00000369 | TT-20251026-00330 | Reference_telecom | Region_4 | JED1MN0187 | JED0187 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 05:18:43 | 10/26/2025 05:18:43 | 10/26/2025 17:18:43 | Fronthaul loop back connectivity check failure at JED1MN0187-NR2.6-P2 @ Sceco | 10/26/2025 04:29:58 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/26/2025 04:29:51 | P1 | 5G | jeddah | Sceco | 5G NSA | JED1MN0187 | FLM_TE |  |  | PCM-20251026-00000350 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/26/2025 05:18:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000182 | PCM-20251026-00000370 | TT-20251026-00345 | Reference_telecom | Region_4 | JED0017-ZJe03-CSG-03 | JED0017 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 05:19:02 | 10/26/2025 05:19:02 | 10/26/2025 17:19:02 | Optical Invalid at JED0017-ZJe03-CSG-03 // TT-20250426-00572 @ Sceco | 10/26/2025 03:13:16 | Minor | 101-2505224 | Optical Invalid | 10/26/2025 03:12:58 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0017-ZJe03-CSG-03 | FLM_TE | [8 empty] | API | 10/26/2025 05:19:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000183 | PCM-20251026-00000371 | TT-20251026-00346 | Telecom | Region_4 | BHR1M7308 | BHR0308 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 05:20:07 | 10/26/2025 09:43:24 | 10/26/2025 11:20:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR1M7308-P1-HUB-CA-L800-SBTS @ Sceco | 10/26/2025 05:19:11 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 05:19:03 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | BHR1M7308 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 05:20:07 | 10/26/2025 09:43:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000184 | PCM-20251026-00000374 | TT-20251026-00350 | EM | Region_4 | JED1U6760 | JED6060 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/26/2025 05:24:14 | 10/26/2025 05:24:14 | 10/26/2025 17:24:14 | AIRCON 2 FAILURE at JED1U6760-G9-L18-SBTS-P3 @ Sceco | 10/26/2025 05:16:11 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 05:16:03 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6760 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 05:24:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000185 | PCM-20251026-00000375 | TT-20251026-00351 | EM | Region_4 | MKYL0913 | MKYL0913 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/26/2025 05:24:45 | 10/26/2025 05:24:45 | 10/26/2025 17:24:45 | SHELTER DOOR OPEN;Default System Time at MKYL0913-GSM-UMTS-P2 @ Generator_SG | 10/26/2025 05:24:21 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/25/2025 03:12:04 | P2 | 2G | alaith | Generator_SG | 2G NSA | MKYL0913 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 05:24:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000186 | PCM-20251026-00000377 | TT-20251026-00354 | EM | Region_6 | BHAQ1M8435 | BHAQ2435 |  |  |  | SHAH KHALID | 10/26/2025 05:25:47 | 10/26/2025 10:20:14 | 10/26/2025 17:25:47 | Genset Running at BHAQ1M8435-P3 -G900-L800-SBTS @ Generator_DG | 10/26/2025 05:17:46 | Minor | 7103 | Genset Running | 10/26/2025 05:17:40 | P3 | 4G | Albaha | Generator_DG | LTE NSA | BHAQ1M8435 | FLM_EM | [5 empty] | Genset Running |  |  | API | 10/26/2025 05:25:47 | 10/26/2025 10:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000187 | PCM-20251026-00000385 | TT-20251026-00353 | Telecom | Region_4 | YLM0756 | YLM0756 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:30:29 | 10/26/2025 05:30:29 | 10/26/2025 09:30:29 | 1(5G) sites down under YLM0756-GSM-UMTS-P1 @ Generator_DG | 10/26/2025 05:22:12 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 05:22:08 | P1 | 2G | alaith | Generator_DG | 5G SA | YLM0756-GSM-UMTS-P1 | FLM_TE | YLM0756 | Results: DOWN SITE HUB YLM0756-GSM-UMTS-P1 YLM0756 Summary: Hub: YLM0756, Down Count: 1, Down Sites: YLM0756-GSM-UMTS-P1 Alarm Summary: YLM0756 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.9.12:8080] [URL:http://10.88.9.12:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 05:30:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000188 | PCM-20251026-00000391 | TT-20251026-00359 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 05:34:37 | 10/26/2025 05:34:37 | 10/26/2025 11:34:37 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/26/2025 05:22:46 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 05:22:43 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251026-00000384 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 05:34:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000189 | PCM-20251026-00000392 | TT-20251026-00357 | Telecom | Region_4 | JED1M7498 | JED0498 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 05:34:49 | 10/26/2025 10:36:47 | 10/26/2025 09:34:49 | BASE STATION ANTENNA LINE PROBLEM at JED1M7498-CA-L800-L900-P1-HUB-WDM @ Sceco | 10/26/2025 05:20:12 | Critical | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 05:20:06 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7498 | FLM_TE |  |  | PCM-20251026-00000380 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 05:34:49 | 10/26/2025 10:36:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000190 | PCM-20251026-00000393 | TT-20251026-00358 | Reference_telecom | Region_6 | QLW1M8370 | QLW2370 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 05:36:34 | 10/26/2025 10:55:20 | 10/26/2025 17:36:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 04:26:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 03:29:12 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_TE |  |  | PCM-20251026-00000383 | Please close the alarm during site down | Please close the alarm during site down |  |  |  | API | 10/26/2025 05:36:34 | 10/26/2025 10:52:38 | 10/26/2025 10:55:09 |  |  | 10/26/2025 10:55:20 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000191 | PCM-20251026-00000396 | TT-20251026-00349 | Reference_telecom | Region_5 | USMD1M3704 | USMD0704 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 05:40:27 | 10/26/2025 05:40:27 | 10/26/2025 11:40:27 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at USMD1M3704-P2-USF @ Sceco | 10/26/2025 04:55:39 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 04:53:30 | P2 | 3G | makkah | Sceco | 3G SA | USMD1M3704 | FLM_TE |  |  | PCM-20251026-00000373 | Please check the VSWR issue | Please check the VSWR issue |  |  |  | API | 10/26/2025 05:40:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000193 | PCM-20251026-00000398 | TT-20251026-00273 | Reference_telecom | Region_5 | MAK0981 | MAK0981 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 05:42:01 | 10/26/2025 05:42:01 | 10/26/2025 11:42:01 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MAK0981-P2 @ Sceco | 10/26/2025 04:01:07 | Major | 7607 | TRX OPERATION DEGRADED | 10/26/2025 04:01:02 | P2 | 2G | makkah | Sceco | 2G_TRX NSA | MAK0981 | FLM_TE |  |  | PCM-20251026-00000305 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/26/2025 05:42:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000194 | PCM-20251026-00000399 | TT-20251026-00371 | Telecom | Region_4 | YLM0740 | YLM0740 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:45:32 | 10/26/2025 05:45:32 | 10/26/2025 11:45:32 | 1(2G) sites down under YLM0740-P2-USF/YLM0740-P2-USF @ Sceco | 10/26/2025 05:37:23 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 05:37:18 | P2 | 2G | alaith | Sceco | 2G SA | YLM0740-P2-USF | FLM_TE | YLM0740 | Results: DOWN SITE HUB YLM0740-P2-USF YLM0740 Summary: Hub: YLM0740, Down Count: 1, Down Sites: YLM0740-P2-USF Alarm Summary: YLM0740 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 05:45:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000195 | PCM-20251026-00000403 | TT-20251026-00377 | EM | Region_4 | MUMA1M8337 | MUMA2337 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 05:49:03 | 10/26/2025 09:29:24 | 10/26/2025 17:49:03 | COMMERCIAL POWER FAILURE at MUMA1M8337-G9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 05:40:57 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/26/2025 05:40:49 | P3 | 4G | jeddah | Sceco | LTE NSA | MUMA1M8337 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/26/2025 05:49:03 | 10/26/2025 09:29:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000197 | PCM-20251026-00000407 | TT-20251026-00266 | Telecom | Region_4 | JDJZ0768 | JDJZ0768 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:53:16 | 10/26/2025 05:53:16 | 10/26/2025 07:53:16 | 14(2G) 21(3G) 1(LTE) 2(5G) sites down under SDY0737-P3 @ Generator_SG | 10/26/2025 03:53:01 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:52:55 | P1 | 2G | qunfuddah | Generator_DG | 2G_3G_5G SA | YLM0768-P3 2G_3G_5G,SDY0737-P3 2G_3G,YLM0746-P3 3G,SDY0870-P3 2G_3G,YLM0745-P3 3G,SDY0146-P3 2G_3G,YLM0161-P3 2G_3G,BIK0156-P3 3G,SDY0145-P3 3G,YLM0149-P3 3G,SDY0163-P3 2G_3G,SDY0148-P3 3G,YLM0757-P3 3G,YLM0789-P3 3G,SDY0147-P3 3G,SDY0162-P3 2G_3G,SDY0158-P3 3G,MLJI0744-P3 3G,SDY0739-P3 3G,YLM2368-P3 2G,YLM0752-P1 2G,SDY0766-P3 2G,YLM0391-P1 2G,MKYL0908-P2 2G,YLM2369-P1 2G | FLM_TE | JDJZ0768 | Results: DOWN SITE HUB YLM0768-P3 YLM0768 SDY0737-P3 SDY0737 YLM0746-P3 YLM0746 SDY0870-P3 Need to check YLM0745-P3 YLM2368 SDY0146-P3 SDY0146 YLM0161-P3 SDY0147 BIK0156-P3 SDY0147 SDY0145-P3 Need to check YLM0149-P3 SDY0147 SDY0163-P3 SDY0737 SDY0148-P3 SDY0148 YLM0757-P3 YLM0757 YLM0789-P3 YLM2368 SDY0147-P3 SDY0147 SDY0162-P3 SDY0147 SDY0158-P3 SDY0147 MLJI0744-P3 YLM2368 SDY0739-P3 SDY0147 YLM2368-P3 YLM2368 YLM0752-P1 SDY0147 SDY0766-P3 Need to check YLM0391-P1 YLM2368 MKYL0908-P2 Need to check YLM2369-P1 YLM2369 Summary: Hub: YLM0768, Down Count: 1, Down Sites: YLM0768-P3 Hub: SDY0737, Down Count: 2, Down Sites: SDY0737-P3, SDY0163-P3 Hub: YLM0746, Down Count: 1, Down Sites: YLM0746-P3 Hub: YLM2368, Down Count: 5, Down Sites: YLM0745-P3, YLM0789-P3, MLJI0744-P3, YLM2368-P3, YLM0391-P1 Hub: SDY0146, Down Count: 1, Down Sites: SDY0146-P3 Hub: SDY0147, Down Count: 8, Down Sites: YLM0161-P3, BIK0156-P3, YLM0149-P3, SDY0147-P3, SDY0162-P3, SDY0158-P3, SDY0739-P3, YLM0752-P1 Hub: SDY0148, Down Count: 1, Down Sites: SDY0148-P3 Hub: YLM0757, Down Count: 1, Down Sites: YLM0757-P3 Hub: YLM2369, Down Count: 1, Down Sites: YLM2369-P1 Alarm Summary: YLM0768 No Active Alarm on HUB SDY0737 No Active Alarm on HUB YLM0746 No Active Alarm on HUB HUB site not found YLM2368 No Active Alarm on HUB SDY0146 No Active Alarm on HUB SDY0147 Alarm Active on HUB SDY0148 No Active Alarm on HUB YLM0757 No Active Alarm on HUB YLM2369 No Active Alarm on HUB | PCM-20251026-00000337 | Thanks to check locally as no action can be taken from our side | Thanks to check locally as no action can be taken from our side |  | sites down |  | API | 10/26/2025 05:53:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000198 | PCM-20251026-00000408 | TT-20251026-00381 | Telecom | Region_4 | JED0435 | JED0435 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 05:53:41 | 10/26/2025 06:48:33 | 10/26/2025 09:53:41 | JED0723 NODE ISOLATED | 10/26/2025 05:53:12 | Critical | 1-12843 | OSC_LOS | 10/26/2025 05:53:01 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0435 | FLM_TE | [5 empty] | 0-1-C-9-F1AST4-1(RM1/TM1(FROM JED0723))-OSC:1 |  |  | API | 10/26/2025 05:53:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000200 | PCM-20251026-00000410 | TT-20251026-00383 | Reference_telecom | Region_2 | RIYA2U6760A | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/26/2025 05:54:12 | 10/26/2025 05:54:12 | 10/26/2025 11:54:12 | RF Out of Service at RIYA2U6760A-P3 @ Sceco | 10/26/2025 05:48:14 | Major | 29248 | RF Out of Service | 10/26/2025 05:48:00 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6760A | FLM_TE | [8 empty] | API | 10/26/2025 05:54:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000202 | PCM-20251026-00000412 | TT-20251026-00380 | Telecom | Region_4 | SDY0170 | SDY0170 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:58:03 | 10/26/2025 05:58:03 | 10/26/2025 11:58:03 | 1(5G) sites down under SDY0170-GSM-UMTS-P3 @ Generator_SG | 10/26/2025 05:49:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 05:49:54 | P3 | 2G | qunfuddah | Generator_SG | 5G SA | SDY0170-GSM-UMTS-P3 | FLM_TE | SDY0170 | Results: DOWN SITE HUB SDY0170-GSM-UMTS-P3 SDY0170 Summary: Hub: SDY0170, Down Count: 1, Down Sites: SDY0170-GSM-UMTS-P3 Alarm Summary: SDY0170 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.25.116:8080] [URL:http://10.88.25.116:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 05:58:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000205 | PCM-20251026-00000418 | TT-20251026-00392 | Telecom | Region_4 | TFBH0892 | TFBH0892 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 06:00:56 | 10/26/2025 09:33:55 | 10/26/2025 12:00:56 | LAN_LOC at TFBH0892_OSC1 @ Sceco_STB | 10/26/2025 01:55:48 | Major | 1-12926 | LAN_LOC | 10/26/2025 01:55:15 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_TE | [5 empty] | 0-TO MIS0359(1-A)-8-T1SCC-4(ETH1/ETH1)-COM:1 |  |  | API | 10/26/2025 06:00:56 | 10/26/2025 09:33:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000206 | PCM-20251026-00000419 | TT-20251026-00393 | Telecom | Region_1 | ARR0625 | ARR0625 |  |  |  | Muhammad Zubair Guilzar | 10/26/2025 06:00:57 | 10/26/2025 06:15:29 | 10/26/2025 18:00:57 | RF Unit Maintenance Link Failure at ARR0625-P2_SRAN @ Sceco | 10/26/2025 01:08:42 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 01:07:00 | P2 | SRAN | arar | Sceco | 2G NSA | ARR0625 | FLM_TE | [8 empty] | API | 10/26/2025 06:00:57 | 10/26/2025 06:15:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000208 | PCM-20251026-00000421 | TT-20251026-00395 | Telecom | Region_4 | TFBH0892 | TFBH0892 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 06:00:58 | 10/26/2025 09:33:55 | 10/26/2025 12:00:58 | LAN_LOC at TFBH0892_ELC @ Sceco_STB | 10/26/2025 01:55:25 | Major | 1-12926 | LAN_LOC | 10/26/2025 01:55:15 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_TE | [5 empty] | 0-ELC(1-C)-7-T1SCC-5(ETH2&EXT1/ETH2&EXT1)-COM:1 |  |  | API | 10/26/2025 06:00:58 | 10/26/2025 09:33:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000210 | PCM-20251026-00000427 | TT-20251026-00399 | Telecom | Region_6 | DAR1MT0901 | DAR0901 |  |  |  | Muhammad Ali | 10/26/2025 06:04:00 | 10/26/2025 06:04:00 | 10/26/2025 10:04:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR1MT0901-P1 @ Generator_DG | 10/26/2025 06:03:09 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:03:01 | P1 | 4G | raith | Generator_DG | 5G_Cell SA | DAR1MT0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 06:04:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000211 | PCM-20251026-00000428 | TT-20251026-00400 | Telecom | Region_4 | JED1M7235 | JED0235 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 06:05:02 | 10/26/2025 09:43:25 | 10/26/2025 18:05:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7235-P3-CA-L900-L800-SBTS @ Generator_SG | 10/26/2025 06:04:01 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:03:50 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7235 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 06:05:02 | 10/26/2025 09:43:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000212 | PCM-20251026-00000429 | TT-20251026-00401 | EM | Region_6 | ABDB1M7841 | ABDB0841 |  |  |  | Aziz Ul Haq Umar Gul | 10/26/2025 06:05:03 | 10/26/2025 10:49:08 | 10/26/2025 18:05:03 | SHELTER DOOR OPEN at ABDB1M7841-P3-L800-SBTS @ Generator_SG | 10/26/2025 06:04:27 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 06:04:21 | P3 | 4G | derb | Generator_SG | LTE NSA | ABDB1M7841 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 06:05:03 | 10/26/2025 10:49:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000214 | PCM-20251026-00000434 | TT-20251026-00370 | EM | Region_5 | USMD0704 | USMD0704 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 06:09:47 | 10/26/2025 06:34:35 | 10/26/2025 18:09:47 | TRX FAULTY (FF FF FF FF FF FF shared:S) at USMD0704-P2-USF RFC Violation due to time exceeded(CRQ000000538814) | 10/26/2025 05:31:24 | Minor | 7606 | TRX FAULTY | 10/26/2025 05:31:20 | P2 | 2G | makkah | Sceco | 2G_Cell SA | USMD0704 | FLM_TE |  |  | PCM-20251026-00000395 | No Power Issue | No Power Issue |  |  |  | API | 10/26/2025 06:09:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000218 | PCM-20251026-00000440 | TT-20251025-01836 | Telecom | Region_6 | TLT0375 | TLT0375 |  |  |  | Umair Abbas Muhammad Abbas | 10/26/2025 06:12:28 | 10/26/2025 06:20:27 | 10/26/2025 12:12:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at TLT0375-GSM-UMTS-P3 @ Generator_SG | 10/25/2025 22:06:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:06:14 | P3 | 2G | turaib | Generator_SG | 5G_Cell SA | TLT0375 | FLM_TE |  |  | PCM-20251026-00000436 | Please visit to check the HW issue | Please visit to check the HW issue |  |  |  | API | 10/26/2025 06:12:28 | 10/26/2025 06:20:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000219 | PCM-20251026-00000441 | TT-20251026-00374 | Reference_telecom | Region_6 | TLT1M3375 | TLT0375 |  |  |  | Umair Abbas Muhammad Abbas | 10/26/2025 06:13:23 | 10/26/2025 06:20:28 | 10/26/2025 12:13:23 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TLT1M3375-P3 @ Generator_SG | 10/26/2025 05:19:21 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 05:17:12 | P3 | 3G | turaib | Generator_SG | 3G SA | TLT1M3375 | FLM_TE |  |  | PCM-20251026-00000401 | Please visit to check the HW issue | Please visit to check the HW issue |  |  |  | API | 10/26/2025 06:13:23 | 10/26/2025 06:20:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000220 | PCM-20251026-00000442 | TT-20251026-00375 | Reference_telecom | Region_6 | KMBS0666 | KMBS0666 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 06:13:44 | 10/26/2025 06:13:44 | 10/26/2025 12:13:44 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at KMBS0666-GSM-UMTS-P2-USF @ Sceco | 10/26/2025 05:42:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 05:42:44 | P2 | 2G | bisha | Sceco | 5G_Cell SA | KMBS0666 | FLM_TE |  |  | PCM-20251026-00000402 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/26/2025 06:13:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000221 | PCM-20251026-00000445 | TT-20251026-00405 | Telecom | Region_4 | NSH0193 | NSH0193 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 06:15:34 | 10/26/2025 06:15:34 | 10/26/2025 12:15:34 | 1(2G) sites down under NSH0193-P3/NSH0193-P3 @ Sceco | 10/26/2025 06:07:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:07:11 | P3 | 2G | qunfuddah | Sceco | 2G SA | NSH0193-P3 | FLM_TE | NSH0193 | Results: DOWN SITE HUB NSH0193-P3 NSH0193 Summary: Hub: NSH0193, Down Count: 1, Down Sites: NSH0193-P3 Alarm Summary: NSH0193 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 06:15:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000223 | PCM-20251026-00000451 | TT-20251026-00414 | EM | Region_4 | SQR0074 | SQR0074 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 06:22:58 | 10/26/2025 09:54:23 | 10/26/2025 12:22:58 | 1(2G/LTE) sites down under SQR0074-P2-USF/SQR0074-P2-USF @ Generator_SG | 10/26/2025 06:14:42 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:14:36 | P2 | 2G | adam | Generator_SG | 2G SA | SQR0074-P2-USF | FLM_TE | SQR0074 | Results: DOWN SITE HUB SQR0074-P2-USF SQR0074 Summary: Hub: SQR0074, Down Count: 1, Down Sites: SQR0074-P2-USF Alarm Summary: SQR0074 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 06:22:58 | 10/26/2025 09:54:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000225 | PCM-20251026-00000453 | TT-20251026-00190 | Telecom | Region_1 | DAM-IPsec-9811-01 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/26/2025 06:24:58 | 10/26/2025 06:24:58 | 10/26/2025 18:24:58 | Dust Net Clean Alarm at DAM-IPsec-9811-01 @ Sceco_STB | 10/26/2025 02:49:05 | Minor | 101-3067995 | Dust Net Clean Alarm | 10/26/2025 02:49:02 | P1 | IPBB | dammam | Sceco_STB | IPRAN NSA | DAM-IPsec-9811-01 | FLM_TE |  |  | PCM-20251026-00000224 | Please close the case from your side | Please close the case from your side |  |  |  | API | 10/26/2025 06:24:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000226 | PCM-20251026-00000454 | TT-20251026-00404 | Telecom | Region_6 | SRA2359 | SRA2359 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 06:25:22 | 10/26/2025 09:44:45 | 10/26/2025 12:25:22 | 4(2G) 4(LTE) sites down under SRA2362-P3,QLW2376-P3,QLW2370-P3,QLW2374-P3-P3/QLW2374-P3-P3 @ Generator_SG | 10/26/2025 06:07:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:07:25 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2362-P3 2G_LTE,QLW2376-P3 2G_LTE,QLW2374-P3-P3 2G_LTE,QLW2370-P3 2G_LTE | FLM_EM | SRA2359 | Results: DOWN SITE HUB SRA2362-P3 SRA2362 QLW2376-P3 QLW2376 QLW2374-P3-P3 QLW2374 QLW2370-P3 QLW2370 Summary: Hub: SRA2362, Down Count: 1, Down Sites: SRA2362-P3 Hub: QLW2376, Down Count: 1, Down Sites: QLW2376-P3 Hub: QLW2374, Down Count: 1, Down Sites: QLW2374-P3-P3 Hub: QLW2370, Down Count: 1, Down Sites: QLW2370-P3 Alarm Summary: SRA2362 Alarm Active on HUB QLW2376 Alarm Active on HUB QLW2374 Alarm Active on HUB QLW2370 No Active Alarm on HUB | PCM-20251026-00000444 | SRA2359 | SRA2359 |  | sites down |  | API | 10/26/2025 06:25:22 | 10/26/2025 09:44:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000229 | PCM-20251026-00000460 | TT-20251026-00410 | Reference_telecom | Region_6 | ABH1M7234 | ABH0234 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 06:31:56 | 10/26/2025 06:31:56 | 10/26/2025 18:31:56 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABH1M7234-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/26/2025 04:25:13 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 04:16:45 | P2 | 4G | abha | Sceco | LTE NSA | ABH1M7234 | FLM_TE |  |  | PCM-20251026-00000446 | Please close alarm during site down | Please close alarm during site down |  |  |  | API | 10/26/2025 06:31:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026000230 | PCM-20251026-00000461 | TT-20251026-00418 | Reference_telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/26/2025 06:32:52 | 10/26/2025 11:00:29 | 10/26/2025 12:32:52 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/26/2025 06:24:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:24:50 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251026-00000456 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/26/2025 06:32:52 | 10/26/2025 10:59:17 | 10/26/2025 10:59:26 | 10/26/2025 11:00:27 | 10/26/2025 11:00:29 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000231 | PCM-20251026-00000463 | TT-20251026-00347 | EM | Region_3 | YNB2046 | YNB2046 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 06:33:11 | 10/26/2025 06:33:11 | 10/26/2025 12:33:11 | 1(2G/3G/LTE) sites down under YNB2046-P2/YB1MBSCH01 @ Sceco | 10/26/2025 05:19:06 | Major | 22214 | NodeB Unavailable | 10/26/2025 05:19:03 | P2 | SRAN | yanbu | Sceco | 3G_LTE SA | YNB2046-P2 | FLM_TE | YNB2046 | Dear FLM Team, hub site is YNB2046 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM | PCM-20251026-00000457 | Dear FLM Team, hub site is YNB2046 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM | Dear FLM Team, hub site is YNB2046 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM |  | sites down |  | API | 10/26/2025 06:33:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000232 | PCM-20251026-00000464 | TT-20251026-00435 | Telecom | Region_1 | KSB0031 | KSB0031 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | Muhammad Zubair Guilzar | 10/26/2025 06:37:03 | 10/26/2025 08:46:23 | 10/26/2025 12:37:03 | BBU CPRI Interface Error at KSB0031-P3-WDM_SRAN @ Sceco_STB | 10/26/2025 06:32:37 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 06:30:00 | P3 | SRAN | arar | Sceco_STB | 2G NSA | KSB0031 | FLM_TE | [8 empty] | API | 10/26/2025 06:37:03 | 10/26/2025 06:49:44 | 10/26/2025 06:49:51 | 10/26/2025 06:49:59 | 10/26/2025 06:55:35 | 10/26/2025 08:46:23 |  | Muhammad Zubair Guilzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000233 | PCM-20251026-00000466 | TT-20251026-00440 | EM | Region_6 | BSA1M8308 | BSA2308 |  |  |  | Asad Saddiq | 10/26/2025 06:42:44 | 10/26/2025 07:20:15 | 10/26/2025 18:42:44 | SHELTER DOOR OPEN;Default System Time at BSA1M8308-G9-L800-L1800-L2100-SBTS-P3 @ Generator_SG | 10/26/2025 06:42:23 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/26/2025 03:01:05 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8308 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 06:42:44 | 10/26/2025 07:20:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000235 | PCM-20251026-00000477 | TT-20251026-00467 | Reference_telecom | Region_6 | BCAL1M3714 | BCAL0714 |  |  |  | Hamid Ullah Muhammad Alam Khan | 10/26/2025 06:56:49 | 10/26/2025 06:56:49 | 10/26/2025 12:56:49 | CELL OPERATION DEGRADED (Rx signal level failure) at BCAL1M3714-P1-HUB-WBB-G3 (Ref:TT-20251023-01612) @ Sceco_STB | 10/25/2025 08:07:15 | Major | 7654 | CELL OPERATION DEGRADED | 10/25/2025 08:06:58 | P1 | 3G | bisha | Sceco_STB | LTE_Cell SA | BCAL1M3714 | FLM_TE | [5 empty] | Rx signal level failure |  |  | API | 10/26/2025 06:56:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000236 | PCM-20251026-00000478 | TT-20251026-00454 | EM | Region_5 | USMD0704 | USMD0704 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 06:56:59 | 10/26/2025 07:45:01 | 10/26/2025 12:56:59 | 1(2G/3G/5G) sites down under USMD0704-P2-USF @ Sceco | 10/26/2025 06:48:41 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 06:48:38 | P2 | 2G | makkah | Sceco | 5G SA | USMD0704-GSM-UMTS-P2-USF | FLM_TE | USMD0704 | Results: DOWN SITE HUB USMD0704-GSM-UMTS-P2-USF USMD0704 Summary: Hub: USMD0704, Down Count: 1, Down Sites: USMD0704-GSM-UMTS-P2-USF Alarm Summary: USMD0704 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.98.154.244:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 06:56:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000237 | PCM-20251026-00000480 | TT-20251026-00469 | Reference_EM | Region_3 | DBQL2M5259 | DBQL0259 |  |  |  | Abdelwahab Mahmoud Abdelwahab Abboud | 10/26/2025 06:57:43 | 10/26/2025 06:57:43 | 10/26/2025 18:57:43 | Door opening alarm at DBQL2M5259-P3 @ Sceco | 10/26/2025 06:57:20 | Minor | 65101 | Door opening alarm | 10/26/2025 06:57:16 | P3 | 2G | tabouk | Sceco | 2G NSA | DBQL2M5259 | FLM_EM | [8 empty] | API | 10/26/2025 06:57:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000238 | PCM-20251026-00000484 | TT-20251026-00474 | Reference_telecom | Region_6 | KMS0133 | KMS0133 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 07:01:21 | 10/26/2025 07:01:21 | 10/26/2025 19:01:21 | BASE STATION SERVICE PROBLEM (No feedback signal) at KMS0133-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 06:56:38 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:56:28 | P3 | 2G | khamis mushyet | Sceco | LTE_Cell SA | KMS0133 | FLM_TE | [5 empty] | No feedback signal |  |  | API | 10/26/2025 07:01:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000239 | PCM-20251026-00000485 | TT-20251026-00475 | EM | Region_6 | SRA1M8359 | SRA2359 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 07:01:21 | 10/26/2025 09:44:46 | 10/26/2025 19:01:21 | SHELTER DOOR OPEN at SRA1M8359-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/26/2025 07:01:12 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 07:01:04 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8359 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 07:01:21 | 10/26/2025 09:44:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000240 | PCM-20251026-00000486 | TT-20251026-00476 | Telecom | Region_1 | KBR2M7155 | KBR0155 |  |  |  | Imran Ali Yousaf | 10/26/2025 07:02:12 | 10/26/2025 09:39:55 | 10/26/2025 13:02:12 | Cell Unavailable at KBR2M7155-P3-L800 @ Sceco | 10/26/2025 07:01:26 | Major | 29240 | Cell Unavailable | 10/26/2025 07:01:03 | P3 | 4G | dammam | Sceco | LTE SA | KBR2M7155 | FLM_TE | [8 empty] | API | 10/26/2025 07:02:12 | 10/26/2025 09:39:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000241 | PCM-20251026-00000488 | TT-20251026-00479 | Telecom | Region_4 | JED1MN0196 | JED0196 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 07:02:53 | 10/26/2025 07:02:53 | 10/26/2025 13:02:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0196-NR2.6 @ Sceco | 10/26/2025 07:02:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:02:06 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0196 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:02:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000242 | PCM-20251026-00000489 | TT-20251026-00481 | Reference_telecom | Region_6 | MHA0517 | MHA0517 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 07:03:39 | 10/26/2025 07:03:39 | 10/26/2025 13:03:39 | BASE STATION SERVICE PROBLEM (TX out of order) at MHA0517-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 (Ref:TT-20251025-01774) @ Sceco | 10/25/2025 23:11:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 23:11:40 | P3 | 2G | khamis mushyet | Sceco | LTE_Cell SA | MHA0517 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/26/2025 07:03:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000243 | PCM-20251026-00000491 | TT-20251026-00472 | Telecom | Region_3 | MDV2M1072 | MDV0072 |  |  |  | TAUSEEF ILYAS | 10/26/2025 07:06:00 | 10/26/2025 07:16:46 | 10/26/2025 13:06:00 | 1(2G) sites down under MDV0072-P2-Rehome/R2_RY2_HWBSC01 @ Sceco | 10/26/2025 06:57:56 | Major | 21807 | OML Fault | 10/26/2025 06:57:47 | P2 | 2G | madinah | Sceco | 2G SA | MDV0072-P2-Rehome | FLM_TE | MDV0072 | Results: DOWN SITE HUB MDV0072-P2-Rehome MDV0072 Summary: Hub: MDV0072, Down Count: 1, Down Sites: MDV0072-P2-Rehome Alarm Summary: MDV0072 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:06:00 | 10/26/2025 07:16:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000245 | PCM-20251026-00000496 | TT-20251026-00480 | EM | Region_4 | JED2029 | JED2029 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/26/2025 07:08:29 | 10/26/2025 11:03:42 | 10/26/2025 13:08:29 | 1(2G/5G) sites down under JED2029-P3/JED2029-P3 @ Sceco | 10/26/2025 07:00:27 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 07:00:22 | P3 | 2G | jeddah | Sceco | 2G SA | JED2029-P3 | FLM_TE | JED2029 | Results: DOWN SITE HUB JED2029-P3 JED2029 Summary: Hub: JED2029, Down Count: 1, Down Sites: JED2029-P3 Alarm Summary: JED2029 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:08:29 | 10/26/2025 11:03:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000246 | PCM-20251026-00000497 | TT-20251026-00488 | Reference_telecom | Region_6 | TNM1M7727 | TNM0727 | Equipment | BSS_HW_Stuck | Reset Air Scale | Fawad Khan | 10/26/2025 07:08:48 | 10/26/2025 09:40:26 | 10/26/2025 13:08:48 | BASE STATION SERVICE PROBLEM (FSP Reset Needed) at TNM1M7727-G9-NL8-L18-NL21-SBTS-P2 (Ref:TT-20251025-01307) @ Sceco | 10/25/2025 15:36:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:36:02 | P2 | 4G | mohail | Sceco | 5G_Cell SA | TNM1M7727 | FLM_TE | [5 empty] | FSP Reset Needed |  |  | API | 10/26/2025 07:08:48 | 10/26/2025 08:41:49 | 10/26/2025 09:39:33 |  |  | 10/26/2025 09:40:26 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000248 | PCM-20251026-00000500 | TT-20251026-00490 | Reference_telecom | Region_6 | DUS0058 | DUS0058 |  |  |  | SHAH KHALID | 10/26/2025 07:10:58 | 10/26/2025 10:20:14 | 10/26/2025 13:10:58 | BASE STATION ANTENNA LINE PROBLEM (Antenna line device HW failure) at DUS0058-G9-L8-L18-L21-NR2.6-SBTS-P3 (Ref:TT-20251023-00637) @ Sceco | 10/23/2025 18:53:36 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/23/2025 18:53:31 | P3 | 2G | Albaha | Sceco | LTE SA | DUS0058 | FLM_TE | [5 empty] | Antenna line device HW failure |  |  | API | 10/26/2025 07:10:58 | 10/26/2025 10:20:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000249 | PCM-20251026-00000501 | TT-20251026-00297 | Reference_telecom | Region_2 | RIY2M7395 | RIY0395 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 07:11:48 | 10/26/2025 09:03:24 | 10/26/2025 19:11:48 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M7395-P2-L900-L800 @ Generator_SG | 10/26/2025 01:26:17 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 01:26:13 | P2 | 4G | riyadh | Generator_SG | 2G NSA | RIY2M7395 | FLM_TE |  |  | PCM-20251026-00000322 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 07:11:48 | 10/26/2025 09:03:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000250 | PCM-20251026-00000505 | TT-20251026-00348 | Reference_telecom | Region_2 | RIY2M7134 | RIY0134 |  |  |  | Waseem Shahzad Ghulam Rasool | 10/26/2025 07:17:38 | 10/26/2025 10:47:10 | 10/26/2025 19:17:38 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M7134-P2-L900-L800 @ Sceco | 10/26/2025 02:21:23 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 02:21:20 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M7134 | FLM_TE |  |  | PCM-20251026-00000372 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 07:17:38 | 10/26/2025 10:47:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000251 | PCM-20251026-00000506 | TT-20251026-00496 | Reference_EM | Region_3 | HLJF2616 | HLJF2616 | Enviroment | Air Condition | Change Fan | Ibrahim Mohamed Yousif Ibrahim | 10/26/2025 07:18:24 | 10/26/2025 09:58:31 | 10/26/2025 13:18:24 | high temprature 32 at HLJF2616-P1-HUB_SRAN @ Generator_SG | 10/26/2025 07:08:02 | Major | 65102 | high temprature 32 | 10/26/2025 07:07:57 | P1 | SRAN | hail | Generator_SG | 2G NSA | HLJF2616 | FLM_EM | [8 empty] | API | 10/26/2025 07:18:24 | 10/26/2025 07:33:28 | 10/26/2025 08:57:09 | 10/26/2025 08:57:11 | 10/26/2025 09:00:12 | 10/26/2025 09:58:31 |  | Ibrahim Mohamed Yousif Ibrahim |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000252 | PCM-20251026-00000510 | TT-20251026-00417 | Telecom | Region_6 | JIZ0074 | JIZ0074 |  |  |  | Osama Hadi | 10/26/2025 07:19:29 | 10/26/2025 07:19:29 | 10/26/2025 13:19:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ0074-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-PI-VIP-ARP @ Sceco_STB | 10/26/2025 06:27:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:27:20 | VIP | 2G | jizan | Sceco_STB | 5G_Cell SA | JIZ0074 | FLM_TE |  |  | PCM-20251026-00000503 | Need to check locally | Need to check locally |  |  |  | API | 10/26/2025 07:19:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000253 | PCM-20251026-00000512 | TT-20251026-00495 | Telecom | Region_4 | JED0294 | JED0294 |  |  |  | Nazeer Mohammed | 10/26/2025 07:21:29 | 10/26/2025 07:21:29 | 10/26/2025 13:21:29 | 1(5G) sites down under JED0294-GSM-P3 @ Generator_SG | 10/26/2025 07:13:02 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 07:13:00 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5471101 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 07:21:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000254 | PCM-20251026-00000513 | TT-20251026-00289 | Telecom | Region_2 | RIY0399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Asad Ali Nadiq Khan | 10/26/2025 07:21:39 | 10/26/2025 10:58:30 | 10/26/2025 19:21:39 | RF Unit Clock Problem at RIY0399-P2_SRAN @ Sceco | 10/26/2025 04:16:55 | Minor | 26538 | RF Unit Clock Problem | 10/26/2025 04:14:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0399 | FLM_TE |  |  | PCM-20251026-00000470 | Dear FLM, Approved based on FLM TS done | Dear FLM, Approved based on FLM TS done |  |  |  | API | 10/26/2025 07:21:39 | 10/26/2025 08:12:28 | 10/26/2025 10:57:47 | 10/26/2025 10:57:57 | 10/26/2025 10:58:02 | 10/26/2025 10:58:30 |  | Asad Ali Nadiq Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000255 | PCM-20251026-00000514 | TT-20251026-00499 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 07:25:38 | 10/26/2025 07:25:38 | 10/26/2025 19:25:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 07:24:38 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:24:32 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0500 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:25:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000256 | PCM-20251026-00000516 | TT-20251026-00461 | Telecom | Region_4 | SJED1S7740 | SJED0740 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 07:30:47 | 10/26/2025 08:07:09 | 10/26/2025 13:30:47 | 2(LTE) sites down under SJED0741-CA-P3,SJED0740-CA-P3 @ Sceco | 10/26/2025 06:50:58 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 06:50:54 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0740-CA-P3 LTE,SJED0741-CA-P3 LTE | FLM_TE | SJED0740 | Results: DOWN SITE HUB SJED0740-CA-P3 SJED0740 SJED0741-CA-P3 SJED0741 Summary: Hub: SJED0740, Down Count: 1, Down Sites: SJED0740-CA-P3 Hub: SJED0741, Down Count: 1, Down Sites: SJED0741-CA-P3 Alarm Summary: SJED0740 No Active Alarm on HUB SJED0741 No Active Alarm on HUB | PCM-20251026-00000482 | SJED0740 | SJED0740 |  | sites down |  | API | 10/26/2025 07:30:47 | 10/26/2025 08:07:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000257 | PCM-20251026-00000517 | TT-20251026-00505 | EM | Region_6 | RJL1M7129 | RJL0129 |  |  |  | Zia Ur Rahamn | 10/26/2025 07:30:48 | 10/26/2025 07:35:59 | 10/26/2025 19:30:48 | RECTIFIER MAINS POWER FAILURE at RJL1M7129-G9-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 07:22:26 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 07:22:21 | P3 | 4G | mohail | Sceco | LTE NSA | RJL1M7129 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 07:30:48 | 10/26/2025 07:35:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000259 | PCM-20251026-00000522 | TT-20251026-00512 | Telecom | Region_2 | RIY2M7573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 07:41:13 | 10/26/2025 09:37:23 | 10/26/2025 13:41:13 | Cell Unavailable at RIY2M7573-P2-L800 @ Sceco | 10/26/2025 07:32:53 | Major | 29240 | Cell Unavailable | 10/26/2025 07:32:31 | P2 | 4G | muzamiah | Sceco | LTE SA | RIY2M7573 | FLM_TE | [8 empty] | API | 10/26/2025 07:41:13 | 10/26/2025 09:37:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000260 | PCM-20251026-00000525 | TT-20251026-00511 | Telecom | Region_3 | BDJD2M3369 | BDJD0369 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 07:45:29 | 10/26/2025 07:45:29 | 10/26/2025 13:45:29 | 1(3G) sites down under BDJD0369-P2/YB1MBSCH01 @ Generator_SG | 10/26/2025 07:37:28 | Major | 22214 | NodeB Unavailable | 10/26/2025 07:37:25 | P3 | 3G | yanbu | Generator_SG | 3G SA | BDJD0369-P2 | FLM_TE | BDJD0369 | Results: DOWN SITE HUB BDJD0369-P2 BDJD0369 Summary: Hub: BDJD0369, Down Count: 1, Down Sites: BDJD0369-P2 Alarm Summary: BDJD0369 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:45:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000261 | PCM-20251026-00000526 | TT-20251026-00127 | Reference_telecom | Region_6 | DAR1M7913 | DAR0913 |  |  |  | Muhammad Ali | 10/26/2025 07:46:10 | 10/26/2025 07:46:10 | 10/26/2025 13:46:10 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at DAR1M7913-NCA-L800-L1800-SBTS @ Generator_SG | 10/26/2025 01:53:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 01:53:44 | P2 | 4G | dair | Generator_SG | 5G_Cell SA | DAR1M7913 | FLM_TE |  |  | PCM-20251026-00000347 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 07:46:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000262 | PCM-20251026-00000531 | TT-20251026-00528 | Telecom | Region_5 | MAK0216 | MAK0216 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 07:48:22 | 10/26/2025 10:19:17 | 10/26/2025 19:48:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0216-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 07:47:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:47:35 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0216 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:48:22 | 10/26/2025 10:19:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000264 | PCM-20251026-00000534 | TT-20251026-00525 | Reference_telecom | Region_4 | FAT2363 | FAT2363 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 07:49:30 | 10/26/2025 09:33:56 | 10/26/2025 19:49:30 | Fronthaul loop back connectivity check failure at FAT2363-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/26/2025 07:17:22 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/26/2025 07:17:17 | P2 | 2G | taif | Sceco | 2G NSA | FAT2363 | FLM_TE |  |  | PCM-20251026-00000528 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/26/2025 07:49:30 | 10/26/2025 09:33:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000265 | PCM-20251026-00000536 | TT-20251026-00530 | Telecom | Region_3 | YBDB0291 | YBDB0291 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 07:49:55 | 10/26/2025 10:15:03 | 10/26/2025 13:49:55 | COMMUN_FAIL at YBDB0291_OCS @ Generator_DG | 10/26/2025 07:46:17 | Major | 1-199 | COMMUN_FAIL | 10/26/2025 07:46:05 | P1 | DWDM | yanbu | Generator_DG | DWDM NSA | YBDB0291 | FLM_TE | [5 empty] | 1-LOCAL-2(1-A)-73-TMF2AUX-OTHER |  |  | API | 10/26/2025 07:49:55 | 10/26/2025 10:15:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000267 | PCM-20251026-00000539 | TT-20251026-00522 | Telecom | Region_4 | JED1U6781 | JED6081 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 07:50:28 | 10/26/2025 07:50:28 | 10/26/2025 13:50:28 | BASE STATION ANTENNA LINE PROBLEM at JED1U6781-G9-L18-L21-P3-CA @ Sceco | 10/26/2025 07:37:33 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 07:37:27 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6781 | FLM_TE |  |  | PCM-20251026-00000524 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 07:50:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000268 | PCM-20251026-00000542 | TT-20251026-00524 | EM | Region_4 | JED2812 | JED2812 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 07:51:59 | 10/26/2025 07:53:01 | 10/26/2025 13:51:59 | 1(2G/LTE/5G) sites down under JED2812-P3/JED2812-P3 @ Sceco | 10/26/2025 07:43:57 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 07:43:51 | P3 | 2G | jeddah | Sceco | 2G SA | JED2812-P3 | FLM_TE | JED2812 | Results: DOWN SITE HUB JED2812-P3 JED2812 Summary: Hub: JED2812, Down Count: 1, Down Sites: JED2812-P3 Alarm Summary: JED2812 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:51:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000269 | PCM-20251026-00000547 | TT-20251026-00471 | Reference_telecom | Region_4 | SHB1M7670 | SHB0670 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 07:55:07 | 10/26/2025 07:55:07 | 10/26/2025 19:55:07 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/26/2025 04:59:30 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 04:59:18 | P3 | 4G | qunfuddah | Sceco | LTE NSA | SHB1M7670 | FLM_TE |  |  | PCM-20251026-00000532 | Thanks to check related links JDJZ0764-JDJZ0763-JDJZ0762 | Thanks to check related links JDJZ0764-JDJZ0763-JDJZ0762 |  |  |  | API | 10/26/2025 07:55:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000271 | PCM-20251026-00000549 | TT-20251026-00544 | Telecom | Region_4 | JED2965 | JED2965 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 07:58:09 | 10/26/2025 10:36:47 | 10/26/2025 13:58:09 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2965-G9-L8-L18-L21-NR2.6-FWA-P1-VIP-SBTS @ Generator_SG | 10/26/2025 07:57:33 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:57:25 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED2965 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:58:09 | 10/26/2025 10:36:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000272 | PCM-20251026-00000550 | TT-20250929-03146 | MW_HC | Region_4 | JED2072 | JED2072 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 07:58:24 | 10/26/2025 07:58:24 | 10/26/2025 19:58:24 | As BO Requested MW Nokia Observing PM errors and ACM flapping for MW link JED0783-JDJZ0761 | 09/29/2025 23:46:55 | Minor | 113388 | LOF | 09/29/2025 23:46:57 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED2072-JED0435 | FLM_TE |  |  | PCM-20251026-00000545 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/26/2025 07:58:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000273 | PCM-20251026-00000552 | TT-20250929-02161 | MW_HC | Region_4 | JED2189 | JED2189 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 07:58:48 | 10/26/2025 10:36:48 | 10/26/2025 19:58:48 | Nokia MW HC_P1 Observing Performance Issue at JED2189_01-JED0368_02 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2189_01-JED0368_02 | FLM_TE |  |  | PCM-20251026-00000544 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/26/2025 07:58:48 | 10/26/2025 10:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000274 | PCM-20251026-00000555 | TT-20251026-00539 | Telecom | Region_6 | QFL1MT0055 | QFL0055 |  |  |  | Osama Hadi | 10/26/2025 07:59:29 | 10/26/2025 07:59:29 | 10/26/2025 13:59:29 | 1(LTE) sites down under QFL0055-P3 @ Sceco | 10/26/2025 07:51:14 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 07:51:10 | P3 | 4G | jizan | Sceco | LTE SA | QFL0055-P3 | FLM_TE | QFL0055 | Results: DOWN SITE HUB QFL0055-P3 QFL0055 Summary: Hub: QFL0055, Down Count: 1, Down Sites: QFL0055-P3 Alarm Summary: QFL0055 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.74.10.212:8080] [URL:http://10.74.10.212:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 07:59:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000275 | PCM-20251026-00000558 | TT-20251026-00536 | Telecom | Region_2 | SRIY0332 | SRIY0332 | Enviroment | SCECO_Failure | SCECO auto restored | Khan zeb Shah nawaz | 10/26/2025 08:00:53 | 10/26/2025 09:57:09 | 10/26/2025 14:00:53 | 3(LTE) sites down under SRIY0332-P3_SRAN,SRIY0330-P3_SRAN,SRIY0331-P3_SRAN @ Sceco | 10/26/2025 07:50:09 | Major | 301 | NE Is Disconnected | 10/26/2025 07:50:06 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0331-P3_SRAN LTE,SRIY0332-P3_SRAN LTE,SRIY0330-P3_SRAN LTE | FLM_EM | SRIY0332 | Dear Team, Hub:- SRIY0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251026-00000551 | Dear Team, Hub:- SRIY0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- SRIY0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/26/2025 08:00:53 | 10/26/2025 09:26:46 | 10/26/2025 09:37:29 | 10/26/2025 09:37:32 | 10/26/2025 09:48:28 | 10/26/2025 09:57:09 |  | Khan zeb Shah nawaz |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000277 | PCM-20251026-00000562 | TT-20251026-00518 | Reference_telecom | Region_4 | YLM1M7752 | YLM0752 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 08:04:09 | 10/26/2025 08:04:09 | 10/26/2025 14:04:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at YLM1M7752-P1-L800-SBTS @ Generator_DG | 10/26/2025 05:43:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 05:42:51 | P1 | 4G | alaith | Generator_DG | LTE NSA | YLM1M7752 | FLM_TE |  |  | PCM-20251026-00000554 | Thanks to check related link NEC >> JDJZ0768-JDJZ0767 | Thanks to check related link NEC >> JDJZ0768-JDJZ0767 |  |  |  | API | 10/26/2025 08:04:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000278 | PCM-20251026-00000565 | TT-20251026-00549 | EM | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/26/2025 08:05:29 | 10/26/2025 08:14:01 | 10/26/2025 14:05:29 | 1(2G/5G) sites down under TURY0688-P3/TURY0688-P3 @ Sceco | 10/26/2025 07:57:12 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 07:57:08 | P3 | 2G | taif | Sceco | 2G SA | TURY0688-P3 | FLM_TE | TURY0688 | Results: DOWN SITE HUB TURY0688-P3 TURY0688 Summary: Hub: TURY0688, Down Count: 1, Down Sites: TURY0688-P3 Alarm Summary: TURY0688 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 08:05:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000279 | PCM-20251026-00000567 | TT-20251026-00502 | Reference_telecom | Region_4 | JED0415 | JED0415 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 08:05:34 | 10/26/2025 08:07:10 | 10/26/2025 20:05:34 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED0415-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 06:57:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:58:34 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0415 | FLM_TE |  |  | PCM-20251026-00000515 | Please check the GPS is locked at site and and 5G is NNN | Please check the GPS is locked at site and and 5G is NNN |  |  |  | API | 10/26/2025 08:05:34 | 10/26/2025 08:07:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000281 | PCM-20251026-00000576 | TT-20251026-00556 | EM | Region_2 | RIYA2U6155 | RIYA6055 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/26/2025 08:10:29 | 10/26/2025 08:10:29 | 10/26/2025 14:10:29 | 1(2G/LTE) sites down under RIYA6055-P3/R2_RY1_HWBSC01 @ Sceco | 10/26/2025 08:02:23 | Major | 21807 | OML Fault | 10/26/2025 08:02:17 | P3 | 2G | riyadh | Sceco | 2G_LTE SA | RIYA6055-P3 | FLM_EM | RIYA6055 | Results: DOWN SITE HUB RIYA6055-P3 RIYA6055 Summary: Hub: RIYA6055, Down Count: 1, Down Sites: RIYA6055-P3 Alarm Summary: RIYA6055 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 08:10:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000282 | PCM-20251026-00000581 | TT-20251026-00564 | Telecom | Region_6 | JIZ2087 | JIZ2087 |  |  |  | Osama Hadi | 10/26/2025 08:12:07 | 10/26/2025 08:12:07 | 10/26/2025 20:12:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ2087-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 08:11:11 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:11:01 | P3 | 2G | jizan | Sceco | 5G_Cell SA | JIZ2087 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:12:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000283 | PCM-20251026-00000584 | TT-20251026-00566 | Telecom | Region_5 | MAK1M9095 | MAK0095 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/26/2025 08:12:37 | 10/26/2025 08:12:37 | 10/26/2025 14:12:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9095-P2-L800 @ Sceco | 10/26/2025 08:11:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:11:38 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9095 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:12:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000284 | PCM-20251026-00000586 | TT-20251026-00567 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 08:13:08 | 10/26/2025 08:13:08 | 10/26/2025 14:13:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/26/2025 08:12:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:12:05 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:13:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000286 | PCM-20251026-00000594 | TT-20251026-00575 | EM | Region_6 | BSA1M8289 | BSA2289 |  |  |  | Asad Saddiq | 10/26/2025 08:17:47 | 10/26/2025 08:40:25 | 10/26/2025 20:17:47 | RECTIFIER MAINS POWER FAILURE at BSA1M8289-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 08:09:32 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 08:09:26 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BSA1M8289 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 08:17:47 | 10/26/2025 08:40:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000287 | PCM-20251026-00000597 | TT-20251026-00580 | Telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 08:19:21 | 10/26/2025 09:37:23 | 10/26/2025 20:19:21 | RF Unit Clock Problem at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 08:13:40 | Minor | 26538 | RF Unit Clock Problem | 10/26/2025 08:11:07 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_TE | [8 empty] | API | 10/26/2025 08:19:21 | 10/26/2025 09:37:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000290 | PCM-20251026-00000602 | TT-20251026-00586 | Telecom | Region_5 | MAK1M9619 | MAK0619 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 08:21:55 | 10/26/2025 08:21:55 | 10/26/2025 20:21:55 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MAK1M9619-P2-CA-L800-SBTS @ Sceco | 10/26/2025 08:13:54 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 08:13:46 | P2 | 4G | makkah | Sceco | LTE NSA | MAK1M9619 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/26/2025 08:21:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000292 | PCM-20251026-00000609 | TT-20251026-00595 | Telecom | Region_2 | RIY2M7573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 08:24:51 | 10/26/2025 09:37:24 | 10/26/2025 14:24:51 | Cell Unavailable at RIY2M7573-P2-L800 @ Sceco | 10/26/2025 08:24:37 | Major | 29240 | Cell Unavailable | 10/26/2025 08:23:04 | P2 | 4G | muzamiah | Sceco | LTE SA | RIY2M7573 | FLM_TE | [8 empty] | API | 10/26/2025 08:24:51 | 10/26/2025 09:37:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000293 | PCM-20251026-00000615 | TT-20251026-00602 | Reference_EM | Region_3 | AHT2339 | AHT2339 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 08:30:12 | 10/26/2025 08:30:12 | 10/26/2025 20:30:12 | Mains Failure at AHT2339-P3-USF_SRAN @ Sceco | 10/26/2025 08:20:13 | Minor | 65109 | Mains Failure | 10/26/2025 08:20:09 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2339 | FLM_EM | [8 empty] | API | 10/26/2025 08:30:12 | [10 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251026000295 | PCM-20251026-00000617 | TT-20251026-00604 | Reference_EM | Region_3 | MDN2042 | MDN2042 |  |  |  | Shafique Ahmad Sardar Ali | 10/26/2025 08:30:42 | 10/26/2025 09:30:14 | 10/26/2025 20:30:42 | Mains Failure at MDN2042-P2_SRAN @ Sceco | 10/26/2025 08:20:52 | Minor | 65109 | Mains Failure | 10/26/2025 08:20:48 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2042 | FLM_EM | [8 empty] | API | 10/26/2025 08:30:42 | 10/26/2025 08:48:24 | 10/26/2025 08:49:03 | 10/26/2025 08:49:05 | 10/26/2025 09:30:14 | [6 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000297 | PCM-20251026-00000621 | TT-20251021-00654 | Reference_telecom | Region_4 | JED2596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 08:31:13 | 10/26/2025 08:31:13 | 10/26/2025 20:31:13 | LossOfSignal observed in JED2596 towards 10.1.230.53 @ Sceco | 10/20/2025 18:06:57 | Minor |  | LossOfSignal | 10/20/2025 18:05:32 | P1 | 2G | jeddah | Sceco | TX NSA | JED2596 | FLM_TE |  |  | PCM-20251026-00000579 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:31:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000298 | PCM-20251026-00000622 | TT-20251022-00463 | Reference_telecom | Region_4 | JED2176 | JED2176 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 08:31:24 | 10/26/2025 08:31:24 | 10/26/2025 20:31:24 | Degrade observed in JED2176 towards 10.10.183.66 @ Sceco | 10/21/2025 16:39:16 | Minor |  | Degrade | 10/21/2025 16:39:11 | P3 | 2G | jeddah | Sceco | TX NSA | JED2176 | FLM_TE |  |  | PCM-20251026-00000585 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:31:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000299 | PCM-20251026-00000623 | TT-20251022-02019 | Reference_telecom | Region_4 | JED2992 | JED2992 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 08:31:35 | 10/26/2025 08:31:35 | 10/26/2025 20:31:35 | ReplaceableUnitProblem observed in JED2992 towards 10.10.185.28 @ Sceco | 10/22/2025 07:12:18 | Minor |  | ReplaceableUnitProblem | 10/22/2025 07:12:13 | P3 | 2G | jeddah | Sceco | TX NSA | JED2992 | FLM_TE |  |  | PCM-20251026-00000580 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:31:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000300 | PCM-20251026-00000624 | TT-20251026-00607 | Telecom | Region_6 | WDS0441 | WDS0441 |  |  |  | Ahmed Mamdouh Helal Helal | 10/26/2025 08:32:15 | 10/26/2025 08:32:15 | 10/26/2025 14:32:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at WDS0441-GSM-UMTS-P3 @ Sceco | 10/26/2025 08:31:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:31:26 | P3 | 2G | wadi dawasar | Sceco | 5G_Cell SA | WDS0441 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:32:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000301 | PCM-20251026-00000626 | TT-20251021-01390 | MW_HC | Region_4 | JED2985 | JED2985 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 08:33:02 | 10/26/2025 10:36:48 | 10/26/2025 20:33:02 | Nokia MW HC_P2 Observing Modem Down at JED2985 -JED0411 _6 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2985 -JED0411 _6 | FLM_TE |  |  | PCM-20251026-00000583 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:33:02 | 10/26/2025 10:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000302 | PCM-20251026-00000627 | TT-20251026-00600 | EM | Region_6 | BHAB0824 | BHAB0824 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 08:33:59 | 10/26/2025 08:33:59 | 10/26/2025 14:33:59 | 1(2G/3G/LTE) sites down under BHAB0824-P2-WBB-G3/BHAB0824-P2-WBB-G3 @ Sceco | 10/26/2025 08:25:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:25:52 | P2 | 2G | makhwa | Sceco | 2G_3G_LTE SA | BHAB0824-P2-WBB-G3 | FLM_EM | BHAB0824 | Results: DOWN SITE HUB BHAB0824-P2-WBB-G3 BHAB0824 Summary: Hub: BHAB0824, Down Count: 1, Down Sites: BHAB0824-P2-WBB-G3 Alarm Summary: BHAB0824 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 08:33:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000304 | PCM-20251026-00000632 | TT-20251026-00578 | Telecom | Region_6 | AQQ0841 | AQQ0841 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 08:37:47 | 10/26/2025 08:37:47 | 10/26/2025 12:37:47 | 6(2G) 4(LTE) sites down under AQQ0057-P3 @ Sceco | 10/26/2025 08:15:50 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:15:47 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | BSA2289-P3-P3 2G_LTE,AQQ2157-P3 2G_LTE,AQQ2170-P3 2G_LTE,AQQ2425-P3 2G_LTE,AQQ0057-P3 2G,AQQ0841-P3 2G | FLM_EM | AQQ0841 | BSA2289-P3-P3 2G_LTE BSA2289 Loss of signal AQQ2157-P3 2G_LTE AQQ0841 Node Rebooted AQQ0057-P3 2G AQQ0841 Node Rebooted AQQ0841-P3 2G AQQ0841 Node Rebooted | PCM-20251026-00000607 | BSA2289-P3-P3 2G_LTE BSA2289 Loss of signal AQQ2157-P3 2G_LTE AQQ0841 Node Rebooted AQQ0057-P3 2G AQQ0841 Node Rebooted AQQ0841-P3 2G AQQ0841 Node Rebooted | BSA2289-P3-P3 2G_LTE BSA2289 Loss of signal AQQ2157-P3 2G_LTE AQQ0841 Node Rebooted AQQ0057-P3 2G AQQ0841 Node Rebooted AQQ0841-P3 2G AQQ0841 Node Rebooted |  | sites down |  | API | 10/26/2025 08:37:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000308 | PCM-20251026-00000639 | TT-20251026-00622 | EM | Region_6 | AQQ1M8427 | AQQ2423 |  |  |  | Abdul Shakor Abassi | 10/26/2025 08:38:58 | 10/26/2025 08:38:58 | 10/26/2025 20:38:58 | SHELTER DOOR OPEN at AQQ1M8427-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 08:38:36 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 08:38:26 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8427 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 08:38:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000309 | PCM-20251026-00000640 | TT-20251026-00614 | EM | Region_5 | MAK1U6993 | MAK6093 |  |  |  | Muhammad Sajjad | 10/26/2025 08:39:00 | 10/26/2025 10:09:04 | 10/26/2025 12:39:00 | 1(2G/LTE) sites down under MAK6093-P1-VIP-HAJJ-HRM @ Sceco | 10/26/2025 08:30:51 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 08:30:48 | VIP | 4G | makkah | Sceco | LTE SA | MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM | FLM_TE | MAK6093 | Results: DOWN SITE HUB MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM MAK6093 Summary: Hub: MAK6093, Down Count: 1, Down Sites: MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM Alarm Summary: MAK6093 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.248.20:8080] [URL:http://10.98.248.20:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 08:39:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000310 | PCM-20251026-00000641 | TT-20251026-00579 | Telecom | Region_6 | AQQ0841 | AQQ0841 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 08:41:10 | 10/26/2025 08:41:10 | 10/26/2025 14:41:10 | 2(2G) 2(LTE) sites down under AQQ2424-P3,AQQ2426-P3/AQQ2426-P3 @ Generator_SG | 10/26/2025 08:15:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:15:47 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | AQQ2424-P3 2G_LTE,AQQ2426-P3 2G_LTE | FLM_EM | AQQ0841 | AQQ0841 Node Rebooted | PCM-20251026-00000608 | AQQ0841 Node Rebooted | AQQ0841 Node Rebooted |  | sites down |  | API | 10/26/2025 08:41:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000311 | PCM-20251026-00000644 | TT-20251026-00631 | EM | Region_3 | MDN2564 | MDN2564 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/26/2025 08:43:37 | 10/26/2025 08:43:37 | 10/26/2025 20:43:37 | NETECO: Insufficient Redundant Rectifiers at MDN2564 @ Generator_DG | 10/26/2025 08:37:14 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/26/2025 08:37:14 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDN2564 | FLM_EM | [8 empty] | API | 10/26/2025 08:43:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000312 | PCM-20251026-00000645 | TT-20251026-00592 | Telecom | Region_6 | BSA2310 | BSA2310 |  |  |  | Asad Saddiq | 10/26/2025 08:43:37 | 10/26/2025 09:35:59 | 10/26/2025 14:43:37 | 4(2G) 4(LTE) sites down under BHAB2015-P3,BSA2313-P3-CAP,BSA2316-P3-CAP,BSA2310-P3/BSA2310-P3 @ Sceco | 10/26/2025 08:20:37 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:20:33 | P3 | 2G | bisha | Sceco | 2G_LTE SA | BSA2310-P3 2G_LTE,BSA2316-P3-CAP 2G_LTE | FLM_EM | BSA2310 | BSA2310 Suspected power issue | PCM-20251026-00000612 | BSA2310 Suspected power issue | BSA2310 Suspected power issue |  | sites down |  | API | 10/26/2025 08:43:37 | 10/26/2025 09:35:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000313 | PCM-20251026-00000648 | TT-20251026-00633 | Telecom | Region_5 | MAK0216 | MAK0216 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 08:46:13 | 10/26/2025 10:19:17 | 10/26/2025 20:46:13 | BASE STATION INFORMATION (No module fan detected) at MAK0216-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 08:38:03 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 08:37:45 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0216 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/26/2025 08:46:13 | 10/26/2025 10:19:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000316 | PCM-20251026-00000655 | TT-20251026-00643 | Telecom | Region_6 | DBY0121 | DBY0121 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/26/2025 08:51:54 | 10/26/2025 08:51:54 | 10/26/2025 20:51:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at DBY0121-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 08:51:16 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:51:08 | P2 | 2G | jizan | Sceco | 5G_Cell SA | DBY0121 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:51:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000319 | PCM-20251026-00000661 | TT-20251026-00649 | Telecom | [7 empty] | 10/26/2025 08:54:39 | 10/26/2025 08:54:39 | 10/26/2025 20:54:39 | HC for RIY2822 | 10/26/2025 08:53:54 | Minor | 676767672 | Health Check-WO to TE FME | 10/26/2025 08:53:56 | VIP | SRAN |  | Generator_DG | 3G NSA | RIY2822 | FLM_TE | [8 empty] | API | 10/26/2025 08:54:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000320 | PCM-20251026-00000666 | TT-20251026-00632 | Telecom | Region_4 | MKJD0566 | MKJD0566 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 08:56:54 | 10/26/2025 09:43:25 | 10/26/2025 20:56:54 | WMKJD0001 complete down | 10/26/2025 08:29:54 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/26/2025 08:29:54 | P1 | 2G | jeddah | Sceco | Wifi SA | WMKJD0001 | FLM_TE | MKJD0566 | Dear team , HUB: MKJD0566 We observing no issue at the HUB ,kindly check locally | PCM-20251026-00000647 | Dear team , HUB: MKJD0566 We observing no issue at the HUB ,kindly check locally | Dear team , HUB: MKJD0566 We observing no issue at the HUB ,kindly check locally |  |  |  | API | 10/26/2025 08:56:54 | 10/26/2025 09:43:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000322 | PCM-20251026-00000672 | TT-20251026-00659 | Reference_EM | Region_1 | ARM2M1712 | ARM0712 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 08:59:40 | 10/26/2025 08:59:40 | 10/26/2025 20:59:40 | Door opening alarm at ARM2M1712-P3 @ Sceco | 10/26/2025 08:59:30 | Minor | 65101 | Door opening alarm | 10/26/2025 08:59:25 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1712 | FLM_EM | [8 empty] | API | 10/26/2025 08:59:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000323 | PCM-20251026-00000677 | TT-20251026-00661 | Reference_EM | Region_1 | HFF2733 | HFF2733 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/26/2025 09:02:13 | 10/26/2025 10:00:45 | 10/26/2025 21:02:13 | NETECO: AC Failure at HFF2733 @ Sceco | 10/26/2025 08:55:49 | Minor | 10202 | AC Failure | 10/26/2025 08:55:49 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2733 | FLM_EM | [8 empty] | API | 10/26/2025 09:02:13 | 10/26/2025 09:26:56 | 10/26/2025 10:00:32 |  |  | 10/26/2025 10:00:45 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000326 | PCM-20251026-00000682 | TT-20251026-00669 | Telecom | Region_4 | JED2029 | JED2029 | Equipment | FAN Cleaning | Reset FAN | Abdullah Ahmad Mohammad Abdelsheekh | 10/26/2025 09:05:19 | 10/26/2025 09:44:42 | 10/26/2025 21:05:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2029-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 09:04:36 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:04:26 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2029 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:05:19 | 10/26/2025 09:16:57 | 10/26/2025 09:19:27 | 10/26/2025 09:19:30 | 10/26/2025 09:19:33 | 10/26/2025 09:44:42 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000327 | PCM-20251026-00000683 | TT-20251026-00670 | Reference_EM | Region_1 | HFF2733 | HFF2733 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/26/2025 09:05:50 | 10/26/2025 10:00:27 | 10/26/2025 21:05:50 | Mains Failure at HFF2733-P2_SRAN @ Sceco | 10/26/2025 08:55:58 | Minor | 65109 | Mains Failure | 10/26/2025 08:55:52 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2733 | FLM_EM | [8 empty] | API | 10/26/2025 09:05:50 | 10/26/2025 09:26:57 | 10/26/2025 09:53:21 | 10/26/2025 09:53:24 | 10/26/2025 09:53:27 | 10/26/2025 10:00:27 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000330 | PCM-20251026-00000690 | TT-20251026-00666 | EM | Region_6 | ALA2196 | ALA2196 |  |  |  | Asad Saddiq | 10/26/2025 09:09:30 | 10/26/2025 09:36:00 | 10/26/2025 15:09:30 | 1(2G/LTE) sites down under ALA2196-P3/ALA2196-P3 @ Generator_SG | 10/26/2025 09:01:38 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:01:35 | P3 | 2G | bisha | Generator_SG | 2G_LTE SA | ALA2196-P3 | FLM_EM | ALA2196 | Results: DOWN SITE HUB ALA2196-P3 ALA2196 Summary: Hub: ALA2196, Down Count: 1, Down Sites: ALA2196-P3 Alarm Summary: ALA2196 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:09:30 | 10/26/2025 09:36:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000332 | PCM-20251026-00000693 | TT-20251026-00637 | EM | Region_1 | SAR0073 | SAR0073 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/26/2025 09:12:15 | 10/26/2025 09:12:15 | 10/26/2025 13:12:15 | 1(2G/LTE) sites down under SAR0073-P1-HUB-USF/SK1BSCH01 @ Generator_DG | 10/26/2025 08:47:31 | Critical | 21825 | CSL Fault | 10/26/2025 08:47:29 | P1 | SRAN | quriyat | Generator_DG | 2G_LTE SA | SAR0073-P1-HUB-USF | FLM_TE | SAR0073 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SAR0073 DIR SAR0074,Kindly visit the link and perform the HC at mentioned link . | PCM-20251026-00000667 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SAR0073 DIR SAR0074,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SAR0073 DIR SAR0074,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/26/2025 09:12:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000334 | PCM-20251026-00000697 | TT-20251026-00668 | Telecom | Region_6 | BHMF0859 | BHMF0859 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/26/2025 09:14:23 | 10/26/2025 10:23:11 | 10/26/2025 15:14:23 | 1(2G) 1(LTE) 1(5G) sites down under BHMF0859-G9-SBTS-P3,BHMF0856-P3/BHMF0856-P3 @ Sceco | 10/26/2025 09:02:00 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:01:57 | P3 | 2G | makhwa | Sceco | 2G_LTE_5G SA | BHMF0856-P3 2G_LTE,BHMF0859-G9-SBTS-P3 5G | FLM_TE | BHMF0859 | Dear team , HUB: BHMF0859 We observing Low RSL at the HUB ,kindly check locally | PCM-20251026-00000691 | Dear team , HUB: BHMF0859 We observing Low RSL at the HUB ,kindly check locally | Dear team , HUB: BHMF0859 We observing Low RSL at the HUB ,kindly check locally |  | sites down |  | API | 10/26/2025 09:14:23 | 10/26/2025 10:20:15 | 10/26/2025 10:22:52 |  |  | 10/26/2025 10:23:11 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000335 | PCM-20251026-00000698 | TT-20251026-00676 | Telecom | Region_4 | JDJZ0776-LL-CSG-01 | JDJZ0776 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:14:36 | 10/26/2025 09:14:36 | 10/26/2025 13:14:36 | The Device is offline at JDJZ0776-LL-CSG-01 @ Sceco_STB | 10/26/2025 09:14:05 | Critical | 101-7 | The Device is offline | 10/26/2025 09:14:03 | P2 | IPRAN | qunfuddah | Sceco_STB | IPRAN SA | JDJZ0776-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 09:14:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000336 | PCM-20251026-00000699 | TT-20251026-00677 | Telecom | Region_4 | JED0265 | JED0265 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 09:14:36 | 10/26/2025 10:36:48 | 10/26/2025 21:14:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0265-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 09:13:44 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:13:34 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0265 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:14:36 | 10/26/2025 10:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000337 | PCM-20251026-00000700 | TT-20251026-00571 | Reference_telecom | Region_6 | SRA1M8362 | SRA2362 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 09:14:45 | 10/26/2025 10:56:00 | 10/26/2025 21:14:45 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SRA1M8362-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 06:20:32 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:16:28 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8362 | FLM_TE |  |  | PCM-20251026-00000591 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:14:45 | 10/26/2025 10:52:39 | 10/26/2025 10:55:48 |  |  | 10/26/2025 10:56:00 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000338 | PCM-20251026-00000702 | TT-20251026-00679 | Telecom | Region_3 | HQL2041 | HQL2041 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 09:15:11 | 10/26/2025 10:15:03 | 10/26/2025 21:15:11 | GNSS Clock Output Unavailable at HQL2041-P3_SRAN @ Sceco | 10/25/2025 17:56:09 | Minor | 26124 | GNSS Clock Output Unavailable | 10/25/2025 17:54:37 | P3 | SRAN | tabouk | Sceco | 2G NSA | HQL2041 | FLM_TE | [8 empty] | API | 10/26/2025 09:15:11 | 10/26/2025 10:15:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000339 | PCM-20251026-00000703 | TT-20251026-00570 | Reference_telecom | Region_6 | QLW1M8374 | QLW2374 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 09:15:16 | 10/26/2025 10:56:39 | 10/26/2025 21:15:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8374-G9-L8-L18-SBTS-P3-P3 @ Generator_SG | 10/26/2025 06:20:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:15:39 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8374 | FLM_TE |  |  | PCM-20251026-00000590 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:15:16 | 10/26/2025 10:52:40 | 10/26/2025 10:56:29 |  |  | 10/26/2025 10:56:39 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000340 | PCM-20251026-00000705 | TT-20251026-00558 | Reference_telecom | Region_6 | QLW1M8372 | QLW2372 |  |  |  | Manzoor Ahmed | 10/26/2025 09:15:59 | 10/26/2025 10:52:40 | 10/26/2025 15:15:59 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8372-G9-L8-L18-SBTS @ Generator_SG | 10/26/2025 06:13:16 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:07:33 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8372 | FLM_TE |  |  | PCM-20251026-00000571 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:15:59 | 10/26/2025 10:52:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000341 | PCM-20251026-00000706 | TT-20251026-00557 | Reference_telecom | Region_6 | QLW1M8376 | QLW2376 |  |  |  | Manzoor Ahmed | 10/26/2025 09:16:12 | 10/26/2025 10:52:41 | 10/26/2025 15:16:12 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8376-G9-L8-L18-SBTS-CAP @ Generator_SG | 10/26/2025 06:13:23 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:07:15 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8376 | FLM_TE |  |  | PCM-20251026-00000569 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:16:12 | 10/26/2025 10:52:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000342 | PCM-20251026-00000707 | TT-20251026-00660 | Reference_telecom | Region_6 | WDS1M3441 | WDS0441 |  |  |  | Ahmed Mamdouh Helal Helal | 10/26/2025 09:16:56 | 10/26/2025 09:16:56 | 10/26/2025 15:16:56 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at WDS1M3441-P3 @ Sceco | 10/26/2025 08:33:32 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 08:31:20 | P3 | 3G | wadi dawasar | Sceco | 3G SA | WDS1M3441 | FLM_TE |  |  | PCM-20251026-00000674 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:16:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000343 | PCM-20251026-00000708 | TT-20251026-00671 | Telecom | Region_3 | HAL0928 | HAL0928 |  |  |  | Atif Shahzad Muhammad Ajaib | 10/26/2025 09:17:59 | 10/26/2025 09:17:59 | 10/26/2025 21:17:59 | Time Synchronization Failure at HAL2M3929-P2 @ Sceco | 10/26/2025 08:59:39 | Minor | 26266 | Time Synchronization Failure | 10/26/2025 08:59:05 | P2 | SRAN | hail | Sceco | 3G NSA | HAL2M3929 | FLM_TE | HAL0928 | Hub is HAL0928 We are observing ETH_LOS ,ETH_LINK_DOWN alarms flapped at hub site ,Kindly send to FLM to check cable connection at site. | PCM-20251026-00000696 | Hub is HAL0928 We are observing ETH_LOS ,ETH_LINK_DOWN alarms flapped at hub site ,Kindly send to FLM to check cable connection at site. | Hub is HAL0928 We are observing ETH_LOS ,ETH_LINK_DOWN alarms flapped at hub site ,Kindly send to FLM to check cable connection at site. |  |  |  | API | 10/26/2025 09:17:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000345 | PCM-20251026-00000710 | TT-20251026-00448 | Telecom | Region_4 | JED0063 | JED0063 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 09:19:04 | 10/26/2025 09:19:04 | 10/26/2025 15:19:04 | 3(2G) 2(5G) sites down under JED0415-P2,JED0144-P2,JED0063-P2/JED0063-P2 @ Sceco | 10/26/2025 06:45:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:45:00 | P2 | 2G | jeddah | Sceco | 2G SA | JED0063-P2 2G,JED0415-P2 2G,JED0144-P2 2G | FLM_TE | JED0063 | Results: DOWN SITE HUB JED0063-P2 JED0063 JED0415-P2 JED0415 JED0144-P2 JED0415 Summary: Hub: JED0063, Down Count: 1, Down Sites: JED0063-P2 Hub: JED0415, Down Count: 2, Down Sites: JED0415-P2, JED0144-P2 Alarm Summary: JED0063 No Active Alarm on HUB JED0415 No Active Alarm on HUB | PCM-20251026-00000695 | Please close TT with rectification RC. | Please close TT with rectification RC. |  | sites down |  | API | 10/26/2025 09:19:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000346 | PCM-20251026-00000713 | TT-20251026-00688 | Reference_telecom | Region_4 | JED2129 | JED2129 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 09:19:15 | 10/26/2025 09:19:15 | 10/26/2025 21:19:15 | InternalCommunicationProblem observed in JED2129 towards 10.1.229.217 @ Sceco | 10/25/2025 21:19:32 | Minor |  | InternalCommunicationProblem | 10/25/2025 21:19:01 | P3 | 2G | jeddah | Sceco | TX NSA | JED2129 | FLM_TE | [8 empty] | API | 10/26/2025 09:19:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000348 | PCM-20251026-00000717 | TT-20251026-00683 | EM | Region_4 | JDJZ2139 | JDJZ2139 |  |  |  | Khizer Hayat | 10/26/2025 09:21:42 | 10/26/2025 09:25:01 | 10/26/2025 15:21:42 | 1(2G/LTE) sites down under JDJZ2139-P3/JDJZ2139-P3 @ Sceco_STB | 10/26/2025 09:13:33 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:22 | P3 | 2G | jeddah | Sceco_STB | 2G SA | JDJZ2139-P3 | FLM_TE | JDJZ2139 | Results: DOWN SITE HUB JDJZ2139-P3 JDJZ2139 Summary: Hub: JDJZ2139, Down Count: 1, Down Sites: JDJZ2139-P3 Alarm Summary: JDJZ2139 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:21:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000349 | PCM-20251026-00000718 | TT-20251026-00684 | EM | Region_4 | MUMA2337 | MUMA2337 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 09:21:44 | 10/26/2025 09:29:25 | 10/26/2025 15:21:44 | 1(2G/LTE) sites down under MUMA2337-P3/MUMA2337-P3 @ Sceco | 10/26/2025 09:13:29 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:22 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | MUMA2337-P3 | FLM_EM | MUMA2337 | Results: DOWN SITE HUB MUMA2337-P3 MUMA2337 Summary: Hub: MUMA2337, Down Count: 1, Down Sites: MUMA2337-P3 Alarm Summary: MUMA2337 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:21:44 | 10/26/2025 09:29:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000350 | PCM-20251026-00000720 | TT-20251026-00693 | Reference_telecom | Region_2 | RYD0939 | RYD0939 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 09:22:21 | 10/26/2025 09:23:44 | 10/26/2025 21:22:21 | RF Unit RX Channel RTWP/RSSI Unbalanced at RYD0939-P3_SRAN @ Sceco | 10/26/2025 06:22:09 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/26/2025 06:22:06 | P3 | SRAN | rumah | Sceco | 2G NSA | RYD0939 | FLM_TE | [8 empty] | API | 10/26/2025 09:22:21 | 10/26/2025 09:23:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000351 | PCM-20251026-00000722 | TT-20251026-00582 | Telecom | Region_6 | QFL1MT0055 | QFL0055 |  |  |  | Osama Hadi | 10/26/2025 09:22:35 | 10/26/2025 09:22:35 | 10/26/2025 15:22:35 | CELL SERVICE PROBLEM (Cell disabled due to unknown problem; logs collected) at QFL1MT0055-P3 @ Sceco | 10/26/2025 08:10:25 | Major | 7114 | CELL SERVICE PROBLEM | 10/26/2025 08:14:52 | P3 | 4G | jizan | Sceco | 5G_Cell SA | QFL1MT0055 | FLM_TE |  |  | PCM-20251026-00000599 | Request to check GPS Hw, cable connectivity & relocating the GPS where sky visibility will show excellent. | Request to check GPS Hw, cable connectivity & relocating the GPS where sky visibility will show excellent. |  |  |  | API | 10/26/2025 09:22:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000353 | PCM-20251026-00000724 | TT-20251026-00698 | Telecom | Region_4 | JED0237 | JED0237 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 09:23:53 | 10/26/2025 10:36:49 | 10/26/2025 21:23:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0237-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 09:23:10 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:23:00 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0237 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:23:53 | 10/26/2025 10:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000354 | PCM-20251026-00000728 | TT-20251026-00689 | Telecom | Region_4 | MUMA1M8409 | MUMA2409 |  |  |  | Khizer Hayat | 10/26/2025 09:24:33 | 10/26/2025 09:24:33 | 10/26/2025 15:24:33 | 1(LTE) sites down under MUMA2409-G9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 09:16:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:16:09 | P3 | 4G | jeddah | Sceco | LTE SA | MUMA2409-G9-L8-L18-SBTS-P3 | FLM_TE | MUMA2409 | Results: DOWN SITE HUB MUMA2409-G9-L8-L18-SBTS-P3 MUMA2409 Summary: Hub: MUMA2409, Down Count: 1, Down Sites: MUMA2409-G9-L8-L18-SBTS-P3 Alarm Summary: MUMA2409 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.169.93.54:8080] [URL:http://10.169.93.54:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:24:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000355 | PCM-20251026-00000729 | TT-20251026-00702 | Reference_telecom | Region_6 | ARF0072 | ARF0072 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 09:24:37 | 10/26/2025 10:36:07 | 10/26/2025 21:24:37 | AS BO Requested MW HC For Link ARF0072-ARF0191 | 10/26/2025 09:23:53 | Minor | 113388 | LOF | 10/26/2025 09:23:53 | P3 | 2G | khamis mushyet | Sceco | TX NSA | ARF0072-ARF0191 | FLM_TE | [5 empty] | AS BO Requested MW HC For Link ARF0072-ARF0191 |  |  | API | 10/26/2025 09:24:37 | 10/26/2025 10:36:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000356 | PCM-20251026-00000731 | TT-20251026-00681 | Telecom | Region_4 | JDJZ0776 | JDJZ0776 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 09:26:13 | 10/26/2025 10:34:43 | 10/26/2025 11:26:13 | 34(2G) 14(3G) 20(LTE) 18(5G) sites down under JDJZ2181-P3 @ Generator_SG | 10/26/2025 09:13:28 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:21 | P1 | 2G | qunfuddah | Sceco_STB | 2G_3G_LTE_5G SA | SQUN0105-P3 LTE,JDJZ0775-P2 2G_3G_5G,QUN0338-P2-WBB-G3 2G_3G_LTE,SQUN0020 LTE,JDJZ0774-P1-VIP 2G_3G_5G,QUN0341-P1-VIP-WBB-G3 2G_3G_5G,BHMF2143-P3 2G_LTE,MUMA0772-P3 2G_3G_LTE,BHMF0858-P3 2G_5G,JDJZ2097-P3 2G_LTE,SQUN0008-P3 LTE,MUMA0781-P3-WBB-G3 2G_5G,MUMA2204-P3-CAP 2G_LTE,JDJZ2156-P3 2G_5G,FRS0085-P2-WBB-G3 2G_3G_LTE,QUN0334-P2 2G_3G_5G,QUN0337-P1-VIP 2G_3G,QUN0336-P2-WBB-G3 2G_3G,JDJZ0776-P1-HUB-FON-WBB-G3 2G_3G,QUN0335-P2 2G_3G,MUMA0774-P3-WBB-G3 2G_3G,FRS0086-P2-WBB-G3 2G_3G,MUMA0773-P3 2G_3G,JDJZ2181-P3 2G,BHMF2137-P3 2G,JDJZ2071-P3 2G,FRS2199-P3 2G,JDJZ2000-P3 2G,FRS2410-P3 2G,FRS2420-P3 2G,BHMF0857-P3-WBB-G3 2G,FRS2155-P3 2G,MUMA2198-P3-CAP 2G,NWN0477-P2 2G,MUMA2070-P3-P3 2G,BHMF2373-P3 2G,FRS2020-P3-CAP 2G | FLM_TE | JDJZ0776 | Dear team , HUB: JDJZ0776 We observing Visibility down at the HUB ,kindly check locally as HUB is P2 Router | PCM-20251026-00000715 | Dear team , HUB: JDJZ0776 We observing Visibility down at the HUB ,kindly check locally as HUB is P2 Router | Dear team , HUB: JDJZ0776 We observing Visibility down at the HUB ,kindly check locally as HUB is P2 Router |  | sites down |  | API | 10/26/2025 09:26:13 | 10/26/2025 09:54:24 | 10/26/2025 10:01:20 | 10/26/2025 10:01:23 | 10/26/2025 10:01:25 | 10/26/2025 10:34:43 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000357 | PCM-20251026-00000733 | TT-20251026-00682 | Telecom | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/26/2025 09:27:35 | 10/26/2025 09:27:35 | 10/26/2025 15:27:35 | 2(2G) 1(LTE) sites down under JED6020-GSM-P3,HBI2412-P3/HBI2412-P3 @ Generator_DG | 10/26/2025 09:13:33 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:22 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | HBI2412-P3 2G_LTE,JED6020-GSM-P3 2G | FLM_EM | JED6020 | DOWN SITE HUB TX FB JED6020 JED6020 Node Rebooted HBI2412 JDJZ0776 Check with IP Ran as HUB is P2 router | PCM-20251026-00000716 | DOWN SITE HUB TX FB JED6020 JED6020 Node Rebooted HBI2412 JDJZ0776 Check with IP Ran as HUB is P2 router | DOWN SITE HUB TX FB JED6020 JED6020 Node Rebooted HBI2412 JDJZ0776 Check with IP Ran as HUB is P2 router |  | sites down |  | API | 10/26/2025 09:27:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000358 | PCM-20251026-00000735 | TT-20251026-00699 | Telecom | Region_4 | SQUN1S7104 | SQUN0104 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:28:59 | 10/26/2025 09:28:59 | 10/26/2025 13:28:59 | 1(LTE) sites down under SQUN0104-P1-VIP @ Sceco | 10/26/2025 09:20:42 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:20:39 | VIP | 4G | qunfuddah | Sceco | LTE SA | SQUN0104-P1-VIP | FLM_TE | SQUN0104 | Results: DOWN SITE HUB SQUN0104-P1-VIP SQUN0104 Summary: Hub: SQUN0104, Down Count: 1, Down Sites: SQUN0104-P1-VIP Alarm Summary: SQUN0104 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.0.188:8080] [URL:http://10.98.0.188:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:28:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000359 | PCM-20251026-00000736 | TT-20251026-00707 | Telecom | Region_6 | RJL1M7129 | RJL0129 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/26/2025 09:29:03 | 10/26/2025 09:29:03 | 10/26/2025 21:29:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at RJL1M7129-G9-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 09:28:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:27:56 | P3 | 4G | mohail | Sceco | 5G_Cell SA | RJL1M7129 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:29:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000363 | PCM-20251026-00000745 | TT-20251025-00872 | Reference_telecom | Region_4 | JED2561 | JED2561 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 09:34:13 | 10/26/2025 09:53:47 | 10/26/2025 21:34:13 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2561-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/25/2025 09:57:46 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 09:54:41 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2561 | FLM_TE |  |  | PCM-20251025-00000798 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/26/2025 09:34:13 | 10/26/2025 09:53:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000365 | PCM-20251026-00000751 | TT-20251026-00710 | Telecom | Region_4 | SQUN1S7106 | SQUN0106 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/26/2025 09:35:29 | 10/26/2025 09:35:29 | 10/26/2025 15:35:29 | 1(LTE) sites down under SQUN0106-P3 @ Sceco | 10/26/2025 09:27:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:27:09 | P3 | 4G | qunfuddah | Sceco | LTE SA | SQUN0106-P3 | FLM_TE | SQUN0106 | Results: DOWN SITE HUB SQUN0106-P3 SQUN0106 Summary: Hub: SQUN0106, Down Count: 1, Down Sites: SQUN0106-P3 Alarm Summary: SQUN0106 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.0.252:8080] [URL:http://10.98.0.252:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:35:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000367 | PCM-20251026-00000752 | TT-20251026-00719 | Reference_EM | Region_3 | AHT2172 | AHT2172 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 09:35:46 | 10/26/2025 09:35:46 | 10/26/2025 21:35:46 | Mains Failure at AHT2172-P3_SRAN @ Sceco | 10/26/2025 09:25:41 | Minor | 65109 | Mains Failure | 10/26/2025 09:25:36 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2172 | FLM_EM | [8 empty] | API | 10/26/2025 09:35:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000369 | PCM-20251026-00000754 | TT-20251026-00721 | Telecom | Region_3 | MDN0188 | MDN0188 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 09:36:17 | 10/26/2025 09:36:17 | 10/26/2025 21:36:17 | BBU DC Output Out of Range at MDN0188-P2_SRAN @ Sceco | 10/26/2025 09:33:26 | Minor | 26112 | BBU DC Output Out of Range | 10/26/2025 09:31:52 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0188 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000370 | PCM-20251026-00000758 | TT-20251026-00725 | Reference_telecom | Region_4 | JED2601 | JED2601 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 09:36:48 | 10/26/2025 09:36:48 | 10/26/2025 21:36:48 | LagPortDown observed in JED2601 towards 10.3.232.164 @ Sceco | 10/25/2025 21:36:40 | Minor |  | LagPortDown | 10/25/2025 21:36:29 | P3 | 2G | jeddah | Sceco | TX NSA | JED2601 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000371 | PCM-20251026-00000757 | TT-20251026-00724 | Reference_telecom | Region_4 | JED2602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 09:36:48 | 10/26/2025 09:36:48 | 10/26/2025 21:36:48 | LossOfSignal observed in JED2602_02 towards 10.3.232.163 @ Sceco | 10/25/2025 21:36:40 | Minor |  | LossOfSignal | 10/25/2025 21:36:28 | P3 | 2G | jeddah | Sceco | TX NSA | JED2602 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000372 | PCM-20251026-00000756 | TT-20251026-00723 | Telecom | Region_3 | MDN0188 | MDN0188 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 09:36:49 | 10/26/2025 09:36:49 | 10/26/2025 21:36:49 | RF Unit Maintenance Link Failure at MDN0188-P2_SRAN @ Sceco | 10/26/2025 09:33:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 09:31:18 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0188 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000373 | PCM-20251026-00000759 | TT-20251026-00727 | Telecom | Region_4 | JED1MN2910 | JED2910 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 09:37:50 | 10/26/2025 10:36:49 | 10/26/2025 15:37:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/26/2025 09:36:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:36:43 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:37:50 | 10/26/2025 10:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000375 | PCM-20251026-00000763 | TT-20251026-00715 | Telecom | Region_4 | JED2234 | JED2234 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 09:40:18 | 10/26/2025 09:43:25 | 10/26/2025 15:40:18 | LOCAL BLOCK at JED2234-P3 @ Sceco | 10/26/2025 09:30:03 | Major | 7208 | LOCAL BLOCK | 10/26/2025 09:29:50 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2234 | FLM_TE |  |  | PCM-20251026-00000746 | HW alarm active on LTE, kindly check | HW alarm active on LTE, kindly check |  |  |  | API | 10/26/2025 09:40:18 | 10/26/2025 09:43:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000377 | PCM-20251026-00000769 | TT-20251026-00730 | Telecom | Region_4 | JED1M7685 | JED0685 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 09:44:38 | 10/26/2025 09:44:38 | 10/26/2025 15:44:38 | BASE STATION ANTENNA LINE PROBLEM at JED1M7685-CA-L900-L800-SBTS @ Sceco_STB | 10/26/2025 09:31:27 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 09:31:24 | P3 | 4G | jeddah | Sceco_STB | LTE NSA | JED1M7685 | FLM_TE |  |  | PCM-20251026-00000761 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/26/2025 09:44:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000378 | PCM-20251026-00000770 | TT-20251026-00735 | Telecom | Region_4 | JED6028 | JED6028 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 09:46:07 | 10/26/2025 09:46:07 | 10/26/2025 15:46:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6028-GSM-P3 @ Sceco | 10/26/2025 09:45:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:45:13 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED6028 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:46:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000379 | PCM-20251026-00000771 | TT-20251026-00736 | EM | Region_3 | RUSF9024 | RUSF9024 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/26/2025 09:46:37 | 10/26/2025 09:46:37 | 10/26/2025 13:46:37 | RELAY_ALARM_MAJOR at RUSF9024_NE_1 @ Generator_DG | 10/26/2025 09:44:51 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/26/2025 09:44:41 | P3 | Repeater | madinah | Generator_DG | TX NSA | RUSF9024 | FLM_EM | [8 empty] | API | 10/26/2025 09:46:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000380 | PCM-20251026-00000772 | TT-20251025-00489 | Reference_telecom | Region_5 | MAK0760 | MAK0760 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 09:46:58 | 10/26/2025 09:46:58 | 10/26/2025 21:46:58 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MAK0760-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-NEW @ Sceco | 10/25/2025 05:53:02 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 05:52:55 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0760 | FLM_TE |  |  | PCM-20251025-00000424 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/26/2025 09:46:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000381 | PCM-20251026-00000774 | TT-20251025-00459 | Reference_telecom | Region_4 | JED1MN0202 | JED0202 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 09:47:45 | 10/26/2025 09:47:45 | 10/26/2025 15:47:45 | BASE STATION CONNECTIVITY PROBLEM (NR GTP-U Path Failure) at JED1MN0202-NR2.6-P2 @ Sceco | 10/25/2025 07:30:59 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 07:30:51 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0202 | FLM_TE |  |  | PCM-20251025-00000400 | Kindly check and support to restore as site is down | Kindly check and support to restore as site is down |  |  |  | API | 10/26/2025 09:47:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000382 | PCM-20251026-00000779 | TT-20251025-00107 | Reference_telecom | Region_4 | GMK1M7175 | GMK0175 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 09:48:24 | 10/26/2025 09:48:24 | 10/26/2025 21:48:24 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at GMK1M7175-G9-NL8-L18-SBTS-P2-USF @ Sceco | 10/25/2025 00:03:16 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 00:03:13 | P2 | 4G | qunfuddah | Sceco | LTE NSA | GMK1M7175 | FLM_TE |  |  | PCM-20251025-00000101 | Kindly check high VSWR alarm is active | Kindly check high VSWR alarm is active |  |  |  | API | 10/26/2025 09:48:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000383 | PCM-20251026-00000780 | TT-20251026-00700 | Reference_telecom | Region_4 | JDJZ0778-LL-CSG-01 | JDJZ0778 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:49:15 | 10/26/2025 09:49:15 | 10/26/2025 21:49:15 | MW Link Down at JDJZ0778-LL-CSG-01 To HLA0423 REF:TT-20251026-00504 @ Sceco_STB | 10/26/2025 07:29:36 | Minor | 101-2505274 | Physical Port Down | 10/26/2025 07:28:51 | P1 | IPRAN | qunfuddah | Sceco_STB | IPRAN SA | JDJZ0778-LL-CSG-01 | FLM_TE |  |  | PCM-20251026-00000726 | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . |  |  |  | API | 10/26/2025 09:49:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000384 | PCM-20251026-00000781 | TT-20251026-00742 | MW_HC | Region_4 | JDJZ0776 | JDJZ0776 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:49:45 | 10/26/2025 09:49:45 | 10/26/2025 21:49:45 | AS BO Requested MW HC For Link JDJZ9048-JDJZ0776 , Counting PM errors | 10/26/2025 09:49:22 | Minor | 113388 | LOF | 10/26/2025 09:49:22 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ9048-JDJZ0776 | FLM_TE | [5 empty] | AS BO Requested MW HC For Link JDJZ9048-JDJZ0776 , Counting PM errors |  |  | API | 10/26/2025 09:49:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000385 | PCM-20251026-00000787 | TT-20251026-00738 | Telecom | Region_6 | STLT1S7707 | STLT0707 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/26/2025 09:52:59 | 10/26/2025 10:47:41 | 10/26/2025 15:52:59 | 1(LTE) sites down under STLT0707-P3 @ Sceco | 10/26/2025 09:44:44 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:44:40 | P3 | 4G | tathleeth | Sceco | LTE SA | STLT0707-P3 | FLM_TE | STLT0707 | Results: DOWN SITE HUB STLT0707-P3 STLT0707 Summary: Hub: STLT0707, Down Count: 1, Down Sites: STLT0707-P3 Alarm Summary: STLT0707 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.89.119.148:8080] [URL:http://10.89.119.148:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:52:59 | 10/26/2025 10:47:25 | 10/26/2025 10:47:34 |  |  | 10/26/2025 10:47:41 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000386 | PCM-20251026-00000788 | TT-20251026-00720 | Telecom | Region_4 | JED0017 | JED0017 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 09:53:45 | 10/26/2025 09:53:45 | 10/26/2025 15:53:45 | 2(LTE) sites down under JED2234-L800-CA-P3,JED0017-CA-L900-L800-SBTS-P3 @ Sceco | 10/26/2025 09:32:43 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:32:39 | P1 | 2G | jeddah | Sceco | LTE SA | JED2234-L800-CA-P3 LTE,JED0017-CA-L900-L800-SBTS-P3 LTE | FLM_TE | JED0017 | DOWN SITE HUB TX FB JED2234 JED2234 Observing no issue at HUB , kindly check locally JED0017 JED0017 Link flapping at HUB | PCM-20251026-00000765 | DOWN SITE HUB TX FB JED2234 JED2234 Observing no issue at HUB , kindly check locally JED0017 JED0017 Link flapping at HUB | DOWN SITE HUB TX FB JED2234 JED2234 Observing no issue at HUB , kindly check locally JED0017 JED0017 Link flapping at HUB |  | sites down |  | API | 10/26/2025 09:53:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000387 | PCM-20251026-00000789 | TT-20251026-00741 | Telecom | Region_2 | SRIY0183 | SRIY0183 |  |  |  | Waseem Shahzad Ghulam Rasool | 10/26/2025 09:53:59 | 10/26/2025 10:47:11 | 10/26/2025 13:53:59 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/26/2025 09:45:44 | Critical | 301 | NE Is Disconnected | 10/26/2025 09:45:42 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:53:59 | 10/26/2025 10:47:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000388 | PCM-20251026-00000791 | TT-20251026-00753 | EM | [7 empty] | 10/26/2025 09:54:54 | 10/26/2025 09:54:54 | 10/26/2025 13:54:54 | AIR CONDITION 1&2 at RPTRA-SEC0008_OCS @ Sceco | 10/26/2025 09:53:28 | Critical | 1-12307 | AIR CONDITION 1&2 | 10/26/2025 09:53:20 | P1 | DWDM |  | Sceco | DWDM NSA | RPTRA | FLM_EM | [5 empty] | 0-TO 8065-SEC0003&MJM0495(1-A)-71-E1EFI-[AIR CONDITION 1&2]:4 |  |  | API | 10/26/2025 09:54:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000393 | PCM-20251026-00000797 | TT-20251026-00761 | Reference_EM | Region_2 | QSRY0741 | QSRY0741 |  |  |  | Moin Uddin | 10/26/2025 10:01:06 | 10/26/2025 10:01:06 | 10/26/2025 22:01:06 | Fire Fighting system alarm at QSRY0741-P2_SRAN @ Sceco | 10/26/2025 09:50:56 | Minor | 65111 | Fire Fighting system alarm | 10/26/2025 09:50:54 | P2 | SRAN | muzamiah | Sceco | 2G NSA | QSRY0741 | FLM_EM | [8 empty] | API | 10/26/2025 10:01:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000399 | PCM-20251026-00000809 | TT-20251026-00766 | Reference_EM | Region_1 | ARM2M1712 | ARM0712 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 10:07:17 | 10/26/2025 10:07:17 | 10/26/2025 22:07:17 | DC Power Fail at ARM2M1712-P3 @ Sceco | 10/26/2025 09:56:58 | Minor | 65106 | DC Power Fail | 10/26/2025 09:56:55 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1712 | FLM_EM | [8 empty] | API | 10/26/2025 10:07:17 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000403 | PCM-20251026-00000820 | TT-20251026-00775 | Telecom | Region_4 | JED1MN2666 | JED2666 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 10:10:55 | 10/26/2025 10:24:21 | 10/26/2025 16:10:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2666-NR2.6-P3 @ Sceco | 10/26/2025 10:09:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:09:47 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2666 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:10:55 | 10/26/2025 10:24:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000406 | PCM-20251026-00000822 | TT-20251026-00777 | Telecom | Region_2 | RIY2M8278 | RIY2278 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Farmanullah Akbar Jan | 10/26/2025 10:12:20 | 10/26/2025 11:01:51 | 10/26/2025 16:12:20 | Cell Unavailable at RIY2M8278-P3-CA-L800 @ Sceco | 10/26/2025 10:10:03 | Major | 29240 | Cell Unavailable | 10/26/2025 10:08:30 | P3 | 4G | riyadh | Sceco | LTE SA | RIY2M8278 | FLM_TE | [8 empty] | API | 10/26/2025 10:12:20 | 10/26/2025 10:22:56 | 10/26/2025 11:01:25 | 10/26/2025 11:01:27 | 10/26/2025 11:01:30 | 10/26/2025 11:01:51 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000407 | PCM-20251026-00000825 | TT-20251026-00756 | Telecom | Region_4 | KHY2251 | KHY2251 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/26/2025 10:12:29 | 10/26/2025 10:12:29 | 10/26/2025 16:12:29 | 2(2G) 1(LTE) sites down under JED0296-P2-USF,KHY2251-P3/KHY2251-P3 @ Generator_SG | 10/26/2025 09:55:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:55:25 | P3 | 2G | jeddah | Generator_SG | 2G SA | JED0296-P2-USF 2G,KHY2251-P3 2G | FLM_EM | KHY2251 | JED0296 Visibility down KHY2251 Suspected power issue | PCM-20251026-00000804 | JED0296 Visibility down KHY2251 Suspected power issue | JED0296 Visibility down KHY2251 Suspected power issue |  | sites down |  | API | 10/26/2025 10:12:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Departed | CM20251026000409 | PCM-20251026-00000829 | TT-20251026-00772 | Telecom | Region_5 | MAK0378 | MAK0378 |  |  |  | IJAZ ALI | 10/26/2025 10:13:59 | 10/26/2025 10:37:14 | 10/26/2025 14:13:59 | 1(2G) sites down under MAK0378-P1-HRM/MAK0378-P1-HRM @ Sceco | 10/26/2025 10:05:53 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:05:49 | P1 | 2G | makkah | Sceco | 2G SA | MAK0378-P1-HRM | FLM_TE | MAK0378 | Results: DOWN SITE HUB MAK0378-P1-HRM MAK0378 Summary: Hub: MAK0378, Down Count: 1, Down Sites: MAK0378-P1-HRM Alarm Summary: MAK0378 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 10:13:59 | 10/26/2025 10:35:18 | 10/26/2025 10:37:11 | 10/26/2025 10:37:14 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000410 | PCM-20251026-00000836 | TT-20251026-00787 | Telecom | Region_2 | RIY2278 | RIY2278 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Farmanullah Akbar Jan | 10/26/2025 10:15:33 | 10/26/2025 11:01:17 | 10/26/2025 16:15:33 | BBU CPRI Interface Error at RIY2278-P3_SRAN-PC @ Sceco | 10/26/2025 10:10:56 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 10:08:23 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2278 | FLM_TE | [8 empty] | API | 10/26/2025 10:15:33 | 10/26/2025 10:22:56 | 10/26/2025 11:00:40 | 10/26/2025 11:00:47 | 10/26/2025 11:00:50 | 10/26/2025 11:01:17 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000411 | PCM-20251026-00000839 | TT-20251026-00791 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 10:17:07 | 10/26/2025 10:17:07 | 10/26/2025 22:17:07 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/26/2025 10:09:00 | Minor | 7103 | HIGH TEMP | 10/26/2025 10:08:52 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/26/2025 10:17:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000414 | PCM-20251026-00000843 | TT-20251026-00645 | Telecom | Region_2 | RIY2605-CSG-01 | RIY2605 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 10:20:06 | 10/26/2025 10:20:06 | 10/26/2025 14:20:06 | The Device is offline at RIY2605-CSG-01 @ Sceco | 10/26/2025 08:52:59 | Critical | 101-7 | The Device is offline | 10/26/2025 08:52:57 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIY2605-CSG-01 | FLM_TE |  |  | PCM-20251026-00000741 | Please re-check the power again , if no power issue please check the below ports and arrange with DMDM FL and DWDM BO IPRAN side : RIY2605-CSG-01 >>> GigabitEthernet0-3-0 RYQS0573-ZRi01-4-CSG-02 >>> GigabitEthernet0-9-0 | Please re-check the power again , if no power issue please check the below ports and arrange with DMDM FL and DWDM BO IPRAN side : RIY2605-CSG-01 >>> GigabitEthernet0-3-0 RYQS0573-ZRi01-4-CSG-02 >>> GigabitEthernet0-9-0 |  |  |  | API | 10/26/2025 10:20:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000415 | PCM-20251026-00000844 | TT-20251026-00795 | EM | [7 empty] | 10/26/2025 10:20:13 | 10/26/2025 10:20:13 | 10/26/2025 22:20:13 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 10:11:50 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/26/2025 10:11:39 | P3 | 4G |  | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | API | 10/26/2025 10:20:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000418 | PCM-20251026-00000852 | TT-20251026-00794 | Telecom | Region_6 | QIS0102 | QIS0102 |  |  |  | Khurram Nawaz Muhammad Akram | 10/26/2025 10:25:08 | 10/26/2025 10:52:45 | 10/26/2025 16:25:08 | 2(2G) 2(3G) 2(LTE) sites down under WJZ0066-P3,QIS0102-P2/QIS0102-P2 @ Sceco | 10/26/2025 10:15:42 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:15:38 | P2 | 2G | jizan | Sceco | 2G_3G_LTE SA | WJZ0066-P3 2G_3G_LTE,QIS0102-P2 2G_3G_LTE | FLM_EM | QIS0102 | DOWN SITE HUB TX FB WJZ0066 WJZ0066 Suspected Power issue at HUB QIS0102 QIS0102 Suspected Power issue at HUB | PCM-20251026-00000850 | DOWN SITE HUB TX FB WJZ0066 WJZ0066 Suspected Power issue at HUB QIS0102 QIS0102 Suspected Power issue at HUB | DOWN SITE HUB TX FB WJZ0066 WJZ0066 Suspected Power issue at HUB QIS0102 QIS0102 Suspected Power issue at HUB |  | sites down |  | API | 10/26/2025 10:25:08 | 10/26/2025 10:52:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000419 | PCM-20251026-00000853 | TT-20251022-01456 | Reference_telecom | Region_6 | TNMS0711 | TNMS0711 |  |  |  | Fawad Khan | 10/26/2025 10:25:23 | 10/26/2025 10:31:20 | 10/26/2025 22:25:23 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/22/2025 13:53:58 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:53:49 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251026-00000817 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:23 | 10/26/2025 10:31:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000420 | PCM-20251026-00000854 | TT-20251024-00668 | Reference_telecom | Region_6 | TNMS0711 | TNMS0711 |  |  |  | Fawad Khan | 10/26/2025 10:25:29 | 10/26/2025 10:31:21 | 10/26/2025 22:25:29 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/24/2025 10:39:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 10:38:53 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251026-00000814 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:29 | 10/26/2025 10:31:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000421 | PCM-20251026-00000855 | TT-20251025-00883 | Reference_telecom | Region_6 | TNMS0711 | TNMS0711 |  |  |  | Fawad Khan | 10/26/2025 10:25:39 | 10/26/2025 10:31:21 | 10/26/2025 22:25:39 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/25/2025 11:53:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:53:39 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251026-00000811 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:39 | 10/26/2025 10:31:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000422 | PCM-20251026-00000856 | TT-20251026-00287 | Telecom | Region_6 | SDA0507 | SDA0507 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 10:25:48 | 10/26/2025 10:25:48 | 10/26/2025 22:25:48 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at SDA0507-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Generator_SG | 10/26/2025 04:15:41 | Minor | 7114 | CELL SERVICE PROBLEM | 10/26/2025 04:15:34 | P3 | 2G | abha | Generator_SG | 5G_Cell SA | SDA0507 | FLM_TE |  |  | PCM-20251026-00000312 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000423 | PCM-20251026-00000857 | TT-20251026-00141 | Reference_telecom | Region_4 | JED1U6052 | JED6152 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 10:25:55 | 10/26/2025 10:25:55 | 10/26/2025 16:25:55 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/26/2025 02:00:23 | Major | 7654 | CELL OPERATION DEGRADED | 10/26/2025 02:00:10 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251026-00000181 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000424 | PCM-20251026-00000858 | TT-20251025-00218 | Reference_telecom | Region_5 | MAK1U6909 | MAK6009 |  |  |  | Mosab Nasr eldeen Mohamed | 10/26/2025 10:26:02 | 10/26/2025 10:26:02 | 10/26/2025 16:26:02 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at MAK1U6909-CA-P1-HRM-SBTS @ Sceco | 10/25/2025 03:33:35 | Major | 7654 | CELL OPERATION DEGRADED | 10/25/2025 03:33:26 | P1 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6909 | FLM_TE |  |  | PCM-20251025-00000197 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:26:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000425 | PCM-20251026-00000859 | TT-20251024-01373 | Reference_telecom | Region_5 | MAK1U6907 | MAK6007 |  |  |  | Mosab Nasr eldeen Mohamed | 10/26/2025 10:26:08 | 10/26/2025 10:26:08 | 10/26/2025 22:26:08 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at MAK1U6907-CA-SBTS-P3 @ Sceco | 10/24/2025 21:14:31 | Minor | 7654 | CELL OPERATION DEGRADED | 10/24/2025 21:14:21 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6907 | FLM_TE |  |  | PCM-20251024-00001250 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:26:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000426 | PCM-20251026-00000860 | TT-20251026-00801 | Telecom | Region_6 | BLJ0046-LL-CSG-01 | BLJ0046 |  |  |  | Manzoor Ahmed | 10/26/2025 10:26:56 | 10/26/2025 10:52:42 | 10/26/2025 22:26:56 | Bad Package Error Rising at BLJ0046-LL-CSG-01 @ Sceco | 10/26/2025 10:26:30 | Minor | 101-2501403 | Bad Package Error Rising | 10/26/2025 10:26:23 | P2 | IPRAN | Albaha | Sceco | IPRAN NSA | BLJ0046-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 10:26:56 | 10/26/2025 10:52:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000427 | PCM-20251026-00000861 | TT-20251026-00120 | EM | Region_5 | MAK6185 | MAK6085 |  |  |  | IJAZ ALI | 10/26/2025 10:27:48 | 10/26/2025 10:29:21 | 10/26/2025 16:27:48 | TRX FAULTY (00 00 00 83 11 00) at MAK6185-P1-HRM @ Sceco | 10/26/2025 01:47:35 | Major | 7606 | TRX FAULTY | 10/26/2025 01:47:31 | P1 | 2G | makkah | Sceco | 2G_Cell SA | MAK6185 | FLM_TE |  |  | PCM-20251026-00000381 | No Power Issue | No Power Issue |  |  |  | API | 10/26/2025 10:27:48 | 10/26/2025 10:29:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000428 | PCM-20251026-00000863 | TT-20251026-00807 | Reference_EM | Region_1 | ARM0886 | ARM0886 |  |  |  | Dileesh Muringothil Devarajan | 10/26/2025 10:29:29 | 10/26/2025 10:40:27 | 10/26/2025 16:29:29 | Mains Failure at ARM0886-P1-VIP_SRAN @ Sceco | 10/26/2025 10:19:31 | Major | 65109 | Mains Failure | 10/26/2025 10:19:27 | VIP | SRAN | khafji | Sceco | 2G NSA | ARM0886 | FLM_EM | [8 empty] | API | 10/26/2025 10:29:29 | 10/26/2025 10:40:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000429 | PCM-20251026-00000866 | TT-20251026-00810 | Telecom | Region_2 | RIY2M7399 | RIY0399 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 10:30:42 | 10/26/2025 11:00:33 | 10/26/2025 16:30:42 | Cell Unavailable at RIY2M7399-P2-L900-L800 @ Sceco | 10/26/2025 10:29:18 | Major | 29240 | Cell Unavailable | 10/26/2025 10:27:46 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7399 | FLM_TE | [8 empty] | API | 10/26/2025 10:30:42 | 10/26/2025 11:00:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000430 | PCM-20251026-00000867 | TT-20251026-00813 | Reference_EM | Region_3 | RSP0036 | RSP0036 |  |  |  | Sayed Satoor | 10/26/2025 10:32:04 | 10/26/2025 10:32:04 | 10/26/2025 16:32:04 | high temprature 40 at RSP0036-P1-VIP_SRAN @ Generator_SG | 10/26/2025 10:21:46 | Major | 65103 | high temprature 40 | 10/26/2025 10:21:40 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0036 | FLM_EM | [8 empty] | API | 10/26/2025 10:32:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000431 | PCM-20251026-00000869 | TT-20251026-00785 | Telecom | Region_4 | YLM1M7391 | YLM0391 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 10:33:03 | 10/26/2025 10:33:03 | 10/26/2025 14:33:03 | PLR threshold crossed on TWAMP-1 at 131 sites under R4 | 10/26/2025 10:07:24 | Critical | 61611 | TWAMP PLR Threshold Crossed | 10/26/2025 10:07:24 | P1 | 4G | alaith | Generator_SG | 2G_3G_LTE_5G SA | YLM1M7391-L800-P1-SBTS YLM1M7876-L800-SBTS-P1 MKYL1M7912-G9-U9-NL8-SBTS-P2 NNL1M7137-G9-NL8-L18-SBTS-P3 GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 HAM1M7025-G9-U9-NL8-SBTS-P2-USF NSH1M7168-G9-U9-NL8-SBTS-P3 GMK1M7175-G9-NL8-L18-SBTS-P2-USF YLM1M8369-L800-P1-SBTS GMK1M7349-L800-CA-P3-USF SIR1M7050-G9-U9-NL8-SBTS-P2-USF NNL1M7084-G9-NL8-L18-SBTS-P2-USF LTH2121-G9-L8-L18-L21-NR2.6-SBTS-P3 LTH1M8122-CA-L800-SBTS HLA1M8095-G9-L8-L18-L21-SBTS-P3 HLA1M7424-P2-CA-L800-SBTS JED1M7839-CA-L900-P1-VIP HLA1M7422-P3-CA-L800-SBTS-WBB-G3 HLA1M7425-P3-L800 LTH2201-G9-L8-L18-L21-NNR2.6-SBTS-P3 NNL1M7139-G9-U9-NL8-SBTS-P3 SDY1M7163-G9-U9-NL8-SBTS-P3 LTH0329-G9-L8-L18-L21-NR2.6-SBTS-P2 SQSH1M7150-G9-NL8-L18-SBTS-P2-USF YLM1M7789-L800-P3 SQSH1M7022-USF-P3 NNL1M7164-G9-U9-NL8-SBTS-P3 LTH0638-G9-L8-L18-L21-NR2.6-SBTS-P2 UKHA1M7733-G9-U9-NL8-P1-HUB-USF JDMD1M7861-L800-SBTS-P2 MKMD1M7556-L800-P2 JDMD1M7863-G9-L8-SBTS-P1-HUB-USF MKMD1M7555-L800-P2 FRJ1M7043-G9-U9-NL8-NL18-SBTS-P2-USF GMQ1M7153-G9-U9-NL8-SBTS-P2-USF MLJI1M7095-G9-U9-NL8-SBTS-P2-USF SHB1M7611-CA SDY1M7738-G9-U9-NL8-SBTS-P1 DKA1M7347-G9-L8-L18-SBTS-P3 BIK1M7153-L800-CA-P3 GMK1M7167-L800-SBTS-P3 MKMD1M8252-P3-L800 JED2928-G9-L18-NNR2.6-SBTS-P3 JZMA1M8202-G9-L8-SBTS-P3 NSH1M7218-USF-P3 SIR1M7125-USF-P3 HAM1M7357-USF-L800-L2100-P3 JDJZ0771-G9-L8-L18-L21-NNR2.6-SBTS-P1-HUB-USF GMQ1M7038-G9-U9-NL8-NL18-SBTS-P2-USF BIK1M7154-G9-U9-NL8-NL18-SBTS-P2 HJR1M7149-USF-P3 UKZ1M7067-USF-P3-L800 JDJZ1M7769-G9-U9-NL8-NL18-NL21-SBTS-P1-USF SDY1M7766-L800-SBTS-P3 JDJZ0774-G9-L8-L18-L21-NNR2.6-SBTS-P1-VIP NNL1M7104-G9-L8-SBTS-P3 NSH1M7128-G9-NL8-L18-SBTS-P2-USF JDJZ1M7776-P1-CA-L800 FRS2020-G9-L8-L18-L21-SBTS-P3 JDJZ2156-G9-L8-L18-SBTS-P3 MKYL1M7908-P2 MUMA1M8204-G9-L8-L18-L21-SBTS-P3-CAP MUMA0781-G9-L8-L18-SBTS-P3 JDJZ1M7777-G9-L8-L18-L21-SBTS-P2-HUB-WBB-G3 SIR1M7155-G9-U9-NL8-SBTS-P2-USF YLM1M7740-USF-P3 HBI1M7353-G9-L8-L18-SBTS-P3 MKSH1M7170-G9-U9-NL8-SBTS-P2-USF JZMA1M7822-G9-L8-NL18-SBTS-P2-WBB-G3 JZMA1M7824-G9-L8-SBTS-P3 JDJZ1M8418-G9-L8-L18-SBTS-CAP UKZ1M7166-USF-P3 THA1M7736-P3-CA-L800-WBB-G3 JZMA1M8415-G9-L8-L18-SBTS-P3 MLJI1M7374-G9-U9-NL8-SBTS-P2-USF HBI1M8412-G9-L8-L18-SBTS-P3 NSH1M7165-G9-L9-L18-SBTS-P3 NWN1M7477-G9-NL8-L18-L21-SBTS-P2 QAL1M7721-G9-L18-SBTS-P2-USF QUZ1M7738-P3-CA-L800 QUZ1M8417-G9-L8-L18-L21-SBTS NNL1M7102-USF-P3 UKHA1M7731-G9-L18-SBTS-P1-HUB-USF MUMA1M7772-G9-L8-SBTS-P3 BHMF1M7857-G9-L8-L18-SBTS-P3 NSH1M7127-USF-P3 JZMA1M8101-G9-L8-L18-SBTS-P3-CAP UKHA1M7630-CA-L800-USF-P3 QHN1M7737-P3-CA-L800 QUN1M7336-CA-L800-P3 HLA1M8439-G9-L8-L18-L21-SBTS DGB1M8169-USF-P3 FRS2155-G9-L8-L18-L21-SBTS-P3 QUZ0739-L800-L1800-CA-NR2.6-FWA-P1-VIP JZMA1M8414-G9-L8-L18-L21-SBTS-P3-CAP HBI1M8008-G9-L8-L18-L21-SBTS-P3 BHMF1M8137-G9-L8-L18-SBTS-P3 BHMF1M8143-G9-L8-L18-SBTS-P3 QUN0341-G9-L8-L18-L21-SBTS-P1-VIP JDJZ2000-G9-L8-L18-SBTS-P3 GMK1M7442-G-U9-NL8-NL18-SBTS-P2-USF SHB1M7671-P3 JDJZ1M7778-G9-L8-L18-SBTS-P1-HUB-FON QUN1M7334-CA-L800-P3 UKHA1M7028-G9-L18-SBTS-P1-HUB ASQ1M7342-P1-HUB-USF YLM1M7752-P1-L800-SBTS HLA1M7423-P1-HUB-CA-L800 UKHA1M7344-G9-NL8-NL18-SBTS-P1-HUB BHMF1M8373-G9-L8-SBTS-P3 JZMA1M7825-G9-U9-NL8-NL18-NL21-SBTS-P2-WBB-G3 BHMF0858-L800-SBTS-P3 HLA1MT0423-P1 NNL1M7158-G9-U9-L18-SBTS-P3 FRS1M7086-G9-L8-L18-L21-SBTS-P2-WBB-G3 QUN0337-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP QUN1M7335-P2-CA-L800 JDJZ1M8097-G9-L8-L18-L21-SBTS-P3 FRS1M7085-G9-L8-SBTS-P2 GMK1M7350-G9-U9-NL8-SBTS-P2-USF MLJI1M7103-G9-U9-NL8-SBTS-P2-USF QUN1M7338-CA-L800-P3 MUMA1M8070-G9-L8-L18-L21-SBTS-P3 MUMA1M8198-G9-L8-L18-L21-SBTS-P3-CAP NNL1M7101-G9-U9-NL8-SBTS-P3 LTH0330-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB GMK1M7046-G9-NL8-L18-SBTS-P2-USF FRS2410-G9-L8-L18-L21-SBTS-P3 FRS2420-G9-L8-L18-SBTS-P3 JDJZ1M8181-G9-L8-L18-SBTS-P3 KUL1M7006-USF-P3 | FLM_TE |  |  | PCM-20251026-00000833 | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . |  |  |  | API | 10/26/2025 10:33:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000432 | PCM-20251026-00000870 | TT-20251026-00816 | Telecom | Region_6 | DRB0902 | DRB0902 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 10:33:07 | 10/26/2025 11:04:27 | 10/26/2025 16:33:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at DRB0902-GSM-UMTS-P3 @ Sceco | 10/26/2025 10:32:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:32:18 | P3 | 2G | derb | Sceco | 5G_Cell SA | DRB0902 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:33:07 | 10/26/2025 11:04:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000433 | PCM-20251026-00000877 | TT-20251026-00826 | Telecom | Region_6 | JDJZ1M7885 | JDJZ0885 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 10:42:55 | 10/26/2025 11:04:27 | 10/26/2025 22:42:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JDJZ1M7885-G9-U9-L18-SBTS-P2-HUB @ Sceco_STB | 10/26/2025 10:42:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:42:07 | P1 | 4G | derb | Sceco_STB | 5G_Cell SA | JDJZ1M7885 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:42:55 | 10/26/2025 11:04:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000434 | PCM-20251026-00000879 | TT-20251026-00831 | Reference_EM | Region_1 | HFB2M5001 | HFB0001 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/26/2025 10:44:59 | 10/26/2025 10:44:59 | 10/26/2025 16:44:59 | Mains Failure at HFB2M5001-P1-DIA @ Generator_SG | 10/26/2025 10:35:05 | Major | 65109 | Mains Failure | 10/26/2025 10:35:02 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5001 | FLM_EM | [8 empty] | API | 10/26/2025 10:44:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000435 | PCM-20251026-00000882 | TT-20251026-00835 | Reference_EM | Region_2 | RIYD6037 | RIYD6037 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 10:46:33 | 10/26/2025 10:46:33 | 10/26/2025 16:46:33 | high temprature 32 at RIYD6037-P1-VIP_SRAN @ Sceco | 10/26/2025 10:25:30 | Major | 65102 | high temprature 32 | 10/26/2025 10:46:22 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_EM | [8 empty] | API | 10/26/2025 10:46:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000436 | PCM-20251026-00000884 | TT-20251026-00836 | EM | Region_6 | BSA1M8289 | BSA2289 |  |  |  | Asad Saddiq | 10/26/2025 10:47:03 | 10/26/2025 10:47:03 | 10/26/2025 22:47:03 | SHELTER DOOR OPEN;Default System Time at BSA1M8289-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 10:46:56 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/26/2025 03:01:03 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BSA1M8289 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 10:47:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000437 | PCM-20251026-00000886 | TT-20251026-00838 | EM | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Gamal Mohamed Farag | 10/26/2025 10:47:04 | 10/26/2025 10:47:04 | 10/26/2025 22:47:04 | HIGH TEMPERATURE 32 DEGREE C at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/26/2025 10:39:06 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/26/2025 10:38:56 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7558 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/26/2025 10:47:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000438 | PCM-20251026-00000888 | TT-20251026-00843 | Telecom | Region_6 | ARF1MN0066 | ARF0066 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 10:48:36 | 10/26/2025 10:48:36 | 10/26/2025 16:48:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at ARF1MN0066-NR2.6-P3 @ Sceco_STB | 10/26/2025 10:47:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:47:34 | P3 | 5G | al harja | Sceco_STB | 5G_Cell SA | ARF1MN0066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:48:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000440 | PCM-20251026-00000891 | TT-20251026-00848 | EM | Region_4 | TF1_CORE | TF1 |  |  |  | Farghal Ashour Hassan Farghal | 10/26/2025 10:49:07 | 10/26/2025 10:49:07 | 10/26/2025 16:49:07 | DOOR OPEN ALARM at TF1_CORE-P1-VIP @ Sceco_STB | 10/26/2025 10:48:35 | Major | 7103 | DOOR OPEN ALARM | 10/26/2025 10:48:31 | P1 | BSC | taif | Sceco_STB | 2G NSA | TF1_CORE | FLM_EM | [5 empty] | DOOR OPEN ALARM |  |  | API | 10/26/2025 10:49:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000441 | PCM-20251026-00000892 | TT-20251026-00851 | EM | Region_6 | KHS0333 | KHS0333 |  |  |  | Amir Abbas Arif Raza | 10/26/2025 10:50:40 | 10/26/2025 10:50:40 | 10/26/2025 22:50:40 | SHELTER DOOR OPEN;Default System Time at KHS0333-GSM-UMTS-P2-USF @ Sceco | 10/26/2025 10:50:07 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/26/2025 03:01:17 | P2 | 2G | khamis mushyet | Sceco | 2G NSA | KHS0333 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 10:50:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000442 | PCM-20251026-00000897 | TT-20251026-00842 | EM | Region_6 | KHS0333 | KHS0333 |  |  |  | Amir Abbas Arif Raza | 10/26/2025 10:53:29 | 10/26/2025 10:53:29 | 10/26/2025 16:53:29 | 1(2G/3G/5G) sites down under KHS0333-P2-USF/KHS0333-P2-USF @ Sceco | 10/26/2025 10:45:28 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:45:25 | P2 | 2G | khamis mushyet | Sceco | 2G_3G_5G SA | KHS0333-P2-USF | FLM_EM | KHS0333 | Results: DOWN SITE HUB KHS0333-P2-USF KHS0333 Summary: Hub: KHS0333, Down Count: 1, Down Sites: KHS0333-P2-USF Alarm Summary: KHS0333 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 10:53:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000444 | PCM-20251026-00000898 | TT-20251026-00859 | Telecom | Region_2 | RAS2248 | RAS2248 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/26/2025 10:53:46 | 10/26/2025 10:53:46 | 10/26/2025 22:53:46 | ALD Maintenance Link Failure at RAS2248-FWA-P1-VIP_SRAN @ Sceco | 10/26/2025 10:51:18 | Minor | 26541 | ALD Maintenance Link Failure | 10/26/2025 10:49:43 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS2248 | FLM_TE | [8 empty] | API | 10/26/2025 10:53:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000446 | PCM-20251026-00000900 | TT-20251026-00861 | Telecom | Region_5 | HAJ1W0342 | HAJ1W0342 |  |  |  | Muhammad Saleem Iqbal | 10/26/2025 10:54:44 | 10/26/2025 10:54:44 | 10/26/2025 22:54:44 | HAJ1W0342 Partial down | 10/26/2025 10:47:54 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/26/2025 10:47:54 | P3 | WIFI | makkah | Sceco | Wifi SA | HAJ1W0342-AP01 | FLM_TE | [8 empty] | API | 10/26/2025 10:54:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000447 | PCM-20251026-00000903 | TT-20251026-00867 | Telecom | Region_6 | BSA1M8289 | BSA2289 |  |  |  | Hamid Ullah Muhammad Alam Khan | 10/26/2025 10:57:54 | 10/26/2025 10:57:54 | 10/26/2025 22:57:54 | BASE STATION INFORMATION (No module fan detected) at BSA1M8289-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 10:49:31 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 10:49:27 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BSA1M8289 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/26/2025 10:57:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000449 | PCM-20251026-00000906 | TT-20251026-00857 | Telecom | Region_4 | SMLJI1S7905 | SMLJI0905 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 10:58:01 | 10/26/2025 10:58:01 | 10/26/2025 16:58:01 | 1(LTE) sites down under SMLJI0905-USF-P3 @ Sceco | 10/26/2025 10:49:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 10:49:54 | P3 | 4G | alaith | Sceco | LTE SA | SMLJI0905-USF-P3 | FLM_TE | SMLJI0905 | Results: DOWN SITE HUB SMLJI0905-USF-P3 SMLJI0905 Summary: Hub: SMLJI0905, Down Count: 1, Down Sites: SMLJI0905-USF-P3 Alarm Summary: SMLJI0905 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.103.124:8080] [URL:http://10.88.103.124:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 10:58:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000452 | PCM-20251026-00000914 | TT-20251026-00864 | Telecom | Region_2 | RIY2343 | RIY2343 |  |  |  | Asad Ali Nadiq Khan | 10/26/2025 11:02:30 | 10/26/2025 11:02:30 | 10/26/2025 15:02:30 | 1(5G) sites down under RIY2343-P1_SRAN @ Sceco | 10/26/2025 10:55:49 | Critical | 29840 | gNodeB Out of Service | 10/26/2025 10:54:15 | P1 | SRAN | riyadh | Sceco | 5G SA | RIY2343-P1_SRAN | FLM_TE | RIY2343 | Results: DOWN SITE HUB RIY2343-P1_SRAN RIY2343 Summary: Hub: RIY2343, Down Count: 1, Down Sites: RIY2343-P1_SRAN Alarm Summary: RIY2343 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 11:02:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000453 | PCM-20251026-00000916 | TT-20251019-02090 | MW_HC | Region_4 | TFBH9446 | TFBH9446 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 11:03:20 | 10/26/2025 11:03:20 | 10/26/2025 23:03:20 | NEC MW HC_P0 Observing Modem Down at TFBH9446(10.88.221.34)--TFBH9451(10.88.221.41) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9446(10.88.221.34)--TFBH9451(10.88.221.41) | FLM_TE | TFBH9446 | Kindly share RCA , HC Time , clearance time | PCM-20251026-00000908 | Kindly share RCA , HC Time , clearance time | Kindly share RCA , HC Time , clearance time |  |  |  | API | 10/26/2025 11:03:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000809 | PCM-20251025-00001776 | TT-20251025-01838 | Reference_EM | Region_2 | RIY0185 | RIY0185 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Ajmal Hafeez Hafeez Ahmed Awan | 10/25/2025 22:09:01 | 10/25/2025 23:49:16 | 10/26/2025 10:09:01 | Door opening alarm at RIY0185-P2_SRAN @ Sceco | 10/25/2025 22:08:31 | Minor | 65101 | Door opening alarm | 10/25/2025 22:08:27 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0185 | FLM_EM | [8 empty] | API | 10/25/2025 22:09:01 | 10/25/2025 22:18:38 | 10/25/2025 23:14:46 | 10/25/2025 23:14:50 | 10/25/2025 23:14:57 | 10/25/2025 23:49:16 |  | Ajmal Hafeez Hafeez Ahmed Awan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000810 | PCM-20251025-00001782 | TT-20251025-01846 | Reference_EM | Region_2 | QSDH2711 | QSDH2711 | Equipment | FAN Cleaning | Clean FAN | Moustafa Elzaafarany Abdellah | 10/25/2025 22:15:46 | 10/25/2025 22:55:48 | 10/26/2025 10:15:46 | Door opening alarm at QSDH2711-P2_SRAN @ Generator_SG | 10/25/2025 22:15:23 | Minor | 65101 | Door opening alarm | 10/25/2025 22:15:20 | P2 | SRAN | dawadmi | Generator_SG | 2G NSA | QSDH2711 | FLM_EM | [8 empty] | API | 10/25/2025 22:15:46 | 10/25/2025 22:34:33 | 10/25/2025 22:34:50 | 10/25/2025 22:34:52 | 10/25/2025 22:34:54 | 10/25/2025 22:55:48 |  | Moustafa Elzaafarany Abdellah |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000813 | PCM-20251025-00001789 | TT-20251025-01857 | Reference_EM | Region_2 | RIY2923 | RIY2923 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/25/2025 22:25:36 | 10/26/2025 00:11:29 | 10/26/2025 10:25:36 | Generator failure at RIY2923-P2_SRAN @ Generator_SG | 10/25/2025 22:15:07 | Minor | 65114 | Generator failure | 10/25/2025 22:15:04 | P3 | SRAN | al kharj | Generator_SG | 2G NSA | RIY2923 | FLM_EM | [8 empty] | API | 10/25/2025 22:25:36 | 10/26/2025 00:11:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000815 | PCM-20251025-00001792 | TT-20251025-01860 | Reference_EM | Region_1 | KBR0200 | KBR0200 | Enviroment | Fire Alarm | Reset Fire Pannel | Abdul Malik Shaik | 10/25/2025 22:31:16 | 10/25/2025 23:49:22 | 10/26/2025 10:31:16 | Fire Fighting system alarm at KBR0200-P3_SRAN @ Sceco | 10/25/2025 22:20:58 | Minor | 65111 | Fire Fighting system alarm | 10/25/2025 22:20:53 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0200 | FLM_EM | [8 empty] | API | 10/25/2025 22:31:16 | 10/25/2025 22:36:07 | 10/25/2025 23:09:52 | 10/25/2025 23:09:55 | 10/25/2025 23:34:06 | 10/25/2025 23:49:22 |  | Abdul Malik Shaik |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000832 | PCM-20251025-00001840 | TT-20251025-01895 | EM | Region_2 | BRK9101 | BRK9101 |  |  |  | ABUZAR Ahmed Humida Mustafa | 10/25/2025 23:14:42 | 10/25/2025 23:14:42 | 10/26/2025 03:14:42 | RELAY_ALARM_CRITICAL at BRK9101_NE_1 @ Power Cube | 10/25/2025 23:13:42 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/25/2025 23:13:30 | P1 | Repeater | aflaj | Power Cube | TX NSA | BRK9101 | FLM_EM | [8 empty] | API | 10/25/2025 23:14:42 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000006 | PCM-20251026-00000010 | TT-20251026-00011 | Reference_EM | Region_2 | UNZ0158 | UNZ0158 | Enviroment | Air Condition | Change Fan | Shahid Ahmed Shah Nawaz | 10/26/2025 00:12:31 | 10/26/2025 01:26:40 | 10/26/2025 12:12:31 | Air condition 2 failure alarm at UNZ0158-P2_SRAN @ Sceco | 10/26/2025 00:01:55 | Minor | 65105 | Air condition 2 failure alarm | 10/26/2025 00:01:52 | P2 | SRAN | buraidah | Sceco | 2G NSA | UNZ0158 | FLM_EM | [8 empty] | API | 10/26/2025 00:12:31 | 10/26/2025 00:15:25 | 10/26/2025 00:34:23 | 10/26/2025 00:34:25 | 10/26/2025 01:01:33 | 10/26/2025 01:26:40 |  | Shahid Ahmed Shah Nawaz |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000011 | PCM-20251026-00000018 | TT-20251026-00012 | Telecom | Region_2 | RIY0707 | RIY0707 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/26/2025 00:17:51 | 10/26/2025 00:17:51 | 10/26/2025 12:17:51 | RF Unit Maintenance Link Failure at RIY0707-P1-VIP-DIA_SRAN @ Sceco | 10/26/2025 00:10:34 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 00:08:51 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0707 | FLM_EM |  |  | PCM-20251026-00000013 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 00:17:51 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000012 | PCM-20251026-00000020 | TT-20251026-00020 | Reference_EM | Region_1 | ARM0993 | ARM0993 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 00:18:40 | 10/26/2025 02:32:30 | 10/26/2025 12:18:40 | Generator failure at ARM0993-P2_SRAN-PC @ Power Cube | 10/26/2025 00:08:15 | Minor | 65114 | Generator failure | 10/26/2025 00:08:12 | P2 | SRAN | hafouf | Power Cube | 2G NSA | ARM0993 | FLM_EM | [8 empty] | API | 10/26/2025 00:18:40 | 10/26/2025 02:32:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000018 | PCM-20251026-00000030 | TT-20251026-00024 | Reference_EM | Region_1 | JBL0471 | JBL0471 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 00:21:45 | 10/26/2025 00:28:23 | 10/26/2025 06:21:45 | Mains Failure at JBL0471-P1-DIA_SRAN @ Sceco | 10/26/2025 00:11:49 | Major | 65109 | Mains Failure | 10/26/2025 00:11:45 | P1 | SRAN | jubail | Sceco | 2G NSA | JBL0471 | FLM_EM | [8 empty] | API | 10/26/2025 00:21:45 | 10/26/2025 00:28:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000022 | PCM-20251026-00000055 | TT-20251026-00042 | Reference_EM | Region_2 | HIL2471 | HIL2471 |  |  |  | Farman Ullah Muhammad Nazir | 10/26/2025 00:34:11 | 10/26/2025 00:34:11 | 10/26/2025 12:34:11 | Door opening alarm at HIL2471-P2_SRAN @ Sceco | 10/26/2025 00:33:46 | Minor | 65101 | Door opening alarm | 10/26/2025 00:33:41 | P2 | SRAN | al rass | Sceco | 2G NSA | HIL2471 | FLM_EM | [8 empty] | API | 10/26/2025 00:34:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000023 | PCM-20251026-00000057 | TT-20251026-00043 | EM | Region_1 | URY9013 | URY9013 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/26/2025 00:34:46 | 10/26/2025 10:24:37 | 10/26/2025 12:34:46 | NETECO: Speed Sensor Failure at URY9013 @ Power Cube | 10/26/2025 00:27:59 | Minor | 8143 | Speed Sensor Failure | 10/26/2025 00:27:59 | P3 | Repeater | jubail | Power Cube | 2G NSA | URY9013 | FLM_EM | [8 empty] | API | 10/26/2025 00:34:46 | 10/26/2025 10:24:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000028 | PCM-20251026-00000071 | TT-20251026-00054 | Reference_EM | Region_1 | ARM0881 | ARM0881 |  |  |  | Nazar Mohammed Siddig Abdalla | 10/26/2025 00:45:35 | 10/26/2025 00:45:35 | 10/26/2025 12:45:35 | Generator failure at ARM0881-P3_SRAN-PC @ Power Cube | 10/26/2025 00:35:05 | Minor | 65114 | Generator failure | 10/26/2025 00:35:01 | P3 | SRAN | hafouf | Power Cube | 2G NSA | ARM0881 | FLM_EM | [8 empty] | API | 10/26/2025 00:45:35 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000031 | PCM-20251026-00000075 | TT-20251026-00057 | Reference_EM | Region_1 | KBR0200 | KBR0200 |  |  |  | Abdul Malik Shaik | 10/26/2025 00:51:45 | 10/26/2025 00:51:45 | 10/26/2025 12:51:45 | Door opening alarm at KBR0200-P3_SRAN @ Sceco | 10/26/2025 00:51:23 | Minor | 65101 | Door opening alarm | 10/26/2025 00:51:19 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0200 | FLM_EM | [8 empty] | API | 10/26/2025 00:51:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000032 | PCM-20251026-00000076 | TT-20251026-00060 | Reference_EM | Region_2 | RIY0430 | RIY0430 |  |  |  | Amr Abbas Zaghloul Abbas | 10/26/2025 00:54:21 | 10/26/2025 00:54:21 | 10/26/2025 06:54:21 | Door opening alarm at RIY0430-P1-HUB_SRAN-FON @ Sceco | 10/26/2025 00:53:34 | Major | 65101 | Door opening alarm | 10/26/2025 00:53:31 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0430 | FLM_EM | [8 empty] | API | 10/26/2025 00:54:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000054 | PCM-20251026-00000111 | TT-20251026-00084 | Reference_EM | Region_2 | RAS0044 | RAS0044 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Shazlly Mahmoud Abouzied Mahmoud | 10/26/2025 01:17:05 | 10/26/2025 03:02:09 | 10/26/2025 13:17:05 | Minor Rec alarm at RAS0044-P2_SRAN @ Sceco | 10/26/2025 01:06:42 | Minor | 65108 | Minor Rec alarm | 10/26/2025 01:06:40 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS0044 | FLM_EM | [8 empty] | API | 10/26/2025 01:17:05 | 10/26/2025 01:53:24 | 10/26/2025 01:54:13 | 10/26/2025 01:54:16 | 10/26/2025 02:19:30 | 10/26/2025 03:02:09 |  | Shazlly Mahmoud Abouzied Mahmoud |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000055 | PCM-20251026-00000115 | TT-20251026-00086 | Reference_EM | Region_1 | YBR0669 | YBR0669 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 01:20:18 | 10/26/2025 02:32:31 | 10/26/2025 13:20:18 | DC power fail at YBR0669-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 01:09:40 | Minor | 65106 | DC power fail | 10/26/2025 01:09:36 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0669 | FLM_EM | [8 empty] | API | 10/26/2025 01:20:18 | 10/26/2025 02:32:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000069 | PCM-20251026-00000152 | TT-20251026-00113 | Reference_EM | Region_1 | YBR0603 | YBR0603 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 01:50:06 | 10/26/2025 02:32:32 | 10/26/2025 13:50:06 | DC power fail at YBR0603-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 01:39:36 | Minor | 65106 | DC power fail | 10/26/2025 01:39:32 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0603 | FLM_EM | [8 empty] | API | 10/26/2025 01:50:06 | 10/26/2025 02:32:32 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000080 | PCM-20251026-00000168 | TT-20251026-00129 | EM | Region_1 | KBR0163 | KBR0163 | Enviroment | Air Condition | Change Fan | Yasser Mohamed Abdelnabi Ibrahim | 10/26/2025 02:03:30 | 10/26/2025 04:33:52 | 10/26/2025 06:03:30 | high temprature 40 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 01:59:10 | Critical | 65103 | high temprature 40 | 10/26/2025 01:59:07 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/26/2025 02:03:30 | 10/26/2025 04:28:06 | 10/26/2025 04:33:34 |  |  | 10/26/2025 04:33:52 |  | Yasser Mohamed Abdelnabi Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251026000111 | PCM-20251026-00000222 | TT-20251026-00187 | Reference_EM | Region_1 | YBR0725 | YBR0725 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 02:47:26 | 10/26/2025 02:47:26 | 10/26/2025 14:47:26 | Door opening alarm at YBR0725-P2-USF_SRAN-PC @ Power Cube | 10/26/2025 02:46:52 | Minor | 65101 | Door opening alarm | 10/26/2025 02:46:48 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0725 | FLM_EM | [8 empty] | API | 10/26/2025 02:47:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000117 | PCM-20251026-00000238 | TT-20251026-00209 | Reference_EM | Region_1 | JBKH2338 | JBKH2338 |  |  |  | Dileesh Muringothil Devarajan | 10/26/2025 03:10:46 | 10/26/2025 10:40:27 | 10/26/2025 09:10:46 | Mains Failure at JBKH2338-P1-VIP_ARP_SRAN @ Sceco | 10/26/2025 03:00:44 | Major | 65109 | Mains Failure | 10/26/2025 03:00:40 | VIP | SRAN | khafji | Sceco | 2G NSA | JBKH2338 | FLM_EM | [8 empty] | API | 10/26/2025 03:10:46 | 10/26/2025 10:40:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000171 | PCM-20251026-00000349 | TT-20251026-00328 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/26/2025 04:57:36 | 10/26/2025 09:15:49 | 10/26/2025 16:57:36 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/26/2025 04:51:09 | Minor | 40564 | Genset Fault | 10/26/2025 04:51:09 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/26/2025 04:57:36 | 10/26/2025 09:14:30 | 10/26/2025 09:15:38 |  |  | 10/26/2025 09:15:49 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251026000180 | PCM-20251026-00000367 | TT-20251026-00342 | Reference_EM | Region_2 | RIY2131 | RIY2131 | Enviroment | Air Condition | Change Fan | Ajmal Hafeez Hafeez Ahmed Awan | 10/26/2025 05:15:41 | 10/26/2025 05:51:10 | 10/26/2025 17:15:41 | high temprature 40 at RIY2131-P2_SRAN @ Sceco | 10/26/2025 05:05:02 | Minor | 65103 | high temprature 40 | 10/26/2025 05:04:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2131 | FLM_EM | [8 empty] | API | 10/26/2025 05:15:41 | 10/26/2025 05:37:16 | 10/26/2025 05:37:52 | 10/26/2025 05:37:56 | 10/26/2025 05:38:00 | 10/26/2025 05:51:10 |  | Ajmal Hafeez Hafeez Ahmed Awan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000192 | PCM-20251026-00000397 | TT-20251026-00372 | Reference_EM | Region_1 | TRF2507 | TRF2507 |  |  |  | Ragab Farg Abdel Nabi Bekhatro | 10/26/2025 05:42:01 | 10/26/2025 06:20:05 | 10/26/2025 17:42:01 | Low battery voltage at TRF2507-P2-USF_SRAN @ Generator_SG | 10/26/2025 05:31:24 | Minor | 65110 | Low battery voltage | 10/26/2025 05:31:22 | P2 | SRAN | arar | Generator_SG | 2G NSA | TRF2507 | FLM_EM | [8 empty] | API | 10/26/2025 05:42:01 | 10/26/2025 06:20:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000196 | PCM-20251026-00000406 | TT-20251026-00379 | Reference_EM | Region_2 | RIY2704 | RIY2704 | Enviroment | Genset failure_AVR | Change Generator AVR | Mahmoud Hefny Ali Ahmed | 10/26/2025 05:52:56 | 10/26/2025 08:26:25 | 10/26/2025 11:52:56 | Air condition 2 failure alarm at RIY2704-P1-VIP_SRAN @ Sceco | 10/26/2025 05:42:25 | Major | 65105 | Air condition 2 failure alarm | 10/26/2025 05:42:22 | VIP | SRAN | muzamiah | Sceco | 2G NSA | RIY2704 | FLM_EM | [8 empty] | API | 10/26/2025 05:52:56 | 10/26/2025 07:50:20 | 10/26/2025 07:51:16 | 10/26/2025 07:51:20 | 10/26/2025 08:00:34 | 10/26/2025 08:26:25 |  | Mahmoud Hefny Ali Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000203 | PCM-20251026-00000414 | TT-20251026-00388 | Reference_EM | Region_2 | RIY0748 | RIY0748 |  |  |  | Moin Uddin | 10/26/2025 06:00:41 | 10/26/2025 06:00:41 | 10/26/2025 18:00:41 | Minor Rec alarm at RIY0748-P2_SRAN @ Sceco | 10/26/2025 05:50:25 | Minor | 65108 | Minor Rec alarm | 10/26/2025 05:50:21 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0748 | FLM_EM | [8 empty] | API | 10/26/2025 06:00:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000209 | PCM-20251026-00000415 | TT-20251026-00389 | Reference_EM | Region_2 | RIY0573 | RIY0573 |  |  |  | Moin Uddin | 10/26/2025 06:01:10 | 10/26/2025 06:01:10 | 10/26/2025 18:01:10 | Mains Failure at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 05:00:43 | Minor | 65109 | Mains Failure | 10/26/2025 04:59:54 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_EM | [8 empty] | API | 10/26/2025 06:01:10 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000215 | PCM-20251026-00000435 | TT-20251026-00391 | Reference_telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Moin Uddin | 10/26/2025 06:10:01 | 10/26/2025 06:10:01 | 10/26/2025 18:10:01 | RF Unit RX Channel RTWP/RSSI Too Low at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 05:43:14 | Minor | 26521 | RF Unit RX Channel RTWP/RSSI Too Low | 10/26/2025 05:43:10 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_EM |  |  | PCM-20251026-00000417 | power alarms reported | power alarms reported |  |  |  | API | 10/26/2025 06:10:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000216 | PCM-20251026-00000437 | TT-20251026-00394 | Telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Moin Uddin | 10/26/2025 06:10:21 | 10/26/2025 06:10:21 | 10/26/2025 12:10:21 | BBU CPRI Interface Error at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 05:02:59 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 05:31:29 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_EM |  |  | PCM-20251026-00000420 | power alarms reported | power alarms reported |  |  |  | API | 10/26/2025 06:10:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000222 | PCM-20251026-00000450 | TT-20251026-00403 | Telecom | Region_1 | TRF2507 | TRF2507 | Enviroment | Genset failure_Starting Battery | Change Generator battery | Ragab Farg Abdel Nabi Bekhatro | 10/26/2025 06:19:56 | 10/26/2025 08:09:22 | 10/26/2025 12:19:56 | 2(2G) 2(3G) 2(LTE) sites down under TRF2506-P3-USF,TRF2507-P2-USF/AR1BSCH01 @ Generator_SG | 10/26/2025 06:07:33 | Major | 21825 | CSL Fault | 10/26/2025 06:07:32 | P2 | SRAN | arar | Generator_SG | 2G_3G_LTE SA | TRF2507-P2-USF 2G_3G_LTE,TRF2506-P3-USF 2G_3G_LTE | FLM_EM |  | Dear Team, Hub:- TRF2507 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251026-00000443 | Dear Team, Hub:- TRF2507 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- TRF2507 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/26/2025 06:19:56 | 10/26/2025 06:20:06 | 10/26/2025 07:42:54 | 10/26/2025 07:42:59 | 10/26/2025 07:43:03 | 10/26/2025 08:00:54 |  | Ragab Farg Abdel Nabi Bekhatro |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000228 | PCM-20251026-00000458 | TT-20251026-00419 | Reference_EM | Region_1 | QRH2432 | QRH2432 |  |  |  | Khaled Mohamed Abdulla Wahba | 10/26/2025 06:30:36 | 10/26/2025 06:33:39 | 10/26/2025 12:30:36 | Mains Failure at QRH2M2432-P1-VIP @ Generator_SG | 10/26/2025 06:20:37 | Major | 65109 | Mains Failure | 10/26/2025 06:20:31 | VIP | 2G | dammam | Generator_SG | 2G NSA | QRH2M2432 | FLM_EM | [8 empty] | API | 10/26/2025 06:30:36 | 10/26/2025 06:33:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000244 | PCM-20251026-00000493 | TT-20251026-00485 | EM | Region_1 | DMJR0165 | DMJR0165 |  |  |  | Hassan rabie | 10/26/2025 07:06:45 | 10/26/2025 08:06:51 | 10/26/2025 11:06:45 | Genset running at DMJR0165-P1-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 07:04:53 | Critical | 65112 | Genset running | 10/26/2025 07:04:50 | P1 | SRAN | arar | Sceco_STB | 2G NSA | DMJR0165 | FLM_EM | [8 empty] | API | 10/26/2025 07:06:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000263 | PCM-20251026-00000530 | TT-20251026-00527 | Reference_EM | Region_2 | DUB0015 | DUB0015 | Enviroment | Genset failure_Pump | Change Fuel Pump | Fritz Ian Generale | 10/26/2025 07:48:35 | 10/26/2025 10:36:29 | 10/26/2025 19:48:35 | Generator failure at DUB0015-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 07:38:04 | Minor | 65114 | Generator failure | 10/26/2025 07:38:00 | P3 | SRAN | al kharj | Power Cube | 2G NSA | DUB0015 | FLM_EM | [8 empty] | API | 10/26/2025 07:48:35 | 10/26/2025 10:35:24 | 10/26/2025 10:35:57 | 10/26/2025 10:35:59 | 10/26/2025 10:36:03 | 10/26/2025 10:36:29 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000266 | PCM-20251026-00000535 | TT-20251026-00529 | Reference_EM | Region_2 | RYAB0604 | RYAB0604 |  |  |  | Kazi Jalil Allimiya | 10/26/2025 07:50:19 | 10/26/2025 10:16:38 | 10/26/2025 19:50:19 | high temprature 40 at RYAB0604-P3_SRAN @ Sceco | 10/26/2025 07:39:43 | Minor | 65103 | high temprature 40 | 10/26/2025 07:39:39 | P3 | SRAN | al kharj | Sceco | 2G NSA | RYAB0604 | FLM_EM | [8 empty] | API | 10/26/2025 07:50:19 | 10/26/2025 10:16:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000270 | PCM-20251026-00000546 | TT-20251026-00540 | Reference_EM | Region_2 | RIY2112 | RIY2112 |  |  |  | Vignesh Sivakumar Sivakumar | 10/26/2025 07:55:17 | 10/26/2025 07:55:17 | 10/26/2025 13:55:17 | Mains Failure at RIY2112-P1-SHOP_SRAN @ Sceco | 10/26/2025 07:44:55 | Major | 65109 | Mains Failure | 10/26/2025 07:44:51 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2112 | FLM_EM | [8 empty] | API | 10/26/2025 07:55:17 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000276 | PCM-20251026-00000559 | TT-20251026-00551 | Reference_EM | Region_1 | JBL0441 | JBL0441 |  |  |  | Ahmed Hassan Ahmed Hassanin | 10/26/2025 08:02:31 | 10/26/2025 08:02:31 | 10/26/2025 20:02:31 | Generator failure at JBL0441-P3_SRAN @ Generator_DG | 10/26/2025 07:52:08 | Minor | 65114 | Generator failure | 10/26/2025 07:52:04 | P3 | SRAN | jubail | Generator_DG | 2G NSA | JBL0441 | FLM_EM | [8 empty] | API | 10/26/2025 08:02:31 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000296 | PCM-20251026-00000619 | TT-20251026-00606 | Reference_EM | Region_2 | RYRN0633 | RYRN0633 |  |  |  | Saleem Khan Amir Dost | 10/26/2025 08:30:55 | 10/26/2025 10:06:27 | 10/26/2025 20:30:55 | Mains Failure at RYRN2M5633-P3 @ Sceco | 10/26/2025 08:20:51 | Minor | 65109 | Mains Failure | 10/26/2025 08:20:41 | P3 | 2G | quweyah | Sceco | 2G NSA | RYRN2M5633 | FLM_EM | [8 empty] | API | 10/26/2025 08:30:55 | 10/26/2025 10:06:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Preparation | CM20251026000303 | PCM-20251026-00000628 | TT-20251026-00615 | Reference_EM | Region_1 | HRBD0125 | HRBD0125 |  |  |  | Mahmoud Youssef Mohamed Ahmed | 10/26/2025 08:35:36 | 10/26/2025 10:15:46 | 10/26/2025 14:35:36 | Mains Failure at HRBD0125-P1-HUB_SRAN @ Generator_SG | 10/26/2025 08:25:41 | Major | 65109 | Mains Failure | 10/26/2025 08:25:36 | P1 | SRAN | hafr | Generator_SG | 2G NSA | HRBD0125 | FLM_EM | [8 empty] | API | 10/26/2025 08:35:36 | 10/26/2025 09:06:45 | 10/26/2025 10:13:37 | 10/26/2025 10:13:40 | 10/26/2025 10:15:46 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000315 | PCM-20251026-00000649 | TT-20251026-00634 | Reference_EM | Region_2 | KHJ0469 | KHJ0469 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/26/2025 08:47:25 | 10/26/2025 08:47:25 | 10/26/2025 20:47:25 | High temperature 32C alarm at KHJ2M1469-P3 @ Sceco | 10/26/2025 08:37:06 | Minor | 65102 | High temperature 32C alarm | 10/26/2025 08:37:02 | P3 | 2G | al kharj | Sceco | 2G NSA | KHJ2M1469 | FLM_EM | [8 empty] | API | 10/26/2025 08:47:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000321 | PCM-20251026-00000670 | TT-20251026-00658 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 08:59:22 | 10/26/2025 09:36:34 | 10/26/2025 14:59:22 | high temprature 32 at RIY0232-P1_SRAN @ Sceco | 10/26/2025 08:48:57 | Major | 65102 | high temprature 32 | 10/26/2025 08:48:53 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/26/2025 08:59:22 | 10/26/2025 09:36:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000325 | PCM-20251026-00000680 | TT-20251026-00665 | Reference_EM | Region_1 | HFF0821 | HFF0821 |  |  |  | Moustafa Mohamed Saleh Saif | 10/26/2025 09:04:31 | 10/26/2025 10:59:18 | 10/26/2025 21:04:31 | high temprature 40 at HFF0821-P2-USF_SRAN-PC @ Power Cube | 10/26/2025 08:54:06 | Minor | 65103 | high temprature 40 | 10/26/2025 08:54:02 | P2 | SRAN | hafouf | Power Cube | 2G NSA | HFF0821 | FLM_EM | [8 empty] | API | 10/26/2025 09:04:31 | 10/26/2025 10:59:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000328 | PCM-20251026-00000685 | TT-20251026-00653 | Telecom | Region_2 | RYMK2261 | RYMK2261 |  |  |  | Saleem Khan Amir Dost | 10/26/2025 09:07:25 | 10/26/2025 10:06:28 | 10/26/2025 13:07:25 | 5(2G) 5(LTE) sites down under R2_RY1_HWBSC01 @ Generator_SG | 10/26/2025 08:53:17 | Critical | 21825 | CSL Fault | 10/26/2025 08:53:13 | P3 | SRAN | muzamiah | Power Cube | 2G_LTE SA | RIY2800-P3 2G_LTE,UMA2181-P3 2G_LTE,UMA2062-P3 2G_LTE,RIY2943-P1-VIP 2G_LTE,RYMK2261-P3 2G_LTE | FLM_EM |  | SITES HUB FB UMA2062-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 UMA2181-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RIY2800-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RIY2943-P1-VIP 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RYMK2261-P3 2G RYMK2261 suspecting power issue at hub site | PCM-20251026-00000673 | SITES HUB FB UMA2062-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 UMA2181-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RIY2800-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RIY2943-P1-VIP 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RYMK2261-P3 2G RYMK2261 suspecting power issue at hub site | SITES HUB FB UMA2062-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 UMA2181-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RIY2800-P3 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RIY2943-P1-VIP 2G RIY2605 Observing visibility down at both ends P2: RIY2605 RYMK2261-P3 2G RYMK2261 suspecting power issue at hub site |  | sites down |  | API | 10/26/2025 09:07:25 | 10/26/2025 10:06:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000329 | PCM-20251026-00000689 | TT-20251026-00672 | Reference_EM | Region_2 | RIY2068 | RIY2068 |  |  |  | Kadri Jalal Mohammed Asmail | 10/26/2025 09:09:10 | 10/26/2025 11:00:33 | 10/26/2025 21:09:10 | Door opening alarm at RIY2068-P3_SRAN @ Sceco | 10/26/2025 09:08:32 | Minor | 65101 | Door opening alarm | 10/26/2025 09:08:28 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2068 | FLM_EM | [8 empty] | API | 10/26/2025 09:09:10 | 10/26/2025 11:00:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000333 | PCM-20251026-00000694 | TT-20251026-00675 | Reference_EM | Region_1 | JBL0441 | JBL0441 |  |  |  | Ahmed Hassan Ahmed Hassanin | 10/26/2025 09:13:15 | 10/26/2025 09:13:15 | 10/26/2025 21:13:15 | Door opening alarm at JBL0441-P3_SRAN @ Generator_DG | 10/26/2025 09:12:42 | Minor | 65101 | Door opening alarm | 10/26/2025 09:12:40 | P3 | SRAN | jubail | Generator_DG | 2G NSA | JBL0441 | FLM_EM | [8 empty] | API | 10/26/2025 09:13:15 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000344 | PCM-20251026-00000709 | TT-20251026-00685 | Reference_EM | Region_2 | RIY0046 | RIY0046 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 09:18:56 | 10/26/2025 09:36:35 | 10/26/2025 15:18:56 | Mains Failure at RIY0046-P1-DIA_SRAN-FON @ Sceco | 10/26/2025 09:08:59 | Major | 65109 | Mains Failure | 10/26/2025 09:08:56 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0046 | FLM_EM | [8 empty] | API | 10/26/2025 09:18:56 | 10/26/2025 09:36:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251026000347 | PCM-20251026-00000711 | TT-20251026-00686 | Reference_EM | Region_2 | QSHL0890 | QSHL0890 |  |  |  | Farman Ullah Muhammad Nazir | 10/26/2025 09:19:32 | 10/26/2025 09:19:32 | 10/26/2025 21:19:32 | Mains Failure at QSHL0890-P2_SRAN @ Sceco | 10/26/2025 09:09:06 | Minor | 65109 | Mains Failure | 10/26/2025 09:09:03 | P2 | SRAN | buraidah | Sceco | 2G NSA | QSHL0890 | FLM_EM | [8 empty] | API | 10/26/2025 09:19:32 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000352 | PCM-20251026-00000723 | TT-20251026-00695 | Reference_EM | Region_2 | MZH0491 | MZH0491 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/26/2025 09:23:06 | 10/26/2025 09:23:06 | 10/26/2025 21:23:06 | Generator failure at MZH0491-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 09:12:33 | Minor | 65114 | Generator failure | 10/26/2025 09:12:30 | P3 | SRAN | muzamiah | Power Cube | 2G NSA | MZH0491 | FLM_EM | [8 empty] | API | 10/26/2025 09:23:06 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000362 | PCM-20251026-00000742 | TT-20251026-00705 | EM | Region_2 | MZH0491 | MZH0491 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/26/2025 09:33:40 | 10/26/2025 09:33:40 | 10/26/2025 15:33:40 | 1(2G/3G/LTE) sites down under MZH0491-P3-USF/R2_RY1_HWBSC01 @ Power Cube | 10/26/2025 09:26:43 | Major | 21825 | CSL Fault | 10/26/2025 09:26:41 | P3 | 2G | muzamiah | Power Cube | 2G_3G_LTE SA | MZH0491-P3-USF | FLM_EM |  | Results: DOWN SITE HUB MZH0491-P3-USF MZH0491 Summary: Hub: MZH0491, Down Count: 1, Down Sites: MZH0491-P3-USF Alarm Summary: MZH0491 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:33:40 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000364 | PCM-20251026-00000748 | TT-20251026-00716 | Reference_EM | Region_2 | AFL0018 | AFL0018 |  |  |  | Irfan Yousaf | 10/26/2025 09:35:00 | 10/26/2025 09:40:27 | 10/26/2025 21:35:00 | Generator failure at AFL0018-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 09:24:24 | Minor | 65114 | Generator failure | 10/26/2025 09:24:20 | P3 | SRAN | al kharj | Power Cube | 2G NSA | AFL0018 | FLM_EM | [8 empty] | API | 10/26/2025 09:35:00 | 10/26/2025 09:40:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000389 | PCM-20251026-00000793 | TT-20251026-00757 | Reference_EM | Region_2 | RIY2343 | RIY2343 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 09:58:45 | 10/26/2025 10:21:04 | 10/26/2025 15:58:45 | Door opening alarm at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:58:15 | Major | 65101 | Door opening alarm | 10/26/2025 09:58:11 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2343 | FLM_EM | [8 empty] | API | 10/26/2025 09:58:45 | 10/26/2025 10:21:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000390 | PCM-20251026-00000794 | TT-20251026-00759 | Reference_EM | Region_1 | TBSK0244 | TBSK0244 |  |  |  | Mahmoud Abdelwanis Massoud Elrashidy | 10/26/2025 09:59:16 | 10/26/2025 10:53:30 | 10/26/2025 21:59:16 | high temprature 32 at TBSK0244-ODC-ENV-ALM @ Generator_DG | 10/26/2025 09:48:49 | Minor | 65102 | high temprature 32 | 10/26/2025 09:48:44 | P3 | SRAN | sakaka | Generator_DG | 2G NSA | TBSK0244 | FLM_EM | [8 empty] | API | 10/26/2025 09:59:16 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251026000392 | PCM-20251026-00000796 | TT-20251026-00760 | Reference_EM | Region_2 | RIY2278 | RIY2278 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:00:51 | 10/26/2025 10:21:04 | 10/26/2025 22:00:51 | Mains Failure at RIY2278-P3_SRAN-PC @ Sceco | 10/26/2025 09:50:51 | Minor | 65109 | Mains Failure | 10/26/2025 09:50:49 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2278 | FLM_EM | [8 empty] | API | 10/26/2025 10:00:51 | 10/26/2025 10:21:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000395 | PCM-20251026-00000801 | TT-20251026-00697 | Telecom | Region_2 | DUB0015 | DUB0015 | Enviroment | Genset failure_Pump | Change Fuel Pump | Fritz Ian Generale | 10/26/2025 10:02:31 | 10/26/2025 10:39:17 | 10/26/2025 14:02:31 | 5(2G) 1(3G) 4(LTE) sites down under KJ1BSCH01 @ Sceco | 10/26/2025 09:21:18 | Critical | 21825 | CSL Fault | 10/26/2025 09:21:18 | P3 | SRAN | al kharj | Power Cube | 2G_3G_LTE SA | DLM0989-P3-USF 2G_3G_LTE,DLM0021-P3-USF 2G_LTE,DLM0023-P3-USF 2G,DLM0020-P3-USF 2G | FLM_EM |  | DUB0015 | PCM-20251026-00000792 | DUB0015 | DUB0015 |  | sites down |  | API | 10/26/2025 10:02:31 | 10/26/2025 10:35:24 | 10/26/2025 10:39:03 |  |  | 10/26/2025 10:39:17 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Preparation | CM20251026000400 | PCM-20251026-00000812 | TT-20251026-00770 | Reference_EM | Region_2 | RIY2343 | RIY2343 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:08:36 | 10/26/2025 10:46:53 | 10/26/2025 16:08:36 | Mains Failure at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:58:15 | Major | 65109 | Mains Failure | 10/26/2025 09:58:11 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2343 | FLM_EM | [8 empty] | API | 10/26/2025 10:08:36 | 10/26/2025 10:21:04 | 10/26/2025 10:21:43 | 10/26/2025 10:21:46 | 10/26/2025 10:46:53 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000402 | PCM-20251026-00000816 | TT-20251026-00755 | Telecom | Region_2 | RIY2003 | RIY2003 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mahmoud Hefny Ali Ahmed | 10/26/2025 10:09:26 | 10/26/2025 10:38:28 | 10/26/2025 16:09:26 | 1(2G) sites down under RIY2003-P3/R2_BR1_HWBSC01 @ Generator_SG | 10/26/2025 09:53:42 | Major | 21825 | CSL Fault | 10/26/2025 09:53:38 | P3 | SRAN | muzamiah | Generator_SG | 2G SA | RIY2003-P3 | FLM_EM |  | Results: DOWN SITE HUB RIY2003-P3 RIY2003 Summary: Hub: RIY2003, Down Count: 1, Down Sites: RIY2003-P3 Alarm Summary: RIY2003 Alarm Active on HUB | PCM-20251026-00000800 | power issue at site | power issue at site |  | sites down |  | API | 10/26/2025 10:09:26 | 10/26/2025 10:37:40 | 10/26/2025 10:37:48 | 10/26/2025 10:37:50 | 10/26/2025 10:37:52 | 10/26/2025 10:38:28 |  | Mahmoud Hefny Ali Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000404 | PCM-20251026-00000819 | TT-20251026-00774 | Reference_EM | Region_1 | DAM0642 | DAM0642 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/26/2025 10:11:11 | 10/26/2025 10:35:46 | 10/26/2025 22:11:11 | high temprature 32 at DAM0642-P3_SRAN @ Sceco | 10/26/2025 10:00:37 | Minor | 65102 | high temprature 32 | 10/26/2025 10:00:34 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM0642 | FLM_EM | [8 empty] | API | 10/26/2025 10:11:11 | 10/26/2025 10:35:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000405 | PCM-20251026-00000821 | TT-20251026-00776 | Reference_EM | Region_1 | HFF2397 | HFF2397 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/26/2025 10:11:40 | 10/26/2025 10:11:40 | 10/26/2025 22:11:40 | Mains Failure at HFF2397-P3_SRAN @ Sceco | 10/26/2025 10:01:20 | Minor | 65109 | Mains Failure | 10/26/2025 10:01:16 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF2397 | FLM_EM | [8 empty] | API | 10/26/2025 10:11:40 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000408 | PCM-20251026-00000827 | TT-20251026-00768 | EM | Region_1 | SLW2996 | SLW2996 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/26/2025 10:13:11 | 10/26/2025 10:13:11 | 10/26/2025 16:13:11 | 1(2G/3G/LTE) sites down under SLW2996-P3/R1_HF_HWBSC01 @ Generator_SG | 10/26/2025 10:05:59 | Major | 21825 | CSL Fault | 10/26/2025 10:05:54 | P3 | 2G | hafouf | Generator_SG | 2G_3G_LTE SA | SLW2996-P3 | FLM_EM |  | Results: DOWN SITE HUB SLW2996-P3 SLW2996 Summary: Hub: SLW2996, Down Count: 1, Down Sites: SLW2996-P3 Alarm Summary: SLW2996 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 10:13:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000412 | PCM-20251026-00000840 | TT-20251026-00763 | Telecom | Region_2 | RIY2343 | RIY2343 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:17:31 | 10/26/2025 10:21:05 | 10/26/2025 22:17:31 | RF Unit Maintenance Link Failure at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:59:57 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 09:58:15 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2343 | FLM_EM |  |  | PCM-20251026-00000805 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 10:17:31 | 10/26/2025 10:21:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000413 | PCM-20251026-00000842 | TT-20251026-00765 | Telecom | Region_2 | RIY2343 | RIY2343 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:18:01 | 10/26/2025 10:21:05 | 10/26/2025 16:18:01 | NR Cell Unavailable at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:59:51 | Major | 29841 | NR Cell Unavailable | 10/26/2025 09:58:17 | P1 | SRAN | riyadh | Sceco | 5G SA | RIY2343 | FLM_EM |  |  | PCM-20251026-00000808 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 10:18:01 | 10/26/2025 10:21:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000416 | PCM-20251026-00000846 | TT-20251026-00797 | Reference_EM | Region_2 | QSDH0709 | QSDH0709 |  |  |  | Mahmoud Hefny Ali Ahmed | 10/26/2025 10:22:31 | 10/26/2025 10:37:41 | 10/26/2025 22:22:31 | Mains Failure at QSDH0709-P2_SRAN @ Sceco | 10/26/2025 10:12:30 | Minor | 65109 | Mains Failure | 10/26/2025 10:12:26 | P2 | SRAN | dawadmi | Sceco | 2G NSA | QSDH0709 | FLM_EM | [8 empty] | API | 10/26/2025 10:22:31 | 10/26/2025 10:37:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000417 | PCM-20251026-00000848 | TT-20251026-00799 | Reference_EM | Region_1 | HFBD2011 | HFBD2011 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 10:23:02 | 10/26/2025 10:23:02 | 10/26/2025 16:23:02 | Generator failure at HFBD2011-P1-HUB_SRAN @ Generator_SG | 10/26/2025 10:12:35 | Major | 65114 | Generator failure | 10/26/2025 10:12:32 | P1 | SRAN | hafouf | Generator_SG | 2G NSA | HFBD2011 | FLM_EM | [8 empty] | API | 10/26/2025 10:23:02 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Departed | CM20251026000439 | PCM-20251026-00000889 | TT-20251026-00844 | Reference_EM | Region_2 | RIY2126 | RIY2126 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 10:48:50 | 10/26/2025 10:59:27 | 10/26/2025 22:48:50 | Mains Failure at RIY2126-P3_SRAN-PC @ Sceco | 10/26/2025 10:38:32 | Minor | 65109 | Mains Failure | 10/26/2025 10:38:29 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2126 | FLM_EM | [8 empty] | API | 10/26/2025 10:48:50 | 10/26/2025 10:56:29 | 10/26/2025 10:59:24 | 10/26/2025 10:59:27 | [7 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000443 | PCM-20251026-00000896 | TT-20251026-00858 | Reference_EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 10:53:31 | 10/26/2025 10:53:31 | 10/26/2025 22:53:31 | Low battery voltage at RIY2431-P2_SRAN @ Sceco | 10/26/2025 10:42:53 | Minor | 65110 | Low battery voltage | 10/26/2025 10:42:48 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/26/2025 10:53:31 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000445 | PCM-20251026-00000899 | TT-20251026-00860 | Reference_EM | Region_1 | DAM0252 | DAM0252 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/26/2025 10:54:31 | 10/26/2025 10:54:31 | 10/26/2025 22:54:31 | Door opening alarm at DAM0252-P2_SRAN @ Sceco | 10/26/2025 10:53:44 | Minor | 65101 | Door opening alarm | 10/26/2025 10:53:41 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0252 | FLM_EM | [8 empty] | API | 10/26/2025 10:54:31 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000450 | PCM-20251026-00000910 | TT-20251026-00868 | Telecom | Region_2 | BUR0053 | BUR0053 |  |  |  | Farman Ullah Muhammad Nazir | 10/26/2025 11:00:50 | 10/26/2025 11:00:50 | 10/26/2025 17:00:50 | BBU Board Maintenance Link Failure at BUR0053-P2_SRAN @ Sceco | 10/26/2025 10:55:11 | Major | 26205 | BBU Board Maintenance Link Failure | 10/26/2025 10:53:38 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0053 | FLM_EM |  |  | PCM-20251026-00000904 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 11:00:50 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000451 | PCM-20251026-00000911 | TT-20251026-00875 | Reference_EM | Region_2 | DLM0023 | DLM0023 |  |  |  | Kazi Jalil Allimiya | 10/26/2025 11:01:16 | 10/26/2025 11:01:16 | 10/26/2025 23:01:16 | high temprature 40 at DLM0023-P3-USF_SRAN-PC @ Sceco | 10/26/2025 10:50:56 | Minor | 65103 | high temprature 40 | 10/26/2025 10:50:52 | P3 | SRAN | al kharj | Sceco | 2G NSA | DLM0023 | FLM_EM | [8 empty] | API | 10/26/2025 11:01:16 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low