Request_Resolved | CM20251025000849 | PCM-20251025-00001875 | TT-20251025-01923 | Telecom | Region_2 | DWD2113 | DWD2113 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Zakir Muhammad Yar Muhammad | 10/25/2025 23:51:37 | 10/26/2025 04:00:42 | 10/26/2025 11:51:37 | RF Unit Maintenance Link Failure at DWD2113-P3_SRAN @ Sceco | 10/25/2025 23:48:06 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/25/2025 23:46:22 | P3 | SRAN | dawadmi | Sceco | 2G NSA | DWD2113 | FLM_TE | [8 empty] | API | 10/25/2025 23:51:37 | 10/26/2025 00:55:55 | 10/26/2025 04:00:18 |  |  | 10/26/2025 04:00:42 |  | Zakir Muhammad Yar Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251025000850 | PCM-20251025-00001876 | TT-20251025-01927 | Telecom | Region_1 | HFF0224 | HFF0224 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/25/2025 23:56:15 | 10/26/2025 09:34:40 | 10/26/2025 05:56:15 | BBU CPRI Interface Error at HFF0224-P3_SRAN @ Generator_SG | 10/25/2025 22:08:46 | Major | 26234 | BBU CPRI Interface Error | 10/25/2025 22:06:13 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | HFF0224 | FLM_TE | [8 empty] | API | 10/25/2025 23:56:15 | 10/26/2025 09:34:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000851 | PCM-20251025-00001878 | TT-20251025-01925 | Telecom | Region_6 | RYNJ0205 | RYNJ0205 | Transsmission | MW_RSL_fading | Fading issue | Saif Muhammad | 10/25/2025 23:58:01 | 10/26/2025 01:43:35 | 10/26/2025 05:58:01 | 1(5G) sites down under RYNJ0205-GSM-P3-HUB @ Generator_SG | 10/25/2025 23:49:59 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/25/2025 23:49:56 | P1 | 2G | wadi dawasar | Generator_SG | 5G SA | RYNJ0205-GSM-P3-HUB | FLM_TE | RYNJ0205 | Results: DOWN SITE HUB RYNJ0205-GSM-P3-HUB RYNJ0205 Summary: Hub: RYNJ0205, Down Count: 1, Down Sites: RYNJ0205-GSM-P3-HUB Alarm Summary: RYNJ0205 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.102.77.84:8080] [URL:http://10.102.77.84:8080/NE3S/1.0/] | sites down |  | API | 10/25/2025 23:58:01 | 10/26/2025 01:42:34 | 10/26/2025 01:43:04 |  |  | 10/26/2025 01:43:35 |  | Saif Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000853 | PCM-20251025-00001881 | TT-20251025-01926 | EM | Region_4 | JED2178 | JED2178 | Equipment | BSS_HW_fault | Replace RF Module | Khaled Mohammad Abdallah | 10/25/2025 23:59:58 | 10/26/2025 08:15:14 | 10/26/2025 05:59:58 | 1(2G/LTE) sites down under JED2178-P3/JED2178-P3 @ Sceco | 10/25/2025 23:51:51 | Major | 7706 | BTS O&M LINK FAILURE | 10/25/2025 23:51:47 | P3 | 2G | jeddah | Sceco | 2G SA | JED2178-P3 | FLM_TE | JED2178 | Results: DOWN SITE HUB JED2178-P3 JED2178 Summary: Hub: JED2178, Down Count: 1, Down Sites: JED2178-P3 Alarm Summary: JED2178 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/25/2025 23:59:58 |  | 10/26/2025 06:10:47 | 10/26/2025 06:10:49 | 10/26/2025 06:10:51 | 10/26/2025 08:15:14 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000001 | PCM-20251026-00000002 | TT-20251026-00001 | Telecom | Region_6 | KMS0168 | KMS0168 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/26/2025 00:04:01 | 10/26/2025 01:03:02 | 10/26/2025 12:04:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS0168-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 00:03:22 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 00:03:14 | P3 | 2G | khamis mushyet | Sceco | 5G_Cell SA | KMS0168 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 00:04:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000002 | PCM-20251026-00000003 | TT-20251026-00002 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 00:04:31 | 10/26/2025 10:00:13 | 10/26/2025 06:04:31 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/25/2025 21:02:52 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/25/2025 21:03:59 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/26/2025 00:04:31 | 10/26/2025 10:00:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000003 | PCM-20251026-00000005 | TT-20251025-01883 | Telecom | Region_6 | JIZ1U6797 | JIZ6097 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/26/2025 00:05:10 | 10/27/2025 03:41:50 | 10/26/2025 06:05:10 | BASE STATION ANTENNA LINE PROBLEM at JIZ1U6797-G9-L18-SBTS-P1-VIP-SHOP @ Sceco | 10/25/2025 22:52:14 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/25/2025 22:52:03 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1U6797 | FLM_TE |  |  | PCM-20251025-00001823 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 00:05:10 | 10/26/2025 03:25:21 | 10/26/2025 19:49:23 |  |  | 10/27/2025 03:41:50 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000004 | PCM-20251026-00000006 | TT-20251026-00003 | Telecom | Region_1 | HFR6002 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 00:07:06 | 10/26/2025 00:30:02 | 10/26/2025 06:07:06 | BBU CPRI Interface Error at HFR6002-P3_SRAN @ Sceco | 10/26/2025 00:02:29 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 00:00:13 | P3 | SRAN | hafr | Sceco | 2G NSA | HFR6002 | FLM_TE | [8 empty] | API | 10/26/2025 00:07:06 | 10/26/2025 00:30:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000005 | PCM-20251026-00000008 | TT-20251026-00006 | EM | Region_3 | YBDB2291 | YBDB2291 | Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue | Sayed Satoor | 10/26/2025 00:07:38 | 10/26/2025 03:41:53 | 10/26/2025 04:07:38 | Mains Failure at YBDB2291-P1-WDM-HUB_SRAN @ Generator_DG | 10/26/2025 00:06:06 | Critical | 65109 | Mains Failure | 10/26/2025 00:06:03 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | YBDB2291 | FLM_EM | [8 empty] | API | 10/26/2025 00:07:38 | 10/26/2025 03:41:05 | 10/26/2025 03:41:34 |  |  | 10/26/2025 03:41:53 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000009 | PCM-20251026-00000014 | TT-20251026-00013 | EM | Region_5 | MKYL1M7910 | MKYL0910 | Enviroment | Air Condition | Change Fan | Muhammad Wahab Tahir Muhammad Afzal | 10/26/2025 00:14:52 | 10/26/2025 02:47:39 | 10/26/2025 06:14:52 | High TEAMPRATURE at MKYL1M7910-G9-L8-L18-L21-SBTS-P1-HUB-USF @ Generator_DG | 10/26/2025 00:06:50 | Major | 7103 | High TEAMPRATURE | 10/26/2025 00:06:41 | P1 | 4G | makkah | Generator_DG | LTE NSA | MKYL1M7910 | FLM_EM | [5 empty] | High TEAMPRATURE |  |  | API | 10/26/2025 00:14:52 | 10/26/2025 01:10:30 | 10/26/2025 01:11:50 | 10/26/2025 01:11:52 | 10/26/2025 01:30:31 | 10/26/2025 02:47:39 |  | Muhammad Wahab Tahir Muhammad Afzal |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000010 | PCM-20251026-00000017 | TT-20251026-00016 | EM | Region_4 | HLA1M8439 | HLA2439 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/26/2025 00:16:55 | 10/26/2025 00:16:55 | 10/26/2025 12:16:55 | LOW FUEL at HLA1M8439-G9-L8-L18-L21-SBTS @ Sceco | 10/26/2025 00:08:50 | Minor | 7103 | LOW FUEL | 10/26/2025 00:08:40 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8439 | FLM_EM | [5 empty] | LOW FUEL |  |  | API | 10/26/2025 00:16:55 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000013 | PCM-20251026-00000023 | TT-20251025-00691 | Reference_telecom | Region_4 | JED1U6720 | JED6020 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 00:19:16 | 10/26/2025 00:19:16 | 10/26/2025 06:19:16 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/25/2025 10:03:17 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/25/2025 10:03:05 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251025-00000600 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/26/2025 00:19:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000015 | PCM-20251026-00000025 | TT-20251026-00023 | Telecom | Region_3 | TBK0232 | TBK0232 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Tahir Abbas Fateh Khan | 10/26/2025 00:20:02 | 10/26/2025 01:21:25 | 10/26/2025 12:20:02 | RF Unit Maintenance Link Failure at TBK0232-P2_SRAN @ Sceco | 10/26/2025 00:15:43 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 00:14:58 | P2 | SRAN | tabouk | Sceco | 2G NSA | TBK0232 | FLM_TE | [8 empty] | API | 10/26/2025 00:20:02 | 10/26/2025 00:22:41 | 10/26/2025 00:42:37 | 10/26/2025 00:42:40 | 10/26/2025 01:04:21 | 10/26/2025 01:21:25 |  | Tahir Abbas Fateh Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000016 | PCM-20251026-00000026 | TT-20251025-01887 | Reference_telecom | Region_4 | JED2040 | JED2040 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 00:20:12 | 10/26/2025 00:20:12 | 10/26/2025 12:20:12 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED2040-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/25/2025 22:59:09 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:59:02 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2040 | FLM_TE |  |  | PCM-20251025-00001832 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 00:20:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000017 | PCM-20251026-00000028 | TT-20251026-00005 | Reference_telecom | Region_2 | RIY2M8123 | RIY2123 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Khan zeb Shah nawaz | 10/26/2025 00:21:21 | 10/26/2025 15:51:50 | 10/26/2025 12:21:21 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8123-P3-L800 @ Sceco | 10/25/2025 21:07:25 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/25/2025 21:07:21 | P3 | 4G | riyadh | Sceco | 2G NSA | RIY2M8123 | FLM_TE |  |  | PCM-20251026-00000007 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/26/2025 00:21:21 | 10/26/2025 15:45:29 | 10/26/2025 15:51:16 |  |  | 10/26/2025 15:51:50 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000020 | PCM-20251026-00000043 | TT-20251026-00026 | EM | Region_6 | SDA0322 | SDA0322 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/26/2025 00:27:29 | 10/26/2025 09:37:17 | 10/26/2025 06:27:29 | 1(2G/LTE) sites down under SDA0322-P3/SDA0322-P3 @ Sceco | 10/26/2025 00:19:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 00:19:08 | P3 | 2G | abha | Sceco | 2G_LTE SA | SDA0322-P3 | FLM_EM | SDA0322 | Results: DOWN SITE HUB SDA0322-P3 SDA0322 Summary: Hub: SDA0322, Down Count: 1, Down Sites: SDA0322-P3 Alarm Summary: SDA0322 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 00:27:29 | 10/26/2025 09:37:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000021 | PCM-20251026-00000052 | TT-20251026-00039 | Telecom | Region_2 | RIY0716 | RIY0716 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | DILSHAD ALI ABDUL HAMEED | 10/26/2025 00:32:25 | 10/26/2025 07:06:26 | 10/26/2025 12:32:25 | BBU DC Output Out of Range at RIY0716-P2_SRAN @ Sceco | 10/26/2025 00:29:03 | Minor | 26112 | BBU DC Output Out of Range | 10/26/2025 00:27:55 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0716 | FLM_TE | [8 empty] | API | 10/26/2025 00:32:25 | 10/26/2025 07:05:18 | 10/26/2025 07:06:04 |  |  | 10/26/2025 07:06:26 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000024 | PCM-20251026-00000061 | TT-20251026-00045 | Telecom | Region_3 | RSP0001-MDC-NE8K-M14-02 | RSP0001 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 00:36:03 | 10/26/2025 00:46:03 | 10/26/2025 12:36:03 | Bad Package Error Rising at RSP0001-MDC-NE8K-M14-02 @ Sceco | 10/26/2025 00:35:48 | Minor | 101-2501403 | Bad Package Error Rising | 10/26/2025 00:35:40 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | RSP0001-MDC-NE8K-M14-02 | FLM_TE | [8 empty] | API | 10/26/2025 00:36:03 | 10/26/2025 00:46:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000026 | PCM-20251026-00000066 | TT-20251026-00044 | Telecom | Region_5 | MDQ0354 | MDQ0354 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/26/2025 00:43:10 | 10/26/2025 00:43:10 | 10/26/2025 06:43:10 | 2(5G) sites down under MDQ2344-GSM-UMTS-P2-USF,MDQ0354-GSM-UMTS-P2-USF @ Generator_SG | 10/26/2025 00:32:05 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 00:32:03 | P2 | 2G | makkah | Generator_SG | 5G SA | MDQ0354-GSM-UMTS-P2-USF 5G,MDQ2344-GSM-UMTS-P2-USF 5G | FLM_TE |  | Results: DOWN SITE HUB MDQ0354-GSM-UMTS-P2-USF Need to check MDQ2344-GSM-UMTS-P2-USF Need to check Summary: Alarm Summary: HUB site not found | PCM-20251026-00000063 | MDQ0354 | MDQ0354 |  | sites down |  | API | 10/26/2025 00:43:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000027 | PCM-20251026-00000068 | TT-20251026-00047 | EM | Region_4 | JED0316 | JED0316 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 00:43:29 | 10/26/2025 10:36:44 | 10/26/2025 06:43:29 | 1(2G/LTE/5G) sites down under JED0316-P2/JED0316-P2 @ Sceco | 10/26/2025 00:35:26 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 00:35:18 | P2 | 2G | jeddah | Sceco | 2G SA | JED0316-P2 | FLM_TE | JED0316 | Results: DOWN SITE HUB JED0316-P2 JED0316 Summary: Hub: JED0316, Down Count: 1, Down Sites: JED0316-P2 Alarm Summary: JED0316 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 00:43:29 | 10/26/2025 10:36:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000030 | PCM-20251026-00000074 | TT-20251025-00297 | Reference_telecom | Region_4 | NSH1M7165 | NSH0165 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 00:51:00 | 10/27/2025 03:32:05 | 10/26/2025 12:51:00 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NSH1M7165-G9-L9-L18-SBTS-P3 @ Generator_SG | 10/25/2025 03:09:05 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 03:07:29 | P3 | 4G | adam | Generator_SG | LTE NSA | NSH1M7165 | FLM_TE |  |  | PCM-20251025-00000263 | Please close site is clear | Please close site is clear |  |  |  | API | 10/26/2025 00:51:00 | 10/26/2025 09:54:22 | 10/27/2025 03:31:53 |  |  | 10/27/2025 03:32:05 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000033 | PCM-20251026-00000078 | TT-20251025-01824 | Reference_telecom | Region_6 | KHS1M7565 | KHS0565 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 00:55:20 | 10/26/2025 03:55:04 | 10/26/2025 06:55:20 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHS1M7565-P2-USF-L900 @ Sceco | 10/25/2025 21:17:03 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 19:51:59 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7565 | FLM_TE |  |  | PCM-20251025-00001761 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:55:20 | 10/26/2025 01:43:42 | 10/26/2025 02:48:56 |  |  | 10/26/2025 03:55:04 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000034 | PCM-20251026-00000079 | TT-20251025-01821 | Reference_telecom | Region_6 | KHS1M7657 | KHS0657 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 00:55:58 | 10/26/2025 03:54:53 | 10/26/2025 06:55:58 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHS1M7657-P3-L900 @ Generator_SG | 10/25/2025 21:17:14 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 19:46:49 | P3 | 4G | turaib | Generator_SG | LTE NSA | KHS1M7657 | FLM_TE |  |  | PCM-20251025-00001752 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:55:58 | 10/26/2025 01:43:43 | 10/26/2025 02:49:00 |  |  | 10/26/2025 03:54:53 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000035 | PCM-20251026-00000080 | TT-20251025-01823 | Reference_telecom | Region_6 | KHS1M7992 | KHS0992 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 00:56:15 | 10/26/2025 03:54:40 | 10/26/2025 06:56:15 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHS1M7992-P2-USF-L900 @ Sceco | 10/25/2025 21:21:18 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 19:51:25 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7992 | FLM_TE |  |  | PCM-20251025-00001760 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:15 | 10/26/2025 01:43:43 | 10/26/2025 02:49:05 |  |  | 10/26/2025 03:54:40 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000036 | PCM-20251026-00000081 | TT-20251025-01123 | Reference_telecom | Region_6 | NJR0020 | NJR0020 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/26/2025 00:56:26 | 10/26/2025 02:21:19 | 10/26/2025 12:56:26 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0020-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/25/2025 11:48:15 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 11:46:37 | P2 | 2G | najran | Sceco | 2G NSA | NJR0020 | FLM_TE |  |  | PCM-20251025-00001038 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:26 | 10/26/2025 01:33:53 | 10/26/2025 02:20:38 |  |  | 10/26/2025 02:21:19 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000037 | PCM-20251026-00000082 | TT-20251025-01431 | Reference_telecom | Region_6 | NJR1M7042 | NJR0042 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/26/2025 00:56:34 | 10/26/2025 02:22:06 | 10/26/2025 12:56:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR1M7042-P2-NCA-L800-SBTS @ Sceco | 10/25/2025 14:59:40 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 14:23:38 | P2 | 4G | najran | Sceco | LTE NSA | NJR1M7042 | FLM_TE |  |  | PCM-20251025-00001370 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:34 | 10/26/2025 01:33:54 | 10/26/2025 02:21:25 |  |  | 10/26/2025 02:22:06 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000038 | PCM-20251026-00000083 | TT-20251026-00063 | Telecom | Region_4 | JED0151 | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 00:56:41 | 10/26/2025 00:56:41 | 10/26/2025 06:56:41 | LOCAL_FAULT at JED0151 (JD1)_ELC @ Sceco_STB | 10/26/2025 00:53:11 | Major | 1-12545 | LOCAL_FAULT | 10/26/2025 00:52:58 | VIP | 2G | jeddah | Sceco_STB | DWDM NSA | JED0151 | FLM_TE | [5 empty] | 5-ELC(3-E)-13-G1M520S-4(RX2/TX2(ISP_PCLS0001JD1-100GE-03))-CLIENT:1 |  |  | API | 10/26/2025 00:56:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000039 | PCM-20251026-00000084 | TT-20251025-00917 | Reference_telecom | Region_6 | TLM1M8248 | TLM2248 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/26/2025 00:56:51 | 10/26/2025 08:39:30 | 10/26/2025 12:56:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TLM1M8248-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/25/2025 10:38:59 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 10:13:55 | P3 | 4G | mohail | Sceco | LTE NSA | TLM1M8248 | FLM_TE |  |  | PCM-20251025-00000841 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:56:51 | 10/26/2025 08:33:21 | 10/26/2025 08:39:17 |  |  | 10/26/2025 08:39:30 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000040 | PCM-20251026-00000085 | TT-20251025-00490 | Reference_telecom | Region_6 | MKW2344 | MKW2344 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/26/2025 00:57:02 | 10/26/2025 10:21:19 | 10/26/2025 12:57:02 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at MKW2344-G9-L8-L18-NR2.6-SBTS-P3 @ Generator_SG | 10/25/2025 07:52:19 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 09:11:31 | P3 | 2G | Baha | Generator_SG | 2G NSA | MKW2344 | FLM_TE |  |  | PCM-20251025-00000426 | PLEASE CLOSE THE SITE IS CLEAR | PLEASE CLOSE THE SITE IS CLEAR |  |  |  | API | 10/26/2025 00:57:02 | 10/26/2025 10:20:12 | 10/26/2025 10:20:57 |  |  | 10/26/2025 10:21:19 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000041 | PCM-20251026-00000087 | TT-20251026-00065 | Telecom | Region_2 | RIYB6029-CSG-01 | RIYB6029 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/26/2025 00:58:15 | 10/26/2025 11:14:32 | 10/26/2025 12:58:15 | Crc error alarm notification at RIYB6029-CSG-01 @ Sceco | 10/26/2025 00:57:39 | Minor | 101-1103100 | Crc error alarm notification | 10/26/2025 00:57:20 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6029-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 00:58:15 | 10/26/2025 11:14:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000042 | PCM-20251026-00000088 | TT-20251025-01311 | Reference_telecom | Region_6 | QFL1M7033 | QFL0033 | Equipment | BSS_HW_Stuck | Reset Air Scale | Mohammed Sideag Mohammed Ali | 10/26/2025 00:58:16 | 10/26/2025 01:06:31 | 10/26/2025 12:58:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at QFL1M7033-P2-CA-L800-SBTS @ Sceco | 10/25/2025 15:19:19 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 06:42:05 | P2 | 4G | jizan | Sceco | LTE NSA | QFL1M7033 | FLM_TE |  |  | PCM-20251025-00001262 | Please close the site is clear | Please close the site is clear |  |  |  | API | 10/26/2025 00:58:16 | 10/26/2025 01:05:53 | 10/26/2025 01:06:15 |  |  | 10/26/2025 01:06:31 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000043 | PCM-20251026-00000089 | TT-20251026-00066 | EM | Region_5 | MAK6028 | MAK6028 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 00:58:45 | 10/26/2025 00:58:45 | 10/26/2025 12:58:45 | AIRCON 2 FAILURE at MAK6028-GSM-P3 @ Sceco | 10/26/2025 00:50:31 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 00:50:25 | P3 | 2G | makkah | Sceco | 2G NSA | MAK6028 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 00:58:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000044 | PCM-20251026-00000090 | TT-20251026-00048 | Telecom | Region_3 | WFR2279 | WFR2279 |  |  |  | Walid Mohamad Fazil | 10/26/2025 00:58:45 | 10/26/2025 01:33:14 | 10/26/2025 06:58:45 | 4(2G) 4(LTE) sites down under R3_MD_HWBSC01 @ Sceco | 10/26/2025 00:36:19 | Major | 21825 | CSL Fault | 10/26/2025 00:36:13 | P3 | SRAN | madinah | Generator_SG | 2G_LTE SA | WFR2321-P3 2G_LTE,WFR2280-P3 2G_LTE | FLM_EM | WFR2279 | Dear Team, Hub:- WFR2279 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251026-00000069 | Dear Team, Hub:- WFR2279 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- WFR2279 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/26/2025 00:58:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000045 | PCM-20251026-00000093 | TT-20251025-00100 | Reference_telecom | Region_4 | NSH1M7128 | NSH0128 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 00:59:46 | 10/26/2025 12:28:54 | 10/26/2025 12:59:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NSH1M7128-G9-NL8-L18-SBTS-P2-USF @ Generator_DG | 10/24/2025 23:49:35 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 23:49:25 | P2 | 4G | adam | Generator_DG | LTE NSA | NSH1M7128 | FLM_TE |  |  | PCM-20251025-00000097 | Please close the site is clear | Please close the site is clear |  |  |  | API | 10/26/2025 00:59:46 | 10/26/2025 12:28:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000046 | PCM-20251026-00000095 | TT-20251026-00068 | Reference_telecom | Region_5 | MAK0628 | MAK0628 | Equipment | SFP_BTS | Replace SFP | Inam ullah | 10/26/2025 01:01:59 | 10/26/2025 10:54:01 | 10/26/2025 13:01:59 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at MAK0628-G9-NL8-NL18-L21-NR2.6-SBTS-P3-NEW @ Sceco | 10/26/2025 00:55:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 00:55:36 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK0628 | FLM_TE |  |  | PCM-20251026-00000094 | kindly support to perform HC,check sfp cable connector connected RMOD | kindly support to perform HC,check sfp cable connector connected RMOD |  |  |  | API | 10/26/2025 01:01:59 | 10/26/2025 09:57:41 | 10/26/2025 09:58:07 | 10/26/2025 09:58:12 | 10/26/2025 10:20:43 | 10/26/2025 10:54:01 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000047 | PCM-20251026-00000097 | TT-20251026-00070 | EM | Region_6 | BSA1M8308 | BSA2308 |  |  |  | Asad Saddiq | 10/26/2025 01:02:22 | 10/26/2025 07:20:14 | 10/26/2025 13:02:22 | RECTIFIER MODULE FAILURE at BSA1M8308-G9-L800-L1800-L2100-SBTS-P3 @ Generator_SG | 10/26/2025 00:53:59 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 00:53:51 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8308 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 01:02:22 | 10/26/2025 07:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000052 | PCM-20251026-00000105 | TT-20251026-00073 | Reference_EM | Region_1 | SKJF0199 | SKJF0199 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Bashir Sahib Rahman | 10/26/2025 01:07:02 | 10/26/2025 01:51:57 | 10/26/2025 07:07:02 | Door opening alarm at SKJF0199-P1-HUB_SRAN @ Sceco | 10/26/2025 01:06:47 | Major | 65101 | Door opening alarm | 10/26/2025 01:06:43 | P1 | SRAN | quriyat | Sceco | 2G NSA | SKJF0199 | FLM_EM | [8 empty] | API | 10/26/2025 01:07:02 | 10/26/2025 01:51:23 | 10/26/2025 01:51:36 |  |  | 10/26/2025 01:51:57 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000053 | PCM-20251026-00000109 | TT-20251026-00074 | Reference_EM | Region_1 | DMJR0132 | DMJR0132 |  |  |  | Elsaid Adel Mohamed Abouhegara | 10/26/2025 01:10:07 | 10/26/2025 01:10:07 | 10/26/2025 13:10:07 | Mains Failure at DMJR0132-P3_SRAN @ Generator_SG | 10/26/2025 01:00:13 | Minor | 65109 | Mains Failure | 10/26/2025 01:00:08 | P3 | SRAN | quriyat | Generator_SG | 2G NSA | DMJR0132 | FLM_EM | [8 empty] | API | 10/26/2025 01:10:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000056 | PCM-20251026-00000120 | TT-20251026-00088 | Reference_telecom | Region_4 | JED0207 | JED0207 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 01:20:59 | 10/26/2025 10:36:44 | 10/26/2025 13:20:59 | LossOfSignal observed in JED0207 towards 10.3.227.85 @ Sceco | 10/25/2025 13:22:03 | Minor |  | LossOfSignal | 10/25/2025 13:20:50 | P2 | 2G | jeddah | Sceco | TX NSA | JED0207 | FLM_TE | [8 empty] | API | 10/26/2025 01:20:59 | 10/26/2025 10:36:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20251026000058 | PCM-20251026-00000127 | TT-20251025-01256 | Telecom | Region_1 | DJL0553-LH | DJL0553 |  |  |  | Syed Fawad Ali | 10/26/2025 01:25:32 | 10/26/2025 05:24:12 | 10/26/2025 07:25:32 | IN_PWR_HIGH ALARM AT DJL0553-LH | 10/25/2025 14:49:09 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/25/2025 14:49:09 | P1 | DWDM | sakaka | Sceco_STB_Rental | DWDM NSA | DJL0553-LH | FLM_TE |  |  | PCM-20251025-00001393 | we observing high power from IP side , so we will check if can we add atteunatour in MW or need SA RFC | we observing high power from IP side , so we will check if can we add atteunatour in MW or need SA RFC |  |  |  | API | 10/26/2025 01:25:32 | 10/26/2025 04:57:49 | 10/26/2025 04:58:00 | 10/26/2025 04:58:03 | 10/26/2025 04:58:07 | 10/26/2025 05:24:12 |  | Syed Fawad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000059 | PCM-20251026-00000129 | TT-20251023-01756 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 01:29:09 | 10/26/2025 11:48:55 | 10/26/2025 07:29:09 | LOCAL_FAULT at YBDB2655_ELC @ Sceco_STB | 10/23/2025 17:44:42 | Major | 1-12545 | LOCAL_FAULT | 10/23/2025 17:44:30 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE |  |  | PCM-20251023-00001807 | you can ignore for now as ports still no in use and still not migrated | you can ignore for now as ports still no in use and still not migrated |  |  |  | API | 10/26/2025 01:29:09 | 10/26/2025 11:48:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000060 | PCM-20251026-00000130 | TT-20251025-01308 | Telecom | Region_4 | JD2 | JD2 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/26/2025 01:30:33 | 10/26/2025 01:30:33 | 10/26/2025 05:30:33 | SCECO :: LINK DOWN B/W HHR1-SEC0039-JD2_LH | 10/25/2025 15:19:35 | Critical | 1-12843 | OSC_LOS | 10/25/2025 15:19:23 | P1 | DWDM | jeddah | Sceco_STB | DWDM NSA | JD2 | FLM_TE |  |  | PCM-20251025-00001477 | will check after SEC team restore link between HHR1-SEC0039-JD2 | will check after SEC team restore link between HHR1-SEC0039-JD2 |  |  |  | API | 10/26/2025 01:30:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000061 | PCM-20251026-00000131 | TT-20251026-00093 | Reference_telecom | Region_6 | TNM0727 | TNM0727 |  |  |  | Fawad Khan | 10/26/2025 01:30:47 | 10/26/2025 08:41:48 | 10/26/2025 13:30:47 | ReplaceableUnitMissing observed in TNM0727_01 towards 10.221.247.84 @ Sceco | 10/25/2025 13:32:00 | Minor |  | ReplaceableUnitMissing | 10/25/2025 13:30:36 | P2 | 2G | mohail | Sceco | TX NSA | TNM0727 | FLM_TE | [8 empty] | API | 10/26/2025 01:30:47 | 10/26/2025 08:41:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000062 | PCM-20251026-00000132 | TT-20251025-01236 | Telecom | Region_2 | RIY2474 | RIY2474 | AutoRecovery | Clear_Before_Investigation | Auto Clear | DILSHAD ALI ABDUL HAMEED | 10/26/2025 01:32:06 | 10/26/2025 02:06:04 | 10/26/2025 07:32:06 | IN_PWR_HIGH ALARM AT RIY2474 | 10/25/2025 14:36:38 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/25/2025 14:36:38 | P2 | SRAN | riyadh | Sceco | DWDM NSA | RIY2474 | FLM_TE |  |  | PCM-20251025-00001506 | alarm stable cleared from long time , no need actions . | alarm stable cleared from long time , no need actions . |  |  |  | API | 10/26/2025 01:32:06 | 10/26/2025 01:49:39 | 10/26/2025 02:05:40 |  |  | 10/26/2025 02:06:04 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000064 | PCM-20251026-00000138 | TT-20251024-00648 | Telecom | Region_4 | JED0151(JD1) | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 01:37:29 | 10/26/2025 01:37:29 | 10/26/2025 07:37:29 | IN_PWR_LOW ALARM AT JED0151(JD1) | 10/24/2025 10:30:43 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/24/2025 10:30:43 | P1 | DWDM | jeddah | Sceco_STB_Rental | DWDM NSA | JED0151 | FLM_TE |  |  | PCM-20251024-00000592 | site now clear , no need actions from FLM side . | site now clear , no need actions from FLM side . |  |  |  | API | 10/26/2025 01:37:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000065 | PCM-20251026-00000148 | TT-20251026-00101 | EM | Region_4 | DGB2169 | DGB2169 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 01:43:58 | 10/26/2025 21:19:15 | 10/26/2025 07:43:58 | 1(2G/5G) sites down under DGB2169-P3/DGB2169-P3 @ Sceco | 10/26/2025 01:35:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 01:35:43 | P3 | 2G | alaith | Sceco | 2G SA | DGB2169-P3 | FLM_TE | DGB2169 | Results: DOWN SITE HUB DGB2169-P3 DGB2169 Summary: Hub: DGB2169, Down Count: 1, Down Sites: DGB2169-P3 Alarm Summary: DGB2169 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 01:43:58 | 10/26/2025 21:19:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251026000066 | PCM-20251026-00000150 | TT-20251026-00080 | EM | Region_3 | HAL0045 | HAL0045 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 01:46:13 | 10/26/2025 09:41:04 | 10/26/2025 07:46:13 | 1(2G/3G) sites down under HAL0045-P3/R3_HL_HWBSC01 @ Generator_SG | 10/26/2025 01:09:32 | Major | 21825 | CSL Fault | 10/26/2025 01:09:28 | P3 | SRAN | hail | Generator_SG | 2G_3G SA | HAL0045-P3 | FLM_TE | HAL0045 | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20251026-00000141 | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally |  | sites down |  | API | 10/26/2025 01:46:13 | 10/26/2025 09:34:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000067 | PCM-20251026-00000151 | TT-20251026-00111 | Reference_telecom | Region_6 | KMS0473 | KMS0473 | Transsmission | MW_HW_stuck | Reset ODU | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 01:49:54 | 10/26/2025 11:30:31 | 10/26/2025 13:49:54 | Degrade observed in KMS0473 towards 10.10.159.35 @ Sceco | 10/25/2025 13:51:33 | Minor |  | Degrade | 10/25/2025 13:49:27 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0473 | FLM_TE | [8 empty] | API | 10/26/2025 01:49:54 | 10/26/2025 03:55:18 | 10/26/2025 11:30:13 |  |  | 10/26/2025 11:30:31 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000068 | PCM-20251026-00000153 | TT-20251026-00112 | Reference_telecom | Region_6 | KMS0064 | KMS0064 | Transsmission | MW_HW_fault | Replace FAN | Muhammad shafiq Muhammad Rasheed | 10/26/2025 01:49:54 | 10/26/2025 15:46:59 | 10/26/2025 13:49:54 | ReplaceableUnitMissing observed in KMS0064 towards 10.10.159.34 @ Sceco | 10/25/2025 13:51:34 | Minor |  | ReplaceableUnitMissing | 10/25/2025 13:49:27 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KMS0064 | FLM_TE | [8 empty] | API | 10/26/2025 01:49:54 | 10/26/2025 10:36:06 | 10/26/2025 12:38:17 | 10/26/2025 12:38:20 | 10/26/2025 13:51:16 | 10/26/2025 15:46:59 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000071 | PCM-20251026-00000161 | TT-20251026-00122 | EM | Region_2 | RIY0298 | RIY0298 |  |  |  | Farhat Saeed Pirzada | 10/26/2025 01:56:05 | 10/26/2025 01:56:05 | 10/26/2025 05:56:05 | Door opening alarm at RIY0298-P1-Core-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 01:55:55 | Critical | 65101 | Door opening alarm | 10/26/2025 01:55:52 | P1 | SRAN | riyadh | Sceco_STB | 2G NSA | RIY0298 | FLM_EM | [8 empty] | API | 10/26/2025 01:56:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000072 | PCM-20251026-00000162 | TT-20251026-00123 | Telecom | Region_2 | RIY0399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Asad Ali Nadiq Khan | 10/26/2025 01:56:36 | 10/26/2025 10:54:28 | 10/26/2025 13:56:36 | RF Unit Maintenance Link Failure at RIY0399-P2_SRAN @ Sceco | 10/26/2025 01:54:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 01:51:19 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0399 | FLM_TE | [8 empty] | API | 10/26/2025 01:56:36 | 10/26/2025 08:12:29 | 10/26/2025 10:06:44 | 10/26/2025 10:07:03 | 10/26/2025 10:07:23 | 10/26/2025 10:54:28 |  | Asad Ali Nadiq Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000074 | PCM-20251026-00000166 | TT-20251025-01389 | Reference_telecom | Region_6 | JIZ0007 | JIZ0007 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/26/2025 01:58:26 | 10/26/2025 19:49:48 | 10/26/2025 13:58:26 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0007-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 14:04:11 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 14:02:22 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0007 | FLM_TE |  |  | PCM-20251026-00000116 | Observed node rebooted @ the same time of alarm occurrence | Observed node rebooted @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 01:58:26 | 10/26/2025 03:25:21 | 10/26/2025 19:49:39 |  |  | 10/26/2025 19:49:48 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000075 | PCM-20251026-00000169 | TT-20251025-00002 | Reference_telecom | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 02:01:10 | 10/26/2025 10:36:45 | 10/26/2025 14:01:10 | BASE STATION CONNECTIVITY PROBLEM (NR GTP-U Path Failure) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/24/2025 23:53:40 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/24/2025 23:53:30 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2259 | FLM_TE |  |  | PCM-20251026-00000110 | Observed related uplink was flapping & currently cleared | Observed related uplink was flapping & currently cleared |  |  |  | API | 10/26/2025 02:01:10 | 10/26/2025 10:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000076 | PCM-20251026-00000170 | TT-20251026-00131 | Reference_EM | Region_1 | KB2 | KB2 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/26/2025 02:01:46 | 10/26/2025 10:11:53 | 10/26/2025 08:01:46 | Door opening alarm at KB2-Main Shelter-Core-P1 @ Sceco_STB | 10/26/2025 02:01:35 | Major | 65101 | Door opening alarm | 10/26/2025 02:01:33 | P1 | DWDM | dammam | Sceco_STB | 2G NSA | KB2 | FLM_EM | [8 empty] | API | 10/26/2025 02:01:46 | 10/26/2025 10:11:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000077 | PCM-20251026-00000171 | TT-20251025-00340 | Reference_telecom | Region_4 | JED1M7783 | JED0783 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 02:01:46 | 10/26/2025 10:36:45 | 10/26/2025 08:01:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED1M7783-CA-L900-L800-SBTS @ Generator_SG | 10/25/2025 03:49:09 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 03:48:55 | P2 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7783 | FLM_TE |  |  | PCM-20251026-00000117 | Observed related uplink was flapping & currently cleared | Observed related uplink was flapping & currently cleared |  |  |  | API | 10/26/2025 02:01:46 | 10/26/2025 10:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000078 | PCM-20251026-00000172 | TT-20251026-00132 | EM | Region_4 | JZMA1M8202 | JZMA2202 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 02:02:51 | 10/26/2025 09:29:23 | 10/26/2025 14:02:51 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JZMA1M8202-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 01:54:34 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/26/2025 01:54:29 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8202 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/26/2025 02:02:51 | 10/26/2025 09:29:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000081 | PCM-20251026-00000175 | TT-20251025-01702 | Reference_telecom | Region_6 | JIZ1MT0168 | JIZ0168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/26/2025 02:04:19 | 10/26/2025 03:30:42 | 10/26/2025 08:04:19 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1MT0168-P3 @ Sceco | 10/25/2025 17:51:56 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 17:45:16 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1MT0168 | FLM_TE |  |  | PCM-20251026-00000122 | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 02:04:19 | 10/26/2025 03:29:29 | 10/26/2025 03:30:29 |  |  | 10/26/2025 03:30:42 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000082 | PCM-20251026-00000176 | TT-20251026-00136 | Telecom | Region_1 | HFF6028 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 02:04:21 | 10/26/2025 21:26:24 | 10/26/2025 14:04:21 | RF Unit Maintenance Link Failure at HFF6028-DCU1 @ Sceco | 10/26/2025 01:51:10 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 01:59:00 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/26/2025 02:04:21 | 10/26/2025 09:34:41 | 10/26/2025 21:26:11 |  |  | 10/26/2025 21:26:24 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000083 | PCM-20251026-00000177 | TT-20251025-01703 | Reference_telecom | Region_6 | JIZ1MT0244 | JIZ0244 | Transsmission | SFP_Transmission | Reset SFP | Zeshan Ali Adnan | 10/26/2025 02:05:03 | 10/26/2025 12:13:50 | 10/26/2025 06:05:03 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1MT0244-P1 @ Sceco | 10/25/2025 17:52:22 | Critical | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 17:45:32 | P1 | 4G | jizan | Sceco | LTE NSA | JIZ1MT0244 | FLM_TE |  |  | PCM-20251026-00000123 | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence | Observed node rebooted @ FE JIZ0243 @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 02:05:03 | 10/26/2025 11:51:07 | 10/26/2025 12:12:51 |  |  | 10/26/2025 12:13:50 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000084 | PCM-20251026-00000178 | TT-20251026-00137 | Telecom | Region_2 | RIY0399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Asad Ali Nadiq Khan | 10/26/2025 02:05:54 | 10/26/2025 10:57:41 | 10/26/2025 08:05:54 | BBU CPRI Interface Error at RIY0399-P2_SRAN @ Sceco | 10/26/2025 02:01:27 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 01:58:53 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0399 | FLM_TE | [8 empty] | API | 10/26/2025 02:05:54 | 10/26/2025 08:12:29 | 10/26/2025 10:57:09 | 10/26/2025 10:57:12 | 10/26/2025 10:57:15 | 10/26/2025 10:57:41 |  | Asad Ali Nadiq Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000085 | PCM-20251026-00000179 | TT-20251025-00108 | Reference_telecom | Region_6 | JIZ0296 | JIZ0296 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/26/2025 02:06:31 | 10/26/2025 03:30:03 | 10/26/2025 14:06:31 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0296-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/25/2025 01:08:24 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 00:03:17 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0296 | FLM_TE |  |  | PCM-20251026-00000121 | Observed node rebooted @ FE JIZ0100 @ the same time of alarm occurrence | Observed node rebooted @ FE JIZ0100 @ the same time of alarm occurrence |  |  |  | API | 10/26/2025 02:06:31 | 10/26/2025 03:29:30 | 10/26/2025 03:29:51 |  |  | 10/26/2025 03:30:03 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000086 | PCM-20251026-00000180 | TT-20251026-00140 | Reference_EM | Region_3 | SML2332 | SML2332 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 02:07:59 | 10/26/2025 02:07:59 | 10/26/2025 14:07:59 | Mains Failure at SML2332-P3-USF_SRAN @ Generator_SG | 10/26/2025 01:58:17 | Minor | 65109 | Mains Failure | 10/26/2025 01:58:12 | P3 | SRAN | hail | Generator_SG | 2G NSA | SML2332 | FLM_EM | [8 empty] | API | 10/26/2025 02:07:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000089 | PCM-20251026-00000184 | TT-20251026-00144 | Telecom | [7 empty] | 10/26/2025 02:11:36 | 10/26/2025 02:11:36 | 10/26/2025 14:11:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2608-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Generator_SG | 10/26/2025 02:10:46 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 02:10:38 | P3 | 2G |  | Generator_SG | 5G_Cell SA | JED2608 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 02:11:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000090 | PCM-20251026-00000185 | TT-20251026-00138 | Telecom | Region_4 | HHR0874 | HHR0874 |  |  |  | Khizer Hayat | 10/26/2025 02:11:59 | 10/26/2025 08:36:48 | 10/26/2025 06:11:59 | 1(5G) sites down under HHR0874-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/26/2025 02:03:32 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 02:03:30 | VIP | 2G | jeddah | Generator_SG | 5G SA | HHR0874-GSM-UMTS-P1-VIP-HHR | FLM_TE | HHR0874 | Results: DOWN SITE HUB HHR0874-GSM-UMTS-P1-VIP-HHR HHR0874 Summary: Hub: HHR0874, Down Count: 1, Down Sites: HHR0874-GSM-UMTS-P1-VIP-HHR Alarm Summary: HHR0874 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5443531 [ACTIVE] [URL:http://10.96.146.244:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 02:11:59 | 10/26/2025 08:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000091 | PCM-20251026-00000186 | TT-20251025-00488 | Reference_telecom | Region_5 | JDMK1M8406 | JDMK2406 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/26/2025 02:12:17 | 10/26/2025 02:12:17 | 10/26/2025 08:12:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JDMK1M8406-CA-P3 @ Generator_SG | 10/25/2025 05:53:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 05:53:15 | P3 | 4G | makkah | Generator_SG | LTE NSA | JDMK1M8406 | FLM_TE |  |  | PCM-20251026-00000118 | Observed node rebooted @ JDMK2406 @ the sane time of alarm occurrence | Observed node rebooted @ JDMK2406 @ the sane time of alarm occurrence |  |  |  | API | 10/26/2025 02:12:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000093 | PCM-20251026-00000188 | TT-20251026-00147 | Telecom | Region_1 | JBL-3459-NE40E-X3-P&PE-01 | JBL0459 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 02:13:09 | 10/26/2025 02:28:03 | 10/26/2025 06:13:09 | The Device is offline at JBL-3459-NE40E-X3-P&PE-01 @ Generator_DG | 10/26/2025 02:12:57 | Critical | 101-7 | The Device is offline | 10/26/2025 02:12:54 | P1 | IPRAN | jubail | Generator_DG | IPRAN SA | JBL-3459-NE40E-X3-P&PE-01 | FLM_TE | [8 empty] | API | 10/26/2025 02:13:09 | 10/26/2025 02:28:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000094 | PCM-20251026-00000191 | TT-20251025-00487 | Reference_telecom | Region_5 | MKJD1M9565 | MKJD0565 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 02:14:35 | 10/26/2025 02:14:35 | 10/26/2025 14:14:35 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MKJD1M9565-G9-L8-L18-L21-SBTS-P2 @ Generator_SG | 10/25/2025 05:53:21 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 05:53:11 | P2 | 4G | makkah | Generator_SG | LTE NSA | MKJD1M9565 | FLM_TE |  |  | PCM-20251026-00000124 | Observed node rebooted @ MKJD0565 @ the sane time of alarm occurrence | Observed node rebooted @ MKJD0565 @ the sane time of alarm occurrence |  |  |  | API | 10/26/2025 02:14:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000096 | PCM-20251026-00000193 | TT-20251026-00142 | EM | Region_4 | JZMA2202 | JZMA2202 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 02:14:59 | 10/26/2025 09:29:24 | 10/26/2025 08:14:59 | 1(2G/LTE) sites down under JZMA2202-P3/JZMA2202-P3 @ Generator_SG | 10/26/2025 02:07:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:07:02 | P3 | 2G | jeddah | Generator_SG | 2G_LTE SA | JZMA2202-P3 | FLM_EM | JZMA2202 | Results: DOWN SITE HUB JZMA2202-P3 JZMA2202 Summary: Hub: JZMA2202, Down Count: 1, Down Sites: JZMA2202-P3 Alarm Summary: JZMA2202 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:14:59 | 10/26/2025 09:29:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000097 | PCM-20251026-00000194 | TT-20251025-01625 | Reference_telecom | Region_6 | BHMF1M7856 | BHMF0856 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/26/2025 02:16:41 | 10/26/2025 10:22:04 | 10/26/2025 14:16:41 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHMF1M7856-G9-L8-L18-SBTS-P3 @ Sceco | 10/25/2025 16:27:29 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 16:22:27 | P3 | 4G | makhwa | Sceco | LTE NSA | BHMF1M7856 | FLM_TE |  |  | PCM-20251026-00000114 | Thanks to rectify related link BHMF0856-BHMF0859 | Thanks to rectify related link BHMF0856-BHMF0859 |  |  |  | API | 10/26/2025 02:16:41 | 10/26/2025 10:20:13 | 10/26/2025 10:21:41 |  |  | 10/26/2025 10:22:04 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000098 | PCM-20251026-00000196 | TT-20251026-00157 | EM | Region_2 | R2_RY4_HWBSC01 | RY4 |  |  |  | Farhat Saeed Pirzada | 10/26/2025 02:18:20 | 10/26/2025 02:18:20 | 10/26/2025 06:18:20 | Intruder Alarm SH1 EQ R at R2_RY4_HWBSC01 @ Sceco_STB | 10/26/2025 02:17:53 | Critical | 65349 | Intruder Alarm SH1 EQ R | 10/26/2025 02:17:48 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY4_HWBSC01 | FLM_EM | [8 empty] | API | 10/26/2025 02:18:20 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000099 | PCM-20251026-00000197 | TT-20251026-00159 | EM | Region_3 | MDTB2547 | MDTB2547 |  |  |  | Mohammed Sadeq Nawaz | 10/26/2025 02:21:55 | 10/26/2025 02:21:55 | 10/26/2025 14:21:55 | NETECO: Communication Fail at MDTB2547 @ Generator_DG | 10/26/2025 02:15:47 | Minor | 20001 | Communication Fail | 10/26/2025 02:15:47 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDTB2547 | FLM_EM | [8 empty] | API | 10/26/2025 02:21:55 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000102 | PCM-20251026-00000204 | TT-20251026-00126 | Reference_telecom | Region_4 | JED1M8986 | JED2986 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 02:25:31 | 10/26/2025 10:36:45 | 10/26/2025 08:25:31 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at JED1M8986-CA-L800-P3 @ Generator_SG | 10/26/2025 01:56:29 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 03:04:31 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8986 | FLM_TE |  |  | PCM-20251026-00000165 | Please close the alarm during site down | Please close the alarm during site down |  |  |  | API | 10/26/2025 02:25:31 | 10/26/2025 10:36:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000103 | PCM-20251026-00000205 | TT-20251026-00114 | Reference_telecom | Region_4 | HAW0300 | HAW0300 |  |  |  | Rashid Shafique | 10/26/2025 02:26:25 | 10/26/2025 14:51:23 | 10/26/2025 14:26:25 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at HAW0300-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/26/2025 01:46:32 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 01:46:23 | P2 | 2G | taif | Generator_SG | 5G_Cell SA | HAW0300 | FLM_TE |  |  | PCM-20251026-00000155 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/26/2025 02:26:25 | 10/26/2025 14:51:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000104 | PCM-20251026-00000208 | TT-20251026-00167 | Telecom | Region_4 | JED1M7312 | JED0312 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 02:28:19 | 10/26/2025 06:09:03 | 10/26/2025 08:28:19 | BASE STATION ANTENNA LINE PROBLEM at JED1M7312-CA-L900-L800-SBTS @ Sceco | 10/26/2025 02:19:48 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 02:19:44 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7312 | FLM_TE |  |  | PCM-20251026-00000207 | kindly support to perform HC,check sfp cable connector connected RMOD | kindly support to perform HC,check sfp cable connector connected RMOD |  |  |  | API | 10/26/2025 02:28:19 | 10/26/2025 06:09:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000105 | PCM-20251026-00000214 | TT-20251026-00181 | Reference_telecom | Region_4 | MKMD0563 | MKMD0563 |  |  |  | Khizer Hayat | 10/26/2025 02:36:23 | 10/26/2025 08:36:49 | 10/26/2025 14:36:23 | DemFail observed in MKMD0563_02 towards 10.3.235.3 @ Sceco_STB | 10/25/2025 14:38:12 | Minor |  | DemFail | 10/25/2025 14:36:05 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKMD0563 | FLM_TE | [8 empty] | API | 10/26/2025 02:36:23 | 10/26/2025 08:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000106 | PCM-20251026-00000215 | TT-20251026-00173 | EM | Region_4 | MKYL0913 | MKYL0913 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/26/2025 02:37:59 | 10/26/2025 11:45:20 | 10/26/2025 08:37:59 | 1(2G/3G/5G) sites down under MKYL0913-P2/MKYL0913-P2 @ Generator_SG | 10/26/2025 02:30:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:30:07 | P2 | 2G | alaith | Generator_SG | 2G_3G SA | MKYL0913-P2 | FLM_EM | MKYL0913 | Results: DOWN SITE HUB MKYL0913-P2 MKYL0913 Summary: Hub: MKYL0913, Down Count: 1, Down Sites: MKYL0913-P2 Alarm Summary: MKYL0913 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:37:59 | 10/26/2025 11:45:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000107 | PCM-20251026-00000216 | TT-20251026-00174 | EM | Region_4 | MKYL0912 | MKYL0912 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/26/2025 02:38:01 | 10/26/2025 14:26:22 | 10/26/2025 08:38:01 | 1(2G/3G) sites down under MKYL0912-P2/MKYL0912-P2 @ Generator_SG | 10/26/2025 02:30:13 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:30:06 | P2 | 2G | makkah | Generator_SG | 2G_3G SA | MKYL0912-P2 | FLM_EM | MKYL0912 | Results: DOWN SITE HUB MKYL0912-P2 MKYL0912 Summary: Hub: MKYL0912, Down Count: 1, Down Sites: MKYL0912-P2 Alarm Summary: MKYL0912 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:38:01 | 10/26/2025 14:26:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000108 | PCM-20251026-00000217 | TT-20251026-00116 | Reference_telecom | Region_4 | MLJI1M3205 | MLJI0205 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 02:38:15 | 10/27/2025 03:32:41 | 10/26/2025 08:38:15 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at MLJI1M3205-P2-USF @ Generator_SG | 10/26/2025 01:23:13 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 01:21:02 | P2 | 3G | alaith | Generator_SG | 3G SA | MLJI1M3205 | FLM_TE |  |  | PCM-20251026-00000154 | Please check the site is down | Please check the site is down |  |  |  | API | 10/26/2025 02:38:15 | 10/26/2025 09:54:23 | 10/27/2025 03:32:29 |  |  | 10/27/2025 03:32:41 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000109 | PCM-20251026-00000218 | TT-20251026-00182 | Telecom | Region_4 | JZMA2421 | JZMA2421 |  |  |  | Khizer Hayat | 10/26/2025 02:42:29 | 10/26/2025 08:36:49 | 10/26/2025 08:42:29 | 1(2G) sites down under JZMA2421-P3/JZMA2421-P3 @ Generator_SG | 10/26/2025 02:34:06 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 02:34:01 | P3 | 2G | jeddah | Generator_SG | 2G SA | JZMA2421-P3 | FLM_TE | JZMA2421 | Results: DOWN SITE HUB JZMA2421-P3 JZMA2421 Summary: Hub: JZMA2421, Down Count: 1, Down Sites: JZMA2421-P3 Alarm Summary: JZMA2421 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 02:42:29 | 10/26/2025 08:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000110 | PCM-20251026-00000220 | TT-20251026-00185 | Telecom | Region_5 | HAJ0011 | HAJ0011 |  |  |  | Muhammad Saleem Iqbal | 10/26/2025 02:44:08 | 10/26/2025 05:13:16 | 10/26/2025 14:44:08 | RF Unit CPRI Interface Error at HAJ0011-P3_SRAN @ Sceco | 10/26/2025 02:38:46 | Minor | 26504 | RF Unit CPRI Interface Error | 10/26/2025 02:37:12 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ0011 | FLM_TE | [8 empty] | API | 10/26/2025 02:44:08 | 10/26/2025 05:13:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000112 | PCM-20251026-00000223 | TT-20251026-00189 | Reference_telecom | Region_4 | MKMD0557 | MKMD0557 |  |  |  | Khizer Hayat | 10/26/2025 02:49:18 | 10/26/2025 08:36:50 | 10/26/2025 14:49:18 | ReplaceableUnitProblem observed in MKMD0557 towards 10.3.235.4 @ Sceco_STB | 10/25/2025 14:49:37 | Minor |  | ReplaceableUnitProblem | 10/25/2025 14:49:11 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKMD0557 | FLM_TE | [8 empty] | API | 10/26/2025 02:49:18 | 10/26/2025 08:36:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000113 | PCM-20251026-00000225 | TT-20251026-00191 | Telecom | Region_6 | JIZ1M7092 | JIZ0092 | Equipment | BSS_HW_Stuck | Reset Air Scale | Osama Hadi | 10/26/2025 02:49:19 | 10/26/2025 05:12:05 | 10/26/2025 08:49:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ1M7092-G9-L8-L18-L21-SBTS-P1-HUB @ Sceco_STB | 10/26/2025 02:48:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 02:48:13 | P1 | 4G | jizan | Sceco_STB | 5G_Cell SA | JIZ1M7092 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 02:49:19 | 10/26/2025 03:25:22 | 10/26/2025 05:02:19 |  |  | 10/26/2025 05:12:05 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000116 | PCM-20251026-00000233 | TT-20251026-00201 | Telecom | Region_4 | JED2001 | JED2001 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 03:02:45 | 10/26/2025 03:02:45 | 10/26/2025 15:02:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2001-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/26/2025 03:02:08 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:01:58 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2001 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 03:02:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000118 | PCM-20251026-00000239 | TT-20251026-00204 | Telecom | Region_6 | BSA2308 | BSA2308 |  |  |  | Asad Saddiq | 10/26/2025 03:13:00 | 10/26/2025 07:20:14 | 10/26/2025 09:13:00 | 4(2G/LTE) sites down under BSA2308-P3,BSA2303-P3,BSA2305-P3,BSA2315-P3 @ Generator_SG | 10/26/2025 03:04:35 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:04:28 | P3 | 2G | bisha | Generator_SG | 2G_LTE SA | BSA2308-P3 | FLM_EM | BSA2308 | Results: DOWN SITE HUB BSA2308-P3 BSA2308 Summary: Hub: BSA2308, Down Count: 1, Down Sites: BSA2308-P3 Alarm Summary: BSA2308 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 03:13:00 | 10/26/2025 07:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000119 | PCM-20251026-00000241 | TT-20251026-00216 | Telecom | Region_4 | JED1-PE | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/26/2025 03:17:13 | 10/26/2025 03:17:13 | 10/26/2025 15:17:13 | Chassis Fail at JED1-PE @ Sceco_STB | 10/26/2025 03:16:37 | Minor | 101-2505202 | Chassis Fail | 10/26/2025 03:16:33 | P1 | IPBB | jeddah | Sceco_STB | IPRAN NSA | JED1-PE | FLM_TE | [8 empty] | API | 10/26/2025 03:17:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000120 | PCM-20251026-00000243 | TT-20251026-00220 | Telecom | Region_5 | MAK1M8523 | MAK2523 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 03:19:17 | 10/26/2025 03:19:17 | 10/26/2025 09:19:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M8523-CA-L800-P3 @ Sceco | 10/26/2025 03:18:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:18:10 | P3 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M8523 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 03:19:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000122 | PCM-20251026-00000245 | TT-20251026-00221 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace CB on Rectifier | DILSHAD ALI ABDUL HAMEED | 10/26/2025 03:20:50 | 10/26/2025 07:12:04 | 10/26/2025 15:20:50 | RF Unit Maintenance Link Failure at RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 03:17:00 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 03:15:17 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0964 | FLM_TE | [8 empty] | API | 10/26/2025 03:20:50 | 10/26/2025 07:08:06 | 10/26/2025 07:11:33 |  |  | 10/26/2025 07:12:04 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000123 | PCM-20251026-00000248 | TT-20251026-00226 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace CB on Rectifier | DILSHAD ALI ABDUL HAMEED | 10/26/2025 03:23:25 | 10/26/2025 07:12:37 | 10/26/2025 15:23:25 | NR DU Cell TRP Unavailable at RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 03:16:51 | Minor | 29870 | NR DU Cell TRP Unavailable | 10/26/2025 03:15:19 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0964 | FLM_TE | [8 empty] | API | 10/26/2025 03:23:25 | 10/26/2025 07:07:55 | 10/26/2025 07:12:10 |  |  | 10/26/2025 07:12:37 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000124 | PCM-20251026-00000249 | TT-20251026-00217 | Telecom | Region_2 | RIY0964 | RIY0964 | Equipment | CB_BTS | Replace DCDU Fuse | DILSHAD ALI ABDUL HAMEED | 10/26/2025 03:23:29 | 10/26/2025 06:20:06 | 10/26/2025 07:23:29 | 1(5G) sites down under RIY0964-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 03:16:51 | Critical | 29840 | gNodeB Out of Service | 10/26/2025 03:15:19 | VIP | SRAN | riyadh | Sceco | 5G SA | RIY0964-P1-PNU-VIP_SRAN | FLM_TE | RIY0964 | Results: DOWN SITE HUB RIY0964-P1-PNU-VIP_SRAN RIY0964 Summary: Hub: RIY0964, Down Count: 1, Down Sites: RIY0964-P1-PNU-VIP_SRAN Alarm Summary: RIY0964 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 03:23:29 | 10/26/2025 05:23:30 | 10/26/2025 05:30:45 | 10/26/2025 05:30:48 | 10/26/2025 06:00:20 | 10/26/2025 06:20:06 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000126 | PCM-20251026-00000255 | TT-20251026-00233 | EM | Region_3 | RUSF9013 | RUSF9013 |  |  |  | Yasser Mohamed Mohamed Yousef | 10/26/2025 03:25:58 | 10/26/2025 03:25:58 | 10/26/2025 07:25:58 | RELAY_ALARM_MAJOR at RUSF9013_NE_1 @ Generator_SG | 10/26/2025 03:24:14 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/26/2025 03:24:02 | P3 | Repeater | yanbu | Generator_SG | TX NSA | RUSF9013 | FLM_EM | [8 empty] | API | 10/26/2025 03:25:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000127 | PCM-20251026-00000256 | TT-20251026-00234 | Reference_telecom | Region_4 | JED1M7564 | JED0564 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 03:25:59 | 10/26/2025 13:19:20 | 10/26/2025 09:25:59 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7564-P1-VIP-CA-L900-L800-SBTS @ Generator_SG | 10/26/2025 03:21:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:21:07 | VIP | 4G | jeddah | Generator_SG | LTE_Cell SA | JED1M7564 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/26/2025 03:25:59 | 10/26/2025 13:19:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000129 | PCM-20251026-00000260 | TT-20251026-00238 | Telecom | Region_2 | RIY0785 | RIY0785 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/26/2025 03:28:34 | 10/26/2025 06:22:55 | 10/26/2025 15:28:34 | RF Unit Maintenance Link Failure at RIY0785-P2_SRAN @ Sceco | 10/26/2025 03:23:41 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 03:23:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0785 | FLM_TE | [8 empty] | API | 10/26/2025 03:28:34 | 10/26/2025 06:22:17 | 10/26/2025 06:22:25 | 10/26/2025 06:22:27 | 10/26/2025 06:22:29 | 10/26/2025 06:22:55 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000130 | PCM-20251026-00000261 | TT-20251026-00239 | Telecom | Region_2 | RIY2M7785 | RIY0785 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/26/2025 03:28:46 | 10/26/2025 06:17:42 | 10/26/2025 09:28:46 | Cell Unavailable at RIY2M7785-P2-L800-L900 @ Sceco | 10/26/2025 03:26:07 | Major | 29240 | Cell Unavailable | 10/26/2025 03:25:41 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7785 | FLM_TE | [8 empty] | API | 10/26/2025 03:28:46 | 10/26/2025 05:24:28 | 10/26/2025 05:27:04 | 10/26/2025 05:50:40 | 10/26/2025 05:53:02 | 10/26/2025 06:17:42 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000131 | PCM-20251026-00000262 | TT-20251026-00194 | Reference_telecom | Region_4 | JED1M7572 | JED0572 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 03:29:12 | 10/26/2025 15:44:33 | 10/26/2025 09:29:12 | Fronthaul loop back connectivity check failure at JED1M7572-P1-DIA-CA-L900-L800-SBTS @ Sceco | 10/26/2025 02:24:06 | Major | 61009 | Fronthaul loop back connectivity check failure | 10/26/2025 02:23:59 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7572 | FLM_TE |  |  | PCM-20251026-00000228 | kindly support to perform HC,check sfp cable connector connected RMOD | kindly support to perform HC,check sfp cable connector connected RMOD |  |  |  | API | 10/26/2025 03:29:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000132 | PCM-20251026-00000263 | TT-20251026-00232 | EM | Region_2 | RYQS2M2575 | RYQS2575 |  |  |  | Asim Mushtaq Mushtaq Ahmad | 10/26/2025 03:29:29 | 10/26/2025 11:14:53 | 10/26/2025 09:29:29 | 1(2G/3G/LTE) sites down under RYQS2575-P2/RY1BSCH02 @ Generator_SG | 10/26/2025 03:22:28 | Major | 21825 | CSL Fault | 10/26/2025 03:22:27 | P2 | 2G | rumah | Generator_SG | 2G_3G_LTE SA | RYQS2575-P2 | FLM_EM | RYQS2575 | Results: DOWN SITE HUB RYQS2575-P2 RYQS2575 Summary: Hub: RYQS2575, Down Count: 1, Down Sites: RYQS2575-P2 Alarm Summary: RYQS2575 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 03:29:29 | 10/26/2025 11:14:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000133 | PCM-20251026-00000264 | TT-20251026-00186 | Reference_telecom | Region_6 | BCH0080 | BCH0080 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 03:30:44 | 10/26/2025 10:54:42 | 10/26/2025 15:30:44 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at BCH0080-G9-NL8-L9-NL18-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 02:41:10 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 02:41:01 | P3 | 2G | Albaha | Sceco | 5G_Cell SA | BCH0080 | FLM_TE |  |  | PCM-20251026-00000221 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 03:30:44 | 10/26/2025 10:52:38 | 10/26/2025 10:54:28 |  |  | 10/26/2025 10:54:42 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000134 | PCM-20251026-00000270 | TT-20251026-00249 | Reference_EM | Region_2 | RIY2977 | RIY2977 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 03:33:14 | 10/26/2025 09:36:34 | 10/26/2025 15:33:14 | Minor Rec alarm at RIY2977-P3_SRAN-PC @ Sceco | 10/26/2025 03:23:12 | Minor | 65108 | Minor Rec alarm | 10/26/2025 03:23:09 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2977 | FLM_EM | [8 empty] | API | 10/26/2025 03:33:14 | 10/26/2025 09:36:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000135 | PCM-20251026-00000271 | TT-20251026-00180 | Reference_telecom | Region_6 | WDS2498 | WDS2498 | Equipment | BSS_HW_Stuck | Reset Air Scale | Ahmed Mamdouh Helal Helal | 10/26/2025 03:33:31 | 10/26/2025 23:01:10 | 10/26/2025 15:33:31 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at WDS2498-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Generator_SG | 10/26/2025 02:05:49 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 02:05:42 | P3 | 2G | wadi dawasar | Generator_SG | 2G NSA | WDS2498 | FLM_TE |  |  | PCM-20251026-00000213 | HW alarm flapping at site,FLM need to restore | HW alarm flapping at site,FLM need to restore |  |  |  | API | 10/26/2025 03:33:31 | 10/26/2025 11:10:50 | 10/26/2025 23:00:55 |  |  | 10/26/2025 23:01:10 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000136 | PCM-20251026-00000272 | TT-20251026-00253 | EM | Region_6 | HJR1M7027 | HJR0027 |  |  |  | Arif Ullah Shah | 10/26/2025 03:36:19 | 10/26/2025 03:49:05 | 10/26/2025 15:36:19 | AIRCON 2 FAILURE at HJR1M7027-P3-L800 @ Sceco | 10/26/2025 03:28:21 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 03:28:15 | P3 | 4G | makhwa | Sceco | LTE NSA | HJR1M7027 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 03:36:19 | 10/26/2025 03:49:05 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000137 | PCM-20251026-00000275 | TT-20251026-00254 | EM | Region_6 | UKHA1M8363 | UKHA2363 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 03:37:21 | 10/26/2025 06:55:22 | 10/26/2025 15:37:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at UKHA1M8363-G9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 03:28:59 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/26/2025 03:28:53 | P3 | 4G | Baha | Sceco | LTE NSA | UKHA1M8363 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/26/2025 03:37:21 | 10/26/2025 06:55:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000138 | PCM-20251026-00000276 | TT-20251026-00251 | Telecom | Region_4 | YLM1M7876 | YLM0876 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 03:39:29 | 10/26/2025 21:19:16 | 10/26/2025 07:39:29 | 1(LTE) sites down under YLM0876-L800-SBTS-P1 @ Generator_DG | 10/26/2025 03:31:27 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 03:31:24 | P1 | 4G | alaith | Generator_DG | LTE SA | YLM0876-L800-SBTS-P1 | FLM_TE |  | Results: DOWN SITE HUB YLM0876-L800-SBTS-P1 Need to check Summary: Alarm Summary: HUB site not found |  |  |  | Timeout connecting to [/10.88.39.44:8080] [URL:http://10.88.39.44:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 03:39:29 | 10/26/2025 21:19:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000139 | PCM-20251026-00000278 | TT-20251026-00255 | Reference_EM | [7 empty] | 10/26/2025 03:40:26 | 10/26/2025 03:40:26 | 10/26/2025 15:40:26 | Mains Failure at RIYB6055-P3_SRAN @ Sceco | 10/26/2025 03:33:18 | Minor | 65109 | Mains Failure | 10/26/2025 03:30:35 | P3 | SRAN |  | Sceco | 2G NSA | RIYB6055 | FLM_EM | [8 empty] | API | 10/26/2025 03:40:26 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000141 | PCM-20251026-00000280 | TT-20251026-00245 | Telecom | Region_6 | SRA2359 | SRA2359 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 03:42:30 | 10/26/2025 09:44:44 | 10/26/2025 09:42:30 | 4(2G) 4(LTE) sites down under SRA2355-P3,MTB2377-P3,SRA2359-P3,QLW2372-P3/QLW2372-P3 @ Generator_SG | 10/26/2025 03:28:53 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:28:50 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2355-P3 2G_LTE,MTB2377-P3 2G_LTE,SRA2359-P3 2G_LTE,QLW2372-P3 2G_LTE | FLM_EM | SRA2359 | Results: DOWN SITE HUB SRA2355-P3 SRA2355 MTB2377-P3 MTB2377 SRA2359-P3 SRA2359 QLW2372-P3 QLW2372 Summary: Hub: SRA2355, Down Count: 1, Down Sites: SRA2355-P3 Hub: MTB2377, Down Count: 1, Down Sites: MTB2377-P3 Hub: SRA2359, Down Count: 1, Down Sites: SRA2359-P3 Hub: QLW2372, Down Count: 1, Down Sites: QLW2372-P3 Alarm Summary: SRA2355 No Active Alarm on HUB MTB2377 No Active Alarm on HUB SRA2359 Alarm Active on HUB QLW2372 Alarm Active on HUB | PCM-20251026-00000274 | SRA2359 | SRA2359 |  | sites down |  | API | 10/26/2025 03:42:30 | 10/26/2025 09:44:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000143 | PCM-20251026-00000284 | TT-20251025-01891 | Telecom | Region_1 | ARM2759 | ARM2759 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 03:45:10 | 10/26/2025 05:10:59 | 10/26/2025 07:45:10 | 1(LTE) sites down under ARM2759-P1_SRAN-PC @ Power Cube | 10/25/2025 23:07:25 | Critical | 301 | NE Is Disconnected | 10/25/2025 23:07:22 | P1 | SRAN | jubail | Power Cube | LTE SA | ARM2759-P1_SRAN-PC | FLM_TE | ARM2759 | Results: DOWN SITE HUB ARM2759-P1_SRAN-PC ARM2759 Summary: Hub: ARM2759, Down Count: 1, Down Sites: ARM2759-P1_SRAN-PC Alarm Summary: ARM2759 No Active Alarm on HUB | PCM-20251026-00000106 | Kindly need HC on link JBKH0095-ARM2759 as bad performance ,RSL degradation exist during this time | Kindly need HC on link JBKH0095-ARM2759 as bad performance ,RSL degradation exist during this time |  | sites down |  | API | 10/26/2025 03:45:10 | 10/26/2025 05:10:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000144 | PCM-20251026-00000285 | TT-20251026-00163 | Telecom | Region_6 | TNM0176 | TNM0176 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Fawad Khan | 10/26/2025 03:46:16 | 10/26/2025 08:54:37 | 10/26/2025 15:46:16 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at TNM0176-G9-L8-L18-NL21-NNR2.6-SBTS-P3 @ Sceco | 10/26/2025 02:19:06 | Minor | 7114 | CELL SERVICE PROBLEM | 10/26/2025 02:19:01 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNM0176 | FLM_TE |  |  | PCM-20251026-00000200 | Please perform the HC for Cell-B and C have sleeping cell issue | Please perform the HC for Cell-B and C have sleeping cell issue |  |  |  | API | 10/26/2025 03:46:16 | 10/26/2025 08:41:49 | 10/26/2025 08:53:57 |  |  | 10/26/2025 08:54:37 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000145 | PCM-20251026-00000287 | TT-20251026-00260 | EM | Region_3 | RUSF9012 | RUSF9012 |  |  |  | Muhammad Imran Muhammad Aslam | 10/26/2025 03:48:43 | 10/26/2025 23:52:29 | 10/26/2025 15:48:43 | NETECO: Communication Fail at RUSF9012 @ Generator_SG | 10/26/2025 03:42:19 | Minor | 20001 | Communication Fail | 10/26/2025 03:42:19 | P3 | Repeater | madinah | Generator_SG | 2G NSA | RUSF9012 | FLM_EM | [8 empty] | API | 10/26/2025 03:48:43 | 10/26/2025 23:52:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000146 | PCM-20251026-00000290 | TT-20251026-00055 | Reference_telecom | Region_6 | KHNJ1M8241 | KHNJ2241 | Equipment | BSS_HW_fault | Replace RF Module | Bilal Anwar Khurshid Anwar | 10/26/2025 03:53:59 | 10/26/2025 17:41:40 | 10/26/2025 15:53:59 | BASE STATION SERVICE PROBLEM (TX out of order) at KHNJ1M8241-CA-L800-P3-SBTS @ Sceco | 10/26/2025 00:45:18 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 00:45:08 | P3 | 4G | al harja | Sceco | LTE_Cell SA | KHNJ1M8241 | FLM_TE |  |  | PCM-20251026-00000269 | Please update once change the HW | Please update once change the HW |  |  |  | API | 10/26/2025 03:53:59 | 10/26/2025 04:02:32 | 10/26/2025 15:11:14 | 10/26/2025 15:11:33 | 10/26/2025 16:02:06 | 10/26/2025 17:41:40 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000147 | PCM-20251026-00000292 | TT-20251026-00261 | Telecom | Region_4 | SDY0763 | SDY0763 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 03:54:59 | 10/26/2025 21:19:17 | 10/26/2025 09:54:59 | 1(5G) sites down under SDY0763-GSM-UMTS-P3 @ Generator_DG | 10/26/2025 03:46:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 03:46:54 | P3 | 2G | alaith | Generator_DG | 5G SA | SDY0763-GSM-UMTS-P3 | FLM_TE | SDY0763 | Results: DOWN SITE HUB SDY0763-GSM-UMTS-P3 SDY0763 Summary: Hub: SDY0763, Down Count: 1, Down Sites: SDY0763-GSM-UMTS-P3 Alarm Summary: SDY0763 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.9.44:8080] [URL:http://10.88.9.44:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 03:54:59 | 10/26/2025 21:19:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000148 | PCM-20251026-00000294 | TT-20251026-00218 | Telecom | Region_5 | MAK2706 | MAK2706 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/26/2025 03:56:31 | 10/26/2025 03:56:31 | 10/26/2025 09:56:31 | 1(2G) sites down under MAK2706-P3/MAK2706-P3 @ Generator_SG | 10/26/2025 03:15:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:15:40 | P3 | 2G | makkah | Generator_SG | 2G SA | MAK2706-P3 | FLM_TE | MAK2706 | Results: DOWN SITE HUB MAK2706-P3 MAK2706 Summary: Hub: MAK2706, Down Count: 1, Down Sites: MAK2706-P3 Alarm Summary: MAK2706 No Active Alarm on HUB | PCM-20251026-00000258 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 03:56:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000149 | PCM-20251026-00000295 | TT-20251026-00267 | EM | Region_3 | R3_MD_HWBSC02 | MD2 | Equipment | BSS_HW_Stuck | Reset Air Scale | Essam Aboulfadil | 10/26/2025 03:57:30 | 10/26/2025 04:48:27 | 10/26/2025 07:57:30 | Air-Condition #2 FA(SH2) at R3_MD_HWBSC02 @ Sceco_STB | 10/26/2025 03:57:16 | Critical | 65353 | Air-Condition #2 FA(SH2) | 10/26/2025 03:57:11 | P1 | BSC | madinah | Sceco_STB | 2G NSA | R3_MD_HWBSC02 | FLM_EM | [8 empty] | API | 10/26/2025 03:57:30 | 10/26/2025 04:14:41 | 10/26/2025 04:14:51 | 10/26/2025 04:14:54 | 10/26/2025 04:18:26 | 10/26/2025 04:48:27 |  | Essam Aboulfadil |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000151 | PCM-20251026-00000297 | TT-20251026-00193 | Reference_telecom | Region_4 | SDY1M3738 | SDY0738 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 03:59:09 | 10/26/2025 21:19:18 | 10/26/2025 09:59:09 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at SDY1M3738-P3 @ Sceco_STB | 10/26/2025 02:25:09 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 02:22:59 | P3 | 3G | alaith | Sceco_STB | 3G SA | SDY1M3738 | FLM_TE |  |  | PCM-20251026-00000226 | Please perform the multiple HW issue | Please perform the multiple HW issue |  |  |  | API | 10/26/2025 03:59:09 | 10/26/2025 21:19:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000156 | PCM-20251026-00000314 | TT-20251026-00288 | Reference_EM | Region_3 | SML2332 | SML2332 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 04:22:47 | 10/26/2025 04:22:47 | 10/26/2025 16:22:47 | Door opening alarm at SML2332-P3-USF_SRAN @ Generator_SG | 10/26/2025 04:22:29 | Minor | 65101 | Door opening alarm | 10/26/2025 04:22:27 | P3 | SRAN | hail | Generator_SG | 2G NSA | SML2332 | FLM_EM | [8 empty] | API | 10/26/2025 04:22:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000157 | PCM-20251026-00000318 | TT-20251026-00258 | Telecom | Region_4 | KMMD0722 | KMMD0722 |  |  |  | Nazeer Mohammed | 10/26/2025 04:24:28 | 10/26/2025 12:23:06 | 10/26/2025 08:24:28 | 5(5G) sites down under KMMD0639-GSM-P2 @ Sceco | 10/26/2025 03:41:26 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 03:41:24 | P1 | 2G | jeddah | Sceco_STB | 5G SA | KMMD0639-GSM-P2 5G,KMMD0754-GSM-P3 5G,KMMD0726-GSM-P3 5G,KMMD0722-GSM-P1-HUB 5G,KMMD0637-GSM-P3 5G | FLM_TE | KMMD0722 | Results: DOWN SITE HUB KMMD0639-GSM-P2 KMMD0639 KMMD0754-GSM-P3 KMMD0754 KMMD0726-GSM-P3 Need to check KMMD0722-GSM-P1-HUB Need to check KMMD0637-GSM-P3 Need to check Summary: Hub: KMMD0639, Down Count: 1, Down Sites: KMMD0639-GSM-P2 Hub: KMMD0754, Down Count: 1, Down Sites: KMMD0754-GSM-P3 Alarm Summary: KMMD0639 No Active Alarm on HUB KMMD0754 No Active Alarm on HUB HUB site not found | PCM-20251026-00000307 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 04:24:28 | 10/26/2025 12:23:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000158 | PCM-20251026-00000321 | TT-20251026-00296 | Reference_telecom | Region_4 | JED0056 | JED0056 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | 10/26/2025 16:25:22 | LossOfSignal observed in JED0056 towards 10.10.146.248 @ Sceco | 10/25/2025 16:26:25 | Minor |  | LossOfSignal | 10/25/2025 16:25:03 | P3 | 2G | jeddah | Sceco | TX NSA | JED0056 | FLM_TE | [8 empty] | API | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000159 | PCM-20251026-00000320 | TT-20251026-00295 | Reference_telecom | Region_4 | JED0899 | JED0899 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | 10/26/2025 16:25:22 | Degrade observed in JED0899_SH04 towards 10.10.146.247 @ Generator_SG | 10/25/2025 16:26:25 | Minor |  | Degrade | 10/25/2025 16:25:02 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0899 | FLM_TE | [8 empty] | API | 10/26/2025 04:25:22 | 10/26/2025 10:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000161 | PCM-20251026-00000324 | TT-20251026-00298 | Telecom | Region_6 | BSH1M7201 | BSH0201 | Equipment | CB_BTS | Replace CB on Rectifier | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 04:31:29 | 10/26/2025 11:05:25 | 10/26/2025 10:31:29 | 1(LTE) sites down under BSH0201-P3-CA-L800 @ Sceco | 10/26/2025 04:23:28 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 04:23:25 | P3 | 4G | baish | Sceco | LTE SA | BSH0201-P3-CA-L800 | FLM_TE | BSH0201 | Results: DOWN SITE HUB BSH0201-P3-CA-L800 BSH0201 Summary: Hub: BSH0201, Down Count: 1, Down Sites: BSH0201-P3-CA-L800 Alarm Summary: BSH0201 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.103.47.228:8080] [URL:http://10.103.47.228:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 04:31:29 | 10/26/2025 11:04:25 | 10/26/2025 11:05:12 |  |  | 10/26/2025 11:05:25 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000162 | PCM-20251026-00000325 | TT-20251026-00278 | Reference_telecom | Region_4 | JED1U6771 | JED6071 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 04:31:57 | 10/26/2025 04:31:57 | 10/26/2025 10:31:57 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1U6771-G9-L18-SBTS-P1-SHOP @ Sceco | 10/26/2025 04:11:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 04:11:26 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1U6771 | FLM_TE |  |  | PCM-20251026-00000310 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/26/2025 04:31:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000163 | PCM-20251026-00000326 | TT-20251026-00305 | Telecom | Region_1 | JBL0468 | JBL0468 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 04:32:06 | 10/26/2025 05:10:59 | 10/26/2025 16:32:06 | RF Unit CPRI Interface Error at JBL0468-P2_SRAN @ Sceco | 10/26/2025 04:26:47 | Minor | 26504 | RF Unit CPRI Interface Error | 10/26/2025 04:25:16 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0468 | FLM_TE | [8 empty] | API | 10/26/2025 04:32:06 | 10/26/2025 05:10:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000167 | PCM-20251026-00000341 | TT-20251026-00320 | EM | Region_6 | BHAB2253 | BHAB2253 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/26/2025 04:50:29 | 10/26/2025 22:20:31 | 10/26/2025 10:50:29 | 1(2G/LTE) sites down under BHAB2253-P3/BHAB2253-P3 @ Generator_SG | 10/26/2025 04:42:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 04:41:59 | P3 | 2G | Albaha | Generator_SG | 2G SA | BHAB2253-P3 | FLM_TE | BHAB2253 | Results: DOWN SITE HUB BHAB2253-P3 BHAB2253 Summary: Hub: BHAB2253, Down Count: 1, Down Sites: BHAB2253-P3 Alarm Summary: BHAB2253 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 04:50:29 | 10/26/2025 08:33:22 | 10/26/2025 08:38:27 |  |  | 10/26/2025 08:38:54 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000172 | PCM-20251026-00000351 | TT-20251026-00332 | Telecom | Region_6 | DAR0918 | DAR0918 | Equipment | BTS_Cable | Replace Fiber Cable | Muhammad Ali | 10/26/2025 05:02:32 | 10/26/2025 12:07:09 | 10/26/2025 11:02:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR0918-GSM-UMTS-P2 @ Sceco | 10/26/2025 05:01:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 05:01:35 | P2 | 2G | dair | Sceco | 5G_Cell SA | DAR0918 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 05:02:32 | 10/26/2025 05:08:31 | 10/26/2025 11:21:35 | 10/26/2025 11:21:38 | 10/26/2025 11:24:28 | 10/26/2025 12:07:09 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000173 | PCM-20251026-00000352 | TT-20251026-00329 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:02:59 | 10/26/2025 21:19:19 | 10/26/2025 11:02:59 | 1(2G) sites down under MKYL0914-P3/MKYL0914-P3 @ Sceco | 10/26/2025 04:54:39 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 04:54:36 | P3 | 2G | alaith | Sceco | 2G SA | MKYL0914-P3 | FLM_TE | MKYL0914 | Results: DOWN SITE HUB MKYL0914-P3 MKYL0914 Summary: Hub: MKYL0914, Down Count: 1, Down Sites: MKYL0914-P3 Alarm Summary: MKYL0914 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 05:02:59 | 10/26/2025 21:19:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000174 | PCM-20251026-00000354 | TT-20251026-00334 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 05:05:08 | 10/26/2025 06:55:23 | 10/26/2025 17:05:08 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/26/2025 04:56:48 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 04:56:38 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 05:05:08 | 10/26/2025 06:55:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000175 | PCM-20251026-00000356 | TT-20251026-00331 | EM | Region_6 | JIZ1M7092 | JIZ0092 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/26/2025 05:06:59 | 10/26/2025 19:48:15 | 10/26/2025 09:06:59 | 1(3G/LTE) sites down under JIZ0092-P1-HUB @ Sceco_STB | 10/26/2025 04:58:34 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 04:58:30 | P1 | 4G | jizan | Sceco_STB | LTE SA | JIZ0092-G9-L8-L18-L21-SBTS-P1-HUB | FLM_TE | JIZ0092 | Results: DOWN SITE HUB JIZ0092-G9-L8-L18-L21-SBTS-P1-HUB JIZ0092 Summary: Hub: JIZ0092, Down Count: 1, Down Sites: JIZ0092-G9-L8-L18-L21-SBTS-P1-HUB Alarm Summary: JIZ0092 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.103.39.84:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 05:06:59 | 10/26/2025 05:12:12 | 10/26/2025 19:48:06 |  |  | 10/26/2025 19:48:15 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000176 | PCM-20251026-00000361 | TT-20251026-00317 | Telecom | Region_6 | JDJZ0885 | JDJZ0885 | Transsmission | MW_RSL_fading | Fading issue | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 05:08:20 | 10/26/2025 11:06:18 | 10/26/2025 09:08:20 | 6(2G) 7(3G) 2(5G) sites down under JDJZ0895-P3 @ Sceco_STB | 10/26/2025 04:35:36 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 04:35:32 | P1 | 2G | derb | Sceco_STB | 2G_3G_5G SA | JDJZ0895-P3 2G_3G_5G,JDJZ0780-P3 2G_3G_5G,JDJZ0782-P3 2G_3G,JDJZ0781-P2 3G,JDJZ0783-P2 2G_3G,QEH0142-P2 2G_3G,JDJZ0885-P1-HUB 3G,HRD0778-P1-VIP 2G | FLM_TE | JDJZ0885 | Results: DOWN SITE HUB JDJZ0895-P3 JDJZ0885 JDJZ0780-P3 JDJZ0885 JDJZ0782-P3 JDJZ0885 JDJZ0781-P2 JDJZ0885 JDJZ0783-P2 JDJZ0885 QEH0142-P2 JDJZ0885 JDJZ0885-P1-HUB JDJZ0885 HRD0778-P1-VIP JDJZ0885 Summary: Hub: JDJZ0885, Down Count: 8, Down Sites: JDJZ0895-P3, JDJZ0780-P3, JDJZ0782-P3, JDJZ0781-P2, JDJZ0783-P2, QEH0142-P2, JDJZ0885-P1-HUB, HRD0778-P1-VIP Alarm Summary: JDJZ0885 No Active Alarm on HUB | PCM-20251026-00000339 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 05:08:20 | 10/26/2025 11:04:26 | 10/26/2025 11:05:50 |  |  | 10/26/2025 11:06:18 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000177 | PCM-20251026-00000362 | TT-20251026-00270 | Reference_telecom | Region_4 | JED1M7223 | JED0223 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/26/2025 05:11:48 | 10/26/2025 17:49:26 | 10/26/2025 11:11:48 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M7223-P1-HUB-CA-L900-L800-SBTS @ Sceco_STB | 10/26/2025 03:56:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 03:56:31 | P1 | 4G | jeddah | Sceco_STB | 5G_Cell SA | JED1M7223 | FLM_TE |  |  | PCM-20251026-00000299 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/26/2025 05:11:48 | 10/26/2025 12:23:08 | 10/26/2025 17:40:21 | 10/26/2025 17:40:23 | 10/26/2025 17:40:26 | 10/26/2025 17:49:26 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000178 | PCM-20251026-00000364 | TT-20251026-00325 | Reference_telecom | Region_4 | JED1M8928 | JED2928 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 05:14:27 | 10/26/2025 12:28:55 | 10/26/2025 11:14:27 | BASE STATION CONNECTIVITY PROBLEM (OMU signaling connection failure in Abis interface;Default System Time) at JED1M8928-USF-P3 @ Sceco | 10/26/2025 04:50:23 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 07/16/2024 13:20:41 | P3 | 4G | qunfuddah | Sceco | LTE NSA | JED1M8928 | FLM_TE |  |  | PCM-20251026-00000346 | Please check the multiple HW issue | Please check the multiple HW issue |  |  |  | API | 10/26/2025 05:14:27 | 10/26/2025 12:28:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000179 | PCM-20251026-00000366 | TT-20251026-00314 | Reference_telecom | Region_6 | BHAB1M8253 | BHAB2253 | Equipment | BTS_Cable | Replace CPRI Cable | Muhammad Jamal Khan Abbas Ali | 10/26/2025 05:15:15 | 10/26/2025 08:44:24 | 10/26/2025 17:15:15 | BASE STATION CONNECTIVITY PROBLEM (S1 SCTP path failure) at BHAB1M8253-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 04:27:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 04:27:11 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8253 | FLM_TE |  |  | PCM-20251026-00000330 | Please check the site down | Please check the site down |  |  |  | API | 10/26/2025 05:15:15 | 10/26/2025 08:33:22 | 10/26/2025 08:44:07 |  |  | 10/26/2025 08:44:24 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000181 | PCM-20251026-00000369 | TT-20251026-00330 | Reference_telecom | Region_4 | JED1MN0187 | JED0187 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 05:18:43 | 10/26/2025 13:19:20 | 10/26/2025 17:18:43 | Fronthaul loop back connectivity check failure at JED1MN0187-NR2.6-P2 @ Sceco | 10/26/2025 04:29:58 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/26/2025 04:29:51 | P1 | 5G | jeddah | Sceco | 5G NSA | JED1MN0187 | FLM_TE |  |  | PCM-20251026-00000350 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/26/2025 05:18:43 | 10/26/2025 13:19:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000182 | PCM-20251026-00000370 | TT-20251026-00345 | Reference_telecom | Region_4 | JED0017-ZJe03-CSG-03 | JED0017 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 05:19:02 | 10/26/2025 05:19:02 | 10/26/2025 17:19:02 | Optical Invalid at JED0017-ZJe03-CSG-03 // TT-20250426-00572 @ Sceco | 10/26/2025 03:13:16 | Minor | 101-2505224 | Optical Invalid | 10/26/2025 03:12:58 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0017-ZJe03-CSG-03 | FLM_TE | [8 empty] | API | 10/26/2025 05:19:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000184 | PCM-20251026-00000374 | TT-20251026-00350 | EM | Region_4 | JED1U6760 | JED6060 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/26/2025 05:24:14 | 10/26/2025 05:24:14 | 10/26/2025 17:24:14 | AIRCON 2 FAILURE at JED1U6760-G9-L18-SBTS-P3 @ Sceco | 10/26/2025 05:16:11 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 05:16:03 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6760 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 05:24:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000185 | PCM-20251026-00000375 | TT-20251026-00351 | EM | Region_4 | MKYL0913 | MKYL0913 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/26/2025 05:24:45 | 10/26/2025 11:45:24 | 10/26/2025 17:24:45 | SHELTER DOOR OPEN;Default System Time at MKYL0913-GSM-UMTS-P2 @ Generator_SG | 10/26/2025 05:24:21 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/25/2025 03:12:04 | P2 | 2G | alaith | Generator_SG | 2G NSA | MKYL0913 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 05:24:45 | 10/26/2025 11:45:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000186 | PCM-20251026-00000377 | TT-20251026-00354 | EM | Region_6 | BHAQ1M8435 | BHAQ2435 |  |  |  | Muhammad Tayyab | 10/26/2025 05:25:47 | 10/26/2025 15:52:22 | 10/26/2025 17:25:47 | Genset Running at BHAQ1M8435-P3 -G900-L800-SBTS @ Generator_DG | 10/26/2025 05:17:46 | Minor | 7103 | Genset Running | 10/26/2025 05:17:40 | P3 | 4G | Albaha | Generator_DG | LTE NSA | BHAQ1M8435 | FLM_EM | [5 empty] | Genset Running |  |  | API | 10/26/2025 05:25:47 | 10/26/2025 15:52:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000187 | PCM-20251026-00000385 | TT-20251026-00353 | Telecom | Region_4 | YLM0756 | YLM0756 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:30:29 | 10/26/2025 21:19:19 | 10/26/2025 09:30:29 | 1(5G) sites down under YLM0756-GSM-UMTS-P1 @ Generator_DG | 10/26/2025 05:22:12 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 05:22:08 | P1 | 2G | alaith | Generator_DG | 5G SA | YLM0756-GSM-UMTS-P1 | FLM_TE | YLM0756 | Results: DOWN SITE HUB YLM0756-GSM-UMTS-P1 YLM0756 Summary: Hub: YLM0756, Down Count: 1, Down Sites: YLM0756-GSM-UMTS-P1 Alarm Summary: YLM0756 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.9.12:8080] [URL:http://10.88.9.12:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 05:30:29 | 10/26/2025 21:19:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000188 | PCM-20251026-00000391 | TT-20251026-00359 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 05:34:37 | 10/26/2025 13:19:21 | 10/26/2025 11:34:37 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/26/2025 05:22:46 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 05:22:43 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251026-00000384 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 05:34:37 | 10/26/2025 13:19:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000189 | PCM-20251026-00000392 | TT-20251026-00357 | Telecom | Region_4 | JED1M7498 | JED0498 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 05:34:49 | 10/26/2025 10:36:47 | 10/26/2025 09:34:49 | BASE STATION ANTENNA LINE PROBLEM at JED1M7498-CA-L800-L900-P1-HUB-WDM @ Sceco | 10/26/2025 05:20:12 | Critical | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 05:20:06 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7498 | FLM_TE |  |  | PCM-20251026-00000380 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 05:34:49 | 10/26/2025 10:36:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000190 | PCM-20251026-00000393 | TT-20251026-00358 | Reference_telecom | Region_6 | QLW1M8370 | QLW2370 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 05:36:34 | 10/26/2025 10:55:20 | 10/26/2025 17:36:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 04:26:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 03:29:12 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_TE |  |  | PCM-20251026-00000383 | Please close the alarm during site down | Please close the alarm during site down |  |  |  | API | 10/26/2025 05:36:34 | 10/26/2025 10:52:38 | 10/26/2025 10:55:09 |  |  | 10/26/2025 10:55:20 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000193 | PCM-20251026-00000398 | TT-20251026-00273 | Reference_telecom | Region_5 | MAK0981 | MAK0981 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 05:42:01 | 10/26/2025 05:42:01 | 10/26/2025 11:42:01 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MAK0981-P2 @ Sceco | 10/26/2025 04:01:07 | Major | 7607 | TRX OPERATION DEGRADED | 10/26/2025 04:01:02 | P2 | 2G | makkah | Sceco | 2G_TRX NSA | MAK0981 | FLM_TE |  |  | PCM-20251026-00000305 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/26/2025 05:42:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000194 | PCM-20251026-00000399 | TT-20251026-00371 | Telecom | Region_4 | YLM0740 | YLM0740 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:45:32 | 10/26/2025 21:19:20 | 10/26/2025 11:45:32 | 1(2G) sites down under YLM0740-P2-USF/YLM0740-P2-USF @ Sceco | 10/26/2025 05:37:23 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 05:37:18 | P2 | 2G | alaith | Sceco | 2G SA | YLM0740-P2-USF | FLM_TE | YLM0740 | Results: DOWN SITE HUB YLM0740-P2-USF YLM0740 Summary: Hub: YLM0740, Down Count: 1, Down Sites: YLM0740-P2-USF Alarm Summary: YLM0740 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 05:45:32 | 10/26/2025 21:19:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000195 | PCM-20251026-00000403 | TT-20251026-00377 | EM | Region_4 | MUMA1M8337 | MUMA2337 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 05:49:03 | 10/26/2025 09:29:24 | 10/26/2025 17:49:03 | COMMERCIAL POWER FAILURE at MUMA1M8337-G9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 05:40:57 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/26/2025 05:40:49 | P3 | 4G | jeddah | Sceco | LTE NSA | MUMA1M8337 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/26/2025 05:49:03 | 10/26/2025 09:29:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000197 | PCM-20251026-00000407 | TT-20251026-00266 | Telecom | Region_4 | JDJZ0768 | JDJZ0768 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:53:16 | 10/26/2025 21:19:21 | 10/26/2025 07:53:16 | 14(2G) 21(3G) 1(LTE) 2(5G) sites down under SDY0737-P3 @ Generator_SG | 10/26/2025 03:53:01 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/26/2025 03:52:55 | P1 | 2G | qunfuddah | Generator_DG | 2G_3G_5G SA | YLM0768-P3 2G_3G_5G,SDY0737-P3 2G_3G,YLM0746-P3 3G,SDY0870-P3 2G_3G,YLM0745-P3 3G,SDY0146-P3 2G_3G,YLM0161-P3 2G_3G,BIK0156-P3 3G,SDY0145-P3 3G,YLM0149-P3 3G,SDY0163-P3 2G_3G,SDY0148-P3 3G,YLM0757-P3 3G,YLM0789-P3 3G,SDY0147-P3 3G,SDY0162-P3 2G_3G,SDY0158-P3 3G,MLJI0744-P3 3G,SDY0739-P3 3G,YLM2368-P3 2G,YLM0752-P1 2G,SDY0766-P3 2G,YLM0391-P1 2G,MKYL0908-P2 2G,YLM2369-P1 2G | FLM_TE | JDJZ0768 | Results: DOWN SITE HUB YLM0768-P3 YLM0768 SDY0737-P3 SDY0737 YLM0746-P3 YLM0746 SDY0870-P3 Need to check YLM0745-P3 YLM2368 SDY0146-P3 SDY0146 YLM0161-P3 SDY0147 BIK0156-P3 SDY0147 SDY0145-P3 Need to check YLM0149-P3 SDY0147 SDY0163-P3 SDY0737 SDY0148-P3 SDY0148 YLM0757-P3 YLM0757 YLM0789-P3 YLM2368 SDY0147-P3 SDY0147 SDY0162-P3 SDY0147 SDY0158-P3 SDY0147 MLJI0744-P3 YLM2368 SDY0739-P3 SDY0147 YLM2368-P3 YLM2368 YLM0752-P1 SDY0147 SDY0766-P3 Need to check YLM0391-P1 YLM2368 MKYL0908-P2 Need to check YLM2369-P1 YLM2369 Summary: Hub: YLM0768, Down Count: 1, Down Sites: YLM0768-P3 Hub: SDY0737, Down Count: 2, Down Sites: SDY0737-P3, SDY0163-P3 Hub: YLM0746, Down Count: 1, Down Sites: YLM0746-P3 Hub: YLM2368, Down Count: 5, Down Sites: YLM0745-P3, YLM0789-P3, MLJI0744-P3, YLM2368-P3, YLM0391-P1 Hub: SDY0146, Down Count: 1, Down Sites: SDY0146-P3 Hub: SDY0147, Down Count: 8, Down Sites: YLM0161-P3, BIK0156-P3, YLM0149-P3, SDY0147-P3, SDY0162-P3, SDY0158-P3, SDY0739-P3, YLM0752-P1 Hub: SDY0148, Down Count: 1, Down Sites: SDY0148-P3 Hub: YLM0757, Down Count: 1, Down Sites: YLM0757-P3 Hub: YLM2369, Down Count: 1, Down Sites: YLM2369-P1 Alarm Summary: YLM0768 No Active Alarm on HUB SDY0737 No Active Alarm on HUB YLM0746 No Active Alarm on HUB HUB site not found YLM2368 No Active Alarm on HUB SDY0146 No Active Alarm on HUB SDY0147 Alarm Active on HUB SDY0148 No Active Alarm on HUB YLM0757 No Active Alarm on HUB YLM2369 No Active Alarm on HUB | PCM-20251026-00000337 | Thanks to check locally as no action can be taken from our side | Thanks to check locally as no action can be taken from our side |  | sites down |  | API | 10/26/2025 05:53:16 | 10/26/2025 21:19:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000198 | PCM-20251026-00000408 | TT-20251026-00381 | Telecom | Region_4 | JED0435 | JED0435 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 05:53:41 | 10/26/2025 13:19:21 | 10/26/2025 09:53:41 | JED0723 NODE ISOLATED | 10/26/2025 05:53:12 | Critical | 1-12843 | OSC_LOS | 10/26/2025 05:53:01 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0435 | FLM_TE | [5 empty] | 0-1-C-9-F1AST4-1(RM1/TM1(FROM JED0723))-OSC:1 |  |  | API | 10/26/2025 05:53:41 | 10/26/2025 13:19:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000200 | PCM-20251026-00000410 | TT-20251026-00383 | Reference_telecom | Region_2 | RIYA2U6760A | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/26/2025 05:54:12 | 10/26/2025 11:14:33 | 10/26/2025 11:54:12 | RF Out of Service at RIYA2U6760A-P3 @ Sceco | 10/26/2025 05:48:14 | Major | 29248 | RF Out of Service | 10/26/2025 05:48:00 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6760A | FLM_TE | [8 empty] | API | 10/26/2025 05:54:12 | 10/26/2025 11:14:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000202 | PCM-20251026-00000412 | TT-20251026-00380 | Telecom | Region_4 | SDY0170 | SDY0170 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 05:58:03 | 10/26/2025 21:19:21 | 10/26/2025 11:58:03 | 1(5G) sites down under SDY0170-GSM-UMTS-P3 @ Generator_SG | 10/26/2025 05:49:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 05:49:54 | P3 | 2G | qunfuddah | Generator_SG | 5G SA | SDY0170-GSM-UMTS-P3 | FLM_TE | SDY0170 | Results: DOWN SITE HUB SDY0170-GSM-UMTS-P3 SDY0170 Summary: Hub: SDY0170, Down Count: 1, Down Sites: SDY0170-GSM-UMTS-P3 Alarm Summary: SDY0170 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.25.116:8080] [URL:http://10.88.25.116:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 05:58:03 | 10/26/2025 21:19:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000205 | PCM-20251026-00000418 | TT-20251026-00392 | Telecom | Region_4 | TFBH0892 | TFBH0892 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 06:00:56 | 10/26/2025 09:33:55 | 10/26/2025 12:00:56 | LAN_LOC at TFBH0892_OSC1 @ Sceco_STB | 10/26/2025 01:55:48 | Major | 1-12926 | LAN_LOC | 10/26/2025 01:55:15 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_TE | [5 empty] | 0-TO MIS0359(1-A)-8-T1SCC-4(ETH1/ETH1)-COM:1 |  |  | API | 10/26/2025 06:00:56 | 10/26/2025 09:33:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000206 | PCM-20251026-00000419 | TT-20251026-00393 | Telecom | Region_1 | ARR0625 | ARR0625 |  |  |  | Muhammad Zubair Guilzar | 10/26/2025 06:00:57 | 10/26/2025 06:15:29 | 10/26/2025 18:00:57 | RF Unit Maintenance Link Failure at ARR0625-P2_SRAN @ Sceco | 10/26/2025 01:08:42 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 01:07:00 | P2 | SRAN | arar | Sceco | 2G NSA | ARR0625 | FLM_TE | [8 empty] | API | 10/26/2025 06:00:57 | 10/26/2025 06:15:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000208 | PCM-20251026-00000421 | TT-20251026-00395 | Telecom | Region_4 | TFBH0892 | TFBH0892 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 06:00:58 | 10/26/2025 09:33:55 | 10/26/2025 12:00:58 | LAN_LOC at TFBH0892_ELC @ Sceco_STB | 10/26/2025 01:55:25 | Major | 1-12926 | LAN_LOC | 10/26/2025 01:55:15 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_TE | [5 empty] | 0-ELC(1-C)-7-T1SCC-5(ETH2&EXT1/ETH2&EXT1)-COM:1 |  |  | API | 10/26/2025 06:00:58 | 10/26/2025 09:33:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000210 | PCM-20251026-00000427 | TT-20251026-00399 | Telecom | Region_6 | DAR1MT0901 | DAR0901 | Equipment | BSS_HW_Stuck | Reset RRU | Muhammad Ali | 10/26/2025 06:04:00 | 10/26/2025 11:28:48 | 10/26/2025 10:04:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR1MT0901-P1 @ Generator_DG | 10/26/2025 06:03:09 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:03:01 | P1 | 4G | raith | Generator_DG | 5G_Cell SA | DAR1MT0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 06:04:00 | 10/26/2025 11:18:21 | 10/26/2025 11:27:25 |  |  | 10/26/2025 11:28:48 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000211 | PCM-20251026-00000428 | TT-20251026-00400 | Telecom | Region_4 | JED1M7235 | JED0235 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 06:05:02 | 10/26/2025 15:42:25 | 10/26/2025 12:05:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7235-P3-CA-L900-L800-SBTS @ Generator_SG | 10/26/2025 06:04:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:03:50 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7235 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 06:05:02 | 10/26/2025 09:43:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000212 | PCM-20251026-00000429 | TT-20251026-00401 | EM | Region_6 | ABDB1M7841 | ABDB0841 |  |  |  | Aziz Ul Haq Umar Gul | 10/26/2025 06:05:03 | 10/26/2025 10:49:08 | 10/26/2025 18:05:03 | SHELTER DOOR OPEN at ABDB1M7841-P3-L800-SBTS @ Generator_SG | 10/26/2025 06:04:27 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 06:04:21 | P3 | 4G | derb | Generator_SG | LTE NSA | ABDB1M7841 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 06:05:03 | 10/26/2025 10:49:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000218 | PCM-20251026-00000440 | TT-20251025-01836 | Telecom | Region_6 | TLT0375 | TLT0375 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Umair Abbas Muhammad Abbas | 10/26/2025 06:12:28 | 10/26/2025 15:48:45 | 10/26/2025 12:12:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at TLT0375-GSM-UMTS-P3 @ Generator_SG | 10/25/2025 22:06:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 22:06:14 | P3 | 2G | turaib | Generator_SG | 5G_Cell SA | TLT0375 | FLM_TE |  |  | PCM-20251026-00000436 | Please visit to check the HW issue | Please visit to check the HW issue |  |  |  | API | 10/26/2025 06:12:28 | 10/26/2025 06:20:27 | 10/26/2025 15:48:24 |  |  | 10/26/2025 15:48:45 |  | Umair Abbas Muhammad Abbas |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000219 | PCM-20251026-00000441 | TT-20251026-00374 | Reference_telecom | Region_6 | TLT1M3375 | TLT0375 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Umair Abbas Muhammad Abbas | 10/26/2025 06:13:23 | 10/26/2025 15:45:29 | 10/26/2025 12:13:23 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TLT1M3375-P3 @ Generator_SG | 10/26/2025 05:19:21 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 05:17:12 | P3 | 3G | turaib | Generator_SG | 3G SA | TLT1M3375 | FLM_TE |  |  | PCM-20251026-00000401 | Please visit to check the HW issue | Please visit to check the HW issue |  |  |  | API | 10/26/2025 06:13:23 | 10/26/2025 06:20:28 | 10/26/2025 15:44:33 |  |  | 10/26/2025 15:45:29 |  | Umair Abbas Muhammad Abbas |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000220 | PCM-20251026-00000442 | TT-20251026-00375 | Reference_telecom | Region_6 | KMBS0666 | KMBS0666 | Equipment | BSS_HW_Stuck | Reset RRU | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 06:13:44 | 10/26/2025 11:28:59 | 10/26/2025 12:13:44 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at KMBS0666-GSM-UMTS-P2-USF @ Sceco | 10/26/2025 05:42:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 05:42:44 | P2 | 2G | bisha | Sceco | 5G_Cell SA | KMBS0666 | FLM_TE |  |  | PCM-20251026-00000402 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/26/2025 06:13:44 | 10/26/2025 11:28:22 | 10/26/2025 11:28:41 |  |  | 10/26/2025 11:28:59 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000221 | PCM-20251026-00000445 | TT-20251026-00405 | Telecom | Region_4 | NSH0193 | NSH0193 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 06:15:34 | 10/26/2025 12:28:55 | 10/26/2025 12:15:34 | 1(2G) sites down under NSH0193-P3/NSH0193-P3 @ Sceco | 10/26/2025 06:07:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:07:11 | P3 | 2G | qunfuddah | Sceco | 2G SA | NSH0193-P3 | FLM_TE | NSH0193 | Results: DOWN SITE HUB NSH0193-P3 NSH0193 Summary: Hub: NSH0193, Down Count: 1, Down Sites: NSH0193-P3 Alarm Summary: NSH0193 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 06:15:34 | 10/26/2025 12:28:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000223 | PCM-20251026-00000451 | TT-20251026-00414 | EM | Region_4 | SQR0074 | SQR0074 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 06:22:58 | 10/27/2025 03:31:31 | 10/26/2025 12:22:58 | 1(2G/LTE) sites down under SQR0074-P2-USF/SQR0074-P2-USF @ Generator_SG | 10/26/2025 06:14:42 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:14:36 | P2 | 2G | adam | Generator_SG | 2G SA | SQR0074-P2-USF | FLM_TE | SQR0074 | Results: DOWN SITE HUB SQR0074-P2-USF SQR0074 Summary: Hub: SQR0074, Down Count: 1, Down Sites: SQR0074-P2-USF Alarm Summary: SQR0074 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 06:22:58 | 10/26/2025 09:54:23 | 10/27/2025 03:31:22 |  |  | 10/27/2025 03:31:31 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000225 | PCM-20251026-00000453 | TT-20251026-00190 | Telecom | Region_1 | DAM-IPsec-9811-01 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/26/2025 06:24:58 | 10/26/2025 06:24:58 | 10/26/2025 18:24:58 | Dust Net Clean Alarm at DAM-IPsec-9811-01 @ Sceco_STB | 10/26/2025 02:49:05 | Minor | 101-3067995 | Dust Net Clean Alarm | 10/26/2025 02:49:02 | P1 | IPBB | dammam | Sceco_STB | IPRAN NSA | DAM-IPsec-9811-01 | FLM_TE |  |  | PCM-20251026-00000224 | Please close the case from your side | Please close the case from your side |  |  |  | API | 10/26/2025 06:24:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000226 | PCM-20251026-00000454 | TT-20251026-00404 | Telecom | Region_6 | SRA2359 | SRA2359 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 06:25:22 | 10/26/2025 09:44:45 | 10/26/2025 12:25:22 | 4(2G) 4(LTE) sites down under SRA2362-P3,QLW2376-P3,QLW2370-P3,QLW2374-P3-P3/QLW2374-P3-P3 @ Generator_SG | 10/26/2025 06:07:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:07:25 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2362-P3 2G_LTE,QLW2376-P3 2G_LTE,QLW2374-P3-P3 2G_LTE,QLW2370-P3 2G_LTE | FLM_EM | SRA2359 | Results: DOWN SITE HUB SRA2362-P3 SRA2362 QLW2376-P3 QLW2376 QLW2374-P3-P3 QLW2374 QLW2370-P3 QLW2370 Summary: Hub: SRA2362, Down Count: 1, Down Sites: SRA2362-P3 Hub: QLW2376, Down Count: 1, Down Sites: QLW2376-P3 Hub: QLW2374, Down Count: 1, Down Sites: QLW2374-P3-P3 Hub: QLW2370, Down Count: 1, Down Sites: QLW2370-P3 Alarm Summary: SRA2362 Alarm Active on HUB QLW2376 Alarm Active on HUB QLW2374 Alarm Active on HUB QLW2370 No Active Alarm on HUB | PCM-20251026-00000444 | SRA2359 | SRA2359 |  | sites down |  | API | 10/26/2025 06:25:22 | 10/26/2025 09:44:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000229 | PCM-20251026-00000460 | TT-20251026-00410 | Reference_telecom | Region_6 | ABH1M7234 | ABH0234 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 06:31:56 | 10/26/2025 14:05:31 | 10/26/2025 18:31:56 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABH1M7234-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/26/2025 04:25:13 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 04:16:45 | P2 | 4G | abha | Sceco | LTE NSA | ABH1M7234 | FLM_TE |  |  | PCM-20251026-00000446 | Please close alarm during site down | Please close alarm during site down |  |  |  | API | 10/26/2025 06:31:56 | 10/26/2025 14:04:41 | 10/26/2025 14:05:21 |  |  | 10/26/2025 14:05:31 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000230 | PCM-20251026-00000461 | TT-20251026-00418 | Reference_telecom | Region_4 | TURY0826 | TURY0826 | Equipment | BSS_HW_fault | Replace RF Module | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/26/2025 06:32:52 | 10/27/2025 07:59:27 | 10/26/2025 12:32:52 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/26/2025 06:24:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:24:50 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251026-00000456 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/26/2025 06:32:52 | 10/26/2025 10:59:17 | 10/26/2025 10:59:26 | 10/26/2025 11:00:27 | 10/26/2025 11:00:29 | 10/27/2025 07:59:27 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000231 | PCM-20251026-00000463 | TT-20251026-00347 | EM | Region_3 | YNB2046 | YNB2046 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/26/2025 06:33:11 | 10/26/2025 15:38:21 | 10/26/2025 12:33:11 | 1(2G/3G/LTE) sites down under YNB2046-P2/YB1MBSCH01 @ Sceco | 10/26/2025 05:19:06 | Major | 22214 | NodeB Unavailable | 10/26/2025 05:19:03 | P2 | SRAN | yanbu | Sceco | 3G_LTE SA | YNB2046-P2 | FLM_TE | YNB2046 | Dear FLM Team, hub site is YNB2046 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM | PCM-20251026-00000457 | Dear FLM Team, hub site is YNB2046 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM | Dear FLM Team, hub site is YNB2046 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. Kindly update TT under FLM EM |  | sites down |  | API | 10/26/2025 06:33:11 | 10/26/2025 11:48:56 | 10/26/2025 15:38:14 |  |  | 10/26/2025 15:38:21 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000232 | PCM-20251026-00000464 | TT-20251026-00435 | Telecom | Region_1 | KSB0031 | KSB0031 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | Muhammad Zubair Guilzar | 10/26/2025 06:37:03 | 10/26/2025 08:46:23 | 10/26/2025 12:37:03 | BBU CPRI Interface Error at KSB0031-P3-WDM_SRAN @ Sceco_STB | 10/26/2025 06:32:37 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 06:30:00 | P3 | SRAN | arar | Sceco_STB | 2G NSA | KSB0031 | FLM_TE | [8 empty] | API | 10/26/2025 06:37:03 | 10/26/2025 06:49:44 | 10/26/2025 06:49:51 | 10/26/2025 06:49:59 | 10/26/2025 06:55:35 | 10/26/2025 08:46:23 |  | Muhammad Zubair Guilzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000233 | PCM-20251026-00000466 | TT-20251026-00440 | EM | Region_6 | BSA1M8308 | BSA2308 |  |  |  | Asad Saddiq | 10/26/2025 06:42:44 | 10/26/2025 07:20:15 | 10/26/2025 18:42:44 | SHELTER DOOR OPEN;Default System Time at BSA1M8308-G9-L800-L1800-L2100-SBTS-P3 @ Generator_SG | 10/26/2025 06:42:23 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/26/2025 03:01:05 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8308 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 06:42:44 | 10/26/2025 07:20:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000235 | PCM-20251026-00000477 | TT-20251026-00467 | Reference_telecom | Region_6 | BCAL1M3714 | BCAL0714 | Equipment | SFP_BTS | Clean SFP | Hamid Ullah Muhammad Alam Khan | 10/26/2025 06:56:49 | 10/26/2025 16:42:07 | 10/26/2025 12:56:49 | CELL OPERATION DEGRADED (Rx signal level failure) at BCAL1M3714-P1-HUB-WBB-G3 (Ref:TT-20251023-01612) @ Sceco_STB | 10/25/2025 08:07:15 | Major | 7654 | CELL OPERATION DEGRADED | 10/25/2025 08:06:58 | P1 | 3G | bisha | Sceco_STB | LTE_Cell SA | BCAL1M3714 | FLM_TE | [5 empty] | Rx signal level failure |  |  | API | 10/26/2025 06:56:49 | 10/26/2025 15:23:54 | 10/26/2025 16:41:48 |  |  | 10/26/2025 16:42:07 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000237 | PCM-20251026-00000480 | TT-20251026-00469 | Reference_EM | Region_3 | DBQL2M5259 | DBQL0259 |  |  |  | Abdelwahab Mahmoud Abdelwahab Abboud | 10/26/2025 06:57:43 | 10/26/2025 06:57:43 | 10/26/2025 18:57:43 | Door opening alarm at DBQL2M5259-P3 @ Sceco | 10/26/2025 06:57:20 | Minor | 65101 | Door opening alarm | 10/26/2025 06:57:16 | P3 | 2G | tabouk | Sceco | 2G NSA | DBQL2M5259 | FLM_EM | [8 empty] | API | 10/26/2025 06:57:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000238 | PCM-20251026-00000484 | TT-20251026-00474 | Reference_telecom | Region_6 | KMS0133 | KMS0133 | Equipment | BSS_HW_Stuck | Reset RRU | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 07:01:21 | 10/26/2025 19:11:15 | 10/26/2025 19:01:21 | BASE STATION SERVICE PROBLEM (No feedback signal) at KMS0133-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 06:56:38 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:56:28 | P3 | 2G | khamis mushyet | Sceco | LTE_Cell SA | KMS0133 | FLM_TE | [5 empty] | No feedback signal |  |  | API | 10/26/2025 07:01:21 | 10/26/2025 11:28:22 | 10/26/2025 19:11:05 |  |  | 10/26/2025 19:11:15 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000239 | PCM-20251026-00000485 | TT-20251026-00475 | EM | Region_6 | SRA1M8359 | SRA2359 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 07:01:21 | 10/26/2025 09:44:46 | 10/26/2025 19:01:21 | SHELTER DOOR OPEN at SRA1M8359-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/26/2025 07:01:12 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 07:01:04 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8359 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 07:01:21 | 10/26/2025 09:44:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000240 | PCM-20251026-00000486 | TT-20251026-00476 | Telecom | Region_1 | KBR2M7155 | KBR0155 |  |  |  | Imran Ali Yousaf | 10/26/2025 07:02:12 | 10/26/2025 09:39:55 | 10/26/2025 13:02:12 | Cell Unavailable at KBR2M7155-P3-L800 @ Sceco | 10/26/2025 07:01:26 | Major | 29240 | Cell Unavailable | 10/26/2025 07:01:03 | P3 | 4G | dammam | Sceco | LTE SA | KBR2M7155 | FLM_TE | [8 empty] | API | 10/26/2025 07:02:12 | 10/26/2025 09:39:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000241 | PCM-20251026-00000488 | TT-20251026-00479 | Telecom | Region_4 | JED1MN0196 | JED0196 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 07:02:53 | 10/26/2025 07:02:53 | 10/26/2025 13:02:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0196-NR2.6 @ Sceco | 10/26/2025 07:02:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:02:06 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0196 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:02:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000242 | PCM-20251026-00000489 | TT-20251026-00481 | Reference_telecom | Region_6 | MHA0517 | MHA0517 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 07:03:39 | 10/26/2025 14:06:13 | 10/26/2025 13:03:39 | BASE STATION SERVICE PROBLEM (TX out of order) at MHA0517-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 (Ref:TT-20251025-01774) @ Sceco | 10/25/2025 23:11:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 23:11:40 | P3 | 2G | khamis mushyet | Sceco | LTE_Cell SA | MHA0517 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/26/2025 07:03:39 | 10/26/2025 14:04:42 | 10/26/2025 14:06:00 |  |  | 10/26/2025 14:06:13 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000243 | PCM-20251026-00000491 | TT-20251026-00472 | Telecom | Region_3 | MDV2M1072 | MDV0072 |  |  |  | TAUSEEF ILYAS | 10/26/2025 07:06:00 | 10/26/2025 07:16:46 | 10/26/2025 13:06:00 | 1(2G) sites down under MDV0072-P2-Rehome/R2_RY2_HWBSC01 @ Sceco | 10/26/2025 06:57:56 | Major | 21807 | OML Fault | 10/26/2025 06:57:47 | P2 | 2G | madinah | Sceco | 2G SA | MDV0072-P2-Rehome | FLM_TE | MDV0072 | Results: DOWN SITE HUB MDV0072-P2-Rehome MDV0072 Summary: Hub: MDV0072, Down Count: 1, Down Sites: MDV0072-P2-Rehome Alarm Summary: MDV0072 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:06:00 | 10/26/2025 07:16:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000245 | PCM-20251026-00000496 | TT-20251026-00480 | EM | Region_4 | JED2029 | JED2029 | Equipment | BSS_HW_Stuck | Reset Interface Card | Abdullah Ahmad Mohammad Abdelsheekh | 10/26/2025 07:08:29 | 10/26/2025 11:25:47 | 10/26/2025 13:08:29 | 1(2G/5G) sites down under JED2029-P3/JED2029-P3 @ Sceco | 10/26/2025 07:00:27 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 07:00:22 | P3 | 2G | jeddah | Sceco | 2G SA | JED2029-P3 | FLM_TE | JED2029 | Results: DOWN SITE HUB JED2029-P3 JED2029 Summary: Hub: JED2029, Down Count: 1, Down Sites: JED2029-P3 Alarm Summary: JED2029 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:08:29 | 10/26/2025 11:03:42 | 10/26/2025 11:06:39 | 10/26/2025 11:06:59 | 10/26/2025 11:07:22 | 10/26/2025 11:25:47 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000246 | PCM-20251026-00000497 | TT-20251026-00488 | Reference_telecom | Region_6 | TNM1M7727 | TNM0727 | Equipment | BSS_HW_Stuck | Reset Air Scale | Fawad Khan | 10/26/2025 07:08:48 | 10/26/2025 09:40:26 | 10/26/2025 13:08:48 | BASE STATION SERVICE PROBLEM (FSP Reset Needed) at TNM1M7727-G9-NL8-L18-NL21-SBTS-P2 (Ref:TT-20251025-01307) @ Sceco | 10/25/2025 15:36:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 15:36:02 | P2 | 4G | mohail | Sceco | 5G_Cell SA | TNM1M7727 | FLM_TE | [5 empty] | FSP Reset Needed |  |  | API | 10/26/2025 07:08:48 | 10/26/2025 08:41:49 | 10/26/2025 09:39:33 |  |  | 10/26/2025 09:40:26 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000248 | PCM-20251026-00000500 | TT-20251026-00490 | Reference_telecom | Region_6 | DUS0058 | DUS0058 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/26/2025 07:10:58 | 10/26/2025 21:09:11 | 10/26/2025 13:10:58 | BASE STATION ANTENNA LINE PROBLEM (Antenna line device HW failure) at DUS0058-G9-L8-L18-L21-NR2.6-SBTS-P3 (Ref:TT-20251023-00637) @ Sceco | 10/23/2025 18:53:36 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/23/2025 18:53:31 | P3 | 2G | Albaha | Sceco | LTE SA | DUS0058 | FLM_TE | [5 empty] | Antenna line device HW failure |  |  | API | 10/26/2025 07:10:58 | 10/26/2025 10:20:14 | 10/26/2025 21:08:57 |  |  | 10/26/2025 21:09:11 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000249 | PCM-20251026-00000501 | TT-20251026-00297 | Reference_telecom | Region_2 | RIY2M7395 | RIY0395 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | DILSHAD ALI ABDUL HAMEED | 10/26/2025 07:11:48 | 10/27/2025 07:00:54 | 10/26/2025 19:11:48 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M7395-P2-L900-L800 @ Generator_SG | 10/26/2025 01:26:17 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 01:26:13 | P2 | 4G | riyadh | Generator_SG | 2G NSA | RIY2M7395 | FLM_TE |  |  | PCM-20251026-00000322 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 07:11:48 | 10/27/2025 07:00:25 | 10/27/2025 07:00:32 |  |  | 10/27/2025 07:00:54 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000250 | PCM-20251026-00000505 | TT-20251026-00348 | Reference_telecom | Region_2 | RIY2M7134 | RIY0134 | AutoRecovery | Clear_Before_Investigation | Auto Clear | WAQAR AHMED BASHIR AHMED | 10/26/2025 07:17:38 | 10/27/2025 08:18:41 | 10/26/2025 19:17:38 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M7134-P2-L900-L800 @ Sceco | 10/26/2025 02:21:23 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 02:21:20 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M7134 | FLM_TE |  |  | PCM-20251026-00000372 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 07:17:38 | [6 empty] | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000251 | PCM-20251026-00000506 | TT-20251026-00496 | Reference_EM | Region_3 | HLJF2616 | HLJF2616 | Enviroment | Air Condition | Change Fan | Ibrahim Mohamed Yousif Ibrahim | 10/26/2025 07:18:24 | 10/26/2025 09:58:31 | 10/26/2025 13:18:24 | high temprature 32 at HLJF2616-P1-HUB_SRAN @ Generator_SG | 10/26/2025 07:08:02 | Major | 65102 | high temprature 32 | 10/26/2025 07:07:57 | P1 | SRAN | hail | Generator_SG | 2G NSA | HLJF2616 | FLM_EM | [8 empty] | API | 10/26/2025 07:18:24 | 10/26/2025 07:33:28 | 10/26/2025 08:57:09 | 10/26/2025 08:57:11 | 10/26/2025 09:00:12 | 10/26/2025 09:58:31 |  | Ibrahim Mohamed Yousif Ibrahim |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000252 | PCM-20251026-00000510 | TT-20251026-00417 | Telecom | Region_6 | JIZ0074 | JIZ0074 | Equipment | BSS_HW_Stuck | Reset RF Module | Osama Hadi | 10/26/2025 07:19:29 | 10/26/2025 19:49:12 | 10/26/2025 13:19:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ0074-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-PI-VIP-ARP @ Sceco_STB | 10/26/2025 06:27:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 06:27:20 | VIP | 2G | jizan | Sceco_STB | 5G_Cell SA | JIZ0074 | FLM_TE |  |  | PCM-20251026-00000503 | Need to check locally | Need to check locally |  |  |  | API | 10/26/2025 07:19:29 | 10/26/2025 12:33:10 | 10/26/2025 19:48:36 |  |  | 10/26/2025 19:49:12 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000253 | PCM-20251026-00000512 | TT-20251026-00495 | Telecom | Region_4 | JED0294 | JED0294 |  |  |  | Nazeer Mohammed | 10/26/2025 07:21:29 | 10/26/2025 12:23:09 | 10/26/2025 13:21:29 | 1(5G) sites down under JED0294-GSM-P3 @ Generator_SG | 10/26/2025 07:13:02 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 07:13:00 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5471101 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 07:21:29 | 10/26/2025 12:23:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000254 | PCM-20251026-00000513 | TT-20251026-00289 | Telecom | Region_2 | RIY0399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Asad Ali Nadiq Khan | 10/26/2025 07:21:39 | 10/26/2025 10:58:30 | 10/26/2025 19:21:39 | RF Unit Clock Problem at RIY0399-P2_SRAN @ Sceco | 10/26/2025 04:16:55 | Minor | 26538 | RF Unit Clock Problem | 10/26/2025 04:14:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0399 | FLM_TE |  |  | PCM-20251026-00000470 | Dear FLM, Approved based on FLM TS done | Dear FLM, Approved based on FLM TS done |  |  |  | API | 10/26/2025 07:21:39 | 10/26/2025 08:12:28 | 10/26/2025 10:57:47 | 10/26/2025 10:57:57 | 10/26/2025 10:58:02 | 10/26/2025 10:58:30 |  | Asad Ali Nadiq Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000255 | PCM-20251026-00000514 | TT-20251026-00499 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 07:25:38 | 10/26/2025 12:24:00 | 10/26/2025 13:25:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 07:24:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:24:32 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0500 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:25:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000256 | PCM-20251026-00000516 | TT-20251026-00461 | Telecom | Region_4 | SJED1S7740 | SJED0740 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 07:30:47 | 10/26/2025 08:07:09 | 10/26/2025 13:30:47 | 2(LTE) sites down under SJED0741-CA-P3,SJED0740-CA-P3 @ Sceco | 10/26/2025 06:50:58 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 06:50:54 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0740-CA-P3 LTE,SJED0741-CA-P3 LTE | FLM_TE | SJED0740 | Results: DOWN SITE HUB SJED0740-CA-P3 SJED0740 SJED0741-CA-P3 SJED0741 Summary: Hub: SJED0740, Down Count: 1, Down Sites: SJED0740-CA-P3 Hub: SJED0741, Down Count: 1, Down Sites: SJED0741-CA-P3 Alarm Summary: SJED0740 No Active Alarm on HUB SJED0741 No Active Alarm on HUB | PCM-20251026-00000482 | SJED0740 | SJED0740 |  | sites down |  | API | 10/26/2025 07:30:47 | 10/26/2025 08:07:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026000257 | PCM-20251026-00000517 | TT-20251026-00505 | EM | Region_6 | RJL1M7129 | RJL0129 |  |  |  | Zia Ur Rahamn | 10/26/2025 07:30:48 | 10/26/2025 11:51:31 | 10/26/2025 19:30:48 | RECTIFIER MAINS POWER FAILURE at RJL1M7129-G9-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 07:22:26 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 07:22:21 | P3 | 4G | mohail | Sceco | LTE NSA | RJL1M7129 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 07:30:48 | 10/26/2025 07:35:59 | 10/26/2025 11:51:25 | 10/26/2025 11:51:28 | 10/26/2025 11:51:31 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000259 | PCM-20251026-00000522 | TT-20251026-00512 | Telecom | Region_2 | RIY2M7573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 07:41:13 | 10/26/2025 09:37:23 | 10/26/2025 13:41:13 | Cell Unavailable at RIY2M7573-P2-L800 @ Sceco | 10/26/2025 07:32:53 | Major | 29240 | Cell Unavailable | 10/26/2025 07:32:31 | P2 | 4G | muzamiah | Sceco | LTE SA | RIY2M7573 | FLM_TE | [8 empty] | API | 10/26/2025 07:41:13 | 10/26/2025 09:37:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000260 | PCM-20251026-00000525 | TT-20251026-00511 | Telecom | Region_3 | BDJD2M3369 | BDJD0369 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/26/2025 07:45:29 | 10/26/2025 15:38:09 | 10/26/2025 13:45:29 | 1(3G) sites down under BDJD0369-P2/YB1MBSCH01 @ Generator_SG | 10/26/2025 07:37:28 | Major | 22214 | NodeB Unavailable | 10/26/2025 07:37:25 | P3 | 3G | yanbu | Generator_SG | 3G SA | BDJD0369-P2 | FLM_TE | BDJD0369 | Results: DOWN SITE HUB BDJD0369-P2 BDJD0369 Summary: Hub: BDJD0369, Down Count: 1, Down Sites: BDJD0369-P2 Alarm Summary: BDJD0369 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:45:29 | 10/26/2025 11:48:57 | 10/26/2025 15:37:59 |  |  | 10/26/2025 15:38:09 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000261 | PCM-20251026-00000526 | TT-20251026-00127 | Reference_telecom | Region_6 | DAR1M7913 | DAR0913 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Muhammad Ali | 10/26/2025 07:46:10 | 10/26/2025 15:00:18 | 10/26/2025 13:46:10 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at DAR1M7913-NCA-L800-L1800-SBTS @ Generator_SG | 10/26/2025 01:53:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 01:53:44 | P2 | 4G | dair | Generator_SG | 5G_Cell SA | DAR1M7913 | FLM_TE |  |  | PCM-20251026-00000347 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 07:46:10 | 10/26/2025 11:18:21 | 10/26/2025 12:46:01 | 10/26/2025 12:46:03 | 10/26/2025 13:17:22 | 10/26/2025 15:00:18 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000262 | PCM-20251026-00000531 | TT-20251026-00528 | Telecom | Region_5 | MAK0216 | MAK0216 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 07:48:22 | 10/26/2025 10:19:17 | 10/26/2025 19:48:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0216-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 07:47:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:47:35 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0216 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:48:22 | 10/26/2025 10:19:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000264 | PCM-20251026-00000534 | TT-20251026-00525 | Reference_telecom | Region_4 | FAT2363 | FAT2363 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 07:49:30 | 10/26/2025 09:33:56 | 10/26/2025 19:49:30 | Fronthaul loop back connectivity check failure at FAT2363-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/26/2025 07:17:22 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/26/2025 07:17:17 | P2 | 2G | taif | Sceco | 2G NSA | FAT2363 | FLM_TE |  |  | PCM-20251026-00000528 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/26/2025 07:49:30 | 10/26/2025 09:33:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000265 | PCM-20251026-00000536 | TT-20251026-00530 | Telecom | Region_3 | YBDB0291 | YBDB0291 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 07:49:55 | 10/26/2025 10:15:03 | 10/26/2025 13:49:55 | COMMUN_FAIL at YBDB0291_OCS @ Generator_DG | 10/26/2025 07:46:17 | Major | 1-199 | COMMUN_FAIL | 10/26/2025 07:46:05 | P1 | DWDM | yanbu | Generator_DG | DWDM NSA | YBDB0291 | FLM_TE | [5 empty] | 1-LOCAL-2(1-A)-73-TMF2AUX-OTHER |  |  | API | 10/26/2025 07:49:55 | 10/26/2025 10:15:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000267 | PCM-20251026-00000539 | TT-20251026-00522 | Telecom | Region_4 | JED1U6781 | JED6081 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 07:50:28 | 10/26/2025 07:50:28 | 10/26/2025 13:50:28 | BASE STATION ANTENNA LINE PROBLEM at JED1U6781-G9-L18-L21-P3-CA @ Sceco | 10/26/2025 07:37:33 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 07:37:27 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6781 | FLM_TE |  |  | PCM-20251026-00000524 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/26/2025 07:50:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000268 | PCM-20251026-00000542 | TT-20251026-00524 | EM | Region_4 | JED2812 | JED2812 | Equipment | PMR_Power_Cable_RRU | Replace Power Cable | Abdullah Ahmad Mohammad Abdelsheekh | 10/26/2025 07:51:59 | 10/26/2025 19:51:19 | 10/26/2025 13:51:59 | 1(2G/LTE/5G) sites down under JED2812-P3/JED2812-P3 @ Sceco | 10/26/2025 07:43:57 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 07:43:51 | P3 | 2G | jeddah | Sceco | 2G SA | JED2812-P3 | FLM_TE | JED2812 | Results: DOWN SITE HUB JED2812-P3 JED2812 Summary: Hub: JED2812, Down Count: 1, Down Sites: JED2812-P3 Alarm Summary: JED2812 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 07:51:59 | 10/26/2025 18:10:22 | 10/26/2025 18:15:28 | 10/26/2025 18:15:31 | 10/26/2025 18:15:35 | 10/26/2025 19:51:19 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000269 | PCM-20251026-00000547 | TT-20251026-00471 | Reference_telecom | Region_4 | SHB1M7670 | SHB0670 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 07:55:07 | 10/26/2025 21:19:22 | 10/26/2025 19:55:07 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/26/2025 04:59:30 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 04:59:18 | P3 | 4G | qunfuddah | Sceco | LTE NSA | SHB1M7670 | FLM_TE |  |  | PCM-20251026-00000532 | Thanks to check related links JDJZ0764-JDJZ0763-JDJZ0762 | Thanks to check related links JDJZ0764-JDJZ0763-JDJZ0762 |  |  |  | API | 10/26/2025 07:55:07 | 10/26/2025 21:19:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000271 | PCM-20251026-00000549 | TT-20251026-00544 | Telecom | Region_4 | JED2965 | JED2965 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 07:58:09 | 10/26/2025 10:36:47 | 10/26/2025 13:58:09 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2965-G9-L8-L18-L21-NR2.6-FWA-P1-VIP-SBTS @ Generator_SG | 10/26/2025 07:57:33 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 07:57:25 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED2965 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 07:58:09 | 10/26/2025 10:36:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000272 | PCM-20251026-00000550 | TT-20250929-03146 | MW_HC | Region_4 | JED2072 | JED2072 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 07:58:24 | 10/26/2025 13:19:21 | 10/26/2025 19:58:24 | As BO Requested MW Nokia Observing PM errors and ACM flapping for MW link JED0783-JDJZ0761 | 09/29/2025 23:46:55 | Minor | 113388 | LOF | 09/29/2025 23:46:57 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED2072-JED0435 | FLM_TE |  |  | PCM-20251026-00000545 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/26/2025 07:58:24 | 10/26/2025 13:19:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000273 | PCM-20251026-00000552 | TT-20250929-02161 | MW_HC | Region_4 | JED2189 | JED2189 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 07:58:48 | 10/26/2025 10:36:48 | 10/26/2025 19:58:48 | Nokia MW HC_P1 Observing Performance Issue at JED2189_01-JED0368_02 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2189_01-JED0368_02 | FLM_TE |  |  | PCM-20251026-00000544 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/26/2025 07:58:48 | 10/26/2025 10:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000274 | PCM-20251026-00000555 | TT-20251026-00539 | Telecom | Region_6 | QFL1MT0055 | QFL0055 | Equipment | BTS_Cable | Reconnect GPS Cable | Osama Hadi | 10/26/2025 07:59:29 | 10/26/2025 22:03:12 | 10/26/2025 13:59:29 | 1(LTE) sites down under QFL0055-P3 @ Sceco | 10/26/2025 07:51:14 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 07:51:10 | P3 | 4G | jizan | Sceco | LTE SA | QFL0055-P3 | FLM_TE | QFL0055 | Results: DOWN SITE HUB QFL0055-P3 QFL0055 Summary: Hub: QFL0055, Down Count: 1, Down Sites: QFL0055-P3 Alarm Summary: QFL0055 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.74.10.212:8080] [URL:http://10.74.10.212:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 07:59:29 | 10/26/2025 12:33:11 | 10/26/2025 21:24:24 | 10/26/2025 21:24:28 | 10/26/2025 21:24:32 | 10/26/2025 22:03:12 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000275 | PCM-20251026-00000558 | TT-20251026-00536 | Telecom | Region_2 | SRIY0332 | SRIY0332 | Enviroment | SCECO_Failure | SCECO auto restored | Khan zeb Shah nawaz | 10/26/2025 08:00:53 | 10/26/2025 09:57:09 | 10/26/2025 14:00:53 | 3(LTE) sites down under SRIY0332-P3_SRAN,SRIY0330-P3_SRAN,SRIY0331-P3_SRAN @ Sceco | 10/26/2025 07:50:09 | Major | 301 | NE Is Disconnected | 10/26/2025 07:50:06 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0331-P3_SRAN LTE,SRIY0332-P3_SRAN LTE,SRIY0330-P3_SRAN LTE | FLM_EM | SRIY0332 | Dear Team, Hub:- SRIY0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251026-00000551 | Dear Team, Hub:- SRIY0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- SRIY0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  | sites down |  | API | 10/26/2025 08:00:53 | 10/26/2025 09:26:46 | 10/26/2025 09:37:29 | 10/26/2025 09:37:32 | 10/26/2025 09:48:28 | 10/26/2025 09:57:09 |  | Khan zeb Shah nawaz |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000277 | PCM-20251026-00000562 | TT-20251026-00518 | Reference_telecom | Region_4 | YLM1M7752 | YLM0752 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 08:04:09 | 10/26/2025 21:19:23 | 10/26/2025 14:04:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at YLM1M7752-P1-L800-SBTS @ Generator_DG | 10/26/2025 05:43:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 05:42:51 | P1 | 4G | alaith | Generator_DG | LTE NSA | YLM1M7752 | FLM_TE |  |  | PCM-20251026-00000554 | Thanks to check related link NEC >> JDJZ0768-JDJZ0767 | Thanks to check related link NEC >> JDJZ0768-JDJZ0767 |  |  |  | API | 10/26/2025 08:04:09 | 10/26/2025 21:19:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000278 | PCM-20251026-00000565 | TT-20251026-00549 | EM | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/26/2025 08:05:29 | 10/26/2025 14:51:25 | 10/26/2025 14:05:29 | 1(2G/5G) sites down under TURY0688-P3/TURY0688-P3 @ Sceco | 10/26/2025 07:57:12 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 07:57:08 | P3 | 2G | taif | Sceco | 2G SA | TURY0688-P3 | FLM_TE | TURY0688 | Results: DOWN SITE HUB TURY0688-P3 TURY0688 Summary: Hub: TURY0688, Down Count: 1, Down Sites: TURY0688-P3 Alarm Summary: TURY0688 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 08:05:29 | 10/26/2025 14:51:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000279 | PCM-20251026-00000567 | TT-20251026-00502 | Reference_telecom | Region_4 | JED0415 | JED0415 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 08:05:34 | 10/26/2025 08:07:10 | 10/26/2025 20:05:34 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED0415-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 06:57:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:58:34 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0415 | FLM_TE |  |  | PCM-20251026-00000515 | Please check the GPS is locked at site and and 5G is NNN | Please check the GPS is locked at site and and 5G is NNN |  |  |  | API | 10/26/2025 08:05:34 | 10/26/2025 08:07:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000281 | PCM-20251026-00000576 | TT-20251026-00556 | EM | Region_2 | RIYA2U6155 | RIYA6055 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/26/2025 08:10:29 | 10/26/2025 12:02:23 | 10/26/2025 14:10:29 | 1(2G/LTE) sites down under RIYA6055-P3/R2_RY1_HWBSC01 @ Sceco | 10/26/2025 08:02:23 | Major | 21807 | OML Fault | 10/26/2025 08:02:17 | P3 | 2G | riyadh | Sceco | 2G_LTE SA | RIYA6055-P3 | FLM_EM | RIYA6055 | Results: DOWN SITE HUB RIYA6055-P3 RIYA6055 Summary: Hub: RIYA6055, Down Count: 1, Down Sites: RIYA6055-P3 Alarm Summary: RIYA6055 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 08:10:29 | 10/26/2025 12:02:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000282 | PCM-20251026-00000581 | TT-20251026-00564 | Telecom | Region_6 | JIZ2087 | JIZ2087 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/26/2025 08:12:07 | 10/26/2025 19:47:58 | 10/26/2025 20:12:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ2087-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 08:11:11 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:11:01 | P3 | 2G | jizan | Sceco | 5G_Cell SA | JIZ2087 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:12:07 | 10/26/2025 12:33:11 | 10/26/2025 19:47:49 |  |  | 10/26/2025 19:47:58 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000283 | PCM-20251026-00000584 | TT-20251026-00566 | Telecom | Region_5 | MAK1M9095 | MAK0095 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/26/2025 08:12:37 | 10/26/2025 08:12:37 | 10/26/2025 14:12:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9095-P2-L800 @ Sceco | 10/26/2025 08:11:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:11:38 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9095 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:12:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000284 | PCM-20251026-00000586 | TT-20251026-00567 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 08:13:08 | 10/26/2025 08:13:08 | 10/26/2025 14:13:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/26/2025 08:12:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:12:05 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:13:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000286 | PCM-20251026-00000594 | TT-20251026-00575 | EM | Region_6 | BSA1M8289 | BSA2289 |  |  |  | Asad Saddiq | 10/26/2025 08:17:47 | 10/26/2025 08:40:25 | 10/26/2025 20:17:47 | RECTIFIER MAINS POWER FAILURE at BSA1M8289-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 08:09:32 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 08:09:26 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BSA1M8289 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 08:17:47 | 10/26/2025 08:40:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000287 | PCM-20251026-00000597 | TT-20251026-00580 | Telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 08:19:21 | 10/26/2025 09:37:23 | 10/26/2025 20:19:21 | RF Unit Clock Problem at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 08:13:40 | Minor | 26538 | RF Unit Clock Problem | 10/26/2025 08:11:07 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_TE | [8 empty] | API | 10/26/2025 08:19:21 | 10/26/2025 09:37:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000290 | PCM-20251026-00000602 | TT-20251026-00586 | Telecom | Region_5 | MAK1M9619 | MAK0619 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 08:21:55 | 10/26/2025 12:57:08 | 10/26/2025 20:21:55 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MAK1M9619-P2-CA-L800-SBTS @ Sceco | 10/26/2025 08:13:54 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 08:13:46 | P2 | 4G | makkah | Sceco | LTE NSA | MAK1M9619 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/26/2025 08:21:55 | 10/26/2025 12:57:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000292 | PCM-20251026-00000609 | TT-20251026-00595 | Telecom | Region_2 | RIY2M7573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 08:24:51 | 10/26/2025 09:37:24 | 10/26/2025 14:24:51 | Cell Unavailable at RIY2M7573-P2-L800 @ Sceco | 10/26/2025 08:24:37 | Major | 29240 | Cell Unavailable | 10/26/2025 08:23:04 | P2 | 4G | muzamiah | Sceco | LTE SA | RIY2M7573 | FLM_TE | [8 empty] | API | 10/26/2025 08:24:51 | 10/26/2025 09:37:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000293 | PCM-20251026-00000615 | TT-20251026-00602 | Reference_EM | Region_3 | AHT2339 | AHT2339 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 08:30:12 | 10/26/2025 08:30:12 | 10/26/2025 20:30:12 | Mains Failure at AHT2339-P3-USF_SRAN @ Sceco | 10/26/2025 08:20:13 | Minor | 65109 | Mains Failure | 10/26/2025 08:20:09 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2339 | FLM_EM | [8 empty] | API | 10/26/2025 08:30:12 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000295 | PCM-20251026-00000617 | TT-20251026-00604 | Reference_EM | Region_3 | MDN2042 | MDN2042 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Shafique Ahmad Sardar Ali | 10/26/2025 08:30:42 | 10/26/2025 11:19:16 | 10/26/2025 20:30:42 | Mains Failure at MDN2042-P2_SRAN @ Sceco | 10/26/2025 08:20:52 | Minor | 65109 | Mains Failure | 10/26/2025 08:20:48 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2042 | FLM_EM | [8 empty] | API | 10/26/2025 08:30:42 | 10/26/2025 08:48:24 | 10/26/2025 08:49:03 | 10/26/2025 08:49:05 | 10/26/2025 09:30:14 | 10/26/2025 11:19:16 |  | Shafique Ahmad Sardar Ali |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000297 | PCM-20251026-00000621 | TT-20251021-00654 | Reference_telecom | Region_4 | JED2596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 08:31:13 | 10/26/2025 13:19:22 | 10/26/2025 20:31:13 | LossOfSignal observed in JED2596 towards 10.1.230.53 @ Sceco | 10/20/2025 18:06:57 | Minor |  | LossOfSignal | 10/20/2025 18:05:32 | P1 | 2G | jeddah | Sceco | TX NSA | JED2596 | FLM_TE |  |  | PCM-20251026-00000579 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:31:13 | 10/26/2025 13:19:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000298 | PCM-20251026-00000622 | TT-20251022-00463 | Reference_telecom | Region_4 | JED2176 | JED2176 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 08:31:24 | 10/26/2025 13:19:22 | 10/26/2025 20:31:24 | Degrade observed in JED2176 towards 10.10.183.66 @ Sceco | 10/21/2025 16:39:16 | Minor |  | Degrade | 10/21/2025 16:39:11 | P3 | 2G | jeddah | Sceco | TX NSA | JED2176 | FLM_TE |  |  | PCM-20251026-00000585 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:31:24 | 10/26/2025 13:19:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000299 | PCM-20251026-00000623 | TT-20251022-02019 | Reference_telecom | Region_4 | JED2992 | JED2992 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 08:31:35 | 10/26/2025 13:19:22 | 10/26/2025 20:31:35 | ReplaceableUnitProblem observed in JED2992 towards 10.10.185.28 @ Sceco | 10/22/2025 07:12:18 | Minor |  | ReplaceableUnitProblem | 10/22/2025 07:12:13 | P3 | 2G | jeddah | Sceco | TX NSA | JED2992 | FLM_TE |  |  | PCM-20251026-00000580 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:31:35 | 10/26/2025 13:19:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000300 | PCM-20251026-00000624 | TT-20251026-00607 | Telecom | Region_6 | WDS0441 | WDS0441 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Mamdouh Helal Helal | 10/26/2025 08:32:15 | 10/26/2025 11:35:09 | 10/26/2025 14:32:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at WDS0441-GSM-UMTS-P3 @ Sceco | 10/26/2025 08:31:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:31:26 | P3 | 2G | wadi dawasar | Sceco | 5G_Cell SA | WDS0441 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:32:15 | 10/26/2025 11:10:51 | 10/26/2025 11:35:02 |  |  | 10/26/2025 11:35:09 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000301 | PCM-20251026-00000626 | TT-20251021-01390 | MW_HC | Region_4 | JED2985 | JED2985 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 08:33:02 | 10/26/2025 10:36:48 | 10/26/2025 20:33:02 | Nokia MW HC_P2 Observing Modem Down at JED2985 -JED0411 _6 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2985 -JED0411 _6 | FLM_TE |  |  | PCM-20251026-00000583 | Dear FLM team , Approved | Dear FLM team , Approved |  |  |  | API | 10/26/2025 08:33:02 | 10/26/2025 10:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000302 | PCM-20251026-00000627 | TT-20251026-00600 | EM | Region_6 | BHAB0824 | BHAB0824 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 08:33:59 | 10/26/2025 11:16:24 | 10/26/2025 14:33:59 | 1(2G/3G/LTE) sites down under BHAB0824-P2-WBB-G3/BHAB0824-P2-WBB-G3 @ Sceco | 10/26/2025 08:25:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:25:52 | P2 | 2G | makhwa | Sceco | 2G_3G_LTE SA | BHAB0824-P2-WBB-G3 | FLM_EM | BHAB0824 | Results: DOWN SITE HUB BHAB0824-P2-WBB-G3 BHAB0824 Summary: Hub: BHAB0824, Down Count: 1, Down Sites: BHAB0824-P2-WBB-G3 Alarm Summary: BHAB0824 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 08:33:59 | 10/26/2025 11:16:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000304 | PCM-20251026-00000632 | TT-20251026-00578 | Telecom | Region_6 | AQQ0841 | AQQ0841 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 08:37:47 | 10/26/2025 11:16:25 | 10/26/2025 12:37:47 | 6(2G) 4(LTE) sites down under AQQ0057-P3 @ Sceco | 10/26/2025 08:15:50 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:15:47 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | BSA2289-P3-P3 2G_LTE,AQQ2157-P3 2G_LTE,AQQ2170-P3 2G_LTE,AQQ2425-P3 2G_LTE,AQQ0057-P3 2G,AQQ0841-P3 2G | FLM_EM | AQQ0841 | BSA2289-P3-P3 2G_LTE BSA2289 Loss of signal AQQ2157-P3 2G_LTE AQQ0841 Node Rebooted AQQ0057-P3 2G AQQ0841 Node Rebooted AQQ0841-P3 2G AQQ0841 Node Rebooted | PCM-20251026-00000607 | BSA2289-P3-P3 2G_LTE BSA2289 Loss of signal AQQ2157-P3 2G_LTE AQQ0841 Node Rebooted AQQ0057-P3 2G AQQ0841 Node Rebooted AQQ0841-P3 2G AQQ0841 Node Rebooted | BSA2289-P3-P3 2G_LTE BSA2289 Loss of signal AQQ2157-P3 2G_LTE AQQ0841 Node Rebooted AQQ0057-P3 2G AQQ0841 Node Rebooted AQQ0841-P3 2G AQQ0841 Node Rebooted |  | sites down |  | API | 10/26/2025 08:37:47 | 10/26/2025 11:16:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000308 | PCM-20251026-00000639 | TT-20251026-00622 | EM | Region_6 | AQQ1M8427 | AQQ2423 |  |  |  | Abdul Shakor Abassi | 10/26/2025 08:38:58 | 10/26/2025 08:38:58 | 10/26/2025 20:38:58 | SHELTER DOOR OPEN at AQQ1M8427-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 08:38:36 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 08:38:26 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8427 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 08:38:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000309 | PCM-20251026-00000640 | TT-20251026-00614 | EM | Region_5 | MAK1U6993 | MAK6093 |  |  |  | Muhammad Sajjad | 10/26/2025 08:39:00 | 10/26/2025 10:09:04 | 10/26/2025 12:39:00 | 1(2G/LTE) sites down under MAK6093-P1-VIP-HAJJ-HRM @ Sceco | 10/26/2025 08:30:51 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 08:30:48 | VIP | 4G | makkah | Sceco | LTE SA | MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM | FLM_TE | MAK6093 | Results: DOWN SITE HUB MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM MAK6093 Summary: Hub: MAK6093, Down Count: 1, Down Sites: MAK6093-G18-L21-SBTS-P1-VIP-HAJJ-HRM Alarm Summary: MAK6093 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.248.20:8080] [URL:http://10.98.248.20:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 08:39:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000310 | PCM-20251026-00000641 | TT-20251026-00579 | Telecom | Region_6 | AQQ0841 | AQQ0841 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 08:41:10 | 10/26/2025 11:16:26 | 10/26/2025 14:41:10 | 2(2G) 2(LTE) sites down under AQQ2424-P3,AQQ2426-P3/AQQ2426-P3 @ Generator_SG | 10/26/2025 08:15:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:15:47 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | AQQ2424-P3 2G_LTE,AQQ2426-P3 2G_LTE | FLM_EM | AQQ0841 | AQQ0841 Node Rebooted | PCM-20251026-00000608 | AQQ0841 Node Rebooted | AQQ0841 Node Rebooted |  | sites down |  | API | 10/26/2025 08:41:10 | 10/26/2025 11:16:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000311 | PCM-20251026-00000644 | TT-20251026-00631 | EM | Region_3 | MDN2564 | MDN2564 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/26/2025 08:43:37 | 10/26/2025 08:43:37 | 10/26/2025 20:43:37 | NETECO: Insufficient Redundant Rectifiers at MDN2564 @ Generator_DG | 10/26/2025 08:37:14 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/26/2025 08:37:14 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDN2564 | FLM_EM | [8 empty] | API | 10/26/2025 08:43:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000312 | PCM-20251026-00000645 | TT-20251026-00592 | Telecom | Region_6 | BSA2310 | BSA2310 |  |  |  | Asad Saddiq | 10/26/2025 08:43:37 | 10/26/2025 09:35:59 | 10/26/2025 14:43:37 | 4(2G) 4(LTE) sites down under BHAB2015-P3,BSA2313-P3-CAP,BSA2316-P3-CAP,BSA2310-P3/BSA2310-P3 @ Sceco | 10/26/2025 08:20:37 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:20:33 | P3 | 2G | bisha | Sceco | 2G_LTE SA | BSA2310-P3 2G_LTE,BSA2316-P3-CAP 2G_LTE | FLM_EM | BSA2310 | BSA2310 Suspected power issue | PCM-20251026-00000612 | BSA2310 Suspected power issue | BSA2310 Suspected power issue |  | sites down |  | API | 10/26/2025 08:43:37 | 10/26/2025 09:35:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000313 | PCM-20251026-00000648 | TT-20251026-00633 | Telecom | Region_5 | MAK0216 | MAK0216 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 08:46:13 | 10/26/2025 10:19:17 | 10/26/2025 20:46:13 | BASE STATION INFORMATION (No module fan detected) at MAK0216-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 08:38:03 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 08:37:45 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0216 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/26/2025 08:46:13 | 10/26/2025 10:19:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000316 | PCM-20251026-00000655 | TT-20251026-00643 | Telecom | Region_6 | DBY0121 | DBY0121 | Equipment | SFP_BTS | Replace SFP | Ansir Iqbal Muhammad Iqbal | 10/26/2025 08:51:54 | 10/26/2025 19:48:36 | 10/26/2025 20:51:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at DBY0121-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 08:51:16 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 08:51:08 | P2 | 2G | jizan | Sceco | 5G_Cell SA | DBY0121 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 08:51:54 | 10/26/2025 14:31:30 | 10/26/2025 19:48:02 |  |  | 10/26/2025 19:48:36 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000319 | PCM-20251026-00000661 | TT-20251026-00649 | Telecom | [7 empty] | 10/26/2025 08:54:39 | 10/26/2025 08:54:39 | 10/26/2025 20:54:39 | HC for RIY2822 | 10/26/2025 08:53:54 | Minor | 676767672 | Health Check-WO to TE FME | 10/26/2025 08:53:56 | VIP | SRAN |  | Generator_DG | 3G NSA | RIY2822 | FLM_TE | [8 empty] | API | 10/26/2025 08:54:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000322 | PCM-20251026-00000672 | TT-20251026-00659 | Reference_EM | Region_1 | ARM2M1712 | ARM0712 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 08:59:40 | 10/26/2025 13:25:50 | 10/26/2025 20:59:40 | Door opening alarm at ARM2M1712-P3 @ Sceco | 10/26/2025 08:59:30 | Minor | 65101 | Door opening alarm | 10/26/2025 08:59:25 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1712 | FLM_EM | [8 empty] | API | 10/26/2025 08:59:40 | 10/26/2025 13:25:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000323 | PCM-20251026-00000677 | TT-20251026-00661 | Reference_EM | Region_1 | HFF2733 | HFF2733 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/26/2025 09:02:13 | 10/26/2025 10:00:45 | 10/26/2025 21:02:13 | NETECO: AC Failure at HFF2733 @ Sceco | 10/26/2025 08:55:49 | Minor | 10202 | AC Failure | 10/26/2025 08:55:49 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2733 | FLM_EM | [8 empty] | API | 10/26/2025 09:02:13 | 10/26/2025 09:26:56 | 10/26/2025 10:00:32 |  |  | 10/26/2025 10:00:45 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000326 | PCM-20251026-00000682 | TT-20251026-00669 | Telecom | Region_4 | JED2029 | JED2029 | Equipment | FAN Cleaning | Reset FAN | Abdullah Ahmad Mohammad Abdelsheekh | 10/26/2025 09:05:19 | 10/26/2025 09:44:42 | 10/26/2025 21:05:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2029-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 09:04:36 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:04:26 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2029 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:05:19 | 10/26/2025 09:16:57 | 10/26/2025 09:19:27 | 10/26/2025 09:19:30 | 10/26/2025 09:19:33 | 10/26/2025 09:44:42 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000327 | PCM-20251026-00000683 | TT-20251026-00670 | Reference_EM | Region_1 | HFF2733 | HFF2733 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/26/2025 09:05:50 | 10/26/2025 10:00:27 | 10/26/2025 21:05:50 | Mains Failure at HFF2733-P2_SRAN @ Sceco | 10/26/2025 08:55:58 | Minor | 65109 | Mains Failure | 10/26/2025 08:55:52 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2733 | FLM_EM | [8 empty] | API | 10/26/2025 09:05:50 | 10/26/2025 09:26:57 | 10/26/2025 09:53:21 | 10/26/2025 09:53:24 | 10/26/2025 09:53:27 | 10/26/2025 10:00:27 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000330 | PCM-20251026-00000690 | TT-20251026-00666 | EM | Region_6 | ALA2196 | ALA2196 |  |  |  | Asad Saddiq | 10/26/2025 09:09:30 | 10/26/2025 09:36:00 | 10/26/2025 15:09:30 | 1(2G/LTE) sites down under ALA2196-P3/ALA2196-P3 @ Generator_SG | 10/26/2025 09:01:38 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:01:35 | P3 | 2G | bisha | Generator_SG | 2G_LTE SA | ALA2196-P3 | FLM_EM | ALA2196 | Results: DOWN SITE HUB ALA2196-P3 ALA2196 Summary: Hub: ALA2196, Down Count: 1, Down Sites: ALA2196-P3 Alarm Summary: ALA2196 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:09:30 | 10/26/2025 09:36:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000332 | PCM-20251026-00000693 | TT-20251026-00637 | EM | Region_1 | SAR0073 | SAR0073 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/26/2025 09:12:15 | 10/26/2025 12:36:09 | 10/26/2025 13:12:15 | 1(2G/LTE) sites down under SAR0073-P1-HUB-USF/SK1BSCH01 @ Generator_DG | 10/26/2025 08:47:31 | Critical | 21825 | CSL Fault | 10/26/2025 08:47:29 | P1 | SRAN | quriyat | Generator_DG | 2G_LTE SA | SAR0073-P1-HUB-USF | FLM_TE | SAR0073 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SAR0073 DIR SAR0074,Kindly visit the link and perform the HC at mentioned link . | PCM-20251026-00000667 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SAR0073 DIR SAR0074,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : SAR0073 DIR SAR0074,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/26/2025 09:12:15 | 10/26/2025 12:36:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000334 | PCM-20251026-00000697 | TT-20251026-00668 | Telecom | Region_6 | BHMF0859 | BHMF0859 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/26/2025 09:14:23 | 10/26/2025 10:23:11 | 10/26/2025 15:14:23 | 1(2G) 1(LTE) 1(5G) sites down under BHMF0859-G9-SBTS-P3,BHMF0856-P3/BHMF0856-P3 @ Sceco | 10/26/2025 09:02:00 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:01:57 | P3 | 2G | makhwa | Sceco | 2G_LTE_5G SA | BHMF0856-P3 2G_LTE,BHMF0859-G9-SBTS-P3 5G | FLM_TE | BHMF0859 | Dear team , HUB: BHMF0859 We observing Low RSL at the HUB ,kindly check locally | PCM-20251026-00000691 | Dear team , HUB: BHMF0859 We observing Low RSL at the HUB ,kindly check locally | Dear team , HUB: BHMF0859 We observing Low RSL at the HUB ,kindly check locally |  | sites down |  | API | 10/26/2025 09:14:23 | 10/26/2025 10:20:15 | 10/26/2025 10:22:52 |  |  | 10/26/2025 10:23:11 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000335 | PCM-20251026-00000698 | TT-20251026-00676 | Telecom | Region_4 | JDJZ0776-LL-CSG-01 | JDJZ0776 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:14:36 | 10/26/2025 12:28:56 | 10/26/2025 13:14:36 | The Device is offline at JDJZ0776-LL-CSG-01 @ Sceco_STB | 10/26/2025 09:14:05 | Critical | 101-7 | The Device is offline | 10/26/2025 09:14:03 | P2 | IPRAN | qunfuddah | Sceco_STB | IPRAN SA | JDJZ0776-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 09:14:36 | 10/26/2025 12:28:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000336 | PCM-20251026-00000699 | TT-20251026-00677 | Telecom | Region_4 | JED0265 | JED0265 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 09:14:36 | 10/26/2025 10:36:48 | 10/26/2025 21:14:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0265-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 09:13:44 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:13:34 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0265 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:14:36 | 10/26/2025 10:36:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000337 | PCM-20251026-00000700 | TT-20251026-00571 | Reference_telecom | Region_6 | SRA1M8362 | SRA2362 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 09:14:45 | 10/26/2025 10:56:00 | 10/26/2025 21:14:45 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SRA1M8362-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 06:20:32 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:16:28 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8362 | FLM_TE |  |  | PCM-20251026-00000591 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:14:45 | 10/26/2025 10:52:39 | 10/26/2025 10:55:48 |  |  | 10/26/2025 10:56:00 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000338 | PCM-20251026-00000702 | TT-20251026-00679 | Telecom | Region_3 | HQL2041 | HQL2041 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 09:15:11 | 10/26/2025 10:15:03 | 10/26/2025 21:15:11 | GNSS Clock Output Unavailable at HQL2041-P3_SRAN @ Sceco | 10/25/2025 17:56:09 | Minor | 26124 | GNSS Clock Output Unavailable | 10/25/2025 17:54:37 | P3 | SRAN | tabouk | Sceco | 2G NSA | HQL2041 | FLM_TE | [8 empty] | API | 10/26/2025 09:15:11 | 10/26/2025 10:15:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000339 | PCM-20251026-00000703 | TT-20251026-00570 | Reference_telecom | Region_6 | QLW1M8374 | QLW2374 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 09:15:16 | 10/26/2025 10:56:39 | 10/26/2025 21:15:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8374-G9-L8-L18-SBTS-P3-P3 @ Generator_SG | 10/26/2025 06:20:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:15:39 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8374 | FLM_TE |  |  | PCM-20251026-00000590 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:15:16 | 10/26/2025 10:52:40 | 10/26/2025 10:56:29 |  |  | 10/26/2025 10:56:39 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000340 | PCM-20251026-00000705 | TT-20251026-00558 | Reference_telecom | Region_6 | QLW1M8372 | QLW2372 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 09:15:59 | 10/26/2025 17:41:43 | 10/26/2025 15:15:59 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8372-G9-L8-L18-SBTS @ Generator_SG | 10/26/2025 06:13:16 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:07:33 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8372 | FLM_TE |  |  | PCM-20251026-00000571 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:15:59 | 10/26/2025 10:52:40 | 10/26/2025 17:41:34 |  |  | 10/26/2025 17:41:43 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000341 | PCM-20251026-00000706 | TT-20251026-00557 | Reference_telecom | Region_6 | QLW1M8376 | QLW2376 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 09:16:12 | 10/26/2025 17:41:20 | 10/26/2025 15:16:12 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QLW1M8376-G9-L8-L18-SBTS-CAP @ Generator_SG | 10/26/2025 06:13:23 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 06:07:15 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8376 | FLM_TE |  |  | PCM-20251026-00000569 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:16:12 | 10/26/2025 10:52:41 | 10/26/2025 17:41:12 |  |  | 10/26/2025 17:41:20 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000342 | PCM-20251026-00000707 | TT-20251026-00660 | Reference_telecom | Region_6 | WDS1M3441 | WDS0441 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Mamdouh Helal Helal | 10/26/2025 09:16:56 | 10/26/2025 11:28:53 | 10/26/2025 15:16:56 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at WDS1M3441-P3 @ Sceco | 10/26/2025 08:33:32 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 08:31:20 | P3 | 3G | wadi dawasar | Sceco | 3G SA | WDS1M3441 | FLM_TE |  |  | PCM-20251026-00000674 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 09:16:56 | 10/26/2025 11:10:52 | 10/26/2025 11:28:46 |  |  | 10/26/2025 11:28:53 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000343 | PCM-20251026-00000708 | TT-20251026-00671 | Telecom | Region_3 | HAL0928 | HAL0928 | Transsmission | SFP_Transmission | Reset SFP | Atif Shahzad Muhammad Ajaib | 10/26/2025 09:17:59 | 10/26/2025 15:41:19 | 10/26/2025 21:17:59 | Time Synchronization Failure at HAL2M3929-P2 @ Sceco | 10/26/2025 08:59:39 | Minor | 26266 | Time Synchronization Failure | 10/26/2025 08:59:05 | P2 | SRAN | hail | Sceco | 3G NSA | HAL2M3929 | FLM_TE | HAL0928 | Hub is HAL0928 We are observing ETH_LOS ,ETH_LINK_DOWN alarms flapped at hub site ,Kindly send to FLM to check cable connection at site. | PCM-20251026-00000696 | Hub is HAL0928 We are observing ETH_LOS ,ETH_LINK_DOWN alarms flapped at hub site ,Kindly send to FLM to check cable connection at site. | Hub is HAL0928 We are observing ETH_LOS ,ETH_LINK_DOWN alarms flapped at hub site ,Kindly send to FLM to check cable connection at site. |  |  |  | API | 10/26/2025 09:17:59 | 10/26/2025 11:36:31 | 10/26/2025 14:14:50 | 10/26/2025 14:14:52 | 10/26/2025 14:14:54 | 10/26/2025 15:41:19 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000345 | PCM-20251026-00000710 | TT-20251026-00448 | Telecom | Region_4 | JED0063 | JED0063 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 09:19:04 | 10/26/2025 09:19:04 | 10/26/2025 15:19:04 | 3(2G) 2(5G) sites down under JED0415-P2,JED0144-P2,JED0063-P2/JED0063-P2 @ Sceco | 10/26/2025 06:45:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 06:45:00 | P2 | 2G | jeddah | Sceco | 2G SA | JED0063-P2 2G,JED0415-P2 2G,JED0144-P2 2G | FLM_TE | JED0063 | Results: DOWN SITE HUB JED0063-P2 JED0063 JED0415-P2 JED0415 JED0144-P2 JED0415 Summary: Hub: JED0063, Down Count: 1, Down Sites: JED0063-P2 Hub: JED0415, Down Count: 2, Down Sites: JED0415-P2, JED0144-P2 Alarm Summary: JED0063 No Active Alarm on HUB JED0415 No Active Alarm on HUB | PCM-20251026-00000695 | Please close TT with rectification RC. | Please close TT with rectification RC. |  | sites down |  | API | 10/26/2025 09:19:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000346 | PCM-20251026-00000713 | TT-20251026-00688 | Reference_telecom | Region_4 | JED2129 | JED2129 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 09:19:15 | 10/26/2025 09:19:15 | 10/26/2025 21:19:15 | InternalCommunicationProblem observed in JED2129 towards 10.1.229.217 @ Sceco | 10/25/2025 21:19:32 | Minor |  | InternalCommunicationProblem | 10/25/2025 21:19:01 | P3 | 2G | jeddah | Sceco | TX NSA | JED2129 | FLM_TE | [8 empty] | API | 10/26/2025 09:19:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000348 | PCM-20251026-00000717 | TT-20251026-00683 | EM | Region_4 | JDJZ2139 | JDJZ2139 |  |  |  | Khizer Hayat | 10/26/2025 09:21:42 | 10/26/2025 11:14:19 | 10/26/2025 15:21:42 | 1(2G/LTE) sites down under JDJZ2139-P3/JDJZ2139-P3 @ Sceco_STB | 10/26/2025 09:13:33 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:22 | P3 | 2G | jeddah | Sceco_STB | 2G SA | JDJZ2139-P3 | FLM_TE | JDJZ2139 | Results: DOWN SITE HUB JDJZ2139-P3 JDJZ2139 Summary: Hub: JDJZ2139, Down Count: 1, Down Sites: JDJZ2139-P3 Alarm Summary: JDJZ2139 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:21:42 | 10/26/2025 11:14:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000349 | PCM-20251026-00000718 | TT-20251026-00684 | EM | Region_4 | MUMA2337 | MUMA2337 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 09:21:44 | 10/26/2025 09:29:25 | 10/26/2025 15:21:44 | 1(2G/LTE) sites down under MUMA2337-P3/MUMA2337-P3 @ Sceco | 10/26/2025 09:13:29 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:22 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | MUMA2337-P3 | FLM_EM | MUMA2337 | Results: DOWN SITE HUB MUMA2337-P3 MUMA2337 Summary: Hub: MUMA2337, Down Count: 1, Down Sites: MUMA2337-P3 Alarm Summary: MUMA2337 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:21:44 | 10/26/2025 09:29:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000350 | PCM-20251026-00000720 | TT-20251026-00693 | Reference_telecom | Region_2 | RYD0939 | RYD0939 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/26/2025 09:22:21 | 10/26/2025 15:58:43 | 10/26/2025 21:22:21 | RF Unit RX Channel RTWP/RSSI Unbalanced at RYD0939-P3_SRAN @ Sceco | 10/26/2025 06:22:09 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/26/2025 06:22:06 | P3 | SRAN | rumah | Sceco | 2G NSA | RYD0939 | FLM_TE | [8 empty] | API | 10/26/2025 09:22:21 | 10/26/2025 09:23:44 | 10/26/2025 15:58:30 |  |  | 10/26/2025 15:58:43 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000351 | PCM-20251026-00000722 | TT-20251026-00582 | Telecom | Region_6 | QFL1MT0055 | QFL0055 | Equipment | BTS_Cable | Reconnect GPS Cable | Osama Hadi | 10/26/2025 09:22:35 | 10/26/2025 22:04:31 | 10/26/2025 15:22:35 | CELL SERVICE PROBLEM (Cell disabled due to unknown problem; logs collected) at QFL1MT0055-P3 @ Sceco | 10/26/2025 08:10:25 | Major | 7114 | CELL SERVICE PROBLEM | 10/26/2025 08:14:52 | P3 | 4G | jizan | Sceco | 5G_Cell SA | QFL1MT0055 | FLM_TE |  |  | PCM-20251026-00000599 | Request to check GPS Hw, cable connectivity & relocating the GPS where sky visibility will show excellent. | Request to check GPS Hw, cable connectivity & relocating the GPS where sky visibility will show excellent. |  |  |  | API | 10/26/2025 09:22:35 | 10/26/2025 12:33:11 | 10/26/2025 22:03:41 |  |  | 10/26/2025 22:04:31 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000353 | PCM-20251026-00000724 | TT-20251026-00698 | Telecom | Region_4 | JED0237 | JED0237 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 09:23:53 | 10/26/2025 10:36:49 | 10/26/2025 21:23:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0237-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 09:23:10 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:23:00 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0237 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:23:53 | 10/26/2025 10:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000354 | PCM-20251026-00000728 | TT-20251026-00689 | Telecom | Region_4 | MUMA1M8409 | MUMA2409 |  |  |  | Khizer Hayat | 10/26/2025 09:24:33 | 10/26/2025 11:14:19 | 10/26/2025 15:24:33 | 1(LTE) sites down under MUMA2409-G9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 09:16:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:16:09 | P3 | 4G | jeddah | Sceco | LTE SA | MUMA2409-G9-L8-L18-SBTS-P3 | FLM_TE | MUMA2409 | Results: DOWN SITE HUB MUMA2409-G9-L8-L18-SBTS-P3 MUMA2409 Summary: Hub: MUMA2409, Down Count: 1, Down Sites: MUMA2409-G9-L8-L18-SBTS-P3 Alarm Summary: MUMA2409 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.169.93.54:8080] [URL:http://10.169.93.54:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:24:33 | 10/26/2025 11:14:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000356 | PCM-20251026-00000731 | TT-20251026-00681 | Telecom | Region_4 | JDJZ0776 | JDJZ0776 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 09:26:13 | 10/26/2025 10:34:43 | 10/26/2025 11:26:13 | 34(2G) 14(3G) 20(LTE) 18(5G) sites down under JDJZ2181-P3 @ Generator_SG | 10/26/2025 09:13:28 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:21 | P1 | 2G | qunfuddah | Sceco_STB | 2G_3G_LTE_5G SA | SQUN0105-P3 LTE,JDJZ0775-P2 2G_3G_5G,QUN0338-P2-WBB-G3 2G_3G_LTE,SQUN0020 LTE,JDJZ0774-P1-VIP 2G_3G_5G,QUN0341-P1-VIP-WBB-G3 2G_3G_5G,BHMF2143-P3 2G_LTE,MUMA0772-P3 2G_3G_LTE,BHMF0858-P3 2G_5G,JDJZ2097-P3 2G_LTE,SQUN0008-P3 LTE,MUMA0781-P3-WBB-G3 2G_5G,MUMA2204-P3-CAP 2G_LTE,JDJZ2156-P3 2G_5G,FRS0085-P2-WBB-G3 2G_3G_LTE,QUN0334-P2 2G_3G_5G,QUN0337-P1-VIP 2G_3G,QUN0336-P2-WBB-G3 2G_3G,JDJZ0776-P1-HUB-FON-WBB-G3 2G_3G,QUN0335-P2 2G_3G,MUMA0774-P3-WBB-G3 2G_3G,FRS0086-P2-WBB-G3 2G_3G,MUMA0773-P3 2G_3G,JDJZ2181-P3 2G,BHMF2137-P3 2G,JDJZ2071-P3 2G,FRS2199-P3 2G,JDJZ2000-P3 2G,FRS2410-P3 2G,FRS2420-P3 2G,BHMF0857-P3-WBB-G3 2G,FRS2155-P3 2G,MUMA2198-P3-CAP 2G,NWN0477-P2 2G,MUMA2070-P3-P3 2G,BHMF2373-P3 2G,FRS2020-P3-CAP 2G | FLM_TE | JDJZ0776 | Dear team , HUB: JDJZ0776 We observing Visibility down at the HUB ,kindly check locally as HUB is P2 Router | PCM-20251026-00000715 | Dear team , HUB: JDJZ0776 We observing Visibility down at the HUB ,kindly check locally as HUB is P2 Router | Dear team , HUB: JDJZ0776 We observing Visibility down at the HUB ,kindly check locally as HUB is P2 Router |  | sites down |  | API | 10/26/2025 09:26:13 | 10/26/2025 09:54:24 | 10/26/2025 10:01:20 | 10/26/2025 10:01:23 | 10/26/2025 10:01:25 | 10/26/2025 10:34:43 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000357 | PCM-20251026-00000733 | TT-20251026-00682 | Telecom | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/26/2025 09:27:35 | 10/26/2025 18:53:31 | 10/26/2025 15:27:35 | 2(2G) 2(LTE) 1(5G) sites down under JED6020-GSM-P3,HBI2412-P3/HBI2412-P3 @ Generator_DG | 10/26/2025 09:13:33 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:13:22 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | HBI2412-P3 2G_LTE,JED6020-GSM-P3 2G | FLM_EM | JED6020 | DOWN SITE HUB TX FB JED6020 JED6020 Node Rebooted HBI2412 JDJZ0776 Check with IP Ran as HUB is P2 router | PCM-20251026-00000716 | DOWN SITE HUB TX FB JED6020 JED6020 Node Rebooted HBI2412 JDJZ0776 Check with IP Ran as HUB is P2 router | DOWN SITE HUB TX FB JED6020 JED6020 Node Rebooted HBI2412 JDJZ0776 Check with IP Ran as HUB is P2 router |  | sites down |  | API | 10/26/2025 09:27:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000358 | PCM-20251026-00000735 | TT-20251026-00699 | Telecom | Region_4 | SQUN1S7104 | SQUN0104 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:28:59 | 10/26/2025 12:28:57 | 10/26/2025 13:28:59 | 1(LTE) sites down under SQUN0104-P1-VIP @ Sceco | 10/26/2025 09:20:42 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:20:39 | VIP | 4G | qunfuddah | Sceco | LTE SA | SQUN0104-P1-VIP | FLM_TE | SQUN0104 | Results: DOWN SITE HUB SQUN0104-P1-VIP SQUN0104 Summary: Hub: SQUN0104, Down Count: 1, Down Sites: SQUN0104-P1-VIP Alarm Summary: SQUN0104 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.0.188:8080] [URL:http://10.98.0.188:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:28:59 | 10/26/2025 12:28:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000359 | PCM-20251026-00000736 | TT-20251026-00707 | Telecom | Region_6 | RJL1M7129 | RJL0129 |  |  |  | Muhammad Tayyab | 10/26/2025 09:29:03 | 10/26/2025 13:05:33 | 10/26/2025 21:29:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at RJL1M7129-G9-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 09:28:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:27:56 | P3 | 4G | mohail | Sceco | 5G_Cell SA | RJL1M7129 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:29:03 | 10/26/2025 13:05:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000363 | PCM-20251026-00000745 | TT-20251025-00872 | Reference_telecom | Region_4 | JED2561 | JED2561 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 09:34:13 | 10/26/2025 09:53:47 | 10/26/2025 21:34:13 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2561-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/25/2025 09:57:46 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 09:54:41 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2561 | FLM_TE |  |  | PCM-20251025-00000798 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/26/2025 09:34:13 | 10/26/2025 09:53:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000365 | PCM-20251026-00000751 | TT-20251026-00710 | Telecom | Region_4 | SQUN1S7106 | SQUN0106 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/26/2025 09:35:29 | 10/26/2025 23:30:41 | 10/26/2025 15:35:29 | 1(LTE) sites down under SQUN0106-P3 @ Sceco | 10/26/2025 09:27:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:27:09 | P3 | 4G | qunfuddah | Sceco | LTE SA | SQUN0106-P3 | FLM_TE | SQUN0106 | Results: DOWN SITE HUB SQUN0106-P3 SQUN0106 Summary: Hub: SQUN0106, Down Count: 1, Down Sites: SQUN0106-P3 Alarm Summary: SQUN0106 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.0.252:8080] [URL:http://10.98.0.252:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:35:29 | 10/26/2025 23:30:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000367 | PCM-20251026-00000752 | TT-20251026-00719 | Reference_EM | Region_3 | AHT2172 | AHT2172 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 09:35:46 | 10/27/2025 07:11:09 | 10/26/2025 21:35:46 | Mains Failure at AHT2172-P3_SRAN @ Sceco | 10/26/2025 09:25:41 | Minor | 65109 | Mains Failure | 10/26/2025 09:25:36 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2172 | FLM_EM | [8 empty] | API | 10/26/2025 09:35:46 | 10/27/2025 07:11:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000369 | PCM-20251026-00000754 | TT-20251026-00721 | Telecom | Region_3 | MDN0188 | MDN0188 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 09:36:17 | 10/26/2025 21:48:00 | 10/26/2025 21:36:17 | BBU DC Output Out of Range at MDN0188-P2_SRAN @ Sceco | 10/26/2025 09:33:26 | Minor | 26112 | BBU DC Output Out of Range | 10/26/2025 09:31:52 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0188 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:17 | 10/26/2025 11:11:26 | 10/26/2025 21:47:51 |  |  | 10/26/2025 21:48:00 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000370 | PCM-20251026-00000758 | TT-20251026-00725 | Reference_telecom | Region_4 | JED2601 | JED2601 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 09:36:48 | 10/26/2025 13:19:23 | 10/26/2025 21:36:48 | LagPortDown observed in JED2601 towards 10.3.232.164 @ Sceco | 10/25/2025 21:36:40 | Minor |  | LagPortDown | 10/25/2025 21:36:29 | P3 | 2G | jeddah | Sceco | TX NSA | JED2601 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:48 | 10/26/2025 13:19:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000371 | PCM-20251026-00000757 | TT-20251026-00724 | Reference_telecom | Region_4 | JED2602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 09:36:48 | 10/26/2025 13:19:23 | 10/26/2025 21:36:48 | LossOfSignal observed in JED2602_02 towards 10.3.232.163 @ Sceco | 10/25/2025 21:36:40 | Minor |  | LossOfSignal | 10/25/2025 21:36:28 | P3 | 2G | jeddah | Sceco | TX NSA | JED2602 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:48 | 10/26/2025 13:19:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000372 | PCM-20251026-00000756 | TT-20251026-00723 | Telecom | Region_3 | MDN0188 | MDN0188 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 09:36:49 | 10/26/2025 21:48:18 | 10/26/2025 21:36:49 | RF Unit Maintenance Link Failure at MDN0188-P2_SRAN @ Sceco | 10/26/2025 09:33:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 09:31:18 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0188 | FLM_TE | [8 empty] | API | 10/26/2025 09:36:49 | 10/26/2025 11:11:27 | 10/26/2025 21:48:07 |  |  | 10/26/2025 21:48:18 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000373 | PCM-20251026-00000759 | TT-20251026-00727 | Telecom | Region_4 | JED1MN2910 | JED2910 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 09:37:50 | 10/26/2025 10:36:49 | 10/26/2025 15:37:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/26/2025 09:36:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:36:43 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:37:50 | 10/26/2025 10:36:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000375 | PCM-20251026-00000763 | TT-20251026-00715 | Telecom | Region_4 | JED2234 | JED2234 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 09:40:18 | 10/26/2025 09:43:25 | 10/26/2025 15:40:18 | LOCAL BLOCK at JED2234-P3 @ Sceco | 10/26/2025 09:30:03 | Major | 7208 | LOCAL BLOCK | 10/26/2025 09:29:50 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2234 | FLM_TE |  |  | PCM-20251026-00000746 | HW alarm active on LTE, kindly check | HW alarm active on LTE, kindly check |  |  |  | API | 10/26/2025 09:40:18 | 10/26/2025 09:43:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000377 | PCM-20251026-00000769 | TT-20251026-00730 | Telecom | Region_4 | JED1M7685 | JED0685 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 09:44:38 | 10/26/2025 13:19:23 | 10/26/2025 15:44:38 | BASE STATION ANTENNA LINE PROBLEM at JED1M7685-CA-L900-L800-SBTS @ Sceco_STB | 10/26/2025 09:31:27 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 09:31:24 | P3 | 4G | jeddah | Sceco_STB | LTE NSA | JED1M7685 | FLM_TE |  |  | PCM-20251026-00000761 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/26/2025 09:44:38 | 10/26/2025 13:19:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000378 | PCM-20251026-00000770 | TT-20251026-00735 | Telecom | Region_4 | JED6028 | JED6028 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 09:46:07 | 10/26/2025 09:46:07 | 10/26/2025 15:46:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6028-GSM-P3 @ Sceco | 10/26/2025 09:45:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 09:45:13 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED6028 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 09:46:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000379 | PCM-20251026-00000771 | TT-20251026-00736 | EM | Region_3 | RUSF9024 | RUSF9024 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/26/2025 09:46:37 | 10/26/2025 09:46:37 | 10/26/2025 13:46:37 | RELAY_ALARM_MAJOR at RUSF9024_NE_1 @ Generator_DG | 10/26/2025 09:44:51 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/26/2025 09:44:41 | P3 | Repeater | madinah | Generator_DG | TX NSA | RUSF9024 | FLM_EM | [8 empty] | API | 10/26/2025 09:46:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000380 | PCM-20251026-00000772 | TT-20251025-00489 | Reference_telecom | Region_5 | MAK0760 | MAK0760 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 09:46:58 | 10/26/2025 09:46:58 | 10/26/2025 21:46:58 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MAK0760-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-NEW @ Sceco | 10/25/2025 05:53:02 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 05:52:55 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0760 | FLM_TE |  |  | PCM-20251025-00000424 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/26/2025 09:46:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000381 | PCM-20251026-00000774 | TT-20251025-00459 | Reference_telecom | Region_4 | JED1MN0202 | JED0202 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 09:47:45 | 10/26/2025 09:47:45 | 10/26/2025 15:47:45 | BASE STATION CONNECTIVITY PROBLEM (NR GTP-U Path Failure) at JED1MN0202-NR2.6-P2 @ Sceco | 10/25/2025 07:30:59 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 07:30:51 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0202 | FLM_TE |  |  | PCM-20251025-00000400 | Kindly check and support to restore as site is down | Kindly check and support to restore as site is down |  |  |  | API | 10/26/2025 09:47:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000382 | PCM-20251026-00000779 | TT-20251025-00107 | Reference_telecom | Region_4 | GMK1M7175 | GMK0175 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 09:48:24 | 10/26/2025 21:19:24 | 10/26/2025 21:48:24 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at GMK1M7175-G9-NL8-L18-SBTS-P2-USF @ Sceco | 10/25/2025 00:03:16 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/25/2025 00:03:13 | P2 | 4G | qunfuddah | Sceco | LTE NSA | GMK1M7175 | FLM_TE |  |  | PCM-20251025-00000101 | Kindly check high VSWR alarm is active | Kindly check high VSWR alarm is active |  |  |  | API | 10/26/2025 09:48:24 | 10/26/2025 21:19:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000383 | PCM-20251026-00000780 | TT-20251026-00700 | Reference_telecom | Region_4 | JDJZ0778-LL-CSG-01 | JDJZ0778 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 09:49:15 | 10/26/2025 12:28:57 | 10/26/2025 21:49:15 | MW Link Down at JDJZ0778-LL-CSG-01 To HLA0423 REF:TT-20251026-00504 @ Sceco_STB | 10/26/2025 07:29:36 | Minor | 101-2505274 | Physical Port Down | 10/26/2025 07:28:51 | P1 | IPRAN | qunfuddah | Sceco_STB | IPRAN SA | JDJZ0778-LL-CSG-01 | FLM_TE |  |  | PCM-20251026-00000726 | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . |  |  |  | API | 10/26/2025 09:49:15 | 10/26/2025 12:28:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000385 | PCM-20251026-00000787 | TT-20251026-00738 | Telecom | Region_6 | STLT1S7707 | STLT0707 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/26/2025 09:52:59 | 10/26/2025 10:47:41 | 10/26/2025 15:52:59 | 1(LTE) sites down under STLT0707-P3 @ Sceco | 10/26/2025 09:44:44 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 09:44:40 | P3 | 4G | tathleeth | Sceco | LTE SA | STLT0707-P3 | FLM_TE | STLT0707 | Results: DOWN SITE HUB STLT0707-P3 STLT0707 Summary: Hub: STLT0707, Down Count: 1, Down Sites: STLT0707-P3 Alarm Summary: STLT0707 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.89.119.148:8080] [URL:http://10.89.119.148:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 09:52:59 | 10/26/2025 10:47:25 | 10/26/2025 10:47:34 |  |  | 10/26/2025 10:47:41 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000387 | PCM-20251026-00000789 | TT-20251026-00741 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to SCECO failure, was auto restored | Waseem Shahzad Ghulam Rasool | 10/26/2025 09:53:59 | 10/26/2025 12:40:27 | 10/26/2025 13:53:59 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/26/2025 09:45:44 | Critical | 301 | NE Is Disconnected | 10/26/2025 09:45:42 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 09:53:59 | 10/26/2025 10:47:11 | 10/26/2025 12:39:31 |  |  | 10/26/2025 12:40:27 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000388 | PCM-20251026-00000791 | TT-20251026-00753 | EM | [7 empty] | 10/26/2025 09:54:54 | 10/26/2025 09:54:54 | 10/26/2025 13:54:54 | AIR CONDITION 1&2 at RPTRA-SEC0008_OCS @ Sceco | 10/26/2025 09:53:28 | Critical | 1-12307 | AIR CONDITION 1&2 | 10/26/2025 09:53:20 | P1 | DWDM |  | Sceco | DWDM NSA | RPTRA | FLM_EM | [5 empty] | 0-TO 8065-SEC0003&MJM0495(1-A)-71-E1EFI-[AIR CONDITION 1&2]:4 |  |  | API | 10/26/2025 09:54:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000393 | PCM-20251026-00000797 | TT-20251026-00761 | Reference_EM | Region_2 | QSRY0741 | QSRY0741 |  |  |  | Moin Uddin | 10/26/2025 10:01:06 | 10/26/2025 11:20:34 | 10/26/2025 22:01:06 | Fire Fighting system alarm at QSRY0741-P2_SRAN @ Sceco | 10/26/2025 09:50:56 | Minor | 65111 | Fire Fighting system alarm | 10/26/2025 09:50:54 | P2 | SRAN | muzamiah | Sceco | 2G NSA | QSRY0741 | FLM_EM | [8 empty] | API | 10/26/2025 10:01:06 | 10/26/2025 11:20:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000399 | PCM-20251026-00000809 | TT-20251026-00766 | Reference_EM | Region_1 | ARM2M1712 | ARM0712 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 10:07:17 | 10/26/2025 13:25:51 | 10/26/2025 22:07:17 | DC Power Fail at ARM2M1712-P3 @ Sceco | 10/26/2025 09:56:58 | Minor | 65106 | DC Power Fail | 10/26/2025 09:56:55 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1712 | FLM_EM | [8 empty] | API | 10/26/2025 10:07:17 | 10/26/2025 13:25:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000403 | PCM-20251026-00000820 | TT-20251026-00775 | Telecom | Region_4 | JED1MN2666 | JED2666 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 10:10:55 | 10/26/2025 10:24:21 | 10/26/2025 16:10:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2666-NR2.6-P3 @ Sceco | 10/26/2025 10:09:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:09:47 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2666 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:10:55 | 10/26/2025 10:24:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000406 | PCM-20251026-00000822 | TT-20251026-00777 | Telecom | Region_2 | RIY2M8278 | RIY2278 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Farmanullah Akbar Jan | 10/26/2025 10:12:20 | 10/26/2025 11:01:51 | 10/26/2025 16:12:20 | Cell Unavailable at RIY2M8278-P3-CA-L800 @ Sceco | 10/26/2025 10:10:03 | Major | 29240 | Cell Unavailable | 10/26/2025 10:08:30 | P3 | 4G | riyadh | Sceco | LTE SA | RIY2M8278 | FLM_TE | [8 empty] | API | 10/26/2025 10:12:20 | 10/26/2025 10:22:56 | 10/26/2025 11:01:25 | 10/26/2025 11:01:27 | 10/26/2025 11:01:30 | 10/26/2025 11:01:51 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000407 | PCM-20251026-00000825 | TT-20251026-00756 | Telecom | Region_4 | KHY2251 | KHY2251 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/26/2025 10:12:29 | 10/26/2025 10:12:29 | 10/26/2025 16:12:29 | 2(2G) 1(LTE) sites down under JED0296-P2-USF,KHY2251-P3/KHY2251-P3 @ Generator_SG | 10/26/2025 09:55:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 09:55:25 | P3 | 2G | jeddah | Generator_SG | 2G SA | JED0296-P2-USF 2G,KHY2251-P3 2G | FLM_EM | KHY2251 | JED0296 Visibility down KHY2251 Suspected power issue | PCM-20251026-00000804 | JED0296 Visibility down KHY2251 Suspected power issue | JED0296 Visibility down KHY2251 Suspected power issue |  | sites down |  | API | 10/26/2025 10:12:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000410 | PCM-20251026-00000836 | TT-20251026-00787 | Telecom | Region_2 | RIY2278 | RIY2278 | Equipment | SFP_BTS | Clean SFP | Farmanullah Akbar Jan | 10/26/2025 10:15:33 | 10/26/2025 11:10:26 | 10/26/2025 16:15:33 | BBU CPRI Interface Error at RIY2278-P3_SRAN-PC @ Sceco | 10/26/2025 10:10:56 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 10:08:23 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2278 | FLM_TE | [8 empty] | API | 10/26/2025 10:15:33 | 10/26/2025 11:09:39 | 10/26/2025 11:09:49 | 10/26/2025 11:09:53 | 10/26/2025 11:09:56 | 10/26/2025 11:10:26 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000411 | PCM-20251026-00000839 | TT-20251026-00791 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 10:17:07 | 10/26/2025 10:17:07 | 10/26/2025 22:17:07 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/26/2025 10:09:00 | Minor | 7103 | HIGH TEMP | 10/26/2025 10:08:52 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/26/2025 10:17:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000414 | PCM-20251026-00000843 | TT-20251026-00645 | Telecom | Region_2 | RIY2605-CSG-01 | RIY2605 | Transsmission | Fiber CUT | STC LL cut | Mubashar Farooq Abdul Majeed | 10/26/2025 10:20:06 | 10/26/2025 11:11:52 | 10/26/2025 14:20:06 | The Device is offline at RIY2605-CSG-01 @ Sceco | 10/26/2025 08:52:59 | Critical | 101-7 | The Device is offline | 10/26/2025 08:52:57 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIY2605-CSG-01 | FLM_TE |  |  | PCM-20251026-00000741 | Please re-check the power again , if no power issue please check the below ports and arrange with DMDM FL and DWDM BO IPRAN side : RIY2605-CSG-01 >>> GigabitEthernet0-3-0 RYQS0573-ZRi01-4-CSG-02 >>> GigabitEthernet0-9-0 | Please re-check the power again , if no power issue please check the below ports and arrange with DMDM FL and DWDM BO IPRAN side : RIY2605-CSG-01 >>> GigabitEthernet0-3-0 RYQS0573-ZRi01-4-CSG-02 >>> GigabitEthernet0-9-0 |  |  |  | API | 10/26/2025 10:20:06 | 10/26/2025 11:06:49 | 10/26/2025 11:06:56 | 10/26/2025 11:06:59 | 10/26/2025 11:07:03 | 10/26/2025 11:11:52 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000415 | PCM-20251026-00000844 | TT-20251026-00795 | EM | [7 empty] | 10/26/2025 10:20:13 | 10/26/2025 10:20:13 | 10/26/2025 22:20:13 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 10:11:50 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/26/2025 10:11:39 | P3 | 4G |  | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | API | 10/26/2025 10:20:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000418 | PCM-20251026-00000852 | TT-20251026-00794 | Telecom | Region_6 | QIS0102 | QIS0102 |  |  |  | Khurram Nawaz Muhammad Akram | 10/26/2025 10:25:08 | 10/26/2025 10:52:45 | 10/26/2025 16:25:08 | 2(2G) 2(3G) 2(LTE) sites down under WJZ0066-P3,QIS0102-P2/QIS0102-P2 @ Sceco | 10/26/2025 10:15:42 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:15:38 | P2 | 2G | jizan | Sceco | 2G_3G_LTE SA | WJZ0066-P3 2G_3G_LTE,QIS0102-P2 2G_3G_LTE | FLM_EM | QIS0102 | DOWN SITE HUB TX FB WJZ0066 WJZ0066 Suspected Power issue at HUB QIS0102 QIS0102 Suspected Power issue at HUB | PCM-20251026-00000850 | DOWN SITE HUB TX FB WJZ0066 WJZ0066 Suspected Power issue at HUB QIS0102 QIS0102 Suspected Power issue at HUB | DOWN SITE HUB TX FB WJZ0066 WJZ0066 Suspected Power issue at HUB QIS0102 QIS0102 Suspected Power issue at HUB |  | sites down |  | API | 10/26/2025 10:25:08 | 10/26/2025 10:52:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000420 | PCM-20251026-00000854 | TT-20251024-00668 | Reference_telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | SFP_BTS | Replace SFP | Fawad Khan | 10/26/2025 10:25:29 | 10/26/2025 18:29:17 | 10/26/2025 22:25:29 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/24/2025 10:39:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/24/2025 10:38:53 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251026-00000814 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:29 | 10/26/2025 10:31:21 | 10/26/2025 18:28:55 |  |  | 10/26/2025 18:29:17 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251025000607 | PCM-20251025-00001294 | TT-20251025-01355 | Reference_EM | Region_2 | RIY0797 | RIY0797 | Enviroment | Air Condition | Change Fan | Tanveer Ahmad Fateh Muhammad | 10/25/2025 15:43:35 | 10/25/2025 17:51:09 | 10/26/2025 03:43:35 | Air condition 1 failure alarm at RIY0797-P2_SRAN @ Sceco | 10/25/2025 15:35:47 | Minor | 65104 | Air condition 1 failure alarm | 10/25/2025 15:33:17 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0797 | FLM_EM | [8 empty] | API | 10/25/2025 15:43:35 | 10/25/2025 17:02:04 | 10/25/2025 17:38:10 | 10/25/2025 17:38:12 | 10/25/2025 17:38:13 | 10/25/2025 17:51:09 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000619 | PCM-20251025-00001319 | TT-20251025-01383 | Reference_EM | Region_1 | RFH0268 | RFH0268 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Bashir Sahib Rahman | 10/25/2025 15:56:31 | 10/25/2025 16:39:09 | 10/26/2025 03:56:31 | Air-Condition #1 FA(SH2) at RFH2M7268-P3-PC @ Power Cube | 10/25/2025 15:45:52 | Minor | 65052 | Air-Condition #1 FA(SH2) | 10/25/2025 15:45:48 | P3 | 4G | quriyat | Power Cube | 2G NSA | RFH2M7268 | FLM_EM | [8 empty] | API | 10/25/2025 15:56:31 | 10/25/2025 16:38:37 | 10/25/2025 16:38:56 |  |  | 10/25/2025 16:39:09 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000620 | PCM-20251025-00001321 | TT-20251025-01386 | Reference_EM | Region_1 | HFAP2035 | HFAP2035 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/25/2025 15:59:11 | 10/26/2025 15:47:33 | 10/25/2025 21:59:11 | Door opening alarm at HFAP2035-P1-HUB_SRAN @ Sceco | 10/25/2025 15:58:19 | Major | 65101 | Door opening alarm | 10/25/2025 15:58:15 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFAP2035 | FLM_EM | [8 empty] | API | 10/25/2025 15:59:11 | 10/26/2025 15:47:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000625 | PCM-20251025-00001332 | TT-20251025-01395 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 16:05:21 | 10/26/2025 10:21:02 | 10/26/2025 04:05:21 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/25/2025 15:55:04 | Minor | 65107 | Major Rec alarm | 10/25/2025 15:55:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/25/2025 16:05:21 | 10/26/2025 10:21:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000627 | PCM-20251025-00001335 | TT-20251025-01397 | Reference_EM | Region_1 | DAM2474 | DAM2474 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/25/2025 16:06:21 | 10/25/2025 22:23:51 | 10/25/2025 22:06:21 | Low battery voltage at DAM2474-P1-SHOP_SRAN @ Sceco | 10/25/2025 15:55:49 | Major | 65110 | Low battery voltage | 10/25/2025 15:55:45 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2474 | FLM_EM | [8 empty] | API | 10/25/2025 16:06:21 | 10/25/2025 22:23:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000645 | PCM-20251025-00001369 | TT-20251025-01430 | Reference_EM | Region_1 | HFAP2035 | HFAP2035 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/25/2025 16:23:56 | 10/26/2025 15:47:33 | 10/25/2025 22:23:56 | Major Rec alarm at HFAP2035-P1-HUB_SRAN @ Sceco | 10/25/2025 16:13:39 | Major | 65107 | Major Rec alarm | 10/25/2025 16:13:36 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFAP2035 | FLM_EM | [8 empty] | API | 10/25/2025 16:23:56 | 10/26/2025 15:47:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251025000648 | PCM-20251025-00001382 | TT-20251025-01442 | Reference_EM | Region_2 | RAS2248 | RAS2248 |  |  |  | Mohamed Alfatih Mohamed Eltayeb Mohamed | 10/25/2025 16:31:41 | 10/25/2025 16:31:41 | 10/25/2025 22:31:41 | Air condition 1 failure alarm at RAS2248-FWA-P1-VIP_SRAN @ Sceco | 10/25/2025 16:21:04 | Major | 65104 | Air condition 1 failure alarm | 10/25/2025 16:20:59 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS2248 | FLM_EM | [8 empty] | API | 10/25/2025 16:31:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000658 | PCM-20251025-00001404 | TT-20251025-01466 | Reference_EM | Region_2 | RIY2761 | RIY2761 |  |  |  | Adham Adham Hassan Farghal | 10/25/2025 16:46:41 | 10/26/2025 09:36:34 | 10/26/2025 04:46:41 | Mains Failure at RIY2761-P2_SRAN @ Sceco | 10/25/2025 16:36:35 | Minor | 65109 | Mains Failure | 10/25/2025 16:36:32 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2761 | FLM_EM | [8 empty] | API | 10/25/2025 16:46:41 | 10/26/2025 09:36:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000666 | PCM-20251025-00001431 | TT-20251025-01506 | Reference_EM | Region_2 | RIY0446 | RIY0446 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 17:10:55 | 10/26/2025 10:21:03 | 10/26/2025 05:10:55 | Minor Rec alarm at RIY0446-P2_SRAN @ Sceco | 10/25/2025 17:00:39 | Minor | 65108 | Minor Rec alarm | 10/25/2025 17:00:34 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0446 | FLM_EM | [8 empty] | API | 10/25/2025 17:10:55 | 10/26/2025 10:21:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000667 | PCM-20251025-00001432 | TT-20251025-01508 | Reference_EM | Region_1 | SAK0567 | SAK0567 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Amjad Muhammad | 10/25/2025 17:13:01 | 10/26/2025 15:22:24 | 10/26/2025 05:13:01 | Door opening alarm at SAK0567-P2_SRAN @ Sceco | 10/25/2025 17:12:20 | Minor | 65101 | Door opening alarm | 10/25/2025 17:12:17 | P2 | SRAN | sakaka | Sceco | 2G NSA | SAK0567 | FLM_EM | [8 empty] | API | 10/25/2025 17:13:01 | 10/26/2025 10:24:00 | 10/26/2025 15:22:11 |  |  | 10/26/2025 15:22:24 |  | Mohamed Amjad Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000668 | PCM-20251025-00001433 | TT-20251025-01510 | Reference_EM | Region_1 | DAM0440 | DAM0440 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/25/2025 17:13:31 | 10/26/2025 18:01:25 | 10/26/2025 05:13:31 | high temprature 40 at DAM0440-P2_SRAN @ Sceco | 10/25/2025 17:03:13 | Minor | 65103 | high temprature 40 | 10/25/2025 17:03:09 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0440 | FLM_EM | [8 empty] | API | 10/25/2025 17:13:31 | 10/25/2025 17:16:07 | 10/26/2025 18:01:17 |  |  | 10/26/2025 18:01:25 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000671 | PCM-20251025-00001446 | TT-20251025-01344 | Telecom | Region_1 | HMBY2429 | HMBY2429 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/25/2025 17:19:56 | 10/25/2025 17:48:27 | 10/26/2025 05:19:56 | Transmission Optical Interface Error at HMBY2429-P1-VIP_SRAN @ Generator_SG | 10/25/2025 15:32:43 | Minor | 26222 | Transmission Optical Interface Error | 10/25/2025 15:31:09 | VIP | SRAN | dammam | Generator_SG | 2G NSA | HMBY2429 | FLM_EM |  |  | PCM-20251025-00001284 | power issue at site | power issue at site |  |  |  | API | 10/25/2025 17:19:56 | 10/25/2025 17:46:04 | 10/25/2025 17:48:15 |  |  | 10/25/2025 17:48:27 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251025000678 | PCM-20251025-00001459 | TT-20251025-01531 | Reference_EM | Region_1 | ABQ0530 | ABQ0530 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 10/25/2025 17:27:01 | 10/26/2025 12:20:14 | 10/25/2025 23:27:01 | Door opening alarm at ABQ0530-P1-USF-HUB_SRAN-PC @ Power Cube | 10/25/2025 17:26:10 | Major | 65101 | Door opening alarm | 10/25/2025 17:26:06 | P1 | SRAN | dammam | Power Cube | 2G NSA | ABQ0530 | FLM_EM | [8 empty] | API | 10/25/2025 17:27:01 | 10/26/2025 12:19:56 | 10/26/2025 12:20:07 |  |  | 10/26/2025 12:20:14 |  | Ahmed AbdELmoaz Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000691 | PCM-20251025-00001493 | TT-20251025-01562 | Reference_EM | Region_1 | ABQ0530 | ABQ0530 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 10/25/2025 17:43:26 | 10/26/2025 12:20:24 | 10/25/2025 23:43:26 | Generator failure at ABQ0530-P1-USF-HUB_SRAN-PC @ Power Cube | 10/25/2025 17:33:05 | Major | 65114 | Generator failure | 10/25/2025 17:33:01 | P1 | SRAN | dammam | Power Cube | 2G NSA | ABQ0530 | FLM_EM | [8 empty] | API | 10/25/2025 17:43:26 | 10/26/2025 12:19:57 | 10/26/2025 12:20:18 |  |  | 10/26/2025 12:20:24 |  | Ahmed AbdELmoaz Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000702 | PCM-20251025-00001522 | TT-20251025-01588 | Reference_EM | Region_2 | HYN0067 | HYN0067 |  |  |  | Kazi Jalil Allimiya | 10/25/2025 18:00:06 | 10/26/2025 10:16:37 | 10/26/2025 06:00:06 | Door opening alarm at HYN0067-P3-USF_SRAN-PC @ Power Cube | 10/25/2025 17:59:26 | Minor | 65101 | Door opening alarm | 10/25/2025 17:52:35 | P3 | SRAN | aflaj | Power Cube | 2G NSA | HYN0067 | FLM_EM | [8 empty] | API | 10/25/2025 18:00:06 | 10/26/2025 10:16:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000705 | PCM-20251025-00001526 | TT-20251025-01593 | Reference_EM | Region_2 | RIY0395 | RIY0395 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 10/25/2025 18:08:51 | 10/27/2025 05:28:19 | 10/26/2025 06:08:51 | Door opening alarm at RIY0395-P2_SRAN @ Generator_SG | 10/25/2025 18:08:08 | Minor | 65101 | Door opening alarm | 10/25/2025 18:08:03 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0395 | FLM_EM | [8 empty] | API | 10/25/2025 18:08:51 | 10/27/2025 05:28:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000721 | PCM-20251025-00001556 | TT-20251025-01638 | EM | Region_1 | RYHR9915 | RYHR9915 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 18:42:56 | 10/26/2025 09:14:03 | 10/26/2025 06:42:56 | NETECO: Genset Work Abnormal at RYHR9915 @ Generator_SG | 10/25/2025 18:36:27 | Minor | 40561 | Genset Work Abnormal | 10/25/2025 18:36:27 | P3 | Repeater | hafr | Generator_SG | 2G NSA | RYHR9915 | FLM_EM | [8 empty] | API | 10/25/2025 18:42:56 | 10/25/2025 19:08:19 | 10/26/2025 09:13:55 |  |  | 10/26/2025 09:14:03 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000729 | PCM-20251025-00001571 | TT-20251025-01652 | EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 19:02:00 | 10/26/2025 09:20:15 | 10/26/2025 07:02:00 | NETECO: Communication Failure at RIY2431 @ Sceco | 10/25/2025 18:55:32 | Minor | 13750 | Communication Failure | 10/25/2025 18:55:32 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/25/2025 19:02:00 | 10/26/2025 09:20:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000734 | PCM-20251025-00001591 | TT-20251025-01671 | EM | Region_2 | RIY0041 | RIY0041 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 19:21:11 | 10/26/2025 09:20:16 | 10/25/2025 23:21:11 | Mains Failure at RIY0041-P1-DIA-WDM_SRAN @ Sceco | 10/25/2025 19:19:11 | Critical | 65109 | Mains Failure | 10/25/2025 19:19:07 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0041 | FLM_EM | [8 empty] | API | 10/25/2025 19:21:11 | 10/26/2025 09:20:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251025000735 | PCM-20251025-00001592 | TT-20251025-01672 | EM | Region_2 | RIY0041 | RIY0041 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/25/2025 19:21:40 | 10/26/2025 09:20:16 | 10/25/2025 23:21:40 | ACU FAILURE at RIY0041_HYB @ Sceco | 10/25/2025 19:19:45 | Critical | 1-12307 | ACU FAILURE | 10/25/2025 19:19:35 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0041 | FLM_EM | [5 empty] | 0-TO RIY0202(1-A)-72-E1EFI-ACU FAILURE:2 |  |  | API | 10/25/2025 19:21:40 | 10/26/2025 09:20:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251025000738 | PCM-20251025-00001596 | TT-20251025-01676 | EM | Region_1 | DAM0440 | DAM0440 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/25/2025 19:24:16 | 10/26/2025 11:03:39 | 10/26/2025 07:24:16 | TEMP_ALARM at DAM0440_NE_1_SDB @ Sceco | 10/25/2025 19:18:45 | Minor | 1-166 | TEMP_ALARM | 10/25/2025 19:18:35 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0440 | FLM_EM | [8 empty] | API | 10/25/2025 19:24:16 | 10/25/2025 19:59:22 | 10/26/2025 10:30:48 | 10/26/2025 10:30:51 | 10/26/2025 10:30:54 | 10/26/2025 11:03:39 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251025000748 | PCM-20251025-00001608 | TT-20251025-01691 | Reference_EM | Region_2 | RIY0518 | RIY0518 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/25/2025 19:33:35 | 10/26/2025 10:21:03 | 10/26/2025 07:33:35 | Minor Rec alarm at RIY0518-P2_SRAN @ Sceco | 10/25/2025 19:23:01 | Minor | 65108 | Minor Rec alarm | 10/25/2025 19:22:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0518 | FLM_EM | [8 empty] | API | 10/25/2025 19:33:35 | 10/26/2025 10:21:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000750 | PCM-20251025-00001610 | TT-20251025-01694 | Reference_EM | Region_2 | UNK0183 | UNK0183 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Omar Fathy Mahmoud Elsayed | 10/25/2025 19:37:10 | 10/25/2025 22:57:04 | 10/26/2025 07:37:10 | Door opening alarm at UNK2M5183-P3 @ Generator_SG | 10/25/2025 19:36:47 | Minor | 65101 | Door opening alarm | 10/25/2025 19:36:43 | P3 | 2G | buraidah | Generator_SG | 2G NSA | UNK2M5183 | FLM_EM | [8 empty] | API | 10/25/2025 19:37:10 | 10/25/2025 22:14:48 | 10/25/2025 22:15:31 | 10/25/2025 22:15:55 | 10/25/2025 22:16:12 | 10/25/2025 22:57:04 |  | Omar Fathy Mahmoud Elsayed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000752 | PCM-20251025-00001614 | TT-20251025-01698 | Reference_EM | Region_1 | ARM0879 | ARM0879 |  |  |  | Nazar Mohammed Siddig Abdalla | 10/25/2025 19:39:46 | 10/26/2025 14:55:15 | 10/26/2025 07:39:46 | Low battery voltage at ARM0879-P3_SRAN-PC @ Power Cube | 10/25/2025 19:35:16 | Minor | 65110 | Low battery voltage | 10/25/2025 19:29:10 | P3 | SRAN | hafouf | Power Cube | 2G NSA | ARM0879 | FLM_EM | [8 empty] | API | 10/25/2025 19:39:46 | 10/26/2025 14:55:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000758 | PCM-20251025-00001632 | TT-20251025-01721 | Reference_EM | Region_1 | HFF0224 | HFF0224 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/25/2025 19:58:21 | 10/26/2025 16:34:22 | 10/26/2025 07:58:21 | high temprature 40 at HFF0224-P3_SRAN @ Generator_SG | 10/25/2025 19:47:41 | Minor | 65103 | high temprature 40 | 10/25/2025 19:47:37 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | HFF0224 | FLM_EM | [8 empty] | API | 10/25/2025 19:58:21 | 10/26/2025 16:34:22 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000762 | PCM-20251025-00001638 | TT-20251025-01724 | Reference_EM | Region_1 | HFF0015 | HFF0015 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/25/2025 20:01:56 | 10/25/2025 21:13:40 | 10/26/2025 08:01:56 | Door opening alarm at HFF0015-P2_SRAN @ Sceco | 10/25/2025 20:01:24 | Minor | 65101 | Door opening alarm | 10/25/2025 20:01:21 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0015 | FLM_EM | [8 empty] | API | 10/25/2025 20:01:56 | 10/25/2025 20:48:15 | 10/25/2025 21:07:50 | 10/25/2025 21:07:57 | 10/25/2025 21:08:17 | 10/25/2025 21:13:40 |  | Shahid Khan Dilawar Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251025000773 | PCM-20251025-00001662 | TT-20251025-01738 | Reference_EM | Region_1 | RAF2521 | RAF2521 |  |  |  | Murtada Awad AbdElwahab Ahmed | 10/25/2025 20:32:26 | 10/25/2025 20:32:26 | 10/26/2025 08:32:26 | Mains Failure at RAF2521-P2-USF_SRAN @ Sceco | 10/25/2025 20:22:10 | Minor | 65109 | Mains Failure | 10/25/2025 20:22:05 | P2 | SRAN | rafha | Sceco | 2G NSA | RAF2521 | FLM_EM | [8 empty] | API | 10/25/2025 20:32:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000779 | PCM-20251025-00001678 | TT-20251025-01756 | Reference_EM | Region_1 | DMJ9917 | DMJ9917 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/25/2025 20:46:26 | 10/26/2025 16:15:13 | 10/26/2025 08:46:26 | Low fuel alarm at DMJ9917-RPT @ Generator_SG | 10/25/2025 20:35:51 | Minor | 65115 | Low fuel alarm | 10/25/2025 20:35:48 | P3 | Repeater | hafr | Generator_SG | 3G NSA | DMJ9917 | FLM_EM | [8 empty] | API | 10/25/2025 20:46:26 | 10/25/2025 20:51:02 | 10/26/2025 16:14:39 |  |  | 10/26/2025 16:15:13 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000809 | PCM-20251025-00001776 | TT-20251025-01838 | Reference_EM | Region_2 | RIY0185 | RIY0185 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Ajmal Hafeez Hafeez Ahmed Awan | 10/25/2025 22:09:01 | 10/25/2025 23:49:16 | 10/26/2025 10:09:01 | Door opening alarm at RIY0185-P2_SRAN @ Sceco | 10/25/2025 22:08:31 | Minor | 65101 | Door opening alarm | 10/25/2025 22:08:27 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0185 | FLM_EM | [8 empty] | API | 10/25/2025 22:09:01 | 10/25/2025 22:18:38 | 10/25/2025 23:14:46 | 10/25/2025 23:14:50 | 10/25/2025 23:14:57 | 10/25/2025 23:49:16 |  | Ajmal Hafeez Hafeez Ahmed Awan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000810 | PCM-20251025-00001782 | TT-20251025-01846 | Reference_EM | Region_2 | QSDH2711 | QSDH2711 | Equipment | FAN Cleaning | Clean FAN | Moustafa Elzaafarany Abdellah | 10/25/2025 22:15:46 | 10/25/2025 22:55:48 | 10/26/2025 10:15:46 | Door opening alarm at QSDH2711-P2_SRAN @ Generator_SG | 10/25/2025 22:15:23 | Minor | 65101 | Door opening alarm | 10/25/2025 22:15:20 | P2 | SRAN | dawadmi | Generator_SG | 2G NSA | QSDH2711 | FLM_EM | [8 empty] | API | 10/25/2025 22:15:46 | 10/25/2025 22:34:33 | 10/25/2025 22:34:50 | 10/25/2025 22:34:52 | 10/25/2025 22:34:54 | 10/25/2025 22:55:48 |  | Moustafa Elzaafarany Abdellah |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000813 | PCM-20251025-00001789 | TT-20251025-01857 | Reference_EM | Region_2 | RIY2923 | RIY2923 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/25/2025 22:25:36 | 10/26/2025 00:11:29 | 10/26/2025 10:25:36 | Generator failure at RIY2923-P2_SRAN @ Generator_SG | 10/25/2025 22:15:07 | Minor | 65114 | Generator failure | 10/25/2025 22:15:04 | P3 | SRAN | al kharj | Generator_SG | 2G NSA | RIY2923 | FLM_EM | [8 empty] | API | 10/25/2025 22:25:36 | 10/26/2025 00:11:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251025000815 | PCM-20251025-00001792 | TT-20251025-01860 | Reference_EM | Region_1 | KBR0200 | KBR0200 | Enviroment | Fire Alarm | Reset Fire Pannel | Abdul Malik Shaik | 10/25/2025 22:31:16 | 10/25/2025 23:49:22 | 10/26/2025 10:31:16 | Fire Fighting system alarm at KBR0200-P3_SRAN @ Sceco | 10/25/2025 22:20:58 | Minor | 65111 | Fire Fighting system alarm | 10/25/2025 22:20:53 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0200 | FLM_EM | [8 empty] | API | 10/25/2025 22:31:16 | 10/25/2025 22:36:07 | 10/25/2025 23:09:52 | 10/25/2025 23:09:55 | 10/25/2025 23:34:06 | 10/25/2025 23:49:22 |  | Abdul Malik Shaik |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251025000832 | PCM-20251025-00001840 | TT-20251025-01895 | EM | Region_2 | BRK9101 | BRK9101 |  |  |  | ABUZAR Ahmed Humida Mustafa | 10/25/2025 23:14:42 | 10/27/2025 02:18:30 | 10/26/2025 03:14:42 | RELAY_ALARM_CRITICAL at BRK9101_NE_1 @ Power Cube | 10/25/2025 23:13:42 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/25/2025 23:13:30 | P1 | Repeater | aflaj | Power Cube | TX NSA | BRK9101 | FLM_EM | [8 empty] | API | 10/25/2025 23:14:42 | 10/27/2025 02:18:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000006 | PCM-20251026-00000010 | TT-20251026-00011 | Reference_EM | Region_2 | UNZ0158 | UNZ0158 | Enviroment | Air Condition | Change Fan | Shahid Ahmed Shah Nawaz | 10/26/2025 00:12:31 | 10/26/2025 01:26:40 | 10/26/2025 12:12:31 | Air condition 2 failure alarm at UNZ0158-P2_SRAN @ Sceco | 10/26/2025 00:01:55 | Minor | 65105 | Air condition 2 failure alarm | 10/26/2025 00:01:52 | P2 | SRAN | buraidah | Sceco | 2G NSA | UNZ0158 | FLM_EM | [8 empty] | API | 10/26/2025 00:12:31 | 10/26/2025 00:15:25 | 10/26/2025 00:34:23 | 10/26/2025 00:34:25 | 10/26/2025 01:01:33 | 10/26/2025 01:26:40 |  | Shahid Ahmed Shah Nawaz |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000011 | PCM-20251026-00000018 | TT-20251026-00012 | Telecom | Region_2 | RIY0707 | RIY0707 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/26/2025 00:17:51 | 10/26/2025 00:17:51 | 10/26/2025 12:17:51 | RF Unit Maintenance Link Failure at RIY0707-P1-VIP-DIA_SRAN @ Sceco | 10/26/2025 00:10:34 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 00:08:51 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0707 | FLM_EM |  |  | PCM-20251026-00000013 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 00:17:51 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000012 | PCM-20251026-00000020 | TT-20251026-00020 | Reference_EM | Region_1 | ARM0993 | ARM0993 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 00:18:40 | 10/26/2025 02:32:30 | 10/26/2025 12:18:40 | Generator failure at ARM0993-P2_SRAN-PC @ Power Cube | 10/26/2025 00:08:15 | Minor | 65114 | Generator failure | 10/26/2025 00:08:12 | P2 | SRAN | hafouf | Power Cube | 2G NSA | ARM0993 | FLM_EM | [8 empty] | API | 10/26/2025 00:18:40 | 10/26/2025 02:32:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000018 | PCM-20251026-00000030 | TT-20251026-00024 | Reference_EM | Region_1 | JBL0471 | JBL0471 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 00:21:45 | 10/26/2025 00:28:23 | 10/26/2025 06:21:45 | Mains Failure at JBL0471-P1-DIA_SRAN @ Sceco | 10/26/2025 00:11:49 | Major | 65109 | Mains Failure | 10/26/2025 00:11:45 | P1 | SRAN | jubail | Sceco | 2G NSA | JBL0471 | FLM_EM | [8 empty] | API | 10/26/2025 00:21:45 | 10/26/2025 00:28:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000022 | PCM-20251026-00000055 | TT-20251026-00042 | Reference_EM | Region_2 | HIL2471 | HIL2471 |  |  |  | Farman Ullah Muhammad Nazir | 10/26/2025 00:34:11 | 10/26/2025 12:27:16 | 10/26/2025 12:34:11 | Door opening alarm at HIL2471-P2_SRAN @ Sceco | 10/26/2025 00:33:46 | Minor | 65101 | Door opening alarm | 10/26/2025 00:33:41 | P2 | SRAN | al rass | Sceco | 2G NSA | HIL2471 | FLM_EM | [8 empty] | API | 10/26/2025 00:34:11 | 10/26/2025 12:27:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000023 | PCM-20251026-00000057 | TT-20251026-00043 | EM | Region_1 | URY9013 | URY9013 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/26/2025 00:34:46 | 10/26/2025 10:24:37 | 10/26/2025 12:34:46 | NETECO: Speed Sensor Failure at URY9013 @ Power Cube | 10/26/2025 00:27:59 | Minor | 8143 | Speed Sensor Failure | 10/26/2025 00:27:59 | P3 | Repeater | jubail | Power Cube | 2G NSA | URY9013 | FLM_EM | [8 empty] | API | 10/26/2025 00:34:46 | 10/26/2025 10:24:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000028 | PCM-20251026-00000071 | TT-20251026-00054 | Reference_EM | Region_1 | ARM0881 | ARM0881 |  |  |  | Nazar Mohammed Siddig Abdalla | 10/26/2025 00:45:35 | 10/26/2025 14:55:16 | 10/26/2025 12:45:35 | Generator failure at ARM0881-P3_SRAN-PC @ Power Cube | 10/26/2025 00:35:05 | Minor | 65114 | Generator failure | 10/26/2025 00:35:01 | P3 | SRAN | hafouf | Power Cube | 2G NSA | ARM0881 | FLM_EM | [8 empty] | API | 10/26/2025 00:45:35 | 10/26/2025 14:55:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000031 | PCM-20251026-00000075 | TT-20251026-00057 | Reference_EM | Region_1 | KBR0200 | KBR0200 | Enviroment | Fire Alarm | Reset Fire Pannel | Abdul Malik Shaik | 10/26/2025 00:51:45 | 10/26/2025 22:08:21 | 10/26/2025 12:51:45 | Door opening alarm at KBR0200-P3_SRAN @ Sceco | 10/26/2025 00:51:23 | Minor | 65101 | Door opening alarm | 10/26/2025 00:51:19 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0200 | FLM_EM | [8 empty] | API | 10/26/2025 00:51:45 | 10/26/2025 20:09:08 | 10/26/2025 21:23:50 | 10/26/2025 21:23:52 | 10/26/2025 21:27:01 | 10/26/2025 22:08:21 |  | Abdul Malik Shaik |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000032 | PCM-20251026-00000076 | TT-20251026-00060 | Reference_EM | Region_2 | RIY0430 | RIY0430 |  |  |  | Amr Abbas Zaghloul Abbas | 10/26/2025 00:54:21 | 10/26/2025 00:54:21 | 10/26/2025 06:54:21 | Door opening alarm at RIY0430-P1-HUB_SRAN-FON @ Sceco | 10/26/2025 00:53:34 | Major | 65101 | Door opening alarm | 10/26/2025 00:53:31 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0430 | FLM_EM | [8 empty] | API | 10/26/2025 00:54:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000054 | PCM-20251026-00000111 | TT-20251026-00084 | Reference_EM | Region_2 | RAS0044 | RAS0044 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Shazlly Mahmoud Abouzied Mahmoud | 10/26/2025 01:17:05 | 10/26/2025 03:02:09 | 10/26/2025 13:17:05 | Minor Rec alarm at RAS0044-P2_SRAN @ Sceco | 10/26/2025 01:06:42 | Minor | 65108 | Minor Rec alarm | 10/26/2025 01:06:40 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS0044 | FLM_EM | [8 empty] | API | 10/26/2025 01:17:05 | 10/26/2025 01:53:24 | 10/26/2025 01:54:13 | 10/26/2025 01:54:16 | 10/26/2025 02:19:30 | 10/26/2025 03:02:09 |  | Shazlly Mahmoud Abouzied Mahmoud |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000055 | PCM-20251026-00000115 | TT-20251026-00086 | Reference_EM | Region_1 | YBR0669 | YBR0669 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 01:20:18 | 10/26/2025 02:32:31 | 10/26/2025 13:20:18 | DC power fail at YBR0669-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 01:09:40 | Minor | 65106 | DC power fail | 10/26/2025 01:09:36 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0669 | FLM_EM | [8 empty] | API | 10/26/2025 01:20:18 | 10/26/2025 02:32:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000069 | PCM-20251026-00000152 | TT-20251026-00113 | Reference_EM | Region_1 | YBR0603 | YBR0603 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 01:50:06 | 10/26/2025 02:32:32 | 10/26/2025 13:50:06 | DC power fail at YBR0603-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 01:39:36 | Minor | 65106 | DC power fail | 10/26/2025 01:39:32 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0603 | FLM_EM | [8 empty] | API | 10/26/2025 01:50:06 | 10/26/2025 02:32:32 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000080 | PCM-20251026-00000168 | TT-20251026-00129 | EM | Region_1 | KBR0163 | KBR0163 | Enviroment | Air Condition | Change Fan | Yasser Mohamed Abdelnabi Ibrahim | 10/26/2025 02:03:30 | 10/26/2025 04:33:52 | 10/26/2025 06:03:30 | high temprature 40 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 01:59:10 | Critical | 65103 | high temprature 40 | 10/26/2025 01:59:07 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/26/2025 02:03:30 | 10/26/2025 04:28:06 | 10/26/2025 04:33:34 |  |  | 10/26/2025 04:33:52 |  | Yasser Mohamed Abdelnabi Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251026000111 | PCM-20251026-00000222 | TT-20251026-00187 | Reference_EM | Region_1 | YBR0725 | YBR0725 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 02:47:26 | 10/26/2025 19:19:03 | 10/26/2025 14:47:26 | Door opening alarm at YBR0725-P2-USF_SRAN-PC @ Power Cube | 10/26/2025 02:46:52 | Minor | 65101 | Door opening alarm | 10/26/2025 02:46:48 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0725 | FLM_EM | [8 empty] | API | 10/26/2025 02:47:26 | 10/26/2025 19:19:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000117 | PCM-20251026-00000238 | TT-20251026-00209 | Reference_EM | Region_1 | JBKH2338 | JBKH2338 |  |  |  | Dileesh Muringothil Devarajan | 10/26/2025 03:10:46 | 10/26/2025 10:40:27 | 10/26/2025 09:10:46 | Mains Failure at JBKH2338-P1-VIP_ARP_SRAN @ Sceco | 10/26/2025 03:00:44 | Major | 65109 | Mains Failure | 10/26/2025 03:00:40 | VIP | SRAN | khafji | Sceco | 2G NSA | JBKH2338 | FLM_EM | [8 empty] | API | 10/26/2025 03:10:46 | 10/26/2025 10:40:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000171 | PCM-20251026-00000349 | TT-20251026-00328 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/26/2025 04:57:36 | 10/26/2025 09:15:49 | 10/26/2025 16:57:36 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/26/2025 04:51:09 | Minor | 40564 | Genset Fault | 10/26/2025 04:51:09 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/26/2025 04:57:36 | 10/26/2025 09:14:30 | 10/26/2025 09:15:38 |  |  | 10/26/2025 09:15:49 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251026000180 | PCM-20251026-00000367 | TT-20251026-00342 | Reference_EM | Region_2 | RIY2131 | RIY2131 | Enviroment | Air Condition | Change Fan | Ajmal Hafeez Hafeez Ahmed Awan | 10/26/2025 05:15:41 | 10/26/2025 05:51:10 | 10/26/2025 17:15:41 | high temprature 40 at RIY2131-P2_SRAN @ Sceco | 10/26/2025 05:05:02 | Minor | 65103 | high temprature 40 | 10/26/2025 05:04:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2131 | FLM_EM | [8 empty] | API | 10/26/2025 05:15:41 | 10/26/2025 05:37:16 | 10/26/2025 05:37:52 | 10/26/2025 05:37:56 | 10/26/2025 05:38:00 | 10/26/2025 05:51:10 |  | Ajmal Hafeez Hafeez Ahmed Awan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251026000192 | PCM-20251026-00000397 | TT-20251026-00372 | Reference_EM | Region_1 | TRF2507 | TRF2507 | Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator Battery | Ragab Farg Abdel Nabi Bekhatro | 10/26/2025 05:42:01 | 10/26/2025 11:49:57 | 10/26/2025 17:42:01 | Low battery voltage at TRF2507-P2-USF_SRAN @ Generator_SG | 10/26/2025 05:31:24 | Minor | 65110 | Low battery voltage | 10/26/2025 05:31:22 | P2 | SRAN | arar | Generator_SG | 2G NSA | TRF2507 | FLM_EM | [8 empty] | API | 10/26/2025 05:42:01 | 10/26/2025 06:20:05 | 10/26/2025 11:25:50 | 10/26/2025 11:25:54 | 10/26/2025 11:25:57 | 10/26/2025 11:49:57 |  | Ragab Farg Abdel Nabi Bekhatro |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000196 | PCM-20251026-00000406 | TT-20251026-00379 | Reference_EM | Region_2 | RIY2704 | RIY2704 | Enviroment | Genset failure_AVR | Change Generator AVR | Mahmoud Hefny Ali Ahmed | 10/26/2025 05:52:56 | 10/26/2025 08:26:25 | 10/26/2025 11:52:56 | Air condition 2 failure alarm at RIY2704-P1-VIP_SRAN @ Sceco | 10/26/2025 05:42:25 | Major | 65105 | Air condition 2 failure alarm | 10/26/2025 05:42:22 | VIP | SRAN | muzamiah | Sceco | 2G NSA | RIY2704 | FLM_EM | [8 empty] | API | 10/26/2025 05:52:56 | 10/26/2025 07:50:20 | 10/26/2025 07:51:16 | 10/26/2025 07:51:20 | 10/26/2025 08:00:34 | 10/26/2025 08:26:25 |  | Mahmoud Hefny Ali Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251026000203 | PCM-20251026-00000414 | TT-20251026-00388 | Reference_EM | Region_2 | RIY0748 | RIY0748 |  |  |  | Moin Uddin | 10/26/2025 06:00:41 | 10/26/2025 11:21:04 | 10/26/2025 18:00:41 | Minor Rec alarm at RIY0748-P2_SRAN @ Sceco | 10/26/2025 05:50:25 | Minor | 65108 | Minor Rec alarm | 10/26/2025 05:50:21 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0748 | FLM_EM | [8 empty] | API | 10/26/2025 06:00:41 | 10/26/2025 11:20:32 | 10/26/2025 11:20:59 | 10/26/2025 11:21:01 | 10/26/2025 11:21:04 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000209 | PCM-20251026-00000415 | TT-20251026-00389 | Reference_EM | Region_2 | RIY0573 | RIY0573 |  |  |  | Moin Uddin | 10/26/2025 06:01:10 | 10/26/2025 11:20:32 | 10/26/2025 18:01:10 | Mains Failure at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 05:00:43 | Minor | 65109 | Mains Failure | 10/26/2025 04:59:54 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_EM | [8 empty] | API | 10/26/2025 06:01:10 | 10/26/2025 11:20:32 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000215 | PCM-20251026-00000435 | TT-20251026-00391 | Reference_telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Moin Uddin | 10/26/2025 06:10:01 | 10/26/2025 11:20:33 | 10/26/2025 18:10:01 | RF Unit RX Channel RTWP/RSSI Too Low at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 05:43:14 | Minor | 26521 | RF Unit RX Channel RTWP/RSSI Too Low | 10/26/2025 05:43:10 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_EM |  |  | PCM-20251026-00000417 | power alarms reported | power alarms reported |  |  |  | API | 10/26/2025 06:10:01 | 10/26/2025 11:20:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000216 | PCM-20251026-00000437 | TT-20251026-00394 | Telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Moin Uddin | 10/26/2025 06:10:21 | 10/26/2025 11:20:33 | 10/26/2025 12:10:21 | BBU CPRI Interface Error at RIY0573-P2_SRAN-FON @ Sceco | 10/26/2025 05:02:59 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 05:31:29 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_EM |  |  | PCM-20251026-00000420 | power alarms reported | power alarms reported |  |  |  | API | 10/26/2025 06:10:21 | 10/26/2025 11:20:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000228 | PCM-20251026-00000458 | TT-20251026-00419 | Reference_EM | Region_1 | QRH2432 | QRH2432 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/26/2025 06:30:36 | 10/26/2025 13:23:46 | 10/26/2025 12:30:36 | Mains Failure at QRH2M2432-P1-VIP @ Generator_SG | 10/26/2025 06:20:37 | Major | 65109 | Mains Failure | 10/26/2025 06:20:31 | VIP | 2G | dammam | Generator_SG | 2G NSA | QRH2M2432 | FLM_EM | [8 empty] | API | 10/26/2025 06:30:36 | 10/26/2025 06:33:39 | 10/26/2025 12:49:19 | 10/26/2025 12:49:23 | 10/26/2025 13:12:35 | 10/26/2025 13:23:46 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000244 | PCM-20251026-00000493 | TT-20251026-00485 | EM | Region_1 | DMJR0165 | DMJR0165 | Transsmission | IPRAN_Fluctuation | Change Port | Hassan rabie | 10/26/2025 07:06:45 | 10/27/2025 00:01:40 | 10/26/2025 11:06:45 | Genset running at DMJR0165-P1-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 07:04:53 | Critical | 65112 | Genset running | 10/26/2025 07:04:50 | P1 | SRAN | arar | Sceco_STB | 2G NSA | DMJR0165 | FLM_EM | [8 empty] | API | 10/26/2025 07:06:45 | 10/26/2025 20:42:52 | 10/27/2025 00:01:32 |  |  | 10/27/2025 00:01:40 |  | Hassan rabie |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000263 | PCM-20251026-00000530 | TT-20251026-00527 | Reference_EM | Region_2 | DUB0015 | DUB0015 | Enviroment | Genset failure_Pump | Change Fuel Pump | Fritz Ian Generale | 10/26/2025 07:48:35 | 10/26/2025 10:36:29 | 10/26/2025 19:48:35 | Generator failure at DUB0015-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 07:38:04 | Minor | 65114 | Generator failure | 10/26/2025 07:38:00 | P3 | SRAN | al kharj | Power Cube | 2G NSA | DUB0015 | FLM_EM | [8 empty] | API | 10/26/2025 07:48:35 | 10/26/2025 10:35:24 | 10/26/2025 10:35:57 | 10/26/2025 10:35:59 | 10/26/2025 10:36:03 | 10/26/2025 10:36:29 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000266 | PCM-20251026-00000535 | TT-20251026-00529 | Reference_EM | Region_2 | RYAB0604 | RYAB0604 |  |  |  | Kazi Jalil Allimiya | 10/26/2025 07:50:19 | 10/26/2025 10:16:38 | 10/26/2025 19:50:19 | high temprature 40 at RYAB0604-P3_SRAN @ Sceco | 10/26/2025 07:39:43 | Minor | 65103 | high temprature 40 | 10/26/2025 07:39:39 | P3 | SRAN | al kharj | Sceco | 2G NSA | RYAB0604 | FLM_EM | [8 empty] | API | 10/26/2025 07:50:19 | 10/26/2025 10:16:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000270 | PCM-20251026-00000546 | TT-20251026-00540 | Reference_EM | Region_2 | RIY2112 | RIY2112 |  |  |  | Vignesh Sivakumar Sivakumar | 10/26/2025 07:55:17 | 10/26/2025 13:03:06 | 10/26/2025 13:55:17 | Mains Failure at RIY2112-P1-SHOP_SRAN @ Sceco | 10/26/2025 07:44:55 | Major | 65109 | Mains Failure | 10/26/2025 07:44:51 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2112 | FLM_EM | [8 empty] | API | 10/26/2025 07:55:17 | 10/26/2025 13:03:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251026000276 | PCM-20251026-00000559 | TT-20251026-00551 | Reference_EM | Region_1 | JBL0441 | JBL0441 | Enviroment | Genset failure_High Temperature | Change Generator radiator | Ahmed Hassan Ahmed Hassanin | 10/26/2025 08:02:31 | 10/26/2025 18:53:31 | 10/26/2025 20:02:31 | Generator failure at JBL0441-P3_SRAN @ Generator_DG | 10/26/2025 07:52:08 | Minor | 65114 | Generator failure | 10/26/2025 07:52:04 | P3 | SRAN | jubail | Generator_DG | 2G NSA | JBL0441 | FLM_EM | [8 empty] | API | 10/26/2025 08:02:31 | 10/26/2025 16:34:17 | 10/26/2025 18:53:24 |  |  | 10/26/2025 18:53:31 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000296 | PCM-20251026-00000619 | TT-20251026-00606 | Reference_EM | Region_2 | RYRN0633 | RYRN0633 |  |  |  | Saleem Khan Amir Dost | 10/26/2025 08:30:55 | 10/26/2025 10:06:27 | 10/26/2025 20:30:55 | Mains Failure at RYRN2M5633-P3 @ Sceco | 10/26/2025 08:20:51 | Minor | 65109 | Mains Failure | 10/26/2025 08:20:41 | P3 | 2G | quweyah | Sceco | 2G NSA | RYRN2M5633 | FLM_EM | [8 empty] | API | 10/26/2025 08:30:55 | 10/26/2025 10:06:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251026000303 | PCM-20251026-00000628 | TT-20251026-00615 | Reference_EM | Region_1 | HRBD0125 | HRBD0125 | Equipment | Power Cable_RRU_BTS | Change Port on DCDU | Mahmoud Youssef Mohamed Ahmed | 10/26/2025 08:35:36 | 10/26/2025 11:16:09 | 10/26/2025 14:35:36 | Mains Failure at HRBD0125-P1-HUB_SRAN @ Generator_SG | 10/26/2025 08:25:41 | Major | 65109 | Mains Failure | 10/26/2025 08:25:36 | P1 | SRAN | hafr | Generator_SG | 2G NSA | HRBD0125 | FLM_EM | [8 empty] | API | 10/26/2025 08:35:36 | 10/26/2025 09:06:45 | 10/26/2025 10:13:37 | 10/26/2025 10:13:40 | 10/26/2025 10:15:46 | 10/26/2025 11:16:09 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000315 | PCM-20251026-00000649 | TT-20251026-00634 | Reference_EM | Region_2 | KHJ0469 | KHJ0469 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/26/2025 08:47:25 | 10/26/2025 08:47:25 | 10/26/2025 20:47:25 | High temperature 32C alarm at KHJ2M1469-P3 @ Sceco | 10/26/2025 08:37:06 | Minor | 65102 | High temperature 32C alarm | 10/26/2025 08:37:02 | P3 | 2G | al kharj | Sceco | 2G NSA | KHJ2M1469 | FLM_EM | [8 empty] | API | 10/26/2025 08:47:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000321 | PCM-20251026-00000670 | TT-20251026-00658 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 08:59:22 | 10/26/2025 09:36:34 | 10/26/2025 14:59:22 | high temprature 32 at RIY0232-P1_SRAN @ Sceco | 10/26/2025 08:48:57 | Major | 65102 | high temprature 32 | 10/26/2025 08:48:53 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/26/2025 08:59:22 | 10/26/2025 09:36:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000325 | PCM-20251026-00000680 | TT-20251026-00665 | Reference_EM | Region_1 | HFF0821 | HFF0821 |  |  |  | Moustafa Mohamed Saleh Saif | 10/26/2025 09:04:31 | 10/26/2025 10:59:18 | 10/26/2025 21:04:31 | high temprature 40 at HFF0821-P2-USF_SRAN-PC @ Power Cube | 10/26/2025 08:54:06 | Minor | 65103 | high temprature 40 | 10/26/2025 08:54:02 | P2 | SRAN | hafouf | Power Cube | 2G NSA | HFF0821 | FLM_EM | [8 empty] | API | 10/26/2025 09:04:31 | 10/26/2025 10:59:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000329 | PCM-20251026-00000689 | TT-20251026-00672 | Reference_EM | Region_2 | RIY2068 | RIY2068 |  |  |  | Kadri Jalal Mohammed Asmail | 10/26/2025 09:09:10 | 10/26/2025 11:00:33 | 10/26/2025 21:09:10 | Door opening alarm at RIY2068-P3_SRAN @ Sceco | 10/26/2025 09:08:32 | Minor | 65101 | Door opening alarm | 10/26/2025 09:08:28 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2068 | FLM_EM | [8 empty] | API | 10/26/2025 09:09:10 | 10/26/2025 11:00:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000333 | PCM-20251026-00000694 | TT-20251026-00675 | Reference_EM | Region_1 | JBL0441 | JBL0441 | Enviroment | Genset failure_High Temperature | Change Generator water pump | Ahmed Hassan Ahmed Hassanin | 10/26/2025 09:13:15 | 10/26/2025 18:53:20 | 10/26/2025 21:13:15 | Door opening alarm at JBL0441-P3_SRAN @ Generator_DG | 10/26/2025 09:12:42 | Minor | 65101 | Door opening alarm | 10/26/2025 09:12:40 | P3 | SRAN | jubail | Generator_DG | 2G NSA | JBL0441 | FLM_EM | [8 empty] | API | 10/26/2025 09:13:15 | 10/26/2025 16:34:19 | 10/26/2025 18:53:14 |  |  | 10/26/2025 18:53:20 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000344 | PCM-20251026-00000709 | TT-20251026-00685 | Reference_EM | Region_2 | RIY0046 | RIY0046 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 09:18:56 | 10/26/2025 09:36:35 | 10/26/2025 15:18:56 | Mains Failure at RIY0046-P1-DIA_SRAN-FON @ Sceco | 10/26/2025 09:08:59 | Major | 65109 | Mains Failure | 10/26/2025 09:08:56 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0046 | FLM_EM | [8 empty] | API | 10/26/2025 09:18:56 | 10/26/2025 09:36:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251026000347 | PCM-20251026-00000711 | TT-20251026-00686 | Reference_EM | Region_2 | QSHL0890 | QSHL0890 | Enviroment | SCECO_Failure | SCECO auto restored | Farman Ullah Muhammad Nazir | 10/26/2025 09:19:32 | 10/26/2025 12:27:39 | 10/26/2025 21:19:32 | Mains Failure at QSHL0890-P2_SRAN @ Sceco | 10/26/2025 09:09:06 | Minor | 65109 | Mains Failure | 10/26/2025 09:09:03 | P2 | SRAN | buraidah | Sceco | 2G NSA | QSHL0890 | FLM_EM | [8 empty] | API | 10/26/2025 09:19:32 | 10/26/2025 12:27:17 | 10/26/2025 12:27:31 |  |  | 10/26/2025 12:27:39 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000352 | PCM-20251026-00000723 | TT-20251026-00695 | Reference_EM | Region_2 | MZH0491 | MZH0491 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/26/2025 09:23:06 | 10/26/2025 15:20:47 | 10/26/2025 21:23:06 | Generator failure at MZH0491-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 09:12:33 | Minor | 65114 | Generator failure | 10/26/2025 09:12:30 | P3 | SRAN | muzamiah | Power Cube | 2G NSA | MZH0491 | FLM_EM | [8 empty] | API | 10/26/2025 09:23:06 | 10/26/2025 15:20:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000364 | PCM-20251026-00000748 | TT-20251026-00716 | Reference_EM | Region_2 | AFL0018 | AFL0018 | Enviroment | SCECO_Failure | SCECO auto restored | Irfan Yousaf | 10/26/2025 09:35:00 | 10/26/2025 20:34:54 | 10/26/2025 21:35:00 | Generator failure at AFL0018-P3-USF_SRAN-PC @ Power Cube | 10/26/2025 09:24:24 | Minor | 65114 | Generator failure | 10/26/2025 09:24:20 | P3 | SRAN | al kharj | Power Cube | 2G NSA | AFL0018 | FLM_EM | [8 empty] | API | 10/26/2025 09:35:00 | 10/26/2025 09:40:27 | 10/26/2025 20:34:32 |  |  | 10/26/2025 20:34:54 |  | Irfan Yousaf |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000389 | PCM-20251026-00000793 | TT-20251026-00757 | Reference_EM | Region_2 | RIY2343 | RIY2343 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 09:58:45 | 10/26/2025 10:21:04 | 10/26/2025 15:58:45 | Door opening alarm at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:58:15 | Major | 65101 | Door opening alarm | 10/26/2025 09:58:11 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2343 | FLM_EM | [8 empty] | API | 10/26/2025 09:58:45 | 10/26/2025 10:21:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000390 | PCM-20251026-00000794 | TT-20251026-00759 | Reference_EM | Region_1 | TBSK0244 | TBSK0244 | Equipment | PMR_Power_Cable_RRU | Change Port on FPFH | Mahmoud Abdelwanis Massoud Elrashidy | 10/26/2025 09:59:16 | 10/26/2025 15:20:15 | 10/26/2025 21:59:16 | high temprature 32 at TBSK0244-ODC-ENV-ALM @ Generator_DG | 10/26/2025 09:48:49 | Minor | 65102 | high temprature 32 | 10/26/2025 09:48:44 | P3 | SRAN | sakaka | Generator_DG | 2G NSA | TBSK0244 | FLM_EM | [8 empty] | API | 10/26/2025 09:59:16 |  | 10/26/2025 12:01:30 | 10/26/2025 12:01:35 | 10/26/2025 12:01:38 | 10/26/2025 15:20:15 |  | Mahmoud Abdelwanis Massoud Elrashidy |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251026000392 | PCM-20251026-00000796 | TT-20251026-00760 | Reference_EM | Region_2 | RIY2278 | RIY2278 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:00:51 | 10/26/2025 10:21:04 | 10/26/2025 22:00:51 | Mains Failure at RIY2278-P3_SRAN-PC @ Sceco | 10/26/2025 09:50:51 | Minor | 65109 | Mains Failure | 10/26/2025 09:50:49 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2278 | FLM_EM | [8 empty] | API | 10/26/2025 10:00:51 | 10/26/2025 10:21:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000400 | PCM-20251026-00000812 | TT-20251026-00770 | Reference_EM | Region_2 | RIY2343 | RIY2343 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:08:36 | 10/26/2025 11:40:02 | 10/26/2025 16:08:36 | Mains Failure at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:58:15 | Major | 65109 | Mains Failure | 10/26/2025 09:58:11 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2343 | FLM_EM | [8 empty] | API | 10/26/2025 10:08:36 | 10/26/2025 10:21:04 | 10/26/2025 10:21:43 | 10/26/2025 10:21:46 | 10/26/2025 10:46:53 | 10/26/2025 11:40:02 |  | Tanveer Ahmad Muhammad Ishaq |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251026000404 | PCM-20251026-00000819 | TT-20251026-00774 | Reference_EM | Region_1 | DAM0642 | DAM0642 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/26/2025 10:11:11 | 10/26/2025 11:23:21 | 10/26/2025 22:11:11 | high temprature 32 at DAM0642-P3_SRAN @ Sceco | 10/26/2025 10:00:37 | Minor | 65102 | high temprature 32 | 10/26/2025 10:00:34 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM0642 | FLM_EM | [8 empty] | API | 10/26/2025 10:11:11 | 10/26/2025 11:22:13 | 10/26/2025 11:23:15 | 10/26/2025 11:23:19 | 10/26/2025 11:23:21 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000405 | PCM-20251026-00000821 | TT-20251026-00776 | Reference_EM | Region_1 | HFF2397 | HFF2397 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/26/2025 10:11:40 | 10/26/2025 16:34:23 | 10/26/2025 22:11:40 | Mains Failure at HFF2397-P3_SRAN @ Sceco | 10/26/2025 10:01:20 | Minor | 65109 | Mains Failure | 10/26/2025 10:01:16 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF2397 | FLM_EM | [8 empty] | API | 10/26/2025 10:11:40 | 10/26/2025 16:34:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000412 | PCM-20251026-00000840 | TT-20251026-00763 | Telecom | Region_2 | RIY2343 | RIY2343 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/26/2025 10:17:31 | 10/26/2025 10:21:05 | 10/26/2025 22:17:31 | RF Unit Maintenance Link Failure at RIY2343-P1_SRAN @ Sceco | 10/26/2025 09:59:57 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 09:58:15 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2343 | FLM_EM |  |  | PCM-20251026-00000805 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 10:17:31 | 10/26/2025 10:21:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000416 | PCM-20251026-00000846 | TT-20251026-00797 | Reference_EM | Region_2 | QSDH0709 | QSDH0709 |  |  |  | Mahmoud Hefny Ali Ahmed | 10/26/2025 10:22:31 | 10/26/2025 10:37:41 | 10/26/2025 22:22:31 | Mains Failure at QSDH0709-P2_SRAN @ Sceco | 10/26/2025 10:12:30 | Minor | 65109 | Mains Failure | 10/26/2025 10:12:26 | P2 | SRAN | dawadmi | Sceco | 2G NSA | QSDH0709 | FLM_EM | [8 empty] | API | 10/26/2025 10:22:31 | 10/26/2025 10:37:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000417 | PCM-20251026-00000848 | TT-20251026-00799 | Reference_EM | Region_1 | HFBD2011 | HFBD2011 |  |  |  | Montasir Awadalla Abdalla Bala | 10/26/2025 10:23:02 | 10/26/2025 19:19:06 | 10/26/2025 16:23:02 | Generator failure at HFBD2011-P1-HUB_SRAN @ Generator_SG | 10/26/2025 10:12:35 | Major | 65114 | Generator failure | 10/26/2025 10:12:32 | P1 | SRAN | hafouf | Generator_SG | 2G NSA | HFBD2011 | FLM_EM | [8 empty] | API | 10/26/2025 10:23:02 | 10/26/2025 19:19:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000421 | PCM-20251026-00000855 | TT-20251025-00883 | Reference_telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Fawad Khan | 10/26/2025 10:25:39 | 10/26/2025 18:28:44 | 10/26/2025 22:25:39 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/25/2025 11:53:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 11:53:39 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251026-00000811 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:39 | 10/26/2025 10:31:21 | 10/26/2025 18:27:36 |  |  | 10/26/2025 18:28:44 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000422 | PCM-20251026-00000856 | TT-20251026-00287 | Telecom | Region_6 | SDA0507 | SDA0507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 10:25:48 | 10/26/2025 14:06:51 | 10/26/2025 22:25:48 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at SDA0507-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Generator_SG | 10/26/2025 04:15:41 | Minor | 7114 | CELL SERVICE PROBLEM | 10/26/2025 04:15:34 | P3 | 2G | abha | Generator_SG | 5G_Cell SA | SDA0507 | FLM_TE |  |  | PCM-20251026-00000312 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:48 | 10/26/2025 14:04:42 | 10/26/2025 14:06:40 |  |  | 10/26/2025 14:06:51 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000423 | PCM-20251026-00000857 | TT-20251026-00141 | Reference_telecom | Region_4 | JED1U6052 | JED6152 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 10:25:55 | 10/26/2025 10:25:55 | 10/26/2025 16:25:55 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/26/2025 02:00:23 | Major | 7654 | CELL OPERATION DEGRADED | 10/26/2025 02:00:10 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251026-00000181 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:25:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000424 | PCM-20251026-00000858 | TT-20251025-00218 | Reference_telecom | Region_5 | MAK1U6909 | MAK6009 |  |  |  | Mosab Nasr eldeen Mohamed | 10/26/2025 10:26:02 | 10/26/2025 10:26:02 | 10/26/2025 16:26:02 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at MAK1U6909-CA-P1-HRM-SBTS @ Sceco | 10/25/2025 03:33:35 | Major | 7654 | CELL OPERATION DEGRADED | 10/25/2025 03:33:26 | P1 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6909 | FLM_TE |  |  | PCM-20251025-00000197 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:26:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000425 | PCM-20251026-00000859 | TT-20251024-01373 | Reference_telecom | Region_5 | MAK1U6907 | MAK6007 |  |  |  | Mosab Nasr eldeen Mohamed | 10/26/2025 10:26:08 | 10/26/2025 10:26:08 | 10/26/2025 22:26:08 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at MAK1U6907-CA-SBTS-P3 @ Sceco | 10/24/2025 21:14:31 | Minor | 7654 | CELL OPERATION DEGRADED | 10/24/2025 21:14:21 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6907 | FLM_TE |  |  | PCM-20251024-00001250 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 10:26:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000426 | PCM-20251026-00000860 | TT-20251026-00801 | Telecom | Region_6 | BLJ0046-LL-CSG-01 | BLJ0046 | Transsmission | SFP_Transmission | Reset SFP | Manzoor Ahmed | 10/26/2025 10:26:56 | 10/26/2025 11:12:41 | 10/26/2025 22:26:56 | Bad Package Error Rising at BLJ0046-LL-CSG-01 @ Sceco | 10/26/2025 10:26:30 | Minor | 101-2501403 | Bad Package Error Rising | 10/26/2025 10:26:23 | P2 | IPRAN | Albaha | Sceco | IPRAN NSA | BLJ0046-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 10:26:56 | 10/26/2025 10:52:42 | 10/26/2025 11:12:26 |  |  | 10/26/2025 11:12:41 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000428 | PCM-20251026-00000863 | TT-20251026-00807 | Reference_EM | Region_1 | ARM0886 | ARM0886 |  |  |  | Dileesh Muringothil Devarajan | 10/26/2025 10:29:29 | 10/26/2025 10:40:27 | 10/26/2025 16:29:29 | Mains Failure at ARM0886-P1-VIP_SRAN @ Sceco | 10/26/2025 10:19:31 | Major | 65109 | Mains Failure | 10/26/2025 10:19:27 | VIP | SRAN | khafji | Sceco | 2G NSA | ARM0886 | FLM_EM | [8 empty] | API | 10/26/2025 10:29:29 | 10/26/2025 10:40:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000429 | PCM-20251026-00000866 | TT-20251026-00810 | Telecom | Region_2 | RIY2M7399 | RIY0399 | Equipment | BSS_HW_fault | Replace RFU | Muhammad Naseer Muhammad Nazir | 10/26/2025 10:30:42 | 10/27/2025 07:03:36 | 10/26/2025 16:30:42 | Cell Unavailable at RIY2M7399-P2-L900-L800 @ Sceco | 10/26/2025 10:29:18 | Major | 29240 | Cell Unavailable | 10/26/2025 10:27:46 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7399 | FLM_TE | [8 empty] | API | 10/26/2025 10:30:42 | 10/27/2025 07:01:18 | 10/27/2025 07:02:51 |  |  | 10/27/2025 07:03:36 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000430 | PCM-20251026-00000867 | TT-20251026-00813 | Reference_EM | Region_3 | RSP0036 | RSP0036 |  |  |  | Sayed Satoor | 10/26/2025 10:32:04 | 10/26/2025 13:56:13 | 10/26/2025 16:32:04 | high temprature 40 at RSP0036-P1-VIP_SRAN @ Generator_SG | 10/26/2025 10:21:46 | Major | 65103 | high temprature 40 | 10/26/2025 10:21:40 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0036 | FLM_EM | [8 empty] | API | 10/26/2025 10:32:04 | 10/26/2025 13:56:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000431 | PCM-20251026-00000869 | TT-20251026-00785 | Telecom | Region_4 | YLM1M7391 | YLM0391 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 10:33:03 | 10/26/2025 21:19:25 | 10/26/2025 14:33:03 | PLR threshold crossed on TWAMP-1 at 131 sites under R4 | 10/26/2025 10:07:24 | Critical | 61611 | TWAMP PLR Threshold Crossed | 10/26/2025 10:07:24 | P1 | 4G | alaith | Generator_SG | 2G_3G_LTE_5G SA | YLM1M7391-L800-P1-SBTS YLM1M7876-L800-SBTS-P1 MKYL1M7912-G9-U9-NL8-SBTS-P2 NNL1M7137-G9-NL8-L18-SBTS-P3 GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 HAM1M7025-G9-U9-NL8-SBTS-P2-USF NSH1M7168-G9-U9-NL8-SBTS-P3 GMK1M7175-G9-NL8-L18-SBTS-P2-USF YLM1M8369-L800-P1-SBTS GMK1M7349-L800-CA-P3-USF SIR1M7050-G9-U9-NL8-SBTS-P2-USF NNL1M7084-G9-NL8-L18-SBTS-P2-USF LTH2121-G9-L8-L18-L21-NR2.6-SBTS-P3 LTH1M8122-CA-L800-SBTS HLA1M8095-G9-L8-L18-L21-SBTS-P3 HLA1M7424-P2-CA-L800-SBTS JED1M7839-CA-L900-P1-VIP HLA1M7422-P3-CA-L800-SBTS-WBB-G3 HLA1M7425-P3-L800 LTH2201-G9-L8-L18-L21-NNR2.6-SBTS-P3 NNL1M7139-G9-U9-NL8-SBTS-P3 SDY1M7163-G9-U9-NL8-SBTS-P3 LTH0329-G9-L8-L18-L21-NR2.6-SBTS-P2 SQSH1M7150-G9-NL8-L18-SBTS-P2-USF YLM1M7789-L800-P3 SQSH1M7022-USF-P3 NNL1M7164-G9-U9-NL8-SBTS-P3 LTH0638-G9-L8-L18-L21-NR2.6-SBTS-P2 UKHA1M7733-G9-U9-NL8-P1-HUB-USF JDMD1M7861-L800-SBTS-P2 MKMD1M7556-L800-P2 JDMD1M7863-G9-L8-SBTS-P1-HUB-USF MKMD1M7555-L800-P2 FRJ1M7043-G9-U9-NL8-NL18-SBTS-P2-USF GMQ1M7153-G9-U9-NL8-SBTS-P2-USF MLJI1M7095-G9-U9-NL8-SBTS-P2-USF SHB1M7611-CA SDY1M7738-G9-U9-NL8-SBTS-P1 DKA1M7347-G9-L8-L18-SBTS-P3 BIK1M7153-L800-CA-P3 GMK1M7167-L800-SBTS-P3 MKMD1M8252-P3-L800 JED2928-G9-L18-NNR2.6-SBTS-P3 JZMA1M8202-G9-L8-SBTS-P3 NSH1M7218-USF-P3 SIR1M7125-USF-P3 HAM1M7357-USF-L800-L2100-P3 JDJZ0771-G9-L8-L18-L21-NNR2.6-SBTS-P1-HUB-USF GMQ1M7038-G9-U9-NL8-NL18-SBTS-P2-USF BIK1M7154-G9-U9-NL8-NL18-SBTS-P2 HJR1M7149-USF-P3 UKZ1M7067-USF-P3-L800 JDJZ1M7769-G9-U9-NL8-NL18-NL21-SBTS-P1-USF SDY1M7766-L800-SBTS-P3 JDJZ0774-G9-L8-L18-L21-NNR2.6-SBTS-P1-VIP NNL1M7104-G9-L8-SBTS-P3 NSH1M7128-G9-NL8-L18-SBTS-P2-USF JDJZ1M7776-P1-CA-L800 FRS2020-G9-L8-L18-L21-SBTS-P3 JDJZ2156-G9-L8-L18-SBTS-P3 MKYL1M7908-P2 MUMA1M8204-G9-L8-L18-L21-SBTS-P3-CAP MUMA0781-G9-L8-L18-SBTS-P3 JDJZ1M7777-G9-L8-L18-L21-SBTS-P2-HUB-WBB-G3 SIR1M7155-G9-U9-NL8-SBTS-P2-USF YLM1M7740-USF-P3 HBI1M7353-G9-L8-L18-SBTS-P3 MKSH1M7170-G9-U9-NL8-SBTS-P2-USF JZMA1M7822-G9-L8-NL18-SBTS-P2-WBB-G3 JZMA1M7824-G9-L8-SBTS-P3 JDJZ1M8418-G9-L8-L18-SBTS-CAP UKZ1M7166-USF-P3 THA1M7736-P3-CA-L800-WBB-G3 JZMA1M8415-G9-L8-L18-SBTS-P3 MLJI1M7374-G9-U9-NL8-SBTS-P2-USF HBI1M8412-G9-L8-L18-SBTS-P3 NSH1M7165-G9-L9-L18-SBTS-P3 NWN1M7477-G9-NL8-L18-L21-SBTS-P2 QAL1M7721-G9-L18-SBTS-P2-USF QUZ1M7738-P3-CA-L800 QUZ1M8417-G9-L8-L18-L21-SBTS NNL1M7102-USF-P3 UKHA1M7731-G9-L18-SBTS-P1-HUB-USF MUMA1M7772-G9-L8-SBTS-P3 BHMF1M7857-G9-L8-L18-SBTS-P3 NSH1M7127-USF-P3 JZMA1M8101-G9-L8-L18-SBTS-P3-CAP UKHA1M7630-CA-L800-USF-P3 QHN1M7737-P3-CA-L800 QUN1M7336-CA-L800-P3 HLA1M8439-G9-L8-L18-L21-SBTS DGB1M8169-USF-P3 FRS2155-G9-L8-L18-L21-SBTS-P3 QUZ0739-L800-L1800-CA-NR2.6-FWA-P1-VIP JZMA1M8414-G9-L8-L18-L21-SBTS-P3-CAP HBI1M8008-G9-L8-L18-L21-SBTS-P3 BHMF1M8137-G9-L8-L18-SBTS-P3 BHMF1M8143-G9-L8-L18-SBTS-P3 QUN0341-G9-L8-L18-L21-SBTS-P1-VIP JDJZ2000-G9-L8-L18-SBTS-P3 GMK1M7442-G-U9-NL8-NL18-SBTS-P2-USF SHB1M7671-P3 JDJZ1M7778-G9-L8-L18-SBTS-P1-HUB-FON QUN1M7334-CA-L800-P3 UKHA1M7028-G9-L18-SBTS-P1-HUB ASQ1M7342-P1-HUB-USF YLM1M7752-P1-L800-SBTS HLA1M7423-P1-HUB-CA-L800 UKHA1M7344-G9-NL8-NL18-SBTS-P1-HUB BHMF1M8373-G9-L8-SBTS-P3 JZMA1M7825-G9-U9-NL8-NL18-NL21-SBTS-P2-WBB-G3 BHMF0858-L800-SBTS-P3 HLA1MT0423-P1 NNL1M7158-G9-U9-L18-SBTS-P3 FRS1M7086-G9-L8-L18-L21-SBTS-P2-WBB-G3 QUN0337-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP QUN1M7335-P2-CA-L800 JDJZ1M8097-G9-L8-L18-L21-SBTS-P3 FRS1M7085-G9-L8-SBTS-P2 GMK1M7350-G9-U9-NL8-SBTS-P2-USF MLJI1M7103-G9-U9-NL8-SBTS-P2-USF QUN1M7338-CA-L800-P3 MUMA1M8070-G9-L8-L18-L21-SBTS-P3 MUMA1M8198-G9-L8-L18-L21-SBTS-P3-CAP NNL1M7101-G9-U9-NL8-SBTS-P3 LTH0330-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB GMK1M7046-G9-NL8-L18-SBTS-P2-USF FRS2410-G9-L8-L18-L21-SBTS-P3 FRS2420-G9-L8-L18-SBTS-P3 JDJZ1M8181-G9-L8-L18-SBTS-P3 KUL1M7006-USF-P3 | FLM_TE |  |  | PCM-20251026-00000833 | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . | Dear FLM team, Kindly perform HC for MW JDJZ9048-JDJZ0776 PM errors on Modem 6 currently muted as WA . |  |  |  | API | 10/26/2025 10:33:03 | 10/26/2025 21:19:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000432 | PCM-20251026-00000870 | TT-20251026-00816 | Telecom | Region_6 | DRB0902 | DRB0902 | Equipment | CB_BTS | Replace CB on Rectifier | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 10:33:07 | 10/26/2025 17:05:18 | 10/26/2025 16:33:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at DRB0902-GSM-UMTS-P3 @ Sceco | 10/26/2025 10:32:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:32:18 | P3 | 2G | derb | Sceco | 5G_Cell SA | DRB0902 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:33:07 | 10/26/2025 11:04:27 | 10/26/2025 17:05:10 |  |  | 10/26/2025 17:05:18 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000433 | PCM-20251026-00000877 | TT-20251026-00826 | Telecom | Region_6 | JDJZ1M7885 | JDJZ0885 | Equipment | CB_BTS | Replace CB on Rectifier | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 10:42:55 | 10/26/2025 17:26:39 | 10/26/2025 22:42:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JDJZ1M7885-G9-U9-L18-SBTS-P2-HUB @ Sceco_STB | 10/26/2025 10:42:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:42:07 | P1 | 4G | derb | Sceco_STB | 5G_Cell SA | JDJZ1M7885 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:42:55 | 10/26/2025 11:04:27 | 10/26/2025 17:26:30 |  |  | 10/26/2025 17:26:39 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000434 | PCM-20251026-00000879 | TT-20251026-00831 | Reference_EM | Region_1 | HFB2M5001 | HFB0001 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/26/2025 10:44:59 | 10/26/2025 10:44:59 | 10/26/2025 16:44:59 | Mains Failure at HFB2M5001-P1-DIA @ Generator_SG | 10/26/2025 10:35:05 | Major | 65109 | Mains Failure | 10/26/2025 10:35:02 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5001 | FLM_EM | [8 empty] | API | 10/26/2025 10:44:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000435 | PCM-20251026-00000882 | TT-20251026-00835 | Reference_EM | Region_2 | RIYD6037 | RIYD6037 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 10:46:33 | 10/26/2025 10:46:33 | 10/26/2025 16:46:33 | high temprature 32 at RIYD6037-P1-VIP_SRAN @ Sceco | 10/26/2025 10:25:30 | Major | 65102 | high temprature 32 | 10/26/2025 10:46:22 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_EM | [8 empty] | API | 10/26/2025 10:46:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000436 | PCM-20251026-00000884 | TT-20251026-00836 | EM | Region_6 | BSA1M8289 | BSA2289 |  |  |  | Asad Saddiq | 10/26/2025 10:47:03 | 10/26/2025 14:02:40 | 10/26/2025 22:47:03 | SHELTER DOOR OPEN;Default System Time at BSA1M8289-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 10:46:56 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/26/2025 03:01:03 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BSA1M8289 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 10:47:03 | 10/26/2025 14:02:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000437 | PCM-20251026-00000886 | TT-20251026-00838 | EM | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Gamal Mohamed Farag | 10/26/2025 10:47:04 | 10/26/2025 23:44:11 | 10/26/2025 22:47:04 | HIGH TEMPERATURE 32 DEGREE C at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/26/2025 10:39:06 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/26/2025 10:38:56 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7558 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/26/2025 10:47:04 | 10/26/2025 23:44:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000438 | PCM-20251026-00000888 | TT-20251026-00843 | Telecom | Region_6 | ARF1MN0066 | ARF0066 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/26/2025 10:48:36 | 10/26/2025 12:40:56 | 10/26/2025 16:48:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at ARF1MN0066-NR2.6-P3 @ Sceco_STB | 10/26/2025 10:47:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:47:34 | P3 | 5G | al harja | Sceco_STB | 5G_Cell SA | ARF1MN0066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 10:48:36 | 10/26/2025 12:40:02 | 10/26/2025 12:40:13 | 10/26/2025 12:40:30 |  | 10/26/2025 12:40:56 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000440 | PCM-20251026-00000891 | TT-20251026-00848 | EM | Region_4 | TF1_CORE | TF1 |  |  |  | Farghal Ashour Hassan Farghal | 10/26/2025 10:49:07 | 10/26/2025 16:01:58 | 10/26/2025 16:49:07 | DOOR OPEN ALARM at TF1_CORE-P1-VIP @ Sceco_STB | 10/26/2025 10:48:35 | Major | 7103 | DOOR OPEN ALARM | 10/26/2025 10:48:31 | P1 | BSC | taif | Sceco_STB | 2G NSA | TF1_CORE | FLM_EM | [5 empty] | DOOR OPEN ALARM |  |  | API | 10/26/2025 10:49:07 | 10/26/2025 16:01:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000441 | PCM-20251026-00000892 | TT-20251026-00851 | EM | Region_6 | KHS0333 | KHS0333 |  |  |  | Amir Abbas Arif Raza | 10/26/2025 10:50:40 | 10/26/2025 10:50:40 | 10/26/2025 22:50:40 | SHELTER DOOR OPEN;Default System Time at KHS0333-GSM-UMTS-P2-USF @ Sceco | 10/26/2025 10:50:07 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/26/2025 03:01:17 | P2 | 2G | khamis mushyet | Sceco | 2G NSA | KHS0333 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/26/2025 10:50:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000442 | PCM-20251026-00000897 | TT-20251026-00842 | EM | Region_6 | KHS0333 | KHS0333 |  |  |  | Amir Abbas Arif Raza | 10/26/2025 10:53:29 | 10/26/2025 10:53:29 | 10/26/2025 16:53:29 | 1(2G/3G/5G) sites down under KHS0333-P2-USF/KHS0333-P2-USF @ Sceco | 10/26/2025 10:45:28 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:45:25 | P2 | 2G | khamis mushyet | Sceco | 2G_3G_5G SA | KHS0333-P2-USF | FLM_EM | KHS0333 | Results: DOWN SITE HUB KHS0333-P2-USF KHS0333 Summary: Hub: KHS0333, Down Count: 1, Down Sites: KHS0333-P2-USF Alarm Summary: KHS0333 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 10:53:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000444 | PCM-20251026-00000898 | TT-20251026-00859 | Telecom | Region_2 | RAS2248 | RAS2248 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Syed Sibtain Naqvi SyedManzoor | 10/26/2025 10:53:46 | 10/26/2025 14:40:30 | 10/26/2025 22:53:46 | ALD Maintenance Link Failure at RAS2248-FWA-P1-VIP_SRAN @ Sceco | 10/26/2025 10:51:18 | Minor | 26541 | ALD Maintenance Link Failure | 10/26/2025 10:49:43 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS2248 | FLM_TE | [8 empty] | API | 10/26/2025 10:53:46 | 10/26/2025 12:29:02 | 10/26/2025 12:29:19 | 10/26/2025 12:29:21 | 10/26/2025 13:32:26 | 10/26/2025 14:40:30 |  | Syed Sibtain Naqvi SyedManzoor |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000454 | PCM-20251026-00000924 | TT-20251008-02080 | MW_HC | Region_5 | MAK0755 | MAK0755 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 11:05:43 | 10/26/2025 12:56:58 | 10/26/2025 23:05:43 | Nokia MW HC_P1 Observing Performance Issue at MAK0755-MAK0520 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK0755-MAK0520 | FLM_TE |  |  | PCM-20251026-00000851 | approved | approved |  |  |  | API | 10/26/2025 11:05:43 | 10/26/2025 12:56:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000456 | PCM-20251026-00000928 | TT-20251026-00890 | Reference_EM | Region_3 | YBDB0979 | YBDB0979 | Enviroment | Air Condition | Change compressor | Eid Fawzi Sayed Ali | 10/26/2025 11:07:44 | 10/26/2025 19:24:48 | 10/26/2025 23:07:44 | high temprature 32 at YBDB0979-P2_SRAN @ Sceco | 10/26/2025 10:57:24 | Minor | 65102 | high temprature 32 | 10/26/2025 10:57:20 | P3 | SRAN | tabouk | Sceco | 2G NSA | YBDB0979 | FLM_EM | [8 empty] | API | 10/26/2025 11:07:44 | 10/26/2025 19:24:15 | 10/26/2025 19:24:37 |  |  | 10/26/2025 19:24:48 |  | Eid Fawzi Sayed Ali |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000457 | PCM-20251026-00000927 | TT-20251026-00891 | Telecom | Region_2 | DWD2113 | DWD2113 |  |  |  | Zakir Muhammad Yar Muhammad | 10/26/2025 11:07:44 | 10/26/2025 11:07:44 | 10/26/2025 23:07:44 | NR DU Cell TRP Unavailable at DWD2113-P3_SRAN @ Sceco | 10/26/2025 11:01:04 | Minor | 29870 | NR DU Cell TRP Unavailable | 10/26/2025 10:59:32 | P3 | SRAN | dawadmi | Sceco | 2G NSA | DWD2113 | FLM_TE | [8 empty] | API | 10/26/2025 11:07:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000460 | PCM-20251026-00000933 | TT-20251026-00897 | EM | Region_3 | RSP0812 | RSP0812 | Enviroment | SCECO_Failure | SCECO auto restored | Sayed Satoor | 10/26/2025 11:09:47 | 10/26/2025 16:08:17 | 10/26/2025 23:09:47 | NETECO: Maintance Reminder at RSP0812 @ Sceco | 10/26/2025 11:03:35 | Minor | 40563 | Maintance Reminder | 10/26/2025 11:03:35 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0812 | FLM_EM | [8 empty] | API | 10/26/2025 11:09:47 | 10/26/2025 13:56:13 | 10/26/2025 13:56:21 | 10/26/2025 16:07:27 |  | 10/26/2025 16:08:17 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000461 | PCM-20251026-00000936 | TT-20251026-00899 | EM | Region_6 | ZHR0692 | ZHR0692 | Enviroment | SCECO_Failure | SCECO auto restored | Irfan Yousaf | 10/26/2025 11:10:18 | 10/26/2025 20:07:19 | 10/26/2025 23:10:18 | RECTIFIER MAINS POWER FAILURE at ZHR0692-GSM-UMTS-P2-USF @ Sceco | 10/26/2025 11:01:58 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 11:01:50 | P2 | 2G | al harja | Sceco | 2G NSA | ZHR0692 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 11:10:18 | 10/26/2025 15:55:49 | 10/26/2025 20:06:12 |  |  | 10/26/2025 20:07:19 |  | Irfan Yousaf |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000462 | PCM-20251026-00000940 | TT-20251026-00903 | Reference_EM | Region_3 | MDN2354 | MDN2354 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/26/2025 11:10:49 | 10/26/2025 11:10:49 | 10/26/2025 23:10:49 | Door opening alarm at MDN2354-P3-USF_SRAN @ Sceco | 10/26/2025 11:10:38 | Minor | 65101 | Door opening alarm | 10/26/2025 11:10:33 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2354 | FLM_EM | [8 empty] | API | 10/26/2025 11:10:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000463 | PCM-20251026-00000943 | TT-20251026-00906 | EM | Region_3 | MDN2354 | MDN2354 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/26/2025 11:10:50 | 10/26/2025 11:10:50 | 10/26/2025 23:10:50 | NETECO: Door Status Sensor Alarm at MDN2354 @ Sceco | 10/26/2025 11:10:31 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 11:10:31 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN2354 | FLM_EM | [8 empty] | API | 10/26/2025 11:10:50 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000464 | PCM-20251026-00000941 | TT-20251026-00904 | EM | Region_4 | HHR0459 | HHR0459 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/26/2025 11:10:50 | 10/26/2025 11:10:50 | 10/26/2025 17:10:50 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at HHR0459-P1-VIP @ Sceco | 10/26/2025 11:02:26 | Major | 7404 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/26/2025 11:02:21 | VIP | 2G | jeddah | Sceco | 2G NSA | HHR0459 | FLM_EM | [8 empty] | API | 10/26/2025 11:10:50 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000466 | PCM-20251026-00000948 | TT-20251026-00892 | Telecom | Region_4 | LTH0330 | LTH0330 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 11:13:00 | 10/26/2025 21:19:25 | 10/26/2025 15:13:00 | 1(5G) sites down under LTH0330-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB @ Sceco_STB | 10/26/2025 11:04:47 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 11:04:44 | P1 | 2G | qunfuddah | Sceco_STB | 5G SA | LTH0330-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB | FLM_TE | LTH0330 | Results: DOWN SITE HUB LTH0330-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB LTH0330 Summary: Hub: LTH0330, Down Count: 1, Down Sites: LTH0330-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB Alarm Summary: LTH0330 Alarm Active on HUB |  |  |  | No route to host [URL:http://10.98.8.220:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 11:13:00 | 10/26/2025 21:19:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000467 | PCM-20251026-00000949 | TT-20251026-00893 | Telecom | Region_4 | UKZ1M7166 | UKZ0166 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 11:13:04 | 10/27/2025 03:30:34 | 10/26/2025 17:13:04 | 1(LTE) sites down under UKZ0166-USF-P3 @ Generator_SG | 10/26/2025 11:04:47 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 11:04:44 | P2 | 4G | adam | Generator_SG | LTE SA | UKZ0166-USF-P3 | FLM_TE | UKZ0166 | Results: DOWN SITE HUB UKZ0166-USF-P3 UKZ0166 Summary: Hub: UKZ0166, Down Count: 1, Down Sites: UKZ0166-USF-P3 Alarm Summary: UKZ0166 No Active Alarm on HUB |  |  |  | No route to host [URL:http://10.88.87.12:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 11:13:04 | 10/26/2025 12:44:28 | 10/27/2025 03:30:23 |  |  | 10/27/2025 03:30:34 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000468 | PCM-20251026-00000951 | TT-20251026-00846 | Reference_telecom | Region_6 | MKW1M8039 | MKW2039 |  |  |  | SHAH KHALID | 10/26/2025 11:13:53 | 10/26/2025 12:35:11 | 10/26/2025 23:13:53 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MKW1M8039-G9-U9-NL8-L18-SBTS-P3 @ Sceco | 10/26/2025 10:43:56 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 10:43:48 | P3 | 4G | makhwa | Sceco | 5G_Cell SA | MKW1M8039 | FLM_TE |  |  | PCM-20251026-00000890 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/26/2025 11:13:53 | 10/26/2025 12:35:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000469 | PCM-20251026-00000953 | TT-20251026-00919 | Reference_telecom | Region_6 | KMS1M8060 | KMS2060 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 11:14:27 | 10/26/2025 11:30:59 | 10/26/2025 23:14:27 | BASE STATION INFORMATION (Unit temperature is high) at KMS1M8060-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/26/2025 10:34:21 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 10:34:17 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M8060 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/26/2025 11:14:27 | 10/26/2025 11:28:23 | 10/26/2025 11:30:44 |  |  | 10/26/2025 11:30:59 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000472 | PCM-20251026-00000959 | TT-20251026-00911 | Telecom | Region_2 | RIYA2U6174c | RIYA6074 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/26/2025 11:16:59 | 10/26/2025 11:35:03 | 10/26/2025 17:16:59 | 1(2G) sites down under RIYA6074-P3/R2_RY1_HWBSC01 @ Sceco | 10/26/2025 11:08:52 | Major | 21807 | OML Fault | 10/26/2025 11:08:42 | P3 | 2G | riyadh | Sceco | 2G SA | RIYA6074-P3 | FLM_TE | RIYA6074 | Results: DOWN SITE HUB RIYA6074-P3 RIYA6074 Summary: Hub: RIYA6074, Down Count: 1, Down Sites: RIYA6074-P3 Alarm Summary: RIYA6074 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 11:16:59 | 10/26/2025 11:35:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000473 | PCM-20251026-00000962 | TT-20251026-00920 | Reference_telecom | Region_4 | SQSH0023 | SQSH0023 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 11:18:16 | 10/26/2025 12:28:59 | 10/26/2025 17:18:16 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at SQSH0023-GSM-UMTS-P2-USF @ Generator_DG | 10/26/2025 11:09:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 11:09:51 | P2 | 2G | qunfuddah | Generator_DG | 5G_Cell SA | SQSH0023 | FLM_TE |  |  | PCM-20251026-00000955 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/26/2025 11:18:16 | 10/26/2025 12:28:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000474 | PCM-20251026-00000963 | TT-20251026-00914 | Telecom | Region_4 | JED0126 | JED0126 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 11:18:29 | 10/26/2025 13:19:24 | 10/26/2025 15:18:29 | 1(2G) sites down under JED0126-P1-HUB/JED0126-P1-HUB @ Sceco_STB | 10/26/2025 11:10:03 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 11:10:00 | P1 | 2G | jeddah | Sceco_STB | 2G SA | JED0126-P1-HUB | FLM_TE | JED0126 | Results: DOWN SITE HUB JED0126-P1-HUB JED0126 Summary: Hub: JED0126, Down Count: 1, Down Sites: JED0126-P1-HUB Alarm Summary: JED0126 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 11:18:29 | 10/26/2025 13:19:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000477 | PCM-20251026-00000968 | TT-20251026-00788 | Reference_telecom | Region_6 | AQQ1M8426 | AQQ2426 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 11:20:58 | 10/26/2025 17:41:01 | 10/26/2025 23:20:58 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at AQQ1M8426-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 08:30:28 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 08:15:28 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8426 | FLM_TE |  |  | PCM-20251026-00000835 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 11:20:58 | 10/26/2025 11:26:41 | 10/26/2025 17:40:52 |  |  | 10/26/2025 17:41:01 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000478 | PCM-20251026-00000971 | TT-20251026-00789 | Reference_telecom | Region_6 | AQQ1M8170 | AQQ2170 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 11:21:09 | 10/26/2025 17:40:39 | 10/26/2025 23:21:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at AQQ1M8170-G9-L800-SBTS-P3 @ Generator_SG | 10/26/2025 08:30:28 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 08:15:59 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8170 | FLM_TE |  |  | PCM-20251026-00000837 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 11:21:09 | 10/26/2025 11:26:42 | 10/26/2025 17:40:31 |  |  | 10/26/2025 17:40:39 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000480 | PCM-20251026-00000974 | TT-20251026-00790 | Reference_telecom | Region_6 | AQQ1M8157 | AQQ2157 |  |  |  | SHAH KHALID | 10/26/2025 11:21:46 | 10/26/2025 12:35:12 | 10/26/2025 17:21:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at AQQ1M8157-G9-L8-L18-SBTS @ Generator_SG | 10/26/2025 08:30:30 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 08:16:07 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8157 | FLM_TE |  |  | PCM-20251026-00000838 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 11:21:46 | 10/26/2025 12:35:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000481 | PCM-20251026-00000978 | TT-20251026-00796 | Reference_telecom | Region_6 | BSA1M8316 | BSA2316 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/26/2025 11:22:16 | 10/27/2025 03:35:56 | 10/26/2025 23:22:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BSA1M8316-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/26/2025 09:31:48 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 08:20:43 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8316 | FLM_TE |  |  | PCM-20251026-00000845 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 11:22:16 | 10/26/2025 15:23:55 | 10/26/2025 17:40:09 | 10/27/2025 03:35:43 |  | 10/27/2025 03:35:56 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000483 | PCM-20251026-00000981 | TT-20251026-00946 | Telecom | Region_2 | RIY2440 | RIY2440 | Equipment | Power Cable_RRU_BTS | Change Port on DCDU | Ejaz Hussain Muhammad Sharif | 10/26/2025 11:23:14 | 10/27/2025 07:21:01 | 10/26/2025 17:23:14 | BBU CPRI Interface Error at RIY2440-P3_SRAN @ Sceco | 10/26/2025 11:18:45 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 11:16:12 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2440 | FLM_TE | [8 empty] | API | 10/26/2025 11:23:14 | 10/26/2025 23:43:07 | 10/27/2025 07:20:38 | 10/27/2025 07:20:42 |  | 10/27/2025 07:21:01 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000484 | PCM-20251026-00000982 | TT-20251026-00947 | EM | Region_6 | MKW1M8121 | MKW2121 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 11:23:44 | 10/26/2025 11:23:44 | 10/26/2025 23:23:44 | SHELTER DOOR OPEN at MKW1M8121-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 11:23:21 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 11:23:16 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8121 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 11:23:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000486 | PCM-20251026-00000986 | TT-20251026-00950 | Telecom | Region_5 | MKTF1M7641 | MKTF0641 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 11:25:17 | 10/26/2025 12:56:59 | 10/26/2025 17:25:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKTF1M7641-P2-USF @ Sceco | 10/26/2025 11:24:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 11:24:12 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MKTF1M7641 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 11:25:17 | 10/26/2025 12:56:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000487 | PCM-20251026-00000988 | TT-20251026-00952 | Telecom | Region_6 | ZHR0493 | ZHR0493 | Equipment | BSS_HW_fault | Replace FAN | Bilal Anwar Khurshid Anwar | 10/26/2025 11:25:48 | 10/26/2025 18:38:45 | 10/26/2025 23:25:48 | BASE STATION INFORMATION (Fan vendor not detected) at ZHR0493-GSM-UMTS-P2-USF @ Sceco | 10/26/2025 11:17:41 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 11:17:31 | P2 | 2G | al harja | Sceco | 2G NSA | ZHR0493 | FLM_TE | [5 empty] | Fan vendor not detected |  |  | API | 10/26/2025 11:25:48 | 10/26/2025 15:10:57 | 10/26/2025 17:41:51 | 10/26/2025 17:41:54 | 10/26/2025 18:12:39 | 10/26/2025 18:38:45 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000489 | PCM-20251026-00000996 | TT-20251026-00961 | EM | Region_6 | SRA1M8353 | SRA2353 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 11:29:56 | 10/26/2025 11:29:56 | 10/26/2025 23:29:56 | SHELTER DOOR OPEN at SRA1M8353-G9-L800-P3-SBTS @ Generator_SG | 10/26/2025 11:29:34 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 11:29:22 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8353 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 11:29:56 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000490 | PCM-20251026-00000999 | TT-20251026-00925 | EM | Region_6 | ZHR0808 | ZHR0808 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Bilal Anwar Khurshid Anwar | 10/26/2025 11:31:30 | 10/26/2025 16:41:56 | 10/26/2025 17:31:30 | 1(2G/3G/5G) sites down under ZHR0808-P3/ZHR0808-P3 @ Generator_SG | 10/26/2025 11:13:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 11:13:53 | P3 | 2G | al harja | Generator_SG | 2G_3G_5G SA | ZHR0808-P3 | FLM_TE | ZHR0808 | Results: DOWN SITE HUB ZHR0808-P3 ZHR0808 Summary: Hub: ZHR0808, Down Count: 1, Down Sites: ZHR0808-P3 Alarm Summary: ZHR0808 Alarm Active on HUB | PCM-20251026-00000976 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 11:31:30 | 10/26/2025 15:10:57 | 10/26/2025 16:41:47 |  |  | 10/26/2025 16:41:56 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000491 | PCM-20251026-00001000 | TT-20251026-00953 | Reference_telecom | Region_1 | HFF2U6729 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 11:31:55 | 10/26/2025 21:28:12 | 10/26/2025 23:31:55 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6729-P3 @ Sceco | 10/26/2025 08:25:27 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 08:25:25 | P3 | 4G | hafouf | Sceco | 2G NSA | HFF2U6729 | FLM_TE |  |  | PCM-20251026-00000989 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 11:31:55 | 10/26/2025 13:51:38 | 10/26/2025 21:27:47 |  |  | 10/26/2025 21:28:12 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000492 | PCM-20251026-00001001 | TT-20251026-00966 | Reference_EM | Region_1 | SMRY0811 | SMRY0811 |  |  |  | Samir Elzain Abdu Gumaa | 10/26/2025 11:32:00 | 10/26/2025 11:32:00 | 10/26/2025 17:32:00 | Air condition 1 failure alarm at SMRY0811-P1-HUB_SRAN @ Generator_SG | 10/26/2025 11:21:43 | Major | 65104 | Air condition 1 failure alarm | 10/26/2025 11:21:35 | P1 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0811 | FLM_EM | [8 empty] | API | 10/26/2025 11:32:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000493 | PCM-20251026-00001014 | TT-20251026-00972 | Telecom | Region_6 | DAR0918 | DAR0918 | Equipment | BSS_HW_Stuck | Reset Air Scale | Muhammad Ali | 10/26/2025 11:40:29 | 10/26/2025 13:29:10 | 10/26/2025 17:40:29 | 1(5G) sites down under DAR0918-GSM-UMTS-P2 @ Sceco | 10/26/2025 11:32:15 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 11:32:11 | P2 | 2G | dair | Sceco | 5G SA | DAR0918-GSM-UMTS-P2 | FLM_TE | DAR0918 | Results: DOWN SITE HUB DAR0918-GSM-UMTS-P2 DAR0918 Summary: Hub: DAR0918, Down Count: 1, Down Sites: DAR0918-GSM-UMTS-P2 Alarm Summary: DAR0918 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.102.93.108:8080] [URL:http://10.102.93.108:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 11:40:29 | 10/26/2025 11:46:29 | 10/26/2025 13:29:00 |  |  | 10/26/2025 13:29:10 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000494 | PCM-20251026-00001016 | TT-20251026-00981 | EM | Region_4 | USF1M7694 | USF0694 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/26/2025 11:41:20 | 10/26/2025 13:34:18 | 10/26/2025 23:41:20 | RECTIFIER MODULE FAILURE at USF1M7694-G9-L8-SBTS-P2-USF @ Sceco | 10/26/2025 11:32:56 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 11:32:48 | P3 | 4G | jeddah | Sceco | LTE NSA | USF1M7694 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 11:41:20 | 10/26/2025 13:34:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000495 | PCM-20251026-00001019 | TT-20251026-00985 | Telecom | Region_2 | RIY2790 | RIY2790 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/26/2025 11:42:25 | 10/26/2025 23:43:08 | 10/26/2025 23:42:25 | HC for RIY2790 | 10/26/2025 11:41:24 | Minor | 676767672 | Health Check-WO to TE FME | 10/26/2025 11:41:27 | P2 | SRAN | riyadh | Sceco | 3G NSA | RIY2790 | FLM_TE | [8 empty] | API | 10/26/2025 11:42:25 | 10/26/2025 23:43:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000497 | PCM-20251026-00001021 | TT-20251026-00940 | Reference_telecom | Region_6 | QIS1M7102 | QIS0102 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Ali | 10/26/2025 11:42:53 | 10/26/2025 18:11:56 | 10/26/2025 23:42:53 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at QIS1M7102-G9-L18-SBTS-P2 @ Sceco | 10/26/2025 11:19:27 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 11:10:30 | P2 | 4G | jizan | Sceco | LTE NSA | QIS1M7102 | FLM_TE |  | Dear FLM , site was down and restored ,kindly check | PCM-20251026-00001004 | Dear FLM , site was down and restored ,kindly check | Dear FLM , site was down and restored ,kindly check |  |  |  | API | 10/26/2025 11:42:53 | 10/26/2025 11:46:30 | 10/26/2025 18:04:45 |  |  | 10/26/2025 18:11:56 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000498 | PCM-20251026-00001022 | TT-20251026-00976 | Telecom | [7 empty] | 10/26/2025 11:43:30 | 10/26/2025 11:43:30 | 10/26/2025 17:43:30 | 1(LTE) sites down under MDN2536-CAP-P3-SRAN @ Sceco | 10/26/2025 11:35:20 | Major | 301 | NE Is Disconnected | 10/26/2025 11:35:18 | P3 | SRAN |  | Sceco | LTE SA | MDN2536-CAP-P3-SRAN | FLM_TE | MDN2536 | Results: DOWN SITE HUB MDN2536-CAP-P3-SRAN MDN2536 Summary: Hub: MDN2536, Down Count: 1, Down Sites: MDN2536-CAP-P3-SRAN Alarm Summary: MDN2536 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 11:43:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000499 | PCM-20251026-00001023 | TT-20251026-00990 | Telecom | Region_1 | DM1 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/26/2025 11:43:35 | 10/26/2025 11:43:35 | 10/26/2025 17:43:35 | Physically identify the Meqyas White Box | 10/26/2025 11:43:23 | Major | 4205 | The interface traffic exceeds the threshold | 10/26/2025 11:43:23 | P1 | DWDM | dammam | Sceco_STB | TTImpacISPNSA | Physically identify the Meqyas White Box | FLM_TE | [8 empty] | API | 10/26/2025 11:43:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000500 | PCM-20251026-00001024 | TT-20251026-00970 | Telecom | [7 empty] | 10/26/2025 11:43:43 | 10/26/2025 11:43:43 | 10/26/2025 17:43:43 | 2(2G) 2(LTE) sites down under HLMD2428-P3-CAP,AIS2666-P3-CAP/R3_MD_HWBSC01 @ Generator_DG | 10/26/2025 11:31:53 | Major | 21825 | CSL Fault | 10/26/2025 11:31:50 | P3 | SRAN |  | Generator_DG | 2G_LTE SA | HLMD2428-P3-CAP 2G_LTE,AIS2666-P3-CAP 2G_LTE | FLM_EM | HLMD2428 | Dear Team, Hub:- HLMD2428 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | PCM-20251026-00001013 | Dear Team, Hub:- HLMD2428 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | Dear Team, Hub:- HLMD2428 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. |  | sites down |  | API | 10/26/2025 11:43:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000501 | PCM-20251026-00001026 | TT-20251026-00941 | Reference_telecom | Region_4 | JED0126 | JED0126 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 11:44:39 | 10/26/2025 13:19:24 | 10/26/2025 17:44:39 | BASE STATION CONNECTIVITY PROBLEM (NR GTP-U Path Failure) at JED0126-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB @ Sceco_STB | 10/26/2025 11:19:12 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 11:09:50 | P1 | 2G | jeddah | Sceco_STB | 2G NSA | JED0126 | FLM_TE |  | dear FLM , site was down , kindly check | PCM-20251026-00001005 | dear FLM , site was down , kindly check | dear FLM , site was down , kindly check |  |  |  | API | 10/26/2025 11:44:39 | 10/26/2025 13:19:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000502 | PCM-20251026-00001027 | TT-20251026-00992 | Telecom | Region_2 | RIY2M2440 | RIY2440 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Waseem Shahzad Ghulam Rasool | 10/26/2025 11:44:52 | 10/26/2025 12:37:10 | 10/26/2025 17:44:52 | GSM Cell out of Service at RIY2M2440-P3 @ Sceco | 10/26/2025 11:43:49 | Major | 21801 | GSM Cell out of Service | 10/26/2025 11:43:46 | P3 | 2G | riyadh | Sceco | 2G SA | RIY2M2440 | FLM_TE | [8 empty] | API | 10/26/2025 11:44:52 | 10/26/2025 11:48:23 | 10/26/2025 11:48:30 | 10/26/2025 11:48:33 | 10/26/2025 11:48:38 | 10/26/2025 12:37:10 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000503 | PCM-20251026-00001028 | TT-20251026-00993 | Reference_telecom | Region_2 | RIY0398 | RIY0398 |  |  |  | Asad Ali Nadiq Khan | 10/26/2025 11:44:56 | 10/26/2025 12:27:46 | 10/26/2025 23:44:56 | MW_LOF at RIY0398_NE_4 @ Sceco | 10/26/2025 07:44:50 | Minor | 1-631 | MW_LOF | 10/26/2025 07:44:38 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0398 | FLM_TE | [8 empty] | API | 10/26/2025 11:44:56 | 10/26/2025 12:27:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000504 | PCM-20251026-00001031 | TT-20251026-00995 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/26/2025 11:47:17 | 10/26/2025 17:56:55 | 10/26/2025 17:47:17 | UMTS Cell Unavailable at SHB2M3689-P3 @ Power Cube | 10/26/2025 11:45:34 | Major | 22202 | UMTS Cell Unavailable | 10/26/2025 11:45:30 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB2M3689 | FLM_TE | [8 empty] | API | 10/26/2025 11:47:17 | 10/26/2025 17:56:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000505 | PCM-20251026-00001033 | TT-20251026-00997 | Telecom | Region_4 | JED6058 | JED6058 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 11:48:02 | 10/26/2025 11:48:02 | 10/26/2025 17:48:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6058-GSM-P3 @ Sceco | 10/26/2025 11:47:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 11:47:12 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED6058 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 11:48:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000506 | PCM-20251026-00001041 | TT-20251026-01005 | Telecom | Region_6 | ABH0280 | ABH0280 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 11:50:37 | 10/26/2025 14:07:30 | 10/26/2025 23:50:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH0280-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/26/2025 11:49:54 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 11:49:46 | P2 | 2G | abha | Sceco | 5G_Cell SA | ABH0280 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 11:50:37 | 10/26/2025 14:04:43 | 10/26/2025 14:07:20 |  |  | 10/26/2025 14:07:30 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000508 | PCM-20251026-00001051 | TT-20251026-00998 | EM | [7 empty] | 10/26/2025 11:53:29 | 10/26/2025 11:54:32 | 10/26/2025 17:53:29 | 1(2G/5G) sites down under JED2608-P3/JED2608-P3 @ Generator_SG | 10/26/2025 11:45:04 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 11:45:00 | P3 | 2G |  | Generator_SG | 2G SA | JED2608-P3 | FLM_TE | JED2608 | Results: DOWN SITE HUB JED2608-P3 JED2608 Summary: Hub: JED2608, Down Count: 1, Down Sites: JED2608-P3 Alarm Summary: JED2608 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 11:53:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000509 | PCM-20251026-00001054 | TT-20251026-01016 | EM | Region_4 | RYMK1M7544 | RYMK0544 |  |  |  | Farghal Ashour Hassan Farghal | 10/26/2025 11:54:13 | 10/26/2025 16:01:59 | 10/26/2025 23:54:13 | HIGH TEMPERATURE 32 DEGREE C at RYMK1M7544-L800-P2-USF @ Sceco | 10/26/2025 11:45:52 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/26/2025 11:45:44 | P2 | 4G | taif | Sceco | LTE NSA | RYMK1M7544 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/26/2025 11:54:13 | 10/26/2025 16:01:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000510 | PCM-20251026-00001053 | TT-20251026-01017 | EM | Region_3 | MDUL2548 | MDUL2548 |  |  |  | Arslan Mustafa Ghulam Mustafa | 10/26/2025 11:54:13 | 10/26/2025 19:27:57 | 10/26/2025 23:54:13 | NETECO: Maintance Reminder at MDUL2548 @ Sceco_STB | 10/26/2025 11:47:44 | Minor | 40563 | Maintance Reminder | 10/26/2025 11:47:44 | P3 | SRAN | madinah | Sceco_STB | 2G NSA | MDUL2548 | FLM_EM | [8 empty] | API | 10/26/2025 11:54:13 | 10/26/2025 19:27:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000512 | PCM-20251026-00001060 | TT-20251026-01023 | Telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Fawad Khan | 10/26/2025 11:56:25 | 10/26/2025 17:27:04 | 10/26/2025 23:56:25 | PT::: As Per BO request need FLM to do HC in TNMS0711 /R6 | 10/26/2025 11:56:17 | Minor | 7100 | BASE STATION HARDWARE PROBLEM | 10/26/2025 11:56:17 | P3 | 2G | namas | Sceco | 2G_3G_LTE_5G NSA | TNMS0711 | FLM_TE | [8 empty] | API | 10/26/2025 11:56:25 | 10/26/2025 12:03:22 | 10/26/2025 12:22:41 | 10/26/2025 12:22:54 |  | 10/26/2025 17:27:04 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000513 | PCM-20251026-00001062 | TT-20251026-01014 | EM | Region_6 | RJL0129 | RJL0129 |  |  |  | Zia Ur Rahamn | 10/26/2025 11:58:29 | 10/26/2025 16:23:59 | 10/26/2025 17:58:29 | 1(2G/3G/LTE) sites down under RJL0129-P3/RJL0129-P3 @ Sceco | 10/26/2025 11:50:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 11:50:43 | P3 | 2G | mohail | Sceco | 2G_3G_LTE SA | RJL0129-P3 | FLM_EM |  | Results: DOWN SITE HUB RJL0129-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/26/2025 11:58:29 | 10/26/2025 16:23:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000514 | PCM-20251026-00001064 | TT-20251026-01027 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/26/2025 12:00:26 | 10/26/2025 15:14:41 | 10/27/2025 00:00:26 | RF Unit CPRI Interface Error at DAM6027-DCU1 @ Sceco | 10/26/2025 11:53:59 | Minor | 26504 | RF Unit CPRI Interface Error | 10/26/2025 11:53:30 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/26/2025 12:00:26 | 10/26/2025 15:14:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000515 | PCM-20251026-00001069 | TT-20251026-00856 | Telecom | Region_5 | MAK0981 | MAK0981 |  |  |  | Amjad Ali Muhammad Parves | 10/26/2025 12:03:54 | 10/26/2025 12:06:14 | 10/26/2025 18:03:54 | 2(2G) 1(LTE) 2(5G) sites down under MAK0981-P2,MAK2555-P3/MAK2555-P3 @ Sceco | 10/26/2025 10:49:40 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:49:36 | P2 | 2G | makkah | Sceco | 2G SA | MAK2555-P3 2G,MAK0981-P2 2G | FLM_TE | MAK0981 | Dear team , Hub: MAK0981 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251026-00000909 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 12:03:54 | 10/26/2025 12:06:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000518 | PCM-20251026-00001078 | TT-20251026-01040 | EM | Region_4 | KHY1M8251 | KHY2251 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/26/2025 12:06:07 | 10/26/2025 12:06:07 | 10/27/2025 00:06:07 | GENERATOR RUNING ALARM at KHY1M8251-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 11:59:16 | Minor | 7103 | GENERATOR RUNING ALARM | 10/26/2025 11:57:46 | P3 | 4G | jeddah | Generator_SG | LTE NSA | KHY1M8251 | FLM_EM | [5 empty] | GENERATOR RUNING ALARM |  |  | API | 10/26/2025 12:06:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000520 | PCM-20251026-00001085 | TT-20251026-01031 | Telecom | Region_5 | BIK1M7785 | BIK0785 |  |  |  | Hazem Ali Moustafa Ali | 10/26/2025 12:07:59 | 10/26/2025 12:07:59 | 10/26/2025 18:07:59 | 1(LTE) sites down under BIK0785-L900-USF-P3 @ Generator_SG | 10/26/2025 11:59:41 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 11:59:38 | P2 | 4G | makkah | Generator_SG | LTE SA | BIK0785-L900-USF-P3 | FLM_TE | BIK0785 | Results: DOWN SITE HUB BIK0785-L900-USF-P3 BIK0785 Summary: Hub: BIK0785, Down Count: 1, Down Sites: BIK0785-L900-USF-P3 Alarm Summary: BIK0785 No Active Alarm on HUB |  |  |  | Operation timed out [URL:http://MRBTS-507785:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 12:07:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000521 | PCM-20251026-00001093 | TT-20251026-01059 | Telecom | Region_4 | TAF2403 | TAF2403 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 12:11:47 | 10/26/2025 12:11:47 | 10/27/2025 00:11:47 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF2403-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/26/2025 12:10:53 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 12:10:45 | P2 | 2G | taif | Sceco | 5G_Cell SA | TAF2403 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 12:11:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000522 | PCM-20251026-00001094 | TT-20251026-01060 | EM | Region_4 | FRS2410 | FRS2410 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 12:11:47 | 10/26/2025 12:11:48 | 10/27/2025 00:11:47 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at FRS2410-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 12:03:34 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/26/2025 12:03:29 | P3 | 2G | qunfuddah | Sceco | 2G NSA | FRS2410 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/26/2025 12:11:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000523 | PCM-20251026-00001095 | TT-20251026-01063 | EM | Region_6 | SRA1M8353 | SRA2353 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 12:14:22 | 10/26/2025 12:14:22 | 10/27/2025 00:14:22 | RECTIFIER MAINS POWER FAILURE at SRA1M8353-G9-L800-P3-SBTS @ Generator_SG | 10/26/2025 12:06:23 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 12:06:02 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8353 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 12:14:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000524 | PCM-20251026-00001101 | TT-20251026-01055 | EM | Region_6 | AHM0027 | AHM0027 |  |  |  | Touseef Ahmed | 10/26/2025 12:15:29 | 10/26/2025 12:15:29 | 10/26/2025 18:15:29 | 1(2G/3G/LTE) sites down under AHM0027-P3/AHM0027-P3 @ Sceco | 10/26/2025 12:07:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 12:07:27 | P3 | 2G | jizan | Sceco | 2G_3G_LTE SA | AHM0027-P3 | FLM_EM | AHM0027 | Results: DOWN SITE HUB AHM0027-P3 AHM0027 Summary: Hub: AHM0027, Down Count: 1, Down Sites: AHM0027-P3 Alarm Summary: AHM0027 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 12:15:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000525 | PCM-20251026-00001102 | TT-20251026-01058 | EM | Region_4 | JED1U6758 | JED6058 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 12:16:29 | 10/26/2025 12:55:31 | 10/26/2025 18:16:29 | 1(LTE/5G) sites down under JED6058-GSM-P3 @ Sceco | 10/26/2025 12:08:10 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 12:08:09 | P3 | 4G | jeddah | Sceco | LTE SA | JED6058-P3 | FLM_TE | JED6058 | Results: DOWN SITE HUB JED6058-P3 JED6058 Summary: Hub: JED6058, Down Count: 1, Down Sites: JED6058-P3 Alarm Summary: JED6058 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.96.228:8080] [URL:http://10.97.96.228:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 12:16:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000526 | PCM-20251026-00001107 | TT-20251026-01061 | Telecom | Region_4 | TAF1M8114 | TAF2114 | Equipment | SFP_BTS | Clean SFP | Asad Ullah Rahim Said | 10/26/2025 12:18:00 | 10/26/2025 18:06:13 | 10/26/2025 18:18:00 | 1(LTE) sites down under TAF2114-CA-L800-SBTS-P2 @ Sceco | 10/26/2025 12:09:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 12:09:53 | P2 | 4G | taif | Sceco | LTE SA | TAF2114-CA-L800-SBTS-P2 | FLM_TE | TAF2114 | Results: DOWN SITE HUB TAF2114-CA-L800-SBTS-P2 TAF2114 Summary: Hub: TAF2114, Down Count: 1, Down Sites: TAF2114-CA-L800-SBTS-P2 Alarm Summary: TAF2114 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-4471780 [ACTIVE] [URL:http://10.98.72.212:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 12:18:00 | 10/26/2025 15:43:35 | 10/26/2025 16:39:16 | 10/26/2025 16:39:19 | 10/26/2025 16:39:21 | 10/26/2025 18:06:13 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000527 | PCM-20251026-00001109 | TT-20251026-01101 | Telecom | Region_6 | ZFR0034 | ZFR0034 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 12:19:33 | 10/26/2025 12:33:11 | 10/27/2025 00:19:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at ZFR0034-G9-L8-L18-NL21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 12:18:30 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 12:18:23 | P3 | 2G | makhwa | Sceco | 5G_Cell SA | ZFR0034 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 12:19:33 | 10/26/2025 12:32:39 | 10/26/2025 12:33:02 |  |  | 10/26/2025 12:33:11 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000528 | PCM-20251026-00001115 | TT-20251026-01113 | Telecom | Region_5 | MAK2091 | MAK2091 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 12:23:40 | 10/26/2025 12:23:40 | 10/27/2025 00:23:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2091-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/26/2025 12:23:01 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 12:22:53 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2091 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 12:23:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000529 | PCM-20251026-00001120 | TT-20251026-01103 | Telecom | Region_6 | ABH0086 | ABH0086 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 12:27:03 | 10/26/2025 14:08:13 | 10/26/2025 18:27:03 | 2(2G) 2(3G) 2(5G) sites down under ABH0086-P2,ABH0303-P2/ABH0303-P2 @ Sceco | 10/26/2025 12:17:39 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 12:17:36 | P2 | 2G | abha | Sceco | 2G SA | ABH0303-P2 2G,ABH0086-P2 2G | FLM_TE | ABH0086 | Dear team , HUB: ABH0086 We observing Link flapping at the HUB ,kindly check locally | PCM-20251026-00001118 | Dear team , HUB: ABH0086 We observing Link flapping at the HUB ,kindly check locally | Dear team , HUB: ABH0086 We observing Link flapping at the HUB ,kindly check locally |  | sites down |  | API | 10/26/2025 12:27:03 | 10/26/2025 14:04:43 | 10/26/2025 14:08:02 |  |  | 10/26/2025 14:08:13 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000531 | PCM-20251026-00001123 | TT-20251026-01112 | EM | Region_6 | ZFR0034 | ZFR0034 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 12:28:31 | 10/26/2025 14:28:26 | 10/26/2025 18:28:31 | 1(2G/3G/5G) sites down under ZFR0034-P3/ZFR0034-P3 @ Sceco | 10/26/2025 12:20:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 12:20:39 | P3 | 2G | makhwa | Sceco | 2G_3G_5G SA | ZFR0034-P3 | FLM_EM | ZFR0034 | Results: DOWN SITE HUB ZFR0034-P3 ZFR0034 Summary: Hub: ZFR0034, Down Count: 1, Down Sites: ZFR0034-P3 Alarm Summary: ZFR0034 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 12:28:31 | 10/26/2025 14:28:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000532 | PCM-20251026-00001126 | TT-20251026-01028 | EM | Region_1 | ARM0712 | ARM0712 |  |  |  | Imran Ali Yousaf | 10/26/2025 12:29:26 | 10/26/2025 17:46:15 | 10/26/2025 18:29:26 | 1(2G/3G/LTE) sites down under ARM0712-P3 @ Sceco | 10/26/2025 11:57:22 | Major | 301 | NE Is Disconnected | 10/26/2025 11:57:18 | P3 | SRAN | dammam | Sceco | LTE SA | ARM0712-P3 | FLM_TE | ARM0712 | Dear FLM, Hub is ARM0712 We are observing ETH_LOS alarm active at hub site ,Kindly send to FLM to check cable connection at site. | PCM-20251026-00001111 | Dear FLM, Hub is ARM0712 We are observing ETH_LOS alarm active at hub site ,Kindly send to FLM to check cable connection at site. | Dear FLM, Hub is ARM0712 We are observing ETH_LOS alarm active at hub site ,Kindly send to FLM to check cable connection at site. |  | sites down |  | API | 10/26/2025 12:29:26 | 10/26/2025 17:46:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000534 | PCM-20251026-00001134 | TT-20251026-01121 | EM | [7 empty] | 10/26/2025 12:31:59 | 10/26/2025 12:31:59 | 10/26/2025 18:31:59 | 1(2G/LTE) sites down under MDN2177-P3-CAP/R3_MD_HWBSC01 @ Generator_DG | 10/26/2025 12:23:39 | Major | 21825 | CSL Fault | 10/26/2025 12:23:37 | P3 | 2G |  | Generator_DG | 2G_LTE SA | MDN2177-P3-CAP | FLM_EM | MDN2177 | Results: DOWN SITE HUB MDN2177-P3-CAP MDN2177 Summary: Hub: MDN2177, Down Count: 1, Down Sites: MDN2177-P3-CAP Alarm Summary: MDN2177 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 12:31:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000535 | PCM-20251026-00001135 | TT-20251008-02012 | MW_HC | Region_5 | MAK0273 | MAK0273 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/26/2025 12:32:13 | 10/26/2025 12:32:13 | 10/27/2025 00:32:13 | Nokia MW HC_P2 Observing Modem Down at MAK0273_01-MAK0053 -19 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK0273_01-MAK0053 -19 | FLM_TE |  |  | PCM-20251026-00001091 | approved | approved |  |  |  | API | 10/26/2025 12:32:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000536 | PCM-20251026-00001139 | TT-20251026-01136 | Telecom | Region_4 | RAB1M7474 | RAB0474 |  |  |  | Khizer Hayat | 10/26/2025 12:34:01 | 10/26/2025 13:29:58 | 10/27/2025 00:34:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at RAB1M7474-G9-NL8-L18-L21-SBTS-P2-USF @ Sceco | 10/26/2025 12:32:59 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 12:32:53 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | RAB1M7474 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 12:34:01 | 10/26/2025 13:29:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000538 | PCM-20251026-00001142 | TT-20251026-01118 | Telecom | Region_4 | RYMK0528 | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/26/2025 12:35:59 | 10/27/2025 07:58:28 | 10/26/2025 18:35:59 | 3(2G) 1(3G) 2(5G) sites down under QSDH0724-P3,RYMK0529-P2,QSDH0723-P3/QSDH0723-P3 @ Generator_SG | 10/26/2025 12:22:33 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 12:22:30 | P1 | 2G | taif | Generator_SG | 2G_3G SA | QSDH0723-P3 2G_5G,QSDH0724-P3 2G_5G,RYMK0529-P2 2G_3G | FLM_TE | RYMK0528 | Dear team , HUB: RYMK0528 We observing Link flapping at the HUB ,kindly check locally | PCM-20251026-00001130 | Dear team , HUB: RYMK0528 We observing Link flapping at the HUB ,kindly check locally | Dear team , HUB: RYMK0528 We observing Link flapping at the HUB ,kindly check locally |  | sites down |  | API | 10/26/2025 12:35:59 | 10/27/2025 07:58:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000539 | PCM-20251026-00001147 | TT-20251026-01142 | Telecom | Region_2 | RIY0359 | RIY0359 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Ejaz Hussain Muhammad Sharif | 10/26/2025 12:36:35 | 10/27/2025 07:00:07 | 10/26/2025 18:36:35 | BBU CPRI Interface Error at RIY0359-P1_SRAN @ Sceco | 10/26/2025 12:33:48 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 12:31:16 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0359 | FLM_TE | [8 empty] | API | 10/26/2025 12:36:35 | 10/27/2025 06:58:02 | 10/27/2025 06:59:43 | 10/27/2025 06:59:48 |  | 10/27/2025 07:00:07 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251026000541 | PCM-20251026-00001151 | TT-20251026-01145 | EM | Region_4 | JED1M7685 | JED0685 |  |  |  | Hussein Sayed Salama Hussein | 10/26/2025 12:39:41 | 10/26/2025 23:37:21 | 10/27/2025 00:39:41 | GENERATOR1 + GENERATOR 2 FAILURE at JED1M7685-CA-L900-L800-SBTS @ Sceco_STB | 10/26/2025 12:31:37 | Minor | 7103 | GENERATOR1 + GENERATOR 2 FAILURE | 10/26/2025 12:31:30 | P3 | 4G | jeddah | Sceco_STB | LTE NSA | JED1M7685 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR 2 FAILURE |  |  | API | 10/26/2025 12:39:41 | 10/26/2025 20:27:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000542 | PCM-20251026-00001152 | TT-20251026-01137 | Telecom | Region_6 | TLT1M7364 | TLT0364 | Transsmission | MW_Visibilty | Replace ETH Cable | Muhammad Afzal Muhammad Aslam | 10/26/2025 12:40:00 | 10/26/2025 15:52:45 | 10/26/2025 18:40:00 | 1(LTE) sites down under TLT0364-P3 @ Sceco | 10/26/2025 12:31:44 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 12:31:40 | P3 | 4G | tathleeth | Sceco | LTE SA | TLT0364-P3 | FLM_TE | TLT0364 | Results: DOWN SITE HUB TLT0364-P3 TLT0364 Summary: Hub: TLT0364, Down Count: 1, Down Sites: TLT0364-P3 Alarm Summary: TLT0364 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.89.23.172:8080] [URL:http://10.89.23.172:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 12:40:00 | 10/26/2025 14:15:49 | 10/26/2025 15:31:44 | 10/26/2025 15:31:46 | 10/26/2025 15:31:49 | 10/26/2025 15:52:45 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000543 | PCM-20251026-00001160 | TT-20251026-01154 | Telecom | Region_4 | JED6231 | JED6131 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 12:46:25 | 10/26/2025 12:46:25 | 10/26/2025 18:46:25 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6231-GSM-P3 @ Sceco | 10/26/2025 12:45:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 12:45:16 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED6231 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 12:46:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000544 | PCM-20251026-00001164 | TT-20251026-01147 | EM | Region_1 | SMN2M5800 | SMN0800 |  |  |  | Shaker Saied Mohamed ElShafie | 10/26/2025 12:46:30 | 10/26/2025 12:46:30 | 10/26/2025 18:46:30 | 1(2G/LTE) sites down under SMN0800-P3/HB1BSCH01 @ Sceco | 10/26/2025 12:38:09 | Major | 21825 | CSL Fault | 10/26/2025 12:38:07 | P3 | 2G | hafr | Sceco | 2G_LTE SA | SMN0800-P3 | FLM_EM | SMN0800 | Results: DOWN SITE HUB SMN0800-P3 SMN0800 Summary: Hub: SMN0800, Down Count: 1, Down Sites: SMN0800-P3 Alarm Summary: SMN0800 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 12:46:30 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000545 | PCM-20251026-00001170 | TT-20251026-01162 | Reference_EM | Region_1 | ARM0712 | ARM0712 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 12:49:30 | 10/26/2025 13:25:51 | 10/27/2025 00:49:30 | Door opening alarm at ARM0712-P3_SRAN @ Sceco | 10/26/2025 12:49:02 | Minor | 65101 | Door opening alarm | 10/26/2025 12:48:58 | P3 | SRAN | dammam | Sceco | 2G NSA | ARM0712 | FLM_EM | [8 empty] | API | 10/26/2025 12:49:30 | 10/26/2025 13:25:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000547 | PCM-20251026-00001177 | TT-20251026-00800 | Reference_telecom | Region_4 | SJED1S7018 | SJED0018 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 12:55:37 | 10/26/2025 13:19:25 | 10/26/2025 16:55:37 | BASE STATION OPERATION DEGRADED (BTS reference clock missing: GPS receiver alarm: not tracking satellites) at SJED1S7018-CA-P1-ARP-HAJJ-VIP @ Sceco | 10/26/2025 10:21:42 | Critical | 7651 | BASE STATION OPERATION DEGRADED | 10/26/2025 10:11:39 | VIP | 4G | jeddah | Sceco | LTE NSA | SJED1S7018 | FLM_TE |  |  | PCM-20251026-00000849 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 12:55:37 | 10/26/2025 13:19:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000548 | PCM-20251026-00001179 | TT-20251026-01064 | Reference_telecom | Region_4 | SQR1M3379 | SQR0379 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 12:55:52 | 10/27/2025 03:31:08 | 10/26/2025 18:55:52 | WCDMA CELL OUT OF USE at SQR1M3379-P2-USF @ Generator_SG | 10/26/2025 12:09:06 | Major | 7771 | WCDMA CELL OUT OF USE | 10/26/2025 12:06:55 | P2 | 3G | alaith | Generator_SG | 3G SA | SQR1M3379 | FLM_TE |  |  | PCM-20251026-00001096 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 12:55:52 | 10/26/2025 16:57:23 | 10/27/2025 03:30:53 |  |  | 10/27/2025 03:31:08 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000549 | PCM-20251026-00001180 | TT-20251026-01143 | Reference_telecom | Region_4 | SQR1M3379 | SQR0379 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 12:56:06 | 10/27/2025 03:30:13 | 10/26/2025 18:56:06 | RNW O&M SCENARIO FAILURE at SQR1M3379-P2-USF @ Generator_SG | 10/26/2025 12:08:09 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/26/2025 12:07:16 | P2 | 3G | alaith | Generator_SG | 3G NSA | SQR1M3379 | FLM_TE |  |  | PCM-20251026-00001148 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/26/2025 12:56:06 | 10/26/2025 16:57:24 | 10/27/2025 03:30:03 |  |  | 10/27/2025 03:30:13 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000551 | PCM-20251026-00001189 | TT-20251026-01178 | EM | Region_6 | BSH1M7080 | BSH0080 |  |  |  | Fizan Ahmed | 10/26/2025 13:01:53 | 10/26/2025 13:01:53 | 10/27/2025 01:01:53 | HIGH TEMPERATURE 32 DEGREE C at BSH1M7080-P3-CA-L800 @ Sceco | 10/26/2025 12:53:57 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/26/2025 12:53:44 | P3 | 4G | baish | Sceco | LTE NSA | BSH1M7080 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/26/2025 13:01:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000552 | PCM-20251026-00001190 | TT-20251026-01182 | Telecom | Region_2 | QSMD0590 | QSMD0590 |  |  |  | Muhammad Naeem Muhammad Gulzar | 10/26/2025 13:03:58 | 10/26/2025 16:51:43 | 10/27/2025 01:03:58 | RF Unit TX Channel Gain Out of Range at QSMD0590-P2_SRAN @ Sceco | 10/26/2025 12:58:30 | Minor | 26520 | RF Unit TX Channel Gain Out of Range | 10/26/2025 12:56:48 | P2 | SRAN | al rass | Sceco | 2G NSA | QSMD0590 | FLM_TE | [8 empty] | API | 10/26/2025 13:03:58 | 10/26/2025 16:51:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000554 | PCM-20251026-00001196 | TT-20251026-01183 | Telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | BSS_HW_fault | Replace RF Module | Fawad Khan | 10/26/2025 13:04:59 | 10/26/2025 18:27:14 | 10/27/2025 01:04:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/26/2025 13:04:07 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 13:03:57 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 13:04:59 | 10/26/2025 14:42:11 | 10/26/2025 18:26:34 |  |  | 10/26/2025 18:27:14 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000555 | PCM-20251026-00001205 | TT-20251026-01192 | EM | Region_6 | BSH1M7080 | BSH0080 |  |  |  | Fizan Ahmed | 10/26/2025 13:09:07 | 10/26/2025 13:09:07 | 10/27/2025 01:09:07 | SHELTER DOOR OPEN at BSH1M7080-P3-CA-L800 @ Sceco | 10/26/2025 13:08:45 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 13:08:33 | P3 | 4G | baish | Sceco | LTE NSA | BSH1M7080 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 13:09:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000556 | PCM-20251026-00001213 | TT-20251026-01190 | EM | Region_3 | MDN2M2534 | MDN2534 |  |  |  | Tasbeeh Ullah Muhammad Yousaf | 10/26/2025 13:13:29 | 10/26/2025 13:13:29 | 10/26/2025 19:13:29 | 1(2G/LTE) sites down under MDN2534-P3/R3_MD_HWBSC02 @ Generator_SG | 10/26/2025 13:05:09 | Major | 21825 | CSL Fault | 10/26/2025 13:05:05 | P3 | 2G | madinah | Generator_SG | 2G_LTE SA | MDN2534-P3 | FLM_EM | MDN2534 | Results: DOWN SITE HUB MDN2534-P3 MDN2534 Summary: Hub: MDN2534, Down Count: 1, Down Sites: MDN2534-P3 Alarm Summary: MDN2534 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 13:13:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000557 | PCM-20251026-00001214 | TT-20251026-01199 | EM | Region_4 | TURY0688 | TURY0688 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/26/2025 13:13:46 | 10/26/2025 13:22:48 | 10/27/2025 01:13:46 | SHELTER DOOR OPEN at TURY0688-GSM-P3 @ Sceco | 10/26/2025 13:13:25 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 13:13:17 | P3 | 2G | taif | Sceco | 2G NSA | TURY0688 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 13:13:46 | 10/26/2025 13:22:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000558 | PCM-20251026-00001215 | TT-20251026-01200 | Telecom | Region_6 | JEC0318 | JEC0318 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/26/2025 13:13:46 | 10/26/2025 19:47:48 | 10/27/2025 01:13:46 | ODU CPU / Cable Open at JEC0318 on 10.154.126.12 @ Generator_SG | 10/26/2025 13:12:55 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/26/2025 13:11:09 | P3 | 2G | baish | Generator_SG | TX NSA | JEC0318 | FLM_TE | [8 empty] | API | 10/26/2025 13:13:46 | 10/26/2025 14:31:31 | 10/26/2025 16:30:46 | 10/26/2025 16:32:30 | 10/26/2025 16:43:06 | 10/26/2025 19:47:48 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000559 | PCM-20251026-00001217 | TT-20251026-01201 | Reference_telecom | Region_4 | JED0235 | JED0235 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 13:14:17 | 10/26/2025 14:42:54 | 10/27/2025 01:14:17 | LossOfSignal observed in JED0235 towards 10.10.147.51 @ Generator_SG | 10/26/2025 01:15:33 | Minor |  | LossOfSignal | 10/26/2025 01:14:04 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0235 | FLM_TE | [8 empty] | API | 10/26/2025 13:14:17 | 10/26/2025 14:42:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000560 | PCM-20251026-00001222 | TT-20251026-01195 | Telecom | Region_4 | JED1MN0550 | JED0550 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 13:15:59 | 10/26/2025 14:42:55 | 10/26/2025 19:15:59 | 1(5G) sites down under JED0550-NR2.6-P3 @ Sceco | 10/26/2025 13:07:41 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 13:07:39 | P2 | 5G | jeddah | Sceco | 5G SA | JED0550-NR2.6-P3 | FLM_TE | JED0550 | Results: DOWN SITE HUB JED0550-NR2.6-P3 JED0550 Summary: Hub: JED0550, Down Count: 1, Down Sites: JED0550-NR2.6-P3 Alarm Summary: JED0550 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.102.217.36:8080] [URL:http://10.102.217.36:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 13:15:59 | 10/26/2025 14:42:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000561 | PCM-20251026-00001223 | TT-20251025-00055 | Telecom | Region_4 | NSH0195 | NSH0195 | Transsmission | MW_HW_fault | Replace Control Card | Mudassar Bashir Bashir Ahmad | 10/26/2025 13:16:21 | 10/26/2025 21:42:44 | 10/26/2025 15:16:21 | 14(2G) 8(3G) 5(LTE) 6(5G) sites down under SIR0050-P2-USF @ Sceco | 10/25/2025 00:54:30 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/25/2025 00:54:25 | P2 | 2G | adam | Sceco_STB | 2G_3G_5G SA | NSH0127-P2-USF 2G_5G,NSH0218-P2-USF 2G_5G,NSH0195-P2-USF 2G_3G,SIR0155-P2-USF 2G_3G,SIR0154-P2-USF 2G_3G,GMQ0153-P2-USF 2G_3G,NSH2169-P3 2G_3G,NNL0216-P2-USF 2G_3G,NSH0138-P3 2G_3G,SIR0050-P2-USF 2G_3G,SIR0125-P2-USF 2G,NSH0128-P2-USF 2G,NSH0165-P3 2G | FLM_TE | NSH0195 | contact BO if need support | PCM-20251025-00000082 | contact BO if need support | contact BO if need support |  | sites down |  | API | 10/26/2025 13:16:21 | 10/26/2025 14:50:38 | 10/26/2025 21:42:22 |  |  | 10/26/2025 21:42:44 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000563 | PCM-20251026-00001227 | TT-20251026-00702 | Reference_telecom | Region_6 | ARF0072 | ARF0072 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 13:18:57 | 10/26/2025 16:49:35 | 10/27/2025 01:18:57 | AS BO Requested MW HC For Link ARF0072-ARF0191 | 10/26/2025 09:23:53 | Minor | 113388 | LOF | 10/26/2025 09:23:53 | P3 | 2G | khamis mushyet | Sceco | TX NSA | ARF0072-ARF0191 | FLM_TE |  | dear FLM , link still counting PM errors , kindly check and share full HC report | PCM-20251026-00001194 | dear FLM , link still counting PM errors , kindly check and share full HC report | dear FLM , link still counting PM errors , kindly check and share full HC report |  |  |  | API | 10/26/2025 13:18:57 | 10/26/2025 16:49:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000564 | PCM-20251026-00001229 | TT-20251026-00772 | EM | Region_5 | MAK0378 | MAK0378 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 13:19:12 | 10/26/2025 13:19:12 | 10/26/2025 17:19:12 | 1(2G/5G) sites down under MAK0378-P1-HRM/MAK0378-P1-HRM @ Sceco | 10/26/2025 10:05:53 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 10:05:49 | P1 | 2G | makkah | Sceco | 2G SA | MAK0378-P1-HRM | FLM_TE | MAK0378 | Results: DOWN SITE HUB MAK0378-P1-HRM MAK0378 Summary: Hub: MAK0378, Down Count: 1, Down Sites: MAK0378-P1-HRM Alarm Summary: MAK0378 No Active Alarm on HUB | PCM-20251026-00001171 | Dear FLM team, kindly check locally airscale continuous flapping | Dear FLM team, kindly check locally airscale continuous flapping |  | sites down |  | API | 10/26/2025 13:19:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000566 | PCM-20251026-00001234 | TT-20251026-01217 | EM | Region_6 | BHAB1M8011 | BHAB2011 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 13:21:01 | 10/26/2025 15:16:02 | 10/27/2025 01:21:01 | RECTIFIER MODULE FAILURE at BHAB1M8011-CA-L800-SBTS-P3 @ Generator_SG | 10/26/2025 13:13:04 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 13:12:57 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8011 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 13:21:01 | 10/26/2025 15:16:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000567 | PCM-20251026-00001235 | TT-20251026-01218 | EM | Region_4 | TURY0688 | TURY0688 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 10/26/2025 13:21:32 | 10/27/2025 08:16:13 | 10/27/2025 01:21:32 | AIRCON 2 FAILURE at TURY0688-GSM-P3 @ Sceco | 10/26/2025 13:13:25 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 13:13:17 | P3 | 2G | taif | Sceco | 2G NSA | TURY0688 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 13:21:32 | 10/26/2025 13:22:49 | 10/27/2025 08:16:02 |  |  | 10/27/2025 08:16:13 |  | Afzal Hussain Anwar Ul Haq |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000568 | PCM-20251026-00001236 | TT-20251026-01171 | Reference_telecom | Region_2 | RIYC2U6721 | RIYC6021 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/26/2025 13:22:02 | 10/26/2025 13:22:02 | 10/27/2025 01:22:02 | Cell RX Channel Interference Noise Power Unbalanced at RIYC2U6721-L800-CA-P3 @ Sceco | 10/26/2025 09:58:37 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 09:58:33 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYC2U6721 | FLM_TE |  |  | PCM-20251026-00001182 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 13:22:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000569 | PCM-20251026-00001241 | TT-20251026-01215 | Telecom | Region_2 | SRIY0395 | SRIY0395 |  |  |  | Muhammad Naseer Muhammad Nazir | 10/26/2025 13:25:43 | 10/26/2025 21:50:00 | 10/26/2025 19:25:43 | 3(LTE) sites down under SRIY0394-P3_SRAN,SRIY0395-P3_SRAN,SRIY0396-P3_SRAN @ Sceco | 10/26/2025 13:16:26 | Major | 301 | NE Is Disconnected | 10/26/2025 13:16:22 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0396-P3_SRAN LTE,SRIY0395-P3_SRAN LTE,SRIY0394-P3_SRAN LTE | FLM_EM | SRIY0395 | Dear Team, Hub:- SRIY0395 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251026-00001238 | Dear Team, Hub:- SRIY0395 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- SRIY0395 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/26/2025 13:25:43 | 10/26/2025 21:50:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000570 | PCM-20251026-00001244 | TT-20251026-01228 | Reference_EM | Region_1 | SKQR0507 | SKQR0507 | Equipment | PMR_Power_Cable_RRU | Change Port on FPFH | Mahmoud Abdelwanis Massoud Elrashidy | 10/26/2025 13:27:12 | 10/26/2025 16:34:49 | 10/27/2025 01:27:12 | Generator failure at SKQR0507-P3_SRAN @ Power Cube | 10/26/2025 13:17:09 | Minor | 65114 | Generator failure | 10/26/2025 13:17:05 | P3 | SRAN | sakaka | Power Cube | 2G NSA | SKQR0507 | FLM_EM | [8 empty] | API | 10/26/2025 13:27:12 | 10/26/2025 15:56:33 | 10/26/2025 16:09:36 | 10/26/2025 16:09:41 | 10/26/2025 16:09:44 | 10/26/2025 16:34:49 |  | Mahmoud Abdelwanis Massoud Elrashidy |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000572 | PCM-20251026-00001249 | TT-20251026-01233 | Reference_EM | Region_2 | RIY2798 | RIY2798 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/26/2025 13:29:48 | 10/26/2025 13:51:50 | 10/27/2025 01:29:48 | Door opening alarm at RIY2798-P2_SRAN @ Sceco | 10/26/2025 13:29:33 | Minor | 65101 | Door opening alarm | 10/26/2025 13:29:31 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2798 | FLM_EM | [8 empty] | API | 10/26/2025 13:29:48 | 10/26/2025 13:51:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000574 | PCM-20251026-00001256 | TT-20251026-01240 | Telecom | Region_2 | RIY2M8163 | RIY2163 | Equipment | SFP_BTS | Clean SFP | Mubashar Farooq Abdul Majeed | 10/26/2025 13:32:37 | 10/26/2025 15:56:08 | 10/26/2025 19:32:37 | Cell Unavailable at RIY2M8163-CA-L900-L800-P1-VIP @ Sceco | 10/26/2025 13:31:42 | Major | 29240 | Cell Unavailable | 10/26/2025 13:30:09 | VIP | 4G | riyadh | Sceco | LTE SA | RIY2M8163 | FLM_TE | [8 empty] | API | 10/26/2025 13:32:37 | 10/26/2025 15:18:23 | 10/26/2025 15:23:56 | 10/26/2025 15:23:59 | 10/26/2025 15:24:04 | 10/26/2025 15:56:08 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000575 | PCM-20251026-00001257 | TT-20251026-01226 | Telecom | Region_6 | ABH0280 | ABH0280 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 13:33:08 | 10/26/2025 14:08:50 | 10/26/2025 19:33:08 | 2(2G) 2(3G) 1(LTE) 2(5G) sites down under ABH0280-P2,MHAB0707-P2/MHAB0707-P2 @ Sceco | 10/26/2025 13:24:23 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 13:24:19 | P2 | 2G | abha | Sceco | 2G_3G_LTE_5G SA | MHAB0707-P2 2G_3G_LTE_5G,ABH0280-P2 2G_3G_5G | FLM_TE | ABH0280 | Dear team , HUB: ABH0280 We observing Link flapping at the HUB ,kindly check locally | PCM-20251026-00001253 | Dear team , HUB: ABH0280 We observing Link flapping at the HUB ,kindly check locally | Dear team , HUB: ABH0280 We observing Link flapping at the HUB ,kindly check locally |  | sites down |  | API | 10/26/2025 13:33:08 | 10/26/2025 14:04:44 | 10/26/2025 14:08:40 |  |  | 10/26/2025 14:08:50 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000576 | PCM-20251026-00001259 | TT-20251026-01241 | EM | Region_6 | TLT0722 | TLT0722 |  |  |  | Muhammad Gomaa | 10/26/2025 13:33:56 | 10/26/2025 15:49:09 | 10/27/2025 01:33:56 | AIRCON 1 FAILURE at TLT0722-GSM-P3 @ Sceco | 10/26/2025 13:25:37 | Minor | 7103 | AIRCON 1 FAILURE | 10/26/2025 13:25:30 | P3 | 2G | tathleeth | Sceco | 2G NSA | TLT0722 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/26/2025 13:33:56 | 10/26/2025 15:49:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251026000577 | PCM-20251026-00001261 | TT-20251026-01232 | Telecom | Region_4 | JED1M7504 | JED0504 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/26/2025 13:34:29 | 10/26/2025 22:15:56 | 10/26/2025 17:34:29 | 1(LTE) sites down under JED0504-CA-L800-P1-VIP-SBTS @ Sceco | 10/26/2025 13:26:17 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 13:26:13 | VIP | 4G | jeddah | Sceco | LTE SA | JED0504-CA-L800-P1-VIP-SBTS | FLM_TE | JED0504 | Results: DOWN SITE HUB JED0504-CA-L800-P1-VIP-SBTS JED0504 Summary: Hub: JED0504, Down Count: 1, Down Sites: JED0504-CA-L800-P1-VIP-SBTS Alarm Summary: JED0504 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.96.16.108:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 13:34:29 | 10/26/2025 22:15:42 | 10/26/2025 22:15:49 | 10/26/2025 22:15:52 | 10/26/2025 22:15:56 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000578 | PCM-20251026-00001262 | TT-20251026-01242 | Reference_EM | Region_1 | RYDM2059 | RYDM2059 |  |  |  | Ahmed AbdELmoaz Ibrahim | 10/26/2025 13:34:57 | 10/26/2025 18:51:21 | 10/27/2025 01:34:57 | Mains Failure at RYDM2059-P2_SRAN @ Sceco_STB | 10/26/2025 13:25:16 | Minor | 65109 | Mains Failure | 10/26/2025 13:25:13 | P2 | SRAN | dammam | Sceco_STB | 2G NSA | RYDM2059 | FLM_EM | [8 empty] | API | 10/26/2025 13:34:57 | 10/26/2025 18:51:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000579 | PCM-20251026-00001264 | TT-20251026-01235 | EM | [7 empty] | 10/26/2025 13:35:58 | 10/26/2025 13:35:58 | 10/26/2025 19:35:58 | 1(2G/LTE) sites down under BDR2112-P3-CAP/R3_MD_HWBSC01 @ Generator_DG | 10/26/2025 13:27:37 | Major | 21825 | CSL Fault | 10/26/2025 13:27:35 | P3 | 2G |  | Generator_DG | 2G_LTE SA | BDR2112-P3-CAP | FLM_EM | BDR2112 | Results: DOWN SITE HUB BDR2112-P3-CAP BDR2112 Summary: Hub: BDR2112, Down Count: 1, Down Sites: BDR2112-P3-CAP Alarm Summary: BDR2112 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 13:35:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000580 | PCM-20251026-00001265 | TT-20251026-01236 | EM | Region_1 | JBL2M1913 | JBL0913 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 13:36:01 | 10/26/2025 23:51:22 | 10/26/2025 19:36:01 | 1(2G/3G/LTE) sites down under JBL0913-P2/R1_JB_HWBSC01 @ Sceco | 10/26/2025 13:29:19 | Major | 21825 | CSL Fault | 10/26/2025 13:29:16 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | JBL0913-P2 | FLM_EM | JBL0913 | Results: DOWN SITE HUB JBL0913-P2 JBL0913 Summary: Hub: JBL0913, Down Count: 1, Down Sites: JBL0913-P2 Alarm Summary: JBL0913 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 13:36:01 | 10/26/2025 23:51:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000582 | PCM-20251026-00001267 | TT-20251005-01481 | Reference_telecom | Region_4 | JED0159 | JED0159 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 13:36:25 | 10/26/2025 13:36:25 | 10/27/2025 01:36:25 | Degrade observed in JED0159_1 towards 10.10.180.2 @ Sceco | 10/04/2025 21:06:24 | Minor |  | Degrade | 10/04/2025 21:06:19 | VIP | 2G | jeddah | Sceco | TX NSA | JED0159 | FLM_TE |  | kindly follow data shared by mail from planning | PCM-20251013-00001667 | kindly follow data shared by mail from planning | kindly follow data shared by mail from planning |  |  |  | API | 10/26/2025 13:36:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000583 | PCM-20251026-00001268 | TT-20251002-01082 | Reference_telecom | Region_4 | JED0159 | JED0159 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 13:37:41 | 10/26/2025 13:37:41 | 10/27/2025 01:37:41 | Nokia Eband Observing LagPortDown-Port 6/5,DemFail-Port 6/5,Degrade-LAG at JED0159_1-10.10.180.2 | 09/22/2025 19:01:22 | Minor |  | LOF | 09/22/2025 19:01:22 | VIP | 2G | jeddah | Sceco | TX NSA | JED0159_1-10.10.180.2 | FLM_TE |  | kindly follow data shared by mail from planning | PCM-20251013-00001665 | kindly follow data shared by mail from planning | kindly follow data shared by mail from planning |  |  |  | API | 10/26/2025 13:37:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000584 | PCM-20251026-00001270 | TT-20251026-01243 | Telecom | Region_2 | RIY2163 | RIY2163 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Mubashar Farooq Abdul Majeed | 10/26/2025 13:38:35 | 10/26/2025 15:56:54 | 10/27/2025 01:38:35 | RF Unit Maintenance Link Failure at RIY2163-P1-VIP_SRAN @ Sceco | 10/26/2025 13:33:14 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 13:33:06 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2163 | FLM_TE | [8 empty] | API | 10/26/2025 13:38:35 | 10/26/2025 15:17:59 | 10/26/2025 15:56:14 | 10/26/2025 15:56:17 | 10/26/2025 15:56:23 | 10/26/2025 15:56:54 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000585 | PCM-20251026-00001272 | TT-20251026-01176 | Telecom | Region_2 | RIY0700 | RIY0700 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 13:39:24 | 10/27/2025 07:29:24 | 10/27/2025 01:39:24 | HC for RIY0700,RIY0580,RIY0338 | 10/26/2025 13:00:09 | Minor | 676767672 | Health Check-WO to TE FME | 10/26/2025 13:00:12 | P1 | SRAN | riyadh | Sceco | 3G NSA | RIY0700 | FLM_TE |  |  | PCM-20251026-00001210 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance End A Point RIY0130_NE_7_V End Z Point RIY0338_NE_1_V | End A Point RIY0130_NE_7_V End Z Point RIY0338_NE_1_V |  |  |  | API | 10/26/2025 13:39:24 | 10/27/2025 07:29:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000586 | PCM-20251026-00001273 | TT-20251026-01246 | EM | Region_6 | HUS1M7159 | HUS0159 |  |  |  | Khurram Nawaz Muhammad Akram | 10/26/2025 13:39:35 | 10/26/2025 14:14:41 | 10/27/2025 01:39:35 | SHELTER DOOR OPEN at HUS1M7159-P3-L800-CA @ Sceco | 10/26/2025 13:39:24 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 13:39:18 | P3 | 4G | jizan | Sceco | LTE NSA | HUS1M7159 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 13:39:35 | 10/26/2025 14:14:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000587 | PCM-20251026-00001274 | TT-20251026-01248 | Reference_EM | Region_3 | MDN2534 | MDN2534 |  |  |  | Tasbeeh Ullah Muhammad Yousaf | 10/26/2025 13:39:36 | 10/26/2025 13:39:36 | 10/27/2025 01:39:36 | Door opening alarm at MDN2534-P3_SRAN @ Generator_SG | 10/26/2025 13:39:25 | Minor | 65101 | Door opening alarm | 10/26/2025 13:33:54 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDN2534 | FLM_EM | [8 empty] | API | 10/26/2025 13:39:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000588 | PCM-20251026-00001275 | TT-20251026-01247 | Reference_EM | Region_1 | HFBD2M5008 | HFBD0008 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/26/2025 13:39:37 | 10/26/2025 15:47:26 | 10/26/2025 19:39:37 | Air-condition #1 failure alarm at HFBD2M5008-P1-HUB @ Generator_SG | 10/26/2025 13:29:32 | Major | 65104 | Air-condition #1 failure alarm | 10/26/2025 13:29:29 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5008 | FLM_EM | [8 empty] | API | 10/26/2025 13:39:37 | 10/26/2025 15:47:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000589 | PCM-20251026-00001277 | TT-20251026-01249 | Telecom | Region_2 | RIY2163 | RIY2163 | Equipment | SFP_BTS | Clean SFP | Mubashar Farooq Abdul Majeed | 10/26/2025 13:40:06 | 10/26/2025 15:57:29 | 10/26/2025 19:40:06 | BBU CPRI Interface Error at RIY2163-P1-VIP_SRAN @ Sceco | 10/26/2025 13:38:11 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 13:32:05 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2163 | FLM_TE | [8 empty] | API | 10/26/2025 13:40:06 | 10/26/2025 15:17:49 | 10/26/2025 15:57:07 | 10/26/2025 15:57:10 | 10/26/2025 15:57:13 | 10/26/2025 15:57:29 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000590 | PCM-20251026-00001278 | TT-20251026-01251 | Telecom | Region_2 | RAS2M4248 | RAS2248 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Syed Sibtain Naqvi SyedManzoor | 10/26/2025 13:41:29 | 10/26/2025 15:17:15 | 10/26/2025 19:41:29 | UMTS Cell Unavailable at RAS2M4248-FWA-P1-VIP @ Sceco | 10/26/2025 13:35:39 | Major | 22202 | UMTS Cell Unavailable | 10/26/2025 13:35:34 | P2 | 3G | al rass | Sceco | 3G SA | RAS2M4248 | FLM_TE | [8 empty] | API | 10/26/2025 13:41:29 | 10/26/2025 15:16:33 | 10/26/2025 15:16:51 |  |  | 10/26/2025 15:17:15 |  | Syed Sibtain Naqvi SyedManzoor |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000591 | PCM-20251026-00001279 | TT-20251026-01237 | EM | Region_1 | JBL0913 | JBL0913 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 13:41:37 | 10/26/2025 23:51:23 | 10/26/2025 17:41:37 | 1(2G/3G/LTE) sites down under JBAP0137-P1/R1_JB_HWBSC01 @ Sceco | 10/26/2025 13:29:19 | Critical | 21825 | CSL Fault | 10/26/2025 13:29:16 | P2 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBAP0137-P1 | FLM_EM | JBL0913 | Dear Team, Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251026-00001276 | Dear Team, Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/26/2025 13:41:37 | 10/26/2025 23:51:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000592 | PCM-20251026-00001283 | TT-20251026-01256 | Telecom | Region_6 | SRA1M8353 | SRA2353 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 13:43:12 | 10/26/2025 17:40:03 | 10/27/2025 01:43:12 | BASE STATION SERVICE PROBLEM (No connection to unit) at SRA1M8353-G9-L800-P3-SBTS @ Generator_SG | 10/26/2025 13:42:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 13:42:08 | P3 | 4G | Baha | Generator_SG | 5G_Cell SA | SRA1M8353 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 13:43:12 | 10/26/2025 14:54:43 | 10/26/2025 17:39:51 |  |  | 10/26/2025 17:40:03 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000593 | PCM-20251026-00001284 | TT-20251026-01259 | Telecom | Region_4 | JED1M7066 | JED0066 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 13:44:14 | 10/26/2025 14:24:00 | 10/27/2025 01:44:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7066-P3-CA-L900-L800-SBTS @ Sceco | 10/26/2025 13:43:17 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 13:43:07 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 13:44:14 | 10/26/2025 14:24:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000595 | PCM-20251026-00001288 | TT-20251026-01250 | Telecom | Region_4 | SWHT1S7913 | SWHT0913 |  |  |  | Rashid Shafique | 10/26/2025 13:45:29 | 10/26/2025 14:51:26 | 10/26/2025 19:45:29 | 1(LTE) sites down under SWHT0913-USF-P3 @ Sceco | 10/26/2025 13:37:28 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 13:37:24 | P3 | 4G | taif | Sceco | LTE SA | SWHT0913-USF-P3 | FLM_TE | SWHT0913 | Results: DOWN SITE HUB SWHT0913-USF-P3 SWHT0913 Summary: Hub: SWHT0913, Down Count: 1, Down Sites: SWHT0913-USF-P3 Alarm Summary: SWHT0913 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.95.220:8080] [URL:http://10.88.95.220:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 13:45:29 | 10/26/2025 14:51:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000596 | PCM-20251026-00001291 | TT-20251026-01254 | EM | Region_1 | DAM2U6111 | DAM6011 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 13:47:03 | 10/26/2025 19:33:57 | 10/26/2025 19:47:03 | 1(2G/3G) sites down under DAM6011-P3/R1_DM_HWBSC01 @ Sceco | 10/26/2025 13:39:15 | Major | 21825 | CSL Fault | 10/26/2025 13:39:12 | P3 | 2G | dammam | Sceco | 2G_3G SA | DAM6011-P3 | FLM_EM | DAM6011 | Results: DOWN SITE HUB DAM6011-P3 DAM6011 Summary: Hub: DAM6011, Down Count: 1, Down Sites: DAM6011-P3 Alarm Summary: DAM6011 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 13:47:03 | 10/26/2025 19:33:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000598 | PCM-20251026-00001304 | TT-20251026-01262 | Telecom | [7 empty] | 10/26/2025 13:51:35 | 10/26/2025 14:49:33 | 10/26/2025 19:51:35 | 3(2G) 2(LTE) sites down under BDR2243-P3-CAP,BDR2110-P3-CAP,BDR2244-P3-CAP/R3_MD_HWBSC01 @ Sceco | 10/26/2025 13:41:51 | Major | 21825 | CSL Fault | 10/26/2025 13:41:47 | P3 | Repeater |  | Sceco | 2G SA | BDR2244-P3-CAP 2G,BDR2110-P3-CAP 2G,BDR2243-P3-CAP 2G | FLM_TE | RUSF9078 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : RUSF9078 DIR RUSF9030,Kindly visit the link and perform the HC at mentioned link . | PCM-20251026-00001298 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : RUSF9078 DIR RUSF9030,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : RUSF9078 DIR RUSF9030,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/26/2025 13:51:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000600 | PCM-20251026-00001312 | TT-20251026-01290 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 13:55:05 | 10/26/2025 13:55:05 | 10/26/2025 19:55:05 | high temprature 32 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/26/2025 13:44:57 | Major | 65102 | high temprature 32 | 10/26/2025 13:44:52 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/26/2025 13:55:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000601 | PCM-20251026-00001313 | TT-20251026-01274 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 13:56:04 | 10/26/2025 15:16:03 | 10/26/2025 19:56:04 | 2(2G) 2(LTE) sites down under BHAB2091-P3,BHAB2103-P3/BHAB2103-P3 @ Generator_DG | 10/26/2025 13:45:36 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 13:45:31 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2091-P3 2G_LTE,BHAB2103-P3 2G_LTE | FLM_EM | BHAB2091 | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251026-00001306 | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/26/2025 13:56:04 | 10/26/2025 15:16:03 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000602 | PCM-20251026-00001314 | TT-20251026-01292 | Reference_EM | Region_3 | HAL0216 | HAL0216 |  |  |  | Mohamed Yasser Zakir Mohamed | 10/26/2025 13:56:37 | 10/26/2025 13:56:37 | 10/27/2025 01:56:37 | Door opening alarm at HAL0216-P2_SRAN @ Sceco | 10/26/2025 13:56:11 | Minor | 65101 | Door opening alarm | 10/26/2025 13:56:07 | P3 | SRAN | hail | Sceco | 2G NSA | HAL0216 | FLM_EM | [8 empty] | API | 10/26/2025 13:56:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000603 | PCM-20251026-00001324 | TT-20251026-01219 | Telecom | Region_2 | RIYD2U6811 | RIYD6111 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 13:59:56 | 10/26/2025 17:56:28 | 10/27/2025 01:59:56 | Cell Capability Degraded at RIYD2U6811-P2 @ Sceco | 10/26/2025 13:17:07 | Minor | 29243 | Cell Capability Degraded | 10/26/2025 13:15:31 | P2 | 4G | riyadh | Sceco | 2G NSA | RIYD2U6811 | FLM_TE |  |  | PCM-20251026-00001237 | please do HC Path eNodeB Function Name=RIYD2U6811-P2, Local Cell ID=0, Cell FDD TDD indication=FDD, NB-IoT Cell Flag=FALSE, TX Channel Numbers In The Cell=1, RX Channel Numbers In The Cell=2, Cell Name=RIYD2U6811A, eNodeB ID=246811, Cell ID=0, Specific Problem=Antenna channel exceptions | please do HC Path eNodeB Function Name=RIYD2U6811-P2, Local Cell ID=0, Cell FDD TDD indication=FDD, NB-IoT Cell Flag=FALSE, TX Channel Numbers In The Cell=1, RX Channel Numbers In The Cell=2, Cell Name=RIYD2U6811A, eNodeB ID=246811, Cell ID=0, Specific Problem=Antenna channel exceptions |  |  |  | API | 10/26/2025 13:59:56 | 10/26/2025 14:43:36 | 10/26/2025 14:44:30 | 10/26/2025 14:59:53 | 10/26/2025 15:00:29 | 10/26/2025 17:56:28 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000604 | PCM-20251026-00001325 | TT-20251026-01300 | Telecom | Region_3 | MDN2984 | MDN2984 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | TAUSEEF ILYAS | 10/26/2025 14:00:15 | 10/26/2025 14:15:27 | 10/27/2025 02:00:15 | RF Unit Maintenance Link Failure at MDN2984-P2_SRAN @ Sceco | 10/26/2025 13:55:50 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 13:55:10 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2984 | FLM_TE | [8 empty] | API | 10/26/2025 14:00:15 | 10/26/2025 14:13:25 | 10/26/2025 14:13:55 | 10/26/2025 14:13:59 | 10/26/2025 14:14:01 | 10/26/2025 14:15:27 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000606 | PCM-20251026-00001327 | TT-20251026-01302 | Telecom | Region_3 | TBK2M4676 | TBK2676 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Tahir Abbas Fateh Khan | 10/26/2025 14:00:15 | 10/26/2025 18:05:36 | 10/27/2025 02:00:15 | ALD Maintenance Link Failure at TBK2M4676-P2 @ Sceco | 10/26/2025 13:57:45 | Minor | 26541 | ALD Maintenance Link Failure | 10/26/2025 13:56:09 | P2 | 3G | tabouk | Sceco | 3G NSA | TBK2M4676 | FLM_TE | [8 empty] | API | 10/26/2025 14:00:15 | 10/26/2025 16:47:12 | 10/26/2025 17:11:19 | 10/26/2025 17:11:23 | 10/26/2025 17:37:23 | 10/26/2025 18:05:36 |  | Tahir Abbas Fateh Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000607 | PCM-20251026-00001329 | TT-20251026-01281 | Reference_telecom | Region_2 | RIYB2U6786 | RIYB6086 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/26/2025 14:00:49 | 10/26/2025 14:00:49 | 10/27/2025 02:00:49 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6786-L1800-CA-P3 @ Sceco | 10/26/2025 10:51:04 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 10:51:01 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6786 | FLM_TE |  |  | PCM-20251026-00001302 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 14:00:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000608 | PCM-20251026-00001330 | TT-20251026-01291 | EM | Region_3 | TBK2U6199 | TBK6099 |  |  |  | Mohammad Mahmoud Abdelazim Tawfic | 10/26/2025 14:00:59 | 10/26/2025 14:00:59 | 10/26/2025 20:00:59 | 1(2G/3G) sites down under TBK6099-P3/R3_TB_HWBSC01 @ Sceco | 10/26/2025 13:53:38 | Major | 21807 | OML Fault | 10/26/2025 13:53:33 | P3 | 2G | tabouk | Sceco | 2G_3G SA | TBK6099-P3 | FLM_EM | TBK6099 | Results: DOWN SITE HUB TBK6099-P3 TBK6099 Summary: Hub: TBK6099, Down Count: 1, Down Sites: TBK6099-P3 Alarm Summary: TBK6099 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 14:00:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000609 | PCM-20251026-00001331 | TT-20251026-01304 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/26/2025 14:01:16 | 10/26/2025 16:29:47 | 10/27/2025 02:01:16 | Door opening alarm at RIY2866-P3_SRAN-PC @ Sceco | 10/26/2025 14:00:42 | Minor | 65101 | Door opening alarm | 10/26/2025 14:00:38 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/26/2025 14:01:16 | 10/26/2025 16:29:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000612 | PCM-20251026-00001339 | TT-20251026-01313 | EM | Region_6 | BHAB1M7819 | BHAB0819 |  |  |  | Arif Ullah Shah | 10/26/2025 14:05:24 | 10/27/2025 08:48:02 | 10/27/2025 02:05:24 | COMMERCIAL POWER FAILURE at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/26/2025 13:56:59 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/26/2025 13:56:54 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7819 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/26/2025 14:05:24 | 10/27/2025 08:48:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000613 | PCM-20251026-00001340 | TT-20251026-01314 | Telecom | Region_4 | JED0869 | JED0869 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 14:05:41 | 10/26/2025 14:29:59 | 10/26/2025 20:05:41 | PT:: FLM Need to perform HC at JED0869 under R4 (BO Request) | 10/26/2025 14:05:29 | Major | 676767671 | Health Check-WO to TE FME | 10/26/2025 14:05:29 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0869 | FLM_TE | [8 empty] | API | 10/26/2025 14:05:41 | 10/26/2025 14:29:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000614 | PCM-20251026-00001345 | TT-20251026-01318 | Reference_telecom | Region_4 | JZMA2202 | JZMA2202 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 14:06:56 | 10/26/2025 14:50:39 | 10/27/2025 02:06:56 | LossOfSignal observed in JZMA2202_01 towards 10.221.243.67 @ Generator_SG | 10/26/2025 02:07:02 | Minor |  | LossOfSignal | 10/26/2025 02:06:25 | P3 | 2G | jeddah | Generator_SG | TX NSA | JZMA2202 | FLM_TE | [8 empty] | API | 10/26/2025 14:06:56 | 10/26/2025 14:50:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000615 | PCM-20251026-00001348 | TT-20251026-01307 | EM | Region_2 | RYQ2M1989 | RYQ0989 |  |  |  | Mohamed Moustafa Aboelmagd Hefny | 10/26/2025 14:07:30 | 10/26/2025 19:33:42 | 10/26/2025 20:07:30 | 1(2G/3G/LTE) sites down under RYQ0989-P2/RY1BSCH02 @ Sceco | 10/26/2025 14:00:49 | Major | 21825 | CSL Fault | 10/26/2025 14:00:47 | P2 | 2G | majma | Sceco | 2G_3G_LTE SA | RYQ0989-P2 | FLM_EM | RYQ0989 | Results: DOWN SITE HUB RYQ0989-P2 RYQ0989 Summary: Hub: RYQ0989, Down Count: 1, Down Sites: RYQ0989-P2 Alarm Summary: RYQ0989 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 14:07:30 | 10/26/2025 19:33:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000616 | PCM-20251026-00001356 | TT-20251026-01287 | Reference_telecom | Region_6 | QJF1M7075 | QJF0075 | Transsmission | SFP_Transmission | Reset SFP | Zeshan Ali Adnan | 10/26/2025 14:09:39 | 10/26/2025 16:12:52 | 10/27/2025 02:09:39 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at QJF1M7075-G9-L18-L21-SBTS-P2 @ Sceco | 10/26/2025 13:53:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 03:02:36 | P2 | 4G | baish | Sceco | LTE NSA | QJF1M7075 | FLM_TE |  |  | PCM-20251026-00001310 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/26/2025 14:09:39 | 10/26/2025 15:53:32 | 10/26/2025 16:10:54 |  |  | 10/26/2025 16:12:52 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000617 | PCM-20251026-00001357 | TT-20251026-01279 | Reference_telecom | Region_6 | ABH0086 | ABH0086 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 14:09:49 | 10/26/2025 15:03:03 | 10/27/2025 02:09:49 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABH0086-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 11:50:36 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 11:50:25 | P2 | 2G | abha | Sceco | 2G NSA | ABH0086 | FLM_TE |  |  | PCM-20251026-00001299 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/26/2025 14:09:49 | 10/26/2025 15:02:41 | 10/26/2025 15:02:53 |  |  | 10/26/2025 15:03:03 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000618 | PCM-20251026-00001359 | TT-20251020-00328 | Reference_telecom | Region_5 | QUB1M8348 | QUB2348 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 14:10:18 | 10/26/2025 14:10:18 | 10/27/2025 02:10:18 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QUB1M8348-G9-NL8-L18-SBTS-P2-USF @ Generator_DG | 10/20/2025 01:44:21 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 01:39:06 | P2 | 4G | makkah | Generator_DG | LTE NSA | QUB1M8348 | FLM_TE |  |  | PCM-20251026-00001159 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/26/2025 14:10:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000619 | PCM-20251026-00001360 | TT-20251020-00151 | Telecom | Region_5 | MAK1M9386 | MAK0386 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/26/2025 14:10:29 | 10/26/2025 14:26:23 | 10/27/2025 02:10:29 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at MAK1M9386-G9-L8-L18-L21-SBTS-P2 @ Generator_SG | 10/20/2025 01:33:37 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 03:02:23 | P2 | 4G | makkah | Generator_SG | LTE NSA | MAK1M9386 | FLM_TE |  |  | PCM-20251026-00001158 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/26/2025 14:10:29 | 10/26/2025 14:26:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000620 | PCM-20251026-00001362 | TT-20251026-01317 | Telecom | Region_4 | KMMD0720 | KMMD0720 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/26/2025 14:12:12 | 10/26/2025 15:23:53 | 10/26/2025 18:12:12 | BASE STATION ANTENNA LINE PROBLEM at KMMD0720-GSM-P1-HUB @ Sceco_STB | 10/26/2025 13:59:40 | Critical | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 13:59:35 | P1 | 2G | jeddah | Sceco_STB | 2G NSA | KMMD0720 | FLM_TE |  |  | PCM-20251026-00001344 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 14:12:12 | 10/26/2025 15:23:07 | 10/26/2025 15:23:48 |  |  | 10/26/2025 15:23:53 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000621 | PCM-20251026-00001363 | TT-20251026-01284 | Telecom | Region_4 | HAW1M8351 | HAW2351 |  |  |  | Rashid Shafique | 10/26/2025 14:12:25 | 10/26/2025 14:51:27 | 10/26/2025 20:12:25 | BASE STATION ANTENNA LINE PROBLEM at HAW1M8351-P3-CA-L800 @ Sceco | 10/26/2025 13:45:47 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 13:45:42 | P2 | 4G | taif | Sceco | LTE NSA | HAW1M8351 | FLM_TE |  |  | PCM-20251026-00001305 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 14:12:25 | 10/26/2025 14:51:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000622 | PCM-20251026-00001365 | TT-20251026-01273 | Reference_telecom | Region_6 | ABH1MN0160 | ABH0160 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Amir Sohail | 10/26/2025 14:12:38 | 10/26/2025 16:21:21 | 10/26/2025 20:12:38 | BASE STATION SERVICE PROBLEM (No connection to unit;SharedMaster) at ABH1MN0160-NR2.6 @ Sceco_STB | 10/26/2025 13:47:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 13:47:46 | P2 | 5G | abha | Sceco_STB | 5G_Cell SA | ABH1MN0160 | FLM_TE |  |  | PCM-20251026-00001295 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 14:12:38 | 10/26/2025 14:30:30 | 10/26/2025 16:21:14 |  |  | 10/26/2025 16:21:21 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000624 | PCM-20251026-00001366 | TT-20251026-01271 | Reference_telecom | Region_6 | ABH1M7103 | ABH0103 | Equipment | BSS_HW_fault | Replace RF Module | Amir Sohail | 10/26/2025 14:12:46 | 10/26/2025 16:20:57 | 10/26/2025 20:12:46 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at ABH1M7103-P2-USF-L900 @ Sceco_STB | 10/26/2025 13:43:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 13:43:28 | P2 | 4G | abha | Sceco_STB | 5G_Cell SA | ABH1M7103 | FLM_TE |  |  | PCM-20251026-00001294 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 14:12:46 | 10/26/2025 14:30:31 | 10/26/2025 16:20:25 | 10/26/2025 16:20:30 |  | 10/26/2025 16:20:57 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000625 | PCM-20251026-00001367 | TT-20251025-00244 | Reference_telecom | Region_4 | TURY0826 | TURY0826 | Equipment | SFP_BTS | Replace SFP | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/26/2025 14:12:52 | 10/27/2025 08:01:41 | 10/26/2025 20:12:52 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/25/2025 04:00:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/25/2025 04:00:03 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251026-00001250 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 14:12:52 | 10/27/2025 07:58:29 | 10/27/2025 08:01:31 |  |  | 10/27/2025 08:01:41 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000628 | PCM-20251026-00001370 | TT-20251026-01334 | EM | Region_6 | BHAQ1M8438 | BHAQ2438 |  |  |  | Fathy Mohamed | 10/26/2025 14:13:39 | 10/26/2025 16:16:51 | 10/27/2025 02:13:39 | AIRCON 1 FAILURE at BHAQ1M8438-G9-L8-SBTS @ Generator_SG | 10/26/2025 14:05:18 | Minor | 7103 | AIRCON 1 FAILURE | 10/26/2025 14:05:10 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAQ1M8438 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/26/2025 14:13:39 | 10/26/2025 16:16:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000629 | PCM-20251026-00001371 | TT-20251026-01326 | Telecom | Region_6 | JEC1M7318 | JEC0318 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/26/2025 14:14:29 | 10/26/2025 18:21:34 | 10/26/2025 18:14:29 | 1(LTE) sites down under JEC0318-VIP-CA-L800 @ Generator_SG | 10/26/2025 14:06:15 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 14:06:11 | VIP | 4G | baish | Generator_SG | LTE SA | JEC0318-VIP-CA-L800 | FLM_TE | JEC0318 | Results: DOWN SITE HUB JEC0318-VIP-CA-L800 JEC0318 Summary: Hub: JEC0318, Down Count: 1, Down Sites: JEC0318-VIP-CA-L800 Alarm Summary: JEC0318 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.4.140:8080] [URL:http://10.97.4.140:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 14:14:29 | 10/26/2025 14:31:31 | 10/26/2025 16:30:34 | 10/26/2025 16:30:38 | 10/26/2025 16:42:48 | 10/26/2025 18:21:34 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000630 | PCM-20251026-00001374 | TT-20251026-01340 | EM | Region_6 | ABBS1M8247 | ABBS2247 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/26/2025 14:15:12 | 10/26/2025 14:15:12 | 10/27/2025 02:15:12 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at ABBS1M8247-L800-P3-SBTS-WBB-G3 @ Sceco | 10/26/2025 14:06:54 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/26/2025 14:06:43 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M8247 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/26/2025 14:15:12 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000631 | PCM-20251026-00001376 | TT-20251026-01342 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/26/2025 14:15:44 | 10/26/2025 16:29:48 | 10/27/2025 02:15:44 | Air condition 1 failure alarm at RIY2866-P3_SRAN-PC @ Sceco | 10/26/2025 14:05:17 | Minor | 65104 | Air condition 1 failure alarm | 10/26/2025 14:05:13 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/26/2025 14:15:44 | 10/26/2025 16:29:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000632 | PCM-20251026-00001377 | TT-20251026-01148 | Reference_telecom | Region_4 | TAF2277 | TAF2277 |  |  |  | Rashid Shafique | 10/26/2025 14:16:34 | 10/26/2025 14:51:28 | 10/26/2025 20:16:34 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TAF2277-P3 @ Sceco | 10/26/2025 12:36:55 | Major | 7607 | TRX OPERATION DEGRADED | 10/26/2025 12:36:51 | P3 | 2G | taif | Sceco | 2G_TRX NSA | TAF2277 | FLM_TE |  |  | PCM-20251026-00001154 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/26/2025 14:16:34 | 10/26/2025 14:51:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000633 | PCM-20251026-00001380 | TT-20251026-01197 | Reference_telecom | Region_4 | HHR1M7494 | HHR0494 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/26/2025 14:17:20 | 10/26/2025 15:24:07 | 10/26/2025 20:17:20 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at HHR1M7494-G9-U9-L8-NL18-SBTS-VIP-HHR @ Generator_SG | 10/26/2025 13:11:16 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 03:04:01 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7494 | FLM_TE |  |  | PCM-20251026-00001211 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/26/2025 14:17:20 | 10/26/2025 15:23:08 | 10/26/2025 15:24:02 |  |  | 10/26/2025 15:24:07 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000635 | PCM-20251026-00001383 | TT-20251026-01257 | Reference_telecom | Region_4 | JED1M8052 | JED2052 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 14:18:03 | 10/26/2025 14:18:03 | 10/27/2025 02:18:03 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at JED1M8052-P3-CA-L900-L800-SBTS @ Sceco | 10/26/2025 13:41:29 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 10:22:05 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M8052 | FLM_TE |  |  | PCM-20251026-00001282 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/26/2025 14:18:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000636 | PCM-20251026-00001389 | TT-20251026-01349 | EM | Region_5 | MAK6092 | MAK6092 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 14:19:51 | 10/26/2025 14:19:51 | 10/27/2025 02:19:51 | AIRCON 2 FAILURE at MAK6092-GSM-P3 @ Sceco | 10/26/2025 14:11:34 | Minor | 7103 | AIRCON 2 FAILURE | 10/26/2025 14:11:27 | P3 | 2G | makkah | Sceco | 2G NSA | MAK6092 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/26/2025 14:19:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000637 | PCM-20251026-00001395 | TT-20251026-01356 | EM | Region_4 | FRS2199 | FRS2199 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 14:23:29 | 10/26/2025 14:23:29 | 10/27/2025 02:23:29 | FIRE Alarm at FRS2199- G9-L8- L18-SBTS-P3 @ Generator_SG | 10/26/2025 14:15:28 | Minor | 7103 | FIRE Alarm | 10/26/2025 14:15:20 | P3 | 2G | qunfuddah | Generator_SG | 2G NSA | FRS2199 | FLM_EM | [5 empty] | FIRE Alarm |  |  | API | 10/26/2025 14:23:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000647 | PCM-20251026-00001402 | TT-20251026-01366 | Telecom | Region_5 | MAK0324 | MAK0324 | Equipment | BSS_HW_fault | Replace FAN | Inam ullah | 10/26/2025 14:29:40 | 10/26/2025 21:04:47 | 10/27/2025 02:29:40 | BASE STATION INFORMATION (No module fan detected) at MAK0324-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/26/2025 14:21:21 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 14:21:13 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0324 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/26/2025 14:29:40 | 10/26/2025 19:14:30 | 10/26/2025 19:45:32 | 10/26/2025 19:45:34 | 10/26/2025 19:45:45 | 10/26/2025 21:04:47 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000648 | PCM-20251026-00001403 | TT-20251026-01367 | EM | Region_5 | MKTF1M9796 | MKTF0796 |  |  |  | Muhammad Shabbir Muhammad | 10/26/2025 14:29:41 | 10/26/2025 14:29:41 | 10/27/2025 02:29:41 | SHELTER DOOR OPEN at MKTF1M9796-G9-NL8-L21-SBTS-P2-USF @ Generator_SG | 10/26/2025 14:29:11 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 14:29:05 | P3 | 4G | makkah | Generator_SG | LTE NSA | MKTF1M9796 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 14:29:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000649 | PCM-20251026-00001404 | TT-20251026-01127 | Reference_telecom | Region_5 | MAK0378 | MAK0378 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 14:30:09 | 10/26/2025 14:30:09 | 10/26/2025 20:30:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MAK0378-G9-L8-L18-L21-NR2.6-SBTS-P1-HRM @ Sceco | 10/26/2025 10:30:31 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 10:30:07 | P1 | 2G | makkah | Sceco | 2G NSA | MAK0378 | FLM_TE |  |  | PCM-20251026-00001361 | Dear FLM team, kindly check airscale port flapping at site | Dear FLM team, kindly check airscale port flapping at site |  |  |  | API | 10/26/2025 14:30:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000650 | PCM-20251026-00001407 | TT-20251026-01268 | Telecom | Region_2 | RIY0298(RY4) | RY4 |  |  |  | Saddam hussain muhammad khan | 10/26/2025 14:30:54 | 10/26/2025 14:30:54 | 10/26/2025 20:30:54 | RMON_ALM_INBADOCTS_OVER ALARM AT RY4,RY3,RY2, RY1 and JD1 NCE flapped and restored | 10/26/2025 13:42:49 | Major | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/26/2025 13:42:49 | P1 | DWDM | riyadh | Sceco_STB_Rental | DWDM NSA | RIY0298(RY4) | FLM_TE |  |  | PCM-20251026-00001347 | Check alarm status with FO | Check alarm status with FO |  |  |  | API | 10/26/2025 14:30:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000652 | PCM-20251026-00001410 | TT-20251026-01371 | Telecom | Region_6 | TLT0922 | TLT0922 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/26/2025 14:31:14 | 10/26/2025 14:32:55 | 10/26/2025 20:31:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at TLT0922-GSM-UMTS-P3 @ Sceco | 10/26/2025 14:30:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 14:30:12 | P3 | 2G | turaib | Sceco | 5G_Cell SA | TLT0922 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 14:31:14 | 10/26/2025 14:32:13 | 10/26/2025 14:32:48 |  |  | 10/26/2025 14:32:55 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000653 | PCM-20251026-00001414 | TT-20251026-01375 | EM | [7 empty] | 10/26/2025 14:31:44 | 10/26/2025 14:31:44 | 10/27/2025 02:31:44 | NETECO: Door Status Sensor Alarm at SML2203 @ Generator_DG | 10/26/2025 14:31:07 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 14:31:07 | P3 | SRAN |  | Generator_DG | 2G NSA | SML2203 | FLM_EM | [8 empty] | API | 10/26/2025 14:31:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000657 | PCM-20251026-00001419 | TT-20251026-01385 | EM | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/26/2025 14:34:50 | 10/26/2025 19:05:32 | 10/27/2025 02:34:50 | SHELTER DOOR OPEN at MKYL0914-GSM-UMTS-P3 @ Sceco | 10/26/2025 14:34:29 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 14:34:24 | P3 | 2G | alaith | Sceco | 2G NSA | MKYL0914 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 14:34:50 | 10/26/2025 19:05:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000661 | PCM-20251026-00001420 | TT-20251026-01387 | Reference_telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/26/2025 14:35:21 | 10/26/2025 14:35:21 | 10/27/2025 02:35:21 | RF Unit RX Channel RTWP/RSSI Unbalanced at MAK6018-DCU-P3 @ Sceco | 10/26/2025 11:34:56 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/26/2025 11:34:51 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/26/2025 14:35:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000663 | PCM-20251026-00001423 | TT-20251026-01389 | Telecom | Region_3 | MDHL0386 | MDHL0386 |  |  |  | Mohamed Naveed | 10/26/2025 14:35:52 | 10/26/2025 15:18:39 | 10/27/2025 02:35:52 | ODU CPU / Cable Open at MDHL0386-MDHL0385_2 on 10.158.215.74 @ Sceco_STB | 10/26/2025 14:34:59 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/26/2025 14:32:17 | P1 | SRAN | hail | Sceco_STB | TX NSA | MDHL0386 | FLM_TE | [8 empty] | API | 10/26/2025 14:35:52 | 10/26/2025 15:18:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000673 | PCM-20251026-00001427 | TT-20251026-01382 | EM | Region_1 | ARM2M1738 | ARM0738 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/26/2025 14:38:38 | 10/26/2025 19:33:57 | 10/26/2025 20:38:38 | 1(2G/3G/LTE) sites down under ARM0738-P3/DM1MBSCH01 @ Sceco | 10/26/2025 14:31:00 | Major | 21825 | CSL Fault | 10/26/2025 14:30:59 | P3 | 2G | dammam | Sceco | 2G_3G_LTE SA | ARM0738-P3 | FLM_EM | ARM0738 | Results: DOWN SITE HUB ARM0738-P3 ARM0738 Summary: Hub: ARM0738, Down Count: 1, Down Sites: ARM0738-P3 Alarm Summary: ARM0738 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 14:38:38 | 10/26/2025 19:33:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000675 | PCM-20251026-00001429 | TT-20251026-01345 | Telecom | Region_6 | WDS9457 | WDS9457 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ahmed Mamdouh Helal Helal | 10/26/2025 14:40:06 | 10/26/2025 16:08:08 | 10/26/2025 18:40:06 | 4(2G) 5(5G) sites down under WDS0758-P3 @ Generator_SG | 10/26/2025 14:14:39 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 14:14:34 | P1 | Repeater | wadi dawasar | Generator_DG | 2G_5G SA | WDS0771-P3 2G_5G,WDS0553-P3 2G_5G,WDS0772-GSM-UMTS-P3 5G,WDS0758-P3 2G_5G,WDS0686-P2-USF 2G_5G | FLM_TE | WDS9457 | Results: DOWN SITE HUB WDS0771-P3 Need to check WDS0553-P3 Need to check WDS0772-GSM-UMTS-P3 Need to check WDS0758-P3 Need to check WDS0686-P2-USF Need to check Summary: Alarm Summary: HUB site not found | PCM-20251026-00001393 | HUB: WDS9457 PM errors on MW WDS9457-WDS9471 | HUB: WDS9457 PM errrors on MW WDS9457-WDS9471 |  | sites down |  | API | 10/26/2025 14:40:06 | 10/26/2025 16:07:30 | 10/26/2025 16:07:47 |  |  | 10/26/2025 16:08:08 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000676 | PCM-20251026-00001430 | TT-20251026-01393 | Reference_EM | Region_3 | MDQS2500 | MDQS2500 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/26/2025 14:41:03 | 10/26/2025 17:08:09 | 10/27/2025 02:41:03 | NETECO: Low Battery Capacity at MDQS2500 @ Generator_DG | 10/26/2025 14:34:47 | Minor | 11357 | Low Battery Capacity | 10/26/2025 14:34:47 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2500 | FLM_EM | [8 empty] | API | 10/26/2025 14:41:03 | 10/26/2025 17:08:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000678 | PCM-20251026-00001432 | TT-20251026-01396 | Telecom | Region_1 | HFF6029 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 14:42:36 | 10/26/2025 21:27:29 | 10/26/2025 20:42:36 | DCU CPRI Interface Error at HFF6029-DCU1 @ Sceco | 10/26/2025 14:36:30 | Major | 26234 | DCU CPRI Interface Error | 10/26/2025 14:35:29 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/26/2025 14:42:36 | 10/26/2025 14:43:34 | 10/26/2025 21:26:43 |  |  | 10/26/2025 21:27:29 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000679 | PCM-20251026-00001434 | TT-20251026-01398 | Telecom | Region_5 | MAK0992 | MAK0992 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 14:43:06 | 10/26/2025 14:43:06 | 10/26/2025 20:43:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0992-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM @ Sceco | 10/26/2025 14:42:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 14:42:03 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0992 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 14:43:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000680 | PCM-20251026-00001436 | TT-20251026-01402 | Telecom | Region_4 | JED1M7504 | JED0504 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 14:44:40 | 10/26/2025 14:44:40 | 10/26/2025 20:44:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7504-CA-L800-P1-VIP-SBTS @ Sceco | 10/26/2025 14:43:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 14:43:42 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7504 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 14:44:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000681 | PCM-20251026-00001438 | TT-20251026-01394 | EM | Region_4 | JED0514 | JED0514 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 14:46:34 | 10/26/2025 14:53:01 | 10/26/2025 20:46:34 | 1(2G/5G) sites down under JED0514-P2/JED0514-P2 @ Sceco | 10/26/2025 14:38:24 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 14:38:19 | P2 | 2G | jeddah | Sceco | 2G SA | JED0514-P2 | FLM_TE | JED0514 | Results: DOWN SITE HUB JED0514-P2 JED0514 Summary: Hub: JED0514, Down Count: 1, Down Sites: JED0514-P2 Alarm Summary: JED0514 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 14:46:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000682 | PCM-20251026-00001442 | TT-20251026-01407 | Reference_telecom | Region_5 | MAK6012 | MAK6012 |  |  |  | Mosab Nasr eldeen Mohamed | 10/26/2025 14:47:30 | 10/26/2025 14:47:30 | 10/27/2025 02:47:30 | PT::FLM need to perform HC at MAK6012-G9-L18-L21-P3-SBTS (BO request) | 10/26/2025 14:47:10 | Minor | 676767671 | Health Check-WO to TE FME | 10/26/2025 14:47:10 | P3 | 2G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK6012-G9-L18-L21-P3-SBTS | FLM_TE | [8 empty] | API | 10/26/2025 14:47:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000683 | PCM-20251026-00001444 | TT-20251026-01412 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/26/2025 14:48:48 | 10/26/2025 14:48:48 | 10/27/2025 02:48:48 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/26/2025 14:40:28 | Minor | 7103 | AIRCON 1 FAILURE | 10/26/2025 14:40:21 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/26/2025 14:48:48 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000684 | PCM-20251026-00001445 | TT-20251026-01388 | Reference_telecom | Region_6 | DRB0911-LL-CSG-01 | DRB0911 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 14:48:54 | 10/26/2025 18:37:36 | 10/26/2025 18:48:54 | MW Physical Port Down at DRB0911-LL-CSG-01 To JDJZ0785 REF:TT-20250106-01934 @ Sceco_STB | 08/04/2025 05:05:02 | Critical | 101-2505274 | Physical Port Down | 08/04/2025 05:02:00 | P3 | IPRAN | derb | Sceco_STB | IPRAN SA | DRB0911-LL-CSG-01 To JDJZ0785 | FLM_TE |  |  | PCM-20251026-00001422 | Dear FLM team, PM errors on MW DRB0165-DRB0911 &DRB0908-JDJZ0785 | Dear FLM team, PM errors on MW DRB0165-DRB0911 &DRB0908-JDJZ0785 |  |  |  | API | 10/26/2025 14:48:54 | 10/26/2025 17:04:49 | 10/26/2025 18:37:26 |  |  | 10/26/2025 18:37:36 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20251026000685 | PCM-20251026-00001446 | TT-20251026-01417 | Reference_telecom | Region_6 | RUS0101 | RUS0101 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 14:49:48 | 10/26/2025 16:50:47 | 10/27/2025 02:49:48 | NEC MW Observing LOF,RX Level at RUS0101-USF(10.154.165.72) | 10/25/2025 13:55:24 | Minor |  | LOF | 10/25/2025 13:55:24 | P2 | 2G | khamis mushyet | Sceco | TX NSA | RUS0101-USF(10.154.165.72) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:48 | 10/26/2025 16:49:36 | 10/26/2025 16:50:44 | 10/26/2025 16:50:47 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000686 | PCM-20251026-00001447 | TT-20251026-01418 | Reference_telecom | Region_6 | BDN0056 | BDN0056 |  |  |  | Manzoor Ahmed | 10/26/2025 14:49:49 | 10/26/2025 14:54:43 | 10/27/2025 02:49:49 | NEC MW Observing ETH TF at BDN0056(10.89.224.69) | 10/25/2025 15:47:12 | Minor |  | LOF | 10/25/2025 15:47:12 | P3 | 2G | Albaha | Sceco | TX NSA | BDN0056(10.89.224.69) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:49 | 10/26/2025 14:54:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000687 | PCM-20251026-00001448 | TT-20251026-01420 | Reference_telecom | Region_1 | DMH0103 | DMH0103 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 14:49:50 | 10/26/2025 15:09:07 | 10/27/2025 02:49:50 | NEC MW Observing LOF,RX Level,LOF,RX Level,High BER at DMH0103-2(10.159.105.153) | 10/25/2025 00:27:36 | Minor |  | LOF | 10/25/2025 00:27:36 | P1 | SRAN | hafr | Generator_SG | TX NSA | DMH0103-2(10.159.105.153) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:50 | 10/26/2025 15:09:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000688 | PCM-20251026-00001449 | TT-20251026-01419 | Telecom | Region_6 | TFBH0887-LL-CSG-01 | TFBH0887 |  |  |  | SHAH KHALID | 10/26/2025 14:49:51 | 10/26/2025 17:41:04 | 10/27/2025 02:49:51 | Bad Package Error Rising at TFBH0887-LL-CSG-01 @ Sceco_STB | 10/26/2025 14:49:41 | Minor | 101-2501403 | Bad Package Error Rising | 10/26/2025 14:49:32 | P3 | IPRAN | makhwa | Sceco_STB | IPRAN NSA | TFBH0887-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/26/2025 14:49:51 | 10/26/2025 17:41:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000689 | PCM-20251026-00001450 | TT-20251026-01421 | Reference_telecom | Region_5 | MKMD0552 | MKMD0552 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 14:49:52 | 10/26/2025 14:49:52 | 10/27/2025 02:49:52 | NEC MW Observing Frame ID,High BER at MKMD0552_3(10.154.143.204) | 10/25/2025 23:03:20 | Minor |  | LOF | 10/25/2025 23:03:20 | P3 | 2G | makkah | Generator_SG | TX NSA | MKMD0552_3(10.154.143.204) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000690 | PCM-20251026-00001451 | TT-20251026-01422 | Reference_telecom | Region_6 | QSB0028 | QSB0028 |  |  |  | Muhammad Ali | 10/26/2025 14:49:53 | 10/26/2025 15:00:23 | 10/27/2025 02:49:53 | NEC MW Observing SFP Type Mismatch at QSB0028(10.89.227.98) | 10/25/2025 13:25:31 | Minor |  | LOF | 10/25/2025 13:25:31 | P2 | 2G | jizan | Sceco | TX NSA | QSB0028(10.89.227.98) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:53 | 10/26/2025 15:00:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000691 | PCM-20251026-00001452 | TT-20251026-01423 | Reference_telecom | Region_6 | BSA0463 | BSA0463 |  |  |  | Hamid Ullah Muhammad Alam Khan | 10/26/2025 14:49:55 | 10/26/2025 15:23:57 | 10/27/2025 02:49:55 | NEC MW Observing Low BER at BSA0463(10.154.162.230) | 10/25/2025 16:11:18 | Minor |  | LOF | 10/25/2025 16:11:18 | P3 | 2G | bisha | Generator_SG | TX NSA | BSA0463(10.154.162.230) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:55 | 10/26/2025 15:23:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000692 | PCM-20251026-00001453 | TT-20251026-01424 | Reference_telecom | Region_6 | BSH0084 | BSH0084 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/26/2025 14:49:57 | 10/26/2025 20:21:15 | 10/27/2025 02:49:57 | NEC MW Observing High BER at BSH0084-3(10.199.24.68) | 10/22/2025 04:27:32 | Minor |  | LOF | 10/22/2025 04:27:32 | P1 | 2G | baish | Sceco_STB | TX NSA | BSH0084-3(10.199.24.68) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:57 | 10/26/2025 20:21:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000693 | PCM-20251026-00001454 | TT-20251026-01425 | Reference_telecom | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 14:49:58 | 10/26/2025 15:09:08 | 10/27/2025 02:49:58 | NEC MW Observing Low BER at DMH0104_1(10.159.105.137) | 10/24/2025 23:59:23 | Minor |  | LOF | 10/24/2025 23:59:23 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104_1(10.159.105.137) | FLM_TE | [8 empty] | API | 10/26/2025 14:49:58 | 10/26/2025 15:09:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000694 | PCM-20251026-00001455 | TT-20251026-01426 | Reference_telecom | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 14:50:05 | 10/26/2025 15:09:08 | 10/27/2025 02:50:05 | NEC MW Observing Low BER at DMH0104-DMH0606(10.159.105.139) | 10/24/2025 23:52:10 | Minor |  | LOF | 10/24/2025 23:52:10 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104-DMH0606(10.159.105.139) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:05 | 10/26/2025 15:09:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000695 | PCM-20251026-00001456 | TT-20251026-01427 | Reference_telecom | Region_1 | DMH0606 | DMH0606 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 14:50:06 | 10/26/2025 15:09:09 | 10/27/2025 02:50:06 | NEC MW Observing High BER at DMH0606-1(10.159.105.140) | 10/24/2025 23:58:59 | Minor |  | LOF | 10/24/2025 23:58:59 | P1 | SRAN | hafr | Generator_SG | TX NSA | DMH0606-1(10.159.105.140) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:06 | 10/26/2025 15:09:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000696 | PCM-20251026-00001457 | TT-20251026-01428 | Reference_telecom | Region_1 | DMJR0173 | DMJR0173 |  |  |  | Muhammad Zubair Guilzar | 10/26/2025 14:50:07 | 10/26/2025 21:42:19 | 10/27/2025 02:50:07 | NEC MW Observing High BER at DMJR0173-1(10.76.116.78) | 10/24/2025 20:56:27 | Minor |  | LOF | 10/24/2025 20:56:27 | P1 | SRAN | arar | Generator_DG | TX NSA | DMJR0173-1(10.76.116.78) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:07 | 10/26/2025 21:42:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000697 | PCM-20251026-00001458 | TT-20251026-01429 | Reference_telecom | Region_1 | JBL2109 | JBL2109 |  |  |  | Rafiq Ahmed Elturifi | 10/26/2025 14:50:08 | 10/26/2025 16:09:45 | 10/27/2025 02:50:08 | NEC MW Observing High BER at JBL2109-1(10.21.217.58) | 10/20/2025 13:46:31 | Minor |  | LOF | 10/20/2025 13:46:31 | P3 | SRAN | jubail | Generator_DG | TX NSA | JBL2109-1(10.21.217.58) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:08 | 10/26/2025 16:09:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000698 | PCM-20251026-00001459 | TT-20251026-01430 | Reference_telecom | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 14:50:10 | 10/26/2025 17:04:49 | 10/27/2025 02:50:10 | NEC MW Observing High BER at JDJZ0785(10.154.164.49) | 10/22/2025 04:15:00 | Minor |  | LOF | 10/22/2025 04:15:00 | P1 | 2G | derb | Sceco_STB | TX NSA | JDJZ0785(10.154.164.49) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:10 | 10/26/2025 17:04:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000699 | PCM-20251026-00001460 | TT-20251026-01431 | Reference_telecom | Region_3 | YBDB0293 | YBDB0293 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 14:50:11 | 10/26/2025 16:50:47 | 10/27/2025 02:50:11 | NEC MW Observing High BER,LOF,Frame ID,Low BER at YBDB0293(10.159.108.230) | 10/19/2025 21:37:20 | Minor |  | LOF | 10/19/2025 21:37:20 | P1 | SRAN | tabouk | Generator_DG | TX NSA | YBDB0293(10.159.108.230) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:11 | 10/26/2025 16:50:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000700 | PCM-20251026-00001461 | TT-20251026-01432 | Reference_telecom | Region_5 | MKMD0552 | MKMD0552 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 14:50:12 | 10/26/2025 14:50:12 | 10/27/2025 02:50:12 | NEC MW Observing High BER at MKMD0552-1(10.154.143.194) | 10/25/2025 23:06:16 | Minor |  | LOF | 10/25/2025 23:06:16 | P3 | 2G | makkah | Generator_SG | TX NSA | MKMD0552-1(10.154.143.194) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000701 | PCM-20251026-00001462 | TT-20251026-01433 | Reference_telecom | Region_4 | QAL0721 | QAL0721 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 14:50:13 | 10/26/2025 21:19:26 | 10/27/2025 02:50:13 | NEC MW Observing High BER,High BER at QAL0721-2(10.88.222.20) | 10/20/2025 16:57:57 | Minor |  | LOF | 10/20/2025 16:57:57 | P1 | 2G | qunfuddah | Sceco | TX NSA | QAL0721-2(10.88.222.20) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:13 | 10/26/2025 21:19:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000702 | PCM-20251026-00001463 | TT-20251026-01434 | Reference_telecom | Region_6 | RYAB0614 | RYAB0614 |  |  |  | Saif Muhammad | 10/26/2025 14:50:14 | 10/26/2025 15:45:21 | 10/27/2025 02:50:14 | NEC MW Observing Low BER at RYAB0614_1(10.199.24.3) | 10/22/2025 04:01:51 | Minor |  | LOF | 10/22/2025 04:01:51 | P3 | 2G | sulail | Sceco | TX NSA | RYAB0614_1(10.199.24.3) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:14 | 10/26/2025 15:45:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000703 | PCM-20251026-00001464 | TT-20251026-01435 | Reference_telecom | Region_4 | RAB0473 | RAB0473 |  |  |  | Khizer Hayat | 10/26/2025 14:50:15 | 10/26/2025 22:28:17 | 10/27/2025 02:50:15 | NEC MW Observing Low BER at RAB0473-5(10.154.114.49) | 10/24/2025 17:08:43 | Minor |  | LOF | 10/24/2025 17:08:43 | P1 | 2G | jeddah | Sceco | TX NSA | RAB0473-5(10.154.114.49) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:15 | 10/26/2025 22:28:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000704 | PCM-20251026-00001465 | TT-20251026-01436 | Reference_telecom | Region_6 | RYAB0640 | RYAB0640 |  |  |  | Muhammad Afzal Muhammad Aslam | 10/26/2025 14:50:16 | 10/26/2025 15:56:12 | 10/27/2025 02:50:16 | NEC MW Observing Low BER at RYAB0640(10.89.220.244) | 10/25/2025 15:59:05 | Minor |  | LOF | 10/25/2025 15:59:05 | P2 | 2G | tathleeth | Sceco | TX NSA | RYAB0640(10.89.220.244) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:16 | 10/26/2025 15:56:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000705 | PCM-20251026-00001466 | TT-20251026-01437 | Reference_telecom | Region_6 | RYNJ0200 | RYNJ0200 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Saif Muhammad | 10/26/2025 14:50:18 | 10/26/2025 16:20:52 | 10/27/2025 02:50:18 | NEC MW Observing Low BER,Low BER at RYNJ0200(10.157.250.51) | 10/22/2025 04:29:25 | Minor |  | LOF | 10/22/2025 04:29:25 | P1 | 2G | wadi dawasar | Generator_DG | TX NSA | RYNJ0200(10.157.250.51) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:18 | 10/26/2025 15:45:21 | 10/26/2025 15:48:22 | 10/26/2025 15:48:27 | 10/26/2025 15:49:00 | 10/26/2025 16:20:52 |  | Saif Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000706 | PCM-20251026-00001467 | TT-20251026-01438 | Reference_telecom | Region_6 | RYNJ0204 | RYNJ0204 |  |  |  | Saif Muhammad | 10/26/2025 14:50:19 | 10/26/2025 15:45:22 | 10/27/2025 02:50:19 | NEC MW Observing Low BER,Low BER at RYNJ0204(10.157.250.58) | 10/22/2025 04:17:30 | Minor |  | LOF | 10/22/2025 04:17:30 | P1 | 2G | wadi dawasar | Generator_DG | TX NSA | RYNJ0204(10.157.250.58) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:19 | 10/26/2025 15:45:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000707 | PCM-20251026-00001469 | TT-20251026-01440 | Reference_telecom | Region_1 | SKQR0507 | SKQR0507 |  |  |  | Syed Fawad Ali | 10/26/2025 14:50:20 | 10/26/2025 19:05:16 | 10/27/2025 02:50:20 | NEC MW Observing High BER at SKQR0507(10.76.110.243) | 10/20/2025 13:52:57 | Minor |  | LOF | 10/20/2025 13:52:57 | P3 | SRAN | sakaka | Power Cube | TX NSA | SKQR0507(10.76.110.243) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:20 | 10/26/2025 19:05:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000708 | PCM-20251026-00001470 | TT-20251026-01441 | Reference_telecom | Region_1 | UQR2313 | UQR2313 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:50:22 | 10/26/2025 17:46:16 | 10/27/2025 02:50:22 | NEC MW Observing High BER at UQR2313(10.74.84.138) | 10/24/2025 12:38:35 | Minor |  | LOF | 10/24/2025 12:38:35 | P3 | SRAN | dammam | Sceco | TX NSA | UQR2313(10.74.84.138) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:22 | 10/26/2025 17:46:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000709 | PCM-20251026-00001471 | TT-20251026-01442 | Reference_telecom | Region_6 | WDS0230 | WDS0230 |  |  |  | Ahmed Mamdouh Helal Helal | 10/26/2025 14:50:22 | 10/26/2025 16:07:32 | 10/27/2025 02:50:22 | NEC MW Observing High BER at WDS0230(10.1.171.243) | 10/22/2025 01:06:39 | Minor |  | LOF | 10/22/2025 01:06:39 | P2 | 2G | wadi dawasar | Sceco | TX NSA | WDS0230(10.1.171.243) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:22 | 10/26/2025 16:07:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000710 | PCM-20251026-00001472 | TT-20251026-01443 | Reference_telecom | Region_6 | TLT0743 | TLT0743 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/26/2025 14:50:23 | 10/26/2025 17:10:25 | 10/27/2025 02:50:23 | NEC MW Observing LOF,RX Level,LOF,LOF,LOF,RX Level,RX Level,Radio Traffic Aggregation Link,LOF,RX Level,RX Level at TLT0743(10.89.224.33) | 10/25/2025 15:12:45 | Minor |  | LOF | 10/25/2025 15:12:45 | P1 | 2G | tathleeth | Sceco_STB | TX NSA | TLT0743(10.89.224.33) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:23 | 10/26/2025 15:56:13 | 10/26/2025 16:24:27 | 10/26/2025 16:24:30 | 10/26/2025 16:24:33 | 10/26/2025 17:10:25 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000711 | PCM-20251026-00001473 | TT-20251026-01444 | Reference_telecom | Region_6 | BHAB0820 | BHAB0820 |  |  |  | SHAH KHALID | 10/26/2025 14:50:25 | 10/26/2025 17:41:04 | 10/27/2025 02:50:25 | NEC MW Observing Power Supply,LOF,RX Level at BHAB0820(10.1.174.36) | 10/21/2025 23:35:03 | Minor |  | LOF | 10/21/2025 23:35:03 | P3 | 2G | makhwa | Sceco | TX NSA | BHAB0820(10.1.174.36) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:25 | 10/26/2025 17:41:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000712 | PCM-20251026-00001474 | TT-20251026-01445 | Reference_telecom | Region_1 | HFF0933 | HFF0933 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 14:50:26 | 10/26/2025 18:32:47 | 10/27/2025 02:50:26 | NEC MW Observing LOF,RX Level at HFF0933(10.74.80.154) | 10/20/2025 11:59:07 | Minor |  | LOF | 10/20/2025 11:59:07 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF0933(10.74.80.154) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:26 | 10/26/2025 18:32:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000713 | PCM-20251026-00001475 | TT-20251026-01446 | Reference_telecom | Region_3 | MDTB0328 | MDTB0328 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 14:50:27 | 10/26/2025 19:31:37 | 10/27/2025 02:50:27 | NEC MW Observing LOF,RX Level at MDTB0328-MDTB0327(10.253.1.226) | 09/24/2025 08:43:38 | Minor |  | LOF | 09/24/2025 08:43:38 | P1 | SRAN | madinah | Sceco_STB | TX NSA | MDTB0328-MDTB0327(10.253.1.226) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:27 | 10/26/2025 19:31:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000714 | PCM-20251026-00001476 | TT-20251026-01447 | Reference_telecom | Region_1 | SKA0184 | SKA0184 |  |  |  | Muhammad Zubair Guilzar | 10/26/2025 14:50:28 | 10/26/2025 21:42:20 | 10/27/2025 02:50:28 | NEC MW Observing LOF,RX Level at SKA0184-Access(10.74.86.36) | 10/21/2025 03:26:17 | Minor |  | LOF | 10/21/2025 03:26:17 | P2 | SRAN | arar | Sceco | TX NSA | SKA0184-Access(10.74.86.36) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:28 | 10/26/2025 21:42:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000715 | PCM-20251026-00001477 | TT-20251026-01448 | Reference_telecom | Region_1 | ABQ2889 | ABQ2889 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:50:29 | 10/26/2025 17:46:16 | 10/27/2025 02:50:29 | NEC MW Observing LOF,Frame ID at ABQ2889(10.76.109.92) | 10/20/2025 13:50:38 | Minor |  | LOF | 10/20/2025 13:50:38 | P2 | SRAN | dammam | Sceco | TX NSA | ABQ2889(10.76.109.92) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:29 | 10/26/2025 17:46:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000716 | PCM-20251026-00001478 | TT-20251026-01449 | Reference_telecom | Region_6 | AHM0027 | AHM0027 |  |  |  | Zeshan Ali Adnan | 10/26/2025 14:50:31 | 10/26/2025 15:53:33 | 10/27/2025 02:50:31 | NEC MW Observing FAN FAIL at AHM0027(10.1.172.120) | 10/18/2025 18:23:34 | Minor |  | LOF | 10/18/2025 18:23:34 | P3 | 2G | jizan | Sceco | TX NSA | AHM0027(10.1.172.120) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:31 | 10/26/2025 15:53:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000717 | PCM-20251026-00001479 | TT-20251026-01450 | Reference_telecom | Region_1 | ARM0873 | ARM0873 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:50:32 | 10/26/2025 17:46:16 | 10/27/2025 02:50:32 | NEC MW Observing RX Level,RX Level,Frame ID,LOF,LOF,LOF,Frame ID,Frame ID at ARM0873(10.21.217.172) | 10/20/2025 13:54:02 | Minor |  | LOF | 10/20/2025 13:54:02 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0873(10.21.217.172) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:32 | 10/26/2025 17:46:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000718 | PCM-20251026-00001480 | TT-20251026-01451 | Reference_telecom | Region_1 | ARR9805 | ARR9805 |  |  |  | Almmoez Almmoez | 10/26/2025 14:50:33 | 10/27/2025 00:00:35 | 10/27/2025 02:50:33 | NEC MW Observing ODU CPU/CABLE OPEN(No.1) at ARR9805-ARR3M1908(10.248.39.67) | 10/24/2025 15:34:06 | Minor |  | LOF | 10/24/2025 15:34:06 | P3 | Repeater | rafha | Generator_DG | TX NSA | ARR9805-ARR3M1908(10.248.39.67) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:33 | 10/27/2025 00:00:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000719 | PCM-20251026-00001481 | TT-20251026-01452 | Reference_telecom | Region_1 | ARR9811 | ARR9811 |  |  |  | Almmoez Almmoez | 10/26/2025 14:50:34 | 10/27/2025 00:00:36 | 10/27/2025 02:50:34 | NEC MW Observing ODU CPU/CABLE OPEN(No.1) at ARR9811-2(10.76.118.43) | 10/24/2025 14:54:47 | Minor |  | LOF | 10/24/2025 14:54:47 | P3 | Repeater | rafha | Generator_SG | TX NSA | ARR9811-2(10.76.118.43) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:34 | 10/27/2025 00:00:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000720 | PCM-20251026-00001482 | TT-20251026-01453 | Reference_telecom | Region_6 | ARS0126 | ARS0126 |  |  |  | Zeshan Ali Adnan | 10/26/2025 14:50:35 | 10/26/2025 15:53:34 | 10/27/2025 02:50:35 | NEC MW Observing ODU CPU / Cable Open,LOF at ARS0126(10.1.174.50) | 10/21/2025 12:13:38 | Minor |  | LOF | 10/21/2025 12:13:38 | P2 | 2G | jizan | Sceco | TX NSA | ARS0126(10.1.174.50) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:35 | 10/26/2025 15:53:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000721 | PCM-20251026-00001483 | TT-20251026-01454 | Reference_telecom | Region_6 | ARS0161 | ARS0161 |  |  |  | Zeshan Ali Adnan | 10/26/2025 14:50:36 | 10/26/2025 15:53:34 | 10/27/2025 02:50:36 | NEC MW Observing XIF,MODEM Power Supply Alarm,MODEM Power Supply Alarm at ARS0161-1(10.154.175.150) | 10/17/2025 17:48:00 | Minor |  | LOF | 10/17/2025 17:48:00 | P2 | 2G | jizan | Sceco | TX NSA | ARS0161-1(10.154.175.150) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:36 | 10/26/2025 15:53:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000722 | PCM-20251026-00001484 | TT-20251026-01455 | Reference_telecom | Region_1 | DAM0295 | DAM0295 | Transsmission | MW_HW_fault | Replace FAN | Shakeel Ahmed Hafeez Ameen | 10/26/2025 14:50:38 | 10/26/2025 17:28:03 | 10/27/2025 02:50:38 | NEC MW Observing FAN FAIL at DAM0295(10.1.218.58) | 10/19/2025 15:12:47 | Minor |  | LOF | 10/19/2025 15:12:47 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0295(10.1.218.58) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:38 | 10/26/2025 15:01:07 | 10/26/2025 17:27:42 |  |  | 10/26/2025 17:28:03 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000723 | PCM-20251026-00001485 | TT-20251026-01456 | Reference_telecom | Region_1 | DMH0105 | DMH0105 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 14:50:39 | 10/26/2025 15:09:10 | 10/27/2025 02:50:39 | NEC MW Observing LOF,LOF at DMH0105-DMH0104(10.159.105.100) | 10/24/2025 23:54:48 | Minor |  | LOF | 10/24/2025 23:54:48 | P1 | SRAN | hafr | Generator_SG | TX NSA | DMH0105-DMH0104(10.159.105.100) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:39 | 10/26/2025 15:09:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000724 | PCM-20251026-00001486 | TT-20251026-01457 | Reference_telecom | Region_1 | DMJR0155 | DMJR0155 |  |  |  | Muhammad Zubair Guilzar | 10/26/2025 14:50:39 | 10/26/2025 21:42:21 | 10/27/2025 02:50:39 | NEC MW Observing LOF at DMJR0155-3(10.76.111.79) | 10/24/2025 23:49:14 | Minor |  | LOF | 10/24/2025 23:49:14 | P1 | SRAN | arar | Sceco_STB | TX NSA | DMJR0155-3(10.76.111.79) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:39 | 10/26/2025 21:42:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000725 | PCM-20251026-00001487 | TT-20251026-01458 | Reference_telecom | Region_6 | FUR0050 | FUR0050 |  |  |  | Mohammed Sideag Mohammed Ali | 10/26/2025 14:50:41 | 10/26/2025 16:53:37 | 10/27/2025 02:50:41 | NEC MW Observing ODU CPU / Cable Open,LOF at FUR0050-3(10.1.172.199) | 10/22/2025 02:53:47 | Minor |  | LOF | 10/22/2025 02:53:47 | P3 | 2G | jizan | Sceco_STB | TX NSA | FUR0050-3(10.1.172.199) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:41 | 10/26/2025 16:53:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20251026000727 | PCM-20251026-00001489 | TT-20251026-01460 | Reference_telecom | Region_1 | JBKH0146 | JBKH0146 |  |  |  | Mohamed Abdelaziz | 10/26/2025 14:50:43 | 10/26/2025 23:32:42 | 10/27/2025 02:50:43 | NEC MW Observing Power Supply at JBKH0146(10.159.106.227) | 10/24/2025 14:48:56 | Minor |  | LOF | 10/24/2025 14:48:56 | P2 | SRAN | khafji | Generator_SG | TX NSA | JBKH0146(10.159.106.227) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:43 | 10/26/2025 16:54:24 | 10/26/2025 22:11:55 | 10/26/2025 22:11:58 | 10/26/2025 22:31:24 | 10/26/2025 23:32:42 |  | Mohamed Abdelaziz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000728 | PCM-20251026-00001490 | TT-20251026-01461 | Reference_telecom | Region_4 | JDJZ0764 | JDJZ0764 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 14:50:44 | 10/26/2025 21:19:27 | 10/27/2025 02:50:44 | NEC MW Observing ETH LOS,LAN Link,High BER,LOF,Frame ID at JDJZ0764-1(10.154.140.69) | 10/20/2025 16:50:00 | Minor |  | LOF | 10/20/2025 16:50:00 | P2 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0764-1(10.154.140.69) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:44 | 10/26/2025 21:19:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000729 | PCM-20251026-00001491 | TT-20251026-01462 | Reference_telecom | Region_4 | JDJZ0765 | JDJZ0765 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 14:50:45 | 10/26/2025 21:19:28 | 10/27/2025 02:50:45 | NEC MW Observing Frame ID,LOF at JDJZ0765-1(10.154.140.83) | 10/24/2025 04:35:21 | Minor |  | LOF | 10/24/2025 04:35:21 | P2 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0765-1(10.154.140.83) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:45 | 10/26/2025 21:19:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000730 | PCM-20251026-00001492 | TT-20251026-01463 | Reference_telecom | Region_4 | JDJZ0768 | JDJZ0768 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 14:50:46 | 10/26/2025 21:19:28 | 10/27/2025 02:50:46 | NEC MW Observing SBY TX Bus Error at JDJZ0768_1(10.88.222.23) | 10/20/2025 16:59:49 | Minor |  | LOF | 10/20/2025 16:59:49 | P1 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0768_1(10.88.222.23) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:46 | 10/26/2025 21:19:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000731 | PCM-20251026-00001493 | TT-20251026-01464 | Reference_telecom | Region_6 | JDSM0791 | JDSM0791 |  |  |  | Zeshan Ali Adnan | 10/26/2025 14:50:48 | 10/26/2025 15:53:35 | 10/27/2025 02:50:48 | NEC MW Observing LOF,RX Level,LOF,RX Level,Low BER at JDSM0791(10.157.253.139) | 10/22/2025 04:29:36 | Minor |  | LOF | 10/22/2025 04:29:36 | P1 | 2G | jizan | Sceco_STB | TX NSA | JDSM0791(10.157.253.139) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:48 | 10/26/2025 15:53:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000732 | PCM-20251026-00001494 | TT-20251026-01465 | Reference_telecom | Region_6 | JEC0090 | JEC0090 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/26/2025 14:50:48 | 10/26/2025 20:21:15 | 10/27/2025 02:50:48 | NEC MW Observing Low BER at JEC0090-2(10.199.24.84) | 10/22/2025 04:30:36 | Minor |  | LOF | 10/22/2025 04:30:36 | VIP | 2G | baish | Sceco_STB | TX NSA | JEC0090-2(10.199.24.84) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:48 | 10/26/2025 20:21:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000733 | PCM-20251026-00001495 | TT-20251026-01466 | Reference_telecom | Region_4 | JED0359 | JED0359 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 14:50:49 | 10/26/2025 14:50:49 | 10/27/2025 02:50:49 | NEC MW Observing LOF,RX Level,Frame ID at JED0359-A1(10.99.254.105) | 10/24/2025 17:18:25 | Minor |  | LOF | 10/24/2025 17:18:25 | P1 | 2G | jeddah | Sceco | TX NSA | JED0359-A1(10.99.254.105) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000734 | PCM-20251026-00001496 | TT-20251026-01467 | Reference_telecom | Region_4 | JED6132 | JED6132 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 14:50:51 | 10/26/2025 14:50:51 | 10/27/2025 02:50:51 | NEC MW Observing LAN Link,LAN Link at JED6132(10.154.126.23) | 10/20/2025 11:15:56 | Minor |  | LOF | 10/20/2025 11:15:56 | P3 | 2G | jeddah | Sceco | TX NSA | JED6132(10.154.126.23) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000735 | PCM-20251026-00001497 | TT-20251026-01468 | Reference_telecom | Region_1 | KFKM0781 | KFKM0781 |  |  |  | Mohamed Abdelaziz | 10/26/2025 14:50:52 | 10/26/2025 16:54:24 | 10/27/2025 02:50:52 | NEC MW Observing High BER,High BER at KFKM0781(10.76.118.73) | 10/24/2025 23:54:17 | Minor |  | LOF | 10/24/2025 23:54:17 | P3 | SRAN | khafji | Generator_SG | TX NSA | KFKM0781(10.76.118.73) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:52 | 10/26/2025 16:54:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000736 | PCM-20251026-00001498 | TT-20251026-01469 | Reference_telecom | Region_1 | KKM2171 | KKM2171 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 14:50:53 | 10/26/2025 15:09:10 | 10/27/2025 02:50:53 | NEC MW Observing TX Bus Error at KKM2171(10.147.11.206) | 10/24/2025 14:59:08 | Minor |  | LOF | 10/24/2025 14:59:08 | P3 | SRAN | hafr | Sceco | TX NSA | KKM2171(10.147.11.206) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:53 | 10/26/2025 15:09:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000737 | PCM-20251026-00001499 | TT-20251026-01470 | Reference_telecom | Region_4 | KMMD9076 | KMMD9076 |  |  |  | Nazeer Mohammed | 10/26/2025 14:50:54 | 10/26/2025 15:23:09 | 10/27/2025 02:50:54 | NEC MW Observing Communication FAIL at KMMD9076(10.154.115.85) | 10/24/2025 17:19:56 | Minor |  | LOF | 10/24/2025 17:19:56 | P1 | Repeater | jeddah | Sceco | TX NSA | KMMD9076(10.154.115.85) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:54 | 10/26/2025 15:23:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000738 | PCM-20251026-00001500 | TT-20251026-01471 | Reference_telecom | Region_3 | MDHL0379 | MDHL0379 |  |  |  | Mohamed Naveed | 10/26/2025 14:50:56 | 10/26/2025 15:18:40 | 10/27/2025 02:50:56 | NEC MW Observing LOF,LOF,LOF,Frame ID,Frame ID,Frame ID,High BER at MDHL0379-MDHL0380(10.253.0.133) | 10/19/2025 21:31:48 | Minor |  | LOF | 10/19/2025 21:31:48 | P1 | SRAN | hail | Sceco_STB | TX NSA | MDHL0379-MDHL0380(10.253.0.133) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:56 | 10/26/2025 15:18:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000739 | PCM-20251026-00001501 | TT-20251026-01472 | Reference_telecom | Region_5 | MDQ0392 | MDQ0392 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/26/2025 14:50:57 | 10/26/2025 14:50:57 | 10/27/2025 02:50:57 | NEC MW Observing IF Cable Short at MDQ0392-1(10.88.220.83) | 10/19/2025 00:27:27 | Minor |  | LOF | 10/19/2025 00:27:27 | P2 | 2G | makkah | Generator_DG | TX NSA | MDQ0392-1(10.88.220.83) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000740 | PCM-20251026-00001502 | TT-20251026-01473 | Reference_telecom | Region_3 | MDTB0327 | MDTB0327 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 14:50:58 | 10/26/2025 19:31:37 | 10/27/2025 02:50:58 | NEC MW Observing ODU CPU / Cable Open,LOF at MDTB0327-MDTB0328(10.253.1.227) | 09/24/2025 08:45:04 | Minor |  | LOF | 09/24/2025 08:45:04 | P1 | SRAN | madinah | Sceco | TX NSA | MDTB0327-MDTB0328(10.253.1.227) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:58 | 10/26/2025 19:31:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000741 | PCM-20251026-00001503 | TT-20251026-01474 | Reference_telecom | Region_3 | MDTB0328 | MDTB0328 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 14:50:59 | 10/26/2025 19:31:38 | 10/27/2025 02:50:59 | NEC MW Observing Radio Traffic Aggregation Link at MDTB0328-MDTB0610(10.253.1.228) | 08/24/2025 09:52:40 | Minor |  | LOF | 08/24/2025 09:52:40 | P1 | SRAN | madinah | Sceco_STB | TX NSA | MDTB0328-MDTB0610(10.253.1.228) | FLM_TE | [8 empty] | API | 10/26/2025 14:50:59 | 10/26/2025 19:31:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000742 | PCM-20251026-00001504 | TT-20251026-01475 | Reference_telecom | Region_3 | MDTB0348 | MDTB0348 |  |  |  | Tahir Abbas Fateh Khan | 10/26/2025 14:51:00 | 10/26/2025 16:47:13 | 10/27/2025 02:51:00 | NEC MW Observing LOF,Frame ID,LOF,Frame ID,LOF,Frame ID,LOF,Frame ID,High BER,High BER,LOF at MDTB0348-MDTB0343(10.154.66.107) | 10/19/2025 21:29:38 | Minor |  | LOF | 10/19/2025 21:29:38 | P1 | SRAN | tabouk | Sceco_STB | TX NSA | MDTB0348-MDTB0343(10.154.66.107) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:00 | 10/26/2025 16:47:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000743 | PCM-20251026-00001505 | TT-20251026-01476 | Reference_telecom | Region_6 | MHL0133 | MHL0133 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/26/2025 14:51:02 | 10/26/2025 17:50:16 | 10/27/2025 02:51:02 | NEC MW Observing IF Cable Short at MHL0133(10.154.171.230) | 10/21/2025 02:39:41 | Minor |  | LOF | 10/21/2025 02:39:41 | P3 | 2G | mohail | Sceco | TX NSA | MHL0133(10.154.171.230) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:02 | 10/26/2025 17:50:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000744 | PCM-20251026-00001506 | TT-20251026-01477 | Reference_telecom | Region_6 | MHL0182 | MHL0182 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/26/2025 14:51:03 | 10/26/2025 17:50:17 | 10/27/2025 02:51:03 | NEC MW Observing LOF,RX Level,Frame ID at MHL0182(10.157.250.24) | 10/22/2025 04:35:42 | Minor |  | LOF | 10/22/2025 04:35:42 | P3 | 2G | mohail | Generator_SG | TX NSA | MHL0182(10.157.250.24) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:03 | 10/26/2025 17:50:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000745 | PCM-20251026-00001507 | TT-20251026-01478 | Reference_telecom | Region_4 | MLJI0186 | MLJI0186 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 14:51:05 | 10/26/2025 16:57:25 | 10/27/2025 02:51:05 | NEC MW Observing RX Level,LOF at MLJI0186-2(10.88.223.147) | 10/22/2025 10:53:06 | Minor |  | LOF | 10/22/2025 10:53:06 | P2 | 2G | alaith | Generator_DG | TX NSA | MLJI0186-2(10.88.223.147) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:05 | 10/26/2025 16:57:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000746 | PCM-20251026-00001508 | TT-20251026-01479 | Reference_telecom | Region_6 | QFL0037 | QFL0037 |  |  |  | Osama Hadi | 10/26/2025 14:51:06 | 10/26/2025 22:04:41 | 10/27/2025 02:51:06 | NEC MW Observing Power Supply at QFL0037(10.157.253.196) | 10/21/2025 02:41:30 | Minor |  | LOF | 10/21/2025 02:41:30 | P2 | 2G | jizan | Sceco | TX NSA | QFL0037(10.157.253.196) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:06 | 10/26/2025 22:04:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000747 | PCM-20251026-00001509 | TT-20251026-01480 | Reference_telecom | Region_1 | RAF9808 | RAF9808 |  |  |  | Almmoez Almmoez | 10/26/2025 14:51:07 | 10/27/2025 00:00:37 | 10/27/2025 02:51:07 | NEC MW Observing ODU CPU/CABLE OPEN(No.1) at RAF9808-2(10.76.117.158) | 10/24/2025 15:02:06 | Minor |  | LOF | 10/24/2025 15:02:06 | P3 | Repeater | rafha | Generator_DG | TX NSA | RAF9808-2(10.76.117.158) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:07 | 10/27/2025 00:00:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000748 | PCM-20251026-00001510 | TT-20251026-01481 | Reference_telecom | Region_1 | SAK9810 | SAK9810 |  |  |  | Syed Fawad Ali | 10/26/2025 14:51:08 | 10/26/2025 19:05:19 | 10/27/2025 02:51:08 | NEC MW Observing ODU CPU/CABLE OPEN at SAK9810-EAS(10.76.107.68) | 10/24/2025 15:38:06 | Minor |  | LOF | 10/24/2025 15:38:06 | P3 | Repeater | sakaka | Generator_DG | TX NSA | SAK9810-EAS(10.76.107.68) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:08 | 10/26/2025 19:05:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000749 | PCM-20251026-00001511 | TT-20251026-01482 | Reference_telecom | Region_6 | SHQ0183 | SHQ0183 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 14:51:09 | 10/26/2025 18:36:11 | 10/27/2025 02:51:09 | NEC MW Observing LOF at SHQ0183(10.154.170.163) | 10/21/2025 16:25:29 | Minor |  | LOF | 10/21/2025 16:25:29 | P3 | 2G | derb | Sceco | TX NSA | SHQ0183(10.154.170.163) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:09 | 10/26/2025 17:04:50 | 10/26/2025 18:36:03 |  |  | 10/26/2025 18:36:11 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000750 | PCM-20251026-00001512 | TT-20251026-01483 | Reference_telecom | Region_3 | YBDB0290 | YBDB0290 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 14:51:10 | 10/26/2025 14:51:10 | 10/27/2025 02:51:10 | NEC MW Observing High BER,High BER,LOF,Frame ID,LOF,Frame ID,Low BER,High BER at YBDB0290(10.159.108.212) | 10/19/2025 21:38:14 | Minor |  | LOF | 10/19/2025 21:38:14 | P1 | SRAN | yanbu | Generator_DG | TX NSA | YBDB0290(10.159.108.212) | FLM_TE | [8 empty] | API | 10/26/2025 14:51:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000751 | PCM-20251026-00001513 | TT-20251026-01484 | Reference_telecom | Region_6 | ABBS0151 | ABBS0151 |  |  |  | Manzoor Ahmed | 10/26/2025 14:51:12 | 10/26/2025 14:54:44 | 10/27/2025 02:51:12 | Nokia Eband Observing InternalCommunicationProblem-Port 8/3,ReplaceableU at ABBS0151-10.221.244.246 | 10/19/2025 19:41:58 | Minor |  | LOF | 10/19/2025 19:41:58 | P3 | 2G | Albaha | Generator_SG | TX NSA | ABBS0151-10.221.244.246 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:12 | 10/26/2025 14:54:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000752 | PCM-20251026-00001514 | TT-20251026-01485 | Reference_telecom | Region_6 | ABBS2189 | ABBS2189 |  |  |  | SHAH KHALID | 10/26/2025 14:51:12 | 10/26/2025 17:41:05 | 10/27/2025 02:51:12 | Nokia Eband Observing LossOfSignal-Port 7/3,InternalCommunicationProblem at ABBS2189_01-10.221.243.227 | 09/17/2025 23:26:53 | Minor |  | LOF | 09/17/2025 23:26:53 | P3 | 2G | Albaha | Generator_SG | TX NSA | ABBS2189_01-10.221.243.227 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:12 | 10/26/2025 17:41:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000753 | PCM-20251026-00001515 | TT-20251026-01486 | Reference_telecom | Region_6 | ABH0162 | ABH0162 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 14:51:14 | 10/26/2025 15:02:41 | 10/27/2025 02:51:14 | Nokia Eband Observing InternalCommunicationProblem-Port 7/3,BandwidthDeg at ABH0162_03-10.10.155.44 | 10/23/2025 20:56:24 | Minor |  | LOF | 10/23/2025 20:56:24 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0162_03-10.10.155.44 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:14 | 10/26/2025 15:02:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000754 | PCM-20251026-00001516 | TT-20251026-01487 | Reference_telecom | Region_6 | ABSD0704 | ABSD0704 | Transsmission | MW_HW_fault | Replace FAN | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 14:51:15 | 10/26/2025 15:03:33 | 10/27/2025 02:51:15 | Nokia Eband Observing HouseKeeping-auxIn-14,HouseKeeping-auxIn-13,HouseK at ABSD0704 _03-10.10.158.93 | 09/27/2025 08:57:46 | Minor |  | LOF | 09/27/2025 08:57:46 | P3 | 2G | abha | Sceco | TX NSA | ABSD0704 _03-10.10.158.93 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:15 | 10/26/2025 15:02:42 | 10/26/2025 15:03:14 |  |  | 10/26/2025 15:03:33 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000755 | PCM-20251026-00001517 | TT-20251026-01488 | Reference_telecom | Region_6 | BHAB2005 | BHAB2005 |  |  |  | SHAH KHALID | 10/26/2025 14:51:16 | 10/26/2025 17:41:06 | 10/27/2025 02:51:16 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A,DemFail-Chan at BHAB2005_02-10.221.243.53 | 09/10/2025 15:26:48 | Minor |  | LOF | 09/10/2025 15:26:48 | P3 | 2G | Albaha | Sceco | TX NSA | BHAB2005_02-10.221.243.53 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:16 | 10/26/2025 17:41:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000756 | PCM-20251026-00001518 | TT-20251026-01489 | Reference_telecom | Region_6 | BHAB2052 | BHAB2052 |  |  |  | SHAH KHALID | 10/26/2025 14:51:17 | 10/26/2025 17:41:06 | 10/27/2025 02:51:17 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at BHAB2052_01-10.221.242.226 | 10/20/2025 01:39:18 | Minor |  | LOF | 10/20/2025 01:39:18 | P3 | 2G | Baha | Generator_SG | TX NSA | BHAB2052_01-10.221.242.226 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:17 | 10/26/2025 17:41:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000757 | PCM-20251026-00001519 | TT-20251026-01490 | Reference_telecom | Region_6 | BHAB2442 | BHAB2442 |  |  |  | SHAH KHALID | 10/26/2025 14:51:18 | 10/26/2025 17:41:07 | 10/27/2025 02:51:18 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at BHAB2442_01-10.221.243.54 | 10/19/2025 19:42:26 | Minor |  | LOF | 10/19/2025 19:42:26 | P3 | 2G | Albaha | Generator_SG | TX NSA | BHAB2442_01-10.221.243.54 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:18 | 10/26/2025 17:41:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000758 | PCM-20251026-00001520 | TT-20251026-01491 | Reference_telecom | Region_6 | BHAB9035 | BHAB9035 | Transsmission | CB_MW | Switch on CB on Rectifier | Fawad Khan | 10/26/2025 14:51:19 | 10/27/2025 00:29:13 | 10/27/2025 02:51:19 | Nokia Eband Observing SecondaryBatteryFail-BHAB9035 at BHAB9035-10.21.69.183 | 08/27/2025 12:48:45 | Minor |  | LOF | 08/27/2025 12:48:45 | P1 | Repeater | namas | Sceco_STB | TX NSA | BHAB9035-10.21.69.183 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:19 | 10/26/2025 18:29:48 | 10/27/2025 00:28:14 |  |  | 10/27/2025 00:29:13 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000759 | PCM-20251026-00001521 | TT-20251026-01492 | Reference_telecom | Region_6 | BHAB9036 | BHAB9036 |  |  |  | Fawad Khan | 10/26/2025 14:51:20 | 10/26/2025 18:29:49 | 10/27/2025 02:51:20 | Nokia Eband Observing ReplaceableUnitProblem-Port 3/2,ReplaceableUnitPro at BHAB9036_09-10.221.243.193 | 10/19/2025 16:48:24 | Minor |  | LOF | 10/19/2025 16:48:24 | P1 | Repeater | namas | Sceco_STB | TX NSA | BHAB9036_09-10.221.243.193 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:20 | 10/26/2025 18:29:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000760 | PCM-20251026-00001522 | TT-20251026-01494 | Reference_telecom | Region_4 | HAW0300 | HAW0300 |  |  |  | Rashid Shafique | 10/26/2025 14:51:21 | 10/26/2025 14:53:28 | 10/27/2025 02:51:21 | Nokia Eband Observing LossOfSignal-Port 1/1 at HAW0300- 01-10.221.240.114 | 10/22/2025 13:48:02 | Minor |  | LOF | 10/22/2025 13:48:02 | P2 | 2G | taif | Generator_SG | TX NSA | HAW0300- 01-10.221.240.114 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:21 | 10/26/2025 14:53:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026000761 | PCM-20251026-00001523 | TT-20251026-01495 | Reference_telecom | Region_4 | JED0025 | JED0025 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 14:51:23 | 10/26/2025 18:17:04 | 10/27/2025 02:51:23 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JED0025-4-10.1.230.21 | 10/22/2025 14:19:54 | Minor |  | LOF | 10/22/2025 14:19:54 | P1 | 2G | jeddah | Sceco | TX NSA | JED0025-4-10.1.230.21 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:23 | 10/26/2025 14:51:32 | 10/26/2025 17:34:48 | 10/26/2025 17:34:50 | 10/26/2025 18:17:04 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000762 | PCM-20251026-00001524 | TT-20251026-01496 | Reference_telecom | Region_4 | JED0026 | JED0026 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 14:51:24 | 10/26/2025 14:51:24 | 10/27/2025 02:51:24 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JED0026-04-10.10.145.70 | 10/21/2025 12:15:24 | Minor |  | LOF | 10/21/2025 12:15:24 | P1 | 2G | jeddah | Sceco | TX NSA | JED0026-04-10.10.145.70 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000763 | PCM-20251026-00001525 | TT-20251026-01497 | Reference_telecom | Region_4 | JED0068 | JED0068 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 14:51:25 | 10/26/2025 14:51:25 | 10/27/2025 02:51:25 | Nokia Eband Observing LossOfSignal-Port 6/5 at JED0068-NE1-10.10.148.194 | 10/11/2025 16:10:59 | Minor |  | LOF | 10/11/2025 16:10:59 | P2 | 2G | jeddah | Sceco | TX NSA | JED0068-NE1-10.10.148.194 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000764 | PCM-20251026-00001526 | TT-20251026-01498 | Reference_telecom | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 14:51:26 | 10/26/2025 17:17:07 | 10/27/2025 02:51:26 | Nokia Eband Observing LossOfSignal-Port 4/5,DemFail-Port 4/5,LossOfSigna at JED0110-04-10.21.70.136 | 10/24/2025 17:23:40 | Minor |  | LOF | 10/24/2025 17:23:40 | VIP | 2G | jeddah | Sceco | TX NSA | JED0110-04-10.21.70.136 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:26 | 10/26/2025 17:17:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000765 | PCM-20251026-00001527 | TT-20251026-01499 | Reference_telecom | Region_4 | JED0125 | JED0125 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 14:51:27 | 10/26/2025 15:35:44 | 10/27/2025 02:51:27 | Nokia Eband Observing Degrade-LAG 1,DemFail-Port 4/5,LagPortDown-Port 4/ at JED0125-12-10.1.224.17 | 10/25/2025 16:11:41 | Minor |  | LOF | 10/25/2025 16:11:41 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED0125-12-10.1.224.17 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:27 | 10/26/2025 15:35:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000766 | PCM-20251026-00001528 | TT-20251026-01500 | Reference_telecom | Region_4 | JED0775 | JED0775 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 14:51:29 | 10/26/2025 14:51:29 | 10/27/2025 02:51:29 | Nokia Eband Observing DemFail-Port 3/5,LagPortDown-Port 3/5,Degrade-LAG at JED0775-02-10.1.229.216 | 10/25/2025 21:13:01 | Minor |  | LOF | 10/25/2025 21:13:01 | P2 | 2G | jeddah | Sceco | TX NSA | JED0775-02-10.1.229.216 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026000767 | PCM-20251026-00001529 | TT-20251026-01501 | Reference_telecom | Region_4 | JED2075 | JED2075 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 14:51:30 | 10/26/2025 14:59:34 | 10/27/2025 02:51:30 | Nokia Eband Observing InternalCommunicationProblem-Port 6/5,LossOfSignal at JED2075-FTK-10.10.180.214 | 10/25/2025 11:56:08 | Minor |  | LOF | 10/25/2025 11:56:08 | P3 | 2G | jeddah | Sceco | TX NSA | JED2075-FTK-10.10.180.214 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:30 | 10/26/2025 14:51:33 | 10/26/2025 14:51:38 | 10/26/2025 14:51:48 | 10/26/2025 14:59:34 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000768 | PCM-20251026-00001530 | TT-20251026-01502 | Reference_telecom | Region_4 | JED2129 | JED2129 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 14:51:31 | 10/26/2025 14:51:31 | 10/27/2025 02:51:31 | Nokia Eband Observing Degrade-LAG 1,LossOfSignal-Port 4/5,InternalCommun at JED2129-10.1.229.217 | 10/25/2025 21:38:54 | Minor |  | LOF | 10/25/2025 21:38:54 | P3 | 2G | jeddah | Sceco | TX NSA | JED2129-10.1.229.217 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000769 | PCM-20251026-00001531 | TT-20251026-01503 | Reference_telecom | Region_4 | JED2601 | JED2601 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 14:51:32 | 10/26/2025 14:55:46 | 10/27/2025 02:51:32 | Nokia Eband Observing DemFail-Port 4/5,Degrade-LAG 1,LagPortDown-Port 4/ at JED2601-10.3.232.164 | 10/25/2025 21:36:29 | Minor |  | LOF | 10/25/2025 21:36:29 | P3 | 2G | jeddah | Sceco | TX NSA | JED2601-10.3.232.164 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:32 | 10/26/2025 14:55:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000770 | PCM-20251026-00001532 | TT-20251026-01504 | Reference_telecom | Region_4 | JED2602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 14:51:33 | 10/26/2025 14:55:46 | 10/27/2025 02:51:33 | Nokia Eband Observing InternalCommunicationProblem-Port 4/5,DemXpicLOS-P at JED2602_02-10.3.232.163 | 10/25/2025 21:36:28 | Minor |  | LOF | 10/25/2025 21:36:28 | P3 | 2G | jeddah | Sceco | TX NSA | JED2602_02-10.3.232.163 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:33 | 10/26/2025 14:55:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000771 | PCM-20251026-00001533 | TT-20251026-01505 | Reference_telecom | Region_6 | JIZ0089 | JIZ0089 |  |  |  | Osama Hadi | 10/26/2025 14:51:34 | 10/26/2025 22:04:42 | 10/27/2025 02:51:34 | Nokia Eband Observing DemFail-Channel 1A,DemFail-Channel 1B at JIZ0089-10.3.86.10 | 09/30/2025 08:59:37 | Minor |  | LOF | 09/30/2025 08:59:37 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0089-10.3.86.10 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:34 | 10/26/2025 22:04:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000772 | PCM-20251026-00001534 | TT-20251026-01506 | Reference_telecom | Region_5 | MAK0011 | MAK0011 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 14:51:35 | 10/26/2025 14:51:35 | 10/27/2025 02:51:35 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 1 at MAK0011-7-10.10.147.81 | 09/08/2025 06:34:53 | Minor |  | LOF | 09/08/2025 06:34:53 | VIP | 2G | makkah | Sceco | TX NSA | MAK0011-7-10.10.147.81 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000773 | PCM-20251026-00001535 | TT-20251026-01507 | Reference_telecom | Region_5 | MAK0014 | MAK0014 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 14:51:37 | 10/26/2025 14:51:37 | 10/27/2025 02:51:37 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 2 at MAK0014_16-10.21.75.49 | 09/27/2025 15:56:08 | Minor |  | LOF | 09/27/2025 15:56:08 | P1 | 2G | makkah | Sceco | TX NSA | MAK0014_16-10.21.75.49 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000774 | PCM-20251026-00001536 | TT-20251026-01508 | Reference_telecom | Region_5 | MAK0058 | MAK0058 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 14:51:37 | 10/26/2025 14:51:37 | 10/27/2025 02:51:37 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A,BandwidthDeg at MAK0058-10-10.10.139.84 | 10/21/2025 05:35:08 | Minor |  | LOF | 10/21/2025 05:35:08 | VIP | 2G | makkah | Sceco | TX NSA | MAK0058-10-10.10.139.84 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000775 | PCM-20251026-00001537 | TT-20251026-01509 | Reference_telecom | Region_5 | MAK0066 | MAK0066 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 14:51:39 | 10/26/2025 14:51:39 | 10/27/2025 02:51:39 | Nokia Eband Observing Degrade-LAG 1,LagPortDown-Port 4/5 at MAK0066-13-10.10.143.33 | 10/07/2025 15:02:02 | Minor |  | LOF | 10/07/2025 15:02:02 | P1 | 2G | makkah | Sceco | TX NSA | MAK0066-13-10.10.143.33 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000776 | PCM-20251026-00001538 | TT-20251026-01510 | Reference_telecom | Region_5 | MAK0190 | MAK0190 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 14:51:40 | 10/26/2025 14:51:40 | 10/27/2025 02:51:40 | Nokia Eband Observing LossOfSignal-Port 6/5,Degrade-LAG 2,Degrade-LAG 3 at MAK0190 SH02-10.3.229.227 | 10/21/2025 04:00:43 | Minor |  | LOF | 10/21/2025 04:00:43 | P2 | 2G | makkah | Sceco | TX NSA | MAK0190 SH02-10.3.229.227 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000777 | PCM-20251026-00001539 | TT-20251026-01511 | Reference_telecom | Region_5 | MAK0190 | MAK0190 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 14:51:40 | 10/26/2025 14:51:40 | 10/27/2025 02:51:40 | Nokia Eband Observing LossOfSignal-Port 6/5,Degrade-LAG 2 at MAK0190_04-10.3.229.230 | 10/21/2025 04:00:43 | Minor |  | LOF | 10/21/2025 04:00:43 | P2 | 2G | makkah | Sceco | TX NSA | MAK0190_04-10.3.229.230 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000778 | PCM-20251026-00001540 | TT-20251026-01512 | Reference_telecom | Region_5 | MAK0754 | MAK0754 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 14:51:43 | 10/26/2025 15:22:59 | 10/27/2025 02:51:43 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at MAK0754- 01-10.3.224.50 | 10/25/2025 03:29:16 | Minor |  | LOF | 10/25/2025 03:29:16 | P2 | 2G | makkah | Sceco | TX NSA | MAK0754- 01-10.3.224.50 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:43 | 10/26/2025 15:22:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000779 | PCM-20251026-00001541 | TT-20251026-01513 | Reference_telecom | Region_5 | MAK0754 | MAK0754 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 14:51:44 | 10/26/2025 15:22:59 | 10/27/2025 02:51:44 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at MAK0754- 2-10.3.224.51 | 10/25/2025 03:43:40 | Minor |  | LOF | 10/25/2025 03:43:40 | P2 | 2G | makkah | Sceco | TX NSA | MAK0754- 2-10.3.224.51 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:44 | 10/26/2025 15:22:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000780 | PCM-20251026-00001542 | TT-20251026-01514 | Reference_telecom | Region_2 | RIY2000 | RIY2000 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 14:51:45 | 10/26/2025 15:00:36 | 10/27/2025 02:51:45 | Nokia Eband Observing DemFail-Port 1/1 at RIY2000-10.3.127.154 | 10/18/2025 07:56:10 | Minor |  | LOF | 10/18/2025 07:56:10 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2000-10.3.127.154 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:45 | 10/26/2025 15:00:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000781 | PCM-20251026-00001543 | TT-20251026-01515 | Reference_telecom | Region_4 | TAF0137 | TAF0137 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 14:51:46 | 10/26/2025 14:51:46 | 10/27/2025 02:51:46 | Nokia Eband Observing DemFail-Port 4/5,LagPortDown-Port 4/5,Degrade-LAG at TAF0137-4-10.1.233.81 | 10/24/2025 22:06:05 | Minor |  | LOF | 10/24/2025 22:06:05 | P2 | 2G | taif | Sceco | TX NSA | TAF0137-4-10.1.233.81 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000782 | PCM-20251026-00001544 | TT-20251026-01516 | Reference_telecom | Region_6 | TFBH0887 | TFBH0887 |  |  |  | SHAH KHALID | 10/26/2025 14:51:47 | 10/26/2025 17:41:08 | 10/27/2025 02:51:47 | Nokia Eband Observing DemFail-Channel 1A,Degrade-LAG 1,LagPortDown-Port at TFBH0887-10.3.228.81 | 10/20/2025 01:48:24 | Minor |  | LOF | 10/20/2025 01:48:24 | P1 | 2G | makhwa | Sceco_STB | TX NSA | TFBH0887-10.3.228.81 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:47 | 10/26/2025 17:41:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000783 | PCM-20251026-00001545 | TT-20251026-01517 | Reference_telecom | Region_2 | WTUM0001 | WTUM0001 |  |  |  | Muhammad Tahir Abdulrazzaq | 10/26/2025 14:51:49 | 10/26/2025 14:54:48 | 10/27/2025 02:51:49 | Nokia Eband Observing LossOfSignal-Port 1/2 at WTUM0001-10.3.126.235 | 09/28/2025 09:28:07 | Minor |  | LOF | 09/28/2025 09:28:07 | P3 | WIFI | Tumair | Sceco | TX NSA | WTUM0001-10.3.126.235 | FLM_TE | [8 empty] | API | 10/26/2025 14:51:49 | 10/26/2025 14:54:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000784 | PCM-20251026-00001546 | TT-20251026-01518 | Reference_telecom | Region_1 | ARM0720 | ARM0720 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:51:50 | 10/26/2025 17:46:17 | 10/27/2025 02:51:50 | MW RTN Observing HARD_BAD,HARD_ERR at ARM0720_NE_2_H | 09/21/2025 10:44:40 | Minor |  | LOF | 09/21/2025 10:44:40 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0720_NE_2_H | FLM_TE | [8 empty] | API | 10/26/2025 14:51:50 | 10/26/2025 17:46:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000786 | PCM-20251026-00001548 | TT-20251026-01520 | Reference_telecom | Region_1 | DAM0440 | DAM0440 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:51:52 | 10/26/2025 17:46:17 | 10/27/2025 02:51:52 | MW RTN Observing TEMP_ALARM,TEMP_ALARM,TEMP_ALARM,TEMP_ALARM at DAM0440_NE_1_SDB | 10/25/2025 19:18:35 | Minor |  | LOF | 10/25/2025 19:18:35 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0440_NE_1_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:51:52 | 10/26/2025 17:46:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000787 | PCM-20251026-00001549 | TT-20251026-01521 | EM | Region_4 | JDJZ1M8418 | JDJZ2418 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 14:51:53 | 10/26/2025 14:51:53 | 10/27/2025 02:51:53 | SHELTER DOOR OPEN at JDJZ1M8418-G9-L8-L18-SBTS-CAP @ Generator_SG | 10/26/2025 14:51:45 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 14:51:33 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JDJZ1M8418 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 14:51:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000788 | PCM-20251026-00001551 | TT-20251026-01523 | Reference_telecom | Region_1 | DAM0471 | DAM0471 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/26/2025 14:51:53 | 10/26/2025 15:01:08 | 10/27/2025 02:51:53 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at DAM0471_NE_5_H | 09/18/2025 13:31:27 | Minor |  | LOF | 09/18/2025 13:31:27 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0471_NE_5_H | FLM_TE | [8 empty] | API | 10/26/2025 14:51:53 | 10/26/2025 15:01:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000789 | PCM-20251026-00001552 | TT-20251026-01524 | Reference_telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/26/2025 14:51:54 | 10/26/2025 15:01:09 | 10/27/2025 02:51:54 | MW RTN Observing BUS_ERR,HARD_BAD,BUS_ERR,POWER_ALM,RADIO_RSL_LOW,R at DAM2066_NE_1_V | 10/02/2025 21:07:23 | Minor |  | LOF | 10/02/2025 21:07:23 | P1 | SRAN | dammam | Sceco | TX NSA | DAM2066_NE_1_V | FLM_TE | [8 empty] | API | 10/26/2025 14:51:54 | 10/26/2025 15:01:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000790 | PCM-20251026-00001553 | TT-20251026-01525 | Reference_telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/26/2025 14:51:56 | 10/26/2025 15:01:09 | 10/27/2025 02:51:56 | MW RTN Observing BUS_ERR,HARD_BAD,BUS_ERR,POWER_ALM,RADIO_RSL_LOW,R at DAM2066_NE_2_H | 10/02/2025 21:07:24 | Minor |  | LOF | 10/02/2025 21:07:24 | P1 | SRAN | dammam | Sceco | TX NSA | DAM2066_NE_2_H | FLM_TE | [8 empty] | API | 10/26/2025 14:51:56 | 10/26/2025 15:01:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000791 | PCM-20251026-00001554 | TT-20251026-01526 | Reference_telecom | Region_1 | DAM2992 | DAM2992 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/26/2025 14:51:57 | 10/26/2025 15:01:10 | 10/27/2025 02:51:57 | MW RTN Observing RADIO_RSL_LOW,PLA_DOWN,MW_LOF,PLA_MEMBER_DOWN_EXT, at DAM2992_NE_4_V | 10/13/2025 10:27:56 | Minor |  | LOF | 10/13/2025 10:27:56 | P2 | SRAN | dammam | Sceco | TX NSA | DAM2992_NE_4_V | FLM_TE | [8 empty] | API | 10/26/2025 14:51:57 | 10/26/2025 15:01:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000792 | PCM-20251026-00001555 | TT-20251026-01527 | Reference_telecom | Region_1 | DAM2992 | DAM2992 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/26/2025 14:51:58 | 10/26/2025 15:01:10 | 10/27/2025 02:51:58 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at DAM2992_NE_5_H | 10/13/2025 10:27:56 | Minor |  | LOF | 10/13/2025 10:27:56 | P2 | SRAN | dammam | Sceco | TX NSA | DAM2992_NE_5_H | FLM_TE | [8 empty] | API | 10/26/2025 14:51:58 | 10/26/2025 15:01:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000793 | PCM-20251026-00001556 | TT-20251026-01528 | Reference_telecom | Region_1 | DMAP2153 | DMAP2153 |  |  |  | Meraj Husain Idd Baksh | 10/26/2025 14:51:59 | 10/26/2025 15:14:42 | 10/27/2025 02:51:59 | MW RTN Observing HARD_BAD at DMAP2153_NE_2_H | 10/17/2025 16:40:42 | Minor |  | LOF | 10/17/2025 16:40:42 | P2 | SRAN | dammam | Sceco | TX NSA | DMAP2153_NE_2_H | FLM_TE | [8 empty] | API | 10/26/2025 14:51:59 | 10/26/2025 15:14:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000794 | PCM-20251026-00001557 | TT-20251026-01529 | Reference_telecom | Region_1 | DRN0134 | DRN0134 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:52:00 | 10/26/2025 17:46:18 | 10/27/2025 02:52:00 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at DRN0134_NE_15_ | 10/04/2025 14:28:50 | Minor |  | LOF | 10/04/2025 14:28:50 | P1 | SRAN | dammam | Sceco | TX NSA | DRN0134_NE_15_ | FLM_TE | [8 empty] | API | 10/26/2025 14:52:00 | 10/26/2025 17:46:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000795 | PCM-20251026-00001558 | TT-20251026-01530 | Reference_telecom | Region_1 | DRN2328 | DRN2328 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:52:02 | 10/26/2025 17:46:19 | 10/27/2025 02:52:02 | MW RTN Observing HARD_BAD at DRN2328_NE_1_V | 10/02/2025 03:05:46 | Minor |  | LOF | 10/02/2025 03:05:46 | P3 | SRAN | dammam | Sceco | TX NSA | DRN2328_NE_1_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:02 | 10/26/2025 17:46:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000797 | PCM-20251026-00001560 | TT-20251026-01532 | Reference_telecom | Region_1 | HMBY0419 | HMBY0419 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:52:04 | 10/26/2025 17:46:19 | 10/27/2025 02:52:04 | MW RTN Observing IF_CABLE_OPEN,IF_CABLE_OPEN,MW_LOF,MW_LOF,MW_LOF,M at HMBY0419_TO_HMBY0422 | 10/24/2025 02:20:20 | Minor |  | LOF | 10/24/2025 02:20:20 | P3 | SRAN | dammam | Generator_SG | TX NSA | HMBY0419_TO_HMBY0422 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:04 | 10/26/2025 17:46:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000798 | PCM-20251026-00001561 | TT-20251026-01533 | Reference_telecom | Region_1 | HMBY0426 | HMBY0426 |  |  |  | Imran Ali Yousaf | 10/26/2025 14:52:05 | 10/26/2025 17:46:20 | 10/27/2025 02:52:05 | MW RTN Observing IN_PWR_LOW at HMBY0426_NE_4_V | 10/20/2025 14:59:21 | Minor |  | LOF | 10/20/2025 14:59:21 | P3 | SRAN | dammam | Sceco | TX NSA | HMBY0426_NE_4_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:05 | 10/26/2025 17:46:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000799 | PCM-20251026-00001562 | TT-20251026-01534 | Reference_telecom | Region_1 | JBL2108 | JBL2108 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 14:52:06 | 10/26/2025 15:03:17 | 10/27/2025 02:52:06 | MW RTN Observing PLA_MEMBER_DOWN_EXT,PLA_MEMBER_DOWN_EXT,PLA_MEMBER at JBL2108_NE_17_SDB | 05/10/2025 18:49:32 | Minor |  | LOF | 05/10/2025 18:49:32 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBL2108_NE_17_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:06 | 10/26/2025 15:03:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000800 | PCM-20251026-00001563 | TT-20251026-01535 | Reference_telecom | Region_1 | JBL2384 | JBL2384 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 14:52:08 | 10/26/2025 15:03:17 | 10/27/2025 02:52:08 | MW RTN Observing ETH_LINK_DOWN,NB_UNREACHABLE at JBL2384_NE_5_H | 10/17/2025 16:16:46 | Minor |  | LOF | 10/17/2025 16:16:46 | P3 | SRAN | jubail | Sceco | TX NSA | JBL2384_NE_5_H | FLM_TE | [8 empty] | API | 10/26/2025 14:52:08 | 10/26/2025 15:03:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000801 | PCM-20251026-00001564 | TT-20251026-01536 | Reference_telecom | Region_1 | JBL2934 | JBL2934 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 14:52:09 | 10/26/2025 15:03:18 | 10/27/2025 02:52:09 | MW RTN Observing PLA_MEMBER_DOWN_EXT at JBL2934_NE_1_V | 10/08/2025 15:42:44 | Minor |  | LOF | 10/08/2025 15:42:44 | P3 | SRAN | jubail | Sceco | TX NSA | JBL2934_NE_1_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:09 | 10/26/2025 15:03:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000802 | PCM-20251026-00001565 | TT-20251026-01537 | Reference_telecom | Region_3 | MDN0720 | MDN0720 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/26/2025 14:52:09 | 10/26/2025 18:16:12 | 10/27/2025 02:52:09 | MW RTN Observing LAG_MEMBER_DOWN at MDN0720_NE_19_V | 10/25/2025 20:04:57 | Minor |  | LOF | 10/25/2025 20:04:57 | P1 | SRAN | madinah | Sceco | TX NSA | MDN0720_NE_19_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:09 | 10/26/2025 18:16:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000804 | PCM-20251026-00001567 | TT-20251026-01539 | Reference_telecom | Region_3 | MDN0801 | MDN0801 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 14:52:12 | 10/26/2025 19:31:38 | 10/27/2025 02:52:12 | MW RTN Observing PLA_PKT_ERR at MDN0801_NE_3_SDB | 10/20/2025 13:54:22 | Minor |  | LOF | 10/20/2025 13:54:22 | P2 | SRAN | madinah | Sceco | TX NSA | MDN0801_NE_3_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:12 | 10/26/2025 19:31:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000805 | PCM-20251026-00001568 | TT-20251026-01540 | Reference_telecom | Region_3 | MDTB2325 | MDTB2325 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 14:52:13 | 10/26/2025 19:31:39 | 10/27/2025 02:52:13 | MW RTN Observing LAG_MEMBER_DOWN at MDTB2325_NE_3 | 10/25/2025 13:53:47 | Minor |  | LOF | 10/25/2025 13:53:47 | P3 | SRAN | madinah | Generator_DG | TX NSA | MDTB2325_NE_3 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:13 | 10/26/2025 19:31:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000806 | PCM-20251026-00001569 | TT-20251026-01541 | Reference_telecom | Region_2 | RIY0078 | RIY0078 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/26/2025 14:52:14 | 10/26/2025 23:43:09 | 10/27/2025 02:52:14 | MW RTN Observing LAG_MEMBER_DOWN,ETH_LOS,RADIO_RSL_LOW,RADIO_RSL_LO at RIY0078_NE_9_FON | 11/19/2024 17:21:02 | Minor |  | LOF | 11/19/2024 17:21:02 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0078_NE_9_FON | FLM_TE | [8 empty] | API | 10/26/2025 14:52:14 | 10/26/2025 23:43:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000807 | PCM-20251026-00001570 | TT-20251026-01542 | Reference_telecom | Region_2 | RIY0202 | RIY0202 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 14:52:15 | 10/27/2025 07:29:24 | 10/27/2025 02:52:15 | MW RTN Observing RADIO_RSL_LOW,PLA_DOWN,PLA_MEMBER_DOWN_EXT,PLA_MEM at RIY0202_NE_5_V | 10/07/2025 17:17:36 | Minor |  | LOF | 10/07/2025 17:17:36 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0202_NE_5_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:15 | 10/27/2025 07:29:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000808 | PCM-20251026-00001571 | TT-20251026-01543 | Reference_telecom | Region_2 | RIY0322 | RIY0322 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Waseem Shahzad Ghulam Rasool | 10/26/2025 14:52:17 | 10/26/2025 15:28:25 | 10/27/2025 02:52:17 | MW RTN Observing PLA_MEMBER_DOWN_EXT,PLA_MEMBER_DOWN_EXT at RIY0322_NE_7_SDB | 10/12/2025 13:26:46 | Minor |  | LOF | 10/12/2025 13:26:46 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0322_NE_7_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:17 | 10/26/2025 15:26:44 | 10/26/2025 15:28:12 |  |  | 10/26/2025 15:28:25 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000809 | PCM-20251026-00001572 | TT-20251026-01544 | Reference_telecom | Region_2 | RIY0363 | RIY0363 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/26/2025 14:52:18 | 10/26/2025 15:28:37 | 10/27/2025 02:52:18 | MW RTN Observing PLA_MEMBER_DOWN_EXT,PLA_MEMBER_DOWN_EXT at RIY0363_NE_3_SDB | 10/12/2025 13:26:46 | Minor |  | LOF | 10/12/2025 13:26:46 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0363_NE_3_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:18 | 10/26/2025 15:26:44 | 10/26/2025 15:28:30 |  |  | 10/26/2025 15:28:37 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000810 | PCM-20251026-00001573 | TT-20251026-01545 | Reference_telecom | Region_2 | RIY0390 | RIY0390 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/26/2025 14:52:19 | 10/26/2025 23:43:12 | 10/27/2025 02:52:19 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0390_NE_10_H | 09/25/2025 10:35:26 | Minor |  | LOF | 09/25/2025 10:35:26 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0390_NE_10_H | FLM_TE | [8 empty] | API | 10/26/2025 14:52:19 | 10/26/2025 23:43:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000811 | PCM-20251026-00001574 | TT-20251026-01546 | Reference_telecom | Region_2 | RIY0390 | RIY0390 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/26/2025 14:52:20 | 10/26/2025 23:43:13 | 10/27/2025 02:52:20 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0390_NE_9_V | 09/25/2025 10:35:26 | Minor |  | LOF | 09/25/2025 10:35:26 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0390_NE_9_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:20 | 10/26/2025 23:43:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000812 | PCM-20251026-00001575 | TT-20251026-01547 | Reference_telecom | Region_2 | RIY0597 | RIY0597 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 14:52:21 | 10/26/2025 15:00:37 | 10/27/2025 02:52:21 | MW RTN Observing RADIO_RSL_LOW,RADIO_RSL_LOW,PLA_DOWN,PLA_MEMBER_DO at RIY0597_NE_5 | 10/22/2024 02:13:19 | Minor |  | LOF | 10/22/2024 02:13:19 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0597_NE_5 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:21 | 10/26/2025 15:00:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000813 | PCM-20251026-00001576 | TT-20251026-01548 | Reference_telecom | Region_2 | RIY0639 | RIY0639 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:22 | 10/26/2025 15:16:20 | 10/27/2025 02:52:22 | MW RTN Observing MW_BER_SD,PLA_MEMBER_DOWN_EXT,PLA_DOWN,MW_LOF,PLA_ at RIY0639_NE_15_SDB | 05/14/2025 04:46:22 | Minor |  | LOF | 05/14/2025 04:46:22 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0639_NE_15_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:22 | 10/26/2025 15:16:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000814 | PCM-20251026-00001577 | TT-20251026-01549 | Reference_telecom | Region_2 | RIY0639 | RIY0639 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:24 | 10/26/2025 15:16:20 | 10/27/2025 02:52:24 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0639_NE_16_V | 05/14/2025 04:46:13 | Minor |  | LOF | 05/14/2025 04:46:13 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0639_NE_16_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:24 | 10/26/2025 15:16:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000815 | PCM-20251026-00001578 | TT-20251026-01552 | Reference_telecom | Region_2 | RIY0692 | RIY0692 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/26/2025 14:52:27 | 10/26/2025 23:43:14 | 10/27/2025 02:52:27 | MW RTN Observing ETH_LOS at RIY0692_NE_3 | 10/20/2025 12:57:39 | Minor |  | LOF | 10/20/2025 12:57:39 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0692_NE_3 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:27 | 10/26/2025 23:43:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000816 | PCM-20251026-00001579 | TT-20251026-01553 | Reference_telecom | Region_2 | RIY0792 | RIY0792 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:28 | 10/26/2025 15:16:21 | 10/27/2025 02:52:28 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0792_NE_25_V | 08/25/2024 08:22:18 | Minor |  | LOF | 08/25/2024 08:22:18 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0792_NE_25_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:28 | 10/26/2025 15:16:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000817 | PCM-20251026-00001580 | TT-20251026-01554 | Reference_telecom | Region_2 | RIY0861 | RIY0861 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:30 | 10/26/2025 15:16:22 | 10/27/2025 02:52:30 | MW RTN Observing POWER_ALM at RIY0861_NE_20_V | 10/23/2025 11:23:09 | Minor |  | LOF | 10/23/2025 11:23:09 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0861_NE_20_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:30 | 10/26/2025 15:16:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000818 | PCM-20251026-00001581 | TT-20251026-01555 | Reference_telecom | Region_2 | RIY0861 | RIY0861 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:31 | 10/26/2025 15:16:23 | 10/27/2025 02:52:31 | MW RTN Observing POWER_ALM at RIY0861_NE_21_H | 10/23/2025 11:23:08 | Minor |  | LOF | 10/23/2025 11:23:08 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0861_NE_21_H | FLM_TE | [8 empty] | API | 10/26/2025 14:52:31 | 10/26/2025 15:16:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000819 | PCM-20251026-00001582 | TT-20251026-01556 | Reference_telecom | Region_2 | RIY0871 | RIY0871 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 14:52:33 | 10/26/2025 15:00:37 | 10/27/2025 02:52:33 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0871_NE_31_H | 06/16/2025 23:48:44 | Minor |  | LOF | 06/16/2025 23:48:44 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0871_NE_31_H | FLM_TE | [8 empty] | API | 10/26/2025 14:52:33 | 10/26/2025 15:00:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000820 | PCM-20251026-00001583 | TT-20251026-01559 | Reference_telecom | Region_2 | RIY2720 | RIY2720 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 14:52:35 | 10/26/2025 15:00:41 | 10/27/2025 02:52:35 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY2720_NE_10_H | 10/05/2024 15:55:02 | Minor |  | LOF | 10/05/2024 15:55:02 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2720_NE_10_H | FLM_TE | [8 empty] | API | 10/26/2025 14:52:35 | 10/26/2025 15:00:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000821 | PCM-20251026-00001584 | TT-20251026-01561 | Reference_telecom | Region_3 | ULA0250 | ULA0250 |  |  |  | Hamayo Din Jalal | 10/26/2025 14:52:41 | 10/27/2025 00:43:45 | 10/27/2025 02:52:41 | MW RTN Observing LASER_CHECK_ERR at ULA0250_NE_5_H | 10/20/2025 18:05:03 | Minor |  | LOF | 10/20/2025 18:05:03 | P2 | SRAN | tabouk | Sceco | TX NSA | ULA0250_NE_5_H | FLM_TE | [8 empty] | API | 10/26/2025 14:52:41 | 10/27/2025 00:43:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000823 | PCM-20251026-00001586 | TT-20251026-01563 | Reference_telecom | Region_2 | RIY2571 | RIY2571 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 14:52:43 | 10/27/2025 07:29:25 | 10/27/2025 02:52:43 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RIY2571_NE_5_SDB | 10/22/2025 16:24:51 | Minor |  | LOF | 10/22/2025 16:24:51 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2571_NE_5_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:43 | 10/27/2025 07:29:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000824 | PCM-20251026-00001587 | TT-20251026-01564 | Reference_telecom | Region_2 | RIY2209 | RIY2209 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 14:52:44 | 10/27/2025 07:29:25 | 10/27/2025 02:52:44 | MW RTN Observing PLA_PKT_ERR at RIY2209_NE_3_SDB | 09/15/2025 11:29:30 | Minor |  | LOF | 09/15/2025 11:29:30 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2209_NE_3_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:44 | 10/27/2025 07:29:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000825 | PCM-20251026-00001588 | TT-20251026-01566 | Reference_telecom | Region_2 | RIY2720 | RIY2720 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 14:52:46 | 10/26/2025 15:00:42 | 10/27/2025 02:52:46 | MW RTN Observing PLA_MEMBER_DOWN_EXT,RADIO_RSL_LOW,PLA_MEMBER_DOWN_ at RIY2720_NE_9_V | 10/05/2024 15:54:27 | Minor |  | LOF | 10/05/2024 15:54:27 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2720_NE_9_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:46 | 10/26/2025 15:00:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000826 | PCM-20251026-00001589 | TT-20251026-01567 | Reference_telecom | Region_2 | SAR0306 | SAR0306 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:48 | 10/26/2025 15:16:24 | 10/27/2025 02:52:48 | MW RTN Observing RADIO_RSL_LOW,RADIO_RSL_LOW,PLA_MEMBER_DOWN_EXT,PL at SAR0306_NE_4 | 10/11/2025 12:07:00 | Minor |  | LOF | 10/11/2025 12:07:00 | P2 | SRAN | rumah | Generator_DG | TX NSA | SAR0306_NE_4 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:48 | 10/26/2025 15:16:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000827 | PCM-20251026-00001590 | TT-20251026-01568 | Reference_telecom | Region_2 | RIY2846 | RIY2846 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:49 | 10/26/2025 15:16:24 | 10/27/2025 02:52:49 | MW RTN Observing PLA_PKT_ERR at RIY2846_NE_3_SDB | 10/21/2025 19:39:33 | Minor |  | LOF | 10/21/2025 19:39:33 | P3 | SRAN | riyadh | Sceco | TX NSA | RIY2846_NE_3_SDB | FLM_TE | [8 empty] | API | 10/26/2025 14:52:49 | 10/26/2025 15:16:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000828 | PCM-20251026-00001591 | TT-20251026-01569 | Reference_telecom | Region_2 | RIY2880 | RIY2880 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 14:52:50 | 10/26/2025 15:16:25 | 10/27/2025 02:52:50 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY2880_NE_4 | 10/13/2025 14:34:21 | Minor |  | LOF | 10/13/2025 14:34:21 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2880_NE_4 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:50 | 10/26/2025 15:16:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000829 | PCM-20251026-00001592 | TT-20251026-01571 | Reference_telecom | Region_1 | YBR0682 | YBR0682 |  |  |  | Mohamed Magdy Fouad Zayed | 10/26/2025 14:52:53 | 10/26/2025 17:56:57 | 10/27/2025 02:52:53 | MW RTN Observing PLA_MEMBER_DOWN_EXT,MW_LOF at YBR0682_NE_1 | 04/28/2025 18:40:55 | Minor |  | LOF | 04/28/2025 18:40:55 | P2 | SRAN | hafouf | Power Cube | TX NSA | YBR0682_NE_1 | FLM_TE | [8 empty] | API | 10/26/2025 14:52:53 | 10/26/2025 17:56:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000830 | PCM-20251026-00001593 | TT-20251026-01572 | Reference_telecom | Region_2 | RIY0871 | RIY0871 |  |  |  | Khan zeb Shah nawaz | 10/26/2025 14:52:53 | 10/26/2025 15:01:25 | 10/27/2025 02:52:53 | MW RTN Observing MW_LOF at RIY0871_NE_32_V | 06/16/2025 23:48:44 | Minor |  | LOF | 06/16/2025 23:48:44 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0871_NE_32_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:53 | 10/26/2025 15:01:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000831 | PCM-20251026-00001594 | TT-20251026-01573 | Reference_telecom | Region_1 | RST0089 | RST0089 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 14:52:55 | 10/26/2025 15:03:18 | 10/27/2025 02:52:55 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RST0089_NE_4_V | 10/17/2025 06:15:31 | Minor |  | LOF | 10/17/2025 06:15:31 | P3 | SRAN | jubail | Sceco | TX NSA | RST0089_NE_4_V | FLM_TE | [8 empty] | API | 10/26/2025 14:52:55 | 10/26/2025 15:03:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000832 | PCM-20251026-00001601 | TT-20251026-01584 | Telecom | Region_2 | RIY2M2796 | RIY2796 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | WAQAR AHMED BASHIR AHMED | 10/26/2025 14:57:46 | 10/26/2025 15:16:02 | 10/26/2025 20:57:46 | GSM Local Cell Unusable at RIY2M2796-P2 @ Sceco | 10/26/2025 14:56:13 | Major | 28016 | GSM Local Cell Unusable | 10/26/2025 14:54:40 | P2 | 2G | riyadh | Sceco | 2G SA | RIY2M2796 | FLM_TE | [8 empty] | API | 10/26/2025 14:57:46 | 10/26/2025 15:02:08 | 10/26/2025 15:07:05 | 10/26/2025 15:07:06 | 10/26/2025 15:07:08 | 10/26/2025 15:16:02 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000833 | PCM-20251026-00001605 | TT-20251026-01577 | Telecom | Region_4 | SJED1S7703 | SJED0703 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 14:59:29 | 10/26/2025 14:59:29 | 10/26/2025 20:59:29 | 1(LTE) sites down under SJED0703-P3-CA @ Sceco | 10/26/2025 14:51:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 14:51:09 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0703-P3-CA | FLM_TE | SJED0703 | Results: DOWN SITE HUB SJED0703-P3-CA SJED0703 Summary: Hub: SJED0703, Down Count: 1, Down Sites: SJED0703-P3-CA Alarm Summary: SJED0703 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.168.92:8080] [URL:http://10.96.168.92:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 14:59:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000834 | PCM-20251026-00001607 | TT-20251026-01587 | Telecom | Region_6 | RYNJ0200 | RYNJ0200 | Equipment | SFP_BTS | Clean SFP | Saif Muhammad | 10/26/2025 14:59:38 | 10/26/2025 15:48:13 | 10/26/2025 20:59:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at RYNJ0200-GSM-P3-HUB @ Generator_DG | 10/26/2025 14:58:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 14:58:39 | P1 | 2G | wadi dawasar | Generator_DG | 5G_Cell SA | RYNJ0200 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 14:59:38 | 10/26/2025 15:45:26 | 10/26/2025 15:46:36 | 10/26/2025 15:46:41 | 10/26/2025 15:46:44 | 10/26/2025 15:48:13 |  | Saif Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000836 | PCM-20251026-00001609 | TT-20251026-01439 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 15:00:11 | 10/26/2025 15:00:11 | 10/26/2025 19:00:11 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/26/2025 14:42:05 | Critical | 7654 | CELL OPERATION DEGRADED | 10/26/2025 14:42:01 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251026-00001468 | Kindly check the VSWR alarm active at site | Kindly check the VSWR alarm active at site |  |  |  | API | 10/26/2025 15:00:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000837 | PCM-20251026-00001613 | TT-20251026-01591 | Reference_EM | Region_3 | AHT2360 | AHT2360 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 15:01:11 | 10/27/2025 07:11:10 | 10/27/2025 03:01:11 | Door opening alarm at AHT2360-P3_SRAN @ Sceco | 10/26/2025 15:00:43 | Minor | 65101 | Door opening alarm | 10/26/2025 15:00:39 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2360 | FLM_EM | [8 empty] | API | 10/26/2025 15:01:11 | 10/27/2025 07:11:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000838 | PCM-20251026-00001614 | TT-20251026-01592 | EM | Region_3 | AHT2360 | AHT2360 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 15:01:11 | 10/27/2025 07:11:11 | 10/27/2025 03:01:11 | NETECO: Door Status Sensor Alarm at AHT2360 @ Sceco | 10/26/2025 15:00:38 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 15:00:38 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2360 | FLM_EM | [8 empty] | API | 10/26/2025 15:01:11 | 10/27/2025 07:11:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000839 | PCM-20251026-00001616 | TT-20251026-01593 | Telecom | Region_6 | ABH0327 | ABH0327 | Equipment | SFP_BTS | Replace SFP | Amir Sohail | 10/26/2025 15:01:42 | 10/26/2025 15:36:08 | 10/27/2025 03:01:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH0327-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 15:00:39 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 15:00:33 | P2 | 2G | abha | Sceco | 5G_Cell SA | ABH0327 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 15:01:42 | 10/26/2025 15:29:20 | 10/26/2025 15:35:50 |  |  | 10/26/2025 15:36:08 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000840 | PCM-20251026-00001617 | TT-20251026-01594 | Telecom | Region_6 | AHM0036 | AHM0036 | Transsmission | SFP_Transmission | Reset SFP | Zeshan Ali Adnan | 10/26/2025 15:01:42 | 10/26/2025 15:55:32 | 10/27/2025 03:01:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at AHM0036-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 15:01:06 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 15:00:55 | P3 | 2G | jizan | Sceco | 5G_Cell SA | AHM0036 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 15:01:42 | 10/26/2025 15:53:35 | 10/26/2025 15:55:03 |  |  | 10/26/2025 15:55:32 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000842 | PCM-20251026-00001621 | TT-20251026-01598 | Telecom | Region_6 | JEC1M7331 | JEC0331 | Equipment | SFP_BTS | Replace SFP | Ansir Iqbal Muhammad Iqbal | 10/26/2025 15:04:18 | 10/26/2025 23:38:09 | 10/26/2025 19:04:18 | BASE STATION SERVICE PROBLEM (No connection to unit) at JEC1M7331-CA-P1-L800-VIP @ Generator_SG | 10/26/2025 15:03:23 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 15:03:10 | VIP | 4G | baish | Generator_SG | 5G_Cell SA | JEC1M7331 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 15:04:18 | 10/26/2025 20:21:16 | 10/26/2025 23:37:51 |  |  | 10/26/2025 23:38:09 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000843 | PCM-20251026-00001622 | TT-20251026-01599 | EM | Region_6 | KHS1M7563 | KHS0563 |  |  |  | Ezat Mohammed | 10/26/2025 15:04:49 | 10/26/2025 15:04:49 | 10/27/2025 03:04:49 | SHELTER DOOR OPEN at KHS1M7563-G9-L9-SBTS-P2-USF @ Sceco | 10/26/2025 15:04:30 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 15:04:20 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7563 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 15:04:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000844 | PCM-20251026-00001625 | TT-20251026-01603 | Telecom | Region_6 | DAR1M7917 | DAR0917 | Equipment | BSS_HW_Stuck | Reset RRU | Muhammad Ali | 10/26/2025 15:05:50 | 10/26/2025 16:32:46 | 10/26/2025 19:05:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR1M7917-P1-CA-L800 @ Generator_SG | 10/26/2025 15:04:51 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 15:04:46 | P1 | 4G | dair | Generator_SG | 5G_Cell SA | DAR1M7917 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 15:05:50 | 10/26/2025 16:32:09 | 10/26/2025 16:32:21 |  |  | 10/26/2025 16:32:46 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000845 | PCM-20251026-00001626 | TT-20251026-01602 | Telecom | Region_3 | MDN2903 | MDN2903 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 15:05:50 | 10/26/2025 19:31:39 | 10/27/2025 03:05:50 | ALD Maintenance Link Failure at MDN2903-P2_SRAN @ Sceco | 10/26/2025 15:03:13 | Minor | 26541 | ALD Maintenance Link Failure | 10/26/2025 15:01:29 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2903 | FLM_TE | [8 empty] | API | 10/26/2025 15:05:50 | 10/26/2025 19:31:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000847 | PCM-20251026-00001629 | TT-20251026-01606 | EM | [7 empty] | 10/26/2025 15:06:52 | 10/26/2025 15:06:52 | 10/27/2025 03:06:52 | NETECO: Genset Fault at MDQS2433 @ Generator_DG | 10/26/2025 15:00:40 | Minor | 40564 | Genset Fault | 10/26/2025 15:00:40 | P3 | SRAN |  | Generator_DG | 2G NSA | MDQS2433 | FLM_EM | [8 empty] | API | 10/26/2025 15:06:52 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000848 | PCM-20251026-00001632 | TT-20251026-01610 | Telecom | Region_3 | MDN2M8906 | MDN2906 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 15:08:32 | 10/26/2025 21:49:39 | 10/26/2025 21:08:32 | Cell Unavailable at MDN2M8906-CA-L800-P2 @ Generator_SG | 10/26/2025 15:02:46 | Major | 29240 | Cell Unavailable | 10/26/2025 15:01:13 | P2 | 4G | madinah | Generator_SG | LTE SA | MDN2M8906 | FLM_TE | [8 empty] | API | 10/26/2025 15:08:32 | 10/26/2025 19:31:40 | 10/26/2025 21:49:33 |  |  | 10/26/2025 21:49:39 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000849 | PCM-20251026-00001634 | TT-20251026-01613 | EM | Region_6 | ABBS1M8247 | ABBS2247 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/26/2025 15:09:59 | 10/26/2025 15:09:59 | 10/27/2025 03:09:59 | SHELTER DOOR OPEN at ABBS1M8247-L800-P3-SBTS-WBB-G3 @ Sceco | 10/26/2025 15:09:25 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 15:09:21 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M8247 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 15:09:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000850 | PCM-20251026-00001635 | TT-20251026-01600 | Telecom | Region_4 | JED1M7320 | JED0320 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 15:09:59 | 10/26/2025 15:35:45 | 10/26/2025 21:09:59 | 1(LTE) sites down under JED0320-CA-L900-L800-SBTS @ Sceco | 10/26/2025 15:01:48 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 15:01:45 | P2 | 4G | jeddah | Sceco | LTE SA | JED0320-CA-L900-L800-SBTS | FLM_TE | JED0320 | Results: DOWN SITE HUB JED0320-CA-L900-L800-SBTS JED0320 Summary: Hub: JED0320, Down Count: 1, Down Sites: JED0320-CA-L900-L800-SBTS Alarm Summary: JED0320 No Active Alarm on HUB |  |  |  | Connection reset [URL:http://10.97.112.148:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 15:09:59 | 10/26/2025 15:35:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000851 | PCM-20251026-00001636 | TT-20251026-01614 | EM | Region_3 | RUSF9012 | RUSF9012 |  |  |  | Muhammad Imran Muhammad Aslam | 10/26/2025 15:10:29 | 10/26/2025 23:52:30 | 10/27/2025 03:10:29 | NETECO: Door Status Sensor Alarm at RUSF9012 @ Generator_SG | 10/26/2025 15:10:20 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 15:10:20 | P3 | Repeater | madinah | Generator_SG | 2G NSA | RUSF9012 | FLM_EM | [8 empty] | API | 10/26/2025 15:10:29 | 10/26/2025 23:52:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251026000854 | PCM-20251026-00001644 | TT-20251026-01409 | Reference_telecom | Region_6 | ARF0066-ZAs02-CSG-01 | ARF0066 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 15:12:41 | 10/26/2025 17:13:46 | 10/26/2025 19:12:41 | MW Link down Down at ARF0066-ZAs02-CSG-01 to KMS0504 REF:TT-20251011-00915 @ Sceco_STB | 08/17/2025 10:35:53 | Critical | 101-2505274 | Physical Port Down | 02/12/2025 11:05:32 | P3 | IPRAN | al harja | Sceco_STB | IPRAN SA | ARF0066-ZAs02-CSG-01 | FLM_TE |  |  | PCM-20251026-00001443 | Dear FLm team, kindly perform HC for MW ARF0191-ARF0072 | Dear FLm team, kindly perform HC for MW ARF0191-ARF0072 |  |  |  | API | 10/26/2025 15:12:41 | 10/26/2025 16:49:37 | 10/26/2025 16:50:18 | 10/26/2025 16:50:21 | 10/26/2025 17:13:46 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000855 | PCM-20251026-00001646 | TT-20251026-01626 | Telecom | Region_1 | DAM2061 | DAM2061 |  |  |  | Imran Ali Yousaf | 10/26/2025 15:13:05 | 10/26/2025 17:46:20 | 10/27/2025 03:13:05 | HC TT for DAM2061 | 10/26/2025 15:12:34 | Minor | 676767672 | Health Check-WO to TE FME | 10/26/2025 15:12:34 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | DAM2061 | FLM_TE | [8 empty] | API | 10/26/2025 15:13:05 | 10/26/2025 17:46:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000856 | PCM-20251026-00001647 | TT-20251026-01609 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/26/2025 15:13:29 | 10/26/2025 17:56:57 | 10/26/2025 21:13:29 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/26/2025 15:05:20 | Major | 22214 | NodeB Unavailable | 10/26/2025 15:05:18 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 15:13:29 | 10/26/2025 17:56:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000857 | PCM-20251026-00001648 | TT-20251026-01611 | Telecom | Region_4 | TAF2277 | TAF2277 |  |  |  | Rashid Shafique | 10/26/2025 15:13:38 | 10/26/2025 15:15:22 | 10/26/2025 21:13:38 | 1(5G) sites down under TAF2277-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/26/2025 15:05:34 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 15:05:32 | P3 | 2G | taif | Sceco | 5G SA | TAF2277-G9-L8-L18-L21-NR2.6-P3 | FLM_TE | TAF2277 | Results: DOWN SITE HUB TAF2277-G9-L8-L18-L21-NR2.6-P3 TAF2277 Summary: Hub: TAF2277, Down Count: 1, Down Sites: TAF2277-G9-L8-L18-L21-NR2.6-P3 Alarm Summary: TAF2277 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.99.176.132:8080] [URL:http://10.99.176.132:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 15:13:38 | 10/26/2025 15:15:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000858 | PCM-20251026-00001650 | TT-20251026-01628 | Telecom | Region_5 | MAK2821 | MAK2821 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/26/2025 15:14:07 | 10/26/2025 15:14:07 | 10/26/2025 21:14:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2821-G9-L8-L18-L21-NR2.6-P3 @ Generator_SG | 10/26/2025 15:13:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 15:13:15 | P3 | 2G | makkah | Generator_SG | 5G_Cell SA | MAK2821 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 15:14:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000859 | PCM-20251026-00001653 | TT-20251026-01632 | EM | [7 empty] | 10/26/2025 15:15:08 | 10/26/2025 15:15:08 | 10/27/2025 03:15:08 | NETECO: Door Status Sensor Alarm at BDR2112 @ Generator_DG | 10/26/2025 15:14:37 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 15:14:37 | P3 | SRAN |  | Generator_DG | 2G NSA | BDR2112 | FLM_EM | [8 empty] | API | 10/26/2025 15:15:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000861 | PCM-20251026-00001660 | TT-20251026-01639 | EM | Region_4 | JDJZ1M8418 | JDJZ2418 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/26/2025 15:19:48 | 10/26/2025 15:19:48 | 10/27/2025 03:19:48 | TOWER LIGHT at JDJZ1M8418-G9-L8-L18-SBTS-CAP @ Generator_SG | 10/26/2025 15:11:29 | Minor | 7103 | TOWER LIGHT | 10/26/2025 15:11:21 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JDJZ1M8418 | FLM_EM | [5 empty] | TOWER LIGHT |  |  | API | 10/26/2025 15:19:48 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000862 | PCM-20251026-00001661 | TT-20251026-01636 | EM | Region_3 | WFR2M2137 | WFR2137 |  |  |  | Muhammad arshad Anwar | 10/26/2025 15:20:59 | 10/26/2025 15:20:59 | 10/26/2025 21:20:59 | 1(2G/LTE) sites down under WFR2137-P3/R3_MD_HWBSC01 @ Sceco | 10/26/2025 15:12:34 | Major | 21825 | CSL Fault | 10/26/2025 15:12:34 | P3 | 2G | madinah | Sceco | 2G_LTE SA | WFR2137-P3 | FLM_EM | WFR2137 | Results: DOWN SITE HUB WFR2137-P3 WFR2137 Summary: Hub: WFR2137, Down Count: 1, Down Sites: WFR2137-P3 Alarm Summary: WFR2137 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 15:20:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000865 | PCM-20251026-00001669 | TT-20251026-01163 | Reference_telecom | Region_5 | MAK1U6993 | MAK6093 |  |  |  | Muhammad Sajjad | 10/26/2025 15:25:03 | 10/26/2025 15:25:03 | 10/26/2025 21:25:03 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MAK1U6993-G18-L21-SBTS-P1-VIP-HAJJ-HRM @ Sceco | 10/26/2025 10:52:17 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 10:50:02 | VIP | 4G | makkah | Sceco | LTE NSA | MAK1U6993 | FLM_TE |  |  | PCM-20251026-00001358 | Dear FLM team, Airscale port flapping at site | Dear FLM team, Airscale port flapping at site |  |  |  | API | 10/26/2025 15:25:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000866 | PCM-20251026-00001672 | TT-20251026-01224 | Reference_telecom | Region_5 | MAK0989 | MAK0989 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 15:25:20 | 10/26/2025 15:25:20 | 10/27/2025 03:25:20 | BASE STATION CONNECTIVITY PROBLEM (S1 SCTP path failure) at MAK0989-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 13:18:49 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 13:18:39 | P3 | 2G | makkah | Sceco | 2G NSA | MAK0989 | FLM_TE |  |  | PCM-20251026-00001382 | Dear FLM team, Airscale port flapping at site | Dear FLM team, Airscale port flapping at site |  |  |  | API | 10/26/2025 15:25:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000868 | PCM-20251026-00001673 | TT-20251026-01661 | Reference_telecom | [7 empty] | 10/26/2025 15:25:28 | 10/26/2025 15:25:28 | 10/27/2025 03:25:28 | ETH_LOS at RIY2822_NE_1_V @ Generator_DG | 10/26/2025 11:25:25 | Minor | 1-235 | ETH_LOS | 10/26/2025 11:25:15 | VIP | SRAN |  | Generator_DG | TX NSA | RIY2822 | FLM_TE | [8 empty] | API | 10/26/2025 15:25:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000870 | PCM-20251026-00001674 | TT-20251026-01263 | Reference_telecom | Region_6 | JEC1M7318 | JEC0318 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/26/2025 15:26:10 | 10/26/2025 20:22:42 | 10/26/2025 21:26:10 | BASE STATION CONNECTIVITY PROBLEM (S1 SCTP path failure) at JEC1M7318-VIP-CA-L800 @ Generator_SG | 10/26/2025 13:38:31 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 13:37:46 | VIP | 4G | baish | Generator_SG | LTE NSA | JEC1M7318 | FLM_TE |  |  | PCM-20251026-00001384 | Dear FLM team, Airscale port flapping at site | Dear FLM team, Airscale port flapping at site |  |  |  | API | 10/26/2025 15:26:10 | 10/26/2025 20:21:17 | 10/26/2025 20:22:10 |  |  | 10/26/2025 20:22:42 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000873 | PCM-20251026-00001682 | TT-20251026-01670 | Telecom | Region_4 | JED0766 | JED0766 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 15:31:59 | 10/26/2025 17:17:08 | 10/26/2025 21:31:59 | PT:: FLM Need to perform HC at JED0766 under R4 | 10/26/2025 15:31:45 | Major | 676767671 | Health Check-WO to TE FME | 10/26/2025 15:31:45 | VIP | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0766 | FLM_TE | [8 empty] | API | 10/26/2025 15:31:59 | 10/26/2025 17:17:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000877 | PCM-20251026-00001688 | TT-20251026-01677 | Telecom | Region_6 | KMS0474 | KMS0474 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 15:35:16 | 10/26/2025 19:11:01 | 10/26/2025 21:35:16 | PT::: As Per BO request need FLM to do HC in KMS0474,KMS0133,ABH0327 /R6 | 10/26/2025 15:34:54 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/26/2025 15:34:54 | P3 | 2G | khamis mushyet | Sceco | 2G_3G_LTE_5G NSA | KMS0474,KMS0133,ABH0327 | FLM_TE | [8 empty] | API | 10/26/2025 15:35:16 | 10/26/2025 16:47:29 | 10/26/2025 19:10:43 |  |  | 10/26/2025 19:11:01 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000878 | PCM-20251026-00001689 | TT-20251026-01678 | Reference_EM | Region_3 | HLUL2425 | HLUL2425 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 15:35:48 | 10/27/2025 07:11:11 | 10/27/2025 03:35:48 | NETECO: Mains Failure at HLUL2425 @ Generator_SG | 10/26/2025 15:29:42 | Minor | 1550 | Mains Failure | 10/26/2025 15:29:42 | P3 | SRAN | hail | Generator_SG | 2G NSA | HLUL2425 | FLM_EM | [8 empty] | API | 10/26/2025 15:35:48 | 10/27/2025 07:11:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000879 | PCM-20251026-00001691 | TT-20251026-01681 | Telecom | Region_6 | JDS1M7162 | JDS0162 | Equipment | SFP_BTS | Clean SFP | Osama Hadi | 10/26/2025 15:37:37 | 10/27/2025 03:41:23 | 10/26/2025 21:37:37 | PT::: As Per BO request need FLM to do HC in JDS1M7162/R6 | 10/26/2025 15:37:10 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/26/2025 15:37:10 | P1 | 4G | jizan | Sceco | 2G_3G_LTE_5G NSA | JDS1M7162 | FLM_TE | [8 empty] | API | 10/26/2025 15:37:37 | 10/26/2025 22:04:46 | 10/26/2025 22:09:52 | 10/26/2025 22:09:57 | 10/26/2025 22:29:26 | 10/27/2025 03:41:23 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000880 | PCM-20251026-00001693 | TT-20251026-01684 | Reference_EM | Region_3 | HLUL2425 | HLUL2425 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 15:39:57 | 10/27/2025 07:11:12 | 10/27/2025 03:39:57 | Mains Failure at HLUL2425-P3_SRAN @ Generator_SG | 10/26/2025 15:29:48 | Minor | 65109 | Mains Failure | 10/26/2025 15:29:45 | P3 | SRAN | hail | Generator_SG | 2G NSA | HLUL2425 | FLM_EM | [8 empty] | API | 10/26/2025 15:39:57 | 10/27/2025 07:11:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000882 | PCM-20251026-00001699 | TT-20251026-01679 | Telecom | Region_4 | JED0792 | JED0792 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 15:46:46 | 10/27/2025 04:33:38 | 10/26/2025 19:46:46 | 1(2G) 1(LTE) 2(5G) sites down under JED6175-GSM-P3,JED0792-P1-DIA @ Sceco | 10/26/2025 15:34:17 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 15:32:29 | P1 | 2G | jeddah | Sceco | LTE_5G SA | JED0792-NR2.6-P2 5G,JED6175-CA-P3 LTE | FLM_TE | JED0792 | DOWN SITE HUB TX FB JED0792 JED0792 Link flapping at HUB JED6175 JED6175 LAN link LOS at HUB | PCM-20251026-00001695 | DOWN SITE HUB TX FB JED0792 JED0792 Link flapping at HUB JED6175 JED6175 LAN link LOS at HUB | DOWN SITE HUB TX FB JED0792 JED0792 Link flapping at HUB JED6175 JED6175 LAN link LOS at HUB |  | sites down |  | API | 10/26/2025 15:46:46 | 10/26/2025 18:15:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000884 | PCM-20251026-00001701 | TT-20251026-01693 | EM | [7 empty] | 10/26/2025 15:50:29 | 10/26/2025 15:50:29 | 10/26/2025 21:50:29 | 1(2G/LTE) sites down under MKMD2562-P3-CAP/R3_MD_HWBSC01 @ Generator_DG | 10/26/2025 15:42:02 | Major | 21825 | CSL Fault | 10/26/2025 15:41:59 | P3 | 2G |  | Generator_DG | 2G_LTE SA | MKMD2562-P3-CAP | FLM_EM | MKMD2562 | Results: DOWN SITE HUB MKMD2562-P3-CAP MKMD2562 Summary: Hub: MKMD2562, Down Count: 1, Down Sites: MKMD2562-P3-CAP Alarm Summary: MKMD2562 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 15:50:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000886 | PCM-20251026-00001708 | TT-20251026-01702 | Telecom | Region_1 | HFF0490 | HFF0490 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 15:54:56 | 10/26/2025 18:32:48 | 10/26/2025 21:54:56 | NR Cell Unavailable at HFF0490-P2_SRAN @ Sceco | 10/26/2025 15:48:26 | Major | 29841 | NR Cell Unavailable | 10/26/2025 15:46:52 | P2 | SRAN | hafouf | Sceco | 5G SA | HFF0490 | FLM_TE | [8 empty] | API | 10/26/2025 15:54:56 | 10/26/2025 18:32:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000887 | PCM-20251026-00001709 | TT-20251022-01456 | Reference_telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | BTS_Cable | Replace CPRI Cable | Fawad Khan | 10/26/2025 15:55:00 | 10/26/2025 18:31:02 | 10/27/2025 03:55:00 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/22/2025 13:53:58 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:53:49 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251026-00001705 | Approved | Approved |  |  |  | API | 10/26/2025 15:55:00 | 10/26/2025 18:29:50 | 10/26/2025 18:30:40 |  |  | 10/26/2025 18:31:02 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000889 | PCM-20251026-00001712 | TT-20251026-01704 | Telecom | Region_5 | MAK1M9678 | MAK0678 |  |  |  | Mosab Nasr eldeen Mohamed | 10/26/2025 15:56:29 | 10/26/2025 15:56:29 | 10/27/2025 03:56:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9678-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/26/2025 15:55:44 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 15:55:34 | P3 | 4G | makkah | Generator_SG | 5G_Cell SA | MAK1M9678 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 15:56:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000890 | PCM-20251026-00001714 | TT-20251026-01696 | Reference_telecom | Region_4 | JED1MN0775 | JED0775 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 15:56:36 | 10/26/2025 15:56:36 | 10/26/2025 21:56:36 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0775-NR2.6-P2 @ Sceco | 10/26/2025 11:46:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 11:46:36 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0775 | FLM_TE |  |  | PCM-20251026-00001698 | Kindly perform HC on site and clean FAN unit and check for any blockage of air | Kindly perform HC on site and clean FAN unit and check for any blockage of air |  |  |  | API | 10/26/2025 15:56:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000891 | PCM-20251026-00001715 | TT-20251026-01646 | Reference_telecom | Region_6 | KMS1M7064 | KMS0064 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/26/2025 15:56:51 | 10/26/2025 16:50:01 | 10/26/2025 21:56:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KMS1M7064-CA-L800 @ Sceco | 10/26/2025 13:29:57 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 13:21:59 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M7064 | FLM_TE |  |  | PCM-20251026-00001664 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/26/2025 15:56:51 | 10/26/2025 16:49:37 | 10/26/2025 16:49:44 | 10/26/2025 16:49:46 |  | 10/26/2025 16:50:01 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000892 | PCM-20251026-00001716 | TT-20251026-01707 | Reference_telecom | Region_6 | TNM0727 | TNM0727 |  |  |  | Fawad Khan | 10/26/2025 15:56:59 | 10/26/2025 18:29:50 | 10/27/2025 03:56:59 | DemFail observed in TNM0727_02 towards 10.221.247.85 @ Sceco | 10/26/2025 03:57:48 | Minor |  | DemFail | 10/26/2025 03:56:51 | P2 | 2G | mohail | Sceco | TX NSA | TNM0727 | FLM_TE | [8 empty] | API | 10/26/2025 15:56:59 | 10/26/2025 18:29:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000893 | PCM-20251026-00001717 | TT-20251026-01668 | Telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 15:57:09 | 10/26/2025 15:57:09 | 10/27/2025 03:57:09 | BASE STATION ANTENNA LINE PROBLEM at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/26/2025 15:23:07 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 15:23:00 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0296 | FLM_TE |  |  | PCM-20251026-00001679 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/26/2025 15:57:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000894 | PCM-20251026-00001718 | TT-20251026-01698 | Telecom | Region_6 | NJR6011 | NJR6011 |  |  |  | Habib Ahmed | 10/26/2025 15:57:27 | 10/27/2025 02:22:10 | 10/26/2025 19:57:27 | 5(2G) 5(3G) 5(LTE) 5(5G) sites down under NJR6011-P3 @ Generator_SG | 10/26/2025 15:46:43 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 15:46:39 | P3 | 2G | najran | Generator_SG | 2G_3G_LTE_5G SA | NJR6016-P3 2G_3G_LTE_5G,NJR6013-P3 2G_3G_LTE_5G,NJR6018-P3 2G_3G_LTE_5G,NJR6011-P3 2G_3G_LTE_5G,NJR6014-P3 2G_3G_LTE_5G | FLM_TE | NJR6011 | Dear Team, HUB: NJR6011 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. | PCM-20251026-00001706 | Dear Team, HUB: NJR6011 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. | Dear Team, HUB: NJR6011 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. |  | sites down |  | API | 10/26/2025 15:57:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000895 | PCM-20251026-00001719 | TT-20251026-01664 | Reference_telecom | Region_6 | SHQ1M7183 | SHQ0183 | Equipment | BTS_Cable | Replace Fiber Cable | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 15:57:38 | 10/27/2025 04:36:46 | 10/26/2025 21:57:38 | CELL OPERATION DEGRADED (Failure in optical interface) at SHQ1M7183-P3 @ Sceco | 10/26/2025 15:19:18 | Major | 7654 | CELL OPERATION DEGRADED | 10/26/2025 15:19:02 | P3 | 4G | derb | Sceco | LTE_Cell SA | SHQ1M7183 | FLM_TE |  |  | PCM-20251026-00001675 | Check the Fiber optical alarm active at site | Check the Fiber optical alarm active at site |  |  |  | API | 10/26/2025 15:57:38 | 10/26/2025 17:04:50 | 10/27/2025 02:37:27 | 10/27/2025 02:37:31 | 10/27/2025 02:37:40 | 10/27/2025 04:36:46 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000896 | PCM-20251026-00001721 | TT-20251026-01713 | Telecom | Region_2 | RIY2M7435 | RIY0435 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Khan zeb Shah nawaz | 10/26/2025 16:00:45 | 10/26/2025 16:29:30 | 10/26/2025 22:00:45 | Cell Unavailable at RIY2M7435-P2-L800-L900 @ Sceco | 10/26/2025 15:59:31 | Major | 29240 | Cell Unavailable | 10/26/2025 15:58:16 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7435 | FLM_TE | [8 empty] | API | 10/26/2025 16:00:45 | 10/26/2025 16:09:43 | 10/26/2025 16:28:50 |  |  | 10/26/2025 16:29:30 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20251026000897 | PCM-20251026-00001724 | TT-20251026-01715 | Telecom | Region_2 | MJM0495 | MJM0495 |  |  |  | Adil Mehboob | 10/26/2025 16:02:09 | 10/26/2025 20:00:57 | 10/26/2025 20:02:09 | OSC_LOS at MJM0495_OCS @ Sceco_STB | 10/26/2025 16:02:01 | Critical | 1-12843 | OSC_LOS | 10/26/2025 16:01:48 | P1 | SRAN | majma | Sceco_STB | DWDM NSA | MJM0495 | FLM_TE | [5 empty] | 0-TO RPTRA-SEC0008(1-A)-12-G2AST4-4(RM4/TM4(TO ZLF0510_OCS, G6WDAPXF(1-B12)-RM1/TM1))-OSC:1 |  |  | API | 10/26/2025 16:02:09 | 10/26/2025 18:44:21 | 10/26/2025 18:49:55 | 10/26/2025 18:50:22 | 10/26/2025 18:50:59 | 10/26/2025 20:00:57 |  | Adil Mehboob |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000898 | PCM-20251026-00001727 | TT-20251026-01710 | EM | [7 empty] | 10/26/2025 16:02:34 | 10/26/2025 16:02:34 | 10/26/2025 22:02:34 | 1(2G/LTE) sites down under AHT2424-P3-CAP/R3_HL_HWBSC01 @ Generator_DG | 10/26/2025 15:54:29 | Major | 21825 | CSL Fault | 10/26/2025 15:54:26 | P3 | 2G |  | Generator_DG | 2G_LTE SA | AHT2424-P3-CAP | FLM_EM | AHT2424 | Results: DOWN SITE HUB AHT2424-P3-CAP AHT2424 Summary: Hub: AHT2424, Down Count: 1, Down Sites: AHT2424-P3-CAP Alarm Summary: AHT2424 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 16:02:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20251026000899 | PCM-20251026-00001728 | TT-20251026-01716 | Telecom | Region_2 | ZLF0510 | ZLF0510 |  |  |  | Yousaf Khan | 10/26/2025 16:02:40 | 10/26/2025 20:07:39 | 10/26/2025 20:02:40 | OSC_LOS at ZLF0510_OCS @ Sceco_STB | 10/26/2025 16:02:15 | Critical | 1-12843 | OSC_LOS | 10/26/2025 16:01:48 | P1 | SRAN | buraidah | Sceco_STB | DWDM NSA | ZLF0510 | FLM_TE | [5 empty] | 0-TO MJM0495(1-A)-10-G2AST4-3(RM3/TM3(TO MJM0495_OCS, G6WDAPXF(1-A02)-RM4/TM4))-OSC:1 |  |  | API | 10/26/2025 16:02:40 | 10/26/2025 18:51:48 | 10/26/2025 18:54:27 | 10/26/2025 18:55:42 | 10/26/2025 18:56:38 | 10/26/2025 20:07:39 |  | Yousaf Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000900 | PCM-20251026-00001732 | TT-20251026-01724 | EM | Region_4 | JDRS1M8225 | JDRS2225 |  |  |  | Farag Ahmed Taha Mohamed | 10/26/2025 16:06:17 | 10/27/2025 06:10:44 | 10/27/2025 04:06:17 | RECTIFIER MALOR ALARM at JDRS1M8225-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 15:57:54 | Minor | 7103 | RECTIFIER MALOR ALARM | 10/26/2025 15:57:46 | P3 | 4G | jeddah | Sceco | LTE NSA | JDRS1M8225 | FLM_EM | [5 empty] | RECTIFIER MALOR ALARM |  |  | API | 10/26/2025 16:06:17 | 10/27/2025 06:10:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000901 | PCM-20251026-00001733 | TT-20251026-01725 | Telecom | [7 empty] | 10/26/2025 16:07:50 | 10/26/2025 16:07:50 | 10/27/2025 04:07:50 | ALD Maintenance Link Failure at RIY2459-P3_SRAN @ Sceco | 10/26/2025 16:04:50 | Minor | 26541 | ALD Maintenance Link Failure | 10/26/2025 16:03:27 | P3 | SRAN |  | Sceco | 2G NSA | RIY2459 | FLM_TE | [8 empty] | API | 10/26/2025 16:07:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000902 | PCM-20251026-00001735 | TT-20251026-01727 | EM | Region_6 | BSR0025 | BSR0025 |  |  |  | Sohail Nasir Mir Afzal | 10/26/2025 16:08:22 | 10/26/2025 16:08:22 | 10/27/2025 04:08:22 | HIGH TEMPERATURE 32 DEGREE C at BSR0025-G9-NL8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 16:00:14 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/26/2025 16:00:02 | P2 | 2G | Albaha | Sceco | 2G NSA | BSR0025 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/26/2025 16:08:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000903 | PCM-20251026-00001736 | TT-20251026-01728 | Telecom | Region_1 | JBL0468 | JBL0468 | Equipment | SFP_BTS | Clean SFP | Tahir Mahmood Hafiz Yar | 10/26/2025 16:08:22 | 10/26/2025 18:19:59 | 10/27/2025 04:08:22 | RF Unit Maintenance Link Failure at JBL0468-P2_SRAN @ Sceco | 10/26/2025 16:04:22 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 16:03:16 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0468 | FLM_TE | [8 empty] | API | 10/26/2025 16:08:22 | 10/26/2025 17:10:12 | 10/26/2025 17:49:40 | 10/26/2025 17:49:43 | 10/26/2025 17:49:45 | 10/26/2025 18:19:59 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000905 | PCM-20251026-00001740 | TT-20251026-01731 | EM | [7 empty] | 10/26/2025 16:08:52 | 10/26/2025 16:08:52 | 10/27/2025 04:08:52 | NETECO: Door Status Sensor Alarm at YNB2095 @ Generator_DG | 10/26/2025 16:08:42 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 16:08:42 | P3 | SRAN |  | Generator_DG | 2G NSA | YNB2095 | FLM_EM | [8 empty] | API | 10/26/2025 16:08:52 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000906 | PCM-20251026-00001741 | TT-20251026-01733 | EM | Region_4 | JIR1M9354 | JIR0354 |  |  |  | Ragb Ahmed Mohamed Abdelazim | 10/26/2025 16:09:23 | 10/26/2025 16:09:23 | 10/27/2025 04:09:23 | RECTIFIER MAINS POWER FAILURE at JIR1M9354-G9-NL8-L21-SBTS-P2 @ Generator_DG | 10/26/2025 16:01:13 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 16:01:02 | VIP | 4G | taif | Generator_DG | LTE NSA | JIR1M9354 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 16:09:23 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000909 | PCM-20251026-00001749 | TT-20251026-01737 | Telecom | Region_1 | JBL0468 | JBL0468 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 16:11:27 | 10/26/2025 17:10:13 | 10/26/2025 22:11:27 | NR Cell Unavailable at JBL0468-P2_SRAN @ Sceco | 10/26/2025 16:04:38 | Major | 29841 | NR Cell Unavailable | 10/26/2025 16:03:04 | P2 | SRAN | jubail | Sceco | 5G SA | JBL0468 | FLM_TE | [8 empty] | API | 10/26/2025 16:11:27 | 10/26/2025 17:10:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000912 | PCM-20251026-00001762 | TT-20251026-01751 | Telecom | Region_6 | BAH1MC0005 | BAH0005 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/26/2025 16:16:06 | 10/26/2025 17:43:33 | 10/26/2025 20:16:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at BAH1MC0005-NR3.5-P1-VIP-SHOP-HUB-DWDM @ Sceco_STB | 10/26/2025 16:15:22 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 16:15:15 | VIP | 5G | Albaha | Sceco_STB | 5G_Cell SA | BAH1MC0005 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 16:16:06 | 10/26/2025 17:41:08 | 10/26/2025 17:42:41 |  |  | 10/26/2025 17:43:33 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000913 | PCM-20251026-00001763 | TT-20251026-01745 | EM | Region_6 | ARF0186 | ARF0186 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/26/2025 16:18:29 | 10/26/2025 19:25:06 | 10/26/2025 22:18:29 | 1(2G/3G/5G) sites down under ARF0186-P2/ARF0186-P2 @ Sceco | 10/26/2025 16:10:25 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 16:10:19 | P2 | 2G | al harja | Sceco | 2G_3G_5G SA | ARF0186-P2 | FLM_EM | ARF0186 | Results: DOWN SITE HUB ARF0186-P2 ARF0186 Summary: Hub: ARF0186, Down Count: 1, Down Sites: ARF0186-P2 Alarm Summary: ARF0186 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 16:18:29 | 10/26/2025 19:25:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000914 | PCM-20251026-00001764 | TT-20251026-01748 | EM | [7 empty] | 10/26/2025 16:19:59 | 10/26/2025 16:19:59 | 10/26/2025 22:19:59 | 1(2G/LTE) sites down under YNB2095-P3-CAP/YB1MBSCH01 @ Generator_DG | 10/26/2025 16:11:57 | Major | 21825 | CSL Fault | 10/26/2025 16:11:55 | P3 | 2G |  | Generator_DG | 2G_LTE SA | YNB2095-P3-CAP | FLM_EM | YNB2095 | Results: DOWN SITE HUB YNB2095-P3-CAP YNB2095 Summary: Hub: YNB2095, Down Count: 1, Down Sites: YNB2095-P3-CAP Alarm Summary: YNB2095 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 16:19:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000915 | PCM-20251026-00001767 | TT-20251026-01766 | EM | Region_6 | KHNJ1M8241 | KHNJ2241 | Enviroment | SCECO_Failure | SCECO auto restored | Irfan Yousaf | 10/26/2025 16:21:48 | 10/26/2025 20:47:41 | 10/27/2025 04:21:48 | AIRCON 1 FAILURE at KHNJ1M8241-CA-L800-P3-SBTS @ Sceco | 10/26/2025 16:13:36 | Minor | 7103 | AIRCON 1 FAILURE | 10/26/2025 16:13:25 | P3 | 4G | al harja | Sceco | LTE NSA | KHNJ1M8241 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/26/2025 16:21:48 | 10/26/2025 16:23:11 | 10/26/2025 20:47:21 |  |  | 10/26/2025 20:47:41 |  | Irfan Yousaf |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000916 | PCM-20251026-00001768 | TT-20251026-01768 | EM | Region_6 | ARF0186 | ARF0186 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/26/2025 16:23:20 | 10/26/2025 19:25:07 | 10/27/2025 04:23:20 | RECTIFIER MODULE FAILURE at ARF0186-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 16:17:35 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 16:15:12 | P2 | 2G | al harja | Sceco | 2G NSA | ARF0186 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 16:23:20 | 10/26/2025 19:25:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000917 | PCM-20251026-00001769 | TT-20251026-01769 | Telecom | Region_4 | JED1MN2602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 16:23:52 | 10/26/2025 17:32:50 | 10/26/2025 22:23:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2602-NR2.6-P3 @ Sceco | 10/26/2025 16:23:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 16:22:58 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2602 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 16:23:52 | 10/26/2025 17:32:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000920 | PCM-20251026-00001773 | TT-20251026-01774 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/26/2025 16:26:57 | 10/26/2025 16:33:15 | 10/27/2025 04:26:57 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/26/2025 16:20:17 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/26/2025 16:20:14 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/26/2025 16:26:57 | 10/26/2025 16:33:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000921 | PCM-20251026-00001776 | TT-20251026-01779 | Telecom | Region_4 | JED1M7225 | JED0225 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 16:28:30 | 10/26/2025 17:17:08 | 10/26/2025 22:28:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7225-CA-L900-L800-SBTS @ Sceco | 10/26/2025 16:27:33 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 16:27:27 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7225 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 16:28:30 | 10/26/2025 17:17:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000923 | PCM-20251026-00001778 | TT-20251026-01782 | EM | Region_6 | UKHA1M8371 | UKHA2371 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 16:29:32 | 10/26/2025 16:39:52 | 10/27/2025 04:29:32 | SHELTER DOOR OPEN at UKHA1M8371-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/26/2025 16:29:19 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 16:29:14 | P3 | 4G | Baha | Generator_DG | LTE NSA | UKHA1M8371 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 16:29:32 | 10/26/2025 16:39:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000924 | PCM-20251026-00001782 | TT-20251026-01790 | EM | [7 empty] | 10/26/2025 16:31:06 | 10/26/2025 16:31:06 | 10/27/2025 04:31:06 | NETECO: Door Status Sensor Alarm at WFR2135 @ Generator_SG | 10/26/2025 16:30:52 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 16:30:52 | P3 | SRAN |  | Generator_SG | 2G NSA | WFR2135 | FLM_EM | [8 empty] | API | 10/26/2025 16:31:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000926 | PCM-20251026-00001789 | TT-20251026-01807 | Telecom | Region_1 | JBL0465(JB1) | JB1 |  |  |  | Tahir Mahmood Hafiz Yar | 10/26/2025 16:35:42 | 10/26/2025 17:10:13 | 10/26/2025 22:35:42 | SALAM links down b/w RIY-DAM (ITCX-802A019) , RIYAD-JUBAIL (ITCX-802A022) and JUBAIL-HFR (ITCX-802A030) | 10/26/2025 16:30:14 | Major | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/26/2025 16:30:14 | P1 | DWDM | jubail | Sceco_STB_Rental | DWDM NSA | SALAM links down b/w(ITCX-802A030) | FLM_TE | [8 empty] | API | 10/26/2025 16:35:42 | 10/26/2025 17:10:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000927 | PCM-20251026-00001790 | TT-20251026-01808 | Reference_telecom | Region_4 | JED6010 | JED6010 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 16:35:44 | 10/26/2025 16:35:44 | 10/27/2025 04:35:44 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6010-DCU @ Sceco | 10/26/2025 13:35:40 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/26/2025 13:35:37 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6010 | FLM_TE | [8 empty] | API | 10/26/2025 16:35:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000928 | PCM-20251026-00001791 | TT-20251026-01809 | EM | [7 empty] | 10/26/2025 16:36:47 | 10/26/2025 16:36:47 | 10/27/2025 04:36:47 | NETECO: Phase L1 Undervoltage at MKMD2562 @ Generator_DG | 10/26/2025 16:30:23 | Minor | 1583 | Phase L1 Undervoltage | 10/26/2025 16:30:23 | P3 | SRAN |  | Generator_DG | 2G NSA | MKMD2562 | FLM_EM | [8 empty] | API | 10/26/2025 16:36:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000929 | PCM-20251026-00001792 | TT-20251026-01792 | EM | [7 empty] | 10/26/2025 16:36:59 | 10/26/2025 16:36:59 | 10/26/2025 22:36:59 | 1(2G/LTE) sites down under MDTB2555-P3-CAP/R3_MD_HWBSC02 @ Generator_SG | 10/26/2025 16:28:32 | Major | 21825 | CSL Fault | 10/26/2025 16:28:28 | P3 | 2G |  | Generator_SG | 2G_LTE SA | MDTB2555-P3-CAP | FLM_EM | MDTB2555 | Results: DOWN SITE HUB MDTB2555-P3-CAP MDTB2555 Summary: Hub: MDTB2555, Down Count: 1, Down Sites: MDTB2555-P3-CAP Alarm Summary: MDTB2555 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 16:36:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000930 | PCM-20251026-00001794 | TT-20251026-01812 | Reference_EM | [7 empty] | 10/26/2025 16:38:20 | 10/26/2025 16:38:20 | 10/27/2025 04:38:20 | NETECO: Phase L3 Undervoltage at MKMD2554 @ Generator_SG | 10/26/2025 16:31:58 | Minor | 1585 | Phase L3 Undervoltage | 10/26/2025 16:31:58 | P3 | SRAN |  | Generator_SG | 2G NSA | MKMD2554 | FLM_EM | [8 empty] | API | 10/26/2025 16:38:20 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000932 | PCM-20251026-00001801 | TT-20251026-01821 | Reference_EM | Region_1 | KFKM0786 | KFKM0786 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 16:43:30 | 10/26/2025 16:43:30 | 10/27/2025 04:43:30 | Mains Failure at KFKM0786-P2_SRAN @ Generator_SG | 10/26/2025 16:33:34 | Minor | 65109 | Mains Failure | 10/26/2025 16:33:30 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0786 | FLM_EM | [8 empty] | API | 10/26/2025 16:43:30 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000933 | PCM-20251026-00001803 | TT-20251026-01815 | Telecom | Region_6 | BCAL1M3714 | BCAL0714 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/26/2025 16:43:59 | 10/26/2025 17:44:46 | 10/26/2025 20:43:59 | 1(3G) sites down under BCAL0714-P1-HUB-WBB-G3/BCAL1M3714-P1-HUB-WBB-G3 @ Sceco_STB | 10/26/2025 16:36:25 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/26/2025 16:35:42 | P1 | 3G | bisha | Sceco_STB | 3G SA | BCAL0714-P1-HUB-WBB-G3 | FLM_TE | BCAL0714 | Results: DOWN SITE HUB BCAL0714-P1-HUB-WBB-G3 BCAL0714 Summary: Hub: BCAL0714, Down Count: 1, Down Sites: BCAL0714-P1-HUB-WBB-G3 Alarm Summary: BCAL0714 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 16:43:59 | 10/26/2025 17:44:22 | 10/26/2025 17:44:33 |  |  | 10/26/2025 17:44:46 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000934 | PCM-20251026-00001804 | TT-20251026-01823 | Reference_EM | Region_3 | MDQS2591 | MDQS2591 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/26/2025 16:44:00 | 10/26/2025 17:08:11 | 10/27/2025 04:44:00 | NETECO: AC Failure at MDQS2591-MS @ Generator_DG | 10/26/2025 16:37:40 | Minor | 10202 | AC Failure | 10/26/2025 16:37:40 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2591 | FLM_EM | [8 empty] | API | 10/26/2025 16:44:00 | 10/26/2025 17:08:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000935 | PCM-20251026-00001806 | TT-20251026-01825 | Reference_EM | Region_1 | HFSW2M2020 | HFSW2020 |  |  |  | Emad fawzi eldebsi | 10/26/2025 16:45:03 | 10/26/2025 16:45:03 | 10/26/2025 22:45:03 | Air-condition #2 failure alarm at HFSW2M2020-P1-HUB @ Generator_SG | 10/26/2025 16:35:03 | Major | 65105 | Air-condition #2 failure alarm | 10/26/2025 16:34:59 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFSW2M2020 | FLM_EM | [8 empty] | API | 10/26/2025 16:45:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000937 | PCM-20251026-00001809 | TT-20251026-01828 | Telecom | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 16:45:33 | 10/26/2025 16:45:33 | 10/27/2025 04:45:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 16:44:38 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 16:44:28 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2259 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 16:45:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026000936 | PCM-20251026-00001808 | TT-20251026-01829 | Telecom | Region_4 | THO0371 | THO0371 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 10/26/2025 16:45:33 | 10/26/2025 18:44:09 | 10/27/2025 04:45:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 16:44:45 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 16:44:41 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | THO0371 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 16:45:33 | 10/26/2025 18:24:18 | 10/26/2025 18:44:05 | 10/26/2025 18:44:07 | 10/26/2025 18:44:09 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000938 | PCM-20251026-00001811 | TT-20251026-01820 | Telecom | Region_4 | NSH1M7218 | NSH0218 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 16:46:03 | 10/27/2025 03:29:03 | 10/26/2025 22:46:03 | 1(LTE) sites down under NSH0218-USF-P3 @ Generator_SG | 10/26/2025 16:38:03 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 16:37:58 | P2 | 4G | adam | Generator_SG | LTE SA | NSH0218-USF-P3 | FLM_TE | NSH0218 | Results: DOWN SITE HUB NSH0218-USF-P3 NSH0218 Summary: Hub: NSH0218, Down Count: 1, Down Sites: NSH0218-USF-P3 Alarm Summary: NSH0218 No Active Alarm on HUB |  |  |  | No route to host [URL:http://10.88.15.252:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 16:46:03 | 10/26/2025 16:57:26 | 10/27/2025 03:28:53 |  |  | 10/27/2025 03:29:03 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000939 | PCM-20251026-00001812 | TT-20251026-01346 | EM | Region_3 | MDN2906 | MDN2906 | Enviroment | SCECO_Failure | SCECO auto restored | Ibrahim Mohammad AbdulMalik alraee | 10/26/2025 16:46:22 | 10/26/2025 21:49:56 | 10/26/2025 22:46:22 | 1(2G/3G/LTE/5G) sites down under MDN2906-P2/R3_MD_HWBSC02 @ Generator_SG | 10/26/2025 14:14:46 | Major | 21825 | CSL Fault | 10/26/2025 14:14:43 | P2 | SRAN | madinah | Generator_SG | 2G_3G_LTE SA | MDN2906-P2 | FLM_TE | MDN2906 | Results: DOWN SITE HUB MDN2906-P2 MDN2906 Summary: Hub: MDN2906, Down Count: 1, Down Sites: MDN2906-P2 Alarm Summary: MDN2906 No Active Alarm on HUB | PCM-20251026-00001394 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 16:46:22 | 10/26/2025 19:31:40 | 10/26/2025 21:49:45 |  |  | 10/26/2025 21:49:56 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000940 | PCM-20251026-00001817 | TT-20251026-01834 | Reference_EM | Region_3 | MDQS2591 | MDQS2591 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/26/2025 16:47:38 | 10/26/2025 17:08:12 | 10/27/2025 04:47:38 | Mains Failure at MDQS2591-P3_SRAN @ Generator_DG | 10/26/2025 16:37:47 | Minor | 65109 | Mains Failure | 10/26/2025 16:37:43 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2591 | FLM_EM | [8 empty] | API | 10/26/2025 16:47:38 | 10/26/2025 17:08:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000941 | PCM-20251026-00001819 | TT-20251026-01836 | MW_HC | Region_2 | RIY0338 | RIY0338 |  |  |  | Farmanullah Akbar Jan | 10/26/2025 16:48:12 | 10/27/2025 07:29:25 | 10/27/2025 04:48:12 | MW RTN Observing PM Errors and RSL degradation observed on MW link RIY0338-RIY0130 ( as per BO request ) | 10/26/2025 16:47:20 | Minor | 1-631 | MW_LOF | 10/26/2025 16:47:20 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0338 RIY0130 | FLM_TE | [5 empty] | MW RTN Observing PM Errors and RSL degradation observed on MW link RIY0338-RIY0130 ( as per BO request ) |  |  | API | 10/26/2025 16:48:12 | 10/27/2025 07:29:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000942 | PCM-20251026-00001820 | TT-20251026-01822 | EM | [7 empty] | 10/26/2025 16:48:59 | 10/26/2025 16:48:59 | 10/26/2025 22:48:59 | 1(2G/LTE) sites down under MKMD2554-P3-CAP/R3_MD_HWBSC01 @ Generator_SG | 10/26/2025 16:40:39 | Major | 21825 | CSL Fault | 10/26/2025 16:40:35 | P3 | 2G |  | Generator_SG | 2G_LTE SA | MKMD2554-P3-CAP | FLM_EM | MKMD2554 | Results: DOWN SITE HUB MKMD2554-P3-CAP MKMD2554 Summary: Hub: MKMD2554, Down Count: 1, Down Sites: MKMD2554-P3-CAP Alarm Summary: MKMD2554 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 16:48:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000943 | PCM-20251026-00001821 | TT-20251026-01837 | Reference_EM | Region_1 | HFB2M5659 | HFB0659 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/26/2025 16:49:10 | 10/26/2025 16:49:10 | 10/27/2025 04:49:10 | Door opening alarm at HFB2M5659-P3 @ Generator_SG | 10/26/2025 16:48:36 | Minor | 65101 | Door opening alarm | 10/26/2025 16:48:34 | P3 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5659 | FLM_EM | [8 empty] | API | 10/26/2025 16:49:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000944 | PCM-20251026-00001822 | TT-20251026-01838 | Reference_EM | [7 empty] | 10/26/2025 16:49:10 | 10/26/2025 16:49:10 | 10/27/2025 04:49:10 | NETECO: AC Failure at BDR2246 @ Sceco | 10/26/2025 16:42:41 | Minor | 10202 | AC Failure | 10/26/2025 16:42:41 | P3 | SRAN |  | Sceco | 2G NSA | BDR2246 | FLM_EM | [8 empty] | API | 10/26/2025 16:49:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000945 | PCM-20251026-00001825 | TT-20251026-01839 | EM | Region_4 | JD2_CORE | JD2 |  |  |  | Faheemuddin Syed Islamuddin | 10/26/2025 16:49:41 | 10/26/2025 16:49:41 | 10/26/2025 22:49:41 | DOOR OPEN ALARM at JD2_CORE-P1-VIP @ Sceco_STB | 10/26/2025 16:49:07 | Major | 7103 | DOOR OPEN ALARM | 10/26/2025 16:49:00 | P1 | 4G | jeddah | Sceco_STB | DWDM NSA | JD2_CORE | FLM_EM | [5 empty] | DOOR OPEN ALARM |  |  | API | 10/26/2025 16:49:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000946 | PCM-20251026-00001826 | TT-20251026-01764 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/26/2025 16:49:56 | 10/26/2025 22:28:18 | 10/27/2025 04:49:56 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/26/2025 16:13:09 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 16:13:02 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251026-00001765 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/26/2025 16:49:56 | 10/26/2025 22:28:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000948 | PCM-20251026-00001830 | TT-20251026-01841 | Telecom | Region_6 | DRB0165 | DRB0165 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 16:50:44 | 10/26/2025 17:06:30 | 10/27/2025 04:50:44 | ODU CPU / Cable Open at DRB0165-IDU on 10.154.164.54 @ Sceco_STB | 10/26/2025 16:49:50 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/26/2025 16:49:34 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0165 | FLM_TE | [8 empty] | API | 10/26/2025 16:50:44 | 10/26/2025 17:04:51 | 10/26/2025 17:06:19 |  |  | 10/26/2025 17:06:30 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000949 | PCM-20251026-00001832 | TT-20251026-01819 | Telecom | Region_4 | NNL0102 | NNL0102 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 16:51:14 | 10/27/2025 03:28:42 | 10/26/2025 22:51:14 | 2(5G) sites down under YLM2368-GSM-UMTS-P3,NNL0102-GSM-P2-USF @ Generator_DG | 10/26/2025 16:38:03 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 16:37:58 | P1 | 2G | alaith | Generator_DG | 5G SA | NNL0102-GSM-P2-USF 5G,YLM2368-GSM-UMTS-P3 5G | FLM_TE | NNL0102 | DOWN SITE HUB TX FB NNL0102 NNL0102 Visibility Down at HUB YLM2368 YLM2368 Visibility Down at HUB | PCM-20251026-00001810 | DOWN SITE HUB TX FB NNL0102 NNL0102 Visibility Down at HUB YLM2368 YLM2368 Visibility Down at HUB | DOWN SITE HUB TX FB NNL0102 NNL0102 Visibility Down at HUB YLM2368 YLM2368 Visibility Down at HUB |  | sites down |  | API | 10/26/2025 16:51:14 | 10/26/2025 16:57:26 | 10/27/2025 03:28:26 |  |  | 10/27/2025 03:28:42 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026000951 | PCM-20251026-00001835 | TT-20251026-00346 | Telecom | Region_4 | BHR1M7308 | BHR0308 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 16:51:36 | 10/26/2025 20:26:53 | 10/26/2025 22:51:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR1M7308-P1-HUB-CA-L800-SBTS @ Sceco | 10/26/2025 05:19:11 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 05:19:03 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | BHR1M7308 | FLM_TE |  |  | PCM-20251026-00001828 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/26/2025 16:51:36 | 10/26/2025 18:15:42 | 10/26/2025 20:26:43 | 10/26/2025 20:26:48 | 10/26/2025 20:26:53 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000952 | PCM-20251026-00001837 | TT-20251026-01845 | EM | Region_4 | HLA1M8439 | HLA2439 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/26/2025 16:52:15 | 10/26/2025 16:52:15 | 10/27/2025 04:52:15 | LOW FUEL at HLA1M8439-G9-L8-L18-L21-SBTS @ Sceco | 10/26/2025 16:44:09 | Minor | 7103 | LOW FUEL | 10/26/2025 16:43:59 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8439 | FLM_EM | [5 empty] | LOW FUEL |  |  | API | 10/26/2025 16:52:15 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000954 | PCM-20251026-00001840 | TT-20251026-01351 | Telecom | Region_4 | JED1M7085 | JED0085 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 16:52:36 | 10/26/2025 17:17:09 | 10/26/2025 22:52:36 | BASE STATION HARDWARE PROBLEM (RX Power too low) at JED1M7085-CA-L900-L800-SBTS @ Sceco | 10/26/2025 14:13:28 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/26/2025 14:13:18 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7085 | FLM_TE |  |  | PCM-20251026-00001390 | FLM need to check RX power and HW. Need to Perform HC at site.. | FLM need to check RX power and HW. Need to Perform HC at site.. |  |  |  | API | 10/26/2025 16:52:36 | 10/26/2025 17:17:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000958 | PCM-20251026-00001855 | TT-20251026-01859 | EM | [7 empty] | 10/26/2025 17:01:35 | 10/26/2025 17:01:35 | 10/27/2025 05:01:35 | NETECO: Door Status Sensor Alarm at BDR2246 @ Sceco | 10/26/2025 17:01:28 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 17:01:28 | P3 | SRAN |  | Sceco | 2G NSA | BDR2246 | FLM_EM | [8 empty] | API | 10/26/2025 17:01:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000959 | PCM-20251026-00001857 | TT-20251026-01860 | Reference_EM | [7 empty] | 10/26/2025 17:02:05 | 10/26/2025 17:02:05 | 10/27/2025 05:02:05 | Door opening alarm at BDR2246-P3_SRAN @ Sceco | 10/26/2025 17:01:37 | Minor | 65101 | Door opening alarm | 10/26/2025 17:01:31 | P3 | SRAN |  | Sceco | 2G NSA | BDR2246 | FLM_EM | [8 empty] | API | 10/26/2025 17:02:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000960 | PCM-20251026-00001859 | TT-20251026-01861 | Telecom | Region_6 | ABBS1M7153 | ABBS0153 |  |  |  | Manzoor Ahmed | 10/26/2025 17:02:26 | 10/26/2025 17:27:24 | 10/26/2025 23:02:26 | PT::: As Per BO request need FLM to do HC in 26 sites/R6 | 10/26/2025 17:02:03 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/26/2025 17:02:03 | P3 | 4G | Albaha | Sceco | 2G_3G_LTE_5G NSA | ABBS1M7153-L800-CA-SBTS-P3-WBB-G3,KMS1M7035-CA-L800,ARS1M8049-CA-L800-P3,JEC1M7286-CA-L800-VIP-P1,ABH1M7169-NCA,ARS1M8049-CA-L800-P3,BLJ1M7053-P3-CA,JEC1M7313-P1-VIP-CA-L800,SBA1M8020-P2-NCA-L800-L2100-SBTS,ABBS1M8161-CA-L800-L900-SBTS-P3-WBB-G3,ABH1M7188-P3-L800,ABH1M7137-P2-CA-L800,SAB1M7054-P2-CA-L800,SUL1M7560-USF-NCA-L800-SBTS,JEC1M7313-P1-VIP-CA-L800,SBA1M8020-P2-NCA-L800-L2100-SBTS,BAH1M7007-CA-L800-P2,BSH1M7034-P3-CA-L800,BSH1M7897-P3-CA,BLUL1M7715-P3-CA-L800-WBB-G3,ABH1M7282-P3-CA-L800,KMS1M7091-CA-L800,ABH1M7027-P1-CA-L800-VIP,WDN1M7187-USF-P3-CA,ZHR1M7138-USF-CA-L800,SBBG1M7045-CA-L800-P1-VIP | FLM_TE | [8 empty] | API | 10/26/2025 17:02:26 | 10/26/2025 17:27:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000961 | PCM-20251026-00001860 | TT-20251026-01862 | Telecom | Region_6 | KMS1MN0474 | KMS0474 | Equipment | BSS_HW_Stuck | Reset RRU | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 17:02:36 | 10/26/2025 20:56:45 | 10/26/2025 23:02:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS1MN0474-NR2.6 @ Sceco | 10/26/2025 17:01:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 17:01:48 | P3 | 5G | khamis mushyet | Sceco | 5G_Cell SA | KMS1MN0474 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 17:02:36 | 10/26/2025 20:56:07 | 10/26/2025 20:56:36 |  |  | 10/26/2025 20:56:45 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000962 | PCM-20251026-00001861 | TT-20251026-01864 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/26/2025 17:03:08 | 10/26/2025 17:03:08 | 10/26/2025 23:03:08 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/26/2025 16:59:24 | Major | 1-12545 | LOCAL_FAULT | 10/26/2025 16:59:14 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE | [5 empty] | 1-ELC(1-E)-2-G1M520S-9(RX7/TX7)-CLIENT:1 |  |  | API | 10/26/2025 17:03:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000964 | PCM-20251026-00001864 | TT-20251026-01867 | Reference_EM | Region_1 | DAM0416 | DAM0416 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/26/2025 17:04:41 | 10/26/2025 17:04:41 | 10/27/2025 05:04:41 | Air condition 1 failure alarm at DAM0416-P2_SRAN @ Sceco | 10/26/2025 16:54:18 | Minor | 65104 | Air condition 1 failure alarm | 10/26/2025 16:54:14 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0416 | FLM_EM | [8 empty] | API | 10/26/2025 17:04:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000965 | PCM-20251026-00001867 | TT-20251023-01170 | Reference_telecom | Region_4 | RAB0719 | RAB0719 |  |  |  | Khizer Hayat | 10/26/2025 17:05:13 | 10/26/2025 22:28:19 | 10/27/2025 05:05:13 | FanFailure observed in RAB0719_01 towards 10.21.72.210 @ Sceco | 10/23/2025 01:00:08 | Minor |  | FanFailure | 10/23/2025 00:59:41 | P2 | 2G | jeddah | Sceco | TX NSA | RAB0719 | FLM_TE |  |  | PCM-20251026-00001668 | Dear FLM team, approved | Dear FLM team, approved |  |  |  | API | 10/26/2025 17:05:13 | 10/26/2025 22:28:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000966 | PCM-20251026-00001868 | TT-20251026-01868 | Reference_EM | Region_1 | RYHF2M2064 | RYHF2064 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/26/2025 17:06:13 | 10/26/2025 17:06:13 | 10/27/2025 05:06:13 | Mains Failure at RYHF2M2064-P3 @ Generator_SG | 10/26/2025 16:56:34 | Minor | 65109 | Mains Failure | 10/26/2025 16:56:30 | P3 | 2G | hafouf | Generator_SG | 2G NSA | RYHF2M2064 | FLM_EM | [8 empty] | API | 10/26/2025 17:06:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000967 | PCM-20251026-00001869 | TT-20251026-01875 | EM | Region_6 | KHNJ1M7855 | KHNJ0855 |  |  |  | Muhammad Shafeeq Muhammad Rafeeq | 10/26/2025 17:07:47 | 10/26/2025 23:13:39 | 10/27/2025 05:07:47 | HIGH TEMPERATURE 32 DEGREE C at KHNJ1M7855-L800-P3 @ Sceco | 10/26/2025 16:59:30 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/26/2025 16:59:23 | P3 | 4G | najran | Sceco | LTE NSA | KHNJ1M7855 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/26/2025 17:07:47 | 10/26/2025 23:13:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000968 | PCM-20251026-00001871 | TT-20251026-01877 | Reference_telecom | Region_5 | MAK6183 | MAK6083 | Equipment | SFP_BTS | Replace SFP | KAMRAN AAMIR | 10/26/2025 17:08:28 | 10/26/2025 19:26:56 | 10/27/2025 05:08:28 | PT::FLM need to perform HC at MAK6183-P1-HRM (BO request) | 10/26/2025 17:08:11 | Minor | 676767671 | Health Check-WO to TE FME | 10/26/2025 17:08:11 | P1 | 2G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK6183-P1-HRM | FLM_TE | [8 empty] | API | 10/26/2025 17:08:28 |  | 10/26/2025 17:58:04 | 10/26/2025 17:58:08 |  | 10/26/2025 19:26:56 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000969 | PCM-20251026-00001878 | TT-20251008-01738 | MW_HC | Region_1 | SLW0915 | SLW0915 |  |  |  | Mohamed Magdy Fouad Zayed | 10/26/2025 17:11:28 | 10/26/2025 17:56:58 | 10/27/2025 05:11:28 | Huawei MW HC_P2 Observing Errors at SLW0915-SLW0913 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | hafouf | Power Cube | TX NSA | SLW0915-SLW0913 | FLM_TE | SLW0915 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251026-00001865 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/26/2025 17:11:28 | 10/26/2025 17:56:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000970 | PCM-20251026-00001879 | TT-20251019-02105 | MW_HC | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 17:12:03 | 10/26/2025 17:48:41 | 10/27/2025 05:12:03 | NEC MW HC_P1 Observing Performance Issue at DMH0104(10.159.105.138)--DMH0606(10.159.105.140) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104(10.159.105.138)--DMH0606(10.159.105.140) | FLM_TE | DMH0104 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251026-00001876 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/26/2025 17:12:03 | 10/26/2025 17:48:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000971 | PCM-20251026-00001884 | TT-20251026-01891 | Reference_telecom | Region_5 | MAK0642 | MAK0642 | Equipment | SFP_BTS | Replace SFP | Inam ullah | 10/26/2025 17:13:34 | 10/26/2025 18:54:08 | 10/27/2025 05:13:34 | PT::FLM need to perform HC at MAK0642-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 (BO request) | 10/26/2025 17:13:23 | Minor | 676767671 | Health Check-WO to TE FME | 10/26/2025 17:13:23 | P2 | 2G | makkah | Generator_SG | 2G_3G_LTE_5G NSA | MAK0642-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | [8 empty] | API | 10/26/2025 17:13:34 | 10/26/2025 17:26:34 | 10/26/2025 17:38:31 | 10/26/2025 17:38:34 | 10/26/2025 17:53:29 | 10/26/2025 18:54:08 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000972 | PCM-20251026-00001885 | TT-20251026-01872 | Telecom | Region_6 | TLM2223 | TLM2223 |  |  |  | Zia Ur Rahamn | 10/26/2025 17:14:05 | 10/26/2025 18:20:14 | 10/26/2025 23:14:05 | 3(2G) 2(LTE) sites down under TLM2223-P3,TLM2248-P3,TNM0724-P3/TNM0724-P3 @ Sceco | 10/26/2025 17:04:19 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 17:04:15 | P3 | 2G | mohail | Generator_SG | 2G_LTE SA | TLM2223-P3 2G_LTE,TLM2248-P3 2G_LTE,TNM0724-P3 2G | FLM_EM | TLM2223 | DOWN SITE HUB TX FB TLM2223-P3 TLM2223 Suspected Power issue at HUB TLM2248-P3 TLM2223 Suspected Power issue at HUB TNM0724 BHAB9035 Suspected Power issue at HUB | PCM-20251026-00001881 | DOWN SITE HUB TX FB TLM2223-P3 TLM2223 Suspected Power issue at HUB TLM2248-P3 TLM2223 Suspected Power issue at HUB TNM0724 BHAB9035 Suspected Power issue at HUB | DOWN SITE HUB TX FB TLM2223-P3 TLM2223 Suspected Power issue at HUB TLM2248-P3 TLM2223 Suspected Power issue at HUB TNM0724 BHAB9035 Suspected Power issue at HUB |  | sites down |  | API | 10/26/2025 17:14:05 | 10/26/2025 18:20:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000973 | PCM-20251026-00001887 | TT-20251026-01883 | EM | [7 empty] | 10/26/2025 17:15:59 | 10/26/2025 17:15:59 | 10/26/2025 23:15:59 | 1(2G/LTE) sites down under WFR2276-P3-CAP/R3_MD_HWBSC01 @ Generator_SG | 10/26/2025 17:07:31 | Major | 21825 | CSL Fault | 10/26/2025 17:07:26 | P3 | 2G |  | Generator_SG | 2G_LTE SA | WFR2276-P3-CAP | FLM_EM | WFR2276 | Results: DOWN SITE HUB WFR2276-P3-CAP WFR2276 Summary: Hub: WFR2276, Down Count: 1, Down Sites: WFR2276-P3-CAP Alarm Summary: WFR2276 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 17:15:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000974 | PCM-20251026-00001888 | TT-20251026-01895 | EM | [7 empty] | 10/26/2025 17:16:03 | 10/26/2025 17:16:03 | 10/26/2025 21:16:03 | DOOR OPEN at BISHA-SEC0012_OCS @ Sceco | 10/26/2025 17:15:49 | Critical | 1-12307 | DOOR OPEN | 10/26/2025 17:15:38 | P1 | DWDM |  | Sceco | DWDM NSA | BISHA | FLM_EM | [5 empty] | 0-TO AL-ALAYA-SEC0011(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/26/2025 17:16:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000975 | PCM-20251026-00001892 | TT-20251026-01889 | EM | [7 empty] | 10/26/2025 17:17:58 | 10/26/2025 17:17:58 | 10/26/2025 23:17:58 | 1(2G/LTE) sites down under HLMD2552-P3-CAP/R3_MD_HWBSC01 @ Generator_DG | 10/26/2025 17:09:51 | Major | 21825 | CSL Fault | 10/26/2025 17:09:48 | P3 | 2G |  | Generator_DG | 2G_LTE SA | HLMD2552-P3-CAP | FLM_EM | HLMD2552 | Results: DOWN SITE HUB HLMD2552-P3-CAP HLMD2552 Summary: Hub: HLMD2552, Down Count: 1, Down Sites: HLMD2552-P3-CAP Alarm Summary: HLMD2552 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 17:17:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000976 | PCM-20251026-00001894 | TT-20251026-01405 | Reference_telecom | Region_4 | JED1MN0141 | JED0141 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 17:18:49 | 10/26/2025 17:18:49 | 10/26/2025 23:18:49 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED1MN0141-NR2.6-P2 @ Sceco | 10/26/2025 14:39:23 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 14:39:13 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0141 | FLM_TE |  |  | PCM-20251026-00001439 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 17:18:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000977 | PCM-20251026-00001895 | TT-20251026-01857 | Telecom | Region_6 | KMS1M7304 | KMS0304 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/26/2025 17:19:25 | 10/26/2025 22:46:43 | 10/26/2025 23:19:25 | BASE STATION ANTENNA LINE PROBLEM at KMS1M7304-P3-CA-L800 @ Sceco | 10/26/2025 16:52:11 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 16:53:29 | P2 | 4G | abha | Sceco | LTE NSA | KMS1M7304 | FLM_TE |  |  | PCM-20251026-00001853 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/26/2025 17:19:25 | 10/26/2025 22:43:47 | 10/26/2025 22:46:26 | 10/26/2025 22:46:28 |  | 10/26/2025 22:46:43 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000978 | PCM-20251026-00001897 | TT-20251026-01842 | Reference_telecom | Region_4 | JED1MN2047 | JED2047 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 17:19:52 | 10/26/2025 17:19:52 | 10/26/2025 23:19:52 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED1MN2047-NR2.6-P3 @ Sceco | 10/26/2025 16:43:42 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 16:43:36 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN2047 | FLM_TE |  |  | PCM-20251026-00001831 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 17:19:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000980 | PCM-20251026-00001898 | TT-20251026-01904 | Reference_EM | Region_1 | RYHF2M2064 | RYHF2064 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/26/2025 17:20:41 | 10/26/2025 17:20:41 | 10/27/2025 05:20:41 | Door opening alarm at RYHF2M2064-P3 @ Generator_SG | 10/26/2025 17:20:15 | Minor | 65101 | Door opening alarm | 10/26/2025 17:20:10 | P3 | 2G | hafouf | Generator_SG | 2G NSA | RYHF2M2064 | FLM_EM | [8 empty] | API | 10/26/2025 17:20:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026000981 | PCM-20251026-00001899 | TT-20251020-01112 | MW_HC | Region_5 | MAK0190 | MAK0190 |  |  |  | Amr Abdulla Ali Othman | 10/26/2025 17:21:58 | 10/26/2025 17:21:58 | 10/27/2025 05:21:58 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0190-MAK2091 | 10/20/2025 11:50:23 | Minor | 113388 | LOF | 10/20/2025 11:50:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0190-MAK2091 | FLM_TE |  |  | PCM-20251026-00001665 | approved | approved |  |  |  | API | 10/26/2025 17:21:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000982 | PCM-20251026-00001900 | TT-20251026-01898 | EM | [7 empty] | 10/26/2025 17:22:00 | 10/26/2025 17:23:01 | 10/26/2025 23:22:00 | 1(2G/5G) sites down under HAW2304-P3/HAW2304-P3 @ Generator_SG | 10/26/2025 17:13:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 17:13:43 | P3 | 2G |  | Generator_SG | 2G SA | HAW2304-P3 | FLM_TE | HAW2304 | Results: DOWN SITE HUB HAW2304-P3 HAW2304 Summary: Hub: HAW2304, Down Count: 1, Down Sites: HAW2304-P3 Alarm Summary: HAW2304 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 17:22:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000983 | PCM-20251026-00001905 | TT-20251026-01705 | Reference_telecom | Region_4 | JED0884 | JED0884 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 17:24:06 | 10/27/2025 06:02:00 | 10/26/2025 23:24:06 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0884-P2 @ Sceco | 10/26/2025 15:49:36 | Major | 7602 | BCF NOTIFICATION | 10/26/2025 15:49:23 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0884 | FLM_TE |  |  | PCM-20251026-00001713 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 17:24:06 | 10/27/2025 06:02:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000984 | PCM-20251026-00001907 | TT-20251026-01386 | Reference_telecom | Region_6 | TRB0945 | TRB0945 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Umair Abbas Muhammad Abbas | 10/26/2025 17:25:11 | 10/26/2025 18:27:25 | 10/26/2025 23:25:11 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TRB0945-P3 @ Generator_SG | 10/26/2025 14:31:12 | Major | 7607 | TRX OPERATION DEGRADED | 10/26/2025 14:30:44 | P3 | 2G | turaib | Generator_SG | 2G_TRX NSA | TRB0945 | FLM_TE |  |  | PCM-20251026-00001421 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 17:25:11 | 10/26/2025 18:27:05 | 10/26/2025 18:27:18 |  |  | 10/26/2025 18:27:25 |  | Umair Abbas Muhammad Abbas |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000985 | PCM-20251026-00001909 | TT-20251026-01916 | EM | Region_6 | BHAB1M8006 | BHAB2006 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 17:27:57 | 10/26/2025 17:39:25 | 10/27/2025 05:27:57 | SHELTER DOOR OPEN at BHAB1M8006-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 17:27:36 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 17:27:30 | P3 | 4G | mohail | Generator_SG | LTE NSA | BHAB1M8006 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 17:27:57 | 10/26/2025 17:39:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000986 | PCM-20251026-00001910 | TT-20251026-01917 | Telecom | Region_6 | ARF0176 | ARF0176 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/26/2025 17:29:29 | 10/26/2025 22:46:12 | 10/26/2025 23:29:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at ARF0176-GSM-P3 @ Sceco | 10/26/2025 17:28:31 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 17:28:25 | P3 | 2G | khamis mushyet | Sceco | 5G_Cell SA | ARF0176 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 17:29:29 | 10/26/2025 22:43:47 | 10/26/2025 22:45:52 | 10/26/2025 22:45:55 |  | 10/26/2025 22:46:12 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000987 | PCM-20251026-00001911 | TT-20251026-01918 | EM | Region_4 | JED1M7309 | JED0309 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/26/2025 17:29:59 | 10/26/2025 17:29:59 | 10/27/2025 05:29:59 | SHELTER DOOR OPEN at JED1M7309-CA-L900-L800-SBTS @ Sceco | 10/26/2025 17:29:37 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 17:29:26 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7309 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 17:29:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000989 | PCM-20251026-00001914 | TT-20251026-01906 | Reference_telecom | Region_4 | JED0229 | JED0229 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 17:35:54 | 10/26/2025 18:15:42 | 10/27/2025 05:35:54 | BASE STATION SERVICE PROBLEM (FSP Reset Needed) at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/26/2025 17:18:11 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 17:18:02 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0229 | FLM_TE |  |  | PCM-20251026-00001902 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/26/2025 17:35:54 | 10/26/2025 18:15:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026000990 | PCM-20251026-00001916 | TT-20251026-01824 | Reference_telecom | Region_4 | JED1MN0884 | JED0884 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 17:36:52 | 10/27/2025 06:02:00 | 10/26/2025 23:36:52 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED1MN0884-NR2.6-P3 @ Sceco | 10/26/2025 16:14:31 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 16:14:23 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0884 | FLM_TE |  |  | PCM-20251026-00001805 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 17:36:52 | 10/27/2025 06:02:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000992 | PCM-20251026-00001919 | TT-20251026-01919 | Telecom | Region_6 | SJIZ0083 | SJIZ0083 | Equipment | SFP_BTS | Replace SFP | Mohammed Sideag Mohammed Ali | 10/26/2025 17:38:24 | 10/26/2025 19:19:20 | 10/26/2025 23:38:24 | 1(3G) 2(LTE) sites down under SJIZ0097-P3-CA,SJIZ0095-P3-CA,SJIZ0083-P3/SJIZ1S5083-P3 @ Sceco | 10/26/2025 17:31:08 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/26/2025 17:30:29 | P3 | SRAN | jizan | Sceco | 3G_LTE SA | SJIZ0097-P3-CA LTE,SJIZ0095-P3-CA LTE,SJIZ0083-P3 3G | FLM_TE | SJIZ0083 | Dear Team, HUB: SJIZ0083 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. | PCM-20251026-00001915 | Dear Team, HUB: SJIZ0083 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. | Dear Team, HUB: SJIZ0083 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. |  | sites down |  | API | 10/26/2025 17:38:24 | 10/26/2025 18:30:20 | 10/26/2025 19:19:05 |  |  | 10/26/2025 19:19:20 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026000993 | PCM-20251026-00001926 | TT-20251026-01932 | EM | [7 empty] | 10/26/2025 17:44:28 | 10/26/2025 17:44:28 | 10/27/2025 05:44:28 | NETECO: Door Status Sensor Alarm at WFR2276 @ Generator_SG | 10/26/2025 17:44:02 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 17:44:02 | P3 | SRAN |  | Generator_SG | 2G NSA | WFR2276 | FLM_EM | [8 empty] | API | 10/26/2025 17:44:28 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026000994 | PCM-20251026-00001928 | TT-20251026-01934 | EM | [7 empty] | 10/26/2025 17:44:59 | 10/26/2025 17:44:59 | 10/27/2025 05:44:59 | NETECO: Door Status Sensor Alarm at MDN2352 @ Sceco | 10/26/2025 17:44:47 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 17:44:47 | P3 | SRAN |  | Sceco | 2G NSA | MDN2352 | FLM_EM | [8 empty] | API | 10/26/2025 17:44:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026000995 | PCM-20251026-00001931 | TT-20251026-01938 | Telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 17:47:03 | 10/27/2025 08:57:17 | 10/26/2025 23:47:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8061-CA-L800-SBTS @ Sceco | 10/26/2025 17:46:06 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 17:45:55 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8061 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 17:47:03 | 10/27/2025 08:57:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026000998 | PCM-20251026-00001937 | TT-20251026-01942 | Reference_EM | Region_3 | AHT2152 | AHT2152 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 17:50:08 | 10/26/2025 17:50:08 | 10/27/2025 05:50:08 | Mains Failure at AHT2152-P3_SRAN @ Generator_SG | 10/26/2025 17:40:24 | Minor | 65109 | Mains Failure | 10/26/2025 17:40:20 | P3 | SRAN | hail | Generator_SG | 2G NSA | AHT2152 | FLM_EM | [8 empty] | API | 10/26/2025 17:50:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001000 | PCM-20251026-00001945 | TT-20251026-00867 | Telecom | Region_6 | BSA1M8289 | BSA2289 |  |  |  | Hamid Ullah Muhammad Alam Khan | 10/26/2025 17:53:16 | 10/26/2025 22:23:26 | 10/27/2025 05:53:16 | BASE STATION INFORMATION (No module fan detected) at BSA1M8289-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 10:49:31 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 10:49:27 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BSA1M8289 | FLM_TE |  |  | PCM-20251026-00001917 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/26/2025 17:53:16 | 10/26/2025 22:23:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001002 | PCM-20251026-00001947 | TT-20251026-01944 | Reference_telecom | Region_4 | TAF1M7168 | TAF0168 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 17:53:37 | 10/26/2025 17:53:37 | 10/26/2025 23:53:37 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TAF1M7168-NCA-L800-SBTS @ Sceco | 10/26/2025 17:47:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 17:47:16 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7168 | FLM_TE |  |  | PCM-20251026-00001942 | RSSI TS Steps: • Clean or Remake Jumper connectors • Check any bending in the Jumper cable. • Confirm MHA HW is OK and Configuration is as per physical connectivity.(If available at site). • RET HW and Values as per design (If available at site). • Hard reset to equipment if values are stuck and not changing at all with above actions. • Sector Swap to check if value swapping to other sector or port. • External interference test as per Care recommendation. • Finally HW replacement. | RSSI TS Steps: • Clean or Remake Jumper connectors • Check any bending in the Jumper cable. • Confirm MHA HW is OK and Configuration is as per physical connectivity.(If available at site). • RET HW and Values as per design (If available at site). • Hard reset to equipment if values are stuck and not changing at all with above actions. • Sector Swap to check if value swapping to other sector or port. • External interference test as per Care recommendation. • Finally HW replacement. |  |  |  | API | 10/26/2025 17:53:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001003 | PCM-20251026-00001948 | TT-20251026-00662 | EM | Region_4 | MKMD0554 | MKMD0554 |  |  |  | Nazeer Mohammed | 10/26/2025 17:54:23 | 10/26/2025 17:54:23 | 10/26/2025 21:54:23 | 1(2G/3G/LTE) sites down under MKMD0554-P1-USF-Trial-asBSC/MKMD0554-P1-USF-Trial-asBSC @ Sceco | 10/26/2025 08:59:37 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 08:59:32 | P1 | 2G | jeddah | Sceco | 2G_3G SA | MKMD0554-P1-USF-Trial-asBSC | FLM_TE | MKMD0554 | Results: DOWN SITE HUB MKMD0554-P1-USF-Trial-asBSC MKMD0554 Summary: Hub: MKMD0554, Down Count: 1, Down Sites: MKMD0554-P1-USF-Trial-asBSC Alarm Summary: MKMD0554 No Active Alarm on HUB | PCM-20251026-00001824 | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site |  | sites down |  | API | 10/26/2025 17:54:23 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001004 | PCM-20251026-00001949 | TT-20251026-01590 | Reference_telecom | Region_4 | HHR1M7505 | HHR0505 |  |  |  | Nazeer Mohammed | 10/26/2025 17:55:14 | 10/26/2025 17:55:14 | 10/26/2025 21:55:14 | BASE STATION OPERATION DEGRADED (ToP reference missing;Default System Time) at HHR1M7505-P1-VIP-HHR-L800 @ Generator_SG | 10/26/2025 14:59:03 | Critical | 7651 | BASE STATION OPERATION DEGRADED | 10/26/2025 14:28:51 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7505 | FLM_TE |  |  | PCM-20251026-00001612 | For GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | For GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/26/2025 17:55:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001006 | PCM-20251026-00001951 | TT-20251026-01946 | Reference_EM | Region_1 | DRN0114 | DRN0114 |  |  |  | Ibrahim said mohamed Elmarhoumy | 10/26/2025 17:55:49 | 10/26/2025 17:55:49 | 10/27/2025 05:55:49 | Door opening alarm at DRN0114-P3_SRAN @ Sceco | 10/26/2025 17:55:29 | Minor | 65101 | Door opening alarm | 10/26/2025 17:55:24 | P3 | SRAN | dammam | Sceco | 2G NSA | DRN0114 | FLM_EM | [8 empty] | API | 10/26/2025 17:55:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001010 | PCM-20251026-00001962 | TT-20251026-01956 | EM | Region_6 | NJR1M7266 | NJR0266 |  |  |  | Habib Ahmed | 10/26/2025 18:04:06 | 10/26/2025 23:51:02 | 10/27/2025 06:04:06 | SHELTER DOOR OPEN at NJR1M7266-P2 @ Generator_SG | 10/26/2025 18:03:47 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 18:03:37 | P2 | 4G | najran | Generator_SG | LTE NSA | NJR1M7266 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 18:04:06 | 10/26/2025 23:51:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001011 | PCM-20251026-00001964 | TT-20251026-01958 | Reference_EM | Region_3 | AHT2152 | AHT2152 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 18:05:08 | 10/26/2025 18:05:08 | 10/27/2025 06:05:08 | Door opening alarm at AHT2152-P3_SRAN @ Generator_SG | 10/26/2025 18:04:58 | Minor | 65101 | Door opening alarm | 10/26/2025 18:04:55 | P3 | SRAN | hail | Generator_SG | 2G NSA | AHT2152 | FLM_EM | [8 empty] | API | 10/26/2025 18:05:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001012 | PCM-20251026-00001967 | TT-20251026-01964 | Telecom | Region_5 | MAK2090 | MAK2090 |  |  |  | Husain Hassan Ishag Omer | 10/26/2025 18:07:42 | 10/26/2025 21:28:59 | 10/27/2025 06:07:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2090-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 18:06:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:06:40 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK2090 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:07:42 | 10/26/2025 21:28:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001014 | PCM-20251026-00001971 | TT-20251026-01968 | Reference_telecom | Region_6 | MHL0139 | MHL0139 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/26/2025 18:08:39 | 10/26/2025 18:08:39 | 10/27/2025 00:08:39 | D-CHANNEL FAILURE at MHL0139-P3 (REF:TT-20251026-01379) @ Sceco | 10/26/2025 14:43:19 | Major | 7705 | D-CHANNEL FAILURE | 10/26/2025 14:42:14 | P3 | 2G | mohail | Sceco | 2G_Cell SA | MHL0139 | FLM_TE | [8 empty] | API | 10/26/2025 18:08:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001015 | PCM-20251026-00001972 | TT-20251026-01373 | Reference_telecom | Region_1 | RFA0004-CSG-01 | RFA0004 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 18:08:41 | 10/26/2025 18:27:52 | 10/27/2025 06:08:41 | p0_MW_Link Down at RFA0004-DM1 Core REF:TT-20251023-00229 | 10/24/2025 03:43:11 | Minor | 15269 | LOS | 10/24/2025 03:43:11 | P3 | IPRAN | hafr | Sceco_STB | IPRAN NSA | p0_MW_Link Down at RFA0004-DM1 Core REF:TT-20251023-00229 | FLM_TE |  |  | PCM-20251026-00001842 | PM Errors and RSL degradation observed on DMH0105-DMH0104 FLM Team please perform health check for the mentioned MW link | PM Errors and RSL degradation observed on DMH0105-DMH0104 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/26/2025 18:08:41 | 10/26/2025 18:27:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001016 | PCM-20251026-00001973 | TT-20251026-01970 | EM | Region_4 | HHR1M7494 | HHR0494 |  |  |  | Anas Mohamedelamin Abbas Mustafa | 10/26/2025 18:09:15 | 10/26/2025 18:56:51 | 10/27/2025 06:09:15 | shelter door at HHR1M7494-G9-U9-L8-NL18-SBTS-VIP-HHR @ Generator_SG | 10/26/2025 18:08:53 | Minor | 7103 | shelter door | 10/26/2025 18:08:47 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7494 | FLM_EM | [5 empty] | shelter door |  |  | API | 10/26/2025 18:09:15 | 10/26/2025 18:56:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001018 | PCM-20251026-00001976 | TT-20251026-01975 | Telecom | Region_5 | MAK1U6983 | MAK6083 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 18:10:17 | 10/26/2025 18:10:17 | 10/27/2025 00:10:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1U6983-G18-L21-SBTS-P1-HRM @ Sceco | 10/26/2025 18:09:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:09:15 | P1 | 4G | makkah | Sceco | 5G_Cell SA | MAK1U6983 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:10:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001024 | PCM-20251026-00001987 | TT-20251026-01983 | Reference_telecom | Region_3 | BDJD0666 | BDJD0666 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:16:01 | 10/26/2025 18:16:01 | 10/27/2025 06:16:01 | GNSS Locked Satellites Insufficient at BDJD0666-P2_SRAN @ Generator_SG | 10/26/2025 15:40:30 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 15:37:06 | P2 | SRAN | yanbu | Generator_SG | 2G NSA | BDJD0666 | FLM_TE | [8 empty] | API | 10/26/2025 18:16:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001026 | PCM-20251026-00001988 | TT-20251026-01984 | Reference_telecom | Region_3 | BDJD2288 | BDJD2288 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:16:39 | 10/26/2025 18:16:39 | 10/27/2025 06:16:39 | GNSS Locked Satellites Insufficient at BDJD2288-P3_SRAN @ Sceco | 10/26/2025 15:04:54 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 15:01:31 | P3 | SRAN | yanbu | Sceco | 2G NSA | BDJD2288 | FLM_TE | [8 empty] | API | 10/26/2025 18:16:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001027 | PCM-20251026-00001989 | TT-20251026-01986 | EM | Region_4 | JED0578 | JED0578 |  |  |  | Amer Attallah Awadallah | 10/26/2025 18:17:32 | 10/26/2025 22:12:13 | 10/27/2025 06:17:32 | DOOR OPEN at JED0578-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/26/2025 18:17:06 | Minor | 7103 | DOOR OPEN | 10/26/2025 18:16:59 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0578 | FLM_EM | [5 empty] | DOOR OPEN |  |  | API | 10/26/2025 18:17:32 | 10/26/2025 22:12:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001028 | PCM-20251026-00001990 | TT-20251026-01985 | Telecom | Region_6 | JIZ1M7040 | JIZ0040 | Equipment | BSS_HW_Stuck | Reset Air Scale | Osama Hadi | 10/26/2025 18:17:32 | 10/26/2025 22:06:00 | 10/27/2025 00:17:32 | BASE STATION SERVICE PROBLEM (FSP subunit lost) at JIZ1M7040-G9-L8-L18-L21-SBTS-P1-HUB @ Generator_DG | 10/26/2025 18:12:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:12:32 | P1 | 4G | jizan | Generator_DG | 5G_Cell SA | JIZ1M7040 | FLM_TE | [5 empty] | FSP subunit lost |  |  | API | 10/26/2025 18:17:32 | 10/26/2025 22:04:52 | 10/26/2025 22:05:37 |  |  | 10/26/2025 22:06:00 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001032 | PCM-20251026-00002002 | TT-20251026-01998 | Telecom | Region_6 | TND1M7407 | TND0407 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 18:22:10 | 10/26/2025 20:56:32 | 10/27/2025 06:22:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at TND1M7407-G9-L9-L21-SBTS-P3 @ Sceco | 10/26/2025 18:21:14 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:20:42 | P3 | 4G | khamis mushyet | Sceco | 5G_Cell SA | TND1M7407 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:22:10 | 10/26/2025 20:56:07 | 10/26/2025 20:56:25 |  |  | 10/26/2025 20:56:32 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001034 | PCM-20251026-00002007 | TT-20251026-02002 | EM | Region_2 | RIY2337 | RIY2337 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 18:23:44 | 10/26/2025 18:23:44 | 10/27/2025 06:23:44 | NETECO: Door Open Alarm at RIY2337 @ Sceco | 10/26/2025 18:23:20 | Minor | 5152 | Door Open Alarm | 10/26/2025 18:23:20 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2337 | FLM_EM | [8 empty] | API | 10/26/2025 18:23:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001035 | PCM-20251026-00002008 | TT-20251026-01890 | EM | Region_3 | MDN2248 | MDN2248 | Enviroment | SCECO_Failure | SCECO auto restored | TAUSEEF ILYAS | 10/26/2025 18:23:46 | 10/27/2025 06:15:21 | 10/27/2025 00:23:46 | 1(2G/LTE) sites down under MDN2248-P3/R3_MD_HWBSC01 @ Generator_SG | 10/26/2025 17:09:51 | Major | 21825 | CSL Fault | 10/26/2025 17:09:50 | P3 | SRAN | madinah | Generator_SG | 2G_LTE SA | MDN2248-P3 | FLM_TE | MDN2248 | Results: DOWN SITE HUB MDN2248-P3 MDN2248 Summary: Hub: MDN2248, Down Count: 1, Down Sites: MDN2248-P3 Alarm Summary: MDN2248 Alarm Active on HUB | PCM-20251026-00001893 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 18:23:46 | 10/26/2025 23:25:21 | 10/27/2025 06:15:12 |  |  | 10/27/2025 06:15:21 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001037 | PCM-20251026-00002011 | TT-20251026-02007 | Reference_telecom | Region_3 | MDYB0410 | MDYB0410 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:25:51 | 10/26/2025 18:25:51 | 10/27/2025 06:25:51 | GNSS Locked Satellites Insufficient at MDYB0410-P1-HUB_SRAN @ Generator_DG | 10/26/2025 12:01:34 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 11:58:11 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB0410 | FLM_TE | [8 empty] | API | 10/26/2025 18:25:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001038 | PCM-20251026-00002012 | TT-20251021-02423 | Telecom | Region_4 | TAF2114 | TAF2114 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 18:26:14 | 10/26/2025 18:26:14 | 10/27/2025 00:26:14 | 1(LTE) sites down under TAF2114-CA-L800-SBTS-P2 @ Sceco | 10/21/2025 21:09:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 21:09:54 | P2 | 2G | taif | Sceco | LTE SA | TAF2114-CA-L800-SBTS-P2 | FLM_TE | TAF2114 | Results: DOWN SITE HUB TAF2114-CA-L800-SBTS-P2 TAF2114 Summary: Hub: TAF2114, Down Count: 1, Down Sites: TAF2114-CA-L800-SBTS-P2 Alarm Summary: TAF2114 No Active Alarm on HUB | PCM-20251026-00001970 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  | sites down |  | API | 10/26/2025 18:26:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001039 | PCM-20251026-00002013 | TT-20251026-01962 | EM | Region_4 | NNL0216 | NNL0216 | Transsmission | MW_HW_fault | Replace IDU | Asad Ur Rehman | 10/26/2025 18:26:39 | 10/26/2025 22:49:13 | 10/27/2025 00:26:39 | 1(2G/3G/5G) sites down under NNL0216-P2-USF/NNL1M3216-P2-USF @ Generator_SG | 10/26/2025 18:04:50 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/26/2025 18:04:09 | P2 | 2G | adam | Generator_SG | 3G SA | NNL0216-P2-USF | FLM_TE | NNL0216 | Dear team, HUB: NNL0216 We are observing RSL Degradation & PM errors . Please send FLM team to check and resolve issue at this link. | PCM-20251026-00002005 | Dear team, HUB: NNL0216 We are observing RSL Degradation & PM errors . Please send FLM team to check and resolve issue at this link. | Dear team, HUB: NNL0216 We are observing RSL Degradation & PM errors . Please send FLM team to check and resolve issue at this link. |  | sites down |  | API | 10/26/2025 18:26:39 | 10/26/2025 20:28:05 | 10/26/2025 20:28:17 | 10/26/2025 20:28:21 | 10/26/2025 20:28:25 | 10/26/2025 22:49:13 |  | Asad Ur Rehman |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026001040 | PCM-20251026-00002014 | TT-20251026-02008 | EM | [7 empty] | 10/26/2025 18:26:49 | 10/26/2025 18:26:49 | 10/27/2025 06:26:49 | NETECO: Genset Fault at RUSF9027 @ Sceco | 10/26/2025 18:20:27 | Minor | 40564 | Genset Fault | 10/26/2025 18:20:27 | P3 | Repeater |  | Sceco | 2G NSA | RUSF9027 | FLM_EM | [8 empty] | API | 10/26/2025 18:26:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001041 | PCM-20251026-00002015 | TT-20251026-01997 | Telecom | Region_6 | ABH1M7361 | ABH0361 | Equipment | BSS_HW_Stuck | Reset RF Module | Amir Sohail | 10/26/2025 18:27:27 | 10/26/2025 22:18:42 | 10/27/2025 06:27:27 | BASE STATION ANTENNA LINE PROBLEM at ABH1M7361-CA-L800-SBTS-P3 @ Sceco | 10/26/2025 18:14:26 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 18:14:20 | P3 | 4G | abha | Sceco | LTE NSA | ABH1M7361 | FLM_TE |  |  | PCM-20251026-00002001 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/26/2025 18:27:27 | 10/26/2025 18:46:44 | 10/26/2025 22:18:26 |  |  | 10/26/2025 22:18:42 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001043 | PCM-20251026-00002017 | TT-20251026-02010 | Reference_telecom | Region_3 | RSP0049 | RSP0049 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:27:59 | 10/26/2025 18:27:59 | 10/27/2025 06:27:59 | GNSS Locked Satellites Insufficient at RSP0049-P1-VIP_SRAN @ Sceco | 10/26/2025 15:46:39 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 15:43:16 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0049 | FLM_TE | [8 empty] | API | 10/26/2025 18:27:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001044 | PCM-20251026-00002018 | TT-20251026-02011 | Telecom | Region_4 | JED1M8812 | JED2812 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 18:28:22 | 10/26/2025 18:28:22 | 10/27/2025 00:28:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8812-CA-L800-P3 @ Sceco | 10/26/2025 18:27:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:27:29 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8812 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:28:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001045 | PCM-20251026-00002019 | TT-20251026-02013 | Reference_EM | Region_1 | KFKM0785 | KFKM0785 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 18:28:23 | 10/26/2025 18:28:23 | 10/27/2025 06:28:23 | Door opening alarm at KFKM0785-P3_SRAN @ Generator_SG | 10/26/2025 18:28:07 | Minor | 65101 | Door opening alarm | 10/26/2025 18:28:04 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0785 | FLM_EM | [8 empty] | API | 10/26/2025 18:28:23 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001046 | PCM-20251026-00002021 | TT-20251026-02015 | Reference_telecom | Region_3 | RSP0053 | RSP0053 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 18:28:27 | 10/26/2025 20:16:08 | 10/27/2025 06:28:27 | GNSS Locked Satellites Insufficient at RSP0053-P1-VIP_SRAN @ Sceco | 10/26/2025 17:59:33 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 17:59:22 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0053 | FLM_TE | [8 empty] | API | 10/26/2025 18:28:27 | 10/26/2025 20:16:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001048 | PCM-20251026-00002022 | TT-20251026-02016 | Reference_telecom | Region_3 | RSP0813 | RSP0813 |  |  |  | Hossam Ali Ahmed Ali | 10/26/2025 18:28:47 | 10/26/2025 20:16:08 | 10/27/2025 06:28:47 | GNSS Locked Satellites Insufficient at RSP0813-P3_SRAN @ Generator_SG | 10/26/2025 17:37:31 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 17:34:07 | P3 | SRAN | Deba | Generator_SG | 2G NSA | RSP0813 | FLM_TE | [8 empty] | API | 10/26/2025 18:28:47 | 10/26/2025 20:16:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001049 | PCM-20251026-00002024 | TT-20251026-02018 | EM | Region_3 | RUSF9040 | RUSF9040 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/26/2025 18:28:53 | 10/26/2025 18:28:53 | 10/27/2025 06:28:53 | NETECO: Insufficient Redundant Rectifiers at RUSF9040 @ Sceco_STB | 10/26/2025 18:22:48 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/26/2025 18:22:48 | P3 | Repeater | madinah | Sceco_STB | 2G NSA | RUSF9040 | FLM_EM | [8 empty] | API | 10/26/2025 18:28:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001050 | PCM-20251026-00002026 | TT-20251026-02020 | Reference_telecom | Region_3 | RSPR0832 | RSPR0832 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:29:37 | 10/26/2025 18:29:37 | 10/27/2025 06:29:37 | GNSS Locked Satellites Insufficient at RSPR0832-P3_SRAN @ Generator_SG | 10/26/2025 16:14:08 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 16:10:45 | P3 | SRAN | yanbu | Generator_SG | 2G NSA | RSPR0832 | FLM_TE | [8 empty] | API | 10/26/2025 18:29:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001051 | PCM-20251026-00002027 | TT-20251026-02021 | Telecom | Region_6 | BAH0005 | BAH0005 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/26/2025 18:29:55 | 10/26/2025 19:34:06 | 10/27/2025 00:29:55 | HARD_ERR at BAH0005_ELC1 @ Sceco | 10/26/2025 18:26:21 | Major | 1-12580 | HARD_ERR | 10/26/2025 18:26:11 | VIP | 2G | Albaha | Sceco | DWDM NSA | BAH0005 | FLM_TE | [5 empty] | 0-ELC(3-A)-1-K1LTXMP-OTHER |  |  | API | 10/26/2025 18:29:55 | 10/26/2025 19:27:28 | 10/26/2025 19:33:20 |  |  | 10/26/2025 19:34:06 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001052 | PCM-20251026-00002028 | TT-20251026-02022 | Reference_telecom | Region_3 | YBDB0290 | YBDB0290 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:29:57 | 10/26/2025 18:29:57 | 10/27/2025 06:29:57 | GNSS Locked Satellites Insufficient at YBDB0290-P1-HUB_SRAN @ Generator_DG | 10/26/2025 16:42:31 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 16:39:08 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | YBDB0290 | FLM_TE | [8 empty] | API | 10/26/2025 18:29:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001053 | PCM-20251026-00002029 | TT-20251026-02023 | Reference_telecom | Region_3 | YNB0112 | YNB0112 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:30:25 | 10/26/2025 18:30:25 | 10/27/2025 06:30:25 | GNSS Locked Satellites Insufficient at YNB0112-P2_SRAN @ Sceco | 10/26/2025 11:53:12 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 11:49:48 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB0112 | FLM_TE | [8 empty] | API | 10/26/2025 18:30:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001054 | PCM-20251026-00002031 | TT-20251026-02024 | Telecom | Region_3 | YNB0167 | YNB0167 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:30:57 | 10/26/2025 18:30:57 | 10/27/2025 06:30:57 | GNSS Locked Satellites Insufficient at YNB0167-P2_SRAN @ Sceco | 10/26/2025 12:30:14 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 12:26:50 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB0167 | FLM_TE | [8 empty] | API | 10/26/2025 18:30:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001055 | PCM-20251026-00002034 | TT-20251026-02027 | Reference_telecom | Region_3 | YNB0174 | YNB0174 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:31:14 | 10/26/2025 18:31:14 | 10/27/2025 06:31:14 | GNSS Locked Satellites Insufficient at YNB0174-P2_SRAN @ Sceco | 10/26/2025 16:01:39 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 15:58:11 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB0174 | FLM_TE | [8 empty] | API | 10/26/2025 18:31:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001056 | PCM-20251026-00002035 | TT-20251026-01977 | Reference_telecom | Region_6 | SJIZ1S7097 | SJIZ0097 | Equipment | SFP_BTS | Replace SFP | Mohammed Sideag Mohammed Ali | 10/26/2025 18:31:23 | 10/26/2025 19:19:55 | 10/27/2025 00:31:23 | BASE STATION OPERATION DEGRADED (BTS reference clock missing: GPS receiver alarm: not tracking satellites) at SJIZ1S7097-P3-CA @ Sceco | 10/26/2025 18:09:38 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/26/2025 17:59:35 | P3 | 4G | jizan | Sceco | LTE NSA | SJIZ1S7097 | FLM_TE |  |  | PCM-20251026-00001978 | FLM need to check GPS issue at site. | FLM need to check GPS issue at site. |  |  |  | API | 10/26/2025 18:31:23 | 10/26/2025 19:19:24 | 10/26/2025 19:19:39 |  |  | 10/26/2025 19:19:55 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001057 | PCM-20251026-00002039 | TT-20251026-02030 | Telecom | Region_6 | JIZ0090 | JIZ0090 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/26/2025 18:31:58 | 10/26/2025 19:20:19 | 10/27/2025 06:31:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ0090-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 18:31:23 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:31:19 | P3 | 2G | jizan | Sceco | 5G_Cell SA | JIZ0090 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:31:58 | 10/26/2025 19:19:25 | 10/26/2025 19:20:07 |  |  | 10/26/2025 19:20:19 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001058 | PCM-20251026-00002040 | TT-20251026-02025 | Reference_telecom | Region_4 | JED1MN0367 | JED0367 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 18:32:24 | 10/26/2025 18:32:24 | 10/27/2025 00:32:24 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at JED1MN0367-NR2.6-P2 @ Sceco | 10/26/2025 18:26:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:26:09 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0367 | FLM_TE |  |  | PCM-20251026-00002032 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/26/2025 18:32:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001059 | PCM-20251026-00002041 | TT-20251026-02031 | Telecom | Region_4 | JD2 | JD2 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/26/2025 18:32:30 | 10/26/2025 18:32:30 | 10/26/2025 22:32:30 | OSC_LOS at JD2_OCS @ Sceco_STB | 10/26/2025 18:32:20 | Critical | 1-12843 | OSC_LOS | 10/26/2025 18:32:09 | P1 | DWDM | jeddah | Sceco_STB | DWDM NSA | JD2 | FLM_TE | [5 empty] | 0-TO JED0102(1-A)-6-G2AST4-4(RM4/TM4(TO HHR1-SEC0039_HYB,TNG6WDAPXF(1-B02)-RM1/TM1))-OSC:1 |  |  | API | 10/26/2025 18:32:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251026001060 | PCM-20251026-00002042 | TT-20251026-02032 | Telecom | [7 empty] | 10/26/2025 18:32:31 | 10/26/2025 18:32:31 | 10/26/2025 22:32:31 | OSC_LOS at HHR1-SEC0039_HYB @ Sceco | 10/26/2025 18:32:21 | Critical | 1-12843 | OSC_LOS | 10/26/2025 18:32:09 | P1 | DWDM |  | Sceco | DWDM NSA | HHR1 | FLM_TE | [5 empty] | 0-TO JD2(1-A)-6-G2AST4-1(RM1/TM1(TO JD2_OCS,TNG6WDAPXF(1-A02)-RM2/TM2))-OSC:1 |  |  | API | 10/26/2025 18:32:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001061 | PCM-20251026-00002043 | TT-20251026-02033 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 18:33:02 | 10/27/2025 08:08:21 | 10/27/2025 00:33:02 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/26/2025 15:32:52 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/26/2025 15:32:40 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/26/2025 18:33:02 | 10/27/2025 08:08:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001062 | PCM-20251026-00002044 | TT-20251026-01331 | Telecom | Region_4 | MLJI0110 | MLJI0110 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 18:33:23 | 10/26/2025 21:19:29 | 10/27/2025 00:33:23 | 3(2G) 3(3G) 2(5G) sites down under MLJI0213-P3,MLJI0110-P3,MLJI0177-P3/MLJI0177-P3 @ Generator_SG | 10/26/2025 14:07:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 14:06:58 | P3 | 2G | alaith | Generator_SG | 2G_3G_5G SA | MLJI0177-P3 2G_3G_5G,MLJI0213-P3 2G_3G_5G,MLJI0110-P3 2G_3G | FLM_TE | MLJI0110 | Dear team , HUB: MLJI0110 We are observing MW visibility down at MLJI0110 Dir MLJI0219 ,Kindly mobilize your team to the site with spares to check this issue locally. Kindly update TT under FLM. | PCM-20251026-00001385 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 18:33:23 | 10/26/2025 21:19:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001064 | PCM-20251026-00002050 | TT-20251026-01996 | Telecom | Region_6 | JDJ0406 | JDJ0406 | Equipment | BSS_HW_fault | Replace ALD | Ansir Iqbal Muhammad Iqbal | 10/26/2025 18:34:53 | 10/26/2025 23:37:30 | 10/27/2025 06:34:53 | BASE STATION ANTENNA LINE PROBLEM at JDJ0406-L8-L18-L21-P3-SBTS @ Generator_SG | 10/26/2025 18:14:05 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 18:13:55 | P3 | 2G | bisha | Generator_SG | 2G NSA | JDJ0406 | FLM_TE |  |  | PCM-20251026-00002000 | FLM need to check ALD and perform HC at site. | FLM need to check ALD and perform HC at site. |  |  |  | API | 10/26/2025 18:34:53 | 10/26/2025 20:21:17 | 10/26/2025 23:37:06 |  |  | 10/26/2025 23:37:30 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001065 | PCM-20251026-00002053 | TT-20251026-02038 | EM | Region_6 | SRA1M8356 | SRA2356 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 18:38:11 | 10/26/2025 18:38:11 | 10/27/2025 06:38:11 | RECTIFIER MODULE FAILURE at SRA1M8356-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 18:30:02 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 18:29:54 | P3 | 4G | Albaha | Generator_SG | LTE NSA | SRA1M8356 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 18:38:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001066 | PCM-20251026-00002054 | TT-20251026-02039 | Reference_EM | Region_1 | HFBD2M5008 | HFBD0008 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/26/2025 18:38:42 | 10/26/2025 18:38:42 | 10/27/2025 00:38:42 | Door opening alarm at HFBD2M5008-P1-HUB @ Generator_SG | 10/26/2025 18:38:19 | Major | 65101 | Door opening alarm | 10/26/2025 18:38:16 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5008 | FLM_EM | [8 empty] | API | 10/26/2025 18:38:42 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001067 | PCM-20251026-00002057 | TT-20251026-02043 | Telecom | Region_1 | QTF2866 | QTF2866 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Meraj Husain Idd Baksh | 10/26/2025 18:41:18 | 10/26/2025 19:32:45 | 10/27/2025 06:41:18 | RF Unit Maintenance Link Failure at QTF2866-P2_SRAN @ Sceco | 10/26/2025 18:36:37 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 18:35:52 | P2 | SRAN | dammam | Sceco | 2G NSA | QTF2866 | FLM_TE | [8 empty] | API | 10/26/2025 18:41:18 | 10/26/2025 19:00:13 | 10/26/2025 19:32:19 | 10/26/2025 19:32:22 | 10/26/2025 19:32:26 | 10/26/2025 19:32:45 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001068 | PCM-20251026-00002060 | TT-20251026-02046 | Telecom | Region_3 | MDN2880 | MDN2880 |  |  |  | Hamayo Din Jalal | 10/26/2025 18:42:20 | 10/27/2025 00:43:46 | 10/27/2025 00:42:20 | NR Cell Unavailable at MDN2880-P3_SRAN @ Sceco | 10/26/2025 18:34:20 | Major | 29841 | NR Cell Unavailable | 10/26/2025 18:33:58 | P2 | SRAN | madinah | Sceco | 5G SA | MDN2880 | FLM_TE | [8 empty] | API | 10/26/2025 18:42:20 | 10/27/2025 00:43:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001069 | PCM-20251026-00002067 | TT-20251026-02052 | Reference_EM | Region_1 | KFKM0785 | KFKM0785 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 18:47:29 | 10/26/2025 18:47:29 | 10/27/2025 06:47:29 | Mains Failure at KFKM0785-P3_SRAN @ Generator_SG | 10/26/2025 18:37:45 | Minor | 65109 | Mains Failure | 10/26/2025 18:37:41 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0785 | FLM_EM | [8 empty] | API | 10/26/2025 18:47:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001070 | PCM-20251026-00002068 | TT-20251026-02053 | Telecom | Region_4 | JED0310 | JED0310 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 18:48:00 | 10/27/2025 06:02:01 | 10/27/2025 00:48:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Generator_SG | 10/26/2025 18:47:05 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:46:55 | VIP | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0310 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:48:00 | 10/27/2025 06:02:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001071 | PCM-20251026-00002069 | TT-20251026-02055 | Telecom | Region_5 | MAK2129 | MAK2129 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/26/2025 18:49:33 | 10/26/2025 18:49:33 | 10/27/2025 06:49:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2129-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 18:48:53 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 18:48:30 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2129 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 18:49:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001072 | PCM-20251026-00002070 | TT-20251026-02057 | Reference_telecom | Region_1 | QTF2M8866 | QTF2866 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Meraj Husain Idd Baksh | 10/26/2025 18:50:45 | 10/26/2025 19:33:11 | 10/27/2025 00:50:45 | Cell Unavailable at QTF2M8866-P2-L800 (REF::TT-20251026-02043) @ Sceco | 10/26/2025 18:36:20 | Major | 29240 | Cell Unavailable | 10/26/2025 18:35:57 | P2 | 4G | dammam | Sceco | LTE SA | QTF2M8866 | FLM_TE | [8 empty] | API | 10/26/2025 18:50:45 | 10/26/2025 19:00:14 | 10/26/2025 19:15:36 | 10/26/2025 19:15:40 | 10/26/2025 19:15:48 | 10/26/2025 19:33:11 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001073 | PCM-20251026-00002074 | TT-20251026-02054 | Telecom | Region_6 | BSH1M7897 | BSH0897 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/26/2025 18:53:29 | 10/26/2025 20:40:50 | 10/27/2025 00:53:29 | 1(LTE) sites down under BSH0897-G9-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 18:44:59 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 18:44:56 | P3 | 4G | baish | Sceco | LTE SA | BSH0897-G9-L18-L21-SBTS-P3 | FLM_TE | BSH0897 | Results: DOWN SITE HUB BSH0897-G9-L18-L21-SBTS-P3 BSH0897 Summary: Hub: BSH0897, Down Count: 1, Down Sites: BSH0897-G9-L18-L21-SBTS-P3 Alarm Summary: BSH0897 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.103.55.124:8080] [URL:http://10.103.55.124:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 18:53:29 | 10/26/2025 20:21:18 | 10/26/2025 20:40:26 |  |  | 10/26/2025 20:40:50 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001074 | PCM-20251026-00002075 | TT-20251026-01403 | Reference_telecom | Region_2 | RIY0631-ZRi01-3-CSG-02 | RIY0631 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 18:53:34 | 10/26/2025 18:53:34 | 10/26/2025 22:53:34 | MW Link Down at RIY0631-ZRi01-3-CSG-02 TO RIY0796 REF:TT-20250922-00730 @ Sceco | 09/22/2025 11:55:49 | Critical | 101-2505274 | Physical Port Down | 09/22/2025 11:55:31 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIY0631-ZRi01-3-CSG-02 | FLM_TE |  |  | PCM-20251026-00002045 | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm |  |  |  | API | 10/26/2025 18:53:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001075 | PCM-20251026-00002076 | TT-20251026-01358 | Reference_telecom | Region_2 | RYDM0656 | RYDM0656 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/26/2025 18:53:39 | 10/26/2025 23:43:14 | 10/26/2025 22:53:39 | MW Physical Port Down at RYDM0656-LL-CSG-01 To RIY0662 REF:TT-20250213-02117 @ Generator_DG | 10/22/2025 03:02:30 | Critical | 101-2505274 | Physical Port Down | 10/22/2025 02:57:37 | P2 | SRAN | riyadh | Generator_DG | IPRAN SA | RYDM0656-LL-CSG-01 | FLM_TE |  | Dear IPRAN, Kindly share port details | PCM-20251026-00002048 | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm |  |  |  | API | 10/26/2025 18:53:39 | 10/26/2025 23:43:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001076 | PCM-20251026-00002077 | TT-20251026-01588 | Reference_telecom | Region_2 | RIY0861 | RIY0861 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 18:54:11 | 10/26/2025 18:54:11 | 10/27/2025 06:54:11 | MW Link down at RIY0861-ZRi01-3-CSG-06 To RIY0781 REF: TT-20250604-01638 @ Sceco | 10/23/2025 11:38:32 | Minor | 101-2505274 | Physical Port Down | 10/23/2025 11:36:41 | P1 | SRAN | riyadh | Sceco | IPRAN SA | RIY0861-ZRi01-3-CSG-06 | FLM_TE |  |  | PCM-20251026-00002052 | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm |  |  |  | API | 10/26/2025 18:54:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001077 | PCM-20251026-00002079 | TT-20251026-01585 | Reference_telecom | Region_2 | RIY0861 | RIY0861 |  |  |  | Mubashar Farooq Abdul Majeed | 10/26/2025 18:54:33 | 10/26/2025 18:54:33 | 10/27/2025 06:54:33 | MW Link down at RIY0861-ZRi01-3-CSG-06 To RIY0394 REF: TT-20250604-01638 @ Sceco | 10/23/2025 11:38:32 | Minor | 101-2505274 | Physical Port Down | 10/23/2025 11:36:49 | P1 | SRAN | riyadh | Sceco | IPRAN SA | RIY0861-ZRi01-3-CSG-06 | FLM_TE |  |  | PCM-20251026-00002051 | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm | The router flapped power from 3 days, and those alarms appeared again, plz ignore and close pcm |  |  |  | API | 10/26/2025 18:54:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026000439 | PCM-20251026-00000889 | TT-20251026-00844 | Reference_EM | Region_2 | RIY2126 | RIY2126 | Enviroment | SCECO_Failure | SCECO auto restored | Mustansar Ali Mushtaq Ahmad | 10/26/2025 10:48:50 | 10/26/2025 11:55:13 | 10/26/2025 22:48:50 | Mains Failure at RIY2126-P3_SRAN-PC @ Sceco | 10/26/2025 10:38:32 | Minor | 65109 | Mains Failure | 10/26/2025 10:38:29 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2126 | FLM_EM | [8 empty] | API | 10/26/2025 10:48:50 | 10/26/2025 10:56:29 | 10/26/2025 10:59:24 | 10/26/2025 10:59:27 |  | 10/26/2025 11:55:13 |  | Mustansar Ali Mushtaq Ahmad |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000443 | PCM-20251026-00000896 | TT-20251026-00858 | Reference_EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 10:53:31 | 10/26/2025 11:55:21 | 10/26/2025 22:53:31 | Low battery voltage at RIY2431-P2_SRAN @ Sceco | 10/26/2025 10:42:53 | Minor | 65110 | Low battery voltage | 10/26/2025 10:42:48 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/26/2025 10:53:31 | 10/26/2025 11:55:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000445 | PCM-20251026-00000899 | TT-20251026-00860 | Reference_EM | Region_1 | DAM0252 | DAM0252 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/26/2025 10:54:31 | 10/26/2025 11:19:01 | 10/26/2025 22:54:31 | Door opening alarm at DAM0252-P2_SRAN @ Sceco | 10/26/2025 10:53:44 | Minor | 65101 | Door opening alarm | 10/26/2025 10:53:41 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0252 | FLM_EM | [8 empty] | API | 10/26/2025 10:54:31 | 10/26/2025 11:19:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000450 | PCM-20251026-00000910 | TT-20251026-00868 | Telecom | Region_2 | BUR0053 | BUR0053 |  |  |  | Farman Ullah Muhammad Nazir | 10/26/2025 11:00:50 | 10/26/2025 12:27:17 | 10/26/2025 17:00:50 | BBU Board Maintenance Link Failure at BUR0053-P2_SRAN @ Sceco | 10/26/2025 10:55:11 | Major | 26205 | BBU Board Maintenance Link Failure | 10/26/2025 10:53:38 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0053 | FLM_EM |  |  | PCM-20251026-00000904 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 11:00:50 | 10/26/2025 12:27:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251026000451 | PCM-20251026-00000911 | TT-20251026-00875 | Reference_EM | Region_2 | DLM0023 | DLM0023 |  |  |  | Kazi Jalil Allimiya | 10/26/2025 11:01:16 | 10/26/2025 11:22:41 | 10/26/2025 23:01:16 | high temprature 40 at DLM0023-P3-USF_SRAN-PC @ Sceco | 10/26/2025 10:50:56 | Minor | 65103 | high temprature 40 | 10/26/2025 10:50:52 | P3 | SRAN | al kharj | Sceco | 2G NSA | DLM0023 | FLM_EM | [8 empty] | API | 10/26/2025 11:01:16 | 10/26/2025 11:20:45 | 10/26/2025 11:21:10 | 10/26/2025 11:21:20 | 10/26/2025 11:22:41 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000465 | PCM-20251026-00000942 | TT-20251026-00905 | Reference_EM | Region_2 | RIY0854 | RIY0854 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/26/2025 11:11:06 | 10/26/2025 11:11:06 | 10/26/2025 17:11:06 | Mains Failure at RIY0854-P1-VIP_SRAN @ Sceco | 10/26/2025 11:00:42 | Major | 65109 | Mains Failure | 10/26/2025 11:00:38 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0854 | FLM_EM | [8 empty] | API | 10/26/2025 11:11:06 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000470 | PCM-20251026-00000947 | TT-20251026-00912 | Reference_EM | Region_1 | TRF2507 | TRF2507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ragab Farg Abdel Nabi Bekhatro | 10/26/2025 11:16:07 | 10/26/2025 12:54:30 | 10/26/2025 23:16:07 | Door opening alarm at TRF2507-P2-USF_SRAN @ Generator_SG | 10/26/2025 11:12:38 | Minor | 65101 | Door opening alarm | 10/26/2025 11:12:34 | P2 | SRAN | arar | Generator_SG | 2G NSA | TRF2507 | FLM_EM | [8 empty] | API | 10/26/2025 11:16:07 | 10/26/2025 11:50:04 | 10/26/2025 12:06:00 | 10/26/2025 12:06:14 | 10/26/2025 12:06:18 | 10/26/2025 12:54:30 |  | Ragab Farg Abdel Nabi Bekhatro |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000638 | PCM-20251026-00001167 | TT-20251026-01159 | EM | Region_1 | ARR9807 | ARR9807 |  |  |  | Ismail Salah Ismail Elbery | 10/26/2025 14:25:58 | 10/27/2025 03:12:50 | 10/27/2025 02:25:58 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/26/2025 12:41:17 | Minor | 40564 | Genset Fault | 10/26/2025 12:41:17 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/26/2025 14:25:58 | 10/27/2025 03:12:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000639 | PCM-20251026-00001169 | TT-20251026-01161 | Reference_EM | Region_1 | HFF2162 | HFF2162 |  |  |  | Moustafa Mohamed Saleh Saif | 10/26/2025 14:26:26 | 10/26/2025 16:04:45 | 10/26/2025 20:26:26 | Door opening alarm at HFF2162-P1-HUB_SRAN @ Sceco | 10/26/2025 12:47:25 | Major | 65101 | Door opening alarm | 10/26/2025 12:47:22 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFF2162 | FLM_EM | [8 empty] | API | 10/26/2025 14:26:26 | 10/26/2025 16:04:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000640 | PCM-20251026-00001212 | TT-20251026-01198 | EM | Region_1 | DMJR0137 | DMJR0137 |  |  |  | Emad Mahmoud Ahmed Mohamed | 10/26/2025 14:26:34 | 10/26/2025 14:36:52 | 10/26/2025 18:26:34 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/26/2025 13:11:42 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/26/2025 13:11:36 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 0-TO DMJR0141(1-A) |  |  | API | 10/26/2025 14:26:34 | 10/26/2025 14:36:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251026000641 | PCM-20251026-00001208 | TT-20251026-01196 | Reference_EM | Region_1 | HRBD0124 | HRBD0124 |  |  |  | Mahmoud Youssef Mohamed Ahmed | 10/26/2025 14:26:40 | 10/26/2025 14:26:40 | 10/26/2025 20:26:40 | Air condition 1 failure alarm at HRBD0124-P1-HUB_SRAN @ Generator_SG | 10/26/2025 13:01:50 | Major | 65104 | Air condition 1 failure alarm | 10/26/2025 13:01:46 | P1 | SRAN | hafr | Generator_SG | 2G NSA | HRBD0124 | FLM_EM | [8 empty] | API | 10/26/2025 14:26:40 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000642 | PCM-20251026-00001181 | TT-20251026-01170 | Reference_EM | Region_2 | QSRY2735 | QSRY2735 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/26/2025 14:27:21 | 10/26/2025 15:20:48 | 10/27/2025 02:27:21 | Mains Failure at QSRY2735-P2_SRAN @ Generator_SG | 10/26/2025 12:48:32 | Minor | 65109 | Mains Failure | 10/26/2025 12:48:27 | P2 | SRAN | muzamiah | Generator_SG | 2G NSA | QSRY2735 | FLM_EM | [8 empty] | API | 10/26/2025 14:27:21 | 10/26/2025 15:20:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026000643 | PCM-20251026-00001201 | TT-20251026-01187 | Reference_EM | Region_1 | SLW2997 | SLW2997 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/26/2025 14:27:27 | 10/26/2025 15:47:27 | 10/27/2025 02:27:27 | Door opening alarm at SLW2997-P3_SRAN @ Generator_SG | 10/26/2025 13:06:42 | Minor | 65101 | Door opening alarm | 10/26/2025 13:06:39 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | SLW2997 | FLM_EM | [8 empty] | API | 10/26/2025 14:27:27 | 10/26/2025 15:47:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000644 | PCM-20251026-00001198 | TT-20251026-01185 | Reference_EM | Region_2 | RIY2984 | RIY2984 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/26/2025 14:27:45 | 10/26/2025 14:44:47 | 10/27/2025 02:27:45 | Door opening alarm at RIY2984-P3_SRAN-PC @ Sceco | 10/26/2025 13:05:38 | Minor | 65101 | Door opening alarm | 10/26/2025 13:05:34 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2984 | FLM_EM | [8 empty] | API | 10/26/2025 14:27:45 | 10/26/2025 14:44:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000645 | PCM-20251026-00001399 | TT-20251026-01363 | Reference_EM | Region_1 | QTF2866 | QTF2866 |  |  |  | Ibrahim said mohamed Elmarhoumy | 10/26/2025 14:27:48 | 10/26/2025 14:27:48 | 10/27/2025 02:27:48 | high temprature 32 at QTF2866-P2_SRAN @ Sceco | 10/26/2025 14:17:31 | Minor | 65102 | high temprature 32 | 10/26/2025 14:17:27 | P2 | SRAN | dammam | Sceco | 2G NSA | QTF2866 | FLM_EM | [8 empty] | API | 10/26/2025 14:27:48 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000646 | PCM-20251026-00001185 | TT-20251026-01175 | Reference_EM | Region_2 | RIY2347 | RIY2347 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 14:27:59 | 10/26/2025 14:27:59 | 10/27/2025 02:27:59 | Mains Failure at RIY2347-P3_SRAN-PC @ Sceco | 10/26/2025 12:50:10 | Minor | 65109 | Mains Failure | 10/26/2025 12:50:06 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2347 | FLM_EM | [8 empty] | API | 10/26/2025 14:27:59 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000654 | PCM-20251026-00001226 | TT-20251026-01209 | Reference_EM | Region_1 | SLW2997 | SLW2997 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/26/2025 14:34:27 | 10/26/2025 15:47:28 | 10/27/2025 02:34:27 | Mains Failure at SLW2997-P3_SRAN @ Generator_SG | 10/26/2025 13:07:32 | Minor | 65109 | Mains Failure | 10/26/2025 13:07:30 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | SLW2997 | FLM_EM | [8 empty] | API | 10/26/2025 14:34:27 | 10/26/2025 15:47:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000655 | PCM-20251026-00001392 | TT-20251026-01354 | EM | Region_2 | RIY2075 | RIY2075 |  |  |  | Hosameldin Mohamed Elzohri Hamed | 10/26/2025 14:34:32 | 10/26/2025 14:34:32 | 10/27/2025 02:34:32 | NETECO: Door Status Sensor Alarm at RIY2075 @ Sceco | 10/26/2025 14:22:01 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 14:22:01 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2075 | FLM_EM | [8 empty] | API | 10/26/2025 14:34:32 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000656 | PCM-20251026-00001391 | TT-20251026-01353 | Reference_EM | Region_2 | RIY2075 | RIY2075 |  |  |  | Hosameldin Mohamed Elzohri Hamed | 10/26/2025 14:34:38 | 10/26/2025 14:34:38 | 10/27/2025 02:34:38 | Door opening alarm at RIY2075-P3_SRAN @ Sceco | 10/26/2025 14:22:08 | Minor | 65101 | Door opening alarm | 10/26/2025 14:22:04 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2075 | FLM_EM | [8 empty] | API | 10/26/2025 14:34:38 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000658 | PCM-20251026-00001378 | TT-20251026-01343 | Reference_EM | Region_1 | DAM0642 | DAM0642 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/26/2025 14:35:08 | 10/26/2025 14:35:08 | 10/27/2025 02:35:08 | Door opening alarm at DAM0642-P3_SRAN @ Sceco | 10/26/2025 14:16:39 | Minor | 65101 | Door opening alarm | 10/26/2025 14:16:35 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM0642 | FLM_EM | [8 empty] | API | 10/26/2025 14:35:08 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000659 | PCM-20251026-00001240 | TT-20251026-01222 | Reference_EM | Region_1 | JBL0966 | JBL0966 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 14:35:19 | 10/26/2025 23:51:24 | 10/27/2025 02:35:19 | Mains Failure at JBL2M1966-P2 @ Sceco | 10/26/2025 13:14:52 | Minor | 65109 | Mains Failure | 10/26/2025 13:14:48 | P2 | 2G | jubail | Sceco | 2G NSA | JBL2M1966 | FLM_EM | [8 empty] | API | 10/26/2025 14:35:19 | 10/26/2025 23:51:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000660 | PCM-20251026-00001243 | TT-20251026-01225 | Reference_EM | Region_1 | JBL2108 | JBL2108 | Enviroment | Genset failure_High Temperature | Change Generator radiator | Ahmed Hassan Ahmed Hassanin | 10/26/2025 14:35:21 | 10/26/2025 18:52:44 | 10/27/2025 02:35:21 | Air condition 2 failure alarm at JBL2108-P2_SRAN-FON @ Generator_DG | 10/26/2025 13:16:19 | Minor | 65105 | Air condition 2 failure alarm | 10/26/2025 13:16:15 | P1 | SRAN | jubail | Generator_DG | 2G NSA | JBL2108 | FLM_EM | [8 empty] | API | 10/26/2025 14:35:21 | 10/26/2025 16:34:22 | 10/26/2025 18:52:24 |  |  | 10/26/2025 18:52:44 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251026000662 | PCM-20251026-00001247 | TT-20251026-01231 | Reference_EM | Region_1 | TBSK0244 | TBSK0244 |  |  |  | Mahmoud Abdelwanis Massoud Elrashidy | 10/26/2025 14:35:40 | 10/26/2025 15:56:36 | 10/27/2025 02:35:40 | Door opening alarm at TBSK0244-ODC-ENV-ALM @ Generator_DG | 10/26/2025 13:28:00 | Minor | 65101 | Door opening alarm | 10/26/2025 13:27:56 | P3 | SRAN | sakaka | Generator_DG | 2G NSA | TBSK0244 | FLM_EM | [8 empty] | API | 10/26/2025 14:35:40 | 10/26/2025 15:56:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251026000664 | PCM-20251026-00001252 | TT-20251026-01239 | Reference_EM | Region_2 | RIY0605 | RIY0605 |  |  |  | Abdelaziz Badie Abdelaziz Saad Elsafty | 10/26/2025 14:36:01 | 10/26/2025 14:36:01 | 10/27/2025 02:36:01 | Door opening alarm at RIY0605-P2_SRAN @ Generator_SG | 10/26/2025 13:31:02 | Minor | 65101 | Door opening alarm | 10/26/2025 13:26:57 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0605 | FLM_EM | [8 empty] | API | 10/26/2025 14:36:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000665 | PCM-20251026-00001354 | TT-20251026-01330 | Reference_EM | Region_1 | SLW2996 | SLW2996 |  |  |  | Mohamed Ramadan Mohamed Gomaa | 10/26/2025 14:36:07 | 10/26/2025 15:47:28 | 10/27/2025 02:36:07 | Door opening alarm at SLW2996-P3_SRAN @ Generator_SG | 10/26/2025 14:08:58 | Minor | 65101 | Door opening alarm | 10/26/2025 14:05:42 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | SLW2996 | FLM_EM | [8 empty] | API | 10/26/2025 14:36:07 | 10/26/2025 15:47:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000666 | PCM-20251026-00001353 | TT-20251026-01327 | Reference_EM | Region_1 | DMJ2271 | DMJ2271 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/26/2025 14:36:14 | 10/26/2025 14:49:21 | 10/27/2025 02:36:14 | NETECO: AC Failure at DMJ2271 @ Generator_SG | 10/26/2025 14:03:09 | Minor | 10202 | AC Failure | 10/26/2025 14:03:09 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJ2271 | FLM_EM | [8 empty] | API | 10/26/2025 14:36:14 | 10/26/2025 14:41:17 | 10/26/2025 14:49:12 |  |  | 10/26/2025 14:49:21 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000667 | PCM-20251026-00001352 | TT-20251026-01325 | Reference_EM | Region_1 | DMJ2271 | DMJ2271 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/26/2025 14:36:21 | 10/26/2025 14:49:07 | 10/27/2025 02:36:21 | Mains Failure at DMJ2271-P2-USF_SRAN @ Generator_SG | 10/26/2025 13:58:57 | Minor | 65109 | Mains Failure | 10/26/2025 13:58:53 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJ2271 | FLM_EM | [8 empty] | API | 10/26/2025 14:36:21 | 10/26/2025 14:41:18 | 10/26/2025 14:48:58 |  |  | 10/26/2025 14:49:07 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000668 | PCM-20251026-00001334 | TT-20251026-01308 | Reference_EM | Region_2 | RIY0112 | RIY0112 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/26/2025 14:37:08 | 10/26/2025 14:44:48 | 10/26/2025 20:37:08 | high temprature 32 at RIY0112-P1-DIA_SRAN @ Sceco | 10/26/2025 12:28:48 | Major | 65102 | high temprature 32 | 10/26/2025 13:52:17 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0112 | FLM_EM | [8 empty] | API | 10/26/2025 14:37:08 | 10/26/2025 14:44:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000669 | PCM-20251026-00001285 | TT-20251026-01260 | Reference_EM | Region_2 | DWD2113 | DWD2113 |  |  |  | Moustafa Elzaafarany Abdellah | 10/26/2025 14:37:45 | 10/26/2025 20:58:58 | 10/27/2025 02:37:45 | Door opening alarm at DWD2113-P3_SRAN @ Sceco | 10/26/2025 13:44:28 | Minor | 65101 | Door opening alarm | 10/26/2025 13:44:24 | P3 | SRAN | dawadmi | Sceco | 2G NSA | DWD2113 | FLM_EM | [8 empty] | API | 10/26/2025 14:37:45 | 10/26/2025 20:58:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000670 | PCM-20251026-00001317 | TT-20251026-01295 | EM | Region_1 | DMJ2271 | DMJ2271 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/26/2025 14:38:08 | 10/26/2025 14:48:54 | 10/27/2025 02:38:08 | NETECO: Door Status Sensor Alarm at DMJ2271 @ Generator_SG | 10/26/2025 13:56:31 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 13:56:31 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJ2271 | FLM_EM | [8 empty] | API | 10/26/2025 14:38:08 | 10/26/2025 14:41:18 | 10/26/2025 14:48:44 |  |  | 10/26/2025 14:48:54 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000671 | PCM-20251026-00001316 | TT-20251026-01294 | Reference_EM | Region_1 | DMJ2271 | DMJ2271 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/26/2025 14:38:14 | 10/26/2025 14:48:39 | 10/27/2025 02:38:14 | Door opening alarm at DMJ2271-P2-USF_SRAN @ Generator_SG | 10/26/2025 13:56:36 | Minor | 65101 | Door opening alarm | 10/26/2025 13:56:32 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJ2271 | FLM_EM | [8 empty] | API | 10/26/2025 14:38:14 | 10/26/2025 14:41:19 | 10/26/2025 14:48:29 |  |  | 10/26/2025 14:48:39 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000672 | PCM-20251026-00001311 | TT-20251026-01289 | Reference_EM | Region_2 | DLM0023 | DLM0023 |  |  |  | Kazi Jalil Allimiya | 10/26/2025 14:38:38 | 10/26/2025 14:38:38 | 10/27/2025 02:38:38 | Door opening alarm at DLM0023-P3-USF_SRAN-PC @ Sceco | 10/26/2025 13:54:39 | Minor | 65101 | Door opening alarm | 10/26/2025 13:49:30 | P3 | SRAN | al kharj | Sceco | 2G NSA | DLM0023 | FLM_EM | [8 empty] | API | 10/26/2025 14:38:38 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000835 | PCM-20251026-00001606 | TT-20251026-01586 | Reference_EM | Region_1 | HMBY2428 | HMBY2428 |  |  |  | Abdul Malik Shaik | 10/26/2025 14:59:50 | 10/27/2025 08:44:37 | 10/27/2025 02:59:50 | Door opening alarm at HMBY2428-P3_SRAN @ Sceco | 10/26/2025 14:59:32 | Minor | 65101 | Door opening alarm | 10/26/2025 14:59:29 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2428 | FLM_EM | [8 empty] | API | 10/26/2025 14:59:50 | 10/27/2025 08:44:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000852 | PCM-20251026-00001638 | TT-20251026-01616 | Reference_EM | Region_2 | RIY0933 | RIY0933 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 15:10:45 | 10/26/2025 15:10:45 | 10/27/2025 03:10:45 | Door opening alarm at RIY0933-P2_SRAN @ Sceco | 10/26/2025 15:10:05 | Minor | 65101 | Door opening alarm | 10/26/2025 15:04:55 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0933 | FLM_EM | [8 empty] | API | 10/26/2025 15:10:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000863 | PCM-20251026-00001663 | TT-20251026-01645 | Reference_EM | Region_2 | BUR0047 | BUR0047 |  |  |  | Farman Ullah Muhammad Nazir | 10/26/2025 15:22:35 | 10/26/2025 15:22:35 | 10/27/2025 03:22:35 | Mains Failure at BUR0047-P2_SRAN @ Sceco | 10/26/2025 15:12:31 | Minor | 65109 | Mains Failure | 10/26/2025 15:12:28 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0047 | FLM_EM | [8 empty] | API | 10/26/2025 15:22:35 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251026000875 | PCM-20251026-00001685 | TT-20251026-01673 | Reference_EM | Region_1 | HFR0472 | HFR0472 |  |  |  | Reda Mohammed Mohamed Hassanein | 10/26/2025 15:33:31 | 10/26/2025 16:29:19 | 10/27/2025 03:33:31 | Air condition 1 failure alarm at HFR0472-P3_SRAN-PC @ Sceco | 10/26/2025 15:23:07 | Minor | 65104 | Air condition 1 failure alarm | 10/26/2025 15:23:04 | P3 | SRAN | hafr | Sceco | 2G NSA | HFR0472 | FLM_EM | [8 empty] | API | 10/26/2025 15:33:31 | 10/26/2025 15:38:50 | 10/26/2025 16:25:26 | 10/26/2025 16:25:28 | 10/26/2025 16:29:19 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000876 | PCM-20251026-00001684 | TT-20251026-01672 | Reference_EM | Region_1 | KBR0177 | KBR0177 |  |  |  | Abdul Malik Shaik | 10/26/2025 15:33:32 | 10/27/2025 08:44:38 | 10/27/2025 03:33:32 | Door opening alarm at KBR0177-P3_SRAN @ Sceco | 10/26/2025 15:33:01 | Minor | 65101 | Door opening alarm | 10/26/2025 15:32:55 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0177 | FLM_EM | [8 empty] | API | 10/26/2025 15:33:32 | 10/27/2025 08:44:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000883 | PCM-20251026-00001700 | TT-20251026-01697 | Reference_EM | Region_2 | KHJ0995 | KHJ0995 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | Fritz Ian Generale | 10/26/2025 15:48:26 | 10/27/2025 08:08:24 | 10/27/2025 03:48:26 | Generator failure at KHJ0995-P2-USF_SRAN-PC @ Sceco | 10/26/2025 15:38:14 | Minor | 65114 | Generator failure | 10/26/2025 15:37:58 | P2 | SRAN | al kharj | Sceco | 2G NSA | KHJ0995 | FLM_EM | [8 empty] | API | 10/26/2025 15:48:26 | 10/27/2025 08:07:55 | 10/27/2025 08:08:02 |  |  | 10/27/2025 08:08:24 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000904 | PCM-20251026-00001737 | TT-20251026-01730 | Reference_EM | Region_1 | DMH0606 | DMH0606 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 16:08:35 | 10/26/2025 16:08:35 | 10/26/2025 22:08:35 | Minor Rec alarm at DMH0606-P1-HUB_SRAN @ Generator_SG | 10/26/2025 15:58:08 | Major | 65108 | Minor Rec alarm | 10/26/2025 15:58:05 | P1 | SRAN | hafr | Generator_SG | 2G NSA | DMH0606 | FLM_EM | [8 empty] | API | 10/26/2025 16:08:35 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026000919 | PCM-20251026-00001771 | TT-20251026-01771 | Reference_EM | Region_2 | KRM0203 | KRM0203 |  |  |  | Mohamed Alfatih Mohamed Eltayeb Mohamed | 10/26/2025 16:25:06 | 10/26/2025 16:25:06 | 10/27/2025 04:25:06 | Mains Failure at KRM0203-P3_SRAN @ Sceco | 10/26/2025 16:14:52 | Minor | 65109 | Mains Failure | 10/26/2025 16:14:49 | P3 | SRAN | al rass | Sceco | 2G NSA | KRM0203 | FLM_EM | [8 empty] | API | 10/26/2025 16:25:06 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000953 | PCM-20251026-00001839 | TT-20251026-01847 | Reference_EM | Region_1 | JBL0345 | JBL0345 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/26/2025 16:52:30 | 10/26/2025 18:01:44 | 10/27/2025 04:52:30 | Battery Faulty at JBL0345-P2_SRAN-PC @ Power Cube | 10/26/2025 16:41:46 | Minor | 65033 | Battery Faulty | 10/26/2025 16:41:43 | P2 | SRAN | dammam | Power Cube | 2G NSA | JBL0345 | FLM_EM | [8 empty] | API | 10/26/2025 16:52:30 | 10/26/2025 18:01:08 | 10/26/2025 18:01:36 |  |  | 10/26/2025 18:01:44 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026000955 | PCM-20251026-00001843 | TT-20251026-01843 | Telecom | Region_1 | DAM0204 | DAM0204 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/26/2025 16:54:45 | 10/26/2025 18:01:44 | 10/27/2025 04:54:45 | RF Unit Maintenance Link Failure at DAM0204-P2_SRAN @ Sceco | 10/26/2025 16:47:24 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 16:45:42 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0204 | FLM_EM |  |  | PCM-20251026-00001833 | power issue at site | power issue at site |  |  |  | API | 10/26/2025 16:54:45 | 10/26/2025 18:01:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000979 | PCM-20251026-00001896 | TT-20251026-01900 | Reference_EM | Region_1 | DAM2672 | DAM2672 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/26/2025 17:19:56 | 10/26/2025 18:02:19 | 10/27/2025 05:19:56 | Door opening alarm at DAM2M4672-P3 @ Generator_SG | 10/26/2025 17:19:09 | Minor | 65101 | Door opening alarm | 10/26/2025 17:19:06 | P3 | 3G | dammam | Generator_SG | 3G NSA | DAM2M4672 | FLM_EM | [8 empty] | API | 10/26/2025 17:19:56 | 10/26/2025 18:01:09 | 10/26/2025 18:01:56 |  |  | 10/26/2025 18:02:19 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026000988 | PCM-20251026-00001913 | TT-20251026-01920 | Reference_EM | Region_2 | ARS0173 | ARS0173 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shazlly Mahmoud Abouzied Mahmoud | 10/26/2025 17:32:16 | 10/26/2025 18:06:28 | 10/27/2025 05:32:16 | Door opening alarm at ARS2M1173-P3 @ Sceco | 10/26/2025 17:31:55 | Minor | 65101 | Door opening alarm | 10/26/2025 17:31:49 | P3 | 2G | al rass | Sceco | 2G NSA | ARS2M1173 | FLM_EM | [8 empty] | API | 10/26/2025 17:32:16 | 10/26/2025 17:51:22 | 10/26/2025 17:51:26 | 10/26/2025 17:51:32 | 10/26/2025 17:59:58 | 10/26/2025 18:06:28 |  | Shazlly Mahmoud Abouzied Mahmoud |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026000997 | PCM-20251026-00001932 | TT-20251026-01939 | Reference_EM | Region_1 | HFF2397 | HFF2397 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/26/2025 17:47:46 | 10/26/2025 17:47:46 | 10/27/2025 05:47:46 | Door opening alarm at HFF2397-P3_SRAN @ Sceco | 10/26/2025 17:47:23 | Minor | 65101 | Door opening alarm | 10/26/2025 17:47:18 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF2397 | FLM_EM | [8 empty] | API | 10/26/2025 17:47:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026001013 | PCM-20251026-00001968 | TT-20251026-01966 | Reference_EM | Region_1 | SAK2903 | SAK2903 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mohammed Kholi | 10/26/2025 18:08:26 | 10/26/2025 19:00:19 | 10/27/2025 06:08:26 | NETECO: Mains Failure at SAK2903 @ Generator_SG | 10/26/2025 18:01:47 | Minor | 1550 | Mains Failure | 10/26/2025 18:01:47 | P3 | SRAN | sakaka | Generator_SG | 2G NSA | SAK2903 | FLM_EM | [8 empty] | API | 10/26/2025 18:08:26 | 10/26/2025 18:16:39 | 10/26/2025 19:00:12 |  |  | 10/26/2025 19:00:19 |  | Mohammed Kholi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026001021 | PCM-20251026-00001979 | TT-20251026-01978 | Reference_EM | Region_1 | SAK2903 | SAK2903 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mohammed Kholi | 10/26/2025 18:12:05 | 10/26/2025 19:00:07 | 10/27/2025 06:12:05 | Mains Failure at SAK2903-P3-USF_SRAN @ Generator_SG | 10/26/2025 18:04:00 | Minor | 65109 | Mains Failure | 10/26/2025 18:01:49 | P3 | SRAN | sakaka | Generator_SG | 2G NSA | SAK2903 | FLM_EM | [8 empty] | API | 10/26/2025 18:12:05 | 10/26/2025 18:16:40 | 10/26/2025 19:00:01 |  |  | 10/26/2025 19:00:07 |  | Mohammed Kholi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001025 | PCM-20251026-00001986 | TT-20251026-01982 | Reference_EM | Region_1 | DMH0105 | DMH0105 |  |  |  | Mahmoud Youssef Mohamed Ahmed | 10/26/2025 18:16:11 | 10/26/2025 18:16:11 | 10/27/2025 00:16:11 | Mains Failure at DMH0105-P1-HUB_SRAN @ Generator_SG | 10/26/2025 18:05:56 | Major | 65109 | Mains Failure | 10/26/2025 18:05:53 | P1 | SRAN | hafr | Generator_SG | 2G NSA | DMH0105 | FLM_EM | [8 empty] | API | 10/26/2025 18:16:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251026001029 | PCM-20251026-00001991 | TT-20251026-01987 | EM | Region_2 | RIY0380 | RIY0380 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/26/2025 18:18:11 | 10/26/2025 18:18:11 | 10/27/2025 06:18:11 | RF Unit External Power Supply Insufficient at RIY0380-P2_SRAN @ Sceco | 10/26/2025 18:04:52 | Minor | 26546 | RF Unit External Power Supply Insufficient | 10/26/2025 18:04:19 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0380 | FLM_EM | [8 empty] | API | 10/26/2025 18:18:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001030 | PCM-20251026-00001992 | TT-20251026-01988 | EM | Region_2 | RIY0448 | RIY0448 |  |  |  | Adham Adham Hassan Farghal | 10/26/2025 18:19:06 | 10/26/2025 18:19:06 | 10/27/2025 06:19:06 | RF Unit External Power Supply Insufficient at RIY0448-P2_SRAN @ Sceco | 10/26/2025 18:17:36 | Minor | 26546 | RF Unit External Power Supply Insufficient | 10/26/2025 18:17:03 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0448 | FLM_EM | [8 empty] | API | 10/26/2025 18:19:06 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026001031 | PCM-20251026-00001996 | TT-20251026-01993 | Reference_EM | Region_1 | KBR0164 | KBR0164 |  |  |  | Abdul Malik Shaik | 10/26/2025 18:19:51 | 10/27/2025 08:44:39 | 10/27/2025 06:19:51 | Mains Failure at KBR0164-P3_SRAN @ Sceco | 10/26/2025 18:11:20 | Minor | 65109 | Mains Failure | 10/26/2025 18:11:16 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0164 | FLM_EM | [8 empty] | API | 10/26/2025 18:19:51 | 10/27/2025 08:44:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026001047 | PCM-20251026-00002020 | TT-20251026-02014 | EM | Region_2 | MJM0495 | MJM0495 |  |  |  | Saeed Ud Din Muhammad Yousaf | 10/26/2025 18:28:36 | 10/27/2025 03:00:23 | 10/26/2025 22:28:36 | Door opening alarm at MJM0495-P1-HUB-WDM_SRAN @ Sceco_STB | 10/26/2025 18:28:05 | Critical | 65101 | Door opening alarm | 10/26/2025 18:28:01 | P1 | SRAN | majma | Sceco_STB | 2G NSA | MJM0495 | FLM_EM | [8 empty] | API | 10/26/2025 18:28:36 | 10/27/2025 03:00:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251026001078 | PCM-20251026-00002081 | TT-20251026-02062 | Telecom | Region_3 | YNB2970 | YNB2970 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:57:00 | 10/26/2025 18:57:00 | 10/27/2025 06:57:00 | GNSS Locked Satellites Insufficient at YNB2970-P2_SRAN @ Sceco | 10/26/2025 13:04:24 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 13:01:01 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB2970 | FLM_TE | [8 empty] | API | 10/26/2025 18:57:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001079 | PCM-20251026-00002082 | TT-20251026-02063 | Telecom | Region_3 | YNB2953 | YNB2953 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:57:13 | 10/26/2025 18:57:13 | 10/27/2025 06:57:13 | GNSS Locked Satellites Insufficient at YNB2953-P2_SRAN @ Sceco | 10/26/2025 11:54:50 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 11:51:28 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB2953 | FLM_TE | [8 empty] | API | 10/26/2025 18:57:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001080 | PCM-20251026-00002083 | TT-20251026-02064 | Telecom | Region_3 | YNB0667 | YNB0667 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:57:21 | 10/26/2025 18:57:21 | 10/27/2025 06:57:21 | GNSS Locked Satellites Insufficient at YNB0667-P2_SRAN @ Sceco | 10/26/2025 11:41:10 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 11:38:01 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB0667 | FLM_TE | [8 empty] | API | 10/26/2025 18:57:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001081 | PCM-20251026-00002084 | TT-20251026-02065 | Telecom | Region_3 | YNB0600 | YNB0600 |  |  |  | Muhammad Sajjad R3 | 10/26/2025 18:57:27 | 10/26/2025 18:57:27 | 10/27/2025 06:57:27 | GNSS Locked Satellites Insufficient at YNB0600-P3_SRAN-PC @ Sceco | 10/26/2025 12:31:50 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/26/2025 12:28:27 | P3 | SRAN | yanbu | Sceco | 2G NSA | YNB0600 | FLM_TE | [8 empty] | API | 10/26/2025 18:57:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001082 | PCM-20251026-00002085 | TT-20251026-01111 | Telecom | Region_5 | MAK0120 | MAK0120 |  |  |  | Atif Javed Javed Hussain | 10/26/2025 18:57:31 | 10/26/2025 18:57:31 | 10/26/2025 22:57:31 | 2(2G) 1(5G) sites down under MAK2088-P1-VIP,MAK0120-P1-VIP-HAJJ-DIA-HRM/MAK0120-P1-VIP-HAJJ-DIA-HRM @ Sceco | 10/26/2025 12:20:14 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 12:20:10 | VIP | 2G | makkah | Sceco | 2G SA | MAK0120-P1-VIP-HAJJ-DIA-HRM 2G,MAK2088-P1-VIP 2G | FLM_TE | MAK0120 | Results: DOWN SITE HUB MAK0120-P1-VIP-HAJJ-DIA-HRM MAK0120 MAK2088-P1-VIP MAK0120 Summary: Hub: MAK0120, Down Count: 2, Down Sites: MAK0120-P1-VIP-HAJJ-DIA-HRM, MAK2088-P1-VIP Alarm Summary: MAK0120 No Active Alarm on HUB | PCM-20251026-00002038 | approved | approved |  | sites down |  | API | 10/26/2025 18:57:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001083 | PCM-20251026-00002086 | TT-20251026-02059 | Telecom | Region_4 | JED0591 | JED0591 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 18:59:13 | 10/26/2025 18:59:13 | 10/27/2025 06:59:13 | BASE STATION ANTENNA LINE PROBLEM at JED0591-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 18:44:32 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 18:44:27 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0591 | FLM_TE |  |  | PCM-20251026-00002073 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/26/2025 18:59:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001085 | PCM-20251026-00002100 | TT-20251026-01963 | EM | Region_4 | NNL0216 | NNL0216 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 19:15:55 | 10/27/2025 03:35:41 | 10/27/2025 01:15:55 | 1(2G/3G) sites down under NNL0139-P3/NNL1M3139-P3 @ Generator_SG | 10/26/2025 18:04:54 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/26/2025 18:04:11 | P2 | 2G | adam | Generator_SG | 2G_3G SA | NNL0139-P3 | FLM_TE | NNL0216 | Results: DOWN SITE HUB NNL0139-P3 NNL0139 Summary: Hub: NNL0139, Down Count: 1, Down Sites: NNL0139-P3 Alarm Summary: NNL0139 No Active Alarm on HUB | PCM-20251026-00002071 | check locally from NNL0216 is link down with PM errors | check locally from NNL0216 is link down with PM errors |  | sites down |  | API | 10/26/2025 19:15:55 | 10/27/2025 03:35:09 | 10/27/2025 03:35:30 |  |  | 10/27/2025 03:35:41 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001088 | PCM-20251026-00002110 | TT-20251026-02093 | Telecom | Region_1 | HFBD2M5008 | HFBD0008 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 19:23:59 | 10/26/2025 21:30:45 | 10/26/2025 23:23:59 | 1(2G) sites down under HFBD0008-P1-HUB/R1_HF_HWBSC01 @ Generator_SG | 10/26/2025 19:15:43 | Critical | 21807 | OML Fault | 10/26/2025 19:15:37 | P1 | 2G | hafouf | Generator_SG | 2G SA | HFBD0008-P1-HUB | FLM_TE | HFBD0008 | Results: DOWN SITE HUB HFBD0008-P1-HUB HFBD0008 Summary: Hub: HFBD0008, Down Count: 1, Down Sites: HFBD0008-P1-HUB Alarm Summary: HFBD0008 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 19:23:59 | 10/26/2025 21:13:52 | 10/26/2025 21:30:32 |  |  | 10/26/2025 21:30:45 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001089 | PCM-20251026-00002112 | TT-20251026-02097 | Telecom | Region_6 | ZHR1M7138 | ZHR0138 | Equipment | CB_BTS | Change Port on FPFH | TALEH MUHAMMAD | 10/26/2025 19:24:40 | 10/26/2025 20:42:18 | 10/27/2025 01:24:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at ZHR1M7138-USF-CA-L800 @ Sceco | 10/26/2025 19:23:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 19:23:29 | P2 | 4G | al harja | Sceco | 5G_Cell SA | ZHR1M7138 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 19:24:40 | 10/26/2025 19:27:14 | 10/26/2025 19:28:23 | 10/26/2025 19:28:25 | 10/26/2025 19:35:50 | 10/26/2025 20:42:18 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001090 | PCM-20251026-00002118 | TT-20251026-02095 | Telecom | Region_6 | BAH1M8233 | BAH2233 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/26/2025 19:28:29 | 10/26/2025 20:23:45 | 10/27/2025 01:28:29 | 1(LTE) sites down under BAH2233-L800-P3-SBTS @ Sceco | 10/26/2025 19:20:13 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 19:20:10 | P3 | 4G | Albaha | Sceco | LTE SA | BAH2233-L800-P3-SBTS | FLM_TE | BAH2233 | Results: DOWN SITE HUB BAH2233-L800-P3-SBTS BAH2233 Summary: Hub: BAH2233, Down Count: 1, Down Sites: BAH2233-L800-P3-SBTS Alarm Summary: BAH2233 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.51.132:8080] [URL:http://10.97.51.132:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 19:28:29 | 10/26/2025 20:23:18 | 10/26/2025 20:23:32 |  |  | 10/26/2025 20:23:45 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001091 | PCM-20251026-00002119 | TT-20251026-02102 | Telecom | Region_6 | MKW0037 | MKW0037 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 19:28:48 | 10/27/2025 00:23:00 | 10/27/2025 07:28:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKW0037-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 19:28:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 19:27:58 | P3 | 2G | makhwa | Sceco | 5G_Cell SA | MKW0037 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 19:28:48 | 10/26/2025 22:01:56 | 10/27/2025 00:22:47 |  |  | 10/27/2025 00:23:00 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001092 | PCM-20251026-00002120 | TT-20251026-02103 | Telecom | Region_2 | RIYA2U6763 | RIYA6063 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 19:28:53 | 10/27/2025 08:08:21 | 10/27/2025 01:28:53 | Cell Unavailable at RIYA2U6763-CA-P3 @ Sceco | 10/26/2025 19:26:09 | Major | 29240 | Cell Unavailable | 10/26/2025 19:24:36 | P3 | 4G | riyadh | Sceco | LTE SA | RIYA2U6763 | FLM_TE | [8 empty] | API | 10/26/2025 19:28:53 | 10/27/2025 08:08:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001093 | PCM-20251026-00002121 | TT-20251026-02104 | Telecom | Region_2 | RIYA6063 | RIYA6063 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 19:29:50 | 10/27/2025 08:08:21 | 10/27/2025 07:29:50 | RF Unit Maintenance Link Failure at RIYA6063-P3_SRAN @ Sceco | 10/26/2025 19:26:14 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 19:24:32 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6063 | FLM_TE | [8 empty] | API | 10/26/2025 19:29:50 | 10/27/2025 08:08:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001095 | PCM-20251026-00002125 | TT-20251026-02109 | Telecom | Region_1 | RDF0015 | RDF0015 | Equipment | SFP_BTS | Replace SFP | Syed Fawad Ali | 10/26/2025 19:33:27 | 10/27/2025 00:36:55 | 10/27/2025 07:33:27 | RF Unit Maintenance Link Failure at RDF0015-P3_SRAN @ Sceco_STB | 10/26/2025 19:29:52 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 19:28:09 | P3 | SRAN | sakaka | Sceco_STB | 2G NSA | RDF0015 | FLM_TE | [8 empty] | API | 10/26/2025 19:33:27 | 10/26/2025 19:42:11 | 10/27/2025 00:17:23 | 10/27/2025 00:17:27 | 10/27/2025 00:17:34 | 10/27/2025 00:36:55 |  | Syed Fawad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001096 | PCM-20251026-00002126 | TT-20251026-02111 | Telecom | Region_4 | JED1M8134 | JED2134 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 19:34:29 | 10/26/2025 20:41:35 | 10/27/2025 01:34:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8134-CA-L800-P3 @ Sceco | 10/26/2025 19:33:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 19:33:49 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8134 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 19:34:29 | 10/26/2025 20:41:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251026001097 | PCM-20251026-00002127 | TT-20251026-02035 | Reference_telecom | Region_2 | RIY2M8796 | RIY2796 |  |  |  | Waseem Shahzad Ghulam Rasool | 10/26/2025 19:34:52 | 10/27/2025 08:07:44 | 10/27/2025 07:34:52 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8796-P2-L900-L800 @ Sceco | 10/26/2025 15:34:01 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 15:33:58 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M8796 | FLM_TE |  |  | PCM-20251026-00002047 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 19:34:52 | 10/27/2025 08:07:03 | 10/27/2025 08:07:44 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001098 | PCM-20251026-00002129 | TT-20251026-02061 | Reference_telecom | Region_1 | JBKH2M7111 | JBKH0111 |  |  |  | Mohamed Abdelaziz | 10/26/2025 19:36:02 | 10/27/2025 00:13:29 | 10/27/2025 07:36:02 | Cell RX Channel Interference Noise Power Unbalanced at JBKH2M7111-L800-P1 @ Generator_SG | 10/26/2025 15:55:30 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 15:55:27 | P1 | 4G | jubail | Generator_SG | 2G NSA | JBKH2M7111 | FLM_TE |  |  | PCM-20251026-00002080 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 19:36:02 | 10/27/2025 00:13:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001099 | PCM-20251026-00002130 | TT-20251026-02091 | EM | Region_1 | JBKH0577 | JBKH0577 |  |  |  | Mohamed Abdelaziz | 10/26/2025 19:36:28 | 10/27/2025 00:13:29 | 10/27/2025 01:36:28 | 1(2G/3G) sites down under JBKH0577-P3-USF/R1_JB_HWBSC01 @ Power Cube | 10/26/2025 19:17:18 | Major | 21825 | CSL Fault | 10/26/2025 19:17:17 | P3 | SRAN | jubail | Power Cube | 2G_3G SA | JBKH0577-P3-USF | FLM_TE | JBKH0577 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : JBKH0577 DIR JBKH0095,Kindly visit the link and perform the HC at mentioned link . | PCM-20251026-00002114 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : JBKH0577 DIR JBKH0095,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : JBKH0577 DIR JBKH0095,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/26/2025 19:36:28 | 10/27/2025 00:13:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001100 | PCM-20251026-00002131 | TT-20251026-02082 | Reference_telecom | Region_3 | MDN2M8887 | MDN2887 |  |  |  | TAUSEEF ILYAS | 10/26/2025 19:36:52 | 10/26/2025 23:25:22 | 10/27/2025 07:36:52 | Cell RX Channel Interference Noise Power Unbalanced at MDN2M8887-P2-L800 @ Sceco | 10/26/2025 16:14:19 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 16:14:15 | P2 | 4G | madinah | Sceco | 2G NSA | MDN2M8887 | FLM_TE |  |  | PCM-20251026-00002098 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 19:36:52 | 10/26/2025 23:25:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001101 | PCM-20251026-00002133 | TT-20251026-02117 | EM | Region_3 | MDQS2437 | MDQS2437 |  |  |  | Ayman Mohamed Sayed Ahmed | 10/26/2025 19:40:42 | 10/26/2025 19:40:42 | 10/27/2025 07:40:42 | NETECO: Water Alarm at MDQS2437 @ Generator_DG | 10/26/2025 19:34:24 | Minor | 5250 | Water Alarm | 10/26/2025 19:34:24 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2437 | FLM_EM | [8 empty] | API | 10/26/2025 19:40:42 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001102 | PCM-20251026-00002134 | TT-20251026-02118 | EM | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 19:41:13 | 10/26/2025 19:41:13 | 10/27/2025 07:41:13 | NETECO: Door Status Sensor Alarm at KFKM0784 @ Generator_SG | 10/26/2025 19:40:50 | Minor | 5152 | Door Status Sensor Alarm | 10/26/2025 19:40:50 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0784 | FLM_EM | [8 empty] | API | 10/26/2025 19:41:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251026001103 | PCM-20251026-00002136 | TT-20251026-02120 | Reference_EM | [7 empty] | 10/26/2025 19:42:14 | 10/26/2025 19:42:14 | 10/27/2025 07:42:14 | NETECO: AC Failure at MDTB2555 @ Generator_SG | 10/26/2025 19:35:56 | Minor | 10202 | AC Failure | 10/26/2025 19:35:56 | P3 | SRAN |  | Generator_SG | 2G NSA | MDTB2555 | FLM_EM | [8 empty] | API | 10/26/2025 19:42:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001105 | PCM-20251026-00002140 | TT-20251026-01804 | EM | Region_4 | JED0947 | JED0947 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 19:51:47 | 10/26/2025 19:51:47 | 10/27/2025 01:51:47 | 1(2G/5G) sites down under JED2886-P3/JED2886-P3 @ Generator_SG | 10/26/2025 16:31:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 16:31:45 | P2 | 2G | jeddah | Sceco | 2G_5G SA | JED2886-P3 | FLM_TE | JED0947 | JED0947 Node Rebooted | PCM-20251026-00002109 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 19:51:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001107 | PCM-20251026-00002142 | TT-20251026-02126 | Reference_EM | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 19:55:40 | 10/26/2025 19:55:40 | 10/27/2025 07:55:40 | NETECO: AC Failure at KFKM0784 @ Generator_SG | 10/26/2025 19:49:25 | Minor | 10202 | AC Failure | 10/26/2025 19:49:25 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0784 | FLM_EM | [8 empty] | API | 10/26/2025 19:55:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001108 | PCM-20251026-00002143 | TT-20251026-02127 | EM | Region_6 | MKW1M8121 | MKW2121 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/26/2025 19:56:11 | 10/26/2025 19:56:11 | 10/27/2025 07:56:11 | RECTIFIER MODULE FAILURE at MKW1M8121-L8-L18-SBTS-P3 @ Generator_SG | 10/26/2025 19:48:16 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 19:48:05 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8121 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 19:56:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001109 | PCM-20251026-00002144 | TT-20251026-02128 | Reference_telecom | Region_4 | QUN0338 | QUN0338 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 19:58:15 | 10/26/2025 21:40:39 | 10/27/2025 07:58:15 | ReplaceableUnitProblem observed in QUN0338_01 towards 10.21.74.210 @ Sceco | 10/26/2025 07:58:02 | Minor |  | ReplaceableUnitProblem | 10/26/2025 07:57:57 | P2 | 2G | qunfuddah | Sceco | TX NSA | QUN0338 | FLM_TE | [8 empty] | API | 10/26/2025 19:58:15 | 10/26/2025 21:40:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001110 | PCM-20251026-00002145 | TT-20251026-02129 | Telecom | Region_6 | ABH0288 | ABH0288 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/26/2025 19:58:16 | 10/27/2025 01:40:54 | 10/27/2025 07:58:16 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH0288-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 19:57:40 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 19:57:33 | P2 | 2G | abha | Sceco | 5G_Cell SA | ABH0288 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 19:58:16 | 10/26/2025 23:23:09 | 10/27/2025 01:40:44 |  |  | 10/27/2025 01:40:54 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001111 | PCM-20251026-00002147 | TT-20251026-02130 | Reference_EM | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/26/2025 19:59:18 | 10/26/2025 19:59:18 | 10/27/2025 07:59:18 | Mains Failure at KFKM0784-P3_SRAN @ Generator_SG | 10/26/2025 19:49:32 | Minor | 65109 | Mains Failure | 10/26/2025 19:49:28 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0784 | FLM_EM | [8 empty] | API | 10/26/2025 19:59:18 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001112 | PCM-20251026-00002149 | TT-20251026-02133 | Reference_EM | Region_1 | DMHF2074 | DMHF2074 |  |  |  | Emad fawzi eldebsi | 10/26/2025 20:03:57 | 10/26/2025 20:03:57 | 10/27/2025 08:03:57 | Mains Failure at DMHF2074-P3_SRAN @ Generator_SG | 10/26/2025 19:53:47 | Minor | 65109 | Mains Failure | 10/26/2025 19:53:44 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | DMHF2074 | FLM_EM | [8 empty] | API | 10/26/2025 20:03:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001113 | PCM-20251026-00002150 | TT-20251026-02135 | Reference_EM | Region_3 | MDN2880 | MDN2880 |  |  |  | Muhamad Hanif Ahmad | 10/26/2025 20:05:29 | 10/26/2025 20:05:29 | 10/27/2025 08:05:29 | Door opening alarm at MDN2880-P3_SRAN @ Sceco | 10/26/2025 20:05:19 | Minor | 65101 | Door opening alarm | 10/26/2025 20:05:15 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2880 | FLM_EM | [8 empty] | API | 10/26/2025 20:05:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001114 | PCM-20251026-00002151 | TT-20251026-02131 | EM | Region_2 | RAS2U6110 | RAS6010 |  |  |  | Mohamed Alfatih Mohamed Eltayeb Mohamed | 10/26/2025 20:05:59 | 10/26/2025 20:05:59 | 10/27/2025 00:05:59 | 1(2G/3G/LTE) sites down under RAS6010-P1-SHOP/R2_BR1_HWBSC01 @ Sceco | 10/26/2025 19:59:07 | Critical | 21825 | CSL Fault | 10/26/2025 19:59:02 | P1 | 2G | al rass | Sceco | 2G_3G_LTE SA | RAS6010-P1-SHOP | FLM_EM | RAS6010 | Results: DOWN SITE HUB RAS6010-P1-SHOP RAS6010 Summary: Hub: RAS6010, Down Count: 1, Down Sites: RAS6010-P1-SHOP Alarm Summary: RAS6010 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 20:05:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001115 | PCM-20251026-00002153 | TT-20251026-02138 | Telecom | Region_1 | HFSW2019 | HFSW2019 | Transsmission | SFP_Transmission | Reset SFP | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 20:06:31 | 10/26/2025 21:25:06 | 10/27/2025 08:06:31 | SFP Removed at HFSW2019 on 10.248.32.136 @ Generator_SG | 10/26/2025 20:05:22 | Minor | SFP Removed | SFP Removed | 10/26/2025 20:05:14 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFSW2019 | FLM_TE | [8 empty] | API | 10/26/2025 20:06:31 | 10/26/2025 21:13:53 | 10/26/2025 21:24:41 |  |  | 10/26/2025 21:25:06 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001116 | PCM-20251026-00002154 | TT-20251026-02139 | Telecom | Region_2 | RIY2718 | RIY2718 | Equipment | CB_BTS | Switch on CB on Rectifier | Muhammad Naseer Muhammad Nazir | 10/26/2025 20:06:32 | 10/26/2025 21:48:13 | 10/27/2025 08:06:32 | BBU DC Output Out of Range at RIY2718-P3_SRAN-PC @ Sceco | 10/26/2025 20:03:38 | Minor | 26112 | BBU DC Output Out of Range | 10/26/2025 20:02:06 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2718 | FLM_TE | [8 empty] | API | 10/26/2025 20:06:32 | 10/26/2025 20:26:51 | 10/26/2025 21:47:45 |  |  | 10/26/2025 21:48:13 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001117 | PCM-20251026-00002155 | TT-20251026-02140 | Telecom | Region_2 | RIY2718 | RIY2718 | Equipment | CB_BTS | Switch on CB on Rectifier | Muhammad Naseer Muhammad Nazir | 10/26/2025 20:07:33 | 10/26/2025 21:49:53 | 10/27/2025 08:07:33 | RF Unit Maintenance Link Failure at RIY2718-P3_SRAN-PC @ Sceco | 10/26/2025 20:03:52 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 20:02:09 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2718 | FLM_TE | [8 empty] | API | 10/26/2025 20:07:33 | 10/26/2025 20:27:06 | 10/26/2025 21:49:30 |  |  | 10/26/2025 21:49:53 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001118 | PCM-20251026-00002156 | TT-20251026-02116 | Telecom | Region_4 | JED2134 | JED2134 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 20:09:18 | 10/26/2025 20:41:36 | 10/27/2025 02:09:18 | 2(2G) 1(LTE) 2(5G) sites down under JED2134-P3,JED2342-P3/JED2342-P3 @ Generator_SG | 10/26/2025 19:37:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 19:37:00 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED2342-P3 2G_5G,JED2134-P3 2G_LTE | FLM_TE | JED2134 | DOWN SITE HUB TX FB JED2342 JED2342 Visibility down at HUB , kindly check locally JED2134 JED2134 LOS to Air Scale | PCM-20251026-00002146 | DOWN SITE HUB TX FB JED2342 JED2342 Visibility down at HUB , kindly check locally JED2134 JED2134 LOS to Air Scale | DOWN SITE HUB TX FB JED2342 JED2342 Visibility down at HUB , kindly check locally JED2134 JED2134 LOS to Air Scale |  | sites down |  | API | 10/26/2025 20:09:18 | 10/26/2025 20:41:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001119 | PCM-20251026-00002158 | TT-20251026-02142 | Telecom | Region_4 | JED1M7878 | JED0878 |  |  |  | Mohammed Ramadan A Abu Abid | 10/26/2025 20:10:09 | 10/27/2025 06:02:02 | 10/27/2025 02:10:09 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7878-P1-CA-L900-L800-SBTS @ Sceco | 10/26/2025 20:09:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:09:14 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7878 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 20:10:09 | 10/27/2025 06:02:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001120 | PCM-20251026-00002161 | TT-20251026-02145 | Telecom | Region_2 | RIY2718 | RIY2718 | Equipment | CB_BTS | Switch on CB on Rectifier | Muhammad Naseer Muhammad Nazir | 10/26/2025 20:10:39 | 10/26/2025 21:47:38 | 10/27/2025 02:10:39 | NR Cell Unavailable at RIY2718-P3_SRAN-PC @ Sceco | 10/26/2025 20:03:44 | Major | 29841 | NR Cell Unavailable | 10/26/2025 20:02:12 | P3 | SRAN | riyadh | Sceco | 5G SA | RIY2718 | FLM_TE | [8 empty] | API | 10/26/2025 20:10:39 | 10/26/2025 20:27:21 | 10/26/2025 20:33:54 | 10/26/2025 20:33:58 | 10/26/2025 21:36:45 | 10/26/2025 21:47:38 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001121 | PCM-20251026-00002163 | TT-20251026-01961 | Telecom | Region_4 | JED2564 | JED2564 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 20:10:46 | 10/27/2025 08:57:18 | 10/27/2025 02:10:46 | 1(2G) 1(LTE) 1(5G) sites down under JED2564-NR2.6-P3,JDRS2225-P3/JDRS2225-P3 @ Sceco | 10/26/2025 18:04:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 18:04:04 | P3 | 2G | jeddah | Generator_SG | 2G_5G SA | JED2564-NR2.6-P3 5G,JDRS2225-P3 2G | FLM_TE | JED2564 | JED2564 | PCM-20251026-00002157 | JED2564 | JED2564 |  | sites down |  | API | 10/26/2025 20:10:46 | 10/27/2025 08:57:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001123 | PCM-20251026-00002167 | TT-20251026-02149 | Telecom | Region_1 | HFSW2019 | HFSW2019 | Transsmission | SFP_Transmission | Reset SFP | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 20:12:43 | 10/26/2025 21:24:35 | 10/27/2025 08:12:43 | SFP Removed at HFSW2019-2 on 10.248.32.137 @ Generator_SG | 10/26/2025 20:08:48 | Minor | SFP Removed | SFP Removed | 10/26/2025 20:11:17 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFSW2019 | FLM_TE | [8 empty] | API | 10/26/2025 20:12:43 | 10/26/2025 21:13:54 | 10/26/2025 21:21:06 |  |  | 10/26/2025 21:24:35 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001124 | PCM-20251026-00002168 | TT-20251026-02141 | EM | Region_6 | DAR0951 | DAR0951 |  |  |  | Muhammad Tayyab | 10/26/2025 20:14:59 | 10/26/2025 20:14:59 | 10/27/2025 00:14:59 | 1(2G/3G/LTE) sites down under DAR0951-P1/DAR0951-P1 @ Sceco | 10/26/2025 20:07:06 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 20:07:01 | P1 | 2G | dair | Sceco | 2G_3G_LTE SA | DAR0951-P1 | FLM_EM | DAR0951 | Results: DOWN SITE HUB DAR0951-P1 DAR0951 Summary: Hub: DAR0951, Down Count: 1, Down Sites: DAR0951-P1 Alarm Summary: DAR0951 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 20:14:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001125 | PCM-20251026-00002169 | TT-20251026-02152 | Telecom | Region_1 | DAM6001 | DAM6001 |  |  |  | Meraj Husain Idd Baksh | 10/26/2025 20:15:50 | 10/26/2025 20:46:46 | 10/27/2025 08:15:50 | ALC Controlling Threshold Crossing (Minor) at DAM6001-DCU2 @ Sceco | 10/26/2025 20:11:24 | Minor | 29804 | ALC Controlling Threshold Crossing (Minor) | 10/26/2025 20:11:20 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6001 | FLM_TE | [8 empty] | API | 10/26/2025 20:15:50 | 10/26/2025 20:46:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001127 | PCM-20251026-00002173 | TT-20251026-02157 | Telecom | Region_1 | Arar-0518-NE40E-X8-PE-01 | ARR0518 |  |  |  | Muhammad Zubair Guilzar | 10/26/2025 20:21:00 | 10/26/2025 21:42:22 | 10/27/2025 08:21:00 | Overlow Input Power of Optical Module at Arar-0518-NE40E-X8-PE-01 @ Sceco_STB | 10/26/2025 20:19:46 | Minor | 101-3067697 | Overlow Input Power of Optical Module | 10/26/2025 20:20:34 | P1 | IPRAN | arar | Sceco_STB | IPRAN NSA | Arar-0518-NE40E-X8-PE-01 | FLM_TE | [8 empty] | API | 10/26/2025 20:21:00 | 10/26/2025 21:42:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251026001129 | PCM-20251026-00002175 | TT-20251026-02159 | Telecom | Region_6 | ARF0186 | ARF0186 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 20:23:04 | 10/26/2025 22:45:25 | 10/27/2025 08:23:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at ARF0186-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 20:22:21 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:22:13 | P2 | 2G | al harja | Sceco | 5G_Cell SA | ARF0186 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 20:23:04 | 10/26/2025 22:43:49 | 10/26/2025 22:45:21 | 10/26/2025 22:45:25 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001130 | PCM-20251026-00002183 | TT-20251026-02160 | Telecom | Region_4 | JED2928 | JED2928 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 20:28:29 | 10/26/2025 21:40:39 | 10/27/2025 02:28:29 | 1(5G) sites down under JED2928-G9-L18-NNR2.6-SBTS-P3 @ Sceco | 10/26/2025 20:20:26 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 20:20:23 | P3 | 2G | qunfuddah | Sceco | 5G SA | JED2928-G9-L18-NNR2.6-SBTS-P3 | FLM_TE | JED2928 | Results: DOWN SITE HUB JED2928-G9-L18-NNR2.6-SBTS-P3 JED2928 Summary: Hub: JED2928, Down Count: 1, Down Sites: JED2928-G9-L18-NNR2.6-SBTS-P3 Alarm Summary: JED2928 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.15.140:8080] [URL:http://10.88.15.140:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 20:28:29 | 10/26/2025 21:40:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001131 | PCM-20251026-00002186 | TT-20251026-02166 | Telecom | Region_4 | JED1M8106 | JED2106 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 20:29:15 | 10/26/2025 20:29:15 | 10/27/2025 02:29:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8106-P3-CA-L800 @ Sceco | 10/26/2025 20:28:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:28:23 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8106 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 20:29:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001135 | PCM-20251026-00002201 | TT-20251026-02086 | Reference_telecom | Region_6 | ARS1M7122 | ARS0122 | Equipment | SFP_BTS | Clean SFP | Zeshan Ali Adnan | 10/26/2025 20:44:27 | 10/27/2025 02:05:13 | 10/27/2025 08:44:27 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at ARS1M7122-CA-L800-SBTS-P3 @ Sceco | 10/26/2025 19:12:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 19:11:51 | P3 | 4G | jizan | Sceco | 5G_Cell SA | ARS1M7122 | FLM_TE |  |  | PCM-20251026-00002101 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 20:44:27 | 10/26/2025 23:26:34 | 10/27/2025 02:04:54 |  |  | 10/27/2025 02:05:13 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001136 | PCM-20251026-00002202 | TT-20251026-02162 | Reference_telecom | Region_4 | JED1M7667 | JED0667 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 20:45:43 | 10/27/2025 08:57:18 | 10/27/2025 08:45:43 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED1M7667-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/26/2025 20:21:42 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:21:32 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7667 | FLM_TE |  |  | PCM-20251026-00002178 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/26/2025 20:45:43 | 10/27/2025 08:57:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001137 | PCM-20251026-00002206 | TT-20251026-02183 | EM | Region_4 | HBI1M8412 | HBI2412 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/26/2025 20:48:23 | 10/26/2025 20:48:23 | 10/27/2025 08:48:23 | RECTIFIER MODULE FAILURE at HBI1M8412-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/26/2025 20:40:18 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 20:40:08 | P3 | 4G | jeddah | Generator_DG | LTE NSA | HBI1M8412 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 20:48:23 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001138 | PCM-20251026-00002210 | TT-20251026-02182 | Reference_telecom | Region_5 | MAK0052 | MAK0052 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/26/2025 20:52:15 | 10/26/2025 20:52:15 | 10/27/2025 08:52:15 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at MAK0052-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/26/2025 20:42:25 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:42:14 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0052 | FLM_TE |  |  | PCM-20251026-00002204 | FLM need to check SFP, Fiber and HW at site. | FLM need to check SFP, Fiber and HW at site. |  |  |  | API | 10/26/2025 20:52:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001139 | PCM-20251026-00002212 | TT-20251026-02188 | Telecom | Region_4 | JED1M7787 | JED0787 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 20:53:02 | 10/26/2025 20:53:02 | 10/27/2025 02:53:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7787-CA-L900-L800-SBTS @ Sceco | 10/26/2025 20:52:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:52:06 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7787 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 20:53:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001142 | PCM-20251026-00002215 | TT-20251026-02195 | Telecom | Region_4 | JED1M7278 | JED0278 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 20:56:07 | 10/26/2025 20:56:07 | 10/27/2025 02:56:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7278-CA-L900-L800-SBTS @ Sceco | 10/26/2025 20:55:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:54:54 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7278 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 20:56:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001144 | PCM-20251026-00002216 | TT-20251026-02186 | Telecom | Region_2 | SRIY2S7386 | SRIY0386 |  |  |  | Asad Ali Nadiq Khan | 10/26/2025 20:57:59 | 10/27/2025 04:17:32 | 10/27/2025 02:57:59 | 1(LTE) sites down under SRIY0386-P3_SRAN @ Sceco | 10/26/2025 20:50:10 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/26/2025 20:49:37 | P3 | 4G | riyadh | Sceco | LTE SA | SRIY0386-P3 | FLM_TE | SRIY0386 | Results: DOWN SITE HUB SRIY0386-P3 SRIY0386 Summary: Hub: SRIY0386, Down Count: 1, Down Sites: SRIY0386-P3 Alarm Summary: SRIY0386 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 20:57:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001145 | PCM-20251026-00002217 | TT-20251026-02189 | Telecom | Region_6 | BAH1M7005 | BAH0005 | Equipment | BSS_HW_Stuck | Reset RRU | SHAH KHALID | 10/26/2025 20:58:01 | 10/26/2025 21:33:12 | 10/27/2025 00:58:01 | 1(LTE) sites down under BAH0005-G9-L8-L18-L21-SBTS-P1-VIP-SHOP-HUB-WDM @ Sceco_STB | 10/26/2025 20:49:42 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 20:49:40 | VIP | 4G | Albaha | Sceco_STB | LTE SA | BAH0005-G9-L8-L18-L21-SBTS-P1-VIP-SHOP-HUB-WDM | FLM_TE | BAH0005 | Results: DOWN SITE HUB BAH0005-G9-L8-L18-L21-SBTS-P1-VIP-SHOP-HUB-WDM BAH0005 Summary: Hub: BAH0005, Down Count: 1, Down Sites: BAH0005-G9-L8-L18-L21-SBTS-P1-VIP-SHOP-HUB-WDM Alarm Summary: BAH0005 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.103.247.100:8080] [URL:http://10.103.247.100:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 20:58:01 | 10/26/2025 21:01:05 | 10/26/2025 21:01:24 | 10/26/2025 21:01:48 | 10/26/2025 21:02:01 | 10/26/2025 21:33:12 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001146 | PCM-20251026-00002218 | TT-20251026-02197 | Reference_telecom | Region_1 | SMN0850 | SMN0850 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/26/2025 20:58:12 | 10/27/2025 02:19:23 | 10/27/2025 02:58:12 | RF Unit VSWR Threshold Crossed at SMN0850-P2-USF_SRAN @ Generator_DG | 10/26/2025 17:58:17 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/26/2025 17:58:05 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0850 | FLM_TE | [8 empty] | API | 10/26/2025 20:58:12 | 10/27/2025 02:19:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001147 | PCM-20251026-00002219 | TT-20251026-02190 | EM | Region_6 | ARS0410 | ARS0410 |  |  |  | Khurram Nawaz Muhammad Akram | 10/26/2025 20:58:29 | 10/26/2025 20:58:29 | 10/27/2025 02:58:29 | 1(2G/3G/5G) sites down under ARS0410-P3/ARS0410-P3 @ Sceco | 10/26/2025 20:50:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 20:50:23 | P3 | 2G | jizan | Sceco | 2G_3G_5G SA | ARS0410-P3 | FLM_EM | ARS0410 | Results: DOWN SITE HUB ARS0410-P3 ARS0410 Summary: Hub: ARS0410, Down Count: 1, Down Sites: ARS0410-P3 Alarm Summary: ARS0410 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/26/2025 20:58:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001150 | PCM-20251026-00002224 | TT-20251026-02193 | Telecom | Region_4 | GMK1M7167 | GMK0167 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 20:59:59 | 10/26/2025 21:19:30 | 10/27/2025 02:59:59 | 1(LTE) sites down under GMK0167-L800-SBTS-P3 @ Generator_SG | 10/26/2025 20:51:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 20:51:54 | P2 | 4G | qunfuddah | Generator_SG | LTE SA | GMK0167-L800-SBTS-P3 | FLM_TE | GMK0167 | Results: DOWN SITE HUB GMK0167-L800-SBTS-P3 GMK0167 Summary: Hub: GMK0167, Down Count: 1, Down Sites: GMK0167-L800-SBTS-P3 Alarm Summary: GMK0167 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.23.132:8080] [URL:http://10.88.23.132:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 20:59:59 | 10/26/2025 21:19:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001152 | PCM-20251026-00002228 | TT-20251026-02201 | Reference_telecom | Region_6 | BHAB9036 | BHAB9036 |  |  |  | Fawad Khan | 10/26/2025 21:03:37 | 10/27/2025 00:29:45 | 10/27/2025 09:03:37 | As per BO request NOKIA MW link BHAB9036-MRD0092 as observed ACM flapping | 10/26/2025 21:02:03 | Minor | 113388 | LOF | 10/26/2025 21:02:05 | P1 | Repeater | namas | Sceco_STB | TX NSA | BHAB9036-MRD0092 | FLM_TE | [8 empty] | API | 10/26/2025 21:03:37 | 10/27/2025 00:29:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001153 | PCM-20251026-00002229 | TT-20251026-02202 | EM | Region_4 | RYMK1M7533 | RYMK0533 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ehab Ali Mohamed Abdou | 10/26/2025 21:05:25 | 10/26/2025 23:54:38 | 10/27/2025 09:05:25 | RECTIFIER MODULE FAILURE at RYMK1M7533-L800-SBTS @ Sceco_STB | 10/26/2025 20:57:13 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/26/2025 20:57:07 | P2 | 4G | taif | Sceco_STB | LTE NSA | RYMK1M7533 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/26/2025 21:05:25 | 10/26/2025 21:21:18 | 10/26/2025 22:25:33 | 10/26/2025 22:25:37 | 10/26/2025 23:11:04 | 10/26/2025 23:54:38 |  | Ehab Ali Mohamed Abdou |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001154 | PCM-20251026-00002230 | TT-20251026-02204 | Telecom | Region_4 | JED1M7933 | JED0933 |  |  |  | Nazeer Mohammed | 10/26/2025 21:06:58 | 10/26/2025 21:06:58 | 10/27/2025 01:06:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7933-CA-L900-L800-FWA-P1-VIP @ Generator_SG | 10/26/2025 21:06:18 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:06:12 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7933 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 21:06:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001155 | PCM-20251026-00002231 | TT-20251026-02206 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/26/2025 21:08:32 | 10/27/2025 08:53:03 | 10/27/2025 09:08:32 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/26/2025 21:00:33 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 21:00:23 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 21:08:32 | 10/27/2025 08:53:03 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001156 | PCM-20251026-00002233 | TT-20251026-02168 | Telecom | Region_4 | HAW0293 | HAW0293 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/26/2025 21:09:44 | 10/27/2025 07:58:29 | 10/27/2025 09:09:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAW0293-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 20:28:50 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:28:46 | P2 | 2G | taif | Sceco | 5G_Cell SA | HAW0293 | FLM_TE |  |  | PCM-20251026-00002209 | No Power Issue | No Power Issue |  |  |  | API | 10/26/2025 21:09:44 | 10/27/2025 07:58:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001158 | PCM-20251026-00002242 | TT-20251026-02220 | Telecom | Region_4 | JED1M8243 | JED2243 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/26/2025 21:15:45 | 10/26/2025 21:15:45 | 10/27/2025 09:15:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8243-L800-CA-SBTS-P3 @ Sceco | 10/26/2025 21:15:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:14:48 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8243 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 21:15:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001160 | PCM-20251026-00002248 | TT-20251026-02228 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/26/2025 21:19:53 | 10/27/2025 08:57:18 | 10/27/2025 09:19:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/26/2025 21:19:05 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:18:57 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 21:19:53 | 10/27/2025 08:57:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001161 | PCM-20251026-00002251 | TT-20251026-02207 | Telecom | Region_6 | RYAB0635 | RYAB0635 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/26/2025 21:21:42 | 10/27/2025 05:29:08 | 10/27/2025 03:21:42 | 3(2G) 3(3G) 1(LTE) 3(5G) sites down under RYAB0635-P3,RYAB0637-P2-USF,RYAB0638-P3/RYAB1M3638-P3 @ Sceco | 10/26/2025 21:06:10 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/26/2025 21:05:32 | P3 | 2G | tathleeth | Sceco | 3G SA | RYAB0638-P3 3G,RYAB0637-P2-USF 3G,RYAB0635-P3 3G | FLM_TE | RYAB0635 | Hub: RYAB0635 We are observing flapped Frame ID, LOF, High BER kindly send team to check locally | PCM-20251026-00002239 | Hub: RYAB0635 We are observing flapped Frame ID, LOF, High BER kindly send team to check locally | Hub: RYAB0635 We are observing flapped Frame ID, LOF, High BER kindly send team to check locally |  | sites down |  | API | 10/26/2025 21:21:42 | 10/26/2025 23:47:41 | 10/26/2025 23:47:56 |  |  | 10/26/2025 23:48:03 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001162 | PCM-20251026-00002254 | TT-20251026-01377 | Reference_telecom | Region_4 | JED0550 | JED0550 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 21:22:44 | 10/26/2025 21:22:44 | 10/27/2025 03:22:44 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0550-P2 @ Sceco | 10/26/2025 14:25:02 | Major | 7602 | BCF NOTIFICATION | 10/26/2025 14:24:48 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0550 | FLM_TE |  |  | PCM-20251026-00001416 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:22:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001163 | PCM-20251026-00002256 | TT-20251026-02236 | Reference_telecom | Region_6 | ABBS0151 | ABBS0151 |  |  |  | Manzoor Ahmed | 10/26/2025 21:24:32 | 10/26/2025 22:01:59 | 10/27/2025 09:24:32 | ReplaceableUnitProblem observed in ABBS0151 towards 10.221.244.246 @ Generator_SG | 10/26/2025 09:24:22 | Minor |  | ReplaceableUnitProblem | 10/26/2025 09:24:18 | P3 | 2G | Albaha | Generator_SG | TX NSA | ABBS0151 | FLM_TE | [8 empty] | API | 10/26/2025 21:24:32 | 10/26/2025 22:01:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001164 | PCM-20251026-00002258 | TT-20251026-02222 | EM | Region_4 | BHR0308 | BHR0308 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/26/2025 21:25:26 | 10/26/2025 21:25:26 | 10/27/2025 01:25:26 | 1(LTE/5G) sites down under BHR0308-P1-HUB-CA-L800-SBTS @ Sceco | 10/26/2025 21:13:56 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 21:13:54 | P1 | 2G | jeddah | Sceco | LTE_5G SA | BHR0308-P1-HUB-CA-L800-SBTS | FLM_TE | BHR0308 | Results: DOWN SITE HUB BHR0308-P1-HUB-CA-L800-SBTS BHR0308 Summary: Hub: BHR0308, Down Count: 1, Down Sites: BHR0308-P1-HUB-CA-L800-SBTS Alarm Summary: BHR0308 No Active Alarm on HUB | PCM-20251026-00002253 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 21:25:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001165 | PCM-20251026-00002261 | TT-20251026-01797 | Reference_telecom | Region_4 | TAF0141 | TAF0141 |  |  |  | Ahmad Kamal Abdelmawla | 10/26/2025 21:31:24 | 10/26/2025 21:31:24 | 10/27/2025 03:31:24 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TAF0141-P2 @ Sceco | 10/26/2025 16:28:35 | Major | 7607 | TRX OPERATION DEGRADED | 10/26/2025 16:28:31 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TAF0141 | FLM_TE |  |  | PCM-20251026-00001784 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:31:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001166 | PCM-20251026-00002262 | TT-20251026-02248 | Telecom | Region_4 | JED0628 | JED0628 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 21:35:24 | 10/26/2025 21:35:24 | 10/27/2025 09:35:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0628-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 21:34:40 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:34:34 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0628 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 21:35:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001167 | PCM-20251026-00002263 | TT-20251026-02250 | Telecom | Region_4 | JED1M7515 | JED0515 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 21:36:27 | 10/26/2025 21:36:27 | 10/27/2025 03:36:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7515-CA-L900-L800-SBTS @ Sceco | 10/26/2025 21:35:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:35:24 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7515 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 21:36:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001168 | PCM-20251026-00002265 | TT-20251026-02223 | Reference_telecom | Region_4 | RAB2116 | RAB2116 |  |  |  | Khizer Hayat | 10/26/2025 21:37:05 | 10/26/2025 22:28:19 | 10/27/2025 09:37:05 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB2116-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 21:12:39 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:12:28 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | RAB2116 | FLM_TE |  |  | PCM-20251026-00002244 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 21:37:05 | 10/26/2025 22:28:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001169 | PCM-20251026-00002266 | TT-20251026-02217 | Reference_telecom | Region_4 | RAB0719 | RAB0719 |  |  |  | Khizer Hayat | 10/26/2025 21:37:25 | 10/26/2025 22:28:20 | 10/27/2025 09:37:25 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0719-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 21:09:24 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:09:16 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0719 | FLM_TE |  |  | PCM-20251026-00002240 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 21:37:25 | 10/26/2025 22:28:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001170 | PCM-20251026-00002267 | TT-20251026-02231 | Reference_telecom | Region_4 | RAB0366 | RAB0366 |  |  |  | Khizer Hayat | 10/26/2025 21:37:46 | 10/26/2025 22:28:20 | 10/27/2025 09:37:46 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3 @ Sceco | 10/26/2025 21:16:52 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:16:46 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0366 | FLM_TE |  |  | PCM-20251026-00002250 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 21:37:46 | 10/26/2025 22:28:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001171 | PCM-20251026-00002268 | TT-20251026-02226 | Reference_telecom | Region_4 | RAB1MN0720 | RAB0720 |  |  |  | Khizer Hayat | 10/26/2025 21:38:07 | 10/26/2025 22:28:21 | 10/27/2025 03:38:07 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB1MN0720-NR2.6-P2 @ Sceco | 10/26/2025 21:12:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:12:46 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | RAB1MN0720 | FLM_TE |  |  | PCM-20251026-00002245 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 21:38:07 | 10/26/2025 22:28:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001172 | PCM-20251026-00002269 | TT-20251026-02230 | Reference_telecom | Region_4 | RAB2990 | RAB2990 |  |  |  | Khizer Hayat | 10/26/2025 21:38:28 | 10/26/2025 22:28:21 | 10/27/2025 09:38:28 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB2990-G9-L8-L18-L21-NR2.6-P3-SBTS @ Sceco | 10/26/2025 21:16:14 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:16:03 | P3 | 2G | Rabigh | Sceco | 5G_Cell SA | RAB2990 | FLM_TE |  |  | PCM-20251026-00002249 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 21:38:28 | 10/26/2025 22:28:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001173 | PCM-20251026-00002270 | TT-20251026-02254 | EM | Region_6 | ARF1M7694 | ARF0694 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/26/2025 21:39:01 | 10/26/2025 21:49:01 | 10/27/2025 09:39:01 | RECTIFIER MAINS POWER FAILURE at ARF1M7694-G9-L9-L18-SBTS-P2 @ Sceco | 10/26/2025 21:30:44 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/26/2025 21:30:37 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | ARF1M7694 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/26/2025 21:39:01 | 10/26/2025 21:49:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001174 | PCM-20251026-00002271 | TT-20251026-02251 | Reference_telecom | Region_4 | RAB0721 | RAB0721 |  |  |  | Khizer Hayat | 10/26/2025 21:41:04 | 10/26/2025 22:28:22 | 10/27/2025 09:41:04 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0721-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/26/2025 21:32:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:31:55 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0721 | FLM_TE |  |  | PCM-20251026-00002264 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/26/2025 21:41:04 | 10/26/2025 22:28:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001175 | PCM-20251026-00002273 | TT-20251026-02256 | Telecom | Region_4 | JED1M8110 | JED2110 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 21:42:06 | 10/26/2025 21:42:06 | 10/27/2025 03:42:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8110-CA-L800-P3 @ Sceco | 10/26/2025 21:40:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:41:10 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8110 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/26/2025 21:42:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001177 | PCM-20251026-00002280 | TT-20251026-01104 | Telecom | Region_4 | JDJZ1M7870 | JDJZ0870 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/26/2025 21:43:32 | 10/26/2025 21:58:54 | 10/27/2025 09:43:32 | CELL SERVICE PROBLEM (Cell disabled due to unknown problem; logs collected) at JDJZ1M7870-G9-NL8-L18-SBTS-P3 @ Sceco | 10/26/2025 12:16:08 | Minor | 7114 | CELL SERVICE PROBLEM | 10/26/2025 12:16:02 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JDJZ1M7870 | FLM_TE |  |  | PCM-20251026-00001110 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:43:32 | 10/26/2025 21:58:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001178 | PCM-20251026-00002281 | TT-20251026-01531 | Reference_telecom | Region_1 | HMBY0410 | HMBY0410 |  |  |  | Imran Ali Yousaf | 10/26/2025 21:44:49 | 10/27/2025 01:57:48 | 10/27/2025 09:44:49 | MW RTN Observing POWER_ALM at HMBY0410_NE_1_SDB | 10/17/2025 03:25:14 | Minor |  | LOF | 10/17/2025 03:25:14 | P3 | SRAN | dammam | Sceco | TX NSA | HMBY0410_NE_1_SDB | FLM_TE |  |  | PCM-20251026-00002247 | Approved and details as shared mail | Approved and details as shared mail |  |  |  | API | 10/26/2025 21:44:49 | 10/27/2025 01:57:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001179 | PCM-20251026-00002282 | TT-20251026-01994 | Reference_telecom | Region_6 | RUS1M7101 | RUS0101 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Muhammad shafiq Muhammad Rasheed | 10/26/2025 21:45:10 | 10/26/2025 22:45:07 | 10/27/2025 03:45:10 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at RUS1M7101-USF-CA-L900-L800-SBTS @ Sceco | 10/26/2025 18:18:35 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 17:24:59 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | RUS1M7101 | FLM_TE |  |  | PCM-20251026-00001998 | Alarm Cleared. FLM need to check and close with RCA. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:45:10 | 10/26/2025 22:43:49 | 10/26/2025 22:44:51 | 10/26/2025 22:44:54 |  | 10/26/2025 22:45:07 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001180 | PCM-20251026-00002283 | TT-20251026-02264 | Reference_EM | Region_2 | RIY0970 | RIY0970 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Mustansar Ali Mushtaq Ahmad | 10/26/2025 21:45:12 | 10/26/2025 23:08:59 | 10/27/2025 03:45:12 | DC power fail at RIY0970-P1-PNU-VIP_SRAN @ Sceco | 10/26/2025 21:34:47 | Major | 65106 | DC power fail | 10/26/2025 21:34:43 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0970 | FLM_EM | [8 empty] | API | 10/26/2025 21:45:12 | 10/26/2025 21:58:26 | 10/26/2025 21:58:52 | 10/26/2025 21:59:13 | 10/26/2025 23:06:21 | 10/26/2025 23:08:59 |  | Mustansar Ali Mushtaq Ahmad |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001181 | PCM-20251026-00002284 | TT-20251026-02028 | Reference_telecom | Region_6 | ALA1M8196 | ALA2196 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/26/2025 21:45:51 | 10/27/2025 03:36:44 | 10/27/2025 09:45:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ALA1M8196-G9-L8-SBTS-P3 @ Generator_SG | 10/26/2025 16:55:07 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 16:31:16 | P3 | 4G | bisha | Generator_SG | LTE NSA | ALA1M8196 | FLM_TE |  |  | PCM-20251026-00002036 | Alarm Cleared. FLM need to check and close with RCA. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:45:51 | 10/26/2025 22:23:26 | 10/27/2025 03:36:32 |  |  | 10/27/2025 03:36:44 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001182 | PCM-20251026-00002285 | TT-20251026-02269 | Telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 21:46:14 | 10/27/2025 02:52:05 | 10/27/2025 03:46:14 | BBU CPRI Interface Error at HFF6036-DCU2 @ Sceco | 10/26/2025 21:40:43 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 21:39:07 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/26/2025 21:46:14 | 10/27/2025 02:52:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001183 | PCM-20251026-00002286 | TT-20251026-02069 | Telecom | Region_1 | TRT2996 | TRT2996 | Equipment | CB_BTS | Replace CB on Rectifier | AbdalHafiz Sirageldin Mohamed Yasin | 10/26/2025 21:47:44 | 10/26/2025 23:33:56 | 10/27/2025 03:47:44 | 2(2G) 1(3G) 2(LTE) sites down under TRT2996-P2,TRT0764-P3/R1_DM_HWBSC01 @ Sceco | 10/26/2025 19:01:19 | Major | 21825 | CSL Fault | 10/26/2025 19:01:16 | P2 | SRAN | dammam | Sceco | 2G_3G_LTE SA | TRT0764-P3 2G_LTE,TRT2996-P2 2G_3G_LTE | FLM_TE | TRT2996 | Dear Team, Hub: TRT2996 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251026-00002277 | telecom issue | telecom issue |  | sites down |  | API | 10/26/2025 21:47:44 | 10/26/2025 21:48:55 | 10/26/2025 22:02:28 | 10/26/2025 22:02:31 | 10/26/2025 22:34:28 | 10/26/2025 23:33:56 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001184 | PCM-20251026-00002287 | TT-20251026-02017 | Reference_telecom | Region_6 | TND1M7408 | TND0408 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/26/2025 21:48:00 | 10/27/2025 02:19:39 | 10/27/2025 09:48:00 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at TND1M7408-G9-L18-L21-L9-SBTS-P2-USF @ Sceco | 10/26/2025 18:24:41 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 18:21:27 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | TND1M7408 | FLM_TE |  |  | PCM-20251026-00002023 | Alarm Cleared. FLM need to check and close with RCA. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:48:00 | 10/26/2025 23:13:35 | 10/27/2025 02:19:30 |  |  | 10/27/2025 02:19:39 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001185 | PCM-20251026-00002290 | TT-20251026-02173 | Reference_telecom | Region_6 | ARF0068 | ARF0068 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad shafiq Muhammad Rasheed | 10/26/2025 21:49:27 | 10/26/2025 22:44:30 | 10/27/2025 09:49:27 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ARF0068-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 18:38:03 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 18:37:57 | P2 | 2G | al harja | Sceco | 2G NSA | ARF0068 | FLM_TE |  |  | PCM-20251026-00002193 | Alarm cleared. FLM need to check and close with RCA. | Alarm cleared. FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:49:27 | 10/26/2025 22:43:50 | 10/26/2025 22:44:11 | 10/26/2025 22:44:14 |  | 10/26/2025 22:44:30 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001186 | PCM-20251026-00002294 | TT-20251026-02029 | Reference_telecom | Region_6 | ULY1M8209 | ULY2209 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/26/2025 21:53:42 | 10/27/2025 03:37:10 | 10/27/2025 09:53:42 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ULY1M8209-G9-L8-SBTS-P3 @ Sceco | 10/26/2025 16:56:13 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 16:31:16 | P3 | 4G | bisha | Sceco | LTE NSA | ULY1M8209 | FLM_TE |  |  | PCM-20251026-00002037 | Alarm Cleared. FLM need to check and close with RCA. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/26/2025 21:53:42 | 10/26/2025 22:23:27 | 10/27/2025 03:36:55 |  |  | 10/27/2025 03:37:10 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001188 | PCM-20251026-00002298 | TT-20251026-02233 | EM | Region_4 | MLJI0204 | MLJI0204 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/26/2025 21:59:04 | 10/27/2025 03:57:17 | 10/27/2025 03:59:04 | 1(2G/3G) sites down under MLJI0204-P3/MLJI0204-P3 @ Generator_SG | 10/26/2025 21:19:57 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 21:19:55 | P3 | 2G | alaith | Generator_SG | 2G_3G SA | MLJI0204-P3 | FLM_TE | MLJI0204 | Results: DOWN SITE HUB MLJI0204-P3 MLJI0204 Summary: Hub: MLJI0204, Down Count: 1, Down Sites: MLJI0204-P3 Alarm Summary: MLJI0204 No Active Alarm on HUB | PCM-20251026-00002260 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 21:59:04 | 10/27/2025 03:35:11 | 10/27/2025 03:57:07 |  |  | 10/27/2025 03:57:17 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001189 | PCM-20251026-00002299 | TT-20251026-02232 | Reference_telecom | Region_4 | RAB1MN0966 | RAB0966 |  |  |  | Khizer Hayat | 10/26/2025 22:00:24 | 10/26/2025 22:28:22 | 10/27/2025 04:00:24 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB1MN0966-NR2.6-P3 @ Sceco | 10/26/2025 21:17:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 21:17:18 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | RAB1MN0966 | FLM_TE |  |  | PCM-20251026-00002252 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/26/2025 22:00:24 | 10/26/2025 22:28:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001190 | PCM-20251026-00002301 | TT-20251026-02279 | Telecom | Region_3 | AHT2M8149 | AHT2149 |  |  |  | Mohamed Naveed | 10/26/2025 22:05:30 | 10/26/2025 22:52:01 | 10/27/2025 04:05:30 | 1(LTE) sites down under AHT2149-L800-P3 @ Sceco | 10/26/2025 21:58:53 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/26/2025 21:57:21 | P3 | 4G | hail | Sceco | LTE SA | AHT2149-L800-P3 | FLM_TE | AHT2149 | Results: DOWN SITE HUB AHT2149-L800-P3 AHT2149 Summary: Hub: AHT2149, Down Count: 1, Down Sites: AHT2149-L800-P3 Alarm Summary: AHT2149 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 22:05:30 | 10/26/2025 22:52:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001191 | PCM-20251026-00002303 | TT-20251026-02137 | Telecom | Region_4 | JED0241 | JED0241 | Transsmission | MW_HW_stuck | Reset IDU | Khaled Mohammad Abdallah | 10/26/2025 22:06:16 | 10/26/2025 23:12:19 | 10/27/2025 04:06:16 | 2(2G) 2(LTE) 2(5G) sites down under JED0241-P2,JED2065-P3/JED2065-P3 @ Sceco | 10/26/2025 20:03:09 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 20:03:06 | P2 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED0241-P2 2G_LTE_5G,JED2065-P3 2G_LTE_5G | FLM_TE | JED0241 | Scattered sites: JED0241, JED2065 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251026-00002190 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 22:06:16 | 10/26/2025 22:32:18 | 10/26/2025 22:33:06 | 10/26/2025 22:33:10 | 10/26/2025 22:33:12 | 10/26/2025 23:12:19 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001192 | PCM-20251026-00002305 | TT-20251026-02283 | Reference_EM | Region_1 | JBL2M3479 | JBL0479 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 22:10:00 | 10/26/2025 23:51:24 | 10/27/2025 10:10:00 | Door opening alarm at JBL2M3479-P3 @ Sceco | 10/26/2025 22:09:48 | Minor | 65101 | Door opening alarm | 10/26/2025 22:09:43 | P3 | 3G | jubail | Sceco | 3G NSA | JBL2M3479 | FLM_EM | [8 empty] | API | 10/26/2025 22:10:00 | 10/26/2025 23:51:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001195 | PCM-20251026-00002313 | TT-20251026-02191 | Telecom | Region_6 | AQQ1M7039 | AQQ0039 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 22:18:30 | 10/27/2025 08:50:49 | 10/27/2025 10:18:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at AQQ1M7039-G9-NL8-L18-NL21-SBTS-P3 @ Sceco | 10/26/2025 20:53:23 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:53:13 | P3 | 4G | Albaha | Sceco | 5G_Cell SA | AQQ1M7039 | FLM_TE |  |  | PCM-20251026-00002302 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/26/2025 22:18:30 | 10/27/2025 08:49:45 | 10/27/2025 08:50:39 |  |  | 10/27/2025 08:50:49 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001198 | PCM-20251026-00002316 | TT-20251026-01719 | Telecom | Region_6 | ABBS1M8247 | ABBS2247 |  |  |  | Fawad Khan | 10/26/2025 22:19:09 | 10/27/2025 00:29:45 | 10/27/2025 10:19:09 | BASE STATION SOFTWARE MANAGEMENT PROBLEM at ABBS1M8247-L800-P3-SBTS-WBB-G3 @ Sceco | 10/26/2025 16:00:54 | Minor | 7111 | BASE STATION SOFTWARE MANAGEMENT PROBLEM | 10/26/2025 16:00:36 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M8247 | FLM_TE |  |  | PCM-20251026-00001730 | FLM need to give factory reset to SM and need to recommission site with latest SW locally | FLM need to give factory reset to SM and need to recommission site with latest SW locally |  |  |  | API | 10/26/2025 22:19:09 | 10/27/2025 00:29:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001199 | PCM-20251026-00002317 | TT-20251026-02290 | Telecom | Region_1 | HFF6030 | HFF6030 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/26/2025 22:19:19 | 10/27/2025 02:52:06 | 10/27/2025 10:19:19 | ODU CPU / Cable Open at HFF6030-1 on 10.158.221.107 @ Sceco | 10/26/2025 22:18:34 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/26/2025 22:04:54 | P3 | SRAN | hafouf | Sceco | TX NSA | HFF6030 | FLM_TE | [8 empty] | API | 10/26/2025 22:19:19 | 10/27/2025 02:52:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251026001200 | PCM-20251026-00002318 | TT-20251026-02291 | Reference_EM | Region_1 | JBL2M1479 | JBL0479 |  |  |  | Hamid Bilal Bashir Ahmed | 10/26/2025 22:21:24 | 10/27/2025 00:12:22 | 10/27/2025 10:21:24 | Mains Failure at JBL2M1479-P3 @ Sceco | 10/26/2025 22:11:22 | Minor | 65109 | Mains Failure | 10/26/2025 22:11:17 | P3 | 2G | jubail | Sceco | 2G NSA | JBL2M1479 | FLM_EM | [8 empty] | API | 10/26/2025 22:21:24 | 10/26/2025 23:51:25 | 10/27/2025 00:10:40 | 10/27/2025 00:10:43 | 10/27/2025 00:12:22 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001201 | PCM-20251026-00002323 | TT-20251026-02295 | Reference_telecom | Region_2 | RIYB2U6722 | RIYB6022 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 22:30:06 | 10/27/2025 08:08:22 | 10/27/2025 10:30:06 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6722-P3-CA @ Sceco | 10/26/2025 19:26:50 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 19:26:45 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6722 | FLM_TE |  |  | PCM-20251026-00002322 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/26/2025 22:30:06 | 10/27/2025 08:08:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001202 | PCM-20251026-00002326 | TT-20251026-02300 | Telecom | Region_6 | AQQ1M7039 | AQQ0039 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/26/2025 22:46:29 | 10/27/2025 08:51:14 | 10/27/2025 04:46:29 | 1(LTE) sites down under AQQ0039-G9-NL8-L18-NL21-SBTS-P3 @ Sceco | 10/26/2025 22:38:29 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/26/2025 22:38:25 | P3 | 4G | Albaha | Sceco | LTE SA | AQQ0039-G9-NL8-L18-NL21-SBTS-P3 | FLM_TE | AQQ0039 | Results: DOWN SITE HUB AQQ0039-G9-NL8-L18-NL21-SBTS-P3 AQQ0039 Summary: Hub: AQQ0039, Down Count: 1, Down Sites: AQQ0039-G9-NL8-L18-NL21-SBTS-P3 Alarm Summary: AQQ0039 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.103.247.76:8080] [URL:http://10.103.247.76:8080/NE3S/1.0/] | sites down |  | API | 10/26/2025 22:46:29 | 10/27/2025 08:49:45 | 10/27/2025 08:51:05 |  |  | 10/27/2025 08:51:14 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001204 | PCM-20251026-00002332 | TT-20251026-02311 | Telecom | Region_6 | ARF0315 | ARF0315 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/26/2025 22:48:14 | 10/26/2025 22:48:14 | 10/27/2025 10:48:14 | BASE STATION INFORMATION (No module fan detected) at ARF0315-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 22:40:08 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 22:39:58 | P3 | 2G | khamis mushyet | Sceco | 2G NSA | ARF0315 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/26/2025 22:48:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001207 | PCM-20251026-00002337 | TT-20251026-02308 | EM | Region_6 | TLT0390 | TLT0390 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/26/2025 22:52:01 | 10/27/2025 05:29:12 | 10/27/2025 04:52:01 | 1(2G/LTE/5G) sites down under TLT0390-P2-USF/TLT0390-P2-USF @ Sceco | 10/26/2025 22:43:59 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 22:43:52 | P2 | 2G | tathleeth | Sceco | 2G SA | TLT0390-P2-USF | FLM_TE | TLT0390 | Results: DOWN SITE HUB TLT0390-P2-USF TLT0390 Summary: Hub: TLT0390, Down Count: 1, Down Sites: TLT0390-P2-USF Alarm Summary: TLT0390 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/26/2025 22:52:01 | 10/26/2025 23:47:42 | 10/26/2025 23:48:15 |  |  | 10/26/2025 23:48:22 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001208 | PCM-20251026-00002339 | TT-20251026-02316 | Telecom | Region_1 | TRT2996 | TRT2996 | Equipment | CB_BTS | Replace CB on Rectifier | Meraj Husain Idd Baksh | 10/26/2025 22:57:33 | 10/27/2025 00:37:37 | 10/27/2025 04:57:33 | BBU CPRI Interface Error at TRT2996-P2_SRAN @ Sceco | 10/26/2025 22:53:09 | Major | 26234 | BBU CPRI Interface Error | 10/26/2025 22:50:37 | P2 | SRAN | dammam | Sceco | 2G NSA | TRT2996 | FLM_TE | [8 empty] | API | 10/26/2025 22:57:33 | 10/26/2025 23:40:24 | 10/27/2025 00:37:07 |  |  | 10/27/2025 00:37:37 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001209 | PCM-20251026-00002340 | TT-20251026-02317 | Telecom | Region_4 | MKJD1M9570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/26/2025 22:58:04 | 10/26/2025 22:58:04 | 10/27/2025 10:58:04 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MKJD1M9570-P3-L800-SBTS @ Generator_DG | 10/26/2025 22:50:02 | Minor | 7115 | BASE STATION INFORMATION | 10/26/2025 22:49:52 | P2 | 4G | jeddah | Generator_DG | LTE NSA | MKJD1M9570 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/26/2025 22:58:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001210 | PCM-20251026-00002341 | TT-20251026-02318 | EM | Region_4 | JED2050 | JED2050 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/26/2025 22:59:06 | 10/26/2025 22:59:06 | 10/27/2025 10:59:06 | SHELTER DOOR OPEN at JED2050-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/26/2025 22:58:32 | Minor | 7103 | SHELTER DOOR OPEN | 10/26/2025 22:58:26 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2050 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/26/2025 22:59:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001211 | PCM-20251026-00002342 | TT-20251026-02304 | EM | Region_1 | JBKH0146 | JBKH0146 |  |  |  | Mohamed Abdelaziz | 10/26/2025 22:59:36 | 10/27/2025 00:13:30 | 10/27/2025 04:59:36 | 1(2G/3G/LTE) sites down under JBKH0146-P2-USF/DM1MBSCH01 @ Generator_SG | 10/26/2025 22:44:00 | Major | 21825 | CSL Fault | 10/26/2025 22:43:58 | P2 | SRAN | khafji | Generator_SG | 2G_3G_LTE SA | JBKH0146-P2-USF | FLM_TE | JBKH0146 | Results: DOWN SITE HUB JBKH0146-P2-USF JBKH0146 Summary: Hub: JBKH0146, Down Count: 1, Down Sites: JBKH0146-P2-USF Alarm Summary: JBKH0146 Alarm Active on HUB | PCM-20251026-00002333 | Telecom issue at site | Telecom issue at site |  | sites down |  | API | 10/26/2025 22:59:36 | 10/27/2025 00:13:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001215 | PCM-20251026-00002349 | TT-20251026-02321 | Telecom | Region_4 | JED1U6739 | JED6039 |  |  |  | Mohamed Farag Abdelbary | 10/26/2025 23:15:33 | 10/26/2025 23:15:33 | 10/27/2025 05:15:33 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/26/2025 22:55:18 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/26/2025 22:55:07 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251026-00002343 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/26/2025 23:15:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001216 | PCM-20251026-00002354 | TT-20250929-02741 | MW_HC | Region_4 | JED1M8045 | JED2045 |  |  |  | BARKAT ALI MAIN HILAL | 10/26/2025 23:24:34 | 10/26/2025 23:24:34 | 10/27/2025 11:24:34 | FLM need to check with access BO locally as TX path clear | 09/29/2025 18:46:52 | Minor | 113388 | LOF | 09/29/2025 18:46:50 | P3 | 4G | jeddah | Sceco | TX NSA | JED1M8045 | FLM_TE |  |  | PCM-20251025-00000765 | Please check for approval over mail with concern team | Please check for approval over mail with concern team |  |  |  | API | 10/26/2025 23:24:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001218 | PCM-20251026-00002360 | TT-20251026-02347 | EM | Region_3 | RUSF9023 | RUSF9023 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/26/2025 23:28:32 | 10/26/2025 23:28:32 | 10/27/2025 11:28:32 | NETECO: Communication Failure at RUSF9023 @ Generator_DG | 10/26/2025 23:22:15 | Minor | 17451 | Communication Failure | 10/26/2025 23:22:15 | P3 | Repeater | hail | Generator_DG | 2G NSA | RUSF9023 | FLM_EM | [8 empty] | API | 10/26/2025 23:28:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001219 | PCM-20251026-00002359 | TT-20251026-02345 | Telecom | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/26/2025 23:28:33 | 10/27/2025 00:23:53 | 10/27/2025 11:28:33 | ODU CPU / Cable Open at JDJZ0785 on 10.154.164.49 @ Sceco_STB | 10/26/2025 23:27:28 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/26/2025 23:12:04 | P1 | 2G | derb | Sceco_STB | TX NSA | JDJZ0785 | FLM_TE | [8 empty] | API | 10/26/2025 23:28:33 | 10/27/2025 00:23:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001220 | PCM-20251026-00002361 | TT-20251026-02350 | Reference_EM | Region_1 | NRKF2M5778 | NRKF0778 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/26/2025 23:29:34 | 10/27/2025 00:41:03 | 10/27/2025 11:29:34 | Minor Rec. alarm at NRKF2M5778-P2 @ Generator_SG | 10/26/2025 23:19:05 | Minor | 65108 | Minor Rec. alarm | 10/26/2025 23:19:01 | P2 | 2G | jubail | Generator_SG | 2G NSA | NRKF2M5778 | FLM_EM | [8 empty] | API | 10/26/2025 23:29:34 | 10/27/2025 00:41:03 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001221 | PCM-20251026-00002365 | TT-20251026-02346 | EM | Region_3 | AHT2091 | AHT2091 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/26/2025 23:33:32 | 10/27/2025 07:11:13 | 10/27/2025 11:33:32 | NETECO: Under Fuel Level at AHT2091 @ Generator_SG | 10/26/2025 23:22:10 | Minor | 301 | Under Fuel Level | 10/26/2025 23:22:10 | P3 | SRAN | hail | Generator_SG | 2G NSA | AHT2091 | FLM_EM | AHT2091 | Results: DOWN SITE HUB AHT2091 AHT2091 Summary: Hub: AHT2091, Down Count: 1, Down Sites: AHT2091 Alarm Summary: AHT2091 No Active Alarm on HUB | [6 empty] | API | 10/26/2025 23:33:32 | 10/27/2025 07:11:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001222 | PCM-20251026-00002371 | TT-20251026-02356 | Telecom | Region_3 | HAL2M3127 | HAL0127 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Atif Shahzad Muhammad Ajaib | 10/26/2025 23:34:57 | 10/27/2025 01:57:50 | 10/27/2025 05:34:57 | Local Cell Unusable at HAL2M3127-P2 @ Sceco | 10/26/2025 23:30:28 | Major | 28203 | Local Cell Unusable | 10/26/2025 23:29:37 | P2 | 3G | hail | Sceco | 3G SA | HAL2M3127 | FLM_TE | [8 empty] | API | 10/26/2025 23:34:57 | 10/27/2025 01:14:23 | 10/27/2025 01:22:24 | 10/27/2025 01:22:28 | 10/27/2025 01:22:33 | 10/27/2025 01:57:50 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001224 | PCM-20251026-00002372 | TT-20251026-02348 | Reference_EM | Region_4 | JED0993 | JED0993 | Transsmission | MW_HW_stuck | Reset IDU | Khaled Mohammad Abdallah | 10/26/2025 23:35:23 | 10/27/2025 01:37:50 | 10/27/2025 05:35:23 | 1(2G/LTE/5G) Sites down under JED0993-P3 (Ref:TT-20251026-02253) | 10/26/2025 21:34:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 21:34:50 | P3 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED0993-P3 | FLM_TE | JED0993 | Results: DOWN SITE HUB JED0993-P3 JED0993 Summary: Hub: JED0993, Down Count: 1, Down Sites: JED0993-P3 Alarm Summary: JED0993 No Active Alarm on HUB | PCM-20251026-00002366 | No Power Issue | No Power Issue |  | sites down |  | API | 10/26/2025 23:35:23 | 10/26/2025 23:37:58 | 10/27/2025 01:37:17 |  |  | 10/27/2025 01:37:50 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001225 | PCM-20251026-00002374 | TT-20251026-02357 | Telecom | Region_1 | DAM0033 | DAM0033 | Equipment | SFP_BTS | Clean SFP | Meraj Husain Idd Baksh | 10/26/2025 23:36:18 | 10/27/2025 07:36:10 | 10/27/2025 11:36:18 | RF Unit CPRI Interface Error at DAM0033-P2_SRAN @ Sceco | 10/26/2025 23:31:46 | Minor | 26504 | RF Unit CPRI Interface Error | 10/26/2025 23:29:12 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0033 | FLM_TE | [8 empty] | API | 10/26/2025 23:36:18 | 10/26/2025 23:40:24 | 10/27/2025 07:26:39 |  |  | 10/27/2025 07:36:10 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001226 | PCM-20251026-00002375 | TT-20251026-02359 | Telecom | Region_3 | HAL2M3127 | HAL0127 |  |  |  | Atif Shahzad Muhammad Ajaib | 10/26/2025 23:36:18 | 10/27/2025 01:14:23 | 10/27/2025 11:36:18 | RF Unit Maintenance Link Failure at HAL2M3127-P2 @ Sceco | 10/26/2025 23:31:06 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 23:31:03 | P2 | 3G | hail | Sceco | 3G NSA | HAL2M3127 | FLM_TE | [8 empty] | API | 10/26/2025 23:36:18 | 10/27/2025 01:14:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001228 | PCM-20251026-00002377 | TT-20251026-02337 | Reference_telecom | Region_4 | LTH2121 | LTH2121 |  |  |  | Riasat Ali Allah Baksh | 10/26/2025 23:37:50 | 10/26/2025 23:37:50 | 10/27/2025 05:37:50 | BCF NOTIFICATION (FF FF FF FF FF FF) at LTH2121-P3 @ Sceco | 10/26/2025 23:15:18 | Major | 7602 | BCF NOTIFICATION | 10/26/2025 23:15:06 | P3 | 2G | jeddah | Sceco | 2G NSA | LTH2121 | FLM_TE |  |  | PCM-20251026-00002352 | observing GPS&PTP issue, please check and do HC locally | observing GPS&PTP issue, please check and do HC locally |  |  |  | API | 10/26/2025 23:37:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001229 | PCM-20251026-00002378 | TT-20251026-02361 | EM | Region_4 | TURY0685 | TURY0685 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/26/2025 23:38:21 | 10/27/2025 08:13:13 | 10/27/2025 05:38:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at TURY0685-GSM-P1-HUB @ Sceco | 10/26/2025 23:30:05 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/26/2025 23:29:54 | P1 | 2G | taif | Sceco | 2G NSA | TURY0685 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/26/2025 23:38:21 | 10/27/2025 08:13:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251026001230 | PCM-20251026-00002382 | TT-20251026-02349 | Telecom | Region_4 | JDRS0756 | JDRS0756 |  |  |  | Khizer Hayat | 10/26/2025 23:43:10 | 10/27/2025 01:31:19 | 10/27/2025 03:43:10 | 9(2G) 6(3G) 3(LTE) 3(5G) sites down under HHR0505-P1-VIP-HHR @ Generator_SG | 10/26/2025 23:26:51 | Critical | 7706 | BTS O&M LINK FAILURE | 10/26/2025 23:26:47 | P1 | 2G | jeddah | Generator_SG | 2G_3G_5G SA | HHR0614-P1-VIP-HHR 2G_3G_5G,KAC0451-P2 2G_3G,JDRS0756-P1-HUB-USF 2G_3G,HHR0505-P1-VIP-HHR 2G_3G,HHR0507-P1-VIP-HHR 2G_3G,NOB0035-P2-USF 2G_3G,HHR0494-P1-VIP-HHR 2G,HJR0111-P3 2G,KAC0453-P3 2G | FLM_TE | JDRS0756 | Site HUB TRM FB HHR0614-P1-VIP-HHR JDRS0756 observing Low BER KAC0451-P2 JDRS0756 observing Low BER JDRS0756-P1-HUB-USF JDRS0756 observing Low BER HHR0505-P1-VIP-HHR HHR0507 observing visibility down HHR0507-P1-VIP-HHR HHR0507 observing visibility down NOB0035-P2-USF NOB0035 Suspecting power issue HHR0494-P1-VIP-HHR HHR0507 observing visibility down HJR0111-P3 HJR0111 Suspecting power issue KAC0453-P3 KAC0453 observing visibility down | PCM-20251026-00002368 | Site HUB TRM FB HHR0614-P1-VIP-HHR JDRS0756 observing Low BER KAC0451-P2 JDRS0756 observing Low BER JDRS0756-P1-HUB-USF JDRS0756 observing Low BER HHR0505-P1-VIP-HHR HHR0507 observing visibility down HHR0507-P1-VIP-HHR HHR0507 observing visibility down NOB0035-P2-USF NOB0035 Suspecting power issue HHR0494-P1-VIP-HHR HHR0507 observing visibility down HJR0111-P3 HJR0111 Suspecting power issue KAC0453-P3 KAC0453 observing visibility down | Site HUB TRM FB HHR0614-P1-VIP-HHR JDRS0756 observing Low BER KAC0451-P2 JDRS0756 observing Low BER JDRS0756-P1-HUB-USF JDRS0756 observing Low BER HHR0505-P1-VIP-HHR HHR0507 observing visibility down HHR0507-P1-VIP-HHR HHR0507 observing visibility down NOB0035-P2-USF NOB0035 Suspecting power issue HHR0494-P1-VIP-HHR HHR0507 observing visibility down HJR0111-P3 HJR0111 Suspecting power issue KAC0453-P3 KAC0453 observing visibility down |  | sites down |  | API | 10/26/2025 23:43:10 | 10/27/2025 01:31:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001231 | PCM-20251026-00002384 | TT-20251026-02370 | Telecom | Region_4 | HJR9400 | HJR9400 |  |  |  | Khizer Hayat | 10/26/2025 23:45:04 | 10/27/2025 01:31:19 | 10/27/2025 11:45:04 | Power Supply at HJR9400 on 10.88.224.108 @ Generator_DG | 10/26/2025 23:42:51 | Minor | Power Supply | Power Supply | 10/26/2025 23:43:34 | P1 | Repeater | jeddah | Generator_DG | TX NSA | HJR9400 | FLM_TE | [8 empty] | API | 10/26/2025 23:45:04 | 10/27/2025 01:31:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001232 | PCM-20251026-00002385 | TT-20251026-02355 | Telecom | Region_4 | JDRS0756 | JDRS0756 |  |  |  | Khizer Hayat | 10/26/2025 23:45:48 | 10/27/2025 01:31:20 | 10/27/2025 05:45:48 | 2(2G) 2(3G) sites down under KAC0461-P2,KAC0456-P3,JED6055-P3/JED6055-P3 @ Sceco | 10/26/2025 23:33:07 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 23:31:26 | P1 | 2G | jeddah | Generator_SG | 2G_3G SA | KAC0461-P2 2G_3G,KAC0456-P3 3G,JED6055-P3 2G | FLM_TE | JDRS0756 | Hub: JDRS0756 We are observing Low BER alarm flapped kindly send team to check locally | PCM-20251026-00002379 | Hub: JDRS0756 We are observing Low BER alarm flapped kindly send team to check locally | Hub: JDRS0756 We are observing Low BER alarm flapped kindly send team to check locally |  | sites down |  | API | 10/26/2025 23:45:48 | 10/27/2025 01:31:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001233 | PCM-20251026-00002388 | TT-20251026-02353 | Reference_telecom | Region_2 | BJD2M7539 | BJD0539 |  |  |  | Zakir Muhammad Yar Muhammad | 10/26/2025 23:47:18 | 10/26/2025 23:47:18 | 10/27/2025 11:47:18 | Cell RX Channel Interference Noise Power Unbalanced at BJD2M7539-P2-L800-L2100 @ Sceco_STB | 10/26/2025 20:32:56 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 20:32:53 | P2 | 4G | dawadmi | Sceco_STB | 2G NSA | BJD2M7539 | FLM_TE |  |  | PCM-20251026-00002364 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/26/2025 23:47:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251026001234 | PCM-20251026-00002391 | TT-20251024-00503 | Reference_telecom | Region_5 | BIK0788 | BIK0788 | Equipment | SFP_BTS | Clean SFP | Muhammad Saleem Iqbal | 10/26/2025 23:49:04 | 10/27/2025 07:13:20 | 10/27/2025 05:49:04 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at BIK0788-P3 @ Generator_SG | 10/24/2025 08:36:52 | Major | 7607 | TRX OPERATION DEGRADED | 10/24/2025 08:36:49 | P3 | 2G | makkah | Generator_SG | 2G_TRX NSA | BIK0788 | FLM_TE |  |  | PCM-20251024-00000430 | Please check RSSI locally | Please check RSSI locally |  |  |  | API | 10/26/2025 23:49:04 | 10/27/2025 03:45:36 | 10/27/2025 04:21:36 | 10/27/2025 04:22:18 | 10/27/2025 05:22:07 | 10/27/2025 07:13:20 |  | Muhammad Saleem Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251026001235 | PCM-20251026-00002395 | TT-20251026-01695 | Reference_telecom | Region_4 | JED0514 | JED0514 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/26/2025 23:52:42 | 10/26/2025 23:52:42 | 10/27/2025 11:52:42 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED0514-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/26/2025 15:14:38 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 15:15:53 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0514 | FLM_TE |  |  | PCM-20251026-00001697 | we have multiple cells down due to HW issue, kindly check and do HC 1-please check power 2-check SM 3-check GPS 4-check cables and connectors | we have multiple cells down due to HW issue, kindly check and do HC 1-please check power 2-check SM 3-check GPS 4-check cables and connectors |  |  |  | API | 10/26/2025 23:52:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001236 | PCM-20251026-00002396 | TT-20251026-02377 | Reference_telecom | Region_2 | HIL2471 | HIL2471 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/26/2025 23:53:50 | 10/27/2025 00:03:53 | 10/27/2025 11:53:50 | RF Unit RX Channel RTWP/RSSI Unbalanced at HIL2471-P2_SRAN @ Sceco | 10/26/2025 20:53:40 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/26/2025 20:53:37 | P2 | SRAN | al rass | Sceco | 2G NSA | HIL2471 | FLM_TE | [8 empty] | API | 10/26/2025 23:53:50 | 10/27/2025 00:03:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251026001238 | PCM-20251026-00002398 | TT-20251026-02382 | Telecom | Region_2 | RIYD6037 | RIYD6037 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/26/2025 23:59:30 | 10/27/2025 08:08:22 | 10/27/2025 11:59:30 | RF Unit Maintenance Link Failure at RIYD6037-DCU2 @ Sceco | 10/26/2025 23:47:14 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/26/2025 23:54:08 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_TE | [8 empty] | API | 10/26/2025 23:59:30 | 10/27/2025 08:08:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000002 | PCM-20251027-00000005 | TT-20251027-00004 | Telecom | Region_4 | JED1M8609 | JED2609 |  |  |  | BARKAT ALI MAIN HILAL | 10/27/2025 00:10:20 | 10/27/2025 00:10:20 | 10/27/2025 06:10:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8609-P3-L800-CA @ Sceco | 10/27/2025 00:09:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 00:09:25 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8609 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 00:10:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000004 | PCM-20251027-00000009 | TT-20251026-02307 | Telecom | Region_1 | JBKH0146 | JBKH0146 |  |  |  | Mohamed Abdelaziz | 10/27/2025 00:11:04 | 10/27/2025 00:13:30 | 10/27/2025 06:11:04 | 1(2G) sites down under NRKF0778-P2/R1_JB_HWBSC01 @ Generator_SG | 10/26/2025 22:43:51 | Major | 21807 | OML Fault | 10/26/2025 22:43:44 | P2 | SRAN | khafji | Generator_SG | 2G SA | NRKF0778-P2 | FLM_TE | JBKH0146 | Dear Team, Hub: JBKH0146 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site | PCM-20251026-00002397 | telecom issue | telecom issue |  | sites down |  | API | 10/27/2025 00:11:04 | 10/27/2025 00:13:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000005 | PCM-20251027-00000010 | TT-20251027-00009 | Telecom | Region_4 | JED1MN2417 | JED2417 |  |  |  | Mohammed Ramadan A Abu Abid | 10/27/2025 00:11:22 | 10/27/2025 06:02:02 | 10/27/2025 06:11:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2417-NR2.6-P3 @ Sceco | 10/27/2025 00:10:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 00:10:10 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2417 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 00:11:22 | 10/27/2025 06:02:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000007 | PCM-20251027-00000014 | TT-20251027-00014 | Telecom | Region_4 | JED1M7224 | JED0224 |  |  |  | Nazeer Mohammed | 10/27/2025 00:20:29 | 10/27/2025 00:20:29 | 10/27/2025 06:20:29 | 1(LTE) sites down under JED0224-P3-CA-L900 @ Sceco | 10/27/2025 00:12:13 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 00:12:09 | P2 | 4G | jeddah | Sceco | LTE SA | JED0224-P3-CA-L900 | FLM_TE | JED0224 | Results: DOWN SITE HUB JED0224-P3-CA-L900 JED0224 Summary: Hub: JED0224, Down Count: 1, Down Sites: JED0224-P3-CA-L900 Alarm Summary: JED0224 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.136.52:8080] [URL:http://10.96.136.52:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 00:20:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000009 | PCM-20251027-00000031 | TT-20251027-00033 | Telecom | Region_1 | RDF0015 | RDF0015 | Equipment | SFP_BTS | Replace SFP | Syed Fawad Ali | 10/27/2025 00:27:54 | 10/27/2025 01:54:28 | 10/27/2025 06:27:54 | BBU CPRI Interface Error at RDF0015-P3_SRAN @ Sceco_STB | 10/27/2025 00:23:36 | Major | 26234 | BBU CPRI Interface Error | 10/27/2025 00:20:54 | P3 | SRAN | sakaka | Sceco_STB | 2G NSA | RDF0015 | FLM_TE | [8 empty] | API | 10/27/2025 00:27:54 | 10/27/2025 01:53:54 | 10/27/2025 01:54:10 |  |  | 10/27/2025 01:54:28 |  | Syed Fawad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000010 | PCM-20251027-00000032 | TT-20251027-00003 | Telecom | Region_3 | HNK2355 | HNK2355 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/27/2025 00:31:27 | 10/27/2025 00:31:27 | 10/27/2025 04:31:27 | 5(2G) 4(LTE) sites down under R3_MD_HWBSC01 @ Generator_SG | 10/27/2025 00:06:46 | Critical | 21825 | CSL Fault | 10/27/2025 00:06:41 | P3 | SRAN | madinah | Sceco | 2G_LTE SA | AHT2159-P3-USF 2G_LTE,HNK2267-P3 2G_LTE,HNK2131-P3 2G_LTE,HNK2355-P3 2G_LTE,HLMD2493-P3 2G | FLM_EM | HNK2355 | Dear Team, Hub: HNK2355 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251027-00000013 | Dear Team, Hub: HNK2355 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: HNK2355 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/27/2025 00:31:27 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000015 | PCM-20251027-00000043 | TT-20251027-00047 | Reference_EM | Region_3 | RSP0039 | RSP0039 |  |  |  | Sayed Satoor | 10/27/2025 00:38:46 | 10/27/2025 03:08:33 | 10/27/2025 06:38:46 | Door opening alarm at RSP0039-P1-ARP-VVIP_SRAN @ Sceco | 10/27/2025 00:38:34 | Major | 65101 | Door opening alarm | 10/27/2025 00:38:30 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0039 | FLM_EM | [8 empty] | API | 10/27/2025 00:38:46 | 10/27/2025 03:08:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000016 | PCM-20251027-00000046 | TT-20251027-00050 | EM | Region_6 | BCH1M8203 | BCH2203 |  |  |  | Fathy Mohamed | 10/27/2025 00:41:51 | 10/27/2025 00:41:51 | 10/27/2025 12:41:51 | RECTIFIER MODULE FAILURE at BCH1M8203-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/27/2025 00:33:54 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/27/2025 00:33:48 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8203 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/27/2025 00:41:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000018 | PCM-20251027-00000049 | TT-20251027-00055 | Reference_telecom | Region_1 | SMN0851 | SMN0851 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/27/2025 00:45:29 | 10/27/2025 02:19:23 | 10/27/2025 12:45:29 | RF Unit RX Channel RTWP/RSSI Unbalanced at SMN0851-P2-USF_SRAN @ Generator_SG | 10/26/2025 21:45:13 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/26/2025 21:45:09 | P2 | SRAN | hafr | Generator_SG | 2G NSA | SMN0851 | FLM_TE | [8 empty] | API | 10/27/2025 00:45:29 | 10/27/2025 02:19:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000019 | PCM-20251027-00000053 | TT-20251026-02198 | Telecom | Region_6 | BLQ0113 | BLQ0113 |  |  |  | Fawad Khan | 10/27/2025 00:51:24 | 10/27/2025 00:51:24 | 10/27/2025 12:51:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at BLQ0113-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/26/2025 20:58:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 20:57:50 | P3 | 2G | namas | Sceco | 5G_Cell SA | BLQ0113 | FLM_TE |  |  | PCM-20251027-00000045 | Site is clear pls close | Site is clear pls close |  |  |  | API | 10/27/2025 00:51:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000020 | PCM-20251027-00000055 | TT-20251027-00060 | EM | Region_5 | MAK6028 | MAK6028 |  |  |  | Atif Javed Javed Hussain | 10/27/2025 00:53:44 | 10/27/2025 00:53:44 | 10/27/2025 12:53:44 | AIRCON 1 FAILURE at MAK6028-GSM-P3 @ Sceco | 10/27/2025 00:45:43 | Minor | 7103 | AIRCON 1 FAILURE | 10/27/2025 00:45:33 | P3 | 2G | makkah | Sceco | 2G NSA | MAK6028 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/27/2025 00:53:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000022 | PCM-20251027-00000058 | TT-20251027-00063 | Telecom | Region_3 | RSP0001-MDC-NE8K-M14-02 | RSP0001 |  |  |  | Hossam Ali Ahmed Ali | 10/27/2025 00:57:53 | 10/27/2025 00:57:53 | 10/27/2025 12:57:53 | Bad Package Error Rising at RSP0001-MDC-NE8K-M14-02 @ Sceco | 10/27/2025 00:57:35 | Minor | 101-2501403 | Bad Package Error Rising | 10/27/2025 00:57:27 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | RSP0001-MDC-NE8K-M14-02 | FLM_TE | [8 empty] | API | 10/27/2025 00:57:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000023 | PCM-20251027-00000060 | TT-20251027-00067 | Telecom | Region_4 | JED0151(JD1) | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/27/2025 01:01:33 | 10/27/2025 01:01:33 | 10/27/2025 07:01:33 | R_LOS & REM_SF ALARMS AT JED0151(JD1) & PEACE CLS | 10/27/2025 00:55:57 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/27/2025 00:55:57 | P1 | DWDM | jeddah | Sceco_STB_Rental | DWDM NSA | JED0151(JD1) & PEACE CLS | FLM_TE | [8 empty] | API | 10/27/2025 01:01:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000026 | PCM-20251027-00000078 | TT-20251027-00087 | EM | Region_4 | JD3_CORE | JD3 |  |  |  | Faheemuddin Syed Islamuddin | 10/27/2025 01:12:20 | 10/27/2025 01:12:20 | 10/27/2025 07:12:20 | DOOR OPEN ALARM EQUIPMENT ROOM at JD3_CORE-P1-VIP @ Sceco_STB | 10/27/2025 01:11:50 | Major | 7103 | DOOR OPEN ALARM EQUIPMENT ROOM | 10/27/2025 01:11:42 | P1 | 4G | jeddah | Sceco_STB | 2G NSA | JD3_CORE | FLM_EM | [5 empty] | DOOR OPEN ALARM EQUIPMENT ROOM |  |  | API | 10/27/2025 01:12:20 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000029 | PCM-20251027-00000088 | TT-20251027-00066 | EM | Region_6 | DAR0916 | DAR0916 | Equipment | BSS_HW_Stuck | Reset Air Scale | Muhammad Ali | 10/27/2025 01:19:56 | 10/27/2025 02:37:24 | 10/27/2025 05:19:56 | 1(3G/5G) sites down under DAR0916-P1/DAR1M3916-P1 @ Sceco | 10/27/2025 00:58:37 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/27/2025 00:57:56 | P2 | 2G | dair | Sceco | 3G_5G SA | DAR0916-P1 | FLM_TE | DAR0916 | Results: DOWN SITE HUB DAR0916-P1 DAR0916 Summary: Hub: DAR0916, Down Count: 1, Down Sites: DAR0916-P1 Alarm Summary: DAR0916 No Active Alarm on HUB | PCM-20251027-00000074 | No Power Issue | No Power Issue |  | sites down |  | API | 10/27/2025 01:19:56 | 10/27/2025 01:28:34 | 10/27/2025 02:37:05 |  |  | 10/27/2025 02:37:24 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000030 | PCM-20251027-00000089 | TT-20251026-01943 | Telecom | Region_4 | JED0271 | JED0271 |  |  |  | Mohammed Ramadan A Abu Abid | 10/27/2025 01:19:58 | 10/27/2025 06:02:03 | 10/27/2025 13:19:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/26/2025 17:50:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 17:50:34 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE |  |  | PCM-20251027-00000084 | No Power Issue | No Power Issue |  |  |  | API | 10/27/2025 01:19:58 | 10/27/2025 06:02:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000031 | PCM-20251027-00000092 | TT-20251026-02368 | Telecom | Region_6 | ABH0173 | ABH0173 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/27/2025 01:21:49 | 10/27/2025 01:30:08 | 10/27/2025 07:21:49 | 2(2G) 2(3G) 1(LTE) 2(5G) sites down under ABH0173-P3,ABH0611-P3/ABH0611-P3 @ Generator_SG | 10/26/2025 23:41:27 | Major | 7706 | BTS O&M LINK FAILURE | 10/26/2025 23:41:24 | P3 | 2G | abha | Sceco | 2G_3G_LTE_5G SA | ABH0173-P3 2G_3G_5G,ABH0611-P3 2G_3G_LTE_5G | FLM_TE | ABH0173 | Results: DOWN SITE HUB ABH0173-P3 ABH0173 ABH0611-P3 ABH0173 Summary: Hub: ABH0173, Down Count: 2, Down Sites: ABH0173-P3, ABH0611-P3 Alarm Summary: ABH0173 Alarm Active on HUB | PCM-20251026-00002392 | Thanks to check locally HUB site ABH0173 | Thanks to check locally HUB site ABH0173 |  | sites down |  | API | 10/27/2025 01:21:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000032 | PCM-20251027-00000095 | TT-20251027-00109 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/27/2025 01:23:41 | 10/27/2025 01:23:41 | 10/27/2025 05:23:41 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/27/2025 01:23:13 | Critical | 65334 | Door open Alarm Equipment room | 10/27/2025 01:23:10 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/27/2025 01:23:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000033 | PCM-20251027-00000098 | TT-20251027-00096 | Telecom | Region_4 | TAF1M7325 | TAF0325 |  |  |  | Ahmad Kamal Abdelmawla | 10/27/2025 01:24:19 | 10/27/2025 01:24:19 | 10/27/2025 13:24:19 | BASE STATION ANTENNA LINE PROBLEM at TAF1M7325-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/27/2025 01:09:27 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/27/2025 01:09:19 | P2 | 4G | taif | Sceco | LTE NSA | TAF1M7325 | FLM_TE |  |  | PCM-20251027-00000085 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/27/2025 01:24:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251027000035 | PCM-20251027-00000105 | TT-20251027-00113 | Telecom | Region_6 | BHAB1M7817 | BHAB0817 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/27/2025 01:27:02 | 10/27/2025 01:44:08 | 10/27/2025 13:27:02 | BASE STATION ANTENNA LINE PROBLEM at BHAB1M7817-G9-L8-SBTS-P2 @ Sceco | 10/27/2025 01:18:01 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/27/2025 01:17:52 | P1 | 4G | abha | Sceco | LTE NSA | BHAB1M7817 | FLM_TE |  |  | PCM-20251027-00000100 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/27/2025 01:27:02 | 10/27/2025 01:33:48 | 10/27/2025 01:42:58 | 10/27/2025 01:44:08 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000036 | PCM-20251027-00000106 | TT-20251026-02071 | Reference_telecom | Region_6 | NJR1M7777 | NJR0777 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/27/2025 01:27:10 | 10/27/2025 03:13:21 | 10/27/2025 13:27:10 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at NJR1M7777-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/26/2025 17:14:23 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 17:05:28 | P3 | 4G | najran | Sceco | LTE NSA | NJR1M7777 | FLM_TE |  |  | PCM-20251027-00000096 | Please close alarm during site down | Please close alarm during site down |  |  |  | API | 10/27/2025 01:27:10 | 10/27/2025 03:12:35 | 10/27/2025 03:13:11 |  |  | 10/27/2025 03:13:21 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000038 | PCM-20251027-00000114 | TT-20251026-02221 | Reference_telecom | Region_6 | QFL1M7033 | QFL0033 |  |  |  | Mohammed Sideag Mohammed Ali | 10/27/2025 01:33:47 | 10/27/2025 01:33:47 | 10/27/2025 13:33:47 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QFL1M7033-P2-CA-L800-SBTS @ Sceco | 10/26/2025 19:47:25 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 19:15:22 | P2 | 4G | jizan | Sceco | LTE NSA | QFL1M7033 | FLM_TE |  |  | PCM-20251027-00000102 | Please lose site is clear | Please lose site is clear |  |  |  | API | 10/27/2025 01:33:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000039 | PCM-20251027-00000117 | TT-20251027-00124 | Reference_EM | Region_1 | HFBD2005 | HFBD2005 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/27/2025 01:35:04 | 10/27/2025 01:35:04 | 10/27/2025 13:35:04 | Mains Failure at HFBD2005-P3_SRAN @ Generator_SG | 10/27/2025 01:25:08 | Minor | 65109 | Mains Failure | 10/27/2025 01:25:04 | P3 | SRAN | hafouf | Generator_SG | 2G NSA | HFBD2005 | FLM_EM | [8 empty] | API | 10/27/2025 01:35:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000041 | PCM-20251027-00000123 | TT-20251027-00135 | Telecom | Region_6 | JEC0089 | JEC0089 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/27/2025 01:40:44 | 10/27/2025 02:19:27 | 10/27/2025 13:40:44 | Power Supply at JEC0089-2 on 10.154.126.4 @ Generator_DG | 10/27/2025 01:39:34 | Minor | Power Supply | Power Supply | 10/27/2025 01:39:29 | VIP | 2G | baish | Generator_DG | TX NSA | JEC0089 | FLM_TE | [8 empty] | API | 10/27/2025 01:40:44 | 10/27/2025 02:19:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000042 | PCM-20251027-00000122 | TT-20251027-00134 | Telecom | Region_3 | HAL2M3127 | HAL0127 | Equipment | SFP_BTS | Replace SFP | Atif Shahzad Muhammad Ajaib | 10/27/2025 01:40:44 | 10/27/2025 02:29:57 | 10/27/2025 07:40:44 | BBU CPRI Interface Error at HAL2M3127-P2 @ Sceco | 10/27/2025 01:36:20 | Major | 26234 | BBU CPRI Interface Error | 10/27/2025 01:33:48 | P2 | 3G | hail | Sceco | 3G NSA | HAL2M3127 | FLM_TE | [8 empty] | API | 10/27/2025 01:40:44 |  | 10/27/2025 02:03:51 | 10/27/2025 02:03:53 | 10/27/2025 02:03:56 | 10/27/2025 02:29:57 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000044 | PCM-20251027-00000127 | TT-20251027-00133 | Telecom | Region_4 | JED1M7007 | JED0007 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/27/2025 01:45:30 | 10/27/2025 01:45:30 | 10/27/2025 05:45:30 | 1(LTE) sites down under JED0007-P1-DIA-CA-L900-L800 @ Sceco | 10/27/2025 01:37:27 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 01:37:24 | P1 | 4G | jeddah | Sceco | LTE SA | JED0007-P1-DIA-CA-L900-L800 | FLM_TE | JED0007 | Results: DOWN SITE HUB JED0007-P1-DIA-CA-L900-L800 JED0007 Summary: Hub: JED0007, Down Count: 1, Down Sites: JED0007-P1-DIA-CA-L900-L800 Alarm Summary: JED0007 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.88.12:8080] [URL:http://10.97.88.12:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 01:45:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000045 | PCM-20251027-00000128 | TT-20251027-00127 | Telecom | Region_2 | RIYA6116 | RIYA6116 |  |  |  | Tanveer Ahmed | 10/27/2025 01:50:26 | 10/27/2025 02:22:10 | 10/27/2025 07:50:26 | 1(2G) sites down under RIYA6116-P3/R2_RY1_HWBSC01 @ Sceco | 10/27/2025 01:32:59 | Major | 21825 | CSL Fault | 10/27/2025 01:32:56 | P3 | SRAN | riyadh | Sceco | 2G SA | RIYA6116-P3 | FLM_TE | RIYA6116 | We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20251027-00000126 | We are not observing any issue at TX end. Kindly visit the site and check issue locally | We are not observing any issue at TX end. Kindly visit the site and check issue locally |  | sites down |  | API | 10/27/2025 01:50:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000046 | PCM-20251027-00000129 | TT-20251027-00140 | Telecom | Region_5 | MAK2709 | MAK2709 |  |  |  | Husain Hassan Ishag Omer | 10/27/2025 01:50:34 | 10/27/2025 01:50:34 | 10/27/2025 07:50:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2709-G9-L8-L18-L21-NR2.6-SBTS @ Sceco | 10/27/2025 01:49:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 01:49:24 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2709 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 01:50:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000049 | PCM-20251027-00000135 | TT-20251027-00148 | Reference_telecom | Region_4 | MLJI1M8370 | MLJI2370 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/27/2025 01:58:49 | 10/27/2025 03:35:11 | 10/27/2025 07:58:49 | CELL FAULTY (VSWR major alarm) at MLJI1M8370-USF-P3 @ Generator_SG | 10/27/2025 01:54:11 | Major | 7653 | CELL FAULTY | 10/27/2025 01:54:03 | P2 | 4G | alaith | Generator_SG | LTE_Cell SA | MLJI1M8370 | FLM_TE | [5 empty] | VSWR major alarm |  |  | API | 10/27/2025 01:58:49 | 10/27/2025 03:35:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000050 | PCM-20251027-00000143 | TT-20251027-00144 | Telecom | Region_3 | YBDB0979 | YBDB0979 |  |  |  | Hossam Ali Ahmed Ali | 10/27/2025 02:04:16 | 10/27/2025 02:04:16 | 10/27/2025 08:04:16 | 3(3G) 2(LTE) sites down under AWJ0538-P3,AWJ0975-P2,YBDB0979-P2/YB1MBSCH01 @ Sceco | 10/27/2025 01:53:11 | Major | 22214 | NodeB Unavailable | 10/27/2025 01:53:09 | P3 | SRAN | tabouk | Sceco | 3G_LTE SA | AWJ0538-P3 3G_LTE,YBDB0979-P2 3G_LTE,AWJ0975-P2 3G | FLM_TE | YBDB0979 | Dear Team, We are observing MW_BER_SD alarms and HU issue at MW LINK YBDB0979 DIR YBDB0297 | PCM-20251027-00000138 | Dear Team, We are observing MW_BER_SD alarms and HU issue at MW LINK YBDB0979 DIR YBDB0297 | Dear Team, We are observing MW_BER_SD alarms and HU issue at MW LINK YBDB0979 DIR YBDB0297 |  | sites down |  | API | 10/27/2025 02:04:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000053 | PCM-20251027-00000146 | TT-20251027-00147 | Telecom | Region_2 | WRIY0062 | RIY0062 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/27/2025 02:06:14 | 10/27/2025 08:07:22 | 10/27/2025 14:06:14 | WRIY0062 Complete Down | 10/27/2025 01:50:41 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/27/2025 01:50:41 | P3 | WIFI | riyadh | Sceco | Wifi SA | WRIY0062 | FLM_TE |  | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally | PCM-20251027-00000134 | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally |  |  |  | API | 10/27/2025 02:06:14 | 10/27/2025 08:07:03 | 10/27/2025 08:07:15 |  |  | 10/27/2025 08:07:22 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000054 | PCM-20251027-00000149 | TT-20251027-00160 | Telecom | Region_1 | HFF6028 | HFF6028 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/27/2025 02:10:42 | 10/27/2025 02:52:07 | 10/27/2025 14:10:42 | RF Unit Maintenance Link Failure at HFF6028-DCU1 @ Sceco | 10/27/2025 01:57:32 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 02:05:23 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/27/2025 02:10:42 | 10/27/2025 02:52:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000055 | PCM-20251027-00000150 | TT-20251027-00082 | Telecom | Region_4 | JED1MN0007 | JED0007 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/27/2025 02:11:36 | 10/27/2025 02:11:36 | 10/27/2025 08:11:36 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1MN0007-NR2.6-P2 @ Sceco | 10/27/2025 01:03:43 | Major | 7114 | CELL SERVICE PROBLEM | 10/27/2025 01:03:31 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0007 | FLM_TE |  |  | PCM-20251027-00000075 | Please perform the HC for cell-B sleeping cell issue | Confirm if user behavior |  |  |  | API | 10/27/2025 02:11:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000056 | PCM-20251027-00000151 | TT-20251027-00149 | Reference_telecom | Region_4 | JED1M8333 | JED2333 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/27/2025 02:12:35 | 10/27/2025 02:12:35 | 10/27/2025 08:12:35 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at JED1M8333-P3-CA-L800 @ Generator_SG | 10/27/2025 01:59:50 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/26/2025 03:03:59 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_TE |  |  | PCM-20251027-00000136 | Please check the site down | Please check the site down |  |  |  | API | 10/27/2025 02:12:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251027000057 | PCM-20251027-00000152 | TT-20251027-00161 | Reference_EM | [7 empty] | 10/27/2025 02:12:46 | 10/27/2025 02:12:46 | 10/27/2025 14:12:46 | NETECO: DC Undervoltage at HLMD2492 @ Generator_SG | 10/27/2025 02:06:42 | Minor | 10153 | DC Undervoltage | 10/27/2025 02:06:42 | P3 | SRAN |  | Generator_SG | 2G NSA | HLMD2492 | FLM_EM | [8 empty] | API | 10/27/2025 02:12:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000059 | PCM-20251027-00000162 | TT-20251027-00167 | Reference_telecom | Region_4 | TAF2390 | TAF2390 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/27/2025 02:18:33 | 10/27/2025 07:58:30 | 10/27/2025 08:18:33 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TAF2390-GSM-P2 @ Sceco | 10/27/2025 02:11:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 02:11:26 | P2 | 2G | taif | Sceco | 5G_Cell SA | TAF2390 | FLM_TE |  |  | PCM-20251027-00000158 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/27/2025 02:18:33 | 10/27/2025 07:58:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000060 | PCM-20251027-00000175 | TT-20251027-00183 | Reference_telecom | Region_6 | BSA2313 | BSA2313 |  |  |  | Hamid Ullah Muhammad Alam Khan | 10/27/2025 02:27:46 | 10/27/2025 03:36:03 | 10/27/2025 14:27:46 | DemFail observed in BSA2313_02 towards 10.221.244.20 @ Sceco | 10/26/2025 14:27:23 | Minor |  | DemFail | 10/26/2025 14:27:18 | P3 | 2G | bisha | Sceco | TX NSA | BSA2313 | FLM_TE | [8 empty] | API | 10/27/2025 02:27:46 | 10/27/2025 03:36:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000061 | PCM-20251027-00000177 | TT-20251027-00166 | Telecom | Region_1 | DMHF2074 | DMHF2074 |  |  |  | Emad fawzi eldebsi | 10/27/2025 02:28:42 | 10/27/2025 02:28:42 | 10/27/2025 08:28:42 | 3(2G) 3(3G) 3(LTE) sites down under DMHF2074-P3,ARM0875-P2,DMHF0076-P2/R1_HF_HWBSC01 @ Sceco | 10/27/2025 02:14:05 | Major | 21825 | CSL Fault | 10/27/2025 02:14:02 | P2 | SRAN | hafouf | Generator_SG | 2G_3G_LTE SA | DMHF2074-P3 2G_3G_LTE,DMHF0076-P2 2G_3G_LTE,ARM0875-P2 2G_3G_LTE | FLM_EM | DMHF2074 | Dear Team, Hub: DMHF2074 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251027-00000169 | Dear Team, Hub: DMHF2074 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: DMHF2074 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/27/2025 02:28:42 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000064 | PCM-20251027-00000183 | TT-20251027-00164 | Telecom | Region_4 | JED6135 | JED6135 |  |  |  | Mohamed Farag Abdelbary | 10/27/2025 02:39:55 | 10/27/2025 02:39:55 | 10/27/2025 14:39:55 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/27/2025 02:09:25 | Minor | 7114 | CELL SERVICE PROBLEM | 10/27/2025 02:09:12 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251027-00000154 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/27/2025 02:39:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000066 | PCM-20251027-00000188 | TT-20251027-00171 | Telecom | Region_6 | ABH1M7179 | ABH0179 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/27/2025 02:41:34 | 10/27/2025 05:53:12 | 10/27/2025 08:41:34 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at ABH1M7179-CA-L800-SBTS @ Sceco | 10/27/2025 02:12:57 | Major | 7114 | CELL SERVICE PROBLEM | 10/27/2025 02:12:48 | P3 | 4G | abha | Sceco | 5G_Cell SA | ABH1M7179 | FLM_TE |  |  | PCM-20251027-00000161 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/27/2025 02:41:34 | 10/27/2025 05:53:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000067 | PCM-20251027-00000189 | TT-20251027-00198 | EM | Region_2 | U2000 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/27/2025 02:42:13 | 10/27/2025 02:42:13 | 10/27/2025 14:42:13 | Switch Device Link Status Fault at U2000 NFV @ Sceco_STB | 10/27/2025 02:35:07 | Minor | 268390415 | Switch Device Link Status Fault | 10/27/2025 02:35:03 | P1 | Performance | riyadh | Sceco_STB | 2G NSA | U2000 | FLM_EM | [8 empty] | API | 10/27/2025 02:42:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251027000068 | PCM-20251027-00000190 | TT-20251027-00199 | Telecom | [7 empty] | 10/27/2025 02:42:14 | 10/27/2025 02:42:14 | 10/27/2025 06:42:14 | The Device is offline at DAM-E1000E-N7-FW-02 @ Sceco_STB | 10/27/2025 02:42:02 | Critical | 101-7 | The Device is offline | 10/27/2025 02:42:00 | P1 | IPBB |  | Sceco_STB | IPRAN SA | DAM-E1000E-N7-FW-02 | FLM_TE | [8 empty] | API | 10/27/2025 02:42:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000071 | PCM-20251027-00000195 | TT-20251027-00200 | Reference_telecom | Region_4 | TAF1M7287 | TAF0287 |  |  |  | Ahmad Kamal Abdelmawla | 10/27/2025 02:47:31 | 10/27/2025 02:47:31 | 10/27/2025 08:47:31 | CELL OPERATION DEGRADED (Antenna Line Device failure) at TAF1M7287-CA-P3 @ Sceco | 10/27/2025 02:35:17 | Major | 7654 | CELL OPERATION DEGRADED | 10/27/2025 02:35:02 | P3 | 4G | taif | Sceco | LTE_Cell SA | TAF1M7287 | FLM_TE |  |  | PCM-20251027-00000191 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/27/2025 02:47:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000072 | PCM-20251027-00000197 | TT-20251027-00209 | Telecom | Region_1 | DM1-OSN7500-SWAP | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/27/2025 02:51:36 | 10/27/2025 02:51:36 | 10/27/2025 08:51:36 | GNE_CONNECT_FAIL Active alarm at DM1-OSN7500-SWAP Connection with gateway DM1-OSN7500-SWAP failed | 10/27/2025 02:43:54 | Major | 0-4 | GNE_CONNECT_FAIL | 10/27/2025 02:43:54 | P1 | TX | dammam | Sceco_STB | TX NSA | DM1-OSN7500-SWAP | FLM_TE | [5 empty] | GNE_CONNECT_FAIL Active alarm at DM1-OSN7500-SWAP Connection with gateway DM1-OSN7500-SWAP failed |  |  | API | 10/27/2025 02:51:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251027000073 | PCM-20251027-00000198 | TT-20251026-02336 | Reference_telecom | Region_6 | DAR0916 | DAR0916 |  |  |  | Muhammad Ali | 10/27/2025 02:52:16 | 10/27/2025 08:06:56 | 10/27/2025 08:52:16 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at DAR0916-GSM-UMTS-P2 @ Sceco | 10/26/2025 23:15:02 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/26/2025 23:14:53 | P2 | 2G | dair | Sceco | 5G_Cell SA | DAR0916 | FLM_TE |  |  | PCM-20251027-00000186 | Post reset still issue is exists FXDB F7172010966, Please check with the spare | Post reset still issue is exists FXDB F7172010966, Please check with the spare |  |  |  | API | 10/27/2025 02:52:16 | 10/27/2025 06:49:04 | 10/27/2025 07:04:35 | 10/27/2025 07:04:39 | 10/27/2025 08:06:56 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000074 | PCM-20251027-00000201 | TT-20251027-00214 | Reference_EM | Region_3 | MDYB0409 | MDYB0409 |  |  |  | Osama Abdelmagid Abdelsalam Wafa | 10/27/2025 02:55:09 | 10/27/2025 02:55:09 | 10/27/2025 08:55:09 | Door opening alarm at MDYB0409-P1-HUB_SRAN @ Generator_DG | 10/27/2025 02:54:41 | Major | 65101 | Door opening alarm | 10/27/2025 02:54:35 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB0409 | FLM_EM | [8 empty] | API | 10/27/2025 02:55:09 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000075 | PCM-20251027-00000202 | TT-20251008-02002 | MW_HC | Region_6 | MKW9711 | MKW9711 |  |  |  | Manzoor Ahmed | 10/27/2025 02:57:12 | 10/27/2025 08:49:46 | 10/27/2025 14:57:12 | Nokia MW HC_P2 Observing Modem Down at MKW9711_01-BHAB0823_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | Repeater | makhwa | Sceco | TX NSA | MKW9711_01-BHAB0823_02 | FLM_TE |  |  | PCM-20251027-00000172 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/27/2025 02:57:12 | 10/27/2025 08:49:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000077 | PCM-20251027-00000207 | TT-20251027-00018 | Reference_telecom | Region_6 | KHS1M7993 | KHS0993 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/27/2025 03:05:47 | 10/27/2025 03:05:47 | 10/27/2025 09:05:47 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at KHS1M7993-P2-USF-L900 @ Sceco | 10/27/2025 00:19:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 00:18:54 | P2 | 4G | khamis mushyet | Sceco | 5G_Cell SA | KHS1M7993 | FLM_TE |  |  | PCM-20251027-00000174 | Alarm is clear please close | Alarm is clear please close |  |  |  | API | 10/27/2025 03:05:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000080 | PCM-20251027-00000214 | TT-20251027-00230 | Reference_telecom | Region_6 | BHAB1M8006 | BHAB2006 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/27/2025 03:13:44 | 10/27/2025 03:13:44 | 10/27/2025 15:13:44 | BASE STATION SERVICE PROBLEM (TX out of order) at BHAB1M8006-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/27/2025 03:08:56 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 03:08:48 | P3 | 4G | mohail | Generator_SG | LTE_Cell SA | BHAB1M8006 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/27/2025 03:13:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000081 | PCM-20251027-00000217 | TT-20251027-00229 | EM | Region_6 | MKW2121 | MKW2121 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/27/2025 03:18:29 | 10/27/2025 03:18:29 | 10/27/2025 09:18:29 | 1(2G/LTE) sites down under MKW2121-P3/MKW2121-P3 @ Generator_SG | 10/27/2025 03:10:29 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 03:10:25 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | MKW2121-P3 | FLM_EM | MKW2121 | Results: DOWN SITE HUB MKW2121-P3 MKW2121 Summary: Hub: MKW2121, Down Count: 1, Down Sites: MKW2121-P3 Alarm Summary: MKW2121 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 03:18:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251027000082 | PCM-20251027-00000218 | TT-20251027-00243 | EM | [7 empty] | 10/27/2025 03:26:40 | 10/27/2025 03:26:40 | 10/27/2025 15:26:40 | NETECO: Maintenance Reminder at HLMD2552 @ Generator_DG | 10/27/2025 03:20:30 | Minor | 40563 | Maintenance Reminder | 10/27/2025 03:20:30 | P3 | SRAN |  | Generator_DG | 2G NSA | HLMD2552 | FLM_EM | [8 empty] | API | 10/27/2025 03:26:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000083 | PCM-20251027-00000219 | TT-20251027-00210 | Reference_telecom | Region_2 | RIYC2U6725 | RIYC6025 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/27/2025 03:28:00 | 10/27/2025 03:28:00 | 10/27/2025 15:28:00 | Cell RX Channel Interference Noise Power Unbalanced at RIYC2U6725-L800-CA-P3 @ Sceco | 10/26/2025 23:52:12 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/26/2025 23:52:08 | P2 | 4G | riyadh | Sceco | 2G NSA | RIYC2U6725 | FLM_TE |  |  | PCM-20251027-00000199 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/27/2025 03:28:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000085 | PCM-20251027-00000221 | TT-20251027-00232 | Reference_telecom | Region_6 | BCH0080 | BCH0080 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/27/2025 03:28:23 | 10/27/2025 08:50:11 | 10/27/2025 15:28:23 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at BCH0080-G9-NL8-L9-NL18-NR2.6-SBTS-P3 @ Sceco | 10/27/2025 03:11:19 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 03:11:11 | P3 | 2G | Albaha | Sceco | 5G_Cell SA | BCH0080 | FLM_TE |  |  | PCM-20251027-00000215 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/27/2025 03:28:23 | 10/27/2025 08:49:46 | 10/27/2025 08:50:02 |  |  | 10/27/2025 08:50:11 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000091 | PCM-20251027-00000251 | TT-20251027-00270 | Telecom | Region_4 | SQR1M3183 | SQR0183 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/27/2025 04:04:59 | 10/27/2025 04:18:29 | 10/27/2025 10:04:59 | 1(3G) sites down under SQR0183-P2-USF/SQR1M3183-P2-USF @ Generator_SG | 10/27/2025 03:57:22 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/27/2025 03:56:41 | P2 | 3G | alaith | Generator_SG | 3G SA | SQR0183-P2-USF | FLM_TE |  | Results: DOWN SITE HUB SQR0183-P2-USF Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/27/2025 04:04:59 | 10/27/2025 04:17:45 | 10/27/2025 04:18:15 |  |  | 10/27/2025 04:18:29 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000092 | PCM-20251027-00000261 | TT-20251027-00275 | Telecom | Region_4 | SQR1M3198 | SQR0198 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/27/2025 04:06:29 | 10/27/2025 04:18:04 | 10/27/2025 10:06:29 | 1(3G) sites down under SQR0198-P2-USF/SQR1M3198-P2-USF @ Generator_SG | 10/27/2025 03:58:49 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/27/2025 03:58:10 | P2 | 3G | adam | Generator_SG | 3G SA | SQR0198-P2-USF | FLM_TE |  | Results: DOWN SITE HUB SQR0198-P2-USF Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/27/2025 04:06:29 | 10/27/2025 04:17:46 | 10/27/2025 04:17:54 |  |  | 10/27/2025 04:18:04 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000093 | PCM-20251027-00000264 | TT-20251027-00288 | Telecom | Region_1 | KBR0155 | KBR0155 |  |  |  | Imran Ali Yousaf | 10/27/2025 04:09:33 | 10/27/2025 04:09:33 | 10/27/2025 16:09:33 | RF Unit Maintenance Link Failure at KBR0155-P3_SRAN @ Sceco | 10/27/2025 04:04:16 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 04:04:10 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0155 | FLM_TE | [8 empty] | API | 10/27/2025 04:09:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000095 | PCM-20251027-00000266 | TT-20251027-00290 | EM | Region_6 | UKHA1M8371 | UKHA2371 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/27/2025 04:11:37 | 10/27/2025 08:53:06 | 10/27/2025 16:11:37 | RECTIFIER MODULE FAILURE at UKHA1M8371-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/27/2025 04:03:29 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/27/2025 04:03:22 | P3 | 4G | Baha | Generator_DG | LTE NSA | UKHA1M8371 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/27/2025 04:11:37 | 10/27/2025 08:53:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000097 | PCM-20251027-00000270 | TT-20251027-00295 | Telecom | Region_5 | MAK1MN0326 | MAK0326 |  |  |  | Atif Javed Javed Hussain | 10/27/2025 04:16:16 | 10/27/2025 04:16:16 | 10/27/2025 16:16:16 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0326-NR2.6-VIP @ Sceco | 10/27/2025 04:08:11 | Minor | 7115 | BASE STATION INFORMATION | 10/27/2025 04:08:03 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0326 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/27/2025 04:16:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000099 | PCM-20251027-00000272 | TT-20251027-00285 | Telecom | Region_6 | MKW2121 | MKW2121 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/27/2025 04:21:24 | 10/27/2025 04:21:25 | 10/27/2025 10:21:24 | 4(2G) 4(LTE) sites down under MKW2140-P3,MKW2128-P3,MKW2131-P3,MKW2133-P3/MKW2133-P3 @ Generator_SG | 10/27/2025 04:04:28 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 04:04:24 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | MKW2140-P3 2G_LTE,MKW2128-P3 2G_LTE,MKW2131-P3 2G_LTE,MKW2133-P3 2G_LTE | FLM_EM | MKW2121 | Hub: MKW2121 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251027-00000268 | Hub: MKW2121 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: MKW2121 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/27/2025 04:21:24 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000102 | PCM-20251027-00000275 | TT-20251027-00304 | Reference_telecom | Region_4 | JED2010 | JED2010 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/27/2025 04:23:29 | 10/27/2025 04:23:29 | 10/27/2025 16:23:29 | LossOfSignal observed in JED2010_02 towards 10.1.225.116 @ Sceco | 10/26/2025 16:24:55 | Minor |  | LossOfSignal | 10/26/2025 16:23:19 | P3 | 2G | jeddah | Sceco | TX NSA | JED2010 | FLM_TE | [8 empty] | API | 10/27/2025 04:23:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000103 | PCM-20251027-00000276 | TT-20251027-00305 | Reference_telecom | Region_4 | JED2812 | JED2812 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/27/2025 04:23:29 | 10/27/2025 04:23:29 | 10/27/2025 16:23:29 | Degrade observed in JED2812 towards 10.1.225.117 @ Sceco | 10/26/2025 16:24:54 | Minor |  | Degrade | 10/26/2025 16:23:17 | P3 | 2G | jeddah | Sceco | TX NSA | JED2812 | FLM_TE | [8 empty] | API | 10/27/2025 04:23:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000104 | PCM-20251027-00000277 | TT-20251027-00306 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/27/2025 04:24:00 | 10/27/2025 04:24:00 | 10/27/2025 08:24:00 | OSC_LOS at YBDB2655_OCS1 @ Sceco_STB | 10/27/2025 04:23:32 | Critical | 1-12843 | OSC_LOS | 10/27/2025 04:23:22 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE | [5 empty] | 0-TO YBDB0290(1-A)-1-B1SAFS-6(RX1/TX1(TO YBDB0290_OCS,B1SAFS(1-A01(TRM1))-OSC:1 |  |  | API | 10/27/2025 04:24:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251027000105 | PCM-20251027-00000278 | TT-20251027-00300 | EM | [7 empty] | 10/27/2025 04:24:59 | 10/27/2025 04:24:59 | 10/27/2025 10:24:59 | 1(2G/LTE) sites down under HLMD2492-P3-CAP/R3_HL_HWBSC01 @ Generator_SG | 10/27/2025 04:16:44 | Major | 21825 | CSL Fault | 10/27/2025 04:16:42 | P3 | 2G |  | Generator_SG | 2G_LTE SA | HLMD2492-P3-CAP | FLM_EM | HLMD2492 | Results: DOWN SITE HUB HLMD2492-P3-CAP HLMD2492 Summary: Hub: HLMD2492, Down Count: 1, Down Sites: HLMD2492-P3-CAP Alarm Summary: HLMD2492 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 04:24:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000106 | PCM-20251027-00000284 | TT-20251027-00312 | Telecom | Region_4 | TAF0135 | TAF0135 |  |  |  | Ahmad Kamal Abdelmawla | 10/27/2025 04:25:33 | 10/27/2025 04:25:33 | 10/27/2025 10:25:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF0135-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Sceco | 10/27/2025 04:24:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 04:24:35 | VIP | 2G | taif | Sceco | 5G_Cell SA | TAF0135 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 04:25:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000107 | PCM-20251027-00000286 | TT-20251027-00302 | Telecom | Region_4 | TAF1M3135 | TAF0135 |  |  |  | Ahmad Kamal Abdelmawla | 10/27/2025 04:27:31 | 10/27/2025 04:27:31 | 10/27/2025 08:27:31 | 1(3G) sites down under TAF0135-P1-VIP/TAF1M3135-P1-VIP @ Sceco | 10/27/2025 04:20:03 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/27/2025 04:19:21 | VIP | 3G | taif | Sceco | 3G SA | TAF0135-P1-VIP | FLM_TE | TAF0135 | Results: DOWN SITE HUB TAF0135-P1-VIP TAF0135 Summary: Hub: TAF0135, Down Count: 1, Down Sites: TAF0135-P1-VIP Alarm Summary: TAF0135 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 04:27:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000110 | PCM-20251027-00000293 | TT-20251027-00324 | Reference_telecom | Region_4 | JED0151 | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/27/2025 04:31:15 | 10/27/2025 04:46:16 | 10/27/2025 08:31:15 | SCECO LINK DOWN B/W JED0151 (JD1)--JD2_LH under RO's Activity ASON and OLP Switching Test at JED0151 (JD1) _JED0002 (JD2) | 10/27/2025 04:30:57 | Critical | 1-12843 | OSC_LOS | 10/27/2025 04:30:43 | VIP | 2G | jeddah | Sceco_STB | DWDM NSA | JED0151 | FLM_TE | [5 empty] | 0-TO JED0213 (JD3)(1-A)-6-G2AST4-3(RM3/TM3(TO JD2_OCS,TNG6WDAPXF(1-B02)-RM2/TM2))-OSC:1 |  |  | API | 10/27/2025 04:31:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000112 | PCM-20251027-00000302 | TT-20251027-00341 | Telecom | Region_5 | MAK2208 | MAK2208 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/27/2025 04:35:53 | 10/27/2025 04:35:53 | 10/27/2025 16:35:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2208-G9-NL8-NL18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/27/2025 04:35:08 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 04:35:00 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2208 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 04:35:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000115 | PCM-20251027-00000313 | TT-20251027-00319 | EM | Region_1 | UQL0282 | UQL0282 |  |  |  | Almmoez Almmoez | 10/27/2025 04:52:53 | 10/27/2025 04:52:53 | 10/27/2025 10:52:53 | 1(2G/3G) sites down under UQL0282-P2/AR1BSCH01 @ Sceco | 10/27/2025 04:28:25 | Major | 21825 | CSL Fault | 10/27/2025 04:28:24 | P2 | SRAN | rafha | Sceco | 2G_3G SA | UQL0282-P2 | FLM_TE | UQL0282 | Dear Team, Hub site is UQL0282 We are observing visibility down at both ends. Kindly visit the site and check the issue locally. | PCM-20251027-00000307 | Dear Team, Hub site is UQL0282 We are observing visibility down at both ends. Kindly visit the site and check the issue locally. | Dear Team, Hub site is UQL0282 We are observing visibility down at both ends. Kindly visit the site and check the issue locally. |  | sites down |  | API | 10/27/2025 04:52:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000116 | PCM-20251027-00000314 | TT-20251027-00359 | Telecom | Region_4 | JED1M8392 | JED2392 |  |  |  | MALIK ATIF ZAMAN | 10/27/2025 04:53:28 | 10/27/2025 08:57:19 | 10/27/2025 10:53:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8392-L800-CA-P3 @ Sceco | 10/27/2025 04:52:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 04:52:19 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8392 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 04:53:28 | 10/27/2025 08:57:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000117 | PCM-20251027-00000323 | TT-20251027-00364 | Reference_telecom | Region_6 | ARF1M7695 | ARF0695 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/27/2025 05:03:56 | 10/27/2025 05:03:56 | 10/27/2025 17:03:56 | BASE STATION SERVICE PROBLEM (Fault between FSM and FSP because of the lack of RP1 clock) at ARF1M7695-P2-USF-SBTS-L800 @ Sceco | 10/27/2025 04:53:15 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 04:53:08 | P2 | 4G | khamis mushyet | Sceco | 5G_Cell SA | ARF1M7695 | FLM_TE |  |  | PCM-20251027-00000318 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/27/2025 05:03:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000119 | PCM-20251027-00000324 | TT-20251027-00367 | Telecom | Region_6 | KMS0599 | KMS0599 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/27/2025 05:04:27 | 10/27/2025 05:04:27 | 10/27/2025 17:04:27 | BASE STATION ANTENNA LINE PROBLEM at KMS0599-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/27/2025 04:54:24 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/27/2025 04:54:13 | P3 | 2G | khamis mushyet | Sceco | 2G NSA | KMS0599 | FLM_TE |  |  | PCM-20251027-00000320 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/27/2025 05:04:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000120 | PCM-20251027-00000325 | TT-20251027-00365 | EM | Region_6 | BHAB1M8253 | BHAB2253 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/27/2025 05:04:29 | 10/27/2025 08:24:01 | 10/27/2025 11:04:29 | 1(2G/LTE) sites down under BHAB2253-P3 @ Generator_SG | 10/27/2025 04:56:28 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 04:56:26 | P3 | 4G | Albaha | Generator_SG | LTE SA | BHAB2253-G9-L8-L18-SBTS-P3 | FLM_TE | BHAB2253 | Results: DOWN SITE HUB BHAB2253-G9-L8-L18-SBTS-P3 BHAB2253 Summary: Hub: BHAB2253, Down Count: 1, Down Sites: BHAB2253-G9-L8-L18-SBTS-P3 Alarm Summary: BHAB2253 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.169.83.142:8080] [URL:http://10.169.83.142:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 05:04:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000121 | PCM-20251027-00000326 | TT-20251027-00371 | Telecom | Region_2 | RYAB2748 | RYAB2748 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Hakim Ullah Raif Ullah Jan | 10/27/2025 05:05:52 | 10/27/2025 06:37:26 | 10/27/2025 17:05:52 | RF Unit Maintenance Link Failure at RYAB2748-P2_SRAN @ Sceco | 10/27/2025 05:02:21 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 05:00:38 | P2 | SRAN | al kharj | Sceco | 2G NSA | RYAB2748 | FLM_TE | [8 empty] | API | 10/27/2025 05:05:52 | 10/27/2025 05:26:03 | 10/27/2025 05:26:22 | 10/27/2025 05:26:25 | 10/27/2025 06:07:55 | 10/27/2025 06:37:26 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000122 | PCM-20251027-00000328 | TT-20251027-00372 | Telecom | Region_2 | RIY0191 | RIY0191 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/27/2025 05:06:22 | 10/27/2025 06:32:45 | 10/27/2025 17:06:22 | RF Unit Maintenance Link Failure at RIY0191-P1-SHOP_SRAN @ Sceco | 10/27/2025 05:01:24 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 05:00:55 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0191 | FLM_TE | [8 empty] | API | 10/27/2025 05:06:22 | 10/27/2025 05:38:19 | 10/27/2025 06:32:14 | 10/27/2025 06:32:16 | 10/27/2025 06:32:20 | 10/27/2025 06:32:45 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000123 | PCM-20251027-00000330 | TT-20251027-00368 | Telecom | Region_4 | JED0911 | JED0911 |  |  |  | Khaled Mohammad Abdallah | 10/27/2025 05:08:29 | 10/27/2025 06:28:21 | 10/27/2025 11:08:29 | 1 (2G) site down under JED0911-P2 @ Sceco | 10/27/2025 05:02:49 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 05:02:45 | P2 | 2G | jeddah | Sceco | 2G SA | JED0911 | FLM_TE | JED0911 | Results: DOWN SITE HUB JED0911 JED0911 Summary: Hub: JED0911, Down Count: 1, Down Sites: JED0911 Alarm Summary: JED0911 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/27/2025 05:08:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251027000124 | PCM-20251027-00000331 | TT-20251027-00374 | EM | [7 empty] | 10/27/2025 05:08:58 | 10/27/2025 05:08:58 | 10/27/2025 17:08:58 | NETECO: Door Status Sensor Alarm at HLMD2492 @ Generator_SG | 10/27/2025 05:08:32 | Minor | 5152 | Door Status Sensor Alarm | 10/27/2025 05:08:32 | P3 | SRAN |  | Generator_SG | 2G NSA | HLMD2492 | FLM_EM | [8 empty] | API | 10/27/2025 05:08:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000125 | PCM-20251027-00000332 | TT-20251027-00376 | Reference_telecom | Region_4 | RYMK0542 | RYMK0542 |  |  |  | Rashid Shafique | 10/27/2025 05:10:00 | 10/27/2025 05:10:00 | 10/27/2025 17:10:00 | DemFail observed in RYMK0542_03 towards 10.3.236.247 @ Sceco_STB | 10/26/2025 17:11:02 | Minor |  | DemFail | 10/26/2025 17:09:52 | P2 | 2G | taif | Sceco_STB | TX NSA | RYMK0542 | FLM_TE | [8 empty] | API | 10/27/2025 05:10:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000126 | PCM-20251027-00000333 | TT-20251027-00377 | Reference_telecom | Region_4 | HAW0296 | HAW0296 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/27/2025 05:13:37 | 10/27/2025 07:58:30 | 10/27/2025 17:13:37 | Degrade observed in HAW0296_09 towards 10.221.241.161 @ Sceco | 10/26/2025 17:14:26 | Minor |  | Degrade | 10/26/2025 17:13:06 | P1 | 2G | taif | Sceco | TX NSA | HAW0296 | FLM_TE | [8 empty] | API | 10/27/2025 05:13:37 | 10/27/2025 07:58:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000128 | PCM-20251027-00000335 | TT-20251027-00382 | Reference_telecom | Region_4 | JED0604 | JED0604 |  |  |  | MALIK ATIF ZAMAN | 10/27/2025 05:17:45 | 10/27/2025 08:57:19 | 10/27/2025 17:17:45 | Degrade observed in JED0604_10 towards 10.10.178.209 @ Sceco | 10/26/2025 17:17:31 | Minor |  | Degrade | 10/26/2025 17:17:27 | P1 | 2G | jeddah | Sceco | TX NSA | JED0604 | FLM_TE | [8 empty] | API | 10/27/2025 05:17:45 | 10/27/2025 08:57:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000129 | PCM-20251027-00000337 | TT-20251027-00391 | Telecom | Region_5 | MAK0945 | MAK0945 |  |  |  | Mosab Nasr eldeen Mohamed | 10/27/2025 05:24:28 | 10/27/2025 05:24:28 | 10/27/2025 17:24:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0945-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/27/2025 05:23:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 05:23:43 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK0945 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 05:24:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000131 | PCM-20251027-00000339 | TT-20251027-00393 | Telecom | Region_6 | TLT1M7324 | TLT0324 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/27/2025 05:26:33 | 10/27/2025 06:56:03 | 10/27/2025 17:26:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at TLT1M7324-L2100-L1800-L800-SBTS-P3 @ Sceco | 10/27/2025 05:25:52 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 05:25:43 | P3 | 4G | tathleeth | Sceco | 5G_Cell SA | TLT1M7324 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 05:26:33 | 10/27/2025 06:55:28 | 10/27/2025 06:55:54 |  |  | 10/27/2025 06:56:03 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000132 | PCM-20251027-00000347 | TT-20251027-00407 | Telecom | Region_2 | RIY0191 | RIY0191 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/27/2025 05:33:25 | 10/27/2025 06:30:43 | 10/27/2025 11:33:25 | 1(LTE) sector down at RIY0191 | 10/27/2025 05:28:13 | Major | 29240 | Cell Unavailable | 10/27/2025 05:28:13 | P1 | SRAN | riyadh | Sceco | 2G SA | RIY0191 | FLM_TE | [6 empty] | sector down |  | API | 10/27/2025 05:33:25 | 10/27/2025 05:37:19 | 10/27/2025 05:38:10 | 10/27/2025 05:38:14 | 10/27/2025 06:04:03 | 10/27/2025 06:30:43 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000134 | PCM-20251027-00000355 | TT-20251027-00408 | Telecom | Region_5 | SOMQ1S7902 | SOMQ0902 |  |  |  | Amjad Ali Muhammad Parves | 10/27/2025 05:38:30 | 10/27/2025 05:38:30 | 10/27/2025 11:38:30 | 1(LTE) sites down under SOMQ0902-USF-P3 @ Sceco | 10/27/2025 05:30:21 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 05:30:18 | P3 | 4G | makkah | Sceco | LTE SA | SOMQ0902-USF-P3 | FLM_TE | SOMQ0902 | Results: DOWN SITE HUB SOMQ0902-USF-P3 SOMQ0902 Summary: Hub: SOMQ0902, Down Count: 1, Down Sites: SOMQ0902-USF-P3 Alarm Summary: SOMQ0902 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.95.172:8080] [URL:http://10.88.95.172:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 05:38:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000135 | PCM-20251027-00000358 | TT-20251027-00416 | EM | Region_6 | BHAQ1M8435 | BHAQ2435 |  |  |  | SHAH KHALID | 10/27/2025 05:42:04 | 10/27/2025 05:42:04 | 10/27/2025 17:42:04 | Genset Running at BHAQ1M8435-P3 -G900-L800-SBTS @ Generator_DG | 10/27/2025 05:33:46 | Minor | 7103 | Genset Running | 10/27/2025 05:33:39 | P3 | 4G | Albaha | Generator_DG | LTE NSA | BHAQ1M8435 | FLM_EM | [5 empty] | Genset Running |  |  | API | 10/27/2025 05:42:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000136 | PCM-20251027-00000364 | TT-20251027-00395 | Telecom | Region_6 | RYAB0630 | RYAB0630 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Mamdouh Helal Helal | 10/27/2025 05:43:57 | 10/27/2025 08:46:05 | 10/27/2025 09:43:57 | 6(2G) 4(3G) 1(LTE) 5(5G) sites down under RYAB0641-P3-USF @ Sceco_STB | 10/27/2025 05:26:00 | Critical | 7706 | BTS O&M LINK FAILURE | 10/27/2025 05:25:54 | P1 | 2G | wadi dawasar | Sceco | 2G_3G_LTE_5G SA | TLT0324-P3 2G_LTE,RYAB0634-P3 2G_5G,RYAB0641-P3-USF 2G_5G,RYAB0639-P2 2G_3G_5G,TLT0667-P3 2G_3G_5G,TLT0389-P3 2G_3G_5G,RYAB0636-P3 3G | FLM_TE | RYAB0630 | Site HUB TRM FB RYAB0639-P2 RYAB0630 observing visibility down RYAB0635-P3 RYAB0630 observing visibility down TLT0389-P3 TLT9474 Suspecting power issue RYAB0637-P2-USF RYAB0630 observing visibility down RYAB0638-P3 RYAB0630 observing visibility down TLT0390-P2-USF RYAB0630 observing visibility down WDS0912-P3 TLT9474 Suspecting power issue TLT0667-P3 TLT9474 Suspecting power issue RYAB0630-P1-HUB-USF RYAB0630 observing visibility down RYAB0632-P1-HUB RYAB0630 observing visibility down RYAB0641-P3-USF RYAB0630 observing visibility down RYAB0634-P3 RYAB0630 observing visibility down RYAB0633-P3-USF RYAB0630 observing visibility down TLT0324-P3 TLT0324 Suspecting power issue | PCM-20251027-00000348 | Site HUB TRM FB RYAB0639-P2 RYAB0630 observing visibility down RYAB0635-P3 RYAB0630 observing visibility down TLT0389-P3 TLT9474 Suspecting power issue RYAB0637-P2-USF RYAB0630 observing visibility down RYAB0638-P3 RYAB0630 observing visibility down TLT0390-P2-USF RYAB0630 observing visibility down WDS0912-P3 TLT9474 Suspecting power issue TLT0667-P3 TLT9474 Suspecting power issue RYAB0630-P1-HUB-USF RYAB0630 observing visibility down RYAB0632-P1-HUB RYAB0630 observing visibility down RYAB0641-P3-USF RYAB0630 observing visibility down RYAB0634-P3 RYAB0630 observing visibility down RYAB0633-P3-USF RYAB0630 observing visibility down TLT0324-P3 TLT0324 Suspecting power issue | Site HUB TRM FB RYAB0639-P2 RYAB0630 observing visibility down RYAB0635-P3 RYAB0630 observing visibility down TLT0389-P3 TLT9474 Suspecting power issue RYAB0637-P2-USF RYAB0630 observing visibility down RYAB0638-P3 RYAB0630 observing visibility down TLT0390-P2-USF RYAB0630 observing visibility down WDS0912-P3 TLT9474 Suspecting power issue TLT0667-P3 TLT9474 Suspecting power issue RYAB0630-P1-HUB-USF RYAB0630 observing visibility down RYAB0632-P1-HUB RYAB0630 observing visibility down RYAB0641-P3-USF RYAB0630 observing visibility down RYAB0634-P3 RYAB0630 observing visibility down RYAB0633-P3-USF RYAB0630 observing visibility down TLT0324-P3 TLT0324 Suspecting power issue |  | sites down |  | API | 10/27/2025 05:43:57 | 10/27/2025 08:36:31 | 10/27/2025 08:45:56 |  |  | 10/27/2025 08:46:05 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000138 | PCM-20251027-00000367 | TT-20251027-00415 | Telecom | Region_5 | USMD0710 | USMD0710 |  |  |  | Amr Abdulla Ali Othman | 10/27/2025 05:45:00 | 10/27/2025 05:45:00 | 10/27/2025 11:45:00 | 1(5G) sites down under USMD0710-GSM-UMTS-P3-USF @ Sceco_STB | 10/27/2025 05:36:35 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 05:36:33 | P1 | 2G | makkah | Sceco_STB | 5G SA | USMD0710-GSM-UMTS-P3-USF | FLM_TE | USMD0710 | Results: DOWN SITE HUB USMD0710-GSM-UMTS-P3-USF USMD0710 Summary: Hub: USMD0710, Down Count: 1, Down Sites: USMD0710-GSM-UMTS-P3-USF Alarm Summary: USMD0710 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.162.36:8080] [URL:http://10.98.162.36:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 05:45:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000139 | PCM-20251027-00000369 | TT-20251027-00426 | Telecom | Region_2 | RIY2M7191 | RIY0191 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/27/2025 05:47:36 | 10/27/2025 06:58:29 | 10/27/2025 11:47:36 | Cell Unavailable at RIY2M7191-P1-SHOP-L900-L800 @ Sceco | 10/27/2025 05:43:33 | Major | 29240 | Cell Unavailable | 10/27/2025 05:43:08 | P1 | 4G | riyadh | Sceco | LTE SA | RIY2M7191 | FLM_TE | [8 empty] | API | 10/27/2025 05:47:36 | 10/27/2025 06:56:06 | 10/27/2025 06:58:07 |  |  | 10/27/2025 06:58:29 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000140 | PCM-20251027-00000370 | TT-20251027-00423 | Telecom | Region_4 | JED1MN2986 | JED2986 |  |  |  | BARKAT ALI MAIN HILAL | 10/27/2025 05:48:59 | 10/27/2025 05:48:59 | 10/27/2025 11:48:59 | 1(5G) sites down under JED2986-NR2.6-P3 @ Generator_SG | 10/27/2025 05:40:33 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 05:40:29 | P3 | 5G | jeddah | Generator_SG | 5G SA | JED2986-NR2.6-P3 | FLM_TE | JED2986 | Results: DOWN SITE HUB JED2986-NR2.6-P3 JED2986 Summary: Hub: JED2986, Down Count: 1, Down Sites: JED2986-NR2.6-P3 Alarm Summary: JED2986 No Active Alarm on HUB |  |  |  | No route to host [URL:http://10.97.52.228:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 05:48:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000141 | PCM-20251027-00000371 | TT-20251027-00427 | Reference_telecom | Region_1 | ARM0875 | ARM0875 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/27/2025 05:50:49 | 10/27/2025 05:50:49 | 10/27/2025 17:50:49 | RF Unit RX Channel RTWP/RSSI Too Low at ARM0875-P2_SRAN @ Generator_SG | 10/27/2025 04:05:52 | Minor | 26521 | RF Unit RX Channel RTWP/RSSI Too Low | 10/27/2025 02:50:24 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | ARM0875 | FLM_TE | [8 empty] | API | 10/27/2025 05:50:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000143 | PCM-20251027-00000376 | TT-20251027-00432 | Reference_telecom | Region_6 | ABH0281 | ABH0281 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/27/2025 05:58:34 | 10/27/2025 06:05:51 | 10/27/2025 17:58:34 | Degrade observed in ABH0281 _05 towards 10.221.248.33 @ Sceco | 10/26/2025 17:58:32 | Minor |  | Degrade | 10/26/2025 17:58:28 | P2 | 2G | abha | Sceco | TX NSA | ABH0281 | FLM_TE | [8 empty] | API | 10/27/2025 05:58:34 | 10/27/2025 06:05:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000144 | PCM-20251027-00000377 | TT-20251027-00430 | Reference_telecom | Region_1 | RAF0506 | RAF0506 |  |  |  | Almmoez Almmoez | 10/27/2025 05:58:47 | 10/27/2025 05:58:47 | 10/27/2025 17:58:47 | IP Clock Link Failure at RAF0506-P2-USF_SRAN @ Generator_SG | 10/27/2025 02:58:22 | Minor | 26263 | IP Clock Link Failure | 10/27/2025 02:56:02 | P2 | SRAN | rafha | Generator_SG | 2G NSA | RAF0506 | FLM_TE |  |  | PCM-20251027-00000374 | Dear IP RAN, site is GU standalone & IP clock is down with below data , please need your check: List IP Clock Link Configuration -------------------------------- Link No. = 0 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.64.158 VRF Index = 0 Server IPv4 = 10.161.136.69 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = ON Clock Server Description = NULL Link No. = 1 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.64.158 VRF Index = 0 Server IPv4 = 10.161.137.69 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = ON Clock Server Description = NULL (Number of results = 2) --- END | Dear IP RAN, site is GU standalone & IP clock is down with below data , please need your check: List IP Clock Link Configuration -------------------------------- Link No. = 0 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.64.158 VRF Index = 0 Server IPv4 = 10.161.136.69 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = ON Clock Server Description = NULL Link No. = 1 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.64.158 VRF Index = 0 Server IPv4 = 10.161.137.69 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = ON Clock Server Description = NULL (Number of results = 2) --- END |  |  |  | API | 10/27/2025 05:58:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000145 | PCM-20251027-00000380 | TT-20251027-00438 | Telecom | Region_1 | KBR0982 | KBR0982 |  |  |  | Imran Ali Yousaf | 10/27/2025 06:01:09 | 10/27/2025 06:01:09 | 10/27/2025 18:01:09 | RF Unit Maintenance Link Failure at KBR0982-P3_SRAN @ Sceco | 10/27/2025 00:51:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 00:49:18 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0982 | FLM_TE | [8 empty] | API | 10/27/2025 06:01:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000146 | PCM-20251027-00000385 | TT-20251027-00443 | Telecom | Region_1 | DAM0240 | DAM0240 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/27/2025 06:01:11 | 10/27/2025 07:38:41 | 10/27/2025 18:01:11 | RF Unit Maintenance Link Failure at DAM0240-P2_SRAN @ Sceco | 10/27/2025 00:51:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 00:49:18 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0240 | FLM_TE | [8 empty] | API | 10/27/2025 06:01:11 | 10/27/2025 07:38:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000147 | PCM-20251027-00000383 | TT-20251027-00441 | Telecom | Region_1 | JBL0143 | JBL0143 |  |  |  | Tahir Mahmood Hafiz Yar | 10/27/2025 06:01:11 | 10/27/2025 06:01:11 | 10/27/2025 18:01:11 | RF Unit Maintenance Link Failure at JBL0143-P2_SRAN @ Sceco | 10/27/2025 00:51:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 00:49:18 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0143 | FLM_TE | [8 empty] | API | 10/27/2025 06:01:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000148 | PCM-20251027-00000384 | TT-20251027-00442 | Telecom | Region_6 | SMT1M3193 | SMT0193 |  |  |  | Zeshan Ali Adnan | 10/27/2025 06:01:12 | 10/27/2025 06:01:12 | 10/27/2025 18:01:12 | BASE STATION NOTIFICATION (Fan failure) at SMT1M3193-P1-VIP @ Sceco | 10/27/2025 05:31:22 | Minor | 7652 | BASE STATION NOTIFICATION | 10/27/2025 05:31:01 | VIP | 3G | jizan | Sceco | 3G NSA | SMT1M3193 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/27/2025 06:01:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000149 | PCM-20251027-00000387 | TT-20251027-00445 | Telecom | Region_2 | BUR0066 | BUR0066 |  |  |  | Raise Ahmed Nisar Ahmed | 10/27/2025 06:01:13 | 10/27/2025 06:01:13 | 10/27/2025 18:01:13 | RF Unit Maintenance Link Failure at BUR0066-P2_SRAN @ Sceco | 10/27/2025 00:51:00 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 00:49:18 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0066 | FLM_TE | [8 empty] | API | 10/27/2025 06:01:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000150 | PCM-20251027-00000393 | TT-20251027-00451 | Reference_telecom | Region_4 | JDRS2225 | JDRS2225 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/27/2025 06:03:45 | 10/27/2025 06:03:45 | 10/27/2025 18:03:45 | LossOfSignal observed in JDRS2225_01 towards 10.3.228.151 @ Sceco | 10/26/2025 18:03:31 | Minor |  | LossOfSignal | 10/26/2025 18:03:27 | P3 | 2G | jeddah | Sceco | TX NSA | JDRS2225 | FLM_TE | [8 empty] | API | 10/27/2025 06:03:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000152 | PCM-20251027-00000394 | TT-20251027-00433 | EM | Region_6 | BCH2203 | BCH2203 |  |  |  | Fathy Mohamed | 10/27/2025 06:04:00 | 10/27/2025 06:04:00 | 10/27/2025 12:04:00 | 1(2G/LTE) sites down under BCH2203-P3/BCH2203-P3 @ Generator_SG | 10/27/2025 05:55:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 05:55:29 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BCH2203-P3 | FLM_EM | BCH2203 | Results: DOWN SITE HUB BCH2203-P3 BCH2203 Summary: Hub: BCH2203, Down Count: 1, Down Sites: BCH2203-P3 Alarm Summary: BCH2203 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 06:04:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000153 | PCM-20251027-00000402 | TT-20251027-00462 | Telecom | Region_2 | RIY0191 | RIY0191 | Equipment | BSS_HW_Stuck | Reset RFU | Ejaz Hussain Muhammad Sharif | 10/27/2025 06:13:34 | 10/27/2025 06:31:52 | 10/27/2025 12:13:34 | BBU CPRI Interface Error at RIY0191-P1-SHOP_SRAN @ Sceco | 10/27/2025 06:09:03 | Major | 26234 | BBU CPRI Interface Error | 10/27/2025 06:06:30 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0191 | FLM_TE | [8 empty] | API | 10/27/2025 06:13:34 | 10/27/2025 06:28:02 | 10/27/2025 06:31:22 | 10/27/2025 06:31:25 | 10/27/2025 06:31:28 | 10/27/2025 06:31:52 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000154 | PCM-20251027-00000403 | TT-20251027-00465 | Reference_telecom | Region_6 | KMS0303 | KMS0303 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/27/2025 06:15:37 | 10/27/2025 06:15:37 | 10/27/2025 18:15:37 | BASE STATION SERVICE PROBLEM (TX out of order) at KMS0303-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/27/2025 06:10:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 06:10:37 | P2 | 2G | abha | Sceco | LTE_Cell SA | KMS0303 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/27/2025 06:15:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000155 | PCM-20251027-00000404 | TT-20251027-00466 | Telecom | Region_4 | JED1M7543 | JED0543 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/27/2025 06:16:08 | 10/27/2025 06:16:08 | 10/27/2025 18:16:08 | CELL SERVICE PROBLEM (BTS configuration error (not enough HW for LCR)) at JED1M7543-P3-CA-L900-L800-SBTS @ Sceco | 10/27/2025 06:11:26 | Minor | 7114 | CELL SERVICE PROBLEM | 10/27/2025 06:11:14 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7543 | FLM_TE | [5 empty] | BTS configuration error (not enough HW for LCR) |  |  | API | 10/27/2025 06:16:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000156 | PCM-20251027-00000407 | TT-20251027-00459 | Telecom | Region_4 | JED1M7857 | JED0857 |  |  |  | BARKAT ALI MAIN HILAL | 10/27/2025 06:17:59 | 10/27/2025 06:17:59 | 10/27/2025 10:17:59 | 1(LTE) sites down under JED0857-P1-CA-L900-L800-SBTS @ Sceco | 10/27/2025 06:09:32 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 06:09:29 | P1 | 4G | jeddah | Sceco | LTE SA | JED0857-P1-CA-L900-L800-SBTS | FLM_TE | JED0857 | Results: DOWN SITE HUB JED0857-P1-CA-L900-L800-SBTS JED0857 Summary: Hub: JED0857, Down Count: 1, Down Sites: JED0857-P1-CA-L900-L800-SBTS Alarm Summary: JED0857 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.97.232.172:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 06:17:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000157 | PCM-20251027-00000409 | TT-20251027-00472 | Reference_telecom | Region_4 | JDRS0621 | JDRS0621 |  |  |  | Khizer Hayat | 10/27/2025 06:20:46 | 10/27/2025 06:20:46 | 10/27/2025 18:20:46 | LossOfSignal observed in JDRS0621_02 towards 10.3.228.149 @ Sceco | 10/26/2025 18:22:30 | Minor |  | LossOfSignal | 10/26/2025 18:20:27 | P2 | 2G | jeddah | Sceco | TX NSA | JDRS0621 | FLM_TE | [8 empty] | API | 10/27/2025 06:20:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000158 | PCM-20251027-00000410 | TT-20251027-00463 | Telecom | Region_2 | SRIY0230 | SRIY0230 |  |  |  | Majid Khan Arsalan Khan | 10/27/2025 06:21:29 | 10/27/2025 06:21:29 | 10/27/2025 10:21:29 | 2(3G) sites down under SRIY0230-P3,SRIY0231-P1-DIA/RY1RNCH05 @ Sceco | 10/27/2025 06:10:44 | Critical | 22214 | NodeB Unavailable | 10/27/2025 06:10:38 | P3 | SRAN | riyadh | Sceco | 3G SA | SRIY0231-P1-DIA 3G,SRIY0230-P3 3G | FLM_EM | SRIY0230 | Dear Team, Hub: SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251027-00000408 | Dear Team, Hub: SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/27/2025 06:21:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251027000160 | PCM-20251027-00000413 | TT-20251027-00473 | Telecom | Region_2 | RYAB2M2748 | RYAB2748 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Hakim Ullah Raif Ullah Jan | 10/27/2025 06:27:08 | 10/27/2025 06:38:25 | 10/27/2025 12:27:08 | GSM Local Cell Unusable at RYAB2M2748-P2 @ Sceco | 10/27/2025 06:26:32 | Major | 28016 | GSM Local Cell Unusable | 10/27/2025 06:24:56 | P2 | 2G | al kharj | Sceco | 2G SA | RYAB2M2748 | FLM_TE | [8 empty] | API | 10/27/2025 06:27:08 | 10/27/2025 06:37:35 | 10/27/2025 06:37:42 | 10/27/2025 06:37:44 | 10/27/2025 06:37:47 | 10/27/2025 06:38:25 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000161 | PCM-20251027-00000414 | TT-20251027-00421 | Reference_telecom | Region_6 | QEH0142 | QEH0142 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/27/2025 06:31:56 | 10/27/2025 06:31:56 | 10/27/2025 12:31:56 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at QEH0142-P2 @ Sceco | 10/27/2025 05:39:07 | Major | 7607 | TRX OPERATION DEGRADED | 10/27/2025 05:39:00 | P2 | 2G | derb | Sceco | 2G_TRX NSA | QEH0142 | FLM_TE |  |  | PCM-20251027-00000363 | sw fallback by system need to change SMOD then perform upgrade | sw fallback by system need to change SMOD then perform upgrade |  |  |  | API | 10/27/2025 06:31:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000162 | PCM-20251027-00000417 | TT-20251027-00449 | Reference_telecom | Region_5 | BIK0788 | BIK0788 |  |  |  | Hazem Ali Moustafa Ali | 10/27/2025 06:34:26 | 10/27/2025 06:34:26 | 10/27/2025 12:34:26 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at BIK0788-P3 @ Generator_SG | 10/27/2025 05:58:19 | Major | 7607 | TRX OPERATION DEGRADED | 10/27/2025 05:58:15 | P3 | 2G | makkah | Generator_SG | 2G_TRX NSA | BIK0788 | FLM_TE |  |  | PCM-20251027-00000391 | Please check door open at site | Please check door open at site |  |  |  | API | 10/27/2025 06:34:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000163 | PCM-20251027-00000419 | TT-20251027-00317 | Reference_telecom | Region_4 | JED1M7223 | JED0223 |  |  |  | Nazeer Mohammed | 10/27/2025 06:35:43 | 10/27/2025 06:35:43 | 10/27/2025 12:35:43 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M7223-P1-HUB-CA-L900-L800-SBTS @ Sceco_STB | 10/27/2025 04:24:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 04:24:17 | P1 | 4G | jeddah | Sceco_STB | 5G_Cell SA | JED1M7223 | FLM_TE |  |  | PCM-20251027-00000290 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/27/2025 06:35:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000167 | PCM-20251027-00000424 | TT-20251027-00490 | Reference_telecom | Region_4 | JED0146 | JED0146 |  |  |  | Mohammed Ramadan A Abu Abid | 10/27/2025 06:40:56 | 10/27/2025 08:36:51 | 10/27/2025 18:40:56 | LagPortDown observed in JED0146_3 towards 10.1.227.218 @ Sceco | 10/26/2025 18:42:49 | Minor |  | LagPortDown | 10/26/2025 18:40:36 | P2 | 2G | jeddah | Sceco | TX NSA | JED0146 | FLM_TE | [8 empty] | API | 10/27/2025 06:40:56 | 10/27/2025 08:36:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251027000168 | PCM-20251027-00000426 | TT-20251027-00492 | EM | [7 empty] | 10/27/2025 06:41:26 | 10/27/2025 06:41:26 | 10/27/2025 18:41:26 | NETECO: Genset Fault at HNK2051 @ Generator_SG | 10/27/2025 06:34:55 | Minor | 40564 | Genset Fault | 10/27/2025 06:34:55 | P3 | SRAN |  | Generator_SG | 2G NSA | HNK2051 | FLM_EM | [8 empty] | API | 10/27/2025 06:41:26 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000170 | PCM-20251027-00000429 | TT-20251027-00494 | Telecom | Region_2 | RYD-E8K-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/27/2025 06:41:58 | 10/27/2025 06:41:58 | 10/27/2025 18:41:58 | Chassis Fail at RYD-E8K-01 @ Sceco_STB | 10/27/2025 06:41:35 | Minor | 101-2505202 | Chassis Fail | 10/27/2025 06:41:31 | P1 | IPBB | riyadh | Sceco_STB | IPRAN NSA | RYD-E8K-01 | FLM_TE | [8 empty] | API | 10/27/2025 06:41:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000171 | PCM-20251027-00000438 | TT-20251027-00507 | EM | Region_6 | TLT0386 | TLT0386 |  |  |  | Faisal Javed Javed Akhtar | 10/27/2025 06:48:10 | 10/27/2025 08:17:17 | 10/27/2025 18:48:10 | RECTIFIER MAINS POWER FAILURE at TLT0386-GSM-P3-HUB @ Sceco_STB | 10/27/2025 06:40:08 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/27/2025 06:40:03 | P1 | 2G | tathleeth | Sceco_STB | 2G NSA | TLT0386 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/27/2025 06:48:10 | 10/27/2025 08:17:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000173 | PCM-20251027-00000447 | TT-20251027-00512 | Reference_EM | Region_3 | HAL0946 | HAL0946 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/27/2025 06:51:16 | 10/27/2025 06:55:06 | 10/27/2025 18:51:16 | Mains Failure at HAL0946-P2_SRAN @ Sceco | 10/27/2025 06:41:25 | Minor | 65109 | Mains Failure | 10/27/2025 06:41:22 | P2 | SRAN | hail | Sceco | 2G NSA | HAL0946 | FLM_EM | [8 empty] | API | 10/27/2025 06:51:16 | 10/27/2025 06:55:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000174 | PCM-20251027-00000448 | TT-20251027-00506 | Telecom | Region_4 | JED0235 | JED0235 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/27/2025 06:51:59 | 10/27/2025 06:51:59 | 10/27/2025 12:51:59 | 1(5G) sites down under JED0235-G9-L8-L18-L21-NNR6-NR2.6-SBTS @ Generator_SG | 10/27/2025 06:43:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 06:43:54 | P2 | 2G | jeddah | Generator_SG | 5G SA | JED0235-G9-L8-L18-L21-NNR6-NR2.6-SBTS | FLM_TE | JED0235 | Results: DOWN SITE HUB JED0235-G9-L8-L18-L21-NNR6-NR2.6-SBTS JED0235 Summary: Hub: JED0235, Down Count: 1, Down Sites: JED0235-G9-L8-L18-L21-NNR6-NR2.6-SBTS Alarm Summary: JED0235 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.120.100:8080] [URL:http://10.97.120.100:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 06:51:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251027000175 | PCM-20251027-00000449 | TT-20251027-00513 | Reference_EM | Region_3 | AHT2160 | AHT2160 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/27/2025 06:52:49 | 10/27/2025 08:14:02 | 10/27/2025 18:52:49 | Genset not in auto mode at AHT2160-P3_SRAN @ Sceco | 10/27/2025 06:42:25 | Minor | 65113 | Genset not in auto mode | 10/27/2025 06:42:21 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2160 | FLM_EM | [8 empty] | API | 10/27/2025 06:52:49 | 10/27/2025 07:11:14 | 10/27/2025 07:11:42 | 10/27/2025 07:12:08 | 10/27/2025 08:14:02 | [6 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000176 | PCM-20251027-00000450 | TT-20251027-00486 | EM | Region_3 | YNB2046 | YNB2046 |  |  |  | Muhammad Sajjad R3 | 10/27/2025 06:53:00 | 10/27/2025 06:53:00 | 10/27/2025 12:53:00 | 1(2G/3G/LTE) sites down under YNB2046-P2/YB1MBSCH01 @ Sceco | 10/27/2025 06:35:46 | Major | 21825 | CSL Fault | 10/27/2025 06:35:43 | P2 | SRAN | yanbu | Sceco | 2G_3G_LTE SA | YNB2046-P2 | FLM_TE | YNB2046 | Kindly visit the site and check issue locally | PCM-20251027-00000446 | Kindly visit the site and check issue locally | Kindly visit the site and check issue locally |  | sites down |  | API | 10/27/2025 06:53:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000177 | PCM-20251027-00000451 | TT-20251027-00515 | Telecom | Region_4 | RYMK0528-LL-CSG | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/27/2025 06:53:20 | 10/27/2025 07:58:31 | 10/27/2025 10:53:20 | The Device is offline at RYMK0528-LL-CSG @ Generator_SG | 10/27/2025 06:53:04 | Critical | 101-7 | The Device is offline | 10/27/2025 06:53:01 | P1 | IPRAN | taif | Generator_SG | IPRAN SA | RYMK0528-LL-CSG | FLM_TE | [8 empty] | API | 10/27/2025 06:53:20 | 10/27/2025 07:58:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000178 | PCM-20251027-00000455 | TT-20251027-00318 | Telecom | Region_1 | UQL-0282-NE40E-X2-PE01 | UQL0282 |  |  |  | Almmoez Almmoez | 10/27/2025 06:55:34 | 10/27/2025 06:55:34 | 10/27/2025 10:55:34 | The Device is offline at UQL-0282-NE40E-X2-PE01 @ Sceco | 10/27/2025 04:29:06 | Critical | 101-7 | The Device is offline | 10/27/2025 04:29:05 | P2 | IPRAN | rafha | Sceco | IPRAN SA | UQL-0282-NE40E-X2-PE01 | FLM_TE |  |  | PCM-20251027-00000310 | Please check | Please check |  |  |  | API | 10/27/2025 06:55:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000179 | PCM-20251027-00000456 | TT-20251027-00520 | EM | Region_6 | BHAQ1M8060 | BHAQ2060 |  |  |  | Sohail Nasir Mir Afzal | 10/27/2025 06:56:25 | 10/27/2025 06:56:25 | 10/27/2025 18:56:25 | SHELTER DOOR OPEN;Default System Time at BHAQ1M8060-G9-L8-SBTS-P3 @ Sceco | 10/27/2025 06:55:55 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/27/2025 03:01:29 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAQ1M8060 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/27/2025 06:56:25 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000180 | PCM-20251027-00000460 | TT-20251027-00519 | EM | Region_6 | BHAQ1M4060 | BHAQ2060 |  |  |  | Sohail Nasir Mir Afzal | 10/27/2025 07:01:00 | 10/27/2025 07:01:00 | 10/27/2025 13:01:00 | 1(3G/LTE) sites down under BHAQ2060-P3/BHAQ1M4060-P3 @ Sceco | 10/27/2025 06:53:21 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/27/2025 06:52:43 | P3 | 3G | Albaha | Sceco | 3G_LTE SA | BHAQ2060-P3 | FLM_EM | BHAQ2060 | Results: DOWN SITE HUB BHAQ2060-P3 BHAQ2060 Summary: Hub: BHAQ2060, Down Count: 1, Down Sites: BHAQ2060-P3 Alarm Summary: BHAQ2060 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 07:01:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000181 | PCM-20251027-00000461 | TT-20251027-00384 | EM | Region_1 | SAR0076 | SAR0076 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/27/2025 07:01:52 | 10/27/2025 07:01:52 | 10/27/2025 11:01:52 | 1(2G/LTE) sites down under SAR0073-P1-HUB-USF/SK1BSCH01 @ Generator_DG | 10/27/2025 05:18:16 | Critical | 21825 | CSL Fault | 10/27/2025 05:18:15 | P1 | SRAN | quriyat | Generator_DG | 2G_LTE SA | SAR0073-P1-HUB-USF | FLM_TE | SAR0076 | ALREADY FB SHARED AND YOU KEEP ESCALATING PCM | PCM-20251027-00000459 | ALREADY FB SHARED AND YOU KEEP ESCALATING PCM | ALREADY FB SHARED AND YOU KEEP ESCALATING PCM |  | sites down |  | API | 10/27/2025 07:01:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000183 | PCM-20251027-00000464 | TT-20251027-00522 | EM | Region_6 | BHAQ1M8060 | BHAQ2060 |  |  |  | Sohail Nasir Mir Afzal | 10/27/2025 07:05:12 | 10/27/2025 07:05:12 | 10/27/2025 19:05:12 | AIRCON 1 FAILURE at BHAQ1M8060-G9-L8-SBTS-P3 @ Sceco | 10/27/2025 06:56:55 | Minor | 7103 | AIRCON 1 FAILURE | 10/27/2025 06:56:49 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAQ1M8060 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/27/2025 07:05:12 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000185 | PCM-20251027-00000468 | TT-20251027-00525 | Telecom | Region_4 | JED6008 | JED6008 |  |  |  | Mohamed Farag Abdelbary | 10/27/2025 07:09:47 | 10/27/2025 07:09:47 | 10/27/2025 19:09:47 | Cell Capability Degraded at JED6008-DCU-P3 @ Sceco | 10/26/2025 19:14:41 | Minor | 28751 | Cell Capability Degraded | 10/26/2025 19:13:08 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/27/2025 07:09:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000186 | PCM-20251027-00000469 | TT-20251027-00526 | Telecom | Region_4 | JED6008 | JED6008 |  |  |  | Mohamed Farag Abdelbary | 10/27/2025 07:09:58 | 10/27/2025 07:09:58 | 10/27/2025 19:09:58 | RFC RF Port Input Power Out of Range at JED6008-DCU-P3 @ Sceco | 10/26/2025 19:13:48 | Minor | 28754 | RFC RF Port Input Power Out of Range | 10/26/2025 19:13:14 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/27/2025 07:09:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000187 | PCM-20251027-00000470 | TT-20251027-00527 | Telecom | Region_1 | DAM0240 | DAM0240 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/27/2025 07:11:17 | 10/27/2025 07:38:42 | 10/27/2025 13:11:17 | BBU CPRI Optical Module or Electrical Port Not Ready at DAM0240-P2_SRAN @ Sceco | 10/27/2025 02:57:50 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 10/27/2025 02:56:18 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0240 | FLM_TE | [8 empty] | API | 10/27/2025 07:11:17 | 10/27/2025 07:38:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000188 | PCM-20251027-00000472 | TT-20251027-00528 | Telecom | Region_1 | JBL0143 | JBL0143 |  |  |  | Tahir Mahmood Hafiz Yar | 10/27/2025 07:11:36 | 10/27/2025 07:11:36 | 10/27/2025 13:11:36 | BBU CPRI Optical Module or Electrical Port Not Ready at JBL0143-P2_SRAN @ Sceco | 10/27/2025 02:44:41 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 10/27/2025 02:43:09 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0143 | FLM_TE | [8 empty] | API | 10/27/2025 07:11:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000189 | PCM-20251027-00000473 | TT-20251027-00529 | Telecom | Region_1 | KBR0982 | KBR0982 |  |  |  | Imran Ali Yousaf | 10/27/2025 07:11:55 | 10/27/2025 07:11:55 | 10/27/2025 13:11:55 | BBU CPRI Optical Module or Electrical Port Not Ready at KBR0982-P3_SRAN @ Sceco | 10/27/2025 02:38:03 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 10/27/2025 02:36:31 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0982 | FLM_TE | [8 empty] | API | 10/27/2025 07:11:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000190 | PCM-20251027-00000474 | TT-20251027-00530 | Telecom | Region_2 | BUR0066 | BUR0066 |  |  |  | Raise Ahmed Nisar Ahmed | 10/27/2025 07:12:20 | 10/27/2025 07:12:20 | 10/27/2025 13:12:20 | BBU CPRI Optical Module or Electrical Port Not Ready at BUR0066-P2_SRAN @ Sceco | 10/27/2025 02:31:54 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 10/27/2025 02:30:23 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0066 | FLM_TE | [8 empty] | API | 10/27/2025 07:12:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000191 | PCM-20251027-00000476 | TT-20251027-00532 | Telecom | Region_2 | RAS0764 | RAS0764 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/27/2025 07:12:52 | 10/27/2025 07:12:52 | 10/27/2025 19:12:52 | GNSS Antenna Fault at RAS0764-P3_SRAN @ Sceco | 10/27/2025 02:28:41 | Minor | 26125 | GNSS Antenna Fault | 10/27/2025 02:27:08 | P3 | SRAN | al rass | Sceco | 2G NSA | RAS0764 | FLM_TE | [8 empty] | API | 10/27/2025 07:12:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000192 | PCM-20251027-00000479 | TT-20251027-00536 | Telecom | Region_4 | JED1M8066 | JED2066 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/27/2025 07:15:03 | 10/27/2025 07:15:03 | 10/27/2025 19:15:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8066-CA-L800-SBTS-P3 @ Generator_SG | 10/27/2025 07:14:05 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 07:13:56 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 07:15:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000193 | PCM-20251027-00000481 | TT-20251027-00543 | Reference_telecom | Region_6 | ARF0066 | ARF0066 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/27/2025 07:16:04 | 10/27/2025 07:16:04 | 10/27/2025 19:16:04 | ReplaceableUnitProblem observed in ARF0066_05 towards 10.21.79.113 @ Sceco_STB | 10/26/2025 19:15:56 | Minor |  | ReplaceableUnitProblem | 10/26/2025 19:15:32 | P1 | 2G | al harja | Sceco_STB | TX NSA | ARF0066 | FLM_TE | [8 empty] | API | 10/27/2025 07:16:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000194 | PCM-20251027-00000483 | TT-20251027-00533 | Telecom | Region_4 | JED0024 | JED0024 |  |  |  | BARKAT ALI MAIN HILAL | 10/27/2025 07:17:47 | 10/27/2025 07:17:47 | 10/27/2025 13:17:47 | BASE STATION HARDWARE PROBLEM (RX Power too low) at JED0024-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/27/2025 07:06:20 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/27/2025 07:06:10 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0024 | FLM_TE |  |  | PCM-20251027-00000477 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/27/2025 07:17:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000198 | PCM-20251027-00000490 | TT-20251027-00548 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/27/2025 07:22:47 | 10/27/2025 08:57:19 | 10/27/2025 11:22:47 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/27/2025 07:22:00 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 07:21:51 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 07:22:47 | 10/27/2025 08:57:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000201 | PCM-20251027-00000494 | TT-20251027-00547 | Telecom | Region_4 | RYMK0665 | RYMK0665 |  |  |  | Ehab Ali Mohamed Abdou | 10/27/2025 07:27:18 | 10/27/2025 08:12:44 | 10/27/2025 19:27:18 | WRYMK0001 Complete Down | 10/27/2025 07:05:56 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/27/2025 07:05:56 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Dear Team, Hub: RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251027-00000487 | Dear Team, Hub: RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/27/2025 07:27:18 | 10/27/2025 08:12:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000203 | PCM-20251027-00000501 | TT-20251027-00554 | Telecom | Region_6 | ABH1U6700 | ABH6000 |  |  |  | Amir Sohail | 10/27/2025 07:32:31 | 10/27/2025 07:32:31 | 10/27/2025 19:32:31 | BASE STATION ANTENNA LINE PROBLEM at ABH1U6700-G9-L18-SBTS-P3 @ Sceco | 10/27/2025 07:22:48 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/27/2025 07:22:41 | P3 | 4G | abha | Sceco | LTE NSA | ABH1U6700 | FLM_TE |  |  | PCM-20251027-00000499 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/27/2025 07:32:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000204 | PCM-20251027-00000506 | TT-20251027-00555 | EM | Region_6 | BHAB2126 | BHAB2126 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/27/2025 07:35:29 | 10/27/2025 07:35:29 | 10/27/2025 13:35:29 | 1(2G/LTE) sites down under BHAB2126-P3/BHAB2126-P3 @ Sceco | 10/27/2025 07:27:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 07:27:10 | P3 | 2G | Baha | Sceco | 2G_LTE SA | BHAB2126-P3 | FLM_EM | BHAB2126 | Results: DOWN SITE HUB BHAB2126-P3 BHAB2126 Summary: Hub: BHAB2126, Down Count: 1, Down Sites: BHAB2126-P3 Alarm Summary: BHAB2126 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 07:35:29 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000205 | PCM-20251027-00000507 | TT-20251027-00553 | EM | Region_4 | JED0543 | JED0543 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/27/2025 07:37:01 | 10/27/2025 07:37:01 | 10/27/2025 13:37:01 | 1(2G/LTE) sites down under JED0543-P2/JED0543-P2 @ Sceco | 10/27/2025 07:24:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 07:24:25 | P2 | 2G | jeddah | Sceco | 2G_LTE SA | JED0543-P2 | FLM_TE | JED0543 | Results: DOWN SITE HUB JED0543-P2 JED0543 Summary: Hub: JED0543, Down Count: 1, Down Sites: JED0543-P2 Alarm Summary: JED0543 No Active Alarm on HUB | PCM-20251027-00000500 | No Power Issue | No Power Issue |  | sites down |  | API | 10/27/2025 07:37:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000206 | PCM-20251027-00000508 | TT-20251027-00565 | EM | Region_6 | BHAB1M8126 | BHAB2126 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/27/2025 07:39:18 | 10/27/2025 07:39:18 | 10/27/2025 19:39:18 | SMOKE ALARM at BHAB1M8126-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/27/2025 07:32:40 | Minor | 7103 | SMOKE ALARM | 10/27/2025 07:31:02 | P3 | 4G | Baha | Sceco | LTE NSA | BHAB1M8126 | FLM_EM | [5 empty] | SMOKE ALARM |  |  | API | 10/27/2025 07:39:18 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000207 | PCM-20251027-00000510 | TT-20251027-00467 | Telecom | Region_4 | JED0235 | JED0235 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/27/2025 07:40:19 | 10/27/2025 07:40:19 | 10/27/2025 13:40:19 | CELL SERVICE PROBLEM (Cell disabled due to unknown problem; logs collected) at JED0235-G9-L8-L18-L21-NNR6-NR2.6-SBTS @ Generator_SG | 10/27/2025 06:11:36 | Major | 7114 | CELL SERVICE PROBLEM | 10/27/2025 06:11:31 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0235 | FLM_TE |  |  | PCM-20251027-00000405 | Please check FXEB are down | Please check FXEB are down |  |  |  | API | 10/27/2025 07:40:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000209 | PCM-20251027-00000512 | TT-20251027-00566 | Reference_EM | Region_2 | RIYA6186 | RIYA6186 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/27/2025 07:40:51 | 10/27/2025 07:40:51 | 10/27/2025 13:40:51 | Door opening alarm at RIYA6186-P1-VIP_SRAN @ Sceco | 10/27/2025 07:40:30 | Major | 65101 | Door opening alarm | 10/27/2025 07:40:26 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYA6186 | FLM_EM | [8 empty] | API | 10/27/2025 07:40:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000210 | PCM-20251027-00000618 | TT-20251027-00678 | EM | Region_6 | TLT0386 | TLT0386 |  |  |  | Faisal Javed Javed Akhtar | 10/27/2025 07:45:29 | 10/27/2025 08:17:18 | 10/27/2025 19:45:29 | SHELTER DOOR OPEN at TLT0386-GSM-P3-HUB @ Sceco_STB | 10/27/2025 07:44:57 | Minor | 7103 | SHELTER DOOR OPEN | 10/27/2025 07:44:46 | P1 | 2G | tathleeth | Sceco_STB | 2G NSA | TLT0386 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/27/2025 07:45:29 | 10/27/2025 08:17:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000212 | PCM-20251027-00000621 | TT-20251027-00675 | Telecom | Region_4 | MDAS1M3775 | MDAS0775 |  |  |  | Amr Abdulla Ali Othman | 10/27/2025 07:47:29 | 10/27/2025 07:47:29 | 10/27/2025 13:47:29 | 1(3G) sites down under MDAS0775-P2-USF/MDAS1M3775-P2-USF @ Sceco | 10/27/2025 07:39:47 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/27/2025 07:39:06 | P2 | 3G | taif | Sceco | 3G SA | MDAS0775-P2-USF | FLM_TE | MDAS0775 | Results: DOWN SITE HUB MDAS0775-P2-USF MDAS0775 Summary: Hub: MDAS0775, Down Count: 1, Down Sites: MDAS0775-P2-USF Alarm Summary: MDAS0775 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 07:47:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000213 | PCM-20251027-00000624 | TT-20251027-00677 | Telecom | Region_3 | YNB2M3291 | YNB0291 |  |  |  | Muhammad Sajjad R3 | 10/27/2025 07:48:59 | 10/27/2025 07:48:59 | 10/27/2025 13:48:59 | 1(3G) sites down under YNB0291-P2/YB1MBSCH01 @ Generator_SG | 10/27/2025 07:40:38 | Major | 22214 | NodeB Unavailable | 10/27/2025 07:40:35 | P2 | 3G | yanbu | Generator_SG | 3G SA | YNB0291-P2 | FLM_TE | YNB0291 | Results: DOWN SITE HUB YNB0291-P2 YNB0291 Summary: Hub: YNB0291, Down Count: 1, Down Sites: YNB0291-P2 Alarm Summary: YNB0291 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 07:48:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000215 | PCM-20251027-00000629 | TT-20251027-00683 | Telecom | Region_1 | HFR6002 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/27/2025 07:50:39 | 10/27/2025 08:08:05 | 10/27/2025 13:50:39 | BBU CPRI Interface Error at HFR6002-P3_SRAN @ Sceco | 10/27/2025 07:46:21 | Major | 26234 | BBU CPRI Interface Error | 10/27/2025 07:43:38 | P3 | SRAN | hafr | Sceco | 2G NSA | HFR6002 | FLM_TE | [8 empty] | API | 10/27/2025 07:50:39 | 10/27/2025 08:08:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000216 | PCM-20251027-00000630 | TT-20251027-00651 | EM | Region_1 | JBL0913 | JBL0913 |  |  |  | Hamid Bilal Bashir Ahmed | 10/27/2025 07:50:44 | 10/27/2025 07:50:44 | 10/27/2025 11:50:44 | 1(2G/3G/LTE) sites down under JBAP0137-P1/R1_JB_HWBSC01 @ Sceco | 10/27/2025 07:40:08 | Critical | 21825 | CSL Fault | 10/27/2025 07:40:06 | P2 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBAP0137-P1 | FLM_EM | JBL0913 | Dear Team, Hub: JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251027-00000625 | Dear Team, Hub: JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub: JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/27/2025 07:50:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000218 | PCM-20251027-00000633 | TT-20251027-00684 | Telecom | Region_6 | TFBH0887-LL-CSG-01 | TFBH0887 |  |  |  | SHAH KHALID | 10/27/2025 07:51:55 | 10/27/2025 07:51:55 | 10/27/2025 19:51:55 | Optical Invalid at TFBH0887-LL-CSG-01 ¦¦ ref TT-20251002-00890 @ Sceco_STB | 10/27/2025 07:32:16 | Minor | 101-2505224 | Optical Invalid | 10/27/2025 07:31:57 | P3 | IPRAN | makhwa | Sceco_STB | IPRAN NSA | TFBH0887-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/27/2025 07:51:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251027000220 | PCM-20251027-00000636 | TT-20251027-00676 | Telecom | Region_5 | MAK0120 | MAK0120 |  |  |  | Jawad Ali Bakht Sher Khan | 10/27/2025 07:53:31 | 10/27/2025 08:23:25 | 10/27/2025 11:53:31 | 2(2G) 1(LTE) 1(5G) sites down under MAK6093-P1-VIP-HAJJ-HRM,MAK0378-P1-HRM/MAK0378-P1-HRM @ Sceco | 10/27/2025 07:39:13 | Critical | 7706 | BTS O&M LINK FAILURE | 10/27/2025 07:39:10 | VIP | 2G | makkah | Sceco | 2G SA | MAK0378-P1-HRM 2G,MAK6093-P1-VIP-HAJJ-HRM 2G | FLM_TE | MAK0120 | Hub: MAK0120 We are observing LOS TO AIRSCALE kindly send team to check locally | PCM-20251027-00000622 | Hub: MAK0120 We are observing LOS TO AIRSCALE kindly send team to check locally | Hub: MAK0120 We are observing LOS TO AIRSCALE kindly send team to check locally |  | sites down |  | API | 10/27/2025 07:53:31 | 10/27/2025 08:21:08 | 10/27/2025 08:23:16 | 10/27/2025 08:23:25 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000221 | PCM-20251027-00000637 | TT-20251027-00686 | Telecom | Region_3 | YBDB0291 | YBDB0291 |  |  |  | Hossam Ali Ahmed Ali | 10/27/2025 07:54:17 | 10/27/2025 07:54:17 | 10/27/2025 13:54:17 | COMMUN_FAIL at YBDB0291_OCS @ Generator_DG | 10/27/2025 07:50:30 | Major | 1-199 | COMMUN_FAIL | 10/27/2025 07:50:19 | P1 | DWDM | yanbu | Generator_DG | DWDM NSA | YBDB0291 | FLM_TE | [5 empty] | 2-LOCAL-1(1-C)-74-TMF2AUX-OTHER |  |  | API | 10/27/2025 07:54:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000222 | PCM-20251027-00000640 | TT-20251027-00679 | Telecom | Region_4 | HHR0481 | HHR0481 |  |  |  | Nazeer Mohammed | 10/27/2025 07:57:18 | 10/27/2025 07:57:18 | 10/27/2025 13:57:18 | 1(2G) 1(5G) sites down under JED0294-GSM-P3,HHR0481-P2/HHR0481-P2 @ Generator_SG | 10/27/2025 07:44:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 07:44:46 | P2 | 2G | jeddah | Generator_SG | 2G_5G SA | JED0294-GSM-P3 5G,HHR0481-P2 2G | FLM_TE | HHR0481 | Scattered sites:HHR0481 We are observing LOS TO AIRSCALE kindly send team to check locally JED0294 observing no alarm flapped | PCM-20251027-00000632 | Scattered sites:HHR0481 We are observing LOS TO AIRSCALE kindly send team to check locally JED0294 observing no alarm flapped | Scattered sites:HHR0481 We are observing LOS TO AIRSCALE kindly send team to check locally JED0294 observing no alarm flapped |  | sites down |  | API | 10/27/2025 07:57:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000223 | PCM-20251027-00000642 | TT-20251027-00687 | Telecom | Region_4 | JED2126 | JED2126 |  |  |  | Mohammed Ramadan A Abu Abid | 10/27/2025 07:59:29 | 10/27/2025 08:36:52 | 10/27/2025 13:59:29 | 1(5G) sites down under JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/27/2025 07:51:17 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 07:51:14 | P3 | 2G | jeddah | Sceco | 5G SA | JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 | FLM_TE | JED2126 | Results: DOWN SITE HUB JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 JED2126 Summary: Hub: JED2126, Down Count: 1, Down Sites: JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 Alarm Summary: JED2126 No Active Alarm on HUB |  |  |  | Connection reset [URL:http://10.98.0.204:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 07:59:29 | 10/27/2025 08:36:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000224 | PCM-20251027-00000643 | TT-20251027-00688 | Telecom | Region_3 | YBDB2M3282 | YBDB0282 |  |  |  | Muhammad Sajjad R3 | 10/27/2025 07:59:59 | 10/27/2025 07:59:59 | 10/27/2025 11:59:59 | 1(3G) sites down under YBDB0282-P1-HUB/YB1MBSCH01 @ Generator_DG | 10/27/2025 07:51:43 | Critical | 22214 | NodeB Unavailable | 10/27/2025 07:51:40 | P1 | 3G | yanbu | Generator_DG | 3G SA | YBDB0282-P1-HUB | FLM_TE | YBDB0282 | Results: DOWN SITE HUB YBDB0282-P1-HUB YBDB0282 Summary: Hub: YBDB0282, Down Count: 1, Down Sites: YBDB0282-P1-HUB Alarm Summary: YBDB0282 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/27/2025 07:59:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251027000225 | PCM-20251027-00000649 | TT-20251027-00694 | EM | [7 empty] | 10/27/2025 08:06:00 | 10/27/2025 08:06:00 | 10/27/2025 14:06:00 | 1(2G/LTE) sites down under AHT2157-P3-CAP/R3_HL_HWBSC01 @ Sceco | 10/27/2025 07:57:30 | Major | 21825 | CSL Fault | 10/27/2025 07:57:28 | P3 | 2G |  | Sceco | 2G_LTE SA | AHT2157-P3-CAP | FLM_EM | AHT2157 | Results: DOWN SITE HUB AHT2157-P3-CAP AHT2157 Summary: Hub: AHT2157, Down Count: 1, Down Sites: AHT2157-P3-CAP Alarm Summary: AHT2157 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 08:06:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000226 | PCM-20251027-00000653 | TT-20251027-00705 | Telecom | Region_4 | JED2126 | JED2126 |  |  |  | Mohammed Ramadan A Abu Abid | 10/27/2025 08:07:43 | 10/27/2025 08:36:53 | 10/27/2025 20:07:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2126-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/27/2025 08:06:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 08:06:40 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2126 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 08:07:43 | 10/27/2025 08:36:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000227 | PCM-20251027-00000656 | TT-20251027-00700 | Telecom | Region_4 | DGB1M8169 | DGB2169 |  |  |  | Riasat Ali Allah Baksh | 10/27/2025 08:10:32 | 10/27/2025 08:10:32 | 10/27/2025 14:10:32 | 1(LTE) sites down under DGB2169-USF-P3 @ Sceco | 10/27/2025 08:02:27 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/27/2025 08:02:24 | P3 | 4G | alaith | Sceco | LTE SA | DGB2169-USF-P3 | FLM_TE | DGB2169 | Results: DOWN SITE HUB DGB2169-USF-P3 DGB2169 Summary: Hub: DGB2169, Down Count: 1, Down Sites: DGB2169-USF-P3 Alarm Summary: DGB2169 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.15.92:8080] [URL:http://10.88.15.92:8080/NE3S/1.0/] | sites down |  | API | 10/27/2025 08:10:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000231 | PCM-20251027-00000661 | TT-20251027-00546 | Telecom | Region_4 | JED0048 | JED0048 |  |  |  | Mohammed Ramadan A Abu Abid | 10/27/2025 08:12:04 | 10/27/2025 08:36:53 | 10/27/2025 20:12:04 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED0048-G9-L8-L18-L21-NNR6-NR2.6-SBTS-BTS-P2 @ Sceco | 10/27/2025 07:13:22 | Minor | 7114 | CELL SERVICE PROBLEM | 10/27/2025 07:13:13 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0048 | FLM_TE |  |  | PCM-20251027-00000484 | Please perform the HC JED1M6N0048K have sleeping cell issue | Please perform the HC JED1M6N0048K have sleeping cell issue |  |  |  | API | 10/27/2025 08:12:04 | 10/27/2025 08:36:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000233 | PCM-20251027-00000662 | TT-20251027-00710 | Telecom | Region_1 | KBR2M7155 | KBR0155 |  |  |  | Imran Ali Yousaf | 10/27/2025 08:12:11 | 10/27/2025 08:12:11 | 10/27/2025 14:12:11 | Cell Unavailable at KBR2M7155-P3-L800 @ Sceco | 10/27/2025 08:10:48 | Major | 29240 | Cell Unavailable | 10/27/2025 08:10:16 | P3 | 4G | dammam | Sceco | LTE SA | KBR2M7155 | FLM_TE | [8 empty] | API | 10/27/2025 08:12:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000235 | PCM-20251027-00000666 | TT-20251027-00713 | Telecom | Region_1 | DAM0359 | DAM0359 |  |  |  | Meraj Husain Idd Baksh | 10/27/2025 08:14:58 | 10/27/2025 08:51:33 | 10/27/2025 14:14:58 | Board Hardware Fault at DAM0359-P2_SRAN @ Sceco | 10/27/2025 08:12:11 | Major | 26200 | Board Hardware Fault | 10/27/2025 08:10:37 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0359 | FLM_TE | [8 empty] | API | 10/27/2025 08:14:58 | 10/27/2025 08:51:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000236 | PCM-20251027-00000667 | TT-20251027-00706 | Telecom | Region_1 | HFR2U6398 | HFR6098 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/27/2025 08:16:00 | 10/27/2025 08:16:00 | 10/27/2025 14:16:00 | 1(3G) sites down under HFR6098-P3/HB1RNCH01 @ Sceco | 10/27/2025 08:07:44 | Major | 22214 | NodeB Unavailable | 10/27/2025 08:07:42 | P3 | 3G | hafr | Sceco | 3G SA | HFR6098-P3 | FLM_TE | HFR6098 | Results: DOWN SITE HUB HFR6098-P3 HFR6098 Summary: Hub: HFR6098, Down Count: 1, Down Sites: HFR6098-P3 Alarm Summary: HFR6098 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 08:16:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000238 | PCM-20251027-00000676 | TT-20251027-00726 | EM | Region_4 | JED6025 | JED6025 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/27/2025 08:23:13 | 10/27/2025 08:23:13 | 10/27/2025 20:23:13 | SHELTER DOOR OPEN at JED6025-GSM-P3 @ Sceco | 10/27/2025 08:22:46 | Minor | 7103 | SHELTER DOOR OPEN | 10/27/2025 08:22:42 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6025 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/27/2025 08:23:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000239 | PCM-20251027-00000678 | TT-20251027-00727 | Telecom | Region_6 | KHS1M7299 | KHS0299 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/27/2025 08:24:14 | 10/27/2025 08:24:14 | 10/27/2025 20:24:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at KHS1M7299-G9-L9-SBTS-P2 @ Sceco_STB | 10/27/2025 08:23:37 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 08:23:26 | P2 | 4G | khamis mushyet | Sceco_STB | 5G_Cell SA | KHS1M7299 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 08:24:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000240 | PCM-20251027-00000680 | TT-20251027-00321 | Telecom | Region_1 | UQL0282 | UQL0282 |  |  |  | Almmoez Almmoez | 10/27/2025 08:24:21 | 10/27/2025 08:24:21 | 10/27/2025 14:24:21 | 1(2G) 1(LTE) sites down under SAK2915-P3-L800-USF,QRY0602-P3-USF/SK1BSCH01 @ Generator_SG | 10/27/2025 04:30:03 | Major | 21825 | CSL Fault | 10/27/2025 04:30:02 | P2 | SRAN | rafha | Sceco | 2G_LTE SA | SAK2915-P3-L800-USF LTE,QRY0602-P3-USF 2G | FLM_TE | SAK2915 | Results: DOWN SITE HUB SAK2915-P3-L800-USF SAK2915 QRY0602-P3-USF QRY0602 Summary: Hub: SAK2915, Down Count: 1, Down Sites: SAK2915-P3-L800-USF Hub: QRY0602, Down Count: 1, Down Sites: QRY0602-P3-USF Alarm Summary: SAK2915 No Active Alarm on HUB QRY0602 No Active Alarm on HUB | PCM-20251027-00000452 | please check | please check |  | sites down |  | API | 10/27/2025 08:24:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251027000241 | PCM-20251027-00000683 | TT-20251027-00730 | EM | [7 empty] | 10/27/2025 08:24:46 | 10/27/2025 08:24:46 | 10/27/2025 20:24:46 | NETECO: Communication Fail at MDUL2706 @ Generator_SG | 10/27/2025 08:18:33 | Minor | 20001 | Communication Fail | 10/27/2025 08:18:33 | P3 | SRAN |  | Generator_SG | 2G NSA | MDUL2706 | FLM_EM | [8 empty] | API | 10/27/2025 08:24:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000244 | PCM-20251027-00000693 | TT-20251027-00743 | Reference_telecom | Region_6 | MHA0517 | MHA0517 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/27/2025 08:30:27 | 10/27/2025 08:30:27 | 10/27/2025 20:30:27 | BASE STATION SERVICE PROBLEM (TX out of order) at MHA0517-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/27/2025 08:25:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 08:25:41 | P3 | 2G | khamis mushyet | Sceco | LTE_Cell SA | MHA0517 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/27/2025 08:30:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000247 | PCM-20251027-00000696 | TT-20251027-00731 | EM | Region_6 | KMBS0666 | KMBS0666 |  |  |  | Ezat Mohammed | 10/27/2025 08:31:00 | 10/27/2025 08:31:00 | 10/27/2025 14:31:00 | 1(2G/3G/5G) sites down under KMBS0666-P2-USF/KMBS0666-P2-USF @ Sceco | 10/27/2025 08:23:12 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 08:23:09 | P2 | 2G | bisha | Sceco | 2G_3G_5G SA | KMBS0666-P2-USF | FLM_EM | KMBS0666 | Results: DOWN SITE HUB KMBS0666-P2-USF KMBS0666 Summary: Hub: KMBS0666, Down Count: 1, Down Sites: KMBS0666-P2-USF Alarm Summary: KMBS0666 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 08:31:00 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000248 | PCM-20251027-00000699 | TT-20251027-00440 | Telecom | Region_2 | RIY2705 | RIY2705 |  |  |  | Hakim Ullah Raif Ullah Jan | 10/27/2025 08:31:51 | 10/27/2025 08:31:51 | 10/27/2025 20:31:51 | Board Not In Position at RIY2705-P3_SRAN @ Generator_DG | 10/27/2025 00:50:33 | Minor | 26204 | Board Not In Position | 10/27/2025 00:49:00 | P3 | SRAN | riyadh | Generator_DG | 2G NSA | RIY2705 | FLM_TE |  |  | PCM-20251027-00000381 | pls check Cabinet No.=0, Subrack No.=0, Slot No.=3, Board Type=UBBP | pls check Cabinet No.=0, Subrack No.=0, Slot No.=3, Board Type=UBBP |  |  |  | API | 10/27/2025 08:31:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000249 | PCM-20251027-00000703 | TT-20251027-00747 | Reference_EM | Region_1 | SMRY0810 | SMRY0810 |  |  |  | Samir Elzain Abdu Gumaa | 10/27/2025 08:34:04 | 10/27/2025 08:34:04 | 10/27/2025 20:34:04 | Major Rec alarm at SMRY0810-P2_SRAN @ Generator_SG | 10/27/2025 08:25:48 | Minor | 65107 | Major Rec alarm | 10/27/2025 08:23:43 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0810 | FLM_EM | [8 empty] | API | 10/27/2025 08:34:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000250 | PCM-20251027-00000704 | TT-20251027-00748 | EM | Region_6 | KMBS1M7665 | KMBS0665 |  |  |  | Ezat Mohammed | 10/27/2025 08:34:04 | 10/27/2025 08:34:04 | 10/27/2025 20:34:04 | COMMERCIAL POWER FAILURE at KMBS1M7665-G9-L9-SBTS-P2-USF @ Sceco | 10/27/2025 08:32:22 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/27/2025 08:22:32 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMBS1M7665 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/27/2025 08:34:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251027000254 | PCM-20251027-00000716 | TT-20251027-00698 | Reference_telecom | Region_6 | MKW1M8133 | MKW2133 |  |  |  | Manzoor Ahmed | 10/27/2025 08:40:27 | 10/27/2025 08:49:47 | 10/27/2025 20:40:27 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at MKW1M8133-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/27/2025 08:02:58 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/27/2025 04:04:42 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8133 | FLM_TE |  |  | PCM-20251027-00000648 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/27/2025 08:40:27 | 10/27/2025 08:49:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000255 | PCM-20251027-00000717 | TT-20251027-00732 | Reference_telecom | Region_4 | DKA1M7347 | DKA0347 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/27/2025 08:40:39 | 10/27/2025 08:40:39 | 10/27/2025 20:40:39 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at DKA1M7347-G9-L8-L18-SBTS-P3 @ Sceco | 10/27/2025 06:26:36 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/27/2025 06:25:59 | P3 | 4G | qunfuddah | Sceco | LTE NSA | DKA1M7347 | FLM_TE |  |  | PCM-20251027-00000685 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/27/2025 08:40:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000257 | PCM-20251027-00000722 | TT-20251027-00765 | Reference_telecom | Region_5 | MAK0654 | MAK0654 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/27/2025 08:44:24 | 10/27/2025 08:44:24 | 10/27/2025 20:44:24 | ReplaceableUnitMissing observed in MAK0654_04 towards 10.3.227.10 @ Sceco | 10/26/2025 20:46:23 | Minor |  | ReplaceableUnitMissing | 10/26/2025 20:44:09 | P2 | 2G | makkah | Sceco | TX NSA | MAK0654 | FLM_TE | [8 empty] | API | 10/27/2025 08:44:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000258 | PCM-20251027-00000723 | TT-20251027-00750 | Reference_telecom | Region_4 | UKZ1M7211 | UKZ0211 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/27/2025 08:45:16 | 10/27/2025 08:45:16 | 10/27/2025 14:45:16 | CELL FAULTY (Failure in optical interface) at UKZ1M7211-USF-P3 @ Generator_SG | 10/27/2025 08:17:34 | Major | 7653 | CELL FAULTY | 10/27/2025 08:30:44 | P2 | 4G | adam | Generator_SG | LTE_Cell SA | UKZ1M7211 | FLM_TE |  |  | PCM-20251027-00000707 | Kindly check the optical cable and SFP at site | Kindly check the optical cable and SFP at site |  |  |  | API | 10/27/2025 08:45:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000259 | PCM-20251027-00000725 | TT-20251027-00735 | Reference_telecom | Region_3 | HAL2M3127 | HAL0127 |  |  |  | Mazin Meshary AlEnzi | 10/27/2025 08:46:20 | 10/27/2025 08:46:20 | 10/27/2025 14:46:20 | UMTS Cell Unavailable at HAL2M3127-P2 (REF::TT-20251027-00134) @ Sceco | 10/27/2025 08:01:19 | Major | 22202 | UMTS Cell Unavailable | 10/27/2025 08:01:16 | P2 | 3G | hail | Sceco | 3G SA | HAL2M3127 | FLM_TE |  |  | PCM-20251027-00000700 | Dear, Approved to replace faulty board referenced to below shared troubleshooting steps & results details Board Name MRRU Board Type WD5MWRUE810 BOM Code 02310KKQ SN(Bar Code) 2102310KKQ4ME8002681 | Dear, Approved to replace faulty board referenced to below shared troubleshooting steps & results details Board Name MRRU Board Type WD5MWRUE810 BOM Code 02310KKQ SN(Bar Code) 2102310KKQ4ME8002681 |  |  |  | API | 10/27/2025 08:46:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000260 | PCM-20251027-00000729 | TT-20251027-00772 | Reference_EM | Region_2 | RIYA2U6174a | RIYA6074 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/27/2025 08:49:03 | 10/27/2025 08:49:03 | 10/27/2025 20:49:03 | Major Rec. alarm at RIYA2U6174A-P3 @ Sceco | 10/27/2025 08:38:46 | Minor | 65107 | Major Rec. alarm | 10/27/2025 08:38:41 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYA2U6174A | FLM_EM | [8 empty] | API | 10/27/2025 08:49:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000262 | PCM-20251027-00000734 | TT-20251027-00775 | Telecom | Region_5 | MAK0106 | MAK0106 |  |  |  | Muhammad Zubair | 10/27/2025 08:50:04 | 10/27/2025 08:50:04 | 10/27/2025 14:50:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0106-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HAJJ-Core-HUB-WDM-HRM @ Sceco_STB | 10/27/2025 08:49:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/27/2025 08:49:23 | VIP | 2G | makkah | Sceco_STB | 5G_Cell SA | MAK0106 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/27/2025 08:50:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000263 | PCM-20251027-00000735 | TT-20251027-00776 | EM | Region_5 | MAK0106 | MAK0106 |  |  |  | Amr Abdellah Emara Abouseada | 10/27/2025 08:50:05 | 10/27/2025 08:50:05 | 10/27/2025 12:50:05 | TRX FAULTY (FF FF FF FF FF FF shared:S) at MAK0106-P1-VIP-HAJJ-Core-HUB-WDM-HRM @ Sceco_STB | 10/27/2025 08:49:28 | Critical | 7606 | TRX FAULTY | 10/27/2025 08:49:23 | VIP | 2G | makkah | Sceco_STB | 2G_Cell SA | MAK0106 | FLM_EM | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/27/2025 08:50:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000264 | PCM-20251027-00000737 | TT-20251027-00725 | Reference_telecom | Region_4 | NOB1M3225 | NOB0225 |  |  |  | Khizer Hayat | 10/27/2025 08:51:29 | 10/27/2025 08:51:29 | 10/27/2025 14:51:29 | WCDMA CELL OUT OF USE at NOB1M3225-P2-USF @ Generator_SG | 10/27/2025 08:17:31 | Major | 7771 | WCDMA CELL OUT OF USE | 10/27/2025 08:15:19 | P2 | 3G | jeddah | Generator_SG | 3G SA | NOB1M3225 | FLM_TE |  |  | PCM-20251027-00000675 | Kindly check the site locally as cells are down due to degraded connectivity | Kindly check the site locally as cells are down due to degraded connectivity |  |  |  | API | 10/27/2025 08:51:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251027000265 | PCM-20251027-00000738 | TT-20251027-00766 | Telecom | Region_4 | JED2392 | JED2392 |  |  |  | MALIK ATIF ZAMAN | 10/27/2025 08:52:29 | 10/27/2025 08:57:20 | 10/27/2025 12:52:29 | 3(2G) 2(LTE) 1(5G) sites down under JED2392-P3,JED0933-FWA-P1-VIP,JED0154-P1-VIP-WDM-FON/JED0154-P1-VIP-WDM-FON @ Sceco | 10/27/2025 08:41:49 | Critical | 7706 | BTS O&M LINK FAILURE | 10/27/2025 08:41:43 | P3 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED0154-P1-VIP-WDM-FON 2G_LTE_5G,JED2392-P3 2G_LTE,JED0933-FWA-P1-VIP 2G | FLM_TE | JED2392 | DOWN SITE HUB TX FB JED2392-P3 JED2392 Observing no issue at HUB , kindly check locally JED0933-FWA-P1-VIP JED0933 Link flapping at HUB JED0154-P1-VIP-WDM-FON JED0154 Check with IP Ran as HUB is P2 router | PCM-20251027-00000733 | DOWN SITE HUB TX FB JED2392-P3 JED2392 Observing no issue at HUB , kindly check locally JED0933-FWA-P1-VIP JED0933 Link flapping at HUB JED0154-P1-VIP-WDM-FON JED0154 Check with IP Ran as HUB is P2 router | DOWN SITE HUB TX FB JED2392-P3 JED2392 Observing no issue at HUB , kindly check locally JED0933-FWA-P1-VIP JED0933 Link flapping at HUB JED0154-P1-VIP-WDM-FON JED0154 Check with IP Ran as HUB is P2 router |  | sites down |  | API | 10/27/2025 08:52:29 | 10/27/2025 08:57:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000266 | PCM-20251027-00000739 | TT-20251027-00692 | Telecom | Region_4 | JED1M8083 | JED2083 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/27/2025 08:52:39 | 10/27/2025 08:52:39 | 10/27/2025 20:52:39 | BASE STATION ANTENNA LINE PROBLEM at JED1M8083-L2100-L1800-L800-P3-SBTS @ Generator_SG | 10/27/2025 07:50:55 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/27/2025 07:50:51 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8083 | FLM_TE |  |  | PCM-20251027-00000641 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/27/2025 08:52:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000267 | PCM-20251027-00000740 | TT-20251027-00689 | Telecom | Region_4 | HHR1M7481 | HHR0481 |  |  |  | Nazeer Mohammed | 10/27/2025 08:52:50 | 10/27/2025 08:52:50 | 10/27/2025 20:52:50 | BASE STATION ANTENNA LINE PROBLEM at HHR1M7481-L800-P3_NCA_L1800-L2100_SBTS @ Generator_SG | 10/27/2025 07:49:31 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/27/2025 07:49:08 | P2 | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7481 | FLM_TE |  |  | PCM-20251027-00000638 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/27/2025 08:52:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251027000268 | PCM-20251027-00000748 | TT-20251027-00784 | Reference_EM | Region_2 | RIYA2U6155 | RIYA6055 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/27/2025 08:55:14 | 10/27/2025 08:55:14 | 10/27/2025 20:55:14 | Door opening alarm at RIYA2U6155-P3 @ Sceco | 10/27/2025 08:55:07 | Minor | 65101 | Door opening alarm | 10/27/2025 08:55:04 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYA2U6155 | FLM_EM | [8 empty] | API | 10/27/2025 08:55:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251027000269 | PCM-20251027-00000753 | TT-20251027-00762 | Telecom | Region_4 | TFSH0674 | TFSH0674 |  |  |  | Walid Magdy Tawfik Elbana | 10/27/2025 08:56:28 | 10/27/2025 08:56:28 | 10/27/2025 14:56:28 | 2(2G) 2(3G) 1(LTE) 1(5G) sites down under TFSH0674-P3,SHF0330-P3/SHF0330-P3 @ Sceco | 10/27/2025 08:39:54 | Major | 7706 | BTS O&M LINK FAILURE | 10/27/2025 08:39:47 | P3 | 2G | taif | Sceco | 2G_3G_LTE SA | SHF0330-P3 2G_3G_LTE,TFSH0674-P3 2G_3G | FLM_EM | TFSH0674 | Dear team , Hub: TFSH0674 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251027-00000726 | Dear team , Hub: TFSH0674 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: TFSH0674 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/27/2025 08:56:28 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251026001094 | PCM-20251026-00002122 | TT-20251026-02105 | Reference_EM | Region_2 | WDS9016 | WDS9016 |  |  |  | Sher Zamin Nasib Muhammad | 10/26/2025 19:30:36 | 10/26/2025 19:30:36 | 10/27/2025 07:30:36 | NETECO: Battery Undervoltage at WDS9016 @ Power Cube | 10/26/2025 19:23:52 | Minor | 8901 | Battery Undervoltage | 10/26/2025 19:23:52 | P1 | Repeater | aflaj | Power Cube | 2G NSA | WDS9016 | FLM_EM | [8 empty] | API | 10/26/2025 19:30:36 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026001104 | PCM-20251026-00002138 | TT-20251026-02122 | Reference_EM | Region_1 | RAQB2126 | RAQB2126 |  |  |  | Mahmoud Youssef Mohamed Ahmed | 10/26/2025 19:48:10 | 10/26/2025 19:48:10 | 10/27/2025 07:48:10 | Door opening alarm at RAQB2126-P3_SRAN @ Sceco | 10/26/2025 19:47:42 | Minor | 65101 | Door opening alarm | 10/26/2025 19:47:39 | P3 | SRAN | hafr | Sceco | 2G NSA | RAQB2126 | FLM_EM | [8 empty] | API | 10/26/2025 19:48:10 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001128 | PCM-20251026-00002174 | TT-20251026-02158 | Reference_EM | Region_2 | RIY2135 | RIY2135 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/26/2025 20:22:45 | 10/26/2025 20:22:45 | 10/27/2025 08:22:45 | Minor Rec alarm at RIY2135-P2_SRAN @ Sceco | 10/26/2025 20:12:28 | Minor | 65108 | Minor Rec alarm | 10/26/2025 20:12:24 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2135 | FLM_EM | [8 empty] | API | 10/26/2025 20:22:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251026001140 | PCM-20251026-00002211 | TT-20251026-02187 | Reference_EM | Region_2 | RUM0582 | RUM0582 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/26/2025 20:53:16 | 10/27/2025 08:29:00 | 10/27/2025 08:53:16 | Mains Failure at RUM0582-P2_SRAN @ Generator_SG | 10/26/2025 20:43:13 | Minor | 65109 | Mains Failure | 10/26/2025 20:43:09 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RUM0582 | FLM_EM | [8 empty] | API | 10/26/2025 20:53:16 | 10/27/2025 08:29:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251026001143 | PCM-20251026-00002214 | TT-20251026-02194 | Reference_EM | Region_2 | FAM0021 | FAM0021 |  |  |  | Moustafa Elzaafarany Abdellah | 10/26/2025 20:56:21 | 10/26/2025 20:58:58 | 10/27/2025 08:56:21 | Major Rec. alarm at FAM2M1021-P3 @ Sceco | 10/26/2025 20:45:48 | Minor | 65107 | Major Rec. alarm | 10/26/2025 20:45:43 | P3 | 2G | dawadmi | Sceco | 2G NSA | FAM2M1021 | FLM_EM | [8 empty] | API | 10/26/2025 20:56:21 | 10/26/2025 20:58:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001151 | PCM-20251026-00002227 | TT-20251026-02200 | EM | Region_2 | RIY2431 | RIY2431 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/26/2025 21:02:01 | 10/26/2025 21:02:01 | 10/27/2025 09:02:01 | NETECO: Communication Failure at RIY2431 @ Sceco | 10/26/2025 20:55:33 | Minor | 13750 | Communication Failure | 10/26/2025 20:55:33 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2431 | FLM_EM | [8 empty] | API | 10/26/2025 21:02:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001157 | PCM-20251026-00002232 | TT-20251026-02209 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/26/2025 21:09:45 | 10/26/2025 21:09:45 | 10/27/2025 09:09:45 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/26/2025 20:59:07 | Minor | 65102 | high temprature 32 | 10/26/2025 20:59:02 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/26/2025 21:09:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251026001159 | PCM-20251026-00002246 | TT-20251026-02227 | Reference_EM | Region_1 | ARM0827 | ARM0827 |  |  |  | Moustafa Mohamed Saleh Saif | 10/26/2025 21:18:06 | 10/26/2025 21:18:06 | 10/27/2025 09:18:06 | Minor Rec alarm at ARM0827-P3_SRAN @ Sceco | 10/26/2025 21:07:30 | Minor | 65108 | Minor Rec alarm | 10/26/2025 21:07:27 | P3 | SRAN | hafouf | Sceco | 2G NSA | ARM0827 | FLM_EM | [8 empty] | API | 10/26/2025 21:18:06 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001187 | PCM-20251026-00002297 | TT-20251026-02276 | Reference_EM | Region_1 | DAM2822 | DAM2822 |  |  |  | Ahmed AbdELmoaz Ibrahim | 10/26/2025 21:55:45 | 10/26/2025 21:55:45 | 10/27/2025 09:55:45 | Door opening alarm at DAM2822-P3_SRAN @ Sceco | 10/26/2025 21:54:57 | Minor | 65101 | Door opening alarm | 10/26/2025 21:54:53 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2822 | FLM_EM | [8 empty] | API | 10/26/2025 21:55:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251026001197 | PCM-20251026-00002315 | TT-20251026-02288 | EM | Region_2 | RIY0589 | RIY0589 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/26/2025 22:19:01 | 10/26/2025 22:19:01 | 10/27/2025 10:19:01 | NETECO: Lithium Battery Communication Failure at RIY0589 @ Sceco | 10/26/2025 22:12:33 | Minor | 13750 | Lithium Battery Communication Failure | 10/26/2025 22:12:33 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY0589 | FLM_EM | [8 empty] | API | 10/26/2025 22:19:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251026001214 | PCM-20251026-00002348 | TT-20251026-02331 | Reference_EM | Region_2 | RIY0413 | RIY0413 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Khalifa Amin Aboueltaher | 10/26/2025 23:14:21 | 10/27/2025 00:49:48 | 10/27/2025 05:14:21 | Mains Failure at RIY0413-P1-SHOP-HUB_SRAN-FON @ Sceco | 10/26/2025 23:05:13 | Major | 65109 | Mains Failure | 10/26/2025 23:05:10 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0413 | FLM_EM | [8 empty] | API | 10/26/2025 23:14:21 | 10/26/2025 23:54:38 | 10/27/2025 00:02:10 | 10/27/2025 00:02:12 | 10/27/2025 00:02:16 | 10/27/2025 00:49:48 |  | Ahmed Khalifa Amin Aboueltaher |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251027000008 | PCM-20251027-00000030 | TT-20251027-00032 | EM | Region_1 | HRD9017 | HRD9017 |  |  |  | Montasir Awadalla Abdalla Bala | 10/27/2025 00:27:36 | 10/27/2025 04:07:11 | 10/27/2025 04:27:36 | RELAY_ALARM_CRITICAL at HRD9017_NE_1 @ Power Cube | 10/27/2025 00:26:31 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/27/2025 00:25:31 | P3 | Repeater | hafouf | Power Cube | TX NSA | HRD9017 | FLM_EM | [8 empty] | API | 10/27/2025 00:27:36 | 10/27/2025 04:07:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251027000012 | PCM-20251027-00000035 | TT-20251027-00005 | Telecom | Region_2 | RIY0413 | RIY0413 |  |  |  | Adham Adham Hassan Farghal | 10/27/2025 00:33:11 | 10/27/2025 00:33:11 | 10/27/2025 12:33:11 | RF Unit Maintenance Link Failure at RIY0413-P1-SHOP-HUB_SRAN-FON @ Sceco | 10/27/2025 00:07:00 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/27/2025 00:05:14 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0413 | FLM_EM |  |  | PCM-20251027-00000006 | power alarms reported | power alarms reported |  |  |  | API | 10/27/2025 00:33:11 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251027000014 | PCM-20251027-00000037 | TT-20251027-00039 | Reference_EM | Region_1 | YBR0607 | YBR0607 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Montasir Awadalla Abdalla Bala | 10/27/2025 00:34:21 | 10/27/2025 05:47:12 | 10/27/2025 12:34:21 | Battery Faulty at YBR0607-P3-USF_SRAN-PC @ Power Cube | 10/27/2025 00:23:40 | Minor | 65033 | Battery Faulty | 10/27/2025 00:23:36 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0607 | FLM_EM | [8 empty] | API | 10/27/2025 00:34:21 | 10/27/2025 04:07:11 | 10/27/2025 04:07:21 | 10/27/2025 04:07:25 | 10/27/2025 04:07:28 | 10/27/2025 05:47:12 |  | Montasir Awadalla Abdalla Bala |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251027000025 | PCM-20251027-00000077 | TT-20251027-00085 | EM | Region_1 | DJL0553 | DJL0553 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mohammed Kholi | 10/27/2025 01:12:06 | 10/27/2025 02:53:09 | 10/27/2025 05:12:06 | Generator failure at DJL0553-P1-HUB-WDM_SRAN @ Sceco_STB | 10/27/2025 01:10:10 | Critical | 65114 | Generator failure | 10/27/2025 01:10:06 | P1 | SRAN | sakaka | Sceco_STB | 2G NSA | DJL0553 | FLM_EM | [8 empty] | API | 10/27/2025 01:12:06 | 10/27/2025 01:30:55 | 10/27/2025 02:53:00 |  |  | 10/27/2025 02:53:09 |  | Mohammed Kholi |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251027000027 | PCM-20251027-00000079 | TT-20251026-01648 | Telecom | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/27/2025 01:12:36 | 10/27/2025 01:12:36 | 10/27/2025 13:12:36 | Power Supply at RYHF2036 on 10.248.32.108 @ Generator_SG | 10/26/2025 15:22:17 | Minor | Power Supply | Power Supply | 10/26/2025 15:13:55 | P2 | SRAN | hafouf | Generator_SG | TX NSA | RYHF2036 | FLM_EM |  |  | PCM-20251026-00001683 | power issue | power issue |  |  |  | API | 10/27/2025 01:12:36 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251027000040 | PCM-20251027-00000119 | TT-20251027-00129 | Reference_EM | Region_2 | AFL0094 | AFL0094 | Enviroment | Genset failure_Starting Battery | Change Generator battery | Saeed Ud Din Muhammad Yousaf | 10/27/2025 01:39:56 | 10/27/2025 04:37:53 | 10/27/2025 07:39:56 | Generator failure at AFL0094-P1-USF_SRAN-PC @ Power Cube | 10/27/2025 01:29:40 | Major | 65114 | Generator failure | 10/27/2025 01:29:36 | P3 | SRAN | aflaj | Power Cube | 2G NSA | AFL0094 | FLM_EM | [8 empty] | API | 10/27/2025 01:39:56 | 10/27/2025 03:07:12 | 10/27/2025 03:08:27 | 10/27/2025 03:08:37 | 10/27/2025 04:03:41 | 10/27/2025 04:37:53 |  | Saeed Ud Din Muhammad Yousaf |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251027000047 | PCM-20251027-00000130 | TT-20251027-00141 | Reference_EM | Region_2 | DLM0485 | DLM0485 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/27/2025 01:53:56 | 10/27/2025 01:53:56 | 10/27/2025 13:53:56 | high temprature 40 at DLM0485-P2_SRAN @ Sceco | 10/27/2025 01:45:55 | Minor | 65103 | high temprature 40 | 10/27/2025 01:43:07 | P2 | SRAN | al kharj | Sceco | 2G NSA | DLM0485 | FLM_EM | [8 empty] | API | 10/27/2025 01:53:56 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251027000048 | PCM-20251027-00000132 | TT-20251027-00143 | Reference_EM | Region_2 | HRHT0132 | HRHT0132 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | ABUZAR Ahmed Humida Mustafa | 10/27/2025 01:55:56 | 10/27/2025 03:27:35 | 10/27/2025 13:55:56 | Generator failure at HRHT0132-P3_SRAN-PC @ Power Cube | 10/27/2025 01:45:15 | Minor | 65114 | Generator failure | 10/27/2025 01:45:12 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HRHT0132 | FLM_EM | [8 empty] | API | 10/27/2025 01:55:56 | 10/27/2025 02:18:31 | 10/27/2025 02:18:48 | 10/27/2025 02:18:54 | 10/27/2025 02:32:54 | 10/27/2025 03:27:35 |  | ABUZAR Ahmed Humida Mustafa |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000065 | PCM-20251027-00000184 | TT-20251027-00195 | Reference_EM | Region_1 | HFF2723 | HFF2723 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/27/2025 02:40:26 | 10/27/2025 02:40:26 | 10/27/2025 14:40:26 | Door opening alarm at HFF2723-P2_SRAN @ Sceco | 10/27/2025 02:39:56 | Minor | 65101 | Door opening alarm | 10/27/2025 02:39:53 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2723 | FLM_EM | [8 empty] | API | 10/27/2025 02:40:26 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000078 | PCM-20251027-00000209 | TT-20251027-00220 | Reference_EM | Region_2 | RIY0456 | RIY0456 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/27/2025 03:07:46 | 10/27/2025 03:07:46 | 10/27/2025 09:07:46 | Mains Failure at RIY0456-P1-VIP-HUB_SRAN-FON @ Sceco | 10/27/2025 02:57:37 | Major | 65109 | Mains Failure | 10/27/2025 02:57:34 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0456 | FLM_EM | [8 empty] | API | 10/27/2025 03:07:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251027000086 | PCM-20251027-00000229 | TT-20251027-00256 | Reference_EM | Region_1 | DAM2061 | DAM2061 |  |  |  | Omer Elfadoul Mohamed Ibrahim | 10/27/2025 03:34:06 | 10/27/2025 04:51:21 | 10/27/2025 09:34:06 | Air condition 1 failure alarm at DAM2061-P1-HUB_SRAN @ Sceco_STB | 10/27/2025 03:23:48 | Major | 65104 | Air condition 1 failure alarm | 10/27/2025 03:23:45 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | DAM2061 | FLM_EM | [8 empty] | API | 10/27/2025 03:34:06 | 10/27/2025 04:51:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000089 | PCM-20251027-00000239 | TT-20251027-00263 | Reference_EM | Region_2 | RIY0136 | RIY0136 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/27/2025 03:53:46 | 10/27/2025 03:53:46 | 10/27/2025 15:53:46 | Air condition 1 failure alarm at RIY0136-P2_SRAN @ Sceco | 10/27/2025 03:43:25 | Minor | 65104 | Air condition 1 failure alarm | 10/27/2025 03:43:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0136 | FLM_EM | [8 empty] | API | 10/27/2025 03:53:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000096 | PCM-20251027-00000267 | TT-20251027-00291 | Reference_EM | Region_2 | RIY2897 | RIY2897 |  |  |  | Amr Abbas Zaghloul Abbas | 10/27/2025 04:11:51 | 10/27/2025 04:11:51 | 10/27/2025 16:11:51 | Door opening alarm at RIY2897-P3_SRAN @ Generator_SG | 10/27/2025 04:11:06 | Minor | 65101 | Door opening alarm | 10/27/2025 04:11:02 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2897 | FLM_EM | [8 empty] | API | 10/27/2025 04:11:51 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000101 | PCM-20251027-00000274 | TT-20251027-00303 | EM | Region_2 | WDS9020 | WDS9020 |  |  |  | Sher Zamin Nasib Muhammad | 10/27/2025 04:23:16 | 10/27/2025 04:23:16 | 10/27/2025 08:23:16 | RELAY_ALARM_CRITICAL at WDS9020_NE_2 @ Power Cube | 10/27/2025 04:22:00 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/27/2025 04:21:47 | P3 | Repeater | aflaj | Power Cube | TX NSA | WDS9020 | FLM_EM | [8 empty] | API | 10/27/2025 04:23:16 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000118 | PCM-20251027-00000322 | TT-20251027-00369 | Reference_EM | Region_2 | RIY0657 | RIY0657 |  |  |  | Moin Uddin | 10/27/2025 05:04:02 | 10/27/2025 05:04:02 | 10/27/2025 17:04:02 | Air condition 1 failure alarm at RIY0657-P2_SRAN @ Sceco | 10/27/2025 04:53:22 | Minor | 65104 | Air condition 1 failure alarm | 10/27/2025 04:53:19 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0657 | FLM_EM | [8 empty] | API | 10/27/2025 05:04:02 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000127 | PCM-20251027-00000334 | TT-20251027-00379 | Reference_EM | Region_2 | UMH0843 | UMH0843 |  |  |  | Ahmed Mahmoud Mohamed Mahmoud | 10/27/2025 05:14:21 | 10/27/2025 05:14:21 | 10/27/2025 17:14:21 | Air condition 1 failure alarm at UMH0843-P3_SRAN @ Generator_SG | 10/27/2025 05:03:51 | Minor | 65104 | Air condition 1 failure alarm | 10/27/2025 05:03:47 | P3 | SRAN | majma | Generator_SG | 2G NSA | UMH0843 | FLM_EM | [8 empty] | API | 10/27/2025 05:14:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000137 | PCM-20251027-00000366 | TT-20251027-00425 | Reference_EM | Region_1 | YBR0607 | YBR0607 |  |  |  | Montasir Awadalla Abdalla Bala | 10/27/2025 05:44:21 | 10/27/2025 05:44:21 | 10/27/2025 17:44:21 | Door opening alarm at YBR0607-P3-USF_SRAN-PC @ Power Cube | 10/27/2025 05:43:44 | Minor | 65101 | Door opening alarm | 10/27/2025 05:43:40 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0607 | FLM_EM | [8 empty] | API | 10/27/2025 05:44:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251027000142 | PCM-20251027-00000373 | TT-20251027-00429 | Reference_EM | Region_1 | DAM2995 | DAM2995 | Enviroment | SCECO_Failure | SCECO auto restored | Abdul Malik Shaik | 10/27/2025 05:52:06 | 10/27/2025 08:44:31 | 10/27/2025 17:52:06 | Minor Rec alarm at DAM2995-P2_SRAN @ Sceco | 10/27/2025 05:42:07 | Minor | 65108 | Minor Rec alarm | 10/27/2025 05:41:25 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2995 | FLM_EM | [8 empty] | API | 10/27/2025 05:52:06 | 10/27/2025 06:01:15 | 10/27/2025 07:04:12 | 10/27/2025 07:04:15 | 10/27/2025 07:04:18 | 10/27/2025 08:44:31 |  | Abdul Malik Shaik |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000151 | PCM-20251027-00000392 | TT-20251027-00450 | Reference_EM | Region_1 | SLW0375 | SLW0375 |  |  |  | Moustafa Mohamed Saleh Saif | 10/27/2025 06:03:56 | 10/27/2025 06:03:56 | 10/27/2025 12:03:56 | Air condition 1 failure alarm at SLW0375-P1-VIP_SRAN @ Sceco | 10/27/2025 05:53:39 | Major | 65104 | Air condition 1 failure alarm | 10/27/2025 05:53:35 | VIP | SRAN | hafouf | Sceco | 2G NSA | SLW0375 | FLM_EM | [8 empty] | API | 10/27/2025 06:03:56 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251027000164 | PCM-20251027-00000421 | TT-20251027-00484 | Reference_EM | Region_2 | ARS0175 | ARS0175 | Enviroment | SCECO_Failure | SCECO auto restored | Shazlly Mahmoud Abouzied Mahmoud | 10/27/2025 06:36:01 | 10/27/2025 08:39:09 | 10/27/2025 18:36:01 | Mains Failure at ARS0175-P2_SRAN @ Sceco | 10/27/2025 06:25:52 | Minor | 65109 | Mains Failure | 10/27/2025 06:25:50 | P2 | SRAN | al rass | Sceco | 2G NSA | ARS0175 | FLM_EM | [8 empty] | API | 10/27/2025 06:36:01 | 10/27/2025 07:14:32 | 10/27/2025 07:18:46 | 10/27/2025 07:18:49 | 10/27/2025 08:10:42 | 10/27/2025 08:39:09 |  | Shazlly Mahmoud Abouzied Mahmoud |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000165 | PCM-20251027-00000420 | TT-20251027-00483 | Reference_EM | Region_2 | RIY0328 | RIY0328 |  |  |  | RANJEET KUMAR YADAV | 10/27/2025 06:36:02 | 10/27/2025 06:36:02 | 10/27/2025 18:36:02 | Door opening alarm at RIY0328-P2_SRAN-FON @ Generator_SG | 10/27/2025 06:35:31 | Minor | 65101 | Door opening alarm | 10/27/2025 06:35:29 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0328 | FLM_EM | [8 empty] | API | 10/27/2025 06:36:02 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251027000166 | PCM-20251027-00000422 | TT-20251027-00487 | Reference_EM | Region_1 | KBR0195 | KBR0195 |  |  |  | Abdul Malik Shaik | 10/27/2025 06:38:36 | 10/27/2025 08:44:40 | 10/27/2025 12:38:36 | Door opening alarm at KBR0195-P1-SHOP_SRAN @ Sceco | 10/27/2025 06:38:00 | Major | 65101 | Door opening alarm | 10/27/2025 06:37:54 | P1 | SRAN | dammam | Sceco | 2G NSA | KBR0195 | FLM_EM | [8 empty] | API | 10/27/2025 06:38:36 | 10/27/2025 08:44:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251027000182 | PCM-20251027-00000462 | TT-20251027-00521 | Reference_EM | Region_1 | DAM2995 | DAM2995 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/27/2025 07:03:55 | 10/27/2025 07:03:55 | 10/27/2025 19:03:55 | Door opening alarm at DAM2995-P2_SRAN @ Sceco | 10/27/2025 07:03:29 | Minor | 65101 | Door opening alarm | 10/27/2025 07:03:26 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2995 | FLM_EM | [8 empty] | API | 10/27/2025 07:03:55 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000199 | PCM-20251027-00000491 | TT-20251027-00550 | Reference_EM | Region_2 | HIL2471 | HIL2471 |  |  |  | Farman Ullah Muhammad Nazir | 10/27/2025 07:23:31 | 10/27/2025 07:23:31 | 10/27/2025 19:23:31 | Door opening alarm at HIL2471-P2_SRAN @ Sceco | 10/27/2025 07:23:09 | Minor | 65101 | Door opening alarm | 10/27/2025 07:15:21 | P2 | SRAN | al rass | Sceco | 2G NSA | HIL2471 | FLM_EM | [8 empty] | API | 10/27/2025 07:23:31 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000200 | PCM-20251027-00000493 | TT-20251027-00552 | Reference_EM | Region_2 | HIL2471 | HIL2471 |  |  |  | Farman Ullah Muhammad Nazir | 10/27/2025 07:26:06 | 10/27/2025 07:26:06 | 10/27/2025 19:26:06 | Air condition 1 failure alarm at HIL2471-P2_SRAN @ Sceco | 10/27/2025 07:23:09 | Minor | 65104 | Air condition 1 failure alarm | 10/27/2025 07:15:21 | P2 | SRAN | al rass | Sceco | 2G NSA | HIL2471 | FLM_EM | [8 empty] | API | 10/27/2025 07:26:06 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000228 | PCM-20251027-00000657 | TT-20251027-00707 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Mohamed Samir Farahat Allam | 10/27/2025 08:11:35 | 10/27/2025 08:11:35 | 10/27/2025 20:11:35 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/27/2025 08:01:12 | Minor | 65102 | high temprature 32 | 10/27/2025 08:01:08 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/27/2025 08:11:35 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000229 | PCM-20251027-00000658 | TT-20251027-00708 | EM | Region_1 | KBR0163 | KBR0163 |  |  |  | Yasser Mohamed Abdelnabi Ibrahim | 10/27/2025 08:11:36 | 10/27/2025 08:11:36 | 10/27/2025 12:11:36 | high temprature 40 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/27/2025 08:09:28 | Critical | 65103 | high temprature 40 | 10/27/2025 08:09:25 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/27/2025 08:11:36 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251027000232 | PCM-20251027-00000660 | TT-20251027-00709 | Reference_EM | Region_2 | RIY0948 | RIY0948 |  |  |  | Kadri Jalal Mohammed Asmail | 10/27/2025 08:12:05 | 10/27/2025 08:12:05 | 10/27/2025 14:12:05 | Mains Failure at RIY0948-P1-VIP_SRAN-FON @ Sceco | 10/27/2025 08:02:01 | Major | 65109 | Mains Failure | 10/27/2025 08:01:55 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0948 | FLM_EM | [8 empty] | API | 10/27/2025 08:12:05 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251027000237 | PCM-20251027-00000671 | TT-20251027-00719 | Reference_EM | Region_1 | NRY0574 | NRY0574 |  |  |  | Dileesh Muringothil Devarajan | 10/27/2025 08:19:50 | 10/27/2025 08:48:01 | 10/27/2025 20:19:50 | Mains Failure at NRY0574-P3-USF_SRAN-PC @ Sceco | 10/27/2025 08:09:52 | Minor | 65109 | Mains Failure | 10/27/2025 08:09:48 | P3 | SRAN | jubail | Sceco | 2G NSA | NRY0574 | FLM_EM | [8 empty] | API | 10/27/2025 08:19:50 | 10/27/2025 08:48:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000245 | PCM-20251027-00000694 | TT-20251027-00744 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/27/2025 08:30:40 | 10/27/2025 08:30:40 | 10/27/2025 20:30:40 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/27/2025 08:20:05 | Minor | 65107 | Major Rec alarm | 10/27/2025 08:20:01 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/27/2025 08:30:40 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000246 | PCM-20251027-00000695 | TT-20251027-00723 | Telecom | Region_2 | RYRN0633 | RYRN0633 |  |  |  | Saleem Khan Amir Dost | 10/27/2025 08:30:50 | 10/27/2025 08:30:50 | 10/27/2025 12:30:50 | 6(2G) 1(3G) 1(LTE) sites down under R2_RY1_HWBSC01 @ Sceco | 10/27/2025 08:19:50 | Critical | 21807 | OML Fault | 10/27/2025 08:19:41 | P3 | SRAN | quweyah | Sceco | 2G_3G_LTE SA | RYRN0767-P2 2G_3G_LTE,RYRN0697-P3 2G,RYRN0633-P3 2G,RYRN0761-P3 2G,RYRN0764-P3 2G,RYRN0754-P3 2G | FLM_EM |  | Dear Team, Hub:- RYRN0633 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251027-00000689 | Dear Team, Hub:- RYRN0633 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYRN0633 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/27/2025 08:30:50 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251027000251 | PCM-20251027-00000709 | TT-20251027-00753 | Reference_EM | Region_2 | RYRN0767 | RYRN0767 |  |  |  | Saleem Khan Amir Dost | 10/27/2025 08:36:51 | 10/27/2025 08:36:51 | 10/27/2025 20:36:51 | DC power fail at RYRN0767-P2_SRAN @ Sceco | 10/27/2025 08:34:37 | Minor | 65106 | DC power fail | 10/27/2025 08:20:57 | P2 | SRAN | quweyah | Sceco | 2G NSA | RYRN0767 | FLM_EM | [8 empty] | API | 10/27/2025 08:36:51 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000252 | PCM-20251027-00000710 | TT-20251027-00745 | EM | Region_2 | HBT0058 | HBT0058 |  |  |  | Kazi Jalil Allimiya | 10/27/2025 08:37:16 | 10/27/2025 08:37:16 | 10/27/2025 14:37:16 | 1(2G/LTE) sites down under HBT0058-P3-USF/KJ1BSCH01 @ Sceco | 10/27/2025 08:28:35 | Major | 21825 | CSL Fault | 10/27/2025 08:28:33 | P3 | 2G | aflaj | Sceco | 2G_LTE SA | HBT0058-P3-USF | FLM_EM |  | Results: DOWN SITE HUB HBT0058-P3-USF HBT0058 Summary: Hub: HBT0058, Down Count: 1, Down Sites: HBT0058-P3-USF Alarm Summary: HBT0058 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 08:37:16 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000256 | PCM-20251027-00000720 | TT-20251027-00763 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/27/2025 08:43:35 | 10/27/2025 08:43:35 | 10/27/2025 20:43:35 | high temprature 32 at RIY0349-P2_SRAN @ Sceco | 10/27/2025 08:33:00 | Minor | 65102 | high temprature 32 | 10/27/2025 08:32:56 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/27/2025 08:43:35 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000261 | PCM-20251027-00000731 | TT-20251027-00774 | Reference_EM | Region_2 | RYRN0633 | RYRN0633 |  |  |  | Saleem Khan Amir Dost | 10/27/2025 08:49:46 | 10/27/2025 08:49:46 | 10/27/2025 20:49:46 | Mains Failure at RYRN2M5633-P3 @ Sceco | 10/27/2025 08:39:50 | Minor | 65109 | Mains Failure | 10/27/2025 08:39:41 | P3 | 2G | quweyah | Sceco | 2G NSA | RYRN2M5633 | FLM_EM | [8 empty] | API | 10/27/2025 08:49:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251027000270 | PCM-20251027-00000754 | TT-20251027-00777 | EM | Region_1 | HFF2244 | HFF2244 |  |  |  | Moustafa Mohamed Saleh Saif | 10/27/2025 08:56:41 | 10/27/2025 08:56:41 | 10/27/2025 14:56:41 | 1(2G/3G/LTE) sites down under HFF2244-P2/R1_HF_HWBSC01 @ Sceco | 10/27/2025 08:49:36 | Major | 21825 | CSL Fault | 10/27/2025 08:49:34 | P2 | 2G | hafouf | Sceco | 2G_3G_LTE SA | HFF2244-P2 | FLM_EM |  | Results: DOWN SITE HUB HFF2244-P2 HFF2244 Summary: Hub: HFF2244, Down Count: 1, Down Sites: HFF2244-P2 Alarm Summary: HFF2244 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/27/2025 08:56:41 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251027000271 | PCM-20251027-00000755 | TT-20251027-00786 | Reference_EM | Region_1 | ARR0909 | ARR0909 |  |  |  | Mohamed Ahmed Goda | 10/27/2025 08:57:00 | 10/27/2025 08:57:00 | 10/27/2025 20:57:00 | Generator failure at ARR0909-P2-USF_SRAN @ Generator_DG | 10/27/2025 08:48:19 | Minor | 65114 | Generator failure | 10/27/2025 08:46:32 | P2 | SRAN | arar | Generator_DG | 2G NSA | ARR0909 | FLM_EM | [8 empty] | API | 10/27/2025 08:57:00 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low