## Full PCM History
Status | Task ID | Order ID | TT ID | TT Type | Region | Site ID | Site Name | Root Cause | Sub Cause | Action Taken | FME | Created At | Last Update | SLA | Title | Create Fault First Time Occured | Fault Level | Alarm ID | Alarm Name | Alarm Time | Priority | Access Type | Area | Power Type | Impact | Impact Site List | Initial Owner | Site Required Action | Linked Sites | Old PCM ID | Old Escalate Reason | Old Escalate Needed Action | Supplementary Information | Down Sites | Fault Recovery Time | Generated By | Dispatched | Delivered | Accept | Departed | Arrived | FME Request | Completed | User Action | Updated Owner | Resolved Owner | Escalated To | Skill | Sub Project | extra_description | pcm_status | canellation_reason | source_name | connectivity_level
Dispatched | CM20230917001143 | PCM-20230917-00001419 | TT-20230917-01525 | Reference_EM | Region_1 | HFSW2M4016 | HFSW2016 |  |  |  | Ali Mohamed | 09/17/2023 11:59:00 | 11/20/2023 15:45:52 | 09/17/2023 15:59:00 | 1(2G/3G/LTE) sites down under HFSW2016-P1-HUB/HF1RNCH01(Ref:TT-20230814-03428) @ Generator_SG | 03/17/2023 07:07:38 | Critical | 301 | NE Is Disconnected | 03/17/2023 07:07:36 | P3 | 3G | hafouf | Generator_SG | 2G_3G_LTE SA | HFSW2016 | FLM_EM | [6 empty] | sites down |  | API | 09/17/2023 11:59:00 | [7 empty] | Force_Majeure |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20240123000727 | PCM-20240123-00000967 | TT-20240123-01204 | MW_HC | Region_6 | RYAB0632 | RYAB0632 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | KAMRAN LIAQAT | 01/23/2024 11:27:07 | 02/26/2024 22:23:15 | 01/23/2024 23:27:07 | As per BO request NEC MW link RYAB0632-RYAB0631 | 01/23/2024 10:24:36 | Minor | 113388 | LOF | 01/23/2024 11:24:42 | P1 | 2G | wadi dawasar | Generator_SG | TX NSA | RYAB0632-RYAB0631 | FLM_TE | [8 empty] | API | 01/23/2024 11:27:07 | 02/26/2024 12:06:13 | 02/26/2024 22:22:33 |  |  | 02/26/2024 22:23:15 |  | KAMRAN LIAQAT | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20240204000594 | PCM-20240204-00000743 | TT-20240204-00969 | Telecom | Region_4 | JED3W6091 | JED3W6091 |  |  |  | Ali Mohamed | 02/04/2024 10:48:45 | 02/19/2024 13:15:32 | 02/04/2024 16:48:45 | switch and 2 APs down at Site JED3W6091 | 02/04/2024 10:05:38 | Major | 987654321 | Complaint-No WO VAS | 02/04/2024 10:05:38 | P3 | WIFI | jeddah | Sceco | Wifi SA | switch and 2 APs down at Site JED3W6091 | FLM_TE |  |  | PCM-20240204-00000645 | switch and 2 APs down at Site JED3W6091 , FLM has to check locally | switch and 2 APs down at Site JED3W6091 , FLM has to check locally |  |  |  | API | 02/04/2024 10:48:45 | [7 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20240311000998 | PCM-20240311-00001275 | TT-20240311-01520 | Reference_telecom | Region_2 | RIY2436 | RIY2436 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Junaid Eisa | 03/11/2024 15:07:38 | 03/18/2024 10:38:46 | 03/12/2024 03:07:38 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY2436_NE_1 | 03/04/2024 13:47:54 | Minor |  | LOF | 03/04/2024 13:47:54 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2436_NE_1 | FLM_TE | [8 empty] | API | 03/11/2024 15:07:38 | [6 empty] | Mubashar Farooq Abdul Majeed | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20240407001049 | PCM-20240407-00001408 | TT-20240407-01485 | MW_HC | Region_2 | RIY2638 | RIY2638 | Transsmission | MW_RSL_fading | Link Alignment Issue | Junaid Eisa | 04/07/2024 13:23:00 | 04/22/2024 18:53:27 | 04/08/2024 01:23:00 | Observed AM_DOWNSHIFT and PM errors on MW link RIY2638 <> RIY0662 ( As per BO request ) | 04/07/2024 13:22:09 | Minor | 1-631 | MW_LOF | 04/07/2024 13:22:09 | P3 | SRAN | riyadh | Sceco | TX NSA | RIY2638 RIY0662 | FLM_TE | [5 empty] | Observed AM_DOWNSHIFT and PM errors on MW link RIY2638 <> RIY0662 ( As per BO request ) |  |  | API | 04/07/2024 13:23:00 | [6 empty] | Ali Raza Abdi Syed Muhammad Taqi Abdi | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20240505000657 | PCM-20240505-00000979 | TT-20240505-01045 | EM | Region_1 | LDAM0006 | LDAM0006 |  |  |  | Gamal Hasan Farag Ali Khalifa | 05/05/2024 08:17:21 | 06/02/2024 15:14:30 | 05/05/2024 14:17:21 | 1(3G/LTE) sites down under LDAM0006-P3/DM1RNC01 @ Sceco | 05/05/2024 07:00:53 | Major | 22214 | NodeB Unavailable | 05/05/2024 07:00:45 | P3 | SRAN | dammam | Sceco | 3G_LTE SA | LDAM0006-P3 | FLM_EM | LDAM0006 | kindly check site locally cause no issue observed from our side. | PCM-20240505-00000943 | kindly check site locally cause no issue observed from our side. | kindly check site locally cause no issue observed from our side. |  | sites down |  | API | 05/05/2024 08:17:21 | 05/05/2024 16:35:39 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20240708000269 | PCM-20240708-00000385 | TT-20240708-00418 | Reference_telecom | Region_2 | RIY0228 | RIY0228 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ali Raza Abdi Syed Muhammad Taqi Abdi | 07/08/2024 02:24:28 | 08/13/2024 20:02:38 | 07/08/2024 14:24:28 | MW RTN Observing IF_CABLE_OPEN,RADIO_RSL_LOW,PLA_DOWN,PLA_MEMBER_DO at RIY0228_NE_5 | 09/07/2023 02:30:32 | Minor |  | LOF | 09/07/2023 02:30:32 | VIP | SRAN | riyadh | Generator_DG | TX NSA | RIY0228_NE_5 | FLM_TE | [8 empty] | API | 07/08/2024 02:24:28 | 08/06/2024 13:11:51 | 08/13/2024 20:02:23 |  |  | 08/13/2024 20:02:38 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20240710001763 | PCM-20240710-00002101 | TT-20240710-02278 | Reference_telecom | Region_2 | RIY0891 | RIY0891 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Junaid Eisa | 07/10/2024 16:25:44 | 08/12/2024 14:29:37 | 07/11/2024 04:25:44 | MW RTN Observing NB_UNREACHABLE,PORT_MODULE_OFFLINE at RIY0891_NE_5_H | 04/06/2024 07:52:42 | Minor |  | LOF | 04/06/2024 07:52:42 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0891_NE_5_H | FLM_TE | [8 empty] | API | 07/10/2024 16:25:44 | [6 empty] | Farmanullah Akbar Jan | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20240714001132 | PCM-20240714-00001500 | TT-20240714-01631 | Telecom | Region_6 | MHL9722 | MHL9722 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Muhammad Jamal Khan Abbas Ali | 07/14/2024 14:37:17 | 10/14/2024 02:06:30 | 07/15/2024 02:37:17 | ODU CPU / Cable Open at MHL9722 on 10.157.250.23 @ Generator_SG | 07/14/2024 14:36:19 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 07/14/2024 14:25:33 | P3 | Repeater | mohail | Generator_SG | TX NSA | MHL9722 | FLM_TE | [8 empty] | API | 07/14/2024 14:37:17 | 07/14/2024 16:08:57 | 10/14/2024 02:06:12 |  |  | 10/14/2024 02:06:30 |  | Muhammad Jamal Khan Abbas Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20240717001290 | PCM-20240717-00001612 | TT-20240717-01832 | Reference_telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Medhat Medhat Mostafa Abdelkader | 07/17/2024 16:03:56 | 08/06/2024 11:52:58 | 07/17/2024 22:03:56 | DCU CPRI Interface Error, RF Unit CPRI Interface Error, FPGA Processing Error at DAM6027 (REF: TT-20240606-01958) | 06/06/2024 20:05:26 | Major | 26234 | DCU CPRI Interface Error | 06/06/2024 20:05:26 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE |  |  | PCM-20240717-00001592 | Need to check many HW alarms DCU CPRI Interface Error, RF Unit CPRI Interface Error, FPGA Processing error at DAM6027-DCU1 & DAM6027-DCU3 | Need to check many HW alarms DCU CPRI Interface Error, RF Unit CPRI Interface Error, FPGA Processing error at DAM6027-DCU1 & DAM6027-DCU3 |  |  |  | API | 07/17/2024 16:03:56 | 07/17/2024 16:35:19 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20240723001066 | PCM-20240723-00001426 | TT-20240723-01624 | Telecom | Region_1 | DMHF0080 | DMHF0080 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SARFARAZ MUHAMMAD HUSSAIN | 07/23/2024 13:58:19 | 09/03/2024 05:01:42 | 07/24/2024 01:58:19 | ODU CPU / Cable Open at DMHF0080-2 on 10.74.77.23 @ Generator_SG | 07/23/2024 13:57:32 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 07/23/2024 13:56:33 | P1 | SRAN | dammam | Generator_SG | TX NSA | DMHF0080 | FLM_TE | [8 empty] | API | 07/23/2024 13:58:19 | 07/23/2024 14:18:12 | 09/03/2024 05:01:02 |  |  | 09/03/2024 05:01:42 |  | SARFARAZ MUHAMMAD HUSSAIN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20240728001197 | PCM-20240728-00001592 | TT-20240728-01589 | MW_HC | Region_1 | UQR2313 | UQR2313 |  |  |  | Junaid Eisa | 07/28/2024 15:15:38 | 08/15/2024 05:52:15 | 07/29/2024 03:15:38 | Observed PM errors on NEC MW link UQR2313(10.74.77.16)-QRH2433(10.74.77.15) ( As per BO request ) | 07/28/2024 15:14:53 | Minor | 1-631 | MW_LOF | 07/28/2024 15:14:53 | P3 | SRAN | dammam | Sceco | TX NSA | UQR2313(10.74.77.16) QRH2433(10.74.77.15) | FLM_TE | [5 empty] | Observed PM errors on NEC MW link UQR2313(10.74.77.16)-QRH2433(10.74.77.15) ( As per BO request ) |  |  | API | 07/28/2024 15:15:38 | [7 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20240806001630 | PCM-20240806-00002081 | TT-20240806-02338 | Reference_telecom | Region_2 | RYQ2M1972 | RYQ0972 | Enviroment | SCECO_Failure | SCECO auto restored | Hakim Ullah Raif Ullah Jan | 08/06/2024 16:43:30 | 12/15/2024 08:33:27 | 08/06/2024 22:43:30 | 1 (2G) site down at RYQ2M1972-P3 Under RY1BSCH02 REF:TT-20240728-01705 @ Sceco | 07/31/2024 02:09:42 | Major | 21825 | CSL Fault | 05/16/2024 01:00:02 | P3 | 2G | majma | Sceco | 2G SA | RYQ2M1972 | FLM_TE |  |  | PCM-20240806-00002059 | telecom issue | telecom issue |  | site down |  | API | 08/06/2024 16:43:30 | 08/07/2024 12:50:36 | 12/15/2024 08:32:20 |  |  | 12/15/2024 08:33:27 |  | Hakim Ullah Raif Ullah Jan | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20240813000018 | PCM-20240813-00000019 | TT-20240813-00017 | Telecom | Region_2 | RIYB6005 | RIYB6005 | Equipment | SFP_BTS | Clean SFP | Mudesir Iqbal Allah Bakhsh | 08/13/2024 00:05:23 | 09/16/2024 20:21:04 | 08/13/2024 06:05:23 | BBU CPRI Interface Error at RIYB6005-P1-SHOP_SRAN @ Sceco | 08/13/2024 00:03:34 | Major | 26234 | BBU CPRI Interface Error | 06/25/2024 01:28:26 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYB6005 | FLM_TE | [8 empty] | API | 08/13/2024 00:05:23 | 08/13/2024 11:15:16 | 09/15/2024 10:36:04 |  |  | 09/16/2024 20:21:04 |  | Mudesir Iqbal Allah Bakhsh | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20240813000036 | PCM-20240813-00000038 | TT-20240813-00039 | Telecom | Region_1 | KBR2U6315 | KBR6015 |  |  |  | Medhat Medhat Mostafa Abdelkader | 08/13/2024 00:06:23 | 09/08/2024 15:06:01 | 08/13/2024 12:06:23 | RF Unit Maintenance Link Failure at KBR2U6315-P3 @ Sceco | 08/13/2024 00:04:31 | Minor | 26235 | RF Unit Maintenance Link Failure | 04/14/2024 14:22:02 | P3 | 3G | dammam | Sceco | 3G NSA | KBR2U6315 | FLM_TE | [8 empty] | API | 08/13/2024 00:06:23 | 08/13/2024 01:45:03 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20240825000857 | PCM-20240825-00001172 | TT-20240825-01203 | Telecom | Region_4 | JED3W6085 | JED3W6085 |  |  |  | Muhammad Salman Muhammad Pervez | 08/25/2024 10:24:48 | 09/04/2024 11:16:45 | 08/25/2024 22:24:48 | AP Down at Site JED3W6085 | 08/25/2024 10:12:00 | Minor | 676767675 | Health Check-WO to TE FME | 08/25/2024 10:12:00 | P3 | WIFI | jeddah | Sceco | Wifi SA | AP Down at Site JED3W6085 | FLM_TE |  |  | PCM-20240825-00001139 | please arrange FLM to the Site to check locally | please arrange FLM to the Site to check locally |  |  |  | API | 08/25/2024 10:24:48 | 08/26/2024 10:59:06 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20240903002245 | PCM-20240903-00002979 | TT-20240903-03343 | Reference_telecom | Region_2 | RIY0139 | RIY0139 |  |  |  | Khan zeb Shah nawaz | 09/03/2024 19:09:18 | 09/29/2024 22:10:06 | 09/04/2024 07:09:18 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0139_NE_6_FON | 04/18/2024 09:35:00 | Minor |  | LOF | 04/18/2024 09:35:00 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0139_NE_6_FON | FLM_TE | [8 empty] | API | 09/03/2024 19:09:18 | 09/04/2024 11:13:28 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20241030001362 | PCM-20241030-00001812 | TT-20241030-01842 | Reference_telecom | Region_2 | RIY2682 | RIY2682 |  |  |  | Junaid Eisa | 10/30/2024 14:17:33 | 11/13/2024 11:09:34 | 10/31/2024 02:17:33 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RIY2682_NE_1_V | 08/09/2024 10:58:36 | Minor |  | LOF | 08/09/2024 10:58:36 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2682_NE_1_V | FLM_TE | [8 empty] | API | 10/30/2024 14:17:33 | [7 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20241120000686 | PCM-20241120-00000926 | TT-20241120-01240 | Telecom | Region_1 | KBR6055 | KBR6055 |  |  |  | Medhat Medhat Mostafa Abdelkader | 11/20/2024 11:42:48 | 11/26/2024 13:12:10 | 11/20/2024 23:42:48 | DCU Optical Module Transmit/Receive Fault at KBR6055-DCU1 @ Sceco | 11/20/2024 11:29:50 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 11/20/2024 11:37:20 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6055 | FLM_TE | [8 empty] | API | 11/20/2024 11:42:48 | 11/20/2024 12:54:16 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20241203001042 | PCM-20241203-00001451 | TT-20241203-01652 | Reference_telecom | Region_1 | RAF2587 | RAF2587 |  |  |  | Junaid Eisa | 12/03/2024 15:18:59 | 12/16/2024 06:26:03 | 12/04/2024 03:18:59 | MW RTN Observing PG_LINK_FAIL,PG_LINK_FAIL,PG_LINK_FAIL,PG_LINK_FAI at RAF2587_NE_1_VRRP | 12/02/2024 22:46:23 | Minor |  | LOF | 12/02/2024 22:46:23 | P1 | SRAN | rafha | Sceco_STB | TX NSA | RAF2587_NE_1_VRRP | FLM_TE | [8 empty] | API | 12/03/2024 15:18:59 | [7 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20241203001052 | PCM-20241203-00001460 | TT-20241203-01662 | Reference_telecom | Region_1 | RAF2514 | RAF2514 | Transsmission | MW_HW_fault | Replace IF Cable | Junaid Eisa | 12/03/2024 15:19:09 | 12/16/2024 06:26:56 | 12/04/2024 03:19:09 | MW RTN Observing IF_CABLE_OPEN,IF_CABLE_OPEN,BD_STATUS,BD_STATUS,XP at RAF2514_NE_2 | 12/02/2024 22:46:13 | Minor |  | LOF | 12/02/2024 22:46:13 | P1 | SRAN | rafha | Generator_DG | TX NSA | RAF2514_NE_2 | FLM_TE | [8 empty] | API | 12/03/2024 15:19:09 | [6 empty] | Almmoez Almmoez | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20241212000556 | PCM-20241212-00000740 | TT-20241212-00976 | Telecom | Region_4 | JED3W6085 | JED3W6085 |  |  |  | Muhammad Salman Muhammad Pervez | 12/12/2024 09:32:37 | 12/26/2024 16:07:06 | 12/12/2024 15:32:37 | Switch and 4 APs down at Site JED3W6085 | 12/12/2024 09:23:29 | Major | 987654321 | Complaint-No WO VAS | 12/12/2024 09:23:29 | P3 | WIFI | jeddah | Sceco | Wifi SA | Switch and 4 APs down at Site JED3W6085 | FLM_TE |  |  | PCM-20241212-00000725 | please arrange FLM to the Site to check locally | please arrange FLM to the Site to check locally |  |  |  | API | 12/12/2024 09:32:37 | 12/14/2024 21:10:50 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20241213000102 | PCM-20241213-00000124 | TT-20241213-00129 | Reference_telecom | Region_6 | BAH0004 | BAH0004 | Transsmission | MW_Problematic | Interference Issue | Junaid Eisa | 12/13/2024 01:45:10 | 12/20/2024 04:47:40 | 12/13/2024 13:45:10 | NEC MW Observing XIF,MODEM Power Supply Alarm,MODEM Power Supply Alarm,LOF,XIF at BAH0004-BAH00017(10.154.175.99) | 04/03/2024 10:13:30 | Minor |  | LOF | 04/03/2024 10:13:30 | P2 | 2G | Albaha | Sceco | TX NSA | BAH0004-BAH00017(10.154.175.99) | FLM_TE | [8 empty] | API | 12/13/2024 01:45:10 | [6 empty] | SHAH KHALID | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20241216001215 | PCM-20241216-00001616 | TT-20241216-01824 | Telecom | Region_4 | JED3W6091 | JED3W6091 |  |  |  | Muhammad Salman Muhammad Pervez | 12/16/2024 17:04:04 | 12/26/2024 16:07:11 | 12/16/2024 21:04:04 | Complete Site JED3W6091 Down | 12/16/2024 17:00:09 | Critical | 676767675 | Health Check-WO to TE FME | 12/16/2024 17:00:09 | P3 | WIFI | jeddah | Sceco | Wifi SA | Complete Site JED3W6091 Down | FLM_TE |  |  | PCM-20241216-00001609 | Complete Site is down , please arrange FLM to the Site to check locally | Complete Site is down , please arrange FLM to the Site to check locally |  |  |  | API | 12/16/2024 17:04:04 | 12/17/2024 14:22:36 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20241218001158 | PCM-20241218-00001815 | TT-20241218-02259 | Reference_telecom | Region_1 | URY9011 | URY9011 |  |  |  | Shakeel Ahmed Hafeez Ameen | 12/18/2024 17:35:48 | 12/28/2024 14:10:45 | 12/19/2024 05:35:48 | MW RTN Observing PG_LINK_FAIL,PLA_MEMBER_DOWN_EXT at URY9011_NE_2_VRRP | 12/09/2024 04:13:50 | Minor |  | LOF | 12/09/2024 04:13:50 | P3 | Repeater | dammam | Sceco | TX NSA | URY9011_NE_2_VRRP | FLM_TE | [8 empty] | API | 12/18/2024 17:35:48 | 12/18/2024 21:17:18 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20241219000982 | PCM-20241219-00001601 | TT-20241219-01782 | Telecom | Region_2 | RIY0822 | RIY0822 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Waseem Shahzad Ghulam Rasool | 12/19/2024 15:07:45 | 02/16/2025 16:22:15 | 12/19/2024 21:07:45 | MW_ Router MW_ RIY0822 to HQ-RIYB6117-LL-CSG-01 _ ISIS Adjacency changed | 12/19/2024 14:47:43 | Major | 2738181 | Link down flapping | 12/19/2024 14:47:43 | P1 | SRAN | riyadh | Sceco | IPRAN NSA | MW_ Router MW_ RIY0822 to HQ-RIYB6117-LL-CSG-01 _ ISIS Adjacency changed | FLM_TE | RIY0822 | We are observing MW_RDI & PLA_MEMBER_DOWN_EXT alarms flapping at MW link RIYB6117 dir RIY0822 | PCM-20241219-00001587 | We are observing MW_RDI & PLA_MEMBER_DOWN_EXT alarms flapping at MW link RIYB6117 dir RIY0822 | We are observing MW_RDI & PLA_MEMBER_DOWN_EXT alarms flapping at MW link RIYB6117 dir RIY0822 |  |  |  | API | 12/19/2024 15:07:45 | 02/16/2025 16:18:24 | 02/16/2025 16:22:06 |  |  | 02/16/2025 16:22:15 |  | Waseem Shahzad Ghulam Rasool | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20241222000440 | PCM-20241222-00000745 | TT-20241222-01024 | MW_HC | Region_4 | JED0803 | JED0803 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | MALIK ATIF ZAMAN | 12/22/2024 08:15:06 | 04/21/2025 15:48:20 | 12/22/2024 20:15:06 | As per BO request NOKIA MW link JED0803-JED6154 | 12/22/2024 08:13:54 | Minor | 113388 | LOF | 12/22/2024 08:13:56 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED0803-JED6154 | FLM_TE | [8 empty] | API | 12/22/2024 08:15:06 | 12/22/2024 11:55:42 | 04/21/2025 12:47:13 | 04/21/2025 12:47:30 | 04/21/2025 13:28:56 | 04/21/2025 15:48:20 |  | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20241224000756 | PCM-20241224-00001022 | TT-20241224-01325 | Reference_telecom | Region_1 | HFF6031 | HFF6031 |  |  |  | Fahim Waxir | 12/24/2024 13:06:12 | 12/28/2024 14:10:49 | 12/25/2024 01:06:12 | RF Unit Maintenance Link Failure at HFF6031-DCU4(Ref::TT-20220828-00969) @ Sceco | 08/28/2022 14:13:50 | Minor | 26235 | RF Unit Maintenance Link Failure | 08/28/2022 14:15:29 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6031 | FLM_TE | [8 empty] | API | 12/24/2024 13:06:12 | 12/24/2024 14:15:04 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20241229000083 | PCM-20241229-00000110 | TT-20241229-00120 | Telecom | Region_1 | HFSW2M2019 | HFSW2019 |  |  |  | Fahim Waxir | 12/29/2024 01:11:58 | 01/03/2025 18:55:56 | 12/29/2024 13:11:58 | NEC As per Visibility report observing Visibility issue at 3 NE under HFSW0019 need check from HFSW0019-1 at 10.248.32.136 | 12/29/2024 01:07:57 | Minor | 2 | NE_NOT_LOGIN | 12/29/2024 01:07:57 | P1 | 2G | hafouf | Generator_SG | TX NSA | HFSW0016-2 10.248.32.135 HFSW0016-1 10.248.32.134 HFSW0019-1 10.248.32.136 | FLM_TE | [5 empty] | NEC As per Visibility report observing Visibility issue at 3 NE under HFSW0019 need check from HFSW0019-1 at 10.248.32.136 |  |  | API | 12/29/2024 01:11:58 | 12/29/2024 11:21:36 | [6 empty] | Force_Majeure |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20241229001272 | PCM-20241229-00001744 | TT-20241229-01884 | Reference_telecom | Region_2 | RIY0639 | RIY0639 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Noman Noman Mazhar Hussain | 12/29/2024 18:08:54 | 07/15/2025 09:40:33 | 12/30/2024 06:08:54 | MW RTN Observing MW_LOF,RADIO_RSL_LOW at RIY0639_NE_17_H | 08/25/2024 10:22:31 | Minor |  | LOF | 08/25/2024 10:22:31 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0639_NE_17_H | FLM_TE | [8 empty] | API | 12/29/2024 18:08:54 | 01/13/2025 09:24:18 | 07/15/2025 09:40:20 | 07/15/2025 09:40:23 |  | 07/15/2025 09:40:33 |  | Noman Noman Mazhar Hussain | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250107001366 | PCM-20250107-00001801 | TT-20250107-01906 | Telecom | Region_1 | HFF6030 | HFF6030 |  |  |  | Fahim Waxir | 01/07/2025 13:10:35 | 01/15/2025 08:58:01 | 01/08/2025 01:10:35 | FPGA Processing Error at HFF6030-DCU3 @ Sceco | 01/06/2025 15:17:02 | Minor | 29801 | FPGA Processing Error | 01/06/2025 15:20:10 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6030 | FLM_TE | [8 empty] | API | 01/07/2025 13:10:35 | 01/07/2025 17:47:55 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250117000702 | PCM-20250117-00000935 | TT-20250117-00900 | Telecom | Region_3 | YNB3W6021 | YNB3W6021 |  |  |  | Muhammad Sajjad R3 | 01/17/2025 16:57:22 | 02/01/2025 14:46:19 | 01/18/2025 04:57:22 | AP Down at Site YNB3W6021 | 01/17/2025 15:11:10 | Minor | 676767675 | Health Check-WO to TE FME | 01/17/2025 15:11:10 | P2 | WIFI | yanbu | Sceco | Wifi SA | YNB3W6021 | FLM_TE |  |  | PCM-20250117-00000802 | Please arrange FLM to the SIte to check AP connection | Please arrange FLM to the SIte to check AP connection |  |  |  | API | 01/17/2025 16:57:22 | 01/18/2025 11:50:15 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250119000964 | PCM-20250119-00001420 | TT-20250119-01438 | Reference_telecom | Region_1 | RST0351 | RST0351 |  |  |  | Junaid Eisa | 01/19/2025 13:39:59 | 01/24/2025 07:30:03 | 01/20/2025 01:39:59 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RST0351_NE_1_V | 01/14/2025 13:42:38 | Minor |  | LOF | 01/14/2025 13:42:38 | P1 | SRAN | jubail | Sceco | TX NSA | RST0351_NE_1_V | FLM_TE | [8 empty] | API | 01/19/2025 13:39:59 | [7 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250119000971 | PCM-20250119-00001427 | TT-20250119-01445 | Reference_telecom | Region_1 | RST0089 | RST0089 |  |  |  | Junaid Eisa | 01/19/2025 13:40:18 | 01/24/2025 07:31:08 | 01/20/2025 01:40:18 | MW RTN Observing MW_BER_SD at RST0089_NE_5_H | 01/14/2025 13:42:18 | Minor |  | LOF | 01/14/2025 13:42:18 | P3 | SRAN | jubail | Sceco | TX NSA | RST0089_NE_5_H | FLM_TE | [8 empty] | API | 01/19/2025 13:40:18 | [7 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250122000471 | PCM-20250122-00000620 | TT-20250122-00832 | Reference_telecom | Region_2 | WRIY0030 | WRIY0030 |  |  |  | Abdelrahim Abdalla Abdelrahim Khairy | 01/22/2025 07:48:13 | 03/08/2025 21:48:56 | 01/22/2025 19:48:13 | WRIY0030 Complete down | 01/22/2025 07:23:42 | Minor | 613007 | Wi-Fi AP Out Of Service | 01/22/2025 07:23:42 | P3 | WIFI | riyadh | Sceco | Wifi SA | WRIY0030 | FLM_TE | WRIY0030 | We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20250122-00000612 | We are not observing any issue at TX end. Kindly visit the site and check issue locally | We are not observing any issue at TX end. Kindly visit the site and check issue locally |  |  |  | API | 01/22/2025 07:48:13 | 03/08/2025 21:48:56 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20250127000469 | PCM-20250127-00000629 | TT-20250127-00335 | Telecom | [7 empty] | 01/27/2025 07:13:10 | 01/27/2025 07:13:10 | 01/27/2025 19:13:10 | Dust Net Clean Alarm at JBL-3322-NE40E-X8-P&PE-01 @ Sceco_STB | 01/27/2025 03:25:05 | Minor | 101-3067995 | Dust Net Clean Alarm | 01/27/2025 03:25:02 | P1 | IPRAN |  | Sceco_STB | IPRAN NSA | JBL-3322-NE40E-X8-P&PE-01 | FLM_EM |  |  | PCM-20250127-00000304 | Please check. | Please check. |  |  |  | API | 01/27/2025 07:13:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20250127000470 | PCM-20250127-00000630 | TT-20250127-00469 | Telecom | [7 empty] | 01/27/2025 07:13:23 | 01/27/2025 07:13:23 | 01/27/2025 19:13:23 | Dust Net Clean Alarm at JBL-3322-NE40E-X8-P&PE-02 @ Sceco_STB | 01/27/2025 04:37:34 | Minor | 101-3067995 | Dust Net Clean Alarm | 01/27/2025 04:37:30 | P1 | IPRAN |  | Sceco_STB | IPRAN NSA | JBL-3322-NE40E-X8-P&PE-02 | FLM_EM |  |  | PCM-20250127-00000431 | Please check. | Please check. |  |  |  | API | 01/27/2025 07:13:23 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250130000677 | PCM-20250130-00000937 | TT-20250130-00979 | Telecom | Region_3 | WMDN0002 | WMDN0002 | Enviroment | SCECO_Failure | SCECO auto restored | Ibrahim Mohammad AbdulMalik alraee | 01/30/2025 11:42:31 | 09/21/2025 19:13:20 | 01/30/2025 23:42:31 | WMDN0002 Complete down | 01/30/2025 11:14:00 | Minor | 613007 | Wi-Fi AP Out Of Service | 01/30/2025 11:14:00 | P3 | WIFI | madinah | Sceco | Wifi SA | WMDN0002 | FLM_TE | WMDN0002 | No TXN. Issue kindly check site locally. | PCM-20250130-00000880 | No TXN. Issue kindly check site locally. | No TXN. Issue kindly check site locally. |  |  |  | API | 01/30/2025 11:42:31 | 09/21/2025 18:53:38 | 09/21/2025 19:13:10 |  |  | 09/21/2025 19:13:20 |  | Ibrahim Mohammad AbdulMalik alraee | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250203000492 | PCM-20250203-00000664 | TT-20250129-01983 | Reference_telecom | Region_4 | TF1 | TF1 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 02/03/2025 10:37:32 | 03/25/2025 12:54:19 | 02/03/2025 16:37:32 | 185(3G) 463 (LTE) sites down under Region_3 REF: TT-20250129-01658 | 01/29/2025 17:01:00 | Major | 301 | NE Is Disconnected | 01/29/2025 17:01:00 | P1 | BSC | taif | Sceco_STB | 3G_LTE SA | find attachment | FLM_EM | TF1 | under same case DWDM TT-20250129-01556 | PCM-20250202-00001953 | under same case DWDM TT-20250129-01556 | under same case DWDM TT-20250129-01556 |  | sites down |  | API | 02/03/2025 10:37:32 | 02/03/2025 12:59:30 | 03/24/2025 16:05:00 |  |  | 03/24/2025 16:05:07 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250204000436 | PCM-20250204-00000617 | TT-20250204-00620 | Telecom | Region_1 | HFF2359 | HFF2359 | Equipment | PMR_Power_Cable_RRU | Replace Outdoor Power Connector | Mohamed Magdy Fouad Zayed | 02/04/2025 07:59:09 | 02/19/2025 09:51:35 | 02/04/2025 13:59:09 | RF Unit Maintenance Link Failure at HFF2359-P2_SRAN | 02/04/2025 04:26:01 | Major | 26235 | RF Unit Maintenance Link Failure | 02/04/2025 04:26:01 | P2 | SRAN | hafouf | Sceco | 2G_3G_LTE SA | HFF2359 | FLM_TE | [8 empty] | API | 02/04/2025 07:59:09 | 02/04/2025 14:05:19 | 02/19/2025 09:51:16 |  |  | 02/19/2025 09:51:35 |  | Mohamed Magdy Fouad Zayed | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250206001241 | PCM-20250206-00001642 | TT-20250206-01729 | Reference_telecom | Region_6 | BLG0039 | BLG0039 | Transsmission | CB_MW | Replace CB on Rectifier | Muhammad Ali | 02/06/2025 17:31:55 | 04/04/2025 00:07:46 | 02/07/2025 05:31:55 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Port 1/1 at BLG0039-10.89.249.122 | 08/03/2023 10:21:09 | Minor |  | LOF | 08/03/2023 10:21:09 | P2 | 2G | jizan | Sceco | TX NSA | BLG0039-10.89.249.122 | FLM_TE | [8 empty] | API | 02/06/2025 17:31:55 | 02/06/2025 19:33:23 | 04/04/2025 00:07:09 |  |  | 04/04/2025 00:07:46 |  | Muhammad Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250209000923 | PCM-20250209-00001456 | TT-20250209-01378 | Reference_telecom | Region_6 | RTH0601 | RTH0601 | Transsmission | CB_MW | Replace CB on Rectifier | Muhammad Ali | 02/09/2025 12:44:51 | 04/04/2025 00:08:19 | 02/10/2025 00:44:51 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Port 1/1 at RTH0601-10.89.249.114 | 04/21/2024 18:26:29 | Minor |  | LOF | 04/21/2024 18:26:29 | P2 | 2G | raith | Generator_SG | TX NSA | RTH0601-10.89.249.114 | FLM_TE | [8 empty] | API | 02/09/2025 12:44:51 | 02/09/2025 14:23:19 | 04/04/2025 00:08:00 |  |  | 04/04/2025 00:08:19 |  | Muhammad Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250221000843 | PCM-20250221-00000930 | TT-20250221-01041 | Reference_telecom | Region_1 | RST0351 | RST0351 |  |  |  | Rafiq Ahmed Elturifi | 02/21/2025 06:48:58 | 02/25/2025 14:07:56 | 02/21/2025 18:48:58 | RTN As per Visibility report observing Visibility issue at 1 NE under RST0351_NE_2_H due to power issue from RST0351_NE_2_H | 02/18/2025 17:19:23 | Minor | 2 | NE_NOT_LOGIN | 02/18/2025 17:19:23 | P1 | SRAN | jubail | Sceco | TX NSA | RST0351_NE_2_H | FLM_TE | [5 empty] | RTN As per Visibility report observing Visibility issue at 1 NE under RST0351_NE_2_H due to power issue from RST0351_NE_2_H |  |  | API | 02/21/2025 06:48:58 | 02/21/2025 10:11:16 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250226001106 | PCM-20250226-00001509 | TT-20250226-01665 | Reference_telecom | Region_4 | JED0380 | JED0380 |  |  |  | Mohammed Ramadan A Abu Abid | 02/26/2025 17:56:49 | 06/01/2025 01:59:27 | 02/27/2025 05:56:49 | Nokia Eband Observing LagPortDown-Port 4/5,Degrade-LAG 1 at JED0380_04-10.10.138.182 | 01/15/2025 06:39:16 | Minor |  | LOF | 01/15/2025 06:39:16 | P3 | 2G | jeddah | Sceco | TX NSA | JED0380_04-10.10.138.182 | FLM_TE | [8 empty] | API | 02/26/2025 17:56:49 | 02/26/2025 18:49:50 | 06/01/2025 01:59:27 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250302000006 | PCM-20250302-00000006 | TT-20250228-01477 | Reference_telecom | Region_1 | KFJ0483 | KFJ0483 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SARFARAZ MUHAMMAD HUSSAIN | 03/02/2025 00:07:24 | 04/28/2025 05:48:58 | 03/02/2025 12:07:24 | MW RTN Observing PLA_PKT_ERR at KFJ0483_NE_3_SDB | 02/23/2025 02:19:28 | Minor |  | LOF | 02/23/2025 02:19:28 | P2 | SRAN | khafji | Sceco | TX NSA | KFJ0483_NE_3_SDB | FLM_TE |  |  | PCM-20250301-00001216 | Dear FLM need HC on link KFJ0483,KFJ2003 as PM ERR observed | Dear FLM need HC on link KFJ0483,KFJ2003 as PM ERR observed |  |  |  | API | 03/02/2025 00:07:24 | 03/09/2025 22:03:49 | 04/28/2025 05:47:14 |  |  | 04/28/2025 05:48:58 |  | SARFARAZ MUHAMMAD HUSSAIN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250308000202 | PCM-20250308-00000268 | TT-20250308-00272 | Reference_EM | Region_1 | SAK2184 | SAK2184 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Mohamed Amjad Muhammad | 03/08/2025 04:21:57 | 03/12/2025 11:04:25 | 03/08/2025 16:21:57 | Air condition 1 failure alarm at SAK2184-P2_SRAN @ Sceco | 03/08/2025 04:11:35 | Minor | 65104 | Air condition 1 failure alarm | 03/08/2025 04:11:33 | P2 | SRAN | sakaka | Sceco | 2G NSA | SAK2184 | FLM_EM | [8 empty] | API | 03/08/2025 04:21:57 | 03/12/2025 11:01:55 | 03/12/2025 11:03:48 |  |  | 03/12/2025 11:04:25 |  | Mohamed Amjad Muhammad | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20250318001308 | PCM-20250318-00001840 | TT-20250318-01423 | Telecom | Region_4 | JED3W6086 | JED3W6086 |  |  |  | Muhammad Salman Muhammad Pervez | 03/18/2025 19:46:45 | 04/09/2025 00:09:47 | 03/19/2025 07:46:45 | Site JED3W6086 partial Down | 03/18/2025 15:00:44 | Minor | 987654321 | Complaint-No WO VAS | 03/18/2025 15:00:44 | P3 | WIFI | jeddah | Sceco | Wifi SA | Site JED3W6086 partial Down | FLM_TE |  |  | PCM-20250318-00001353 | Please arrange FLM to the Site to check AP connection and remade the Connectors AP Sides Cable on port gi10 is open at 0 m AP name : JED3W6086_1-3F-AP10 Mac address: 18:8b:9d:be:f6:d8 | Please arrange FLM to the Site to check AP connection and remade the Connectors AP Sides Cable on port gi10 is open at 0 m AP name : JED3W6086_1-3F-AP10 Mac address: 18:8b:9d:be:f6:d8 |  |  |  | API | 03/18/2025 19:46:45 | [7 empty] | NSN_Care |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250320001643 | PCM-20250320-00002376 | TT-20250320-02364 | Reference_telecom | Region_3 | HLMD0685 | HLMD0685 | Equipment | SFP_BTS | Replace SFP | Ali Mohamed | 03/20/2025 20:48:19 | 04/03/2025 04:18:23 | 03/21/2025 02:48:19 | RF Unit Maintenance Link Failure at HLMD0685-P3_SRAN ref:TT-20250320-01457 01457 | 03/20/2025 13:25:40 | Major | 26218 | RF Unit Maintenance Link TLS Negotiation Failure | 03/20/2025 20:25:41 | P3 | SRAN | hail | Sceco | 2G_3G_5G SA | HLMD0685 | FLM_TE | [8 empty] | API | 03/20/2025 20:48:19 | [6 empty] | ADNAN FAROOQ | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250322000095 | PCM-20250322-00000159 | TT-20250322-00156 | Reference_telecom | Region_4 | JED1W6081 | JED6081 |  |  |  | Muhammad Salman Muhammad Pervez | 03/22/2025 02:26:28 | 04/09/2025 00:09:49 | 03/22/2025 14:26:28 | JED1W6081 Partial down | 03/22/2025 02:11:25 | Minor | 613007 | Wi-Fi AP Out Of Service | 03/22/2025 02:11:25 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_3-6F-AP04 | FLM_TE | [8 empty] | API | 03/22/2025 02:26:28 | [7 empty] | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250327001028 | PCM-20250327-00001389 | TT-20250327-01554 | Reference_telecom | Region_2 | RIY0131 | RIY0131 |  |  |  | Junaid Eisa | 03/27/2025 15:47:31 | 04/11/2025 00:48:36 | 03/28/2025 03:47:31 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0131_NE_2 | 11/10/2024 01:03:59 | Minor |  | LOF | 11/10/2024 01:03:59 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0131_NE_2 | FLM_TE | [8 empty] | API | 03/27/2025 15:47:31 | [7 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20250331000134 | PCM-20250331-00000197 | TT-20250331-00282 | Reference_telecom | Region_4 | TF1-ASG-02 | TF1 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 03/31/2025 05:10:51 | 04/10/2025 20:28:32 | 03/31/2025 17:10:51 | Optical Invalid at TF1-ASG-02 // TT-20250327-00341 @ Sceco_STB | 03/31/2025 03:58:32 | Minor | 101-2505224 | Optical Invalid | 03/31/2025 03:58:14 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | TF1-ASG-02 | FLM_TE | [8 empty] | API | 03/31/2025 05:10:51 | 04/01/2025 09:39:51 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250402001069 | PCM-20250402-00001407 | TT-20250402-01520 | Telecom | Region_1 | RST0352 | RST0352 |  |  |  | Rafiq Ahmed Elturifi | 04/02/2025 18:14:15 | 04/03/2025 01:18:32 | 04/03/2025 00:14:15 | SPAN_LOSS_EXCEED_EOL at RST0352 @ Sceco | 04/02/2025 18:10:09 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 04/02/2025 18:09:59 | P1 | SRAN | jubail | Sceco | DWDM NSA | RST0352 | FLM_TE | [5 empty] | 0-1-C-4-F1DSFIU-4(ELINE1/ELINE2(FROM DAM0353))-OTS:1 |  |  | API | 04/02/2025 18:14:15 | 04/03/2025 01:18:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250411000886 | PCM-20250411-00001212 | TT-20250411-01431 | Telecom | Region_4 | JED0008-ZJe04-CSG-06 | JED0008 | Transsmission | MW_HW_stuck | Reset IDU | Moustafa Mahmoud Ahmed Fathelbab | 04/11/2025 21:20:20 | 06/14/2025 11:32:45 | 04/12/2025 09:20:20 | MW_Link Down_at JED0008-ZJe04-CSG-06 to JD2-ASG-02, JED0211-ZJe04-CSG-04 | 04/11/2025 17:24:19 | Minor | 15269 | LOS | 04/11/2025 17:24:19 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0008 | FLM_TE |  |  | PCM-20250411-00001182 | Dear FLM team, Kindly perform HC for MW JED0813-JED2234 | Dear FLM team, Kindly perform HC for MW JED0813-JED2234 |  |  |  | API | 04/11/2025 21:20:20 | 04/12/2025 10:57:14 | 05/31/2025 13:12:42 | 05/31/2025 13:27:06 | 05/31/2025 13:27:08 | 06/14/2025 11:32:45 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250413000691 | PCM-20250413-00000992 | TT-20250413-01098 | Telecom | Region_4 | NNL0168 | NNL0168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Riasat Ali Allah Baksh | 04/13/2025 12:21:20 | 06/28/2025 23:04:00 | 04/13/2025 18:21:20 | MW_LINK DOWN at LTH0330-SF-CSG-01 TO TFBH9443-LL-CSG-01 @ Sceco_STB | 03/08/2025 01:20:46 | Major | 104-2600148 | LINK DOWN | 03/08/2025 01:20:37 | P3 | 2G | qunfuddah | Generator_DG | IPRAN SA | LTH0330-SF-CSG-01 | FLM_TE | NNL0168 |  | PCM-20250413-00000934 | NNL0168 | NNL0168 |  |  |  | API | 04/13/2025 12:21:20 | 04/14/2025 11:31:45 | 06/28/2025 23:03:53 |  |  | 06/28/2025 23:04:00 |  | Riasat Ali Allah Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250417000431 | PCM-20250417-00000643 | TT-20250417-00756 | Reference_EM | Region_3 | YBDB0670 | YBDB0670 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sayed Satoor | 04/17/2025 09:03:11 | 08/09/2025 15:34:34 | 04/17/2025 15:03:11 | Air condition 1 failure alarm at YBDB0670-P1-HUB_SRAN @ Sceco_STB | 04/17/2025 08:52:45 | Major | 65104 | Air condition 1 failure alarm | 04/17/2025 08:52:41 | P1 | SRAN | yanbu | Sceco_STB | 2G NSA | YBDB0670 | FLM_EM | [8 empty] | API | 04/17/2025 09:03:11 | 04/28/2025 13:57:09 | 08/09/2025 15:34:13 | 08/09/2025 15:34:18 |  | 08/09/2025 15:34:34 |  | Sayed Satoor | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250418000385 | PCM-20250418-00000787 | TT-20250418-00919 | Telecom | Region_4 | JED0155 | JED0155 | Transsmission | MW_HW_stuck | Reset IDU | Abd Elrahman Suliman Mohmed Suliman | 04/18/2025 09:19:59 | 07/08/2025 22:54:21 | 04/18/2025 21:19:59 | As per BO request check visibility down from JED0155 10.10.138.177 | 04/18/2025 09:19:33 | Minor | 113388 | LOF | 04/18/2025 09:19:33 | VIP | 2G | jeddah | Sceco | TX NSA | JED0155 | FLM_TE | [5 empty] | As per BO request check visibility down from JED0155 10.10.138.177 |  |  | API | 04/18/2025 09:19:59 | 05/24/2025 10:28:08 | 07/08/2025 22:54:07 |  |  | 07/08/2025 22:54:21 |  | Abd Elrahman Suliman Mohmed Suliman | Zain_Rollout |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250420001622 | PCM-20250420-00002268 | TT-20250420-02019 | Telecom | Region_4 | RYMK0528 | RYMK0528 |  |  |  | Ayman Salah Hamed Atia | 04/20/2025 21:34:46 | 05/07/2025 11:30:20 | 04/21/2025 09:34:46 | WRYMK0001 is complete down | 04/20/2025 18:32:33 | Minor | 613007 | Wi-Fi AP Out Of Service | 04/20/2025 18:32:33 | P3 | 2G | taif | Generator_SG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0528 | Hub:- RYMK0528 Suspecting power issue at hub site, kindly send EM-FLM team to check and resolve issue at site. | PCM-20250420-00001974 | Hub:- RYMK0528 Suspecting power issue at hub site, kindly send EM-FLM team to check and resolve issue at site. | Hub:- RYMK0528 Suspecting power issue at hub site, kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 04/20/2025 21:34:46 | [7 empty] | Mobily |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250423001416 | PCM-20250423-00001911 | TT-20250423-01988 | Reference_telecom | Region_4 | JED0493 | JED0493 | AutoRecovery | Clear_Before_Investigation | Auto Clear | MALIK ATIF ZAMAN | 04/23/2025 16:46:50 | 07/13/2025 11:12:42 | 04/24/2025 04:46:50 | Nokia Eband Observing BatteryFail-JED0493,LinkDown-Port 1/5,LossOfSignal at JED0493-10.10.146.179 | 04/22/2025 10:33:35 | Minor |  | LOF | 04/22/2025 10:33:35 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0493-10.10.146.179 | FLM_TE | [8 empty] | API | 04/23/2025 16:46:50 | 04/24/2025 16:48:17 | 07/13/2025 11:12:35 |  |  | 07/13/2025 11:12:42 |  | MALIK ATIF ZAMAN | Zain_Rollout |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250423001418 | PCM-20250423-00001913 | TT-20250423-01990 | Reference_telecom | Region_4 | JED0603 | JED0603 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Abdulraqib Abdo Saif Abdulaleem | 04/23/2025 16:46:52 | 06/04/2025 09:27:25 | 04/24/2025 04:46:52 | Nokia Eband Observing LinkDown-Port 4/5,LinkDown-Port 3/5,DemFail-Port 4 at JED0603-3-10.10.146.181 | 04/22/2025 10:33:46 | Minor |  | LOF | 04/22/2025 10:33:46 | P2 | 2G | jeddah | Sceco | TX NSA | JED0603-3-10.10.146.181 | FLM_TE | [8 empty] | API | 04/23/2025 16:46:52 | 05/22/2025 18:50:39 | 06/04/2025 09:27:13 |  |  | 06/04/2025 09:27:25 |  | Abdulraqib Abdo Saif Abdulaleem | Zain_Rollout |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250423001832 | PCM-20250423-00002471 | TT-20250423-02519 | Telecom | Region_4 | JED0431-ZJe08-CSG-01 | JED0431 | Transsmission | IPRAN_Fluctuation | Reset port | Mohammed Altaf Naveed AbdulHakeem | 04/23/2025 20:59:57 | 07/29/2025 08:55:11 | 04/24/2025 08:59:57 | Optical Invalid at JED0431-ZJe08-CSG-01 @ Sceco | 04/23/2025 13:37:39 | Minor | 101-2505224 | Optical Invalid | 04/23/2025 13:37:21 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0431-ZJe08-CSG-01 | FLM_TE | [8 empty] | API | 04/23/2025 20:59:57 | 04/24/2025 08:49:48 | 04/28/2025 11:13:32 |  |  | 07/29/2025 08:55:11 |  | Mohammed Altaf Naveed AbdulHakeem |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250424000900 | PCM-20250424-00001221 | TT-20250424-01198 | Reference_telecom | Region_2 | WRYD0001 | WRYD0001 |  |  |  | Abdelrahim Abdalla Abdelrahim Khairy | 04/24/2025 12:00:48 | 06/05/2025 13:32:39 | 04/25/2025 00:00:48 | WRYD0001 Complete Down | 04/24/2025 11:37:22 | Minor | 613007 | Wi-Fi AP Out Of Service | 04/24/2025 11:37:22 | P3 | WIFI | riyadh | Sceco | Wifi SA | WRYD0001 | FLM_TE |  | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally | PCM-20250424-00001184 | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally | Dear Team, We are not observing any issue at TX end at the fault time. Kindly visit the site and check issue locally |  |  |  | API | 04/24/2025 12:00:48 | 04/24/2025 13:01:24 | 04/25/2025 15:23:21 | 04/25/2025 15:23:24 | 04/25/2025 15:24:24 |  |  |  | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250424001873 | PCM-20250424-00002476 | TT-20250424-02477 | Reference_telecom | Region_1 | ARM0717 | ARM0717 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 04/24/2025 19:41:04 | 04/29/2025 13:05:16 | 04/25/2025 01:41:04 | RF Unit VSWR Threshold Crossed at ARM0717-P3_SRAN @ Sceco | 04/24/2025 18:44:16 | Major | 26529 | RF Unit VSWR Threshold Crossed | 04/24/2025 18:44:03 | P3 | SRAN | dammam | Sceco | 2G NSA | ARM0717 | FLM_TE | [8 empty] | API | 04/24/2025 19:41:04 | 04/24/2025 23:53:00 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250428002313 | PCM-20250428-00003035 | TT-20250428-02915 | Reference_telecom | Region_1 | RAF2514 | RAF2514 |  |  |  | Almmoez Almmoez | 04/28/2025 20:48:36 | 05/07/2025 11:30:44 | 04/29/2025 08:48:36 | IF_CABLE_OPEN at RAF2514_NE_1 @ Generator_DG | 04/28/2025 16:48:11 | Minor | 1-12863 | IF_CABLE_OPEN | 04/28/2025 16:48:01 | P1 | SRAN | rafha | Generator_DG | TX NSA | RAF2514 | FLM_TE | [8 empty] | API | 04/28/2025 20:48:36 | 04/28/2025 20:48:57 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250503001529 | PCM-20250503-00002292 | TT-20250503-02311 | Telecom | Region_4 | JED0078-ZJe03-CSG-02 | JED0078 |  |  |  | Ahmed Adel Abdelaziz elkholy | 05/03/2025 19:09:51 | 05/06/2025 11:19:31 | 05/04/2025 07:09:51 | Optical Invalid at JED0078-ZJe03-CSG-02 @ Sceco | 05/03/2025 17:59:42 | Minor | 101-2505224 | Optical Invalid | 05/03/2025 17:59:24 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0078-ZJe03-CSG-02 | FLM_TE | [8 empty] | API | 05/03/2025 19:09:51 | 05/06/2025 11:19:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20250504000446 | PCM-20250504-00000654 | TT-20250504-00752 | Reference_telecom | Region_4 | JED0086-ZJe03-CSG-05 | JED0086 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 05/04/2025 07:30:05 | 06/07/2025 21:01:45 | 05/04/2025 19:30:05 | Optical Invalid at JED0086-ZJe03-CSG-05 REF:TT-20250504-00429 @ Sceco | 05/04/2025 04:09:06 | Minor | 101-2505224 | Optical Invalid | 05/04/2025 04:08:26 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0086-ZJe03-CSG-05 | FLM_TE | [8 empty] | API | 05/04/2025 07:30:05 | 05/04/2025 08:36:48 | 06/07/2025 21:01:45 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250505001431 | PCM-20250505-00002008 | TT-20250505-02041 | Telecom | Region_3 | HLJF2M5753 | HLJF0753 |  |  |  | Mazin Meshary AlEnzi | 05/05/2025 16:54:58 | 05/07/2025 11:31:13 | 05/06/2025 04:54:58 | Monitoring Device Maintenance Link Failure at HLJF2M5753-P3 @ Generator_SG | 05/05/2025 16:50:56 | Minor | 25600 | Monitoring Device Maintenance Link Failure | 05/05/2025 16:50:34 | P3 | 2G | hail | Generator_SG | 2G NSA | HLJF2M5753 | FLM_TE | [8 empty] | API | 05/05/2025 16:54:58 | 05/05/2025 17:10:32 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250506001846 | PCM-20250506-00002369 | TT-20250506-02538 | Telecom | Region_1 | KBR2U6715 | KBR6015 |  |  |  | Meraj Husain Idd Baksh | 05/06/2025 21:31:05 | 05/12/2025 16:17:15 | 05/07/2025 03:31:05 | RF Out of Service at KBR2U6715-P3 @ Sceco | 05/06/2025 21:26:13 | Major | 29248 | RF Out of Service | 05/06/2025 21:24:41 | P3 | 4G | dammam | Sceco | LTE SA | KBR2U6715 | FLM_TE | [8 empty] | API | 05/06/2025 21:31:05 | 05/06/2025 23:27:41 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250508001519 | PCM-20250508-00002097 | TT-20250508-02076 | Reference_telecom | Region_6 | ABH0501 | ABH0501 | Transsmission | MW_HW_fault | Replace Control Card | Amir Sohail | 05/08/2025 17:37:08 | 06/16/2025 17:24:44 | 05/09/2025 05:37:08 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at ABH0501-10.10.158.84 | 11/24/2024 14:22:01 | Minor |  | LOF | 11/24/2024 14:22:01 | P3 | 2G | abha | Generator_SG | TX NSA | ABH0501-10.10.158.84 | FLM_TE | [8 empty] | API | 05/08/2025 17:37:08 | 05/08/2025 18:02:03 | 05/10/2025 00:09:59 |  |  | 06/16/2025 17:24:44 |  | Amir Sohail | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250508001578 | PCM-20250508-00002158 | TT-20250508-02136 | Reference_telecom | Region_6 | JIZ0151 | JIZ0151 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 05/08/2025 17:38:06 | 06/09/2025 14:02:05 | 05/09/2025 05:38:06 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A,DemFail-Port at JIZ0151_02-10.10.157.247 | 11/21/2024 10:11:08 | Minor |  | LOF | 11/21/2024 10:11:08 | P2 | 2G | jizan | Sceco | TX NSA | JIZ0151_02-10.10.157.247 | FLM_TE | [8 empty] | API | 05/08/2025 17:38:06 | 06/03/2025 21:28:06 | 06/09/2025 14:01:58 |  |  | 06/09/2025 14:02:05 |  | Osama Hadi | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250508001610 | PCM-20250508-00002190 | TT-20250508-02168 | Reference_telecom | Region_6 | SHQ0183 | SHQ0183 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 05/08/2025 17:38:36 | 05/21/2025 14:12:26 | 05/09/2025 05:38:36 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Port 1/1 at SHQ0183-10.89.249.26 | 10/28/2024 12:11:03 | Minor |  | LOF | 10/28/2024 12:11:03 | P3 | 2G | derb | Sceco | TX NSA | SHQ0183-10.89.249.26 | FLM_TE | [8 empty] | API | 05/08/2025 17:38:36 | 05/08/2025 17:43:50 | 05/21/2025 14:11:40 | 05/21/2025 14:11:52 |  | 05/21/2025 14:12:26 |  | Hamid Ullah Muhammad Alam Khan | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250509000416 | PCM-20250509-00000589 | TT-20250509-00708 | EM | Region_3 | RSP0090 | RSP0090 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sayed Satoor | 05/09/2025 09:29:12 | 08/09/2025 15:35:03 | 05/09/2025 15:29:12 | Fan Not Working at RSP0090-P1-VIP_SRAN @ Generator_SG | 05/09/2025 09:27:15 | Major | 65036 | Fan Not Working | 05/09/2025 09:10:02 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0090 | FLM_EM | [8 empty] | API | 05/09/2025 09:29:12 | 05/09/2025 10:35:27 | 08/09/2025 15:34:55 | 08/09/2025 15:34:58 |  | 08/09/2025 15:35:03 |  | Sayed Satoor | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20250509000427 | PCM-20250509-00000605 | TT-20250509-00731 | EM | Region_3 | RSP0034 | RSP0034 | Enviroment | SCECO_Failure | SCECO auto restored | Junaid Eisa | 05/09/2025 09:35:54 | 06/04/2025 14:40:35 | 05/09/2025 21:35:54 | NETECO: BMU Missing at RSP0034-Blade-2 @ Generator_SG | 05/09/2025 09:29:21 | Minor | 13821 | BMU Missing | 05/09/2025 09:29:21 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0034 | FLM_EM | [8 empty] | Manual | 05/09/2025 09:35:54 | [6 empty] | Mohammed Ali Mohammed Wafa | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250511000771 | PCM-20250511-00001161 | TT-20250511-01068 | Reference_telecom | Region_6 | ARS0104 | ARS0104 | Transsmission | MW_HW_fault | Replace IDU | Zeshan Ali Adnan | 05/11/2025 11:40:39 | 05/20/2025 17:21:11 | 05/11/2025 23:40:39 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Channel 1A,DemFail-Chann at ARS0104-10.74.62.90 | 05/01/2025 13:13:59 | Minor |  | LOF | 05/01/2025 13:13:59 | P3 | 2G | jizan | Sceco | TX NSA | ARS0104-10.74.62.90 | FLM_TE | [8 empty] | API | 05/11/2025 11:40:39 | 05/11/2025 12:01:09 | 05/20/2025 17:20:44 | 05/20/2025 17:20:47 |  | 05/20/2025 17:21:11 |  | Zeshan Ali Adnan | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250511000816 | PCM-20250511-00001208 | TT-20250511-01111 | Reference_telecom | Region_6 | SAB0277 | SAB0277 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 05/11/2025 11:41:25 | 05/26/2025 12:51:48 | 05/11/2025 23:41:25 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Port 1/1 at SAB0277-03-10.74.62.98 | 06/18/2024 22:49:04 | Minor |  | LOF | 06/18/2024 22:49:04 | P1 | 2G | baish | Sceco | TX NSA | SAB0277-03-10.74.62.98 | FLM_TE | [8 empty] | API | 05/11/2025 11:41:25 | 05/20/2025 13:15:54 | 05/26/2025 12:50:49 |  |  | 05/26/2025 12:51:48 |  | Ansir Iqbal Muhammad Iqbal | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250513001986 | PCM-20250513-00002639 | TT-20250513-02468 | Telecom | Region_4 | JD3_CORE | JD3 | Equipment | SW | Issue was solved after softaware configuration | Muhammad Mustaqeem Irshad Ali | 05/13/2025 17:18:48 | 10/13/2025 07:04:27 | 05/13/2025 23:18:48 | BASE STATION CONNECTIVITY PROBLEM (OMU signaling connection failure in Abis interface) at JD3_CORE-P1-VIP @ Sceco_STB | 05/13/2025 16:48:52 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 05/13/2025 16:48:43 | P1 | 4G | jeddah | Sceco_STB | 2G NSA | JD3_CORE | FLM_TE |  |  | PCM-20250513-00002574 | FLM need to check and update. | FLM need to check and update. |  |  |  | API | 05/13/2025 17:18:48 | 05/17/2025 15:48:52 | 10/13/2025 07:04:11 |  |  | 10/13/2025 07:04:27 |  | Muhammad Mustaqeem Irshad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250518000013 | PCM-20250518-00000024 | TT-20250518-00022 | Telecom | Region_1 | KBR6055 | KBR6055 |  |  |  | Meraj Husain Idd Baksh | 05/18/2025 00:05:47 | 05/24/2025 21:49:14 | 05/18/2025 12:05:47 | DCU Optical Module Transmit/Receive Fault at KBR6055-DCU2 @ Sceco | 05/18/2025 00:04:00 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/10/2024 13:04:50 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6055 | FLM_TE | [8 empty] | API | 05/18/2025 00:05:47 | 05/18/2025 00:29:57 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250520000694 | PCM-20250520-00001095 | TT-20250520-01082 | Reference_telecom | Region_1 | ARM0720 | ARM0720 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 05/20/2025 11:18:43 | 05/24/2025 21:49:40 | 05/20/2025 23:18:43 | MW RTN Observing HARD_BAD,HARD_ERR at ARM0720_NE_3_V | 11/22/2024 03:31:36 | Minor |  | LOF | 11/22/2024 03:31:36 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0720_NE_3_V | FLM_TE | [8 empty] | API | 05/20/2025 11:18:43 | 05/20/2025 11:31:43 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250520000695 | PCM-20250520-00001096 | TT-20250520-01083 | Reference_telecom | Region_1 | ARM0730 | ARM0730 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 05/20/2025 11:18:44 | 05/24/2025 21:49:40 | 05/20/2025 23:18:44 | MW RTN Observing PLA_MEMBER_DOWN_EXT at ARM0730_NE_7_SDB | 05/19/2025 14:59:36 | Minor |  | LOF | 05/19/2025 14:59:36 | P2 | SRAN | dammam | Sceco | TX NSA | ARM0730_NE_7_SDB | FLM_TE | [8 empty] | API | 05/20/2025 11:18:44 | 05/20/2025 11:31:44 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250520000698 | PCM-20250520-00001099 | TT-20250520-01086 | Reference_telecom | Region_1 | DAM0247 | DAM0247 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Meraj Husain Idd Baksh | 05/20/2025 11:18:48 | 06/01/2025 00:36:20 | 05/20/2025 23:18:48 | MW RTN Observing IF_CABLE_OPEN,IF_CABLE_OPEN,PLA_MEMBER_DOWN_EXT,PL at DAM0247_NE_26_SDB | 09/15/2024 00:26:32 | Minor |  | LOF | 09/15/2024 00:26:32 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0247_NE_26_SDB | FLM_TE | [8 empty] | API | 05/20/2025 11:18:48 | 05/20/2025 12:00:53 | 06/01/2025 00:35:27 |  |  | 06/01/2025 00:36:20 |  | Meraj Husain Idd Baksh | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250520000727 | PCM-20250520-00001127 | TT-20250520-01116 | Reference_telecom | Region_2 | RIY0792 | RIY0792 |  |  |  | Zakir Muhammad Yar Muhammad | 05/20/2025 11:19:24 | 06/05/2025 13:32:45 | 05/20/2025 23:19:24 | MW RTN Observing MW_LOF,RADIO_RSL_LOW at RIY0792_NE_26_H | 08/25/2024 09:51:16 | Minor |  | LOF | 08/25/2024 09:51:16 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0792_NE_26_H | FLM_TE | [8 empty] | API | 05/20/2025 11:19:24 | 05/20/2025 12:57:56 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250521001235 | PCM-20250521-00001697 | TT-20250521-01750 | Telecom | Region_1 | DAM6039 | DAM6039 |  |  |  | Meraj Husain Idd Baksh | 05/21/2025 14:51:58 | 05/26/2025 11:02:20 | 05/22/2025 02:51:58 | RF Unit CPRI Interface Error at DAM6039-P2_SRAN @ Sceco | 05/21/2025 13:35:34 | Minor | 26504 | RF Unit CPRI Interface Error | 05/21/2025 13:32:56 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6039 | FLM_TE | [8 empty] | API | 05/21/2025 14:51:58 | 05/21/2025 16:15:15 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250522002107 | PCM-20250522-00003841 | TT-20250522-02676 | Reference_telecom | Region_3 | RSP0032B | RSP0032B |  |  |  | Muhammad Sajjad R3 | 05/22/2025 18:59:20 | 06/24/2025 15:12:51 | 05/23/2025 00:59:20 | RF Unit VSWR Threshold Crossed at RSP0032B-P1-VIP_SRAN @ Generator_SG | 05/22/2025 15:58:54 | Major | 26529 | RF Unit VSWR Threshold Crossed | 05/22/2025 15:58:50 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0032B | FLM_TE | [8 empty] | API | 05/22/2025 18:59:20 | 06/02/2025 19:09:21 | [6 empty] | STC |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250522002158 | PCM-20250522-00003914 | TT-20250522-02754 | EM | Region_3 | TBK9050 | TBK9050 | Enviroment | Power Cable | Change Generator power cable | Ahmad Mohammed abdelmeguid | 05/22/2025 19:32:07 | 07/28/2025 17:25:52 | 05/22/2025 23:32:07 | WE OBSERVING CRITCAL ALARM AT TBK9050_EAS WITH HIGH TEMP32+ | 05/22/2025 19:30:38 | Critical | NA | LOF/High BER | 05/22/2025 19:30:38 | P3 | Repeater | tabouk | Generator_DG | 2G SA | TBK9050_EAS | FLM_EM | [5 empty] | WE OBSERVING CRITCAL ALARM AT TBK9050_EAS WITH HIGH TEMP32+ |  |  | API | 05/22/2025 19:32:07 | 06/28/2025 08:37:40 | 07/28/2025 17:25:35 |  |  | 07/28/2025 17:25:52 |  | Ahmad Mohammed abdelmeguid | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250524000983 | PCM-20250524-00001443 | TT-20250524-01464 | Telecom | Region_1 | DAM2U6739 | DAM6039 |  |  |  | Meraj Husain Idd Baksh | 05/24/2025 13:35:51 | 06/04/2025 13:20:31 | 05/24/2025 19:35:51 | Cell Unavailable at DAM2U6739-P2 @ Sceco | 05/24/2025 13:33:22 | Major | 29240 | Cell Unavailable | 05/24/2025 13:31:48 | P2 | 4G | dammam | Sceco | LTE SA | DAM2U6739 | FLM_TE | [8 empty] | API | 05/24/2025 13:35:51 | 05/24/2025 17:02:01 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250527000660 | PCM-20250527-00001043 | TT-20250526-00912 | Reference_telecom | Region_1 | DRN2328 | DRN2328 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 05/27/2025 11:17:04 | 07/10/2025 11:10:32 | 05/27/2025 23:17:04 | MW RTN Observing HARD_BAD at DRN2328_NE_2_H | 04/10/2025 05:12:36 | Minor |  | LOF | 04/10/2025 05:12:36 | P3 | SRAN | dammam | Sceco | TX NSA | DRN2328_NE_2_H | FLM_TE |  |  | PCM-20250527-00000963 | Kindly share TS steps | Kindly share TS steps |  |  |  | API | 05/27/2025 11:17:04 | 05/27/2025 11:18:25 | 07/09/2025 07:34:06 | 07/10/2025 11:06:06 | 07/10/2025 11:10:32 |  |  |  | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250529001455 | PCM-20250529-00002060 | TT-20250529-02022 | Reference_telecom | Region_1 | WSA0626 | WSA0626 |  |  |  | Mohamed Magdy Fouad Zayed | 05/29/2025 17:13:17 | 06/05/2025 16:37:02 | 05/30/2025 05:13:17 | MW RTN Observing ETH_LOS at WSA0626_NE_1 | 05/14/2025 20:02:18 | Minor |  | LOF | 05/14/2025 20:02:18 | P3 | SRAN | hafouf | Power Cube | TX NSA | WSA0626_NE_1 | FLM_TE | [8 empty] | API | 05/29/2025 17:13:17 | 05/29/2025 17:39:34 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250530000301 | PCM-20250530-00000512 | TT-20250530-00551 | Telecom | Region_1 | DAM2U6139 | DAM6039 |  |  |  | Meraj Husain Idd Baksh | 05/30/2025 06:51:30 | 06/04/2025 13:20:38 | 05/30/2025 18:51:30 | RF Unit Maintenance Link Failure at DAM2U6139-P2 @ Sceco | 05/29/2025 15:33:10 | Minor | 26235 | RF Unit Maintenance Link Failure | 05/29/2025 15:31:26 | P2 | 2G | dammam | Sceco | 2G NSA | DAM2U6139 | FLM_TE | [8 empty] | API | 05/30/2025 06:51:30 | 05/30/2025 08:27:36 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250530000303 | PCM-20250530-00000514 | TT-20250530-00552 | Telecom | Region_1 | DAM2U6139 | DAM6039 |  |  |  | Meraj Husain Idd Baksh | 05/30/2025 06:51:55 | 06/04/2025 13:20:38 | 05/30/2025 18:51:55 | RF Unit CPRI Interface Error at DAM2U6139-P2 @ Sceco | 05/29/2025 15:32:48 | Minor | 26504 | RF Unit CPRI Interface Error | 05/29/2025 15:31:16 | P2 | 2G | dammam | Sceco | 2G NSA | DAM2U6139 | FLM_TE | [8 empty] | API | 05/30/2025 06:51:55 | 05/30/2025 08:27:37 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250531000137 | PCM-20250531-00000249 | TT-20250531-00252 | MW_HC | Region_3 | YBDB2292 | YBDB2292 | Transsmission | MW_RSL_fading | Fading issue | Hossam Ali Ahmed Ali | 05/31/2025 03:13:39 | 06/23/2025 20:29:05 | 05/31/2025 15:13:39 | ( As per BO request ) PM errors observed on link YBDB0291-YBDB0292 | 05/31/2025 03:12:24 | Minor | 1-631 | MW_LOF | 05/31/2025 03:12:24 | P1 | SRAN | tabouk | Generator_DG | TX NSA | YBDB0291 YBDB0292 | FLM_TE | [5 empty] | ( As per BO request ) PM errors observed on link YBDB0291-YBDB0292 |  |  | API | 05/31/2025 03:13:39 | 06/23/2025 10:11:44 | 06/23/2025 20:28:57 |  |  | 06/23/2025 20:29:05 |  | Hossam Ali Ahmed Ali | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250601000587 | PCM-20250601-00001165 | TT-20250601-01194 | Telecom | Region_4 | JED3W6007 | JED3W6007 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Dilawar Khan Muhammad Nazir | 06/01/2025 10:45:54 | 10/12/2025 10:56:12 | 06/01/2025 22:45:54 | Site JED3W6007 partial Down | 06/01/2025 10:30:51 | Minor | 676767675 | Health Check-WO to TE FME | 06/01/2025 10:30:51 | P3 | WIFI | jeddah | Sceco | Wifi SA | Site JED3W6007 partial Down | FLM_TE |  |  | PCM-20250601-00001142 | please arrange FLM to the SIte to check locally switch and 10 APs are down at the Site | please arrange FLM to the SIte to check locally switch and 10 APs are down at the Site |  |  |  | API | 06/01/2025 10:45:54 | 08/19/2025 12:32:33 | 10/12/2025 10:56:02 |  |  | 10/12/2025 10:56:12 |  | Dilawar Khan Muhammad Nazir | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250601001402 | PCM-20250601-00002418 | TT-20250601-02533 | Reference_telecom | Region_2 | UNZ0091 | UNZ0091 | Transsmission | SFP_Transmission | Replace SFP | Junaid Eisa | 06/01/2025 19:21:55 | 06/17/2025 06:55:06 | 06/02/2025 07:21:55 | BD_STATUS at UNZ0091_NE_7 @ Sceco | 06/01/2025 14:49:56 | Minor | 1-119 | BD_STATUS | 06/01/2025 14:49:43 | P2 | SRAN | buraidah | Sceco | TX NSA | UNZ0091 | FLM_TE | [8 empty] | API | 06/01/2025 19:21:55 | [6 empty] | Muhammad Mohsin Raza | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250602000253 | PCM-20250602-00000395 | TT-20250602-00374 | Telecom | Region_6 | WDS1M4498 | WDS2498 | Equipment | BSS_HW_Stuck | Reset System Module | Musaddiq Adnan | 06/02/2025 05:23:02 | 06/02/2025 05:59:04 | 06/02/2025 11:23:02 | 1(3G) sites down under WDS2498-P3/ABH1RNC02 @ Generator_SG | 06/02/2025 05:15:19 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 06/02/2025 05:14:39 | P3 | 3G | wadi dawasar | Generator_SG | 3G SA | WDS2498-P3 | FLM_TE | WDS2498 | Results: DOWN SITE HUB WDS2498-P3 WDS2498 Summary: Hub: WDS2498, Down Count: 1, Down Sites: WDS2498-P3 Alarm Summary: WDS2498 Alarm Active on HUB |  |  |  |  | sites down |  | API | 06/02/2025 05:23:02 | 06/02/2025 05:35:06 | 06/02/2025 05:58:42 |  |  | 06/02/2025 05:59:04 |  | Musaddiq Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250602001124 | PCM-20250602-00001694 | TT-20250602-01839 | Reference_telecom | Region_2 | RIY2179 | RIY2179 | Enviroment | SCECO_Failure | SCECO auto restored | Pawan Virdi Santokh Singh | 06/02/2025 15:45:31 | 08/31/2025 03:28:54 | 06/02/2025 21:45:31 | 1(2G/LTE) sites down under RIY2179-P2/R2_RY2_HWBSC01 @ Generator_SG REf (TT-20250526-00662) | 05/26/2025 08:23:07 | Major | 21825 | CSL Fault | 05/26/2025 08:23:07 | P2 | SRAN | riyadh | Sceco | 2G_3G SA | RIY2179 | FLM_TE | RIY2179 | Results: DOWN SITE HUB RIY2179 RIY2179 Summary: Hub: RIY2179, Down Count: 1, Down Sites: RIY2179 Alarm Summary: RIY2179 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 06/02/2025 15:45:31 | 06/30/2025 15:46:46 | 08/31/2025 03:28:36 |  |  | 08/31/2025 03:28:54 |  | Pawan Virdi Santokh Singh | STC |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250604000048 | PCM-20250604-00000075 | TT-20250604-00085 | Reference_telecom | Region_4 | JED0088 | JED0088 |  |  |  | Mohammed Ramadan A Abu Abid | 06/04/2025 01:12:03 | 08/02/2025 14:17:40 | 06/04/2025 13:12:03 | LossOfSignal observed in JED0088_04 towards 10.10.191.166 @ Sceco | 06/03/2025 13:13:17 | Minor |  | LossOfSignal | 06/03/2025 13:11:35 | P1 | 2G | jeddah | Sceco | TX NSA | JED0088 | FLM_TE | [8 empty] | API | 06/04/2025 01:12:03 | 06/04/2025 02:23:00 | 06/15/2025 06:22:48 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250604000059 | PCM-20250604-00000096 | TT-20250604-00119 | Reference_telecom | Region_4 | JED2200 | JED2200 |  |  |  | Mohammed Ramadan A Abu Abid | 06/04/2025 01:43:03 | 08/02/2025 14:17:39 | 06/04/2025 13:43:03 | LossOfSignal observed in JED2200 towards 10.10.191.167 @ Sceco | 06/03/2025 13:44:28 | Minor |  | LossOfSignal | 06/03/2025 13:42:57 | VIP | 2G | jeddah | Sceco | TX NSA | JED2200 | FLM_TE | [8 empty] | API | 06/04/2025 01:43:03 | 06/04/2025 02:23:01 | 06/10/2025 01:47:41 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250604000157 | PCM-20250604-00000261 | TT-20250604-00309 | Telecom | Region_5 | HAJ6020 | HAJ6020 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Mohamed Soliman Mohamed | 06/04/2025 04:01:07 | 08/20/2025 19:50:28 | 06/04/2025 10:01:07 | Cell Capability Degraded at HAJ6020 | 06/04/2025 03:17:26 | Major | 29243 | Cell Capability Degraded | 06/04/2025 03:17:26 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ6020 | FLM_TE | [8 empty] | Manual | 06/04/2025 04:01:07 | 06/24/2025 13:20:16 | 08/20/2025 19:49:55 |  |  | 08/20/2025 19:50:28 |  | Ahmed Mohamed Soliman Mohamed | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250604001136 | PCM-20250604-00001615 | TT-20250604-01969 | Reference_telecom | Region_6 | WDN0110 | WDN0110 | Transsmission | MW_HW_fault | Replace ODU | Amir Sohail | 06/04/2025 16:23:25 | 08/30/2025 13:33:58 | 06/05/2025 04:23:25 | Degrade observed in WDN0110_02 towards 10.10.154.119 @ Sceco | 06/04/2025 04:23:04 | Minor |  | Degrade | 06/04/2025 04:22:59 | P2 | 2G | al harja | Sceco | TX NSA | WDN0110 | FLM_TE | [8 empty] | API | 06/04/2025 16:23:25 | 06/04/2025 16:52:23 | 06/10/2025 13:07:57 |  |  | 08/30/2025 13:33:58 |  | Amir Sohail | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250605000818 | PCM-20250605-00001398 | TT-20250605-01000 | Telecom | Region_2 | RY1-ASG-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 06/05/2025 15:57:55 | 06/06/2025 04:17:02 | 06/05/2025 21:57:55 | LINK DOWN at RY1-ASG-01 @ Sceco_STB | 06/05/2025 10:52:37 | Major | 104-2600148 | LINK DOWN | 06/05/2025 10:52:30 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN SA | RY1-ASG-01 | FLM_TE |  |  | PCM-20250605-00000984 | shared via mail | shared via mail |  |  |  | API | 06/05/2025 15:57:55 | 06/06/2025 04:17:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250607000915 | PCM-20250607-00001365 | TT-20250607-01369 | Telecom | Region_1 | HFF6035 | HFF6035 |  |  |  | Muhammad Kashif M M Bashir | 06/07/2025 17:43:13 | 06/17/2025 15:24:35 | 06/08/2025 05:43:13 | DCU Optical Module Transmit/Receive Fault at HFF6035-DCU3 @ Sceco | 06/07/2025 17:34:39 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 06/07/2025 17:37:47 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6035 | FLM_TE | [8 empty] | API | 06/07/2025 17:43:13 | 06/07/2025 19:22:37 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250607000918 | PCM-20250607-00001368 | TT-20250607-01371 | Reference_telecom | Region_1 | HFF6035 | HFF6035 |  |  |  | Muhammad Kashif M M Bashir | 06/07/2025 17:44:16 | 06/17/2025 15:24:35 | 06/07/2025 23:44:16 | RF Unit VSWR Threshold Crossed at HFF6035-DCU2 @ Sceco | 06/07/2025 17:33:46 | Major | 26529 | RF Unit VSWR Threshold Crossed | 06/07/2025 17:39:02 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6035 | FLM_TE | [8 empty] | API | 06/07/2025 17:44:16 | 06/07/2025 19:22:38 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250610001223 | PCM-20250610-00001753 | TT-20250610-01767 | Reference_telecom | Region_4 | JED0901 | JED0901 | AutoRecovery | Clear_Before_Investigation | Auto Clear | MALIK ATIF ZAMAN | 06/10/2025 20:08:38 | 08/09/2025 02:04:58 | 06/11/2025 08:08:38 | LossOfSignal observed in JED0901 towards 10.3.234.242 @ Sceco | 06/10/2025 08:08:36 | Minor |  | LossOfSignal | 06/10/2025 08:08:04 | VIP | 2G | jeddah | Sceco | TX NSA | JED0901 | FLM_TE | [8 empty] | API | 06/10/2025 20:08:38 | 08/03/2025 12:15:18 | 08/09/2025 02:04:51 |  |  | 08/09/2025 02:04:58 |  | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250611000611 | PCM-20250611-00000871 | TT-20250611-00864 | Telecom | Region_1 | HFF6029 | HFF6029 |  |  |  | Muhammad Kashif M M Bashir | 06/11/2025 11:07:38 | 06/17/2025 15:24:39 | 06/11/2025 23:07:38 | DCU Optical Module Transmit/Receive Fault at HFF6029-DCU3 @ Sceco | 06/11/2025 10:59:34 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 06/11/2025 11:00:27 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 06/11/2025 11:07:38 | 06/12/2025 04:41:19 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250611000619 | PCM-20250611-00000879 | TT-20250611-00876 | Telecom | Region_1 | HFF6028 | HFF6028 |  |  |  | Muhammad Kashif M M Bashir | 06/11/2025 11:11:15 | 06/17/2025 15:24:40 | 06/11/2025 23:11:15 | DCU Optical Module Transmit/Receive Fault at HFF6028-DCU1 @ Sceco | 06/11/2025 10:59:07 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 06/11/2025 11:05:59 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 06/11/2025 11:11:15 | 06/12/2025 04:41:20 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250611000746 | PCM-20250611-00001055 | TT-20250611-01045 | Telecom | Region_5 | HAJ6016 | HAJ6016 |  |  |  | Ahmed Mohamed Soliman Mohamed | 06/11/2025 12:38:34 | 06/29/2025 15:14:27 | 06/12/2025 00:38:34 | RF Unit Maintenance Link Failure at HAJ6016-Lamp-P3_SRAN-MML @ Sceco | 06/11/2025 12:35:11 | Minor | 26235 | RF Unit Maintenance Link Failure | 06/11/2025 12:33:26 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ6016 | FLM_TE | [8 empty] | Manual | 06/11/2025 12:38:34 | 06/24/2025 13:20:24 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250611000887 | PCM-20250611-00001251 | TT-20250611-01249 | Reference_telecom | Region_1 | HFF6029 | HFF6029 |  |  |  | Muhammad Kashif M M Bashir | 06/11/2025 14:00:43 | 06/17/2025 15:24:41 | 06/11/2025 20:00:43 | RF Unit VSWR Threshold Crossed at HFF6029-DCU3 @ Sceco | 06/11/2025 10:58:16 | Major | 26529 | RF Unit VSWR Threshold Crossed | 06/11/2025 11:00:27 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 06/11/2025 14:00:43 | 06/12/2025 04:41:20 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250611001369 | PCM-20250611-00001884 | TT-20250611-01928 | Telecom | Region_5 | HAJ6016 | HAJ6016 |  |  |  | Ahmed Mohamed Soliman Mohamed | 06/11/2025 19:12:33 | 06/29/2025 15:14:37 | 06/12/2025 01:12:33 | RHUB CPRI Interface Error at HAJ6016-Lamp-P3_SRAN-MML @ Sceco | 06/11/2025 12:34:52 | Major | 26783 | RHUB CPRI Interface Error | 06/11/2025 12:33:18 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ6016 | FLM_TE | [8 empty] | Manual | 06/11/2025 19:12:33 | 06/24/2025 13:20:31 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250612000039 | PCM-20250612-00000061 | TT-20250612-00073 | Reference_telecom | Region_4 | JED0686 | JED0686 |  |  |  | Mohammed Ramadan A Abu Abid | 06/12/2025 00:52:12 | 08/02/2025 14:17:41 | 06/12/2025 12:52:12 | DemFail observed in JED0686 towards 10.10.181.67 @ Sceco | 06/11/2025 12:54:11 | Minor |  | DemFail | 06/11/2025 12:51:49 | P2 | 2G | jeddah | Sceco | TX NSA | JED0686 | FLM_TE | [8 empty] | API | 06/12/2025 00:52:12 | 06/12/2025 02:57:42 | 06/29/2025 02:15:41 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250615000025 | PCM-20250615-00000039 | TT-20250615-00042 | Reference_telecom | Region_4 | JED0803 | JED0803 | Transsmission | MW_Connectors | Remade Indoor MW Connector | MALIK ATIF ZAMAN | 06/15/2025 00:30:15 | 09/29/2025 13:43:42 | 06/15/2025 12:30:15 | LinkDown observed in JED0803_2 towards 10.10.150.115 @ Generator_SG | 06/14/2025 12:30:43 | Minor |  | LinkDown | 06/14/2025 12:29:55 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED0803 | FLM_TE | [8 empty] | API | 06/15/2025 00:30:15 | 08/03/2025 12:15:19 | 09/29/2025 13:43:31 |  |  | 09/29/2025 13:43:42 |  | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250615000801 | PCM-20250615-00001199 | TT-20250615-01355 | Reference_telecom | Region_2 | RIY0792 | RIY0792 |  |  |  | Zakir Muhammad Yar Muhammad | 06/15/2025 13:01:34 | 07/01/2025 13:51:16 | 06/15/2025 19:01:34 | MW IS-IS Adjacency Changed AT RIY0792-ZRi01-4-CSG-02 // TT-20250318-00672 | 03/18/2025 07:10:38 | Major | 15269 | LOS | 03/18/2025 07:10:38 | VIP | SRAN | riyadh | Sceco | IPRAN_NSA | MW IS-IS Adjacency Changed AT RIY0792-ZRi01-4-CSG-02 // TT-20250318-00672 | FLM_TE | RIY0792 | We are not observing any issue in TX route. | PCM-20250615-00001138 | We are not observing any issue in TX route. | We are not observing any issue in TX route. |  |  |  | API | 06/15/2025 13:01:34 | 06/15/2025 13:56:38 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250615000826 | PCM-20250615-00001235 | TT-20250615-01447 | Reference_telecom | Region_1 | DAM2402 | DAM2402 |  |  |  | Shakeel Ahmed Hafeez Ameen | 06/15/2025 13:18:15 | 06/22/2025 10:21:27 | 06/16/2025 01:18:15 | RF Unit Maintenance Link Failure at DAM2402-P2_SRAN | 06/14/2025 18:34:30 | Minor | 26235 | RF Unit Maintenance Link Failure | 06/14/2025 18:34:30 | P2 | SRAN | dammam | Generator_SG | 2G NSA | DAM2402-P2_SRAN | FLM_TE | [8 empty] | API | 06/15/2025 13:18:15 | 06/15/2025 14:04:32 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250615000872 | PCM-20250615-00001303 | TT-20250615-01507 | Reference_telecom | Region_1 | DAM2402 | DAM2402 |  |  |  | Shakeel Ahmed Hafeez Ameen | 06/15/2025 13:46:53 | 06/22/2025 10:21:27 | 06/16/2025 01:46:53 | BBU CPRI Optical Module or Electrical Port Not Ready at DAM2402-P2_SRAN | 06/14/2025 18:34:30 | Minor | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 06/14/2025 18:34:30 | P2 | SRAN | dammam | Generator_SG | 2G NSA | DAM2402-P2_SRAN | FLM_TE | [8 empty] | API | 06/15/2025 13:46:53 | 06/15/2025 14:04:33 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250615001438 | PCM-20250615-00002062 | TT-20250615-02369 | Telecom | Region_1 | RSK2234 | RSK2234 |  |  |  | Mohamed Abdelaziz | 06/15/2025 20:12:52 | 06/21/2025 17:34:21 | 06/16/2025 08:12:52 | ODU CPU / Cable Open at RSK2234 on 10.159.106.241 @ Generator_SG | 06/15/2025 20:12:14 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 06/15/2025 20:01:50 | P3 | SRAN | jubail | Generator_SG | TX NSA | RSK2234 | FLM_TE | [8 empty] | API | 06/15/2025 20:12:52 | 06/16/2025 00:30:56 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250616000700 | PCM-20250616-00001061 | TT-20250616-01284 | EM | Region_3 | TBK9045 | TBK9045 |  |  |  | Moustafa Samir Omar | 06/16/2025 12:16:36 | 06/21/2025 21:53:11 | 06/16/2025 16:16:36 | HIGH TEMPERATURE observed at TBK9045_EXT | 06/16/2025 12:15:00 | Critical | NA | LOF/High BER | 06/16/2025 12:14:58 | P3 | Repeater | tabouk | Generator_SG | TX NSA | TBK9045_EXT | FLM_EM | [5 empty] | HIGH TEMPERATURE observed at TBK9045_EXT |  |  | API | 06/16/2025 12:16:36 | 06/17/2025 08:10:53 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250616001016 | PCM-20250616-00001513 | TT-20250616-01690 | Telecom | Region_3 | HAL2U6306B | HAL6006 | Equipment | CB_BTS | Switch on Owner AC CB | Atif Shahzad Muhammad Ajaib | 06/16/2025 15:02:35 | 09/29/2025 23:38:41 | 06/16/2025 21:02:35 | Local Cell Capability Decline at HAL2U6306B-P3 @ Sceco | 06/16/2025 14:43:32 | Major | 28206 | Local Cell Capability Decline | 06/16/2025 14:41:53 | P3 | 3G | hail | Sceco | 2G NSA | HAL2U6306B | FLM_TE |  |  | PCM-20250616-00001484 | kindly check subrack 145 | kindly check subrack 145 |  |  |  | API | 06/16/2025 15:02:35 | 06/29/2025 17:23:19 | 08/16/2025 23:31:12 | 08/16/2025 23:31:50 |  | 09/29/2025 23:38:41 |  | Atif Shahzad Muhammad Ajaib | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250616001484 | PCM-20250616-00002084 | TT-20250616-02274 | MW_HC | Region_3 | MDYB0641 | MDYB0641 |  |  |  | Muhammad Sajjad R3 | 06/16/2025 17:02:17 | 07/01/2025 15:09:06 | 06/17/2025 05:02:17 | Huawei HC_P0 Observing Errors at MDYB0641-MDYB0409 | 06/16/2025 16:57:37 | Minor |  | LOF | 06/16/2025 16:57:37 | P1 | SRAN | yanbu | Generator_DG | TX NSA | MDYB0641-MDYB0409 | FLM_TE | [8 empty] | API | 06/16/2025 17:02:17 | 06/17/2025 05:30:38 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250616001509 | PCM-20250616-00002108 | TT-20250616-02303 | MW_HC | Region_3 | AWJ2581 | AWJ2581 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Junaid Eisa | 06/16/2025 17:02:50 | 08/14/2025 05:05:21 | 06/17/2025 05:02:50 | Huawei HC_P2 Observing Errors at AWJ2581-YBDB0978 | 06/16/2025 16:57:37 | Minor |  | LOF | 06/16/2025 16:57:37 | P3 | SRAN | Deba | Generator_SG | TX NSA | AWJ2581-YBDB0978 | FLM_TE | [8 empty] | API | 06/16/2025 17:02:50 | [6 empty] | Hossam Ali Ahmed Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250616001775 | PCM-20250616-00002468 | TT-20250616-02656 | Telecom | Region_3 | HAL2U6706C | HAL6006 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Atif Shahzad Muhammad Ajaib | 06/16/2025 19:33:52 | 07/20/2025 15:09:46 | 06/17/2025 07:33:52 | RF Unit Maintenance Link Failure at HAL2U6706C-P3 @ Sceco | 06/16/2025 14:41:34 | Minor | 26235 | RF Unit Maintenance Link Failure | 06/16/2025 14:39:51 | P3 | 4G | hail | Sceco | 2G NSA | HAL2U6706C | FLM_TE | [8 empty] | API | 06/16/2025 19:33:52 | 06/16/2025 19:41:40 | 07/20/2025 14:51:03 | 07/20/2025 14:51:29 | 07/20/2025 14:51:45 | 07/20/2025 15:09:46 |  | Atif Shahzad Muhammad Ajaib | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250618000131 | PCM-20250618-00000196 | TT-20250618-00062 | Telecom | Region_3 | TBK-0013-NE40E-X8-P&PE-01 | TB1 |  |  |  | Tahir Abbas Fateh Khan | 06/18/2025 02:26:44 | 06/30/2025 06:29:26 | 06/18/2025 08:26:44 | Alarm of failed LAG negotiation at TBK-0013-NE40E-X8-P&PE-01 @ Sceco_STB | 06/18/2025 00:38:55 | Major | 101-1102218 | Alarm of failed LAG negotiation | 06/18/2025 00:38:51 | P1 | IPRAN | tabouk | Sceco_STB | IPRAN SA | TBK-0013-NE40E-X8-P&PE-01 | FLM_TE |  |  | PCM-20250618-00000059 | escalate to RO Team as the alarm sill active | escalate to RO Team as the alarm sill active |  |  |  | API | 06/18/2025 02:26:44 | 06/18/2025 05:24:17 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250621000536 | PCM-20250621-00000801 | TT-20250619-01232 | Reference_telecom | Region_1 | DMAR2011 | DMAR2011 |  |  |  | Dileesh Muringothil Devarajan | 06/21/2025 11:37:00 | 06/25/2025 14:30:03 | 06/21/2025 23:37:00 | BFD Session Fault at DMAR2011-P3-SRAN @ Sceco | 06/17/2025 06:21:47 | Minor | 25899 | BFD Session Fault | 06/17/2025 06:02:19 | P3 | SRAN | jubail | Sceco | 2G NSA | DMAR2011 | FLM_EM | DMAR2011 | Hub : DMAR2011 We are observing ETH_LOS alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. | PCM-20250621-00000790 | Hub : DMAR2011 We are observing ETH_LOS alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. | Hub : DMAR2011 We are observing ETH_LOS alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. |  |  |  | API | 06/21/2025 11:37:00 | 06/22/2025 15:50:36 | [6 empty] | ZAIN Planning |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20250622000994 | PCM-20250622-00001539 | TT-20250622-01617 | Reference_telecom | Region_4 | HJR0235 | HJR0235 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Junaid Eisa | 06/22/2025 15:18:28 | 07/06/2025 14:54:53 | 06/23/2025 03:18:28 | Nokia Eband Observing LinkDown-Port 4/1,DemFail-Port 4/1,LagPortDown-Por at HJR0235-02-10.21.71.201 | 06/18/2025 13:40:09 | Minor |  | LOF | 06/18/2025 13:40:09 | P2 | 2G | jeddah | Generator_DG | TX NSA | HJR0235-02-10.21.71.201 | FLM_TE | [8 empty] | API | 06/22/2025 15:18:28 | [6 empty] | Khizer Hayat | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250622001027 | PCM-20250622-00001572 | TT-20250622-01650 | Reference_telecom | Region_4 | JED6154 | JED6154 |  |  |  | Mohamed Farag Abdelbary | 06/22/2025 15:19:06 | 08/02/2025 14:17:40 | 06/23/2025 03:19:06 | Nokia Eband Observing InternalCommunicationProblem-Port 4/5,LossOfSignal at JED6154-10.10.150.116 | 12/07/2024 00:18:06 | Minor |  | LOF | 12/07/2024 00:18:06 | P3 | 2G | jeddah | Sceco | TX NSA | JED6154-10.10.150.116 | FLM_TE | [8 empty] | API | 06/22/2025 15:19:06 | 06/22/2025 17:50:58 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250622001091 | PCM-20250622-00001643 | TT-20250622-01718 | MW_HC | Region_3 | MDN0097 | MDN0097 |  |  |  | Hussain Ahmad Sultan Muhammad | 06/22/2025 15:25:58 | 07/27/2025 18:42:34 | 06/23/2025 03:25:58 | Huawei HC_P2 Observing Errors at MDN0097-MDN2981 | 06/22/2025 15:24:28 | Minor |  | LOF | 06/22/2025 15:24:28 | P2 | SRAN | madinah | Sceco | TX NSA | MDN0097-MDN2981 | FLM_TE | [8 empty] | API | 06/22/2025 15:25:58 | 07/27/2025 18:42:34 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250622001304 | PCM-20250622-00001935 | TT-20250622-02063 | MW_HC | Region_3 | RSP2800 | RSP2800 |  |  |  | Muhammad Sajjad R3 | 06/22/2025 17:19:48 | 07/03/2025 09:41:35 | 06/23/2025 05:19:48 | Huawei MW_HC for performance issue at link RSP2800 dir YBDB9002,RSP2801 (As per BO request) | 06/22/2025 17:19:21 | Minor | 1-631 | MW_LOF | 06/22/2025 17:19:23 | VIP | SRAN | yanbu | Sceco | TX NSA | RSP2800 dir YBDB9002,RSP2801 | FLM_TE | [8 empty] | API | 06/22/2025 17:19:48 | 06/23/2025 02:26:56 | 07/03/2025 09:25:57 | 07/03/2025 09:26:01 | 07/03/2025 09:41:35 |  |  |  | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250623000074 | PCM-20250623-00000106 | TT-20250623-00103 | EM | Region_3 | TBK9046 | TBK9046 |  |  |  | Moustafa Samir Omar | 06/23/2025 01:22:31 | 07/01/2025 08:30:57 | 06/23/2025 05:22:31 | NEC MW AC1+AC2 FAILURE (INPUT-2) Observed at TBK9046_EXT | 06/23/2025 00:06:34 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 06/23/2025 00:06:34 | P3 | Repeater | tabouk | Generator_DG | TX NSA | TBK9046_EXT | FLM_EM | [5 empty] | NEC MW AC1+AC2 FAILURE (INPUT-2) Observed at TBK9046_EXT |  |  | API | 06/23/2025 01:22:31 | 06/24/2025 09:32:21 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250623000797 | PCM-20250623-00001215 | TT-20250623-01313 | Reference_telecom | Region_6 | AQQ0039 | AQQ0039 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Manzoor Ahmed | 06/23/2025 13:17:20 | 07/03/2025 14:28:59 | 06/24/2025 01:17:20 | LinkDown observed in AQQ0039_02 towards 10.221.246.21 @ Sceco | 06/23/2025 01:17:06 | Minor |  | LinkDown | 06/23/2025 01:17:02 | P3 | 2G | Albaha | Sceco | TX NSA | AQQ0039 | FLM_TE | [8 empty] | API | 06/23/2025 13:17:20 | 07/03/2025 14:28:32 | 07/03/2025 14:28:49 |  |  | 07/03/2025 14:28:59 |  | Manzoor Ahmed | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250623001150 | PCM-20250623-00001710 | TT-20250623-01825 | Reference_telecom | Region_4 | MUMA0772 | MUMA0772 | Transsmission | MW_RSL_fading | Fading issue | Junaid Eisa | 06/23/2025 16:48:07 | 07/06/2025 14:55:47 | 06/24/2025 04:48:07 | LinkDown observed in MUMA0772_01 towards 10.221.243.242 @ Sceco | 06/23/2025 04:48:01 | Minor |  | LinkDown | 06/23/2025 04:47:56 | P3 | 2G | qunfuddah | Sceco | TX NSA | MUMA0772 | FLM_TE | [8 empty] | API | 06/23/2025 16:48:07 | [6 empty] | Mudassar Bashir Bashir Ahmad | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250624000156 | PCM-20250624-00000234 | TT-20250624-00236 | Reference_telecom | Region_6 | AQQ0716 | AQQ0716 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Manzoor Ahmed | 06/24/2025 03:34:56 | 07/13/2025 23:25:03 | 06/24/2025 15:34:56 | LagPortDown observed in AQQ0716_01 towards 10.221.242.142 @ Sceco | 06/23/2025 15:34:50 | Minor |  | LagPortDown | 06/23/2025 15:34:46 | P3 | 2G | Albaha | Sceco | TX NSA | AQQ0716 | FLM_TE | [8 empty] | API | 06/24/2025 03:34:56 | 06/24/2025 10:47:21 | 07/13/2025 23:22:59 |  |  | 07/13/2025 23:25:03 |  | Manzoor Ahmed | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250624000450 | PCM-20250624-00000744 | TT-20250624-00789 | Reference_telecom | Region_2 | BUR0017 | BUR0017 |  |  |  | Raise Ahmed Nisar Ahmed | 06/24/2025 09:02:18 | 08/03/2025 10:33:38 | 06/24/2025 21:02:18 | MW RTN Observing PLA_MEMBER_DOWN_EXT,PORT_MODULE_OFFLINE,NB_UNREACH at BUR0017_NE_11_V | 08/19/2024 16:14:52 | Minor |  | LOF | 08/19/2024 16:14:52 | P1 | SRAN | buraidah | Sceco | TX NSA | BUR0017_NE_11_V | FLM_TE | [8 empty] | API | 06/24/2025 09:02:18 | 08/03/2025 10:33:38 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250624000451 | PCM-20250624-00000745 | TT-20250624-00790 | Reference_telecom | Region_2 | BUR0066 | BUR0066 |  |  |  | Raise Ahmed Nisar Ahmed | 06/24/2025 09:02:20 | 08/03/2025 10:33:39 | 06/24/2025 21:02:20 | MW RTN Observing PLA_MEMBER_DOWN_EXT,NB_UNREACHABLE at BUR0066_NE_1_V | 08/23/2024 23:15:20 | Minor |  | LOF | 08/23/2024 23:15:20 | P2 | SRAN | buraidah | Sceco | TX NSA | BUR0066_NE_1_V | FLM_TE | [8 empty] | API | 06/24/2025 09:02:20 | 08/03/2025 10:33:39 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250624001369 | PCM-20250624-00001982 | TT-20250520-01134 | Reference_telecom | Region_2 | RYMK0507 | RYMK0507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nawaz Sharif Muhammad Iqbal | 06/24/2025 16:22:31 | 07/14/2025 22:35:34 | 06/25/2025 04:22:31 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RYMK0507_NE_8 | 04/28/2025 06:02:55 | Minor |  | LOF | 04/28/2025 06:02:55 | P2 | SRAN | quweyah | Sceco_STB | TX NSA | RYMK0507_NE_8 | FLM_TE |  | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20250624-00001826 | As discussed | As discussed |  |  |  | API | 06/24/2025 16:22:31 | 06/24/2025 18:16:37 | 07/14/2025 22:35:02 |  |  | 07/14/2025 22:35:34 |  | Nawaz Sharif Muhammad Iqbal | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250624001375 | PCM-20250624-00001987 | TT-20250520-01135 | Reference_telecom | Region_2 | RYMK0508 | RYMK0508 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Nawaz Sharif Muhammad Iqbal | 06/24/2025 16:23:21 | 07/09/2025 21:15:23 | 06/25/2025 04:23:21 | MW RTN Observing PLA_MEMBER_DOWN_EXT,MW_LOF at RYMK0508_NE_7 | 04/28/2025 06:02:55 | Minor |  | LOF | 04/28/2025 06:02:55 | P2 | SRAN | quweyah | Sceco_STB | TX NSA | RYMK0508_NE_7 | FLM_TE |  | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20250624-00001825 | As discussed | As discussed |  |  |  | API | 06/24/2025 16:23:21 | 06/24/2025 18:16:37 | 07/09/2025 16:36:06 | 07/09/2025 16:36:09 | 07/09/2025 16:52:40 | 07/09/2025 21:15:23 |  | Nawaz Sharif Muhammad Iqbal | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250624001780 | PCM-20250624-00002589 | TT-20250624-02758 | Telecom | Region_4 | JED1W6081 | JED6081 |  |  |  | Mohamed Farag Abdelbary | 06/24/2025 21:11:41 | 07/09/2025 11:54:27 | 06/25/2025 09:11:41 | JED1W6081 Partial Down | 06/24/2025 21:02:28 | Minor | 613007 | Wi-Fi AP Out Of Service | 06/24/2025 21:02:28 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_2-6F-AP02 | FLM_TE | [8 empty] | API | 06/24/2025 21:11:41 | 06/24/2025 22:23:21 | 06/25/2025 12:18:31 | 06/25/2025 12:18:51 | 06/25/2025 12:19:43 |  |  |  | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250628000396 | PCM-20250628-00000557 | TT-20250628-00603 | Telecom | Region_1 | ARM0885 | ARM0885 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohamed Abdelaziz | 06/28/2025 09:49:39 | 07/03/2025 17:31:12 | 06/28/2025 21:49:39 | ODU CPU / Cable Open at ARM0885 on 10.76.118.88 @ Sceco | 06/28/2025 09:48:48 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 06/28/2025 09:47:32 | P3 | SRAN | khafji | Sceco | TX NSA | ARM0885 | FLM_TE | [8 empty] | API | 06/28/2025 09:49:39 | 06/28/2025 11:59:51 | 07/03/2025 16:30:59 | 07/03/2025 16:31:01 | 07/03/2025 16:31:04 | 07/03/2025 17:31:12 |  | Mohamed Abdelaziz | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250629000179 | PCM-20250629-00000302 | TT-20250629-00291 | Telecom | Region_3 | YB1MBSCH01 | YB2 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 06/29/2025 04:48:58 | 07/01/2025 20:37:18 | 06/29/2025 10:48:58 | Transmission Resource Pool Ping Packet Loss at YB1MBSCH01 | 06/29/2025 04:19:09 | Major | 21394 | Transmission Resource Pool Ping Packet Loss | 06/29/2025 04:19:09 | P1 | BSC | yanbu | Sceco_STB | 2G NSA | YB1MBSCH01 | FLM_TE |  |  | PCM-20250629-00000284 | Dear FLM, Kindly check this case related to 2(2G) 2(3G) sites down under BDJD0666-P2,BDJD0369-P2-YB1MBSCH01 @ Generator_SG TT-20250629-00223 | Dear FLM, Kindly check this case related to 2(2G) 2(3G) sites down under BDJD0666-P2,BDJD0369-P2-YB1MBSCH01 @ Generator_SG TT-20250629-00223 |  |  |  | API | 06/29/2025 04:48:58 | 07/01/2025 19:06:04 | 07/01/2025 20:36:56 |  |  | 07/01/2025 20:37:18 |  | Muhammad Sajjad R3 | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250630000340 | PCM-20250630-00000547 | TT-20250630-00543 | Reference_telecom | Region_4 | HJR9400 | HJR9400 |  |  |  | Junaid Eisa | 06/30/2025 07:10:11 | 07/06/2025 14:56:20 | 06/30/2025 19:10:11 | ReplaceableUnitMissing observed in HJR9400_02 towards 10.21.71.195 @ Generator_DG | 06/29/2025 19:09:47 | Minor |  | ReplaceableUnitMissing | 06/29/2025 19:09:42 | P1 | Repeater | jeddah | Generator_DG | TX NSA | HJR9400 | FLM_TE | [8 empty] | API | 06/30/2025 07:10:11 | [7 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250630000602 | PCM-20250630-00000903 | TT-20250630-00968 | Reference_telecom | Region_1 | ARM0717 | ARM0717 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 06/30/2025 10:06:11 | 07/02/2025 19:34:27 | 06/30/2025 22:06:11 | MW RTN Observing PLA_MEMBER_DOWN_EXT,MW_LOF at ARM0717_NE_3_SDB | 05/20/2025 15:41:31 | Minor |  | LOF | 05/20/2025 15:41:31 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0717_NE_3_SDB | FLM_TE | [8 empty] | API | 06/30/2025 10:06:11 | 06/30/2025 11:23:28 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250630000632 | PCM-20250630-00000934 | TT-20250630-01001 | Reference_telecom | Region_3 | MDN0772 | MDN0772 | Transsmission | SFP_Transmission | Reset SFP | TAUSEEF ILYAS | 06/30/2025 10:06:53 | 09/19/2025 23:00:07 | 06/30/2025 22:06:53 | NEC MW Observing Radio Traffic Aggregation Link at MDN0772_ACCESS_4(10.154.81.177) | 06/16/2025 10:46:09 | Minor |  | LOF | 06/16/2025 10:46:09 | P1 | SRAN | madinah | Sceco_STB | TX NSA | MDN0772_ACCESS_4 | FLM_TE | [8 empty] | API | 06/30/2025 10:06:53 | 06/30/2025 11:32:23 | 07/14/2025 18:19:48 |  |  | 09/19/2025 23:00:07 |  | TAUSEEF ILYAS | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250630000634 | PCM-20250630-00000936 | TT-20250630-01003 | Reference_telecom | Region_3 | MDN0326 | MDN0326 | Transsmission | SFP_Transmission | Reset SFP | TAUSEEF ILYAS | 06/30/2025 10:06:56 | 09/19/2025 22:59:50 | 06/30/2025 22:06:56 | NEC MW Observing LAN Link at MDN0326 Access(10.154.72.65) | 06/16/2025 10:46:17 | Minor |  | LOF | 06/16/2025 10:46:17 | P1 | SRAN | madinah | Sceco | TX NSA | MDN0326 Access | FLM_TE | [8 empty] | API | 06/30/2025 10:06:56 | 06/30/2025 11:32:24 | 07/19/2025 17:35:30 |  |  | 09/19/2025 22:59:50 |  | TAUSEEF ILYAS | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250630000638 | PCM-20250630-00000940 | TT-20250630-01007 | Reference_telecom | Region_3 | MDYB0408 | MDYB0408 |  |  |  | Muhammad Sajjad R3 | 06/30/2025 10:07:00 | 07/01/2025 14:41:10 | 06/30/2025 22:07:00 | NEC MW Observing ETH LOS,MODEM Power Supply Alarm,Radio Traffic Aggregation Link,LAN Link,MODEM Power Supply Alarm at MDYB0408(10.154.69.182) | 06/16/2025 11:01:48 | Minor |  | LOF | 06/16/2025 11:01:48 | P3 | SRAN | madinah | Generator_SG | TX NSA | MDYB0408 | FLM_TE | [8 empty] | API | 06/30/2025 10:07:00 | 06/30/2025 13:21:12 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250630000640 | PCM-20250630-00000942 | TT-20250630-01009 | Reference_telecom | Region_3 | MKMD0322 | MKMD0322 | Transsmission | MW_Connectors | Remade Indoor MW Connector | TAUSEEF ILYAS | 06/30/2025 10:07:03 | 09/19/2025 22:59:24 | 06/30/2025 22:07:03 | NEC MW Observing LAN Link,ETH LOS at MKMD0322-MKMD9031(10.158.215.17) | 06/16/2025 10:46:54 | Minor |  | LOF | 06/16/2025 10:46:54 | P2 | SRAN | madinah | Generator_DG | TX NSA | MKMD0322-MKMD9031 | FLM_TE | [8 empty] | API | 06/30/2025 10:07:03 | 06/30/2025 11:32:25 | 07/19/2025 17:35:40 |  |  | 09/19/2025 22:59:24 |  | TAUSEEF ILYAS | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250630000654 | PCM-20250630-00000956 | TT-20250630-01023 | Reference_telecom | Region_3 | YBDB0283 | YBDB0283 |  |  |  | Muhammad Sajjad R3 | 06/30/2025 10:07:19 | 07/01/2025 15:50:16 | 06/30/2025 22:07:19 | NEC MW Observing LAN Link,LAN Link,ETH LOS,LAG Link,ETH LOS at YBDB0283-YBDB0284(10.154.80.124) | 01/16/2025 11:57:54 | Minor |  | LOF | 01/16/2025 11:57:54 | P1 | SRAN | yanbu | Sceco_STB | TX NSA | YBDB0283-YBDB0284 | FLM_TE | [8 empty] | API | 06/30/2025 10:07:19 | 06/30/2025 13:21:12 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250630000656 | PCM-20250630-00000958 | TT-20250630-01025 | Reference_telecom | Region_3 | YBDB0280 | YBDB0280 |  |  |  | Muhammad Sajjad R3 | 06/30/2025 10:07:22 | 07/01/2025 14:44:03 | 06/30/2025 22:07:22 | NEC MW Observing ETH LOS at YBDB0280(10.154.80.5) | 03/07/2025 14:18:33 | Minor |  | LOF | 03/07/2025 14:18:33 | P1 | SRAN | yanbu | Sceco_STB | TX NSA | YBDB0280 | FLM_TE | [8 empty] | API | 06/30/2025 10:07:22 | 06/30/2025 13:21:13 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250630001654 | PCM-20250630-00002379 | TT-20250630-02444 | Telecom | Region_2 | RYQS0573 | RYQS2573 |  |  |  | Zakir Muhammad Yar Muhammad | 06/30/2025 21:58:12 | 07/01/2025 11:10:43 | 07/01/2025 03:58:12 | SPAN_LOSS_LOWER_GAIN at RYQS0573 @ Sceco_STB_Rental | 06/30/2025 21:54:11 | Major | 1-13650 | SPAN_LOSS_LOWER_GAIN | 06/30/2025 21:54:03 | P1 | DWDM | riyadh | Sceco_STB_Rental | DWDM NSA | RYQS0573 | FLM_TE | [5 empty] | 0-1-C-8-F1DSFIU-4(ELINE1/ELINE2FROM RIY0792))-OTS:1 |  |  | API | 06/30/2025 21:58:12 | 07/01/2025 11:10:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250701000515 | PCM-20250701-00000841 | TT-20250701-00838 | MW_HC | Region_2 | RYQS0578 | RYQS0578 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Tahir Abdulrazzaq | 07/01/2025 10:36:30 | 10/12/2025 10:43:01 | 07/01/2025 22:36:30 | Huawei HC_P1 Observing Errors at RYQS0578-RYQS0579 | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P2 | SRAN | rumah | Sceco | TX NSA | RYQS0578-RYQS0579 | FLM_TE | [8 empty] | API | 07/01/2025 10:36:30 | 09/02/2025 01:05:26 | 10/12/2025 10:38:56 |  |  | 10/12/2025 10:43:01 |  | Muhammad Tahir Abdulrazzaq | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250701000523 | PCM-20250701-00000849 | TT-20250701-00846 | MW_HC | Region_2 | RIY2479 | RIY2479 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ejaz Hussain Muhammad Sharif | 07/01/2025 10:36:39 | 09/28/2025 10:51:13 | 07/01/2025 22:36:39 | Huawei HC_P2 Observing Errors at RIY2479-RIY0390 | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P3 | SRAN | riyadh | Generator_SG | TX NSA | RIY2479-RIY0390 | FLM_TE | [8 empty] | API | 07/01/2025 10:36:39 | 07/31/2025 09:09:40 | 09/28/2025 10:50:52 |  |  | 09/28/2025 10:51:13 |  | Ejaz Hussain Muhammad Sharif | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250701000539 | PCM-20250701-00000865 | TT-20250701-00862 | MW_HC | Region_1 | DAM2477 | DAM2477 | Transsmission | MW_RSL_fading | Link Alignment Issue | Shakeel Ahmed Hafeez Ameen | 07/01/2025 10:36:58 | 10/05/2025 17:52:12 | 07/01/2025 22:36:58 | Huawei HC_P2 Observing Errors at DAM2477-DRN0129 | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P2 | SRAN | dammam | Sceco | TX NSA | DAM2477-DRN0129 | FLM_TE | [8 empty] | API | 07/01/2025 10:36:58 | 07/01/2025 12:13:03 | 10/05/2025 17:52:00 |  |  | 10/05/2025 17:52:12 |  | Shakeel Ahmed Hafeez Ameen | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000592 | PCM-20250701-00000918 | TT-20250701-00915 | MW_HC | Region_3 | YNB0675 | YNB0675 |  |  |  | Muhammad Sajjad R3 | 07/01/2025 10:38:01 | 08/06/2025 09:19:24 | 07/01/2025 22:38:01 | NEC MW HC_P0 Observing Performance Issue at YBYN0305(10.159.106.35)--YNB0675(10.159.106.34) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | VIP | SRAN | yanbu | Sceco_STB | TX NSA | YBYN0305(10.159.106.35)--YNB0675(10.159.106.34) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:01 | 07/01/2025 11:15:29 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000599 | PCM-20250701-00000926 | TT-20250701-00923 | MW_HC | Region_1 | RSK2234 | RSK2234 |  |  |  | Mohamed Abdelaziz | 07/01/2025 10:38:09 | 07/10/2025 14:14:07 | 07/01/2025 22:38:09 | NEC MW HC_P0 Observing Modem Down at RSK0970(10.159.106.240)--RSK2234(10.159.106.241) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P3 | SRAN | jubail | Generator_SG | TX NSA | RSK0970(10.159.106.240)--RSK2234(10.159.106.241) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:09 | 07/01/2025 12:17:09 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250701000604 | PCM-20250701-00000931 | TT-20250701-00928 | MW_HC | Region_1 | JBKH0601 | JBKH0601 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Tahir Mahmood Hafiz Yar | 07/01/2025 10:38:14 | 08/26/2025 18:07:10 | 07/01/2025 22:38:14 | NEC MW HC_P0 Observing Performance Issue at JBKH0069(10.76.111.236)--JBKH0601(10.154.13.7) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P1 | SRAN | jubail | Sceco | TX NSA | JBKH0069(10.76.111.236)--JBKH0601(10.154.13.7) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:14 | 07/01/2025 16:15:07 | 08/26/2025 15:28:06 | 08/26/2025 15:28:09 | 08/26/2025 16:20:31 | 08/26/2025 18:07:10 |  | Tahir Mahmood Hafiz Yar | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250701000606 | PCM-20250701-00000933 | TT-20250701-00930 | MW_HC | Region_1 | JBKH0093 | JBKH0093 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Tahir Mahmood Hafiz Yar | 07/01/2025 10:38:17 | 07/20/2025 20:03:17 | 07/01/2025 22:38:17 | NEC MW HC_P0 Observing Modem Down at JBKH0069(10.76.111.233)--JBKH0093(10.76.111.230) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBKH0069(10.76.111.233)--JBKH0093(10.76.111.230) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:17 | 07/20/2025 16:33:25 | 07/20/2025 16:43:19 | 07/20/2025 16:43:37 | 07/20/2025 17:37:15 | 07/20/2025 20:03:17 |  | Tahir Mahmood Hafiz Yar | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000607 | PCM-20250701-00000934 | TT-20250701-00931 | MW_HC | Region_1 | ARM0872 | ARM0872 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/01/2025 10:38:18 | 07/10/2025 14:14:08 | 07/01/2025 22:38:18 | NEC MW HC_P0 Observing Modem Down at ARM0872(10.21.217.171)--ARM0873(10.21.217.172) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0872(10.21.217.171)--ARM0873(10.21.217.172) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:18 | 07/01/2025 14:06:54 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000608 | PCM-20250701-00000935 | TT-20250701-00932 | MW_HC | Region_1 | ARM0873 | ARM0873 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/01/2025 10:38:19 | 07/10/2025 14:14:09 | 07/01/2025 22:38:19 | NEC MW HC_P0 Observing Modem Down at ARM0871(10.21.217.173)--ARM0873(10.21.217.172) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0871(10.21.217.173)--ARM0873(10.21.217.172) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:19 | 07/01/2025 14:06:55 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000611 | PCM-20250701-00000937 | TT-20250701-00934 | MW_HC | Region_1 | DRN2140 | DRN2140 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/01/2025 10:38:21 | 07/24/2025 15:53:00 | 07/01/2025 22:38:21 | NEC MW HC_P2 Observing Modem Down at DRN0102(10.74.82.98)--DRN2140(10.74.82.99) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P1 | SRAN | dammam | Generator_SG | TX NSA | DRN0102(10.74.82.98)--DRN2140(10.74.82.99) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:21 | 07/01/2025 14:06:56 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000615 | PCM-20250701-00000941 | TT-20250701-00938 | MW_HC | Region_1 | HMBY2434 | HMBY2434 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/01/2025 10:38:26 | 07/28/2025 12:32:00 | 07/01/2025 22:38:26 | NEC MW HC_P0 Observing Modem Down at ARM0734(10.154.6.164)--HMBY2434(10.154.6.166) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | VIP | SRAN | dammam | Sceco | TX NSA | ARM0734(10.154.6.164)--HMBY2434(10.154.6.166) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:26 | 07/01/2025 14:06:56 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000618 | PCM-20250701-00000944 | TT-20250701-00941 | MW_HC | Region_1 | DMHF0080 | DMHF0080 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/01/2025 10:38:29 | 07/10/2025 14:14:10 | 07/01/2025 22:38:29 | NEC MW HC_P2 Observing Modem Down at ARM0705(10.74.77.22)--DMHF0080(10.74.77.23) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P1 | SRAN | dammam | Generator_SG | TX NSA | ARM0705(10.74.77.22)--DMHF0080(10.74.77.23) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:29 | 07/01/2025 14:06:58 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701000621 | PCM-20250701-00000947 | TT-20250701-00944 | MW_HC | Region_1 | DRN0129 | DRN0129 |  |  |  | Shakeel Ahmed Hafeez Ameen | 07/01/2025 10:38:33 | 07/28/2025 12:31:59 | 07/01/2025 22:38:33 | NEC MW HC_P0 Observing Modem Down at ARM0714(10.158.154.132)--DRN0129(10.158.154.129) | 07/01/2025 10:35:52 | Minor |  | LOF | 07/01/2025 10:35:52 | P1 | SRAN | dammam | Sceco | TX NSA | ARM0714(10.158.154.132)--DRN0129(10.158.154.129) | FLM_TE | [8 empty] | API | 07/01/2025 10:38:33 | 07/01/2025 12:13:06 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250701001458 | PCM-20250701-00002155 | TT-20250701-02171 | Reference_telecom | Region_4 | JED1M8243 | JED2243 | Equipment | BSS_HW_fault | Replace RF Module | Kashif Kamboh | 07/01/2025 22:37:13 | 07/21/2025 13:44:32 | 07/02/2025 04:37:13 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M8243-L800-CA-SBTS-P3 @ Sceco (Ref::TT-20250628-01686) | 06/29/2025 18:37:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 06/29/2025 18:37:39 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE SA | JED1M8243-L800-CA-SBTS-P3 | FLM_TE | [8 empty] | API | 07/01/2025 22:37:13 | 07/21/2025 13:44:32 | [5 empty] | Kashif Kamboh | NSN_Care |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250702000167 | PCM-20250702-00000280 | TT-20250702-00302 | EM | Region_4 | JED2640 | JED2640 | Equipment | BSS_HW_Stuck | Reset Air Scale | Bilal hassan shaukat ali | 07/02/2025 03:42:12 | 08/04/2025 00:14:04 | 07/02/2025 09:42:12 | 1(2G/LTE) sites down under JED2640-P3 | 07/02/2025 03:28:47 | Major | 7706 | BTS O&M LINK FAILURE | 07/02/2025 03:28:47 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE SA | JED2640-P3 | FLM_EM | JED2640 | Results: DOWN SITE HUB JED2640-P3 JED2640 Summary: Hub: JED2640, Down Count: 1, Down Sites: JED2640-P3 Alarm Summary: JED2640 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 07/02/2025 03:42:12 | 07/21/2025 23:08:40 | 08/04/2025 00:13:44 |  |  | 08/04/2025 00:14:04 |  | Bilal hassan shaukat ali |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250702000981 | PCM-20250702-00001486 | TT-20250702-01444 | Telecom | Region_4 | SDY0766 | SDY0766 |  |  |  | Riasat Ali Allah Baksh | 07/02/2025 14:49:25 | 07/02/2025 20:57:29 | 07/03/2025 02:49:25 | PT:: BO need to check High PL at SDY0766/R4 (Optimization Request) | 07/02/2025 14:25:31 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 07/02/2025 14:25:32 | P3 | 2G | alaith | Generator_SG | 2G_3G_LTE_5G NSA | SDY0766 | FLM_TE |  |  | PCM-20250702-00001432 | need check JDJZ0766-JDJZ0767 ,QAL0721-LTH0330 | need check JDJZ0766-JDJZ0767 ,QAL0721-LTH0330 |  |  |  | API | 07/02/2025 14:49:25 | 07/02/2025 20:57:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250702001306 | PCM-20250702-00001881 | TT-20250702-01855 | Reference_telecom | Region_6 | BAH0837 | BAH0837 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | SHAH KHALID | 07/02/2025 17:32:42 | 08/04/2025 22:56:24 | 07/03/2025 05:32:42 | Nokia Eband Observing InternalCommunicationProblem-Port 4/1,DemXpicLOS-P at BAH0837_01-10.221.245.83 | 06/29/2025 15:24:34 | Minor |  | LOF | 06/29/2025 15:24:34 | P1 | 2G | Albaha | Sceco | TX NSA | BAH0837_01-10.221.245.83 | FLM_TE | [8 empty] | API | 07/02/2025 17:32:42 | 07/31/2025 15:46:24 | 08/04/2025 22:56:14 |  |  | 08/04/2025 22:56:24 |  | SHAH KHALID | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250703001477 | PCM-20250703-00002189 | TT-20250703-02191 | Reference_telecom | Region_4 | JDJZ0774 | JDJZ0774 |  |  |  | Junaid Eisa | 07/03/2025 19:10:14 | 07/06/2025 14:57:39 | 07/04/2025 07:10:14 | Degrade observed in JDJZ0774_04 towards 10.21.68.145 @ Sceco | 07/03/2025 07:40:02 | Minor |  | Degrade | 07/03/2025 07:09:42 | VIP | 2G | qunfuddah | Sceco | TX NSA | JDJZ0774 | FLM_TE | [8 empty] | API | 07/03/2025 19:10:14 | [7 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250703001503 | PCM-20250703-00002224 | TT-20250703-02227 | Reference_telecom | Region_6 | BLG0041 | BLG0041 |  |  |  | Muhammad Ali | 07/03/2025 19:28:50 | 08/28/2025 13:34:30 | 07/04/2025 07:28:50 | LinkDown observed in BLG0041 towards 10.221.231.100 @ Sceco | 07/03/2025 07:51:46 | Minor |  | LinkDown | 07/03/2025 07:28:45 | P2 | 2G | jizan | Sceco | TX NSA | BLG0041 | FLM_TE | [8 empty] | API | 07/03/2025 19:28:50 | 07/03/2025 20:30:48 | 08/04/2025 17:35:30 | 08/28/2025 13:03:54 | 08/28/2025 13:34:30 |  |  |  | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250704000193 | PCM-20250704-00000306 | TT-20250704-00404 | Reference_telecom | Region_6 | JIZ1M3074 | JIZ0074 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/04/2025 05:36:36 | 07/04/2025 09:25:59 | 07/04/2025 11:36:36 | BASE STATION OPERATION DEGRADED (Failure in replaceable baseband unit) at JIZ1M3074-P1-VIP-ARP (Ref:TT-20250616-00892) | 01/27/2025 08:56:08 | Major | 7604 | BASE STATION OPERATION DEGRADED | 01/27/2025 08:56:08 | VIP | 3G | jizan | Sceco_STB | 3G SA | JIZ1M3074 | FLM_TE | [8 empty] | API | 07/04/2025 05:36:36 | 07/04/2025 08:05:42 | 07/04/2025 09:25:26 |  |  | 07/04/2025 09:25:59 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250706001154 | PCM-20250706-00001746 | TT-20250706-01699 | Reference_telecom | Region_1 | ARM9841 | ARM9841 |  |  |  | Muhammad Kashif M M Bashir | 07/06/2025 17:25:39 | 07/24/2025 15:53:02 | 07/07/2025 05:25:39 | NEC MW Observing RX Level,LOF,RX Level,LOF,Frame ID,Frame ID at ARM9841_IDU2(ARMCO TOWER)(10.125.143.48) | 07/06/2025 10:33:14 | Minor |  | LOF | 07/06/2025 10:33:14 | P3 | Repeater | hafouf | Generator_SG | TX NSA | ARM9841_IDU2(ARMCO TOWER)(10.125.143.48) | FLM_TE | [8 empty] | API | 07/06/2025 17:25:39 | 07/06/2025 19:29:27 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250706001180 | PCM-20250706-00001774 | TT-20250706-01719 | Telecom | Region_4 | JDJZ0774 | JDJZ0774 | Enviroment | SCECO_Failure | SCECO auto restored | Mudassar Bashir Bashir Ahmad | 07/06/2025 17:32:02 | 07/30/2025 11:52:04 | 07/06/2025 21:32:02 | 1(2G/3G) sites down under JDJZ0774-P1-VIP | 07/06/2025 17:22:08 | Critical | 7706 | BTS O&M LINK FAILURE | 07/06/2025 17:22:08 | VIP | 2G | qunfuddah | Sceco | 2G_3G SA | JDJZ0774-P1-VIP | FLM_TE | JDJZ0774 | Results: DOWN SITE HUB JDJZ0774-P1-VIP JDJZ0774 Summary: Hub: JDJZ0774, Down Count: 1, Down Sites: JDJZ0774-P1-VIP Alarm Summary: JDJZ0774 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 07/06/2025 17:32:02 | 07/21/2025 13:25:40 | 07/30/2025 11:51:57 |  |  | 07/30/2025 11:52:04 |  | Mudassar Bashir Bashir Ahmad | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250706001295 | PCM-20250706-00001967 | TT-20250706-01917 | Reference_telecom | Region_6 | BLG0041 | BLG0041 | Transsmission | MW_HW_stuck | Reset ODU | Muhammad Ali | 07/06/2025 19:06:01 | 08/04/2025 18:04:03 | 07/07/2025 07:06:01 | LinkDown observed in BLG0041_01 towards 10.3.86.162 @ Sceco | 07/06/2025 07:07:50 | Minor |  | LinkDown | 07/06/2025 07:05:34 | P2 | 2G | jizan | Sceco | TX NSA | BLG0041 | FLM_TE | [8 empty] | API | 07/06/2025 19:06:01 | 07/06/2025 19:10:49 | 08/04/2025 18:03:51 |  |  | 08/04/2025 18:04:03 |  | Muhammad Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250706001315 | PCM-20250706-00001997 | TT-20250706-01943 | Reference_telecom | Region_6 | JDJ2040 | JDJ2040 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 07/06/2025 19:26:40 | 08/04/2025 17:29:49 | 07/07/2025 07:26:40 | LinkDown observed in JDJ2040 towards 10.89.249.2 @ Sceco | 07/06/2025 07:28:21 | Minor |  | LinkDown | 07/06/2025 07:26:13 | P3 | 2G | baish | Sceco | TX NSA | JDJ2040 | FLM_TE | [8 empty] | API | 07/06/2025 19:26:40 | 07/31/2025 15:49:57 | 08/02/2025 05:03:45 |  |  | 08/04/2025 17:29:49 |  | Ansir Iqbal Muhammad Iqbal | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250706001329 | PCM-20250706-00002014 | TT-20250706-01963 | Reference_telecom | Region_6 | SAB0055 | SAB0055 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 07/06/2025 19:38:02 | 08/03/2025 19:40:30 | 07/07/2025 07:38:02 | LinkDown observed in SAB0055 towards 10.3.86.154 @ Sceco | 07/06/2025 07:38:50 | Minor |  | LinkDown | 07/06/2025 07:37:45 | P2 | 2G | baish | Sceco | TX NSA | SAB0055 | FLM_TE | [8 empty] | API | 07/06/2025 19:38:02 | 07/31/2025 15:49:58 | 08/03/2025 19:36:52 |  |  | 08/03/2025 19:40:30 |  | Ansir Iqbal Muhammad Iqbal | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250707000013 | PCM-20250707-00000017 | TT-20250707-00020 | MW_HC | Region_1 | JBKH0113 | JBKH0113 |  |  |  | Mohamed Abdelaziz | 07/07/2025 00:16:16 | 07/24/2025 15:53:03 | 07/07/2025 12:16:16 | (as per BO request) NEC HC for PM Errors and RSL degradation observed on NEC MW link JBKH2M0088-JBKH0113 Modem 3,4 | 07/07/2025 00:15:15 | Minor | 1-631 | MW_LOF | 07/07/2025 00:15:15 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH2M0088-JBKH0113 | FLM_TE | [5 empty] | (as per BO request) NEC HC for PM Errors and RSL degradation observed on NEC MW link JBKH2M0088-JBKH0113 Modem 3,4 |  |  | API | 07/07/2025 00:16:16 | 07/07/2025 00:40:58 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250707000101 | PCM-20250707-00000190 | TT-20250707-00161 | Telecom | Region_4 | ASQ0342 | ASQ0342 | Transsmission | MW_RSL_fading | Fading issue | Mudassar Bashir Bashir Ahmad | 07/07/2025 02:21:13 | 07/30/2025 12:05:50 | 07/07/2025 06:21:13 | 12(2G) 7(3G) 1(5G) sites down under UKHA0733-P1-HUB-USF | 07/07/2025 02:01:12 | Critical | 7706 | BTS O&M LINK FAILURE | 07/07/2025 02:01:12 | P1 | 2G | adam | Sceco_STB | 2G_3G_LTE_5G SA | UKHA0731-P1-HUB-USF UKHA0028-P1-HUB UKHA0630-P3-USF ASQ0343-P1-HUB-USF UKHA0733-P1-HUB-USF HJR0149-P2-USF ASQ0342-P1-HUB-USF UKZ0166-P2-USF UKZ0067-P2-USF UKHA0345-P1-HUB UKHA0344-P1-HUB GMK0167-P2-USF | FLM_TE | ASQ0342 | Hub: ASQ0342 We are observing Low BER at site kindly send team to check locally | PCM-20250707-00000166 | Hub: ASQ0342 We are observing Low BER at site kindly send team to check locally | Hub: ASQ0342 We are observing Low BER at site kindly send team to check locally |  | sites down |  | API | 07/07/2025 02:21:13 | 07/21/2025 13:25:41 | 07/30/2025 12:05:42 |  |  | 07/30/2025 12:05:50 |  | Mudassar Bashir Bashir Ahmad | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Access | CM20250707000517 | PCM-20250707-00000834 | TT-20250707-00834 | Reference_telecom | Region_4 | HHR0892 | HHR0892 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sarhan Zaki Ali Mohamed | 07/07/2025 09:54:01 | 08/02/2025 14:17:46 | 07/07/2025 21:54:01 | Nokia Eband Observing ReplaceableUnitProblem-Card - 1 at HHR0892-FTK-10.10.180.147 | 05/29/2025 16:22:30 | Minor |  | LOF | 05/29/2025 16:22:30 | P3 | 2G | jeddah | Sceco | TX NSA | HHR0892-FTK-10.10.180.147 | FLM_TE | [8 empty] | API | 07/07/2025 09:54:01 | 07/15/2025 18:23:09 | 07/15/2025 18:29:59 | 07/15/2025 18:30:10 | 07/15/2025 18:58:09 |  |  | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250707000531 | PCM-20250707-00000848 | TT-20250707-00848 | Reference_telecom | Region_6 | SAB0277 | SAB0277 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 07/07/2025 09:54:17 | 08/03/2025 19:41:48 | 07/07/2025 21:54:17 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Port 1/1 at SAB0277_01-10.89.249.58 | 06/18/2024 22:49:03 | Minor |  | LOF | 06/18/2024 22:49:03 | P1 | 2G | baish | Sceco | TX NSA | SAB0277_01-10.89.249.58 | FLM_TE | [8 empty] | API | 07/07/2025 09:54:17 | 07/07/2025 10:28:51 | 07/07/2025 17:45:58 | 07/08/2025 18:22:25 | 07/08/2025 20:24:56 | 08/03/2025 19:41:48 |  | Ansir Iqbal Muhammad Iqbal | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250707000541 | PCM-20250707-00000858 | TT-20250707-00858 | Reference_telecom | Region_6 | SAB0146 | SAB0146 | Transsmission | MW_HW_fault | Replace ODU | Ansir Iqbal Muhammad Iqbal | 07/07/2025 09:54:30 | 07/26/2025 21:41:08 | 07/07/2025 21:54:30 | Nokia Eband Observing LinkDown-Port 4/5,DemFail-Port 4/5 at SAB0146 _01-10.10.155.179 | 06/28/2025 16:47:30 | Minor |  | LOF | 06/28/2025 16:47:30 | P2 | 2G | baish | Sceco | TX NSA | SAB0146 _01-10.10.155.179 | FLM_TE | [8 empty] | API | 07/07/2025 09:54:30 | 07/26/2025 20:38:46 | 07/26/2025 21:40:35 |  |  | 07/26/2025 21:41:08 |  | Ansir Iqbal Muhammad Iqbal | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250707000545 | PCM-20250707-00000862 | TT-20250707-00862 | EM | Region_3 | MDTB9339 | MDTB9339 | Enviroment | SCECO_Failure | SCECO auto restored | Muhamed Ismail Muhamed Daoud | 07/07/2025 09:55:09 | 07/24/2025 15:02:45 | 07/07/2025 13:55:09 | NEC observing INTRUDER ALARM (INPUT-1) at rep(4780-4781 )-MDTB9339 | 07/07/2025 09:54:46 | Critical | 383 | POWER_ALM | 07/07/2025 09:54:47 | P3 | Repeater | madinah | Sceco | TX NSA | MDTB9339 | FLM_EM | [8 empty] | API | 07/07/2025 09:55:09 | 07/21/2025 13:18:04 | 07/24/2025 15:02:37 |  |  | 07/24/2025 15:02:45 |  | Muhamed Ismail Muhamed Daoud | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Access | CM20250707000914 | PCM-20250707-00001361 | TT-20250707-01396 | Telecom | Region_4 | JED0858 | JED0858 |  |  |  | MALIK ATIF ZAMAN | 07/07/2025 13:57:17 | 07/09/2025 10:50:35 | 07/08/2025 01:57:17 | PT::As per Bo request FLM need to perform HC at JED0858 | 07/07/2025 13:57:09 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 07/07/2025 13:57:09 | VIP | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0858 | FLM_TE | [8 empty] | API | 07/07/2025 13:57:17 | 07/07/2025 18:44:04 | 07/08/2025 10:50:05 | 07/08/2025 10:50:08 | 07/09/2025 10:50:14 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250707001209 | PCM-20250707-00001795 | TT-20250707-01846 | Reference_telecom | Region_2 | SRIY0183 | SRIY0183 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Muhammad Naeem Muhammad Gulzar | 07/07/2025 17:38:46 | 10/12/2025 12:09:36 | 07/07/2025 21:38:46 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN/R2_RY1_HWBSC01 @ Sceco(ref:TT-20250707-01212) | 07/07/2025 12:32:34 | Critical | 301 | NE Is Disconnected | 07/07/2025 12:34:05 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183 | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183 SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183 Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 07/07/2025 17:38:46 | 07/08/2025 02:18:33 | 10/12/2025 12:09:17 |  |  | 10/12/2025 12:09:36 |  | Muhammad Naeem Muhammad Gulzar | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250707001441 | PCM-20250707-00002135 | TT-20250707-02272 | Telecom | Region_4 | JED0418 | JED0418 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 07/07/2025 22:25:53 | 07/22/2025 11:35:02 | 07/08/2025 02:25:53 | 1(2G) site down under JED0418-P1 | 07/07/2025 22:15:48 | Critical | 7706 | BTS O&M LINK FAILURE | 07/07/2025 22:15:48 | P1 | 2G | jeddah | Sceco | 2G SA | JED0418-P1 | FLM_TE | JED0418 | Results: DOWN SITE HUB JED0418-P1 JED0418 Summary: Hub: JED0418, Down Count: 1, Down Sites: JED0418-P1 Alarm Summary: JED0418 No Active Alarm on HUB |  |  |  |  | site down |  | API | 07/07/2025 22:25:53 | 07/08/2025 13:07:25 | 07/22/2025 11:34:55 |  |  | 07/22/2025 11:35:02 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250708000334 | PCM-20250708-00000779 | TT-20250708-00816 | Telecom | Region_4 | JED6070_A | JED6070 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 07/08/2025 07:08:01 | 08/07/2025 14:15:21 | 07/08/2025 13:08:01 | (Flapping Issue) ¦¦ CELL OPERATION DEGRADED(VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP | 07/08/2025 07:03:40 | Major | 7654 | CELL OPERATION DEGRADED | 07/08/2025 07:03:40 | VIP | 2G | jeddah | Sceco | LTE SA | JED1U6070_1-P1-VIP-SHOP | FLM_TE | [8 empty] | API | 07/08/2025 07:08:01 | 07/08/2025 18:12:01 | 08/07/2025 14:15:15 |  |  | 08/07/2025 14:15:21 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250708000442 | PCM-20250708-00000947 | TT-20250708-00949 | MW_HC | Region_6 | BAH0017 | BAH0017 | Transsmission | MW_Problematic | Interference Issue | SHAH KHALID | 07/08/2025 08:14:46 | 08/04/2025 22:56:09 | 07/08/2025 20:14:46 | NEC MW HC_P0 vip Observing Modem Down at BAH0004(10.154.175.99)--BAH0017(10.154.175.100) | 07/08/2025 08:13:24 | Minor |  | LOF | 07/08/2025 08:13:24 | P1 | 2G | Albaha | Sceco | TX NSA | BAH0004(10.154.175.99)--BAH0017(10.154.175.100) | FLM_TE | [8 empty] | API | 07/08/2025 08:14:46 | 07/31/2025 15:46:26 | 08/04/2025 22:55:59 |  |  | 08/04/2025 22:56:09 |  | SHAH KHALID | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250708000565 | PCM-20250708-00001071 | TT-20250708-01072 | MW_HC | Region_4 | JED0948 | JED0948 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 07/08/2025 08:17:14 | 08/02/2025 14:17:42 | 07/08/2025 20:17:14 | Nokia MW HC_P0 Observing Performance Issue at JED0948-JED0154-11 | 07/08/2025 08:13:23 | Minor |  | LOF | 07/08/2025 08:13:23 | P3 | 2G | jeddah | Sceco | TX NSA | JED0948-JED0154-11 | FLM_TE | [8 empty] | API | 07/08/2025 08:17:14 | 07/08/2025 12:06:12 | 07/08/2025 12:33:47 | 07/08/2025 12:33:51 | 07/08/2025 13:12:08 |  |  |  | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250708000628 | PCM-20250708-00001135 | TT-20250708-01138 | MW_HC | Region_2 | RIY0390 | RIY0390 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ejaz Hussain Muhammad Sharif | 07/08/2025 08:18:25 | 09/23/2025 08:37:18 | 07/08/2025 20:18:25 | Huawei HC_P2 Observing Errors at RIY0390-RIY2591 | 07/08/2025 08:13:23 | Minor |  | LOF | 07/08/2025 08:13:23 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0390-RIY2591 | FLM_TE | [8 empty] | API | 07/08/2025 08:18:25 | 09/23/2025 08:37:18 | [5 empty] | Ejaz Hussain Muhammad Sharif | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250708000634 | PCM-20250708-00001141 | TT-20250708-01144 | MW_HC | Region_2 | RIY2300 | RIY2300 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Naseer Muhammad Nazir | 07/08/2025 08:18:33 | 09/29/2025 06:56:12 | 07/08/2025 20:18:33 | Huawei HC_P2 Observing Errors at RIY0228-RIY2300 | 07/08/2025 08:13:23 | Minor |  | LOF | 07/08/2025 08:13:23 | VIP | SRAN | riyadh | Generator_SG | TX NSA | RIY0228-RIY2300 | FLM_TE | [8 empty] | API | 07/08/2025 08:18:33 | 09/23/2025 23:34:36 | 09/29/2025 06:55:49 |  |  | 09/29/2025 06:56:12 |  | Muhammad Naseer Muhammad Nazir | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250708000944 | PCM-20250708-00001536 | TT-20250708-01553 | Reference_telecom | Region_6 | BAH0018 | BAH0018 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SHAH KHALID | 07/08/2025 11:38:17 | 08/04/2025 03:12:59 | 07/08/2025 23:38:17 | Nokia Eband Observing LinkDown-Port 3/5,LinkDown-Port 4/5,DemFail-Port 4 at BAH0018_3-10.221.245.123 | 06/24/2025 19:33:28 | Minor |  | LOF | 06/24/2025 19:33:28 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0018_3-10.221.245.123 | FLM_TE | [8 empty] | API | 07/08/2025 11:38:17 | 07/31/2025 15:46:24 | 08/04/2025 03:12:49 |  |  | 08/04/2025 03:12:59 |  | SHAH KHALID | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250708001673 | PCM-20250708-00002554 | TT-20250708-02613 | Reference_telecom | Region_1 | KFJ2003 | KFJ2003 | Transsmission | MW_HW_fault | Remade Ethernet Connector | Mohamed Abdelaziz | 07/08/2025 19:58:02 | 07/29/2025 20:15:58 | 07/09/2025 07:58:02 | MW RTN Observing ETH_LOS at KFJ2003_NE_9_SDB | 07/05/2025 03:40:30 | Minor |  | LOF | 07/05/2025 03:40:30 | P1 | SRAN | khafji | Sceco | TX NSA | KFJ2003_NE_9_SDB | FLM_TE | [8 empty] | API | 07/08/2025 19:58:02 | 07/09/2025 02:56:08 | 07/29/2025 19:53:58 | 07/29/2025 19:54:11 | 07/29/2025 19:54:55 | 07/29/2025 20:15:58 |  | Mohamed Abdelaziz | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250708001710 | PCM-20250708-00002591 | TT-20250708-02650 | Reference_telecom | Region_1 | DRN0102 | DRN0102 | Transsmission | MW_LOW_RSL | Link Alignment Issue | Junaid Eisa | 07/08/2025 19:58:42 | 07/20/2025 16:47:10 | 07/09/2025 07:58:42 | NEC MW Observing LOF,ODU CPU / Cable Open,LOF,ODU CPU / Cable Open at DRN0102(10.74.82.98) | 02/08/2024 11:47:12 | Minor |  | LOF | 02/08/2024 11:47:12 | P3 | SRAN | dammam | Sceco | TX NSA | DRN0102 | FLM_TE | [8 empty] | API | 07/08/2025 19:58:42 | [6 empty] | Shakeel Ahmad Ghulam Murtaza | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250709000054 | PCM-20250709-00000083 | TT-20250709-00103 | Reference_telecom | Region_6 | DMD0043 | DMD0043 | Transsmission | MW_HW_fault | Replace ODU | Zeshan Ali Adnan | 07/09/2025 00:59:58 | 07/31/2025 18:06:45 | 07/09/2025 12:59:58 | LagPortDown observed in DMD0043 towards 10.74.124.120 @ Sceco | 07/08/2025 13:00:16 | Minor |  | LagPortDown | 07/08/2025 12:59:50 | P2 | 2G | jizan | Sceco | TX NSA | DMD0043 | FLM_TE | [8 empty] | API | 07/09/2025 00:59:58 | 07/26/2025 22:35:48 | 07/31/2025 18:06:26 | 07/31/2025 18:06:31 |  | 07/31/2025 18:06:45 |  | Zeshan Ali Adnan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250709000375 | PCM-20250709-00000579 | TT-20250709-00592 | Reference_telecom | Region_4 | JED0365-ZJe03-CSG-06 | JED0365 |  |  |  | Ahmed Adel Abdelaziz elkholy | 07/09/2025 07:46:14 | 07/09/2025 11:54:20 | 07/09/2025 11:46:14 | Physical Port Down at JED0365-ZJe03-CSG-06REF:TT-20250127-01509 @ Sceco | 07/09/2025 00:40:28 | Critical | 101-2505274 | Physical Port Down | 07/09/2025 00:40:19 | P1 | IPRAN | jeddah | Sceco | IPRAN SA | JED0365-ZJe03-CSG-06 | FLM_TE | [8 empty] | API | 07/09/2025 07:46:14 | 07/09/2025 11:54:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250709000378 | PCM-20250709-00000585 | TT-20250709-00596 | Reference_telecom | Region_4 | JED0238-ZJe05-CSG-06 | JED0238 | Equipment | BTS_Cable | Replace Fiber Cable | BARKAT ALI MAIN HILAL | 07/09/2025 07:49:23 | 07/09/2025 13:16:23 | 07/09/2025 19:49:23 | Optical Invalid at JED0238-ZJe05-CSG-06 REF:TT-20250127-01509 @ Sceco | 07/09/2025 00:53:10 | Minor | 101-2505224 | Optical Invalid | 07/09/2025 00:52:52 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0238-ZJe05-CSG-06 | FLM_TE | [8 empty] | API | 07/09/2025 07:49:23 | 07/09/2025 11:35:32 | 07/09/2025 11:36:00 | 07/09/2025 11:36:03 | 07/09/2025 11:36:09 | 07/09/2025 13:16:23 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250709000534 | PCM-20250709-00000819 | TT-20250709-00846 | Reference_telecom | Region_6 | TNM0727 | TNM0727 | Transsmission | SFP_Transmission | Replace SFP | Fawad Khan | 07/09/2025 10:01:24 | 08/04/2025 15:03:37 | 07/09/2025 22:01:24 | ReplaceableUnitMissing observed in TNM0727_01 towards 10.221.247.84 @ Sceco | 07/08/2025 22:00:59 | Minor |  | ReplaceableUnitMissing | 07/08/2025 22:00:55 | P2 | 2G | mohail | Sceco | TX NSA | TNM0727 | FLM_TE | [8 empty] | API | 07/09/2025 10:01:24 | 07/09/2025 11:25:58 | 08/04/2025 15:02:56 |  |  | 08/04/2025 15:03:37 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250709000711 | PCM-20250709-00001062 | TT-20250709-01115 | Reference_telecom | Region_4 | JED0927 | JED0927 |  |  |  | Mohammed Ramadan A Abu Abid | 07/09/2025 12:20:50 | 08/02/2025 14:17:43 | 07/10/2025 00:20:50 | Nokia Eband Observing FanFailure-fanTray-1,ReplaceableUnitProblem-fanTra at JED0927-10.10.138.183 | 03/03/2025 13:14:47 | Minor |  | LOF | 03/03/2025 13:14:47 | VIP | 2G | jeddah | Sceco | TX NSA | JED0927-10.10.138.183 | FLM_TE | [8 empty] | API | 07/09/2025 12:20:50 | 07/09/2025 13:13:40 | 07/10/2025 13:14:09 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250709000717 | PCM-20250709-00001068 | TT-20250709-01121 | Reference_telecom | Region_6 | JIZ0406 | JIZ0406 | Transsmission | MW_HW_fault | Replace ODU | Zeshan Ali Adnan | 07/09/2025 12:20:58 | 07/31/2025 18:06:06 | 07/10/2025 00:20:58 | Nokia Eband Observing LagPortDown-Port 4/1,LagPortDown-Port 4/2 at JIZ0406-10.74.124.50 | 06/12/2025 15:42:04 | Minor |  | LOF | 06/12/2025 15:42:04 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0406-10.74.124.50 | FLM_TE | [8 empty] | API | 07/09/2025 12:20:58 | 07/26/2025 22:35:48 | 07/31/2025 18:05:49 | 07/31/2025 18:05:51 |  | 07/31/2025 18:06:06 |  | Zeshan Ali Adnan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250709001127 | PCM-20250709-00001604 | TT-20250709-01727 | Reference_telecom | Region_3 | DBQL0258 | DBQL0258 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Junaid Eisa | 07/09/2025 16:36:26 | 07/20/2025 09:48:36 | 07/10/2025 04:36:26 | NEC MW Observing Radio Traffic Aggregation Link at DBQL0258(10.74.87.242) | 06/16/2025 10:44:34 | Minor |  | LOF | 06/16/2025 10:44:34 | P2 | SRAN | tabouk | Sceco_STB | TX NSA | DBQL0258 | FLM_TE | [8 empty] | API | 07/09/2025 16:36:26 | [6 empty] | Hossam Ali Ahmed Ali | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250709001158 | PCM-20250709-00001635 | TT-20250709-01758 | Reference_telecom | Region_1 | JBL0757 | JBL0757 |  |  |  | Junaid Eisa | 07/09/2025 16:37:01 | 07/20/2025 16:47:48 | 07/10/2025 04:37:01 | NEC MW Observing FAN FAIL at JBL0757(10.248.32.39) | 06/14/2025 11:37:54 | Minor |  | LOF | 06/14/2025 11:37:54 | P3 | SRAN | jubail | Sceco | TX NSA | JBL0757 | FLM_TE | [8 empty] | API | 07/09/2025 16:37:01 | [7 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250710001357 | PCM-20250710-00001891 | TT-20250710-01907 | Reference_telecom | Region_6 | ABH0004 | ABH0004 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Amir Sohail | 07/10/2025 19:42:06 | 08/13/2025 14:34:22 | 07/11/2025 07:42:06 | LinkDown observed in ABH0004_02 towards 10.89.249.146 @ Sceco | 07/10/2025 07:40:03 | Minor |  | LinkDown | 07/10/2025 07:40:00 | P2 | 2G | abha | Sceco | TX NSA | ABH0004 | FLM_TE | [8 empty] | API | 07/10/2025 19:42:06 | 07/10/2025 19:45:45 | 07/31/2025 18:30:04 |  |  | 08/13/2025 14:34:22 |  | Amir Sohail | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250710001423 | PCM-20250710-00001992 | TT-20250710-02032 | Reference_telecom | Region_4 | JDJZ0776 | JDJZ0776 | Transsmission | MW_HW_fault | Replace ODU | Mudassar Bashir Bashir Ahmad | 07/10/2025 21:39:23 | 08/02/2025 16:12:53 | 07/11/2025 09:39:23 | LinkDown observed in JDJZ0776_11 towards 10.221.243.241 @ Sceco_STB | 07/10/2025 09:41:20 | Minor |  | LinkDown | 07/10/2025 09:39:10 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0776 | FLM_TE | [8 empty] | API | 07/10/2025 21:39:23 | 08/02/2025 16:12:53 | [5 empty] | Mudassar Bashir Bashir Ahmad | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250710001454 | PCM-20250710-00002034 | TT-20250710-02088 | Reference_telecom | Region_6 | MRD0093 | MRD0093 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Fawad Khan | 07/10/2025 22:25:53 | 08/04/2025 15:04:56 | 07/11/2025 10:25:53 | LinkDown observed in MRD0093_02 towards 10.221.243.84 @ Sceco | 07/10/2025 10:27:41 | Minor |  | LinkDown | 07/10/2025 10:25:49 | P2 | 2G | mohail | Sceco | TX NSA | MRD0093 | FLM_TE | [8 empty] | API | 07/10/2025 22:25:53 | 07/11/2025 01:47:24 | 08/04/2025 15:03:51 |  |  | 08/04/2025 15:04:56 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250711000639 | PCM-20250711-00000776 | TT-20250711-00818 | Reference_telecom | Region_4 | JZMA0825 | JZMA0825 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 07/11/2025 04:09:28 | 08/10/2025 15:50:31 | 07/11/2025 16:09:28 | LinkDown observed in JZMA0825_02 towards 10.74.120.83 @ Sceco | 07/10/2025 16:11:33 | Minor |  | LinkDown | 07/10/2025 16:09:10 | P2 | 2G | qunfuddah | Sceco | TX NSA | JZMA0825 | FLM_TE | [8 empty] | API | 07/11/2025 04:09:28 | 08/02/2025 16:12:53 | 08/10/2025 15:50:25 |  |  | 08/10/2025 15:50:31 |  | Mudassar Bashir Bashir Ahmad | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250711000895 | PCM-20250711-00001177 | TT-20250711-01214 | Reference_telecom | Region_6 | MKW9706 | MKW9706 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 07/11/2025 10:31:17 | 08/04/2025 23:04:26 | 07/11/2025 22:31:17 | DemFail observed in MKW9706_02 towards 10.221.243.25 @ Sceco | 07/10/2025 22:32:02 | Minor |  | DemFail | 07/10/2025 22:31:00 | P3 | Repeater | makhwa | Sceco | TX NSA | MKW9706 | FLM_TE | [8 empty] | API | 07/11/2025 10:31:17 | 07/31/2025 15:46:25 | 08/04/2025 23:04:16 |  |  | 08/04/2025 23:04:26 |  | SHAH KHALID | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250712000459 | PCM-20250712-00000641 | TT-20250712-00673 | EM | Region_3 | TBK9044 | TBK9044 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Moustafa Samir Omar | 07/12/2025 09:36:56 | 07/26/2025 16:32:34 | 07/12/2025 13:36:56 | NEC Observing MAIN AC FAIL alarm active at TBK9044 | 07/12/2025 09:30:48 | Critical | 383 | POWER_ALM | 07/12/2025 09:30:48 | P3 | Repeater | tabouk | Generator_DG | TX NSA | TBK9044 | FLM_EM | [5 empty] | NEC Observing MAIN AC FAIL alarm active at TBK9044 |  |  | API | 07/12/2025 09:36:56 | 07/12/2025 12:50:16 | 07/26/2025 16:26:03 | 07/26/2025 16:26:10 | 07/26/2025 16:26:17 | 07/26/2025 16:32:34 |  | Moustafa Samir Omar | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250712000772 | PCM-20250712-00001079 | TT-20250712-00622 | Reference_EM | Region_4 | JED0383 | JED0383 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 07/12/2025 14:02:52 | 07/25/2025 18:12:24 | 07/12/2025 20:02:52 | 1(2G/LTE) site down under JED0383-P3 (Ref:TT-20250711-01990) | 07/12/2025 00:17:19 | Major | 7706 | BTS O&M LINK FAILURE | 07/12/2025 00:17:19 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED0383-P3 | FLM_TE | JED0383 | Results: DOWN SITE HUB JED0383-P3 JED0383 Summary: Hub: JED0383, Down Count: 1, Down Sites: JED0383-P3 Alarm Summary: JED0383 No Active Alarm on HUB | PCM-20250712-00000595 | Team reach site and found access issue due to owner not found and request to come tomorrow afternoon /EM team confirmed no power issue | Team reach site and found access issue due to owner not found and request to come tomorrow afternoon /EM team confirmed no power issue |  | site down |  | API | 07/12/2025 14:02:52 | 07/12/2025 14:56:48 | 07/25/2025 18:12:15 |  |  | 07/25/2025 18:12:24 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250712001004 | PCM-20250712-00001367 | TT-20250712-00982 | Telecom | Region_4 | RAB2163 | RAB2163 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Khizer Hayat | 07/12/2025 16:15:50 | 07/27/2025 18:12:16 | 07/12/2025 22:15:50 | BASE STATION CONNECTIVITY PROBLEM(GTP-U Path Failure) at RAB2163-G9-L8-L18-L21-NR2.6-SBTS-P3 | 07/12/2025 12:33:21 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 07/12/2025 12:33:21 | P3 | 2G | jeddah | Sceco | LTE SA | RAB2163-G9-L8-L18-L21-NR2.6-SBTS-P3 | FLM_TE |  |  | PCM-20250712-00001258 | Dear FLM team, kindly check visibility down RAB0966 | Dear FLM team, kindly check visibility down RAB0966 |  |  |  | API | 07/12/2025 16:15:50 | 07/12/2025 18:20:03 | 07/27/2025 18:12:09 |  |  | 07/27/2025 18:12:16 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250712001416 | PCM-20250712-00001964 | TT-20250712-01993 | EM | Region_3 | TBK9042 | TBK9042 | Enviroment | SCECO_Failure | SCECO auto restored | Abdelwahab Mahmoud Abdelwahab Abboud | 07/12/2025 22:52:15 | 07/22/2025 06:28:45 | 07/13/2025 02:52:15 | RELAY_ALARM_CRITICAL At TBK9042_NE_2 15-CSHNU-DC Power failure:1 | 07/01/2025 17:28:06 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 07/12/2025 22:41:32 | P1 | Repeater | tabouk | Sceco_STB | TX NSA | TBK9042_NE_2 | FLM_EM | [5 empty] | RELAY_ALARM_CRITICAL At TBK9042_NE_2 15-CSHNU-DC Power failure:1 |  |  | API | 07/12/2025 22:52:15 | 07/22/2025 01:10:55 | 07/22/2025 06:28:38 |  |  | 07/22/2025 06:28:45 |  | Abdelwahab Mahmoud Abdelwahab Abboud | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250713000039 | PCM-20250713-00000073 | TT-20250713-00070 | Reference_telecom | Region_4 | BHR2989 | BHR2989 | Transsmission | MW_HW_stuck | Reset Control Card | Moustafa Mahmoud Ahmed Fathelbab | 07/13/2025 00:59:10 | 08/02/2025 14:39:59 | 07/13/2025 12:59:10 | Degrade observed in BHR2989_02 towards 10.3.234.71 @ Sceco | 07/12/2025 12:59:38 | Minor |  | Degrade | 07/12/2025 12:58:50 | P3 | 2G | jeddah | Sceco | TX NSA | BHR2989 | FLM_TE | [8 empty] | API | 07/13/2025 00:59:10 | 08/02/2025 14:17:06 | 08/02/2025 14:39:43 |  |  | 08/02/2025 14:39:59 |  | Moustafa Mahmoud Ahmed Fathelbab | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20250713000366 | PCM-20250713-00000561 | TT-20250713-00565 | Reference_telecom | Region_4 | JZMA9072 | JZMA9072 |  |  |  | Mudassar Bashir Bashir Ahmad | 07/13/2025 07:37:30 | 08/04/2025 18:57:05 | 07/13/2025 19:37:30 | LossOfSignal observed in JZMA9072_01 towards 10.74.120.84 @ Sceco_STB | 07/12/2025 19:39:07 | Minor |  | LossOfSignal | 07/12/2025 19:37:11 | P3 | Repeater | qunfuddah | Sceco_STB | TX NSA | JZMA9072 | FLM_TE | [8 empty] | API | 07/13/2025 07:37:30 | 07/13/2025 12:38:08 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250713000471 | PCM-20250713-00000706 | TT-20250713-00664 | Telecom | Region_4 | DAF0476 | DAF0476 | Equipment | BTS_Cable | Replace Fiber Cable | Bilal hassan shaukat ali | 07/13/2025 08:57:45 | 08/18/2025 00:23:20 | 07/13/2025 14:57:45 | BASE STATION CONNECTIVITY PROBLEM(NR GTP-U Path Failure) at 4 sites under R4 | 07/13/2025 08:33:42 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 07/13/2025 08:33:42 | P2 | 2G | jeddah | Sceco | 5G SA | DAF0476-G9-L8-L18-L21-NR2.6-SBTS-P2 KHL0477-G9-L8-L18-L21-NR2.6-SBTS-P2 KHL0472-G9-L18-L21-NR2.6-SBTS-P1-HUB KHL0709-G9-L8-L18-L21-NR2.6-SBTS-P2 | FLM_TE |  |  | PCM-20250713-00000666 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 07/13/2025 08:57:45 |  | 08/17/2025 22:09:04 | 08/17/2025 22:12:05 | 08/17/2025 22:12:08 | 08/18/2025 00:23:20 |  | Bilal hassan shaukat ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250713000735 | PCM-20250713-00001081 | TT-20250713-01049 | Telecom | Region_6 | DAR0952 | DAR0952 | Transsmission | MW_RSL_fading | Bad Weather | Muhammad Ali | 07/13/2025 11:55:49 | 07/14/2025 10:13:11 | 07/13/2025 15:55:49 | 27(2G/3G/LTE) sites down under DAR0952-P1-HUB @ Sceco | 07/13/2025 11:43:16 | Critical | 7706 | BTS O&M LINK FAILURE | 07/13/2025 11:43:16 | P1 | 2G | raith | Sceco | 2G_3G SA | DAR2913-P3,RTH0653-P3,RTH0606-P2,RTH0601-P2,RTH0652-P2,DAR0921-P2,RTH0651-P3,DAR0952-P1-HUB,DAR0953-P2,DAR0913-P2,DAR0918-P2,DAR0915-P2,DAR0917-P2,DAR0951-P1,DAR0916-P2,RTH0604-P2,RTH0605-P3,DAR0198-P2,DAR2013-P3,DAR0923-P1-HUB,RTH0954-P2,RTH0603-P2,MHL0131-P3,MHL0132-P3,MHL0776-P3-CAP,MHL0858-P3-CAP,MHL0180-P2 | FLM_TE | DAR2913 | Results: DOWN SITE HUB DAR2913-P3 DAR2913 RTH0653-P3 Need to check RTH0606-P2 Need to check RTH0601-P2 Need to check RTH0652-P2 Need to check DAR0921-P2 DAR0923 RTH0651-P3 Need to check DAR0952-P1-HUB DAR0952 DAR0953-P2 DAR0952 DAR0913-P2 DAR0923 DAR0918-P2 DAR0923 DAR0915-P2 DAR0923 DAR0917-P2 DAR0923 DAR0951-P1 DAR0923 DAR0916-P2 DAR0923 RTH0604-P2 Need to check RTH0605-P3 Need to check DAR0198-P2 DAR0923 DAR2013-P3 DAR0923 DAR0923-P1-HUB DAR0923 RTH0954-P2 Need to check RTH0603-P2 Need to check MHL0131-P3 Need to check MHL0132-P3 MHL0132 MHL0776-P3-CAP MHL0776 MHL0858-P3-CAP MHL0858 MHL0180-P2 Need to check Summary: Hub: DAR2913, Down Count: 1, Down Sites: DAR2913-P3 Hub: DAR0923, Down Count: 10, Down Sites: DAR0921-P2, DAR0913-P2, DAR0918-P2, DAR0915-P2, DAR0917-P2, DAR0951-P1, DAR0916-P2, DAR0198-P2, DAR2013-P3, DAR0923-P1-HUB Hub: DAR0952, Down Count: 2, Down Sites: DAR0952-P1-HUB, DAR0953-P2 Hub: MHL0132, Down Count: 1, Down Sites: MHL0132-P3 Hub: MHL0776, Down Count: 1, Down Sites: MHL0776-P3-CAP Hub: MHL0858, Down Count: 1, Down Sites: MHL0858-P3-CAP Alarm Summary: DAR2913 No Active Alarm on HUB HUB site not found DAR0923 Alarm Active on HUB DAR0952 No Active Alarm on HUB MHL0132 Alarm Active on HUB MHL0776 Alarm Active on HUB MHL0858 Alarm Active on HUB |  |  |  |  | sites down |  | API | 07/13/2025 11:55:49 | 07/13/2025 12:38:48 | 07/13/2025 12:39:09 |  |  | 07/13/2025 13:28:59 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250713001467 | PCM-20250713-00002154 | TT-20250713-02063 | Reference_telecom | Region_6 | ABH0004 | ABH0004 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Amir Sohail | 07/13/2025 19:39:48 | 08/13/2025 14:36:58 | 07/14/2025 07:39:48 | LinkDown observed in ABH0004_01 towards 10.89.249.148 @ Sceco | 07/13/2025 07:39:38 | Minor |  | LinkDown | 07/13/2025 07:39:34 | P2 | 2G | abha | Sceco | TX NSA | ABH0004 | FLM_TE | [8 empty] | API | 07/13/2025 19:39:48 | 07/13/2025 20:22:02 | 08/13/2025 14:36:40 |  |  | 08/13/2025 14:36:58 |  | Amir Sohail | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250714000020 | PCM-20250714-00000027 | TT-20250713-01740 | Telecom | Region_4 | JED1MN0503 | JED0503 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 07/14/2025 00:13:21 | 07/22/2025 12:30:08 | 07/14/2025 06:13:21 | BASE STATION CONNECTIVITY PROBLEM(NR GTP-U Path Failure) at 4 sites under R4 | 07/13/2025 16:48:31 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 07/13/2025 16:48:31 | P3 | 5G | jeddah | Sceco | 5G SA | JED1MN0503-NR2.6 HHR1MN0448-NR2.6-P1-VIP-HHR JED1MN2319-NR2.6-P3 JED1MN0921-NR2.6-P3 | FLM_TE |  |  | PCM-20250713-00001820 | PL observed at site during alarm time, FLM need to check and close with RCA. | PL observed at site during alarm time, FLM need to check and close with RCA. |  |  |  | API | 07/14/2025 00:13:21 | 07/14/2025 10:25:30 | 07/22/2025 12:30:00 |  |  | 07/22/2025 12:30:08 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250714000457 | PCM-20250714-00000662 | TT-20250705-01964 | Telecom | Region_2 | RIYB6156 | RIYB6156 |  |  |  | Bilal Ahmad Zahir Ullah | 07/14/2025 08:55:09 | 07/14/2025 11:14:26 | 07/14/2025 14:55:09 | HC:: Multiple Alarms Active at Site RIYB6156 ¦ FLM Need To Check | 07/05/2025 15:50:31 | Major |  | Health Check-WO to TE FME | 07/05/2025 15:50:31 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYB6156 | FLM_TE |  |  | PCM-20250709-00000763 | alarms still active , please check and update as per mail shared attached for further more troubleshooting | alarms still active , please check and update as per mail shared attached for further more troubleshooting |  |  |  | API | 07/14/2025 08:55:09 | 07/14/2025 11:14:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250714000459 | PCM-20250714-00000666 | TT-20250705-01963 | Telecom | Region_2 | RIYA6003 | RIYA6003 | Equipment | BSS_HW_Stuck | Reset Controller Card | Ali Raza Abdi Syed Muhammad Taqi Abdi | 07/14/2025 08:56:52 | 09/21/2025 12:32:35 | 07/14/2025 14:56:52 | HC:: Multiple Alarms Active at Site RIYA6003 ¦ FLM Need To Check | 07/05/2025 15:50:31 | Major |  | Health Check-WO to TE FME | 07/05/2025 15:50:31 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYA6003 | FLM_TE |  |  | PCM-20250709-00000762 | alarms still active , please check and update as per mail shared attached for further more troubleshooting | alarms still active , please check and update as per mail shared attached for further more troubleshooting |  |  |  | API | 07/14/2025 08:56:52 | 07/23/2025 12:21:46 | 07/28/2025 14:52:54 | 07/28/2025 14:53:34 | 07/28/2025 14:53:55 | 09/21/2025 12:32:35 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250714000972 | PCM-20250714-00001345 | TT-20250714-01427 | Telecom | Region_6 | KMBS0673 | KMBS0673 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Saddam Hussain Shah Nawaz Khan | 07/14/2025 14:44:08 | 08/21/2025 12:04:11 | 07/15/2025 02:44:08 | ODU CPU / Cable Open at KMBS0673 on 10.1.173.149 @ Generator_SG | 07/14/2025 14:43:19 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 07/14/2025 14:27:05 | P2 | 2G | bisha | Generator_SG | TX NSA | KMBS0673 | FLM_TE | [8 empty] | API | 07/14/2025 14:44:08 | 07/31/2025 18:37:36 | 08/21/2025 12:03:59 |  |  | 08/21/2025 12:04:11 |  | Saddam Hussain Shah Nawaz Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20250715001046 | PCM-20250715-00001441 | TT-20250715-01438 | Reference_telecom | Region_4 | JDJZ0773 | JDJZ0773 |  |  |  | Mudassar Bashir Bashir Ahmad | 07/15/2025 14:24:07 | 08/04/2025 18:57:36 | 07/16/2025 02:24:07 | Nokia Eband Observing ReplaceableUnitMissing-Port 1/8,ReplaceableUnitMis at JDJZ0773_02-10.10.183.122 | 06/21/2025 14:30:08 | Minor |  | LOF | 06/21/2025 14:30:08 | P2 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0773_02-10.10.183.122 | FLM_TE | [8 empty] | API | 07/15/2025 14:24:07 | 07/15/2025 15:15:25 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250715001148 | PCM-20250715-00001547 | TT-20250715-01541 | MW_HC | Region_1 | DMHF0078 | DMHF0078 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/15/2025 14:26:06 | 07/24/2025 15:53:11 | 07/16/2025 02:26:06 | NEC MW HC_P0 Observing Performance Issue at DMHF0078(10.74.77.4)--HMBY0422(10.74.77.5) | 07/15/2025 14:22:06 | Minor |  | LOF | 07/15/2025 14:22:06 | P1 | SRAN | dammam | Generator_SG | TX NSA | DMHF0078(10.74.77.4)--HMBY0422(10.74.77.5) | FLM_TE | [8 empty] | API | 07/15/2025 14:26:06 | 07/15/2025 15:16:57 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250715001149 | PCM-20250715-00001548 | TT-20250715-01542 | MW_HC | Region_1 | JBKH0110 | JBKH0110 |  |  |  | Mohamed Abdelaziz | 07/15/2025 14:26:07 | 07/24/2025 15:53:18 | 07/16/2025 02:26:07 | NEC MW HC_P0 Observing Performance Issue at JBKH0110(10.159.106.230)--JBKH0112(10.159.106.229) | 07/15/2025 14:22:06 | Minor |  | LOF | 07/15/2025 14:22:06 | P1 | SRAN | jubail | Generator_SG | TX NSA | JBKH0110(10.159.106.230)--JBKH0112(10.159.106.229) | FLM_TE | [8 empty] | API | 07/15/2025 14:26:07 | 07/21/2025 18:22:55 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250715001154 | PCM-20250715-00001552 | TT-20250715-01546 | MW_HC | Region_1 | DMHF0078 | DMHF0078 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 07/15/2025 14:26:11 | 07/24/2025 15:53:12 | 07/16/2025 02:26:11 | NEC MW HC_P1 Observing Performance Issue at DMHF0078(10.74.77.17)--DMHF2077(10.74.77.18) | 07/15/2025 14:22:06 | Minor |  | LOF | 07/15/2025 14:22:06 | P1 | SRAN | dammam | Generator_SG | TX NSA | DMHF0078(10.74.77.17)--DMHF2077(10.74.77.18) | FLM_TE | [8 empty] | API | 07/15/2025 14:26:11 | 07/15/2025 15:16:57 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250715001155 | PCM-20250715-00001553 | TT-20250715-01547 | MW_HC | Region_1 | HFBD0010 | HFBD0010 |  |  |  | Muhammad Kashif M M Bashir | 07/15/2025 14:26:12 | 07/24/2025 15:53:14 | 07/16/2025 02:26:12 | NEC MW HC_P0 Observing Performance Issue at HFBD0010(10.154.27.10)--HFBD0015(10.154.27.1) | 07/15/2025 14:22:06 | Minor |  | LOF | 07/15/2025 14:22:06 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFBD0010(10.154.27.10)--HFBD0015(10.154.27.1) | FLM_TE | [8 empty] | API | 07/15/2025 14:26:12 | 07/15/2025 20:55:14 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250715001156 | PCM-20250715-00001554 | TT-20250715-01548 | MW_HC | Region_1 | KFKM0785 | KFKM0785 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 07/15/2025 14:26:13 | 07/24/2025 15:53:08 | 07/16/2025 02:26:13 | NEC MW HC_P0 Observing Performance Issue at KFKM0785(10.159.105.148)--KFKM0786(10.159.105.147) | 07/15/2025 14:22:06 | Minor |  | LOF | 07/15/2025 14:22:06 | P3 | SRAN | hafr | Generator_SG | TX NSA | KFKM0785(10.159.105.148)--KFKM0786(10.159.105.147) | FLM_TE | [8 empty] | API | 07/15/2025 14:26:13 | 07/15/2025 14:47:24 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250715001162 | PCM-20250715-00001560 | TT-20250715-01554 | MW_HC | Region_1 | ARM0826 | ARM0826 |  |  |  | Mohamed Magdy Fouad Zayed | 07/15/2025 14:26:20 | 07/24/2025 15:53:07 | 07/16/2025 02:26:20 | NEC MW HC_P2 Observing Modem Down at ARM0826(10.125.143.49)--ARM9841(10.125.143.48) | 07/15/2025 14:22:06 | Minor |  | LOF | 07/15/2025 14:22:06 | VIP | SRAN | hafouf | Generator_SG | TX NSA | ARM0826(10.125.143.49)--ARM9841(10.125.143.48) | FLM_TE | [8 empty] | API | 07/15/2025 14:26:20 | 07/15/2025 14:32:33 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250716001098 | PCM-20250716-00001544 | TT-20250716-01657 | Reference_telecom | Region_6 | BSA0450 | BSA0450 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Saddam Hussain Shah Nawaz Khan | 07/16/2025 15:54:46 | 08/04/2025 12:55:19 | 07/17/2025 03:54:46 | LinkDown observed in BSA0450_02 towards 10.221.245.39 @ Sceco | 07/16/2025 03:54:31 | Minor |  | LinkDown | 07/16/2025 03:54:25 | P3 | 2G | bisha | Sceco | TX NSA | BSA0450 | FLM_TE | [8 empty] | API | 07/16/2025 15:54:46 | 07/16/2025 17:13:50 | 08/04/2025 12:54:05 |  |  | 08/04/2025 12:55:19 |  | Saddam Hussain Shah Nawaz Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250716001104 | PCM-20250716-00001551 | TT-20250716-01666 | Reference_telecom | Region_6 | TBL9723 | TBL9723 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Saddam Hussain Shah Nawaz Khan | 07/16/2025 15:58:53 | 08/04/2025 12:55:49 | 07/17/2025 03:58:53 | DemFail observed in TBL9723_01 towards 10.221.245.40 @ Sceco | 07/16/2025 03:58:54 | Minor |  | DemFail | 07/16/2025 03:58:35 | P3 | Repeater | bisha | Sceco | TX NSA | TBL9723 | FLM_TE | [8 empty] | API | 07/16/2025 15:58:53 | 07/31/2025 18:37:37 | 08/04/2025 12:55:34 |  |  | 08/04/2025 12:55:49 |  | Saddam Hussain Shah Nawaz Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250716001408 | PCM-20250716-00001973 | TT-20250716-02049 | Telecom | Region_1 | DAM2U6739 | DAM6039 |  |  |  | Meraj Husain Idd Baksh | 07/16/2025 18:46:22 | 07/20/2025 10:50:43 | 07/17/2025 06:46:22 | Cell Capability Degraded at DAM2U6739-P2 @ Sceco | 07/16/2025 18:30:55 | Minor | 29243 | Cell Capability Degraded | 07/16/2025 18:35:06 | P2 | 4G | dammam | Sceco | 2G NSA | DAM2U6739 | FLM_TE |  |  | PCM-20250716-00001947 | Dear FLM, Kindly check locally as HWs down | Dear FLM, Kindly check locally as HWs down |  |  |  | API | 07/16/2025 18:46:22 | 07/16/2025 19:27:35 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250717000129 | PCM-20250717-00000212 | TT-20250717-00232 | Reference_telecom | Region_4 | SJED1S7378 | SJED0378 |  |  |  | Mohammed Ramadan A Abu Abid | 07/17/2025 03:26:03 | 07/31/2025 13:06:40 | 07/17/2025 09:26:03 | 1(LTE) sites down under SJED0378-CA-P3 @ Sceco (Ref.::TT-20250630-00600) | 06/30/2025 07:35:09 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 06/30/2025 07:35:09 | P3 | 4G | jeddah | Sceco | LTE SA | SJED1S7378-CA-P3 | FLM_TE | SJED1S7378 | Results: DOWN SITE HUB SJED1S7378-CA-P3 SJED1S7378 Summary: Hub: SJED1S7378, Down Count: 1, Down Sites: SJED1S7378-CA-P3 Alarm Summary: SJED1S7378 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 07/17/2025 03:26:03 | 07/17/2025 06:39:37 | 07/17/2025 09:13:21 | [5 empty] | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250717000179 | PCM-20250717-00000281 | TT-20250717-00311 | Reference_telecom | Region_6 | MRD0093 | MRD0093 | Transsmission | SFP_Transmission | Replace SFP | Fawad Khan | 07/17/2025 04:39:57 | 08/04/2025 21:21:35 | 07/17/2025 16:39:57 | LossOfSignal observed in MRD0093_04 towards 10.221.247.83 @ Sceco | 07/16/2025 16:39:51 | Minor |  | LossOfSignal | 07/16/2025 16:39:46 | P2 | 2G | mohail | Sceco | TX NSA | MRD0093 | FLM_TE | [8 empty] | API | 07/17/2025 04:39:57 | 07/17/2025 08:00:07 | 07/31/2025 11:15:32 |  |  | 08/04/2025 21:21:35 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250717000915 | PCM-20250717-00001344 | TT-20250717-01333 | Reference_telecom | Region_6 | BSA2006 | BSA2006 | Equipment | SFP_BTS | Clean SFP | Saddam Hussain Shah Nawaz Khan | 07/17/2025 15:03:40 | 07/17/2025 19:07:51 | 07/17/2025 21:03:40 | Fronthaul loop back connectivity check failure (Fronthaul loop back connectivity check failure) at BSA2006-P3 (Ref:TT-20250711-00177) | 07/16/2025 09:14:56 | Major | 7706 | BTS O&M LINK FAILURE | 07/16/2025 09:14:56 | P3 | 2G | bisha | Generator_SG | 2G SA | BSA2006 | FLM_TE | BSA2006 | Results: DOWN SITE HUB BSA2006 BSA2006 Summary: Hub: BSA2006, Down Count: 1, Down Sites: BSA2006 Alarm Summary: BSA2006 No Active Alarm on HUB | [6 empty] | API | 07/17/2025 15:03:40 | 07/17/2025 15:08:30 | 07/17/2025 19:07:26 |  |  | 07/17/2025 19:07:51 |  | Saddam Hussain Shah Nawaz Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250717000917 | PCM-20250717-00001346 | TT-20250717-01304 | Reference_telecom | Region_6 | ZHR0136 | ZHR0136 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Bilal Anwar Khurshid Anwar | 07/17/2025 15:04:07 | 07/18/2025 01:01:03 | 07/17/2025 21:04:07 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Abnormal Antenna RX Power Measurements) at ZHR0136-P3 (Ref:TT-20250711-00147) | 07/17/2025 03:57:40 | Major | 7114 | CELL SERVICE PROBLEM | 07/17/2025 03:57:40 | P3 | 2G | al harja | Sceco | LTE SA | ZHR0136 | FLM_TE |  |  | PCM-20250717-00001279 | Please check RTWP for Cell-30 | Please check RTWP for Cell-30 |  |  |  | API | 07/17/2025 15:04:07 | 07/17/2025 15:45:04 | 07/18/2025 01:00:36 |  |  | 07/18/2025 01:01:03 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250717000922 | PCM-20250717-00001352 | TT-20250717-01353 | Telecom | Region_6 | MHL1M7533 | MHL0533 | Equipment | SW | Issue was solved after softaware configuration | Muhammad Jamal Khan Abbas Ali | 07/17/2025 15:05:48 | 07/17/2025 18:13:40 | 07/17/2025 21:05:48 | BASE STATION INFORMATION(GNSS time error compared to local clock threshold exceeded) at MHL1M7533-L800-L1800-CA-P3-SBTS | 07/17/2025 14:52:21 | Major | 7115 | BASE STATION INFORMATION | 07/17/2025 14:52:21 | P3 | 4G | mohail | Generator_SG | LTE SA | MHL1M7533 | FLM_TE | [8 empty] | API | 07/17/2025 15:05:48 | 07/17/2025 15:26:00 | 07/17/2025 18:13:27 |  |  | 07/17/2025 18:13:40 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250717001367 | PCM-20250717-00002035 | TT-20250717-01983 | EM | Region_3 | MDHL9054 | MDHL9054 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Zarshad Ali Hassan Gul | 07/17/2025 20:05:03 | 07/28/2025 20:29:49 | 07/18/2025 00:05:03 | Observing MAIN AC + GEN FAIL alarm active at MDHL9054-MDHL0384 | 07/17/2025 19:54:48 | Critical | AC1+AC2 FAILURE (Input-2) | AC1+AC2 FAILURE (Input-2) | 07/17/2025 19:54:48 | P3 | Repeater | hail | Generator_DG | TX NSA | MDHL9054 | FLM_EM | [5 empty] | Observing MAIN AC + GEN FAIL alarm active at MDHL9054-MDHL0384 |  |  | API | 07/17/2025 20:05:03 | 07/28/2025 16:06:17 | 07/28/2025 16:06:47 | 07/28/2025 16:06:54 | 07/28/2025 16:06:57 | 07/28/2025 20:29:49 |  | Zarshad Ali Hassan Gul | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250717001501 | PCM-20250717-00002214 | TT-20250717-01405 | Reference_telecom | Region_6 | SHR0034 | SHR0034 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable Connector | TALEH MUHAMMAD | 07/17/2025 22:55:33 | 07/18/2025 01:54:55 | 07/18/2025 04:55:33 | CELL SERVICE PROBLEM(Sleeping Cell Detection Due To Abnormal Antenna RX Power Measurements) at SHR0034-P3 (Ref:TT-20250714-00084) | 07/16/2025 09:58:33 | Major | 7114 | CELL SERVICE PROBLEM | 07/16/2025 09:58:33 | P3 | 2G | sharurah | Sceco | LTE SA | SHR0034 | FLM_TE |  |  | PCM-20250717-00001409 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 07/17/2025 22:55:33 | 07/18/2025 00:34:14 | 07/18/2025 01:17:18 | 07/18/2025 01:17:28 |  | 07/18/2025 01:54:55 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250718000062 | PCM-20250718-00000092 | TT-20250718-00101 | Reference_EM | Region_2 | RIYA6082 | RIYA6082 |  |  |  | Vignesh Sivakumar Sivakumar | 07/18/2025 01:51:08 | 08/03/2025 18:42:03 | 07/18/2025 07:51:08 | 1(2G/LTE) sites down under RIYA6082-P3 2G/R2_RY1_HWBSC01 @ Sceco(ref:TT-20250718-00060) | 07/18/2025 01:03:26 | Major | 21825 | CSL Fault | 07/18/2025 01:03:26 | P3 | SRAN | riyadh | Sceco | 2G_LTE SA | RIYA6082 | FLM_EM | RIYA6082 | Results: DOWN SITE HUB RIYA6082 RIYA6082 Summary: Hub: RIYA6082, Down Count: 1, Down Sites: RIYA6082 Alarm Summary: RIYA6082 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 07/18/2025 01:51:08 | 07/20/2025 10:55:11 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250718000105 | PCM-20250718-00000181 | TT-20250718-00105 | Reference_telecom | Region_2 | RIY2042 | RIY2042 | Enviroment | SCECO_Failure | SCECO auto restored | Pawan Virdi Santokh Singh | 07/18/2025 03:01:01 | 08/31/2025 03:29:53 | 07/18/2025 09:01:01 | 2(2G) 2(LTE) sites down under RIY2042-P2 2G,RIY0785-P2 2G/R2_RY1_HWBSC01 @ Sceco(ref:TT-20250718-00060) | 07/18/2025 01:03:24 | Major | 21825 | CSL Fault | 07/18/2025 01:03:24 | P2 | SRAN | riyadh | Sceco | 2G_LTE SA | RIY2042-P2 2G,RIY0785-P2 2G | FLM_EM | RIY2042 | Dear Team, Hub:- RIY2042 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250718-00000124 | Dear Team, Hub:- RIY2042 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RIY2042 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 07/18/2025 03:01:01 | 07/20/2025 21:56:54 | 08/31/2025 03:29:02 |  |  | 08/31/2025 03:29:53 |  | Pawan Virdi Santokh Singh | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250719000212 | PCM-20250719-00000295 | TT-20250719-00258 | Telecom | Region_3 | YBDB2289 | YBDB2289 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 07/19/2025 06:19:08 | 08/09/2025 10:15:51 | 07/19/2025 12:19:08 | Adjacent Node IP Address Ping Failure at YB1MBSCH01 | 07/19/2025 05:04:36 | Major | 21392 | Adjacent Node IP Address Ping Failure | 07/19/2025 05:04:36 | P1 | SRAN | yanbu | Sceco_STB | 3G NSA | YB1MBSCH01 | FLM_TE | YBDB2289 | We are observing PM Error and RSL degradation at link: YBDB0289 dir YBDB2655, FLM Kindly visit the link and perform HC at the mentioned link . | PCM-20250719-00000239 | We are observing PM Error and RSL degradation at link: YBDB0289 dir YBDB2655, FLM Kindly visit the link and perform HC at the mentioned link . | We are observing PM Error and RSL degradation at link: YBDB0289 dir YBDB2655, FLM Kindly visit the link and perform HC at the mentioned link . |  |  |  | API | 07/19/2025 06:19:08 | 08/06/2025 13:24:33 | 08/09/2025 10:15:43 |  |  | 08/09/2025 10:15:51 |  | Muhammad Sajjad R3 | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250719000440 | PCM-20250719-00000603 | TT-20250719-00651 | Reference_telecom | Region_1 | URY0762 | URY0762 | Transsmission | MW_HW_fault | Replace IF Cable | AbdalHafiz Sirageldin Mohamed Yasin | 07/19/2025 09:56:31 | 08/06/2025 00:35:16 | 07/19/2025 21:56:31 | BUS_ERR at URY0762_NE_2_VRRP @ Sceco | 07/19/2025 08:59:28 | Minor | 1-377 | BUS_ERR | 07/19/2025 08:56:02 | P2 | SRAN | dammam | Sceco | TX NSA | URY0762 | FLM_TE | [8 empty] | API | 07/19/2025 09:56:31 | 08/06/2025 00:35:16 | [5 empty] | AbdalHafiz Sirageldin Mohamed Yasin | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250719000651 | PCM-20250719-00000884 | TT-20250719-00957 | Reference_EM | Region_1 | SMRY0810 | SMRY0810 |  |  |  | Samir Elzain Abdu Gumaa | 07/19/2025 12:44:56 | 07/21/2025 18:48:10 | 07/20/2025 00:44:56 | Major Rec alarm at SMRY0810-P2_SRAN @ Generator_SG | 07/19/2025 12:34:30 | Minor | 65107 | Major Rec alarm | 07/19/2025 12:34:29 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0810 | FLM_EM | [8 empty] | API | 07/19/2025 12:44:56 | 07/21/2025 18:48:10 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250719001386 | PCM-20250719-00001848 | TT-20250719-01945 | Reference_telecom | Region_4 | BHR2989 | BHR2989 | Transsmission | MW_HW_stuck | Reset IDU | Moustafa Mahmoud Ahmed Fathelbab | 07/19/2025 22:30:19 | 08/06/2025 15:54:41 | 07/20/2025 10:30:19 | Degrade observed in BHR2989_02 towards 10.3.234.70 @ Sceco | 07/19/2025 10:30:16 | Minor |  | Degrade | 07/19/2025 10:30:11 | P3 | 2G | jeddah | Sceco | TX NSA | BHR2989 | FLM_TE | [8 empty] | API | 07/19/2025 22:30:19 | 07/20/2025 10:41:19 | 08/06/2025 15:54:24 |  |  | 08/06/2025 15:54:41 |  | Moustafa Mahmoud Ahmed Fathelbab | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250720000271 | PCM-20250720-00000418 | TT-20250720-00439 | Reference_telecom | Region_6 | BSA0239 | BSA0239 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Saddam Hussain Shah Nawaz Khan | 07/20/2025 05:09:40 | 08/05/2025 15:22:20 | 07/20/2025 17:09:40 | LinkDown observed in BSA0239 towards 10.221.245.34 @ Sceco | 07/19/2025 17:10:21 | Minor |  | LinkDown | 07/19/2025 17:09:08 | P3 | 2G | bisha | Sceco | TX NSA | BSA0239 | FLM_TE | [8 empty] | API | 07/20/2025 05:09:40 | 07/20/2025 11:42:22 | 07/20/2025 18:49:23 | 07/20/2025 18:49:29 | 07/20/2025 18:49:42 | 08/05/2025 15:22:20 |  | Saddam Hussain Shah Nawaz Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250720000386 | PCM-20250720-00000588 | TT-20250717-01509 | Reference_telecom | Region_6 | DMD0325 | DMD0325 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 07/20/2025 07:18:34 | 07/20/2025 11:05:17 | 07/20/2025 13:18:34 | BASE STATION INFORMATION (GNSS time error compared to local clock threshold exceeded) at DMD0325-P3 (Ref:TT-20250711-00190) | 06/29/2025 00:44:49 | Major | 7115 | BASE STATION INFORMATION | 06/29/2025 00:44:49 | P3 | 2G | jizan | Generator_SG | LTE NSA | DMD0325-P3 | FLM_TE |  |  | PCM-20250717-00001517 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 07/20/2025 07:18:34 | 07/20/2025 11:03:08 | 07/20/2025 11:04:50 |  |  | 07/20/2025 11:05:17 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250720000391 | PCM-20250720-00000593 | TT-20250720-00582 | Reference_telecom | Region_6 | BHAB0826 | BHAB0826 | Equipment | SW | Issue was solved after softaware configuration | Manzoor Ahmed | 07/20/2025 07:21:49 | 07/20/2025 15:58:56 | 07/20/2025 13:21:49 | BASE STATION CONNECTIVITY PROBLEM ( Transport layer connection failure in S1 interface ) at BHAB1M7826-G9-U9-U21-NL8-NL18-SBTS-P2 REF ( TT-20250715-01139 ) @ Sceco | 07/15/2025 17:55:29 | Major | 7105 | RAT BASE STATION PROBLEM | 07/15/2025 17:55:29 | P2 | 2G | makhwa | Sceco | 2G_3G_LTE SA | BHAB1M7826 | FLM_TE | [8 empty] | API | 07/20/2025 07:21:49 | 07/20/2025 10:43:43 | 07/20/2025 15:58:48 |  |  | 07/20/2025 15:58:56 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250720000479 | PCM-20250720-00000721 | TT-20250720-00717 | Reference_telecom | Region_6 | BSA0239 | BSA0239 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Saddam Hussain Shah Nawaz Khan | 07/20/2025 08:53:24 | 08/02/2025 18:08:50 | 07/20/2025 20:53:24 | LossOfSignal observed in BSA0239 towards 10.221.245.37 @ Sceco | 07/19/2025 20:55:05 | Minor |  | LossOfSignal | 07/19/2025 20:52:55 | P3 | 2G | bisha | Sceco | TX NSA | BSA0239 | FLM_TE | [8 empty] | API | 07/20/2025 08:53:24 | 07/31/2025 18:37:37 | 08/02/2025 18:08:30 |  |  | 08/02/2025 18:08:50 |  | Saddam Hussain Shah Nawaz Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250720000674 | PCM-20250720-00000979 | TT-20250720-00978 | MW_HC | Region_1 | JBL0457 | JBL0457 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Tahir Mahmood Hafiz Yar | 07/20/2025 11:01:22 | 07/28/2025 14:02:48 | 07/20/2025 23:01:22 | NEC MW HC_P0 Observing Modem Down at JBL0457(10.154.26.162)--JBL0459(10.154.26.161) | 07/20/2025 11:00:29 | Minor |  | LOF | 07/20/2025 11:00:29 | P3 | SRAN | jubail | Generator_SG | TX NSA | JBL0457(10.154.26.162)--JBL0459(10.154.26.161) | FLM_TE | [8 empty] | API | 07/20/2025 11:01:22 | 07/28/2025 14:02:48 | [5 empty] | Tahir Mahmood Hafiz Yar | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250720001276 | PCM-20250720-00001769 | TT-20250720-01767 | Reference_telecom | Region_1 | HFF6008 | HFF6008 |  |  |  | Mohamed Magdy Fouad Zayed | 07/20/2025 17:27:49 | 07/23/2025 13:33:29 | 07/20/2025 23:27:49 | RFC Port Underpower at HFF6008-DCU1(Ref::TT-20250623-02099) @ Sceco | 07/13/2025 13:31:20 | Major | 29803 | RFC Port Underpower | 07/13/2025 13:32:17 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFF6008 | FLM_TE | [8 empty] | API | 07/20/2025 17:27:49 | 07/20/2025 19:27:36 | [6 empty] | STC |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250721000098 | PCM-20250721-00000132 | TT-20250721-00197 | MW_HC | Region_2 | RIY0908 | RIY0908 |  |  |  | Zakir Muhammad Yar Muhammad | 07/21/2025 01:24:28 | 09/22/2025 13:00:13 | 07/21/2025 13:24:28 | Huawei HC_P2 Observing Errors at RIY0908-RIY2990 | 07/21/2025 01:23:17 | Minor |  | LOF | 07/21/2025 01:23:17 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0908-RIY2990 | FLM_TE | [8 empty] | API | 07/21/2025 01:24:28 | 07/21/2025 09:21:44 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250721000108 | PCM-20250721-00000141 | TT-20250721-00210 | MW_HC | Region_2 | RIY0322 | RIY0322 | Transsmission | MW_RSL_fading | Link Alignment Issue | Farmanullah Akbar Jan | 07/21/2025 01:24:42 | 09/27/2025 01:09:04 | 07/21/2025 13:24:42 | Huawei HC_P2 Observing Errors at RIY0322-RIY0363 | 07/21/2025 01:23:16 | Minor |  | LOF | 07/21/2025 01:23:16 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0322-RIY0363 | FLM_TE | [8 empty] | API | 07/21/2025 01:24:42 | 08/09/2025 08:29:25 | 09/27/2025 01:08:31 |  |  | 09/27/2025 01:09:04 |  | Farmanullah Akbar Jan | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250721001010 | PCM-20250721-00001679 | TT-20250721-01718 | Telecom | Region_1 | JBL2M1459 | JBL0459 |  |  |  | Tahir Mahmood Hafiz Yar | 07/21/2025 14:59:38 | 07/28/2025 12:32:05 | 07/22/2025 02:59:38 | ODU CPU / Cable Open at JBL2M1459 on 10.154.26.161 @ Generator_DG | 07/21/2025 14:58:47 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 07/21/2025 14:56:25 | P3 | 2G | jubail | Generator_DG | TX NSA | JBL2M1459 | FLM_TE | [8 empty] | API | 07/21/2025 14:59:38 | 07/21/2025 15:40:19 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250721001570 | PCM-20250721-00002540 | TT-20250721-02491 | Reference_telecom | Region_6 | ABBS0164 | ABBS0164 | Transsmission | MW_HW_fault | Replace Power Board | Fawad Khan | 07/21/2025 22:48:13 | 08/04/2025 15:06:03 | 07/22/2025 10:48:13 | ReplaceableUnitMissing observed in ABBS0164 towards 10.74.123.50 @ Sceco | 07/21/2025 10:47:58 | Minor |  | ReplaceableUnitMissing | 07/21/2025 10:47:53 | P3 | 2G | namas | Sceco | TX NSA | ABBS0164 | FLM_TE | [8 empty] | API | 07/21/2025 22:48:13 | 07/22/2025 00:36:52 | 08/04/2025 15:05:14 |  |  | 08/04/2025 15:06:03 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250722000416 | PCM-20250722-00000657 | TT-20250722-00745 | Reference_telecom | Region_6 | BHAB9038 | BHAB9038 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Fawad Khan | 07/22/2025 07:39:21 | 08/04/2025 15:06:46 | 07/22/2025 19:39:21 | LinkDown observed in BHAB9038 towards 10.1.230.225 @ Generator_SG | 07/21/2025 19:40:53 | Minor |  | LinkDown | 07/21/2025 19:38:52 | P1 | Repeater | namas | Generator_SG | TX NSA | BHAB9038 | FLM_TE | [8 empty] | API | 07/22/2025 07:39:21 | 07/22/2025 10:49:52 | 08/04/2025 15:06:13 |  |  | 08/04/2025 15:06:46 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250722000836 | PCM-20250722-00001207 | TT-20250722-01007 | Reference_telecom | Region_1 | DAM0270 | DAM0270 |  |  |  | AbdalHafiz Sirageldin Mohamed Yasin | 07/22/2025 12:24:36 | 07/28/2025 12:32:06 | 07/23/2025 00:24:36 | Nokia Eband Observing LinkDown-Port 1/1,DemFail-Port 1/1 at DAM0270-10.3.127.74 | 04/29/2025 11:12:11 | Minor |  | LOF | 04/29/2025 11:12:11 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0270-10.3.127.74 | FLM_TE |  | please close with your feedback | PCM-20250722-00001118 | please close with your feedback | please close with your feedback |  |  |  | API | 07/22/2025 12:24:36 | 07/22/2025 14:27:05 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250722001170 | PCM-20250722-00001665 | TT-20250722-01816 | Reference_telecom | Region_2 | RIY2971 | RIY2971 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 07/22/2025 15:46:15 | 08/03/2025 18:42:06 | 07/22/2025 21:46:15 | 2(2G) sites down under RIY2971-P3,RIY2145-P2/R2_RY2_HWBSC01 @ Sceco(ref:TT-20250722-01289) | 07/22/2025 11:56:22 | Major | 21825 | CSL Fault | 07/22/2025 11:56:22 | P3 | SRAN | riyadh | Sceco | 2G SA | RIY2971-P3,RIY2145-P | FLM_EM | RIY2971 | Dear Team, Hub:- RIY2971 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250722-00001664 | Dear Team, Hub:- RIY2971 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RIY2971 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 07/22/2025 15:46:15 | 07/24/2025 02:00:57 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250723000986 | PCM-20250723-00001514 | TT-20250723-01513 | Telecom | Region_4 | RAB2163 | RAB2163 | Transsmission | MW_HW_fault | Replace ODU | Khizer Hayat | 07/23/2025 15:24:29 | 07/27/2025 18:47:48 | 07/24/2025 03:24:29 | PT::TX BO need to check PLR issue at RAB2163 | 07/23/2025 15:08:53 | Minor | 61611 | TWAMP PLR Threshold Crossed | 07/23/2025 15:08:53 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | RAB2163 | FLM_TE |  |  | PCM-20250723-00001480 | Thanks to check RAB2153-RAB0966 | Thanks to check RAB2153-RAB0966 |  |  |  | API | 07/23/2025 15:24:29 | 07/24/2025 01:01:50 | 07/27/2025 18:47:07 |  |  | 07/27/2025 18:47:48 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250723001365 | PCM-20250723-00002036 | TT-20250723-02039 | Reference_telecom | Region_6 | HJR0027 | HJR0027 | Equipment | SFP_BTS | Replace SFP | SHAH KHALID | 07/23/2025 19:05:51 | 09/08/2025 22:39:45 | 07/24/2025 07:05:51 | LinkDown observed in HJR0027 towards 10.88.106.194 @ Sceco | 07/23/2025 07:07:46 | Minor |  | LinkDown | 07/23/2025 07:05:42 | P3 | 2G | makhwa | Sceco | TX NSA | HJR0027 | FLM_TE | [8 empty] | API | 07/23/2025 19:05:51 | 07/23/2025 23:09:20 | 09/08/2025 19:03:02 | 09/08/2025 19:03:04 | 09/08/2025 19:06:44 | 09/08/2025 22:39:45 |  | SHAH KHALID | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250724000653 | PCM-20250724-00000923 | TT-20250724-00938 | Reference_telecom | Region_6 | WRTH0001 | WRTH0001 | Transsmission | MW_HW_stuck | Reset IDU | Muhammad Ali | 07/24/2025 09:31:06 | 08/06/2025 18:02:33 | 07/24/2025 21:31:06 | Nokia Eband Observing LinkDown-Port 1/1 at WRTH0001-L1-10.89.249.115 | 11/27/2023 18:29:39 | Minor |  | LOF | 11/27/2023 18:29:39 | P3 | WIFI | raith | Sceco | TX NSA | WRTH0001-L1-10.89.249.115 | FLM_TE | [8 empty] | API | 07/24/2025 09:31:06 | 08/06/2025 18:02:33 | [5 empty] | Muhammad Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250724000655 | PCM-20250724-00000925 | TT-20250724-00940 | Reference_telecom | Region_6 | ABH0005 | ABH0005 | Transsmission | MW_RSL_fading | Link Blockage | Amir Sohail | 07/24/2025 09:31:09 | 07/31/2025 18:35:24 | 07/24/2025 21:31:09 | Nokia Eband Observing LossOfSignal-Port 3/5,LossOfSignal-Port 4/5,LinkDo at ABH0005-NE2-10.10.158.35 | 07/13/2025 09:23:23 | Minor |  | LOF | 07/13/2025 09:23:23 | P1 | 2G | abha | Sceco | TX NSA | ABH0005-NE2-10.10.158.35 | FLM_TE | [8 empty] | API | 07/24/2025 09:31:09 | 07/24/2025 10:01:52 | 07/24/2025 16:38:55 |  |  | 07/31/2025 18:35:24 |  | Amir Sohail | Relocation_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250724000658 | PCM-20250724-00000928 | TT-20250724-00943 | Reference_telecom | Region_6 | ABH0161 | ABH0161 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Amir Sohail | 07/24/2025 09:31:13 | 07/31/2025 18:36:07 | 07/24/2025 21:31:13 | Nokia Eband Observing ReplaceableUnitMissing-Port 4/5,LinkDown-Port 4/5, at ABH0161_08-10.10.155.65 | 01/25/2025 20:19:25 | Minor |  | LOF | 01/25/2025 20:19:25 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0161_08-10.10.155.65 | FLM_TE | [8 empty] | API | 07/24/2025 09:31:13 | 07/24/2025 10:01:53 | 07/24/2025 16:39:04 |  |  | 07/31/2025 18:36:07 |  | Amir Sohail | Relocation_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250726000015 | PCM-20250726-00000022 | TT-20250726-00019 | Reference_telecom | Region_4 | MKYL0918 | MKYL0918 |  |  |  | Riasat Ali Allah Baksh | 07/26/2025 00:20:13 | 07/26/2025 05:57:09 | 07/26/2025 06:20:13 | 3(2G) 3(3G) 3(5G) sites down under MKYL0919-P2,MKYL0918-P2,MKYL0920-P2 (Ref:TT-20250725-01667) | 07/25/2025 23:56:24 | Major | 7706 | BTS O&M LINK FAILURE | 07/25/2025 23:56:24 | P2 | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G SA | MKYL0919-P2 MKYL0918-P2 MKYL0920-P2 | FLM_TE | MKYL0920 | Results: DOWN SITE HUB MKYL0919-P2 MKYL0920 MKYL0918-P2 MKYL0920 MKYL0920-P2 MKYL0920 Summary: Hub: MKYL0920, Down Count: 3, Down Sites: MKYL0919-P2, MKYL0918-P2, MKYL0920-P2 Alarm Summary: MKYL0920 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 07/26/2025 00:20:13 | 07/26/2025 05:57:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250726000990 | PCM-20250726-00001354 | TT-20250726-01408 | Telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Replace Ethernet Cable | Mohamed Farag Abdelbary | 07/26/2025 15:56:59 | 09/24/2025 17:15:38 | 07/26/2025 19:56:59 | JED1W6081 is partial down | 07/26/2025 15:54:26 | Critical | 613007 | Wi-Fi AP Out Of Service | 07/26/2025 15:54:26 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081 | FLM_TE | [8 empty] | API | 07/26/2025 15:56:59 | 07/26/2025 16:02:50 | 09/24/2025 17:15:26 |  |  | 09/24/2025 17:15:38 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250726001333 | PCM-20250726-00001826 | TT-20250726-01834 | Reference_telecom | Region_3 | MDHL0373 | MDHL0373 |  |  |  | Junaid Eisa | 07/26/2025 20:02:43 | 08/06/2025 00:38:54 | 07/27/2025 08:02:43 | ETH_LINK_DOWN at MDHL0373_NE_1_NN @ Generator_SG | 07/26/2025 16:36:09 | Minor | 1-12793 | ETH_LINK_DOWN | 07/26/2025 16:35:57 | P3 | SRAN | madinah | Generator_SG | TX NSA | MDHL0373 | FLM_TE | [8 empty] | API | 07/26/2025 20:02:43 | [7 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250727000119 | PCM-20250727-00000170 | TT-20250727-00151 | Telecom | Region_3 | YB1MBSCH01 | YB2 |  |  |  | Muhammad Sajjad R3 | 07/27/2025 02:34:05 | 08/05/2025 21:52:34 | 07/27/2025 08:34:05 | Transmission Resource Pool Ping Packet Loss at YB1MBSCH01 | 07/27/2025 01:45:32 | Major | 21394 | Transmission Resource Pool Ping Packet Loss | 07/27/2025 01:45:32 | P1 | BSC | yanbu | Sceco_STB | 2G NSA | YB1MBSCH01 | FLM_TE |  |  | PCM-20250727-00000159 | PM Errors and RSL degradation observed on NEC MW link YBDB0289 TO YBDB2655 | PM Errors and RSL degradation observed on NEC MW link YBDB0289 TO YBDB2655 |  |  |  | API | 07/27/2025 02:34:05 | 07/27/2025 13:41:37 | 08/05/2025 18:22:25 | [5 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250727000601 | PCM-20250727-00000851 | TT-20250727-00834 | Telecom | Region_2 | RIYB6025 | RIYB6025 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 07/27/2025 10:22:08 | 07/28/2025 08:54:55 | 07/27/2025 16:22:08 | HC:: Multiple Alarms Active at Site RIYB6025 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYB6025 | FLM_TE | [8 empty] | API | 07/27/2025 10:22:08 | 07/28/2025 08:54:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250727000603 | PCM-20250727-00000853 | TT-20250727-00836 | Telecom | Region_4 | JED6020 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 07/27/2025 10:22:10 | 09/24/2025 17:15:57 | 07/27/2025 16:22:10 | HC:: Multiple Alarms Active at Site JED6020 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | 2G | jeddah | Sceco | IBS SA | JED6020 | FLM_TE | [8 empty] | API | 07/27/2025 10:22:10 | 07/27/2025 11:55:05 | 09/24/2025 17:15:50 |  |  | 09/24/2025 17:15:57 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250727000605 | PCM-20250727-00000855 | TT-20250727-00838 | Telecom | Region_2 | RIYA6017 | RIYA6017 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | Muhammad Waqas Ashraf Muhammad Ashraf | 07/27/2025 10:22:12 | 07/28/2025 12:57:40 | 07/27/2025 16:22:12 | HC:: Multiple Alarms Active at Site RIYA6017 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYA6017 | FLM_TE | [8 empty] | API | 07/27/2025 10:22:12 |  | 07/27/2025 10:51:56 | 07/27/2025 10:52:25 | 07/27/2025 10:52:50 | 07/28/2025 12:57:40 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250727001104 | PCM-20250727-00001498 | TT-20250727-01390 | Telecom | Region_4 | JED3W6085 | JED3W6085 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 07/27/2025 14:57:06 | 09/24/2025 17:16:13 | 07/28/2025 02:57:06 | Site JED3W6085 partial Down | 07/27/2025 14:26:29 | Minor | 676767675 | Health Check-WO to TE FME | 07/27/2025 14:26:29 | P3 | WIFI | jeddah | Sceco | Wifi SA | Site JED3W6085 partial Down | FLM_TE |  |  | PCM-20250727-00001414 | please arrange FLM to the Site to check AP locally | please arrange FLM to the Site to check AP locally |  |  |  | API | 07/27/2025 14:57:06 | 07/27/2025 15:08:04 | 09/24/2025 17:16:04 |  |  | 09/24/2025 17:16:13 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250727001758 | PCM-20250727-00002424 | TT-20250727-02343 | Telecom | Region_4 | TURY0686 | TURY0686 |  |  |  | Rashid Shafique | 07/27/2025 22:07:13 | 10/22/2025 09:49:59 | 07/28/2025 04:07:13 | PT:: FLM Need to perform HC at TURY0686 under R4 | 07/27/2025 22:06:46 | Major | 676767671 | Health Check-WO to TE FME | 07/27/2025 22:06:46 | P1 | 2G | taif | Sceco | 2G_3G_LTE_5G SA | TURY0686 | FLM_TE | [8 empty] | API | 07/27/2025 22:07:13 | 07/28/2025 14:43:28 | 07/29/2025 23:24:36 | 10/22/2025 08:51:47 | 10/22/2025 09:49:59 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728000575 | PCM-20250728-00000852 | TT-20250728-00895 | Reference_telecom | Region_4 | JED6010 | JED6010 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Mohamed Farag Abdelbary | 07/28/2025 10:47:26 | 09/10/2025 16:36:18 | 07/28/2025 22:47:26 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6010-DCU @ Sceco ¦¦ Reference: TT-20250624-00301 | 06/24/2025 01:27:21 | Minor |  | RF Unit RX Channel RTWP/RSSI Unbalanced | 06/24/2025 01:27:21 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6010 | FLM_TE | [8 empty] | API | 07/28/2025 10:47:26 | 07/29/2025 10:50:44 | 09/10/2025 16:36:03 |  |  | 09/10/2025 16:36:18 |  | Mohamed Farag Abdelbary | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728000576 | PCM-20250728-00000853 | TT-20250728-00896 | Reference_telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 07/28/2025 10:47:27 | 09/24/2025 17:16:27 | 07/28/2025 22:47:27 | External Clock Reference Not Configured at JED6008-DCU-P3 @ Sceco ¦¦ Reference: TT-20250627-00630 | 06/26/2025 16:12:11 | Minor |  | External Clock Reference Not Configured | 06/26/2025 16:12:11 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 07/28/2025 10:47:27 | 07/29/2025 10:50:45 | 09/24/2025 17:16:19 |  |  | 09/24/2025 17:16:27 |  | Mohamed Farag Abdelbary | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20250728000579 | PCM-20250728-00000862 | TT-20250728-00908 | Reference_telecom | Region_3 | MDN6072 | MDN6072 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 07/28/2025 10:47:37 | 09/01/2025 02:14:58 | 07/28/2025 16:47:37 | RFC Port Underpower at MDN6072-Sector C-DCU @ Sceco ¦¦ Reference: TT-20241009-00867 | 09/15/2024 14:44:29 | Major |  | RFC Port Underpower | 09/15/2024 14:44:29 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN6072 | FLM_TE | [8 empty] | API | 07/28/2025 10:47:37 | 07/28/2025 19:00:59 | 08/07/2025 18:16:33 | 09/01/2025 02:14:58 |  |  |  |  | Mobily |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250728000596 | PCM-20250728-00000886 | TT-20250728-00934 | Reference_telecom | Region_2 | RIY2802 | RIY2802 |  |  |  | Zakir Muhammad Yar Muhammad | 07/28/2025 10:48:05 | 08/05/2025 21:52:14 | 07/28/2025 16:48:05 | 1(2G) Sector down at RIY2802-P2_SRAN ¦¦ Reference: TT-20231222-00296 | 11/14/2023 01:24:43 | Major |  | GSM Local Cell Unusable | 11/14/2023 01:24:43 | P3 | SRAN | riyadh | Sceco | 2G SA | RIY2802 | FLM_TE | [6 empty] | sector down |  | API | 07/28/2025 10:48:05 | 07/28/2025 12:40:36 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728001387 | PCM-20250728-00001934 | TT-20250728-01966 | Reference_telecom | Region_6 | JIZ2102 | JIZ2102 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/28/2025 17:43:24 | 08/09/2025 05:44:36 | 07/29/2025 05:43:24 | Nokia Eband Observing LinkDown-Channel 1B,LinkDown-Channel 1A at JIZ2102-10.3.226.119 | 07/19/2025 14:19:09 | Minor |  | LOF | 07/19/2025 14:19:09 | P3 | 2G | jizan | Sceco | TX NSA | JIZ2102-10.3.226.119 | FLM_TE | [8 empty] | API | 07/28/2025 17:43:24 | 08/07/2025 03:39:21 | 08/09/2025 05:44:30 |  |  | 08/09/2025 05:44:36 |  | Osama Hadi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250728001501 | PCM-20250728-00002066 | TT-20250728-01937 | Telecom | Region_4 | JED1MN0312 | JED0312 |  |  |  | Mohammed Ramadan A Abu Abid | 07/28/2025 18:02:26 | 07/29/2025 00:00:11 | 07/29/2025 00:02:26 | PT :: Low availability observed without matching alarm to the availability percentage at JED1MN0312-NR2.6 / R4 (27.07 - 36.24% - JED1MN0312A) | 07/28/2025 17:38:49 | Major | 7604 | BASE STATION OPERATION DEGRADED | 07/28/2025 17:38:50 | P3 | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1MN0312-NR2.6 | FLM_TE |  |  | PCM-20250728-00001894 | FLM need to verfiy SFP as it not detecting at site,mail shared | FLM need to verfiy SFP as it not detecting at site,mail shared |  |  |  | API | 07/28/2025 18:02:26 | 07/29/2025 00:00:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728001587 | PCM-20250728-00002202 | TT-20250728-02203 | Reference_telecom | Region_6 | JDSM0794 | JDSM0794 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/28/2025 19:05:35 | 08/09/2025 05:44:48 | 07/29/2025 07:05:35 | LinkDown observed in JDSM0794 towards 10.74.62.10 @ Sceco | 07/28/2025 07:05:34 | Minor |  | LinkDown | 07/28/2025 07:05:30 | P3 | 2G | jizan | Sceco | TX NSA | JDSM0794 | FLM_TE | [8 empty] | API | 07/28/2025 19:05:35 | 08/07/2025 03:39:20 | 08/09/2025 05:44:42 |  |  | 08/09/2025 05:44:48 |  | Osama Hadi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728001596 | PCM-20250728-00002217 | TT-20250728-02213 | Reference_telecom | Region_6 | SMT0107 | SMT0107 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/28/2025 19:10:14 | 08/09/2025 05:45:38 | 07/29/2025 07:10:14 | LinkDown observed in SMT0107 towards 10.74.62.66 @ Sceco | 07/28/2025 07:10:13 | Minor |  | LinkDown | 07/28/2025 07:10:08 | P2 | 2G | jizan | Sceco | TX NSA | SMT0107 | FLM_TE | [8 empty] | API | 07/28/2025 19:10:14 | 08/07/2025 03:39:19 | 08/09/2025 05:45:32 |  |  | 08/09/2025 05:45:38 |  | Osama Hadi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728001632 | PCM-20250728-00002275 | TT-20250728-02261 | Reference_telecom | Region_6 | JIZ0006 | JIZ0006 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/28/2025 19:38:08 | 08/09/2025 05:45:00 | 07/29/2025 07:38:08 | LinkDown observed in JIZ0006 towards 10.3.86.18 @ Sceco | 07/28/2025 07:39:48 | Minor |  | LinkDown | 07/28/2025 07:38:01 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0006 | FLM_TE | [8 empty] | API | 07/28/2025 19:38:08 | 08/07/2025 03:39:20 | 08/09/2025 05:44:52 |  |  | 08/09/2025 05:45:00 |  | Osama Hadi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728001635 | PCM-20250728-00002278 | TT-20250728-02264 | Reference_telecom | Region_6 | JIZ0241 | JIZ0241 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/28/2025 19:39:10 | 08/09/2025 05:45:26 | 07/29/2025 07:39:10 | LinkDown observed in JIZ0241 towards 10.3.86.60 @ Sceco | 07/28/2025 07:39:55 | Minor |  | LinkDown | 07/28/2025 07:39:00 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0241 | FLM_TE | [8 empty] | API | 07/28/2025 19:39:10 | 08/07/2025 03:39:19 | 08/09/2025 05:45:20 |  |  | 08/09/2025 05:45:26 |  | Osama Hadi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250728001634 | PCM-20250728-00002277 | TT-20250728-02263 | Reference_telecom | Region_6 | JIZ0124 | JIZ0124 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 07/28/2025 19:39:10 | 08/09/2025 05:45:15 | 07/29/2025 07:39:10 | LinkDown observed in JIZ0124 towards 10.3.86.58 @ Sceco | 07/28/2025 07:39:55 | Minor |  | LinkDown | 07/28/2025 07:39:01 | P2 | 2G | jizan | Sceco | TX NSA | JIZ0124 | FLM_TE | [8 empty] | API | 07/28/2025 19:39:10 | 08/07/2025 03:39:20 | 08/09/2025 05:45:04 |  |  | 08/09/2025 05:45:15 |  | Osama Hadi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250729000034 | PCM-20250729-00000071 | TT-20250729-00079 | Reference_telecom | Region_1 | ARM0712 | ARM0712 |  |  |  | Talha Manzoor | 07/29/2025 00:37:18 | 08/05/2025 21:52:19 | 07/29/2025 12:37:18 | HARD_BAD at ARM0712_NE_1_V @ Sceco | 07/28/2025 23:37:04 | Minor | 1-236 | HARD_BAD | 07/28/2025 23:36:55 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0712 | FLM_TE | [8 empty] | API | 07/29/2025 00:37:18 | 07/29/2025 00:59:08 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250730000383 | PCM-20250730-00000652 | TT-20250730-00558 | EM | Region_3 | MDN0063 | MDN0063 |  |  |  | Junaid Eisa | 07/30/2025 07:46:21 | 08/04/2025 19:38:23 | 07/30/2025 11:46:21 | 1(3G/LTE) sites down under MDN0063-P1-HRMCST/MD2RNCH01 @ Generator_SG | 07/30/2025 06:44:23 | Critical | 22214 | NodeB Unavailable | 07/30/2025 06:44:20 | P1 | SRAN | madinah | Generator_SG | 3G_LTE SA | MDN0063-P1-HRMCST | FLM_TE | MDN0063 | Results: DOWN SITE HUB MDN0063-P1-HRMCST MDN0063 Summary: Hub: MDN0063, Down Count: 1, Down Sites: MDN0063-P1-HRMCST Alarm Summary: MDN0063 Alarm Active on HUB | PCM-20250730-00000552 | Telecome issue | Telecome issue |  | sites down |  | API | 07/30/2025 07:46:21 | [7 empty] | ZAIN O-M |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250730000495 | PCM-20250730-00000813 | TT-20250727-00842 | Telecom | Region_2 | RIYA6173 | RIYA6173 | Equipment | BSS_HW_fault | Replace RFU | Muhammad Waqas Ashraf Muhammad Ashraf | 07/30/2025 09:24:01 | 08/06/2025 16:57:55 | 07/30/2025 15:24:01 | HC:: Multiple Alarms Active at Site RIYA6173 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYA6173 | FLM_TE |  |  | PCM-20250727-00002149 | RIYA6173_MU2 is down and Ip for the MU is not reachable , kindly check the Ethernet Cable between the MU and The switch and all the RU under the MU are still down | RIYA6173_MU2 is down and Ip for the MU is not reachable , kindly check the Ethernet Cable between the MU and The switch and all the RU under the MU are still down |  |  |  | API | 07/30/2025 09:24:01 | 08/06/2025 16:57:55 | [5 empty] | Muhammad Waqas Ashraf Muhammad Ashraf | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250730000860 | PCM-20250730-00001241 | TT-20250730-01248 | MW_HC | Region_3 | MDN6030 | MDN6030 |  |  |  | TAUSEEF ILYAS | 07/30/2025 11:29:44 | 08/06/2025 09:14:38 | 07/30/2025 23:29:44 | NEC MW HC_P2 Observing Modem Down at MD2(10.154.89.129)--MDN6030(10.154.89.130) | 07/30/2025 11:03:13 | Minor |  | LOF | 07/30/2025 11:03:13 | P1 | SRAN | madinah | Sceco | TX NSA | MD2(10.154.89.129)--MDN6030(10.154.89.130) | FLM_TE | [8 empty] | API | 07/30/2025 11:29:44 | 07/30/2025 13:57:37 | 08/05/2025 18:46:11 | [5 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250730000882 | PCM-20250730-00001266 | TT-20250730-01273 | MW_HC | Region_1 | DJL2558 | DJL2558 |  |  |  | Mahmoud Mohamed Megahed Sewidan | 07/30/2025 11:34:26 | 08/20/2025 11:35:38 | 07/30/2025 23:34:26 | NEC MW HC_P0 Observing RSL Issue at DJL0553(10.147.4.33)--DJL2558(10.147.4.36) | 07/30/2025 11:03:13 | Minor |  | LOF | 07/30/2025 11:03:13 | P3 | SRAN | sakaka | Sceco | TX NSA | DJL0553(10.147.4.33)--DJL2558(10.147.4.36) | FLM_TE | [8 empty] | API | 07/30/2025 11:34:26 | 07/30/2025 11:55:59 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250730000883 | PCM-20250730-00001267 | TT-20250730-01274 | MW_HC | Region_3 | YNB0663 | YNB0663 |  |  |  | Muhammad Sajjad R3 | 07/30/2025 11:34:29 | 08/06/2025 09:22:47 | 07/30/2025 23:34:29 | Huawei HC_P2 Observing Errors at YNB0637-YNB0663 | 07/30/2025 11:03:13 | Minor |  | LOF | 07/30/2025 11:03:13 | P2 | SRAN | yanbu | Sceco | TX NSA | YNB0637-YNB0663 | FLM_TE | [8 empty] | API | 07/30/2025 11:34:29 | 07/30/2025 13:28:05 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250730001131 | PCM-20250730-00001594 | TT-20250727-00840 | Telecom | Region_2 | RIYA6018 | RIYA6018 |  |  |  | Bilal Ahmad Zahir Ullah | 07/30/2025 13:21:44 | 07/30/2025 16:03:26 | 07/30/2025 19:21:44 | HC:: Multiple Alarms Active at Site RIYA6018 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYA6018 | FLM_TE |  |  | PCM-20250730-00001539 | Kindly alarm Temperature Device related to the FAN , please let FLM at the Site check the FAN may be dusty and needed to be clean after clean please restart the MU , kindly check and share your feedback | Kindly alarm Temperature Device related to the FAN , please let FLM at the Site check the FAN may be dusty and needed to be clean after clean please restart the MU , kindly check and share your feedback |  |  |  | API | 07/30/2025 13:21:44 | 07/30/2025 16:03:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20250730001269 | PCM-20250730-00001779 | TT-20250727-00837 | Telecom | Region_2 | RIYA6005 | RIYA6005 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 07/30/2025 14:31:45 | 07/31/2025 15:08:28 | 07/30/2025 20:31:45 | HC:: Multiple Alarms Active at Site RIYA6005 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYA6005 | FLM_TE |  |  | PCM-20250727-00002154 | There is Master Slave Link Alarm at the RIYA6005_MU1 kindly check , the connection between the MU and the RU , SFPs Modules , monitor board for Master unit and there are RUs are still down at the Site RUs RU508_1 & RU510_1 are offline | There is Master Slave Link Alarm at the RIYA6005_MU1 kindly check , the connection between the MU and the RU , SFPs Modules , monitor board for Master unit and there are RUs are still down at the Site RUs RU508_1 & RU510_1 are offline |  |  |  | API | 07/30/2025 14:31:45 | 07/31/2025 10:32:43 | 07/31/2025 14:24:08 | 07/31/2025 14:24:12 | 07/31/2025 14:24:27 | 07/31/2025 15:08:28 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  | BO_WiFi | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250731000324 | PCM-20250731-00000508 | TT-20250731-00592 | Telecom | Region_1 | DAM1W6004 | DAM6004 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Meraj Husain Idd Baksh | 07/31/2025 07:56:51 | 09/22/2025 00:23:18 | 07/31/2025 19:56:51 | DAM1W6004 is partial down | 07/31/2025 07:46:52 | Minor | 613007 | Wi-Fi AP Out Of Service | 07/31/2025 07:46:52 | P1 | WIFI | dammam | Sceco | Wifi SA | DAM1W6004_2-2F-AP03 | FLM_TE | [8 empty] | API | 07/31/2025 07:56:51 | 09/22/2025 00:23:18 | [5 empty] | Meraj Husain Idd Baksh | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250731000614 | PCM-20250731-00000950 | TT-20250731-01009 | MW_HC | Region_1 | DMH0100 | DMH0100 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 07/31/2025 11:35:20 | 08/05/2025 21:52:27 | 07/31/2025 23:35:20 | NCE MW Observing PM errors at MW link DMH0100 <> DMH0099 ( As per BO request ) | 07/31/2025 11:34:29 | Minor | 12871 | MW_BER_SD | 07/31/2025 11:34:29 | P3 | SRAN | hafr | Generator_SG | TX NSA | DMH0100 DMH0099 | FLM_TE | [5 empty] | NCE MW Observing PM errors at MW link DMH0100 <> DMH0099 ( As per BO request ) |  |  | API | 07/31/2025 11:35:20 | 07/31/2025 11:40:53 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250731001072 | PCM-20250731-00001611 | TT-20250731-01609 | Reference_telecom | Region_2 | KHJ0314 | KHJ0314 | Transsmission | MW_bad_Weather | Sandstorm | Hakim Ullah Raif Ullah Jan | 07/31/2025 15:40:06 | 08/08/2025 14:39:40 | 08/01/2025 03:40:06 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at KHJ0314_NE_3 | 10/31/2024 12:47:33 | Minor |  | LOF | 10/31/2024 12:47:33 | P1 | SRAN | al kharj | Sceco | TX NSA | KHJ0314_NE_3 | FLM_TE | [8 empty] | API | 07/31/2025 15:40:06 | 08/08/2025 14:39:06 | 08/08/2025 14:39:23 |  |  | 08/08/2025 14:39:40 |  | Hakim Ullah Raif Ullah Jan | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250731001080 | PCM-20250731-00001619 | TT-20250731-01618 | Reference_telecom | Region_2 | RIY0130 | RIY0130 | Transsmission | SFP_Transmission | Reset SFP | Farmanullah Akbar Jan | 07/31/2025 15:40:15 | 09/27/2025 01:07:29 | 08/01/2025 03:40:15 | MW RTN Observing PLA_MEMBER_DOWN_EXT,NB_UNREACHABLE,PORT_MODULE_OFF at RIY0130_NE_3_V | 06/15/2025 00:35:35 | Minor |  | LOF | 06/15/2025 00:35:35 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0130_NE_3_V | FLM_TE | [8 empty] | API | 07/31/2025 15:40:15 | 08/01/2025 07:58:29 | 09/27/2025 01:07:05 |  |  | 09/27/2025 01:07:29 |  | Farmanullah Akbar Jan | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250731001091 | PCM-20250731-00001629 | TT-20250731-01628 | Reference_telecom | Region_2 | RIY0670 | RIY0670 |  |  |  | Zakir Muhammad Yar Muhammad | 07/31/2025 15:40:26 | 09/07/2025 14:13:51 | 08/01/2025 03:40:26 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0670_NE_23_H | 07/15/2024 14:37:34 | Minor |  | LOF | 07/15/2024 14:37:34 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0670_NE_23_H | FLM_TE | [8 empty] | API | 07/31/2025 15:40:26 | 07/31/2025 17:40:03 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250731001092 | PCM-20250731-00001630 | TT-20250731-01629 | Reference_telecom | Region_2 | RIY0670 | RIY0670 |  |  |  | Zakir Muhammad Yar Muhammad | 07/31/2025 15:40:27 | 08/07/2025 20:24:12 | 08/01/2025 03:40:27 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at RIY0670_NE_39_H | 03/04/2025 09:40:01 | Minor |  | LOF | 03/04/2025 09:40:01 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0670_NE_39_H | FLM_TE | [8 empty] | API | 07/31/2025 15:40:27 | 07/31/2025 17:40:03 | [6 empty] | Relocation_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250731001098 | PCM-20250731-00001637 | TT-20250731-01636 | Reference_telecom | Region_2 | RIY0840 | RIY0840 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Muhammad Naeem Muhammad Gulzar | 07/31/2025 15:40:34 | 10/12/2025 12:09:06 | 08/01/2025 03:40:34 | MW RTN Observing MW_LOF,RADIO_RSL_LOW at RIY0840_NE_6 | 09/03/2024 21:51:19 | Minor |  | LOF | 09/03/2024 21:51:19 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0840_NE_6 | FLM_TE | [8 empty] | API | 07/31/2025 15:40:34 | 07/31/2025 16:16:50 | 10/12/2025 12:08:53 |  |  | 10/12/2025 12:09:06 |  | Muhammad Naeem Muhammad Gulzar | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250731001102 | PCM-20250731-00001641 | TT-20250731-01640 | Reference_telecom | Region_2 | RIY0891 | RIY0891 | Transsmission | MW_Waveguide | Reconnect Waveguide | Farmanullah Akbar Jan | 07/31/2025 15:40:39 | 09/27/2025 01:08:12 | 08/01/2025 03:40:39 | MW RTN Observing BD_STATUS at RIY0891_NE_3 | 07/22/2025 12:28:50 | Minor |  | LOF | 07/22/2025 12:28:50 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0891_NE_3 | FLM_TE | [8 empty] | API | 07/31/2025 15:40:39 | 08/01/2025 07:58:30 | 09/27/2025 01:07:46 |  |  | 09/27/2025 01:08:12 |  | Farmanullah Akbar Jan | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250731001121 | PCM-20250731-00001659 | TT-20250731-01659 | Reference_telecom | Region_3 | YBDB2291 | YBDB2291 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Hossam Ali Ahmed Ali | 07/31/2025 15:40:59 | 08/11/2025 22:09:04 | 08/01/2025 03:40:59 | MW RTN Observing RADIO_RSL_LOW,RADIO_RSL_LOW,RADIO_RSL_LOW,PG_LINK_ at YBDB2291_NE_14 | 06/19/2025 10:34:16 | Minor |  | LOF | 06/19/2025 10:34:16 | P1 | SRAN | yanbu | Generator_DG | TX NSA | YBDB2291_NE_14 | FLM_TE | [8 empty] | API | 07/31/2025 15:40:59 | 08/08/2025 05:34:23 | 08/11/2025 22:08:44 |  |  | 08/11/2025 22:09:04 |  | Hossam Ali Ahmed Ali | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250731001363 | PCM-20250731-00001953 | TT-20250731-01932 | Reference_telecom | Region_1 | JBKH0095 | JBKH0095 |  |  |  | Mohamed Abdelaziz | 07/31/2025 17:06:23 | 08/05/2025 21:52:28 | 08/01/2025 05:06:23 | NEC MW Observing LOF,RX Level,LOF,LOF,LOF at JBKH0095-2_2(10.76.111.230) | 09/02/2024 18:53:23 | Minor |  | LOF | 09/02/2024 18:53:23 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBKH0095-2_2(10.76.111.230) | FLM_TE | [8 empty] | API | 07/31/2025 17:06:23 | 07/31/2025 18:22:07 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250731001387 | PCM-20250731-00001977 | TT-20250731-01956 | Reference_telecom | Region_3 | MDUL0542 | MDUL0542 |  |  |  | Hamayo Din Jalal | 07/31/2025 17:06:49 | 08/06/2025 09:17:38 | 08/01/2025 05:06:49 | NEC MW Observing LOF,RX Level,RX Level,LOF,LOF at MDUL0542(10.74.79.131) | 06/15/2025 13:33:30 | Minor |  | LOF | 06/15/2025 13:33:30 | P1 | SRAN | madinah | Sceco_STB | TX NSA | MDUL0542(10.74.79.131) | FLM_TE | [8 empty] | API | 07/31/2025 17:06:49 | 08/01/2025 00:27:39 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250731001388 | PCM-20250731-00001978 | TT-20250731-01957 | Reference_telecom | Region_3 | MKMD0321 | MKMD0321 | Transsmission | MW_Connectors | Replace Indoor MW Connector | TAUSEEF ILYAS | 07/31/2025 17:06:49 | 09/19/2025 22:58:45 | 08/01/2025 05:06:49 | NEC MW Observing LOF,LOF,LOF,RX Level,Radio Traffic Aggregation Link,RX Level,LOF,RX Level,RX Level,LAN Link at MKMD0321-HHR2078(10.253.1.130) | 07/12/2025 05:14:57 | Minor |  | LOF | 07/12/2025 05:14:57 | P2 | SRAN | madinah | Sceco_STB | TX NSA | MKMD0321-HHR2078(10.253.1.130) | FLM_TE | [8 empty] | API | 07/31/2025 17:06:49 | 07/31/2025 22:49:10 | 08/05/2025 18:46:19 |  |  | 09/19/2025 22:58:45 |  | TAUSEEF ILYAS | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250801000460 | PCM-20250801-00000683 | TT-20250801-00641 | Reference_telecom | Region_4 | TURY0688 | TURY0688 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 08/01/2025 12:52:19 | 08/03/2025 08:20:31 | 08/01/2025 18:52:19 | 1(2G) site down under TURY0688-P3 (REF_TT-20250801-00519) | 08/01/2025 10:28:23 | Major | 7706 | BTS O&M LINK FAILURE | 08/01/2025 10:28:23 | P3 | 2G | taif | Sceco | 2G_3G_LTE SA | TURY0688 | FLM_EM | TURY0688 | Results: DOWN SITE HUB TURY0688 TURY0688 Summary: Hub: TURY0688, Down Count: 1, Down Sites: TURY0688 Alarm Summary: TURY0688 No Active Alarm on HUB |  |  |  |  | site down |  | API | 08/01/2025 12:52:19 | 08/02/2025 21:43:26 | 08/03/2025 08:20:20 |  |  | 08/03/2025 08:20:31 |  | Afzal Hussain Anwar Ul Haq |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20250801000510 | PCM-20250801-00000746 | TT-20250801-00726 | Telecom | Region_1 | HFF0096 | HFF0096 |  |  |  | Junaid Eisa | 08/01/2025 13:37:30 | 08/06/2025 01:19:28 | 08/02/2025 01:37:30 | ODU CPU / Cable Open at HFF0096-2 on 10.74.82.26 @ Sceco | 08/01/2025 13:36:33 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 08/01/2025 13:36:24 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF0096 | FLM_TE | [8 empty] | API | 08/01/2025 13:37:30 | [7 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250802000024 | PCM-20250802-00000036 | TT-20250802-00026 | Reference_telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 08/02/2025 00:23:45 | 09/24/2025 17:16:43 | 08/02/2025 12:23:45 | JED1W6081 Partial Down | 08/01/2025 23:41:32 | Minor | 613007 | Wi-Fi AP Out Of Service | 08/01/2025 23:41:32 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_1-BF-AP14 | FLM_TE | [8 empty] | API | 08/02/2025 00:23:45 | 08/03/2025 13:34:29 | 09/24/2025 17:16:32 |  |  | 09/24/2025 17:16:43 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250802000212 | PCM-20250802-00000328 | TT-20250802-00279 | Telecom | Region_5 | YAQ0345 | YAQ0345 | Equipment | SFP_BTS | Clean SFP | Jawad Ali Bakht Sher Khan | 08/02/2025 04:47:22 | 08/18/2025 15:41:33 | 08/02/2025 10:47:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at YAQ0345-G9-L9-L18-L21-SBTS-P3 @ Sceco_STB | 08/02/2025 04:46:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 08/02/2025 04:46:35 | P2 | 2G | makkah | Sceco_STB | 5G_Cell SA | YAQ0345 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 08/02/2025 04:47:22 | 08/07/2025 03:39:15 | [5 empty] | Jawad Ali Bakht Sher Khan | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250802001337 | PCM-20250802-00001909 | TT-20250802-01607 | Telecom | Region_4 | JED0965-ZJe04-CSG-01 | JED0965 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 08/02/2025 19:40:17 | 08/02/2025 22:12:09 | 08/03/2025 07:40:17 | Optical Invalid at JED0965-ZJe04-CSG-01 @ Sceco | 08/02/2025 15:37:19 | Minor | 101-2505224 | Optical Invalid | 08/02/2025 15:37:01 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0965-ZJe04-CSG-01 | FLM_TE | [8 empty] | API | 08/02/2025 19:40:17 | 08/02/2025 22:12:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250803000075 | PCM-20250803-00000123 | TT-20250803-00120 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/03/2025 01:36:01 | 09/10/2025 16:38:02 | 08/03/2025 13:36:01 | PT::As per BO request FLM need to perform HC at JED1U6739 | 08/03/2025 01:35:50 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/03/2025 01:35:50 | VIP | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1U6739 | FLM_TE | [8 empty] | API | 08/03/2025 01:36:01 | 08/03/2025 13:34:37 | 09/10/2025 16:37:52 |  |  | 09/10/2025 16:38:02 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250803000496 | PCM-20250803-00000766 | TT-20250803-00580 | Telecom | Region_4 | HLA0423-LL-CSG-01 | HLA0423 | Transsmission | Fiber CUT | Mobily LL cut | Mudassar Bashir Bashir Ahmad | 08/03/2025 09:32:42 | 08/10/2025 15:59:08 | 08/03/2025 21:32:42 | link down HLA0423-LL-CSG-01 to JDJZ0778-LL-CSG-01 | 08/03/2025 08:06:28 | Minor | 15269 | LOS | 08/03/2025 08:06:25 | P1 | IPRAN | qunfuddah | Sceco_STB | IPRAN NSA | HLA0423-LL-CSG-01 | FLM_TE |  | Dear @Shabakkat_FLM_R4 Thanks to check Link HLA0423-JDJZ0778 | PCM-20250803-00000591 | Dear @Shabakkat_FLM_R4 Thanks to check Link HLA0423-JDJZ0778 | Dear @Shabakkat_FLM_R4 Thanks to check Link HLA0423-JDJZ0778 |  |  |  | API | 08/03/2025 09:32:42 | 08/03/2025 09:34:29 | 08/10/2025 15:59:02 |  |  | 08/10/2025 15:59:08 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250803000612 | PCM-20250803-00000959 | TT-20250727-00835 | Telecom | Region_2 | RIYB6027 | RIYB6027 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 08/03/2025 11:05:37 | 08/04/2025 08:36:05 | 08/03/2025 17:05:37 | HC:: Multiple Alarms Active at Site RIYB6027 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYB6027 | FLM_TE |  |  | PCM-20250727-00002160 | There are still active alarms under (RIYB6027_MU5 & RIYB6027_MU6 ) Master Slave Link Alarm kindly check , the connection between the MU and the RU , SFPs Modules , monitor board for Master unit and there is MU4 for this Site is not reachable , kindly check the Ethernet cable between the Switch and Mu | There are still active alarms under (RIYB6027_MU5 & RIYB6027_MU6 ) Master Slave Link Alarm kindly check , the connection between the MU and the RU , SFPs Modules , monitor board for Master unit and there is MU4 for this Site is not reachable , kindly check the Ethernet cable between the Switch and Mu |  |  |  | API | 08/03/2025 11:05:37 | 08/04/2025 08:36:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_Involved_stay | CM20250803000625 | PCM-20250803-00000976 | TT-20250727-00833 | Telecom | Region_2 | RIYB6026 | RIYB6026 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 08/03/2025 11:14:59 | 08/04/2025 12:56:40 | 08/03/2025 17:14:59 | HC:: Multiple Alarms Active at Site RIYB6026 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYB6026 | FLM_TE |  |  | PCM-20250727-00002158 | There are still active alarms under (RIYB6026_MU2) Master Slave Link Alarm kindly check , the connection between the MU and the RU , SFPs Modules , monitor board for Master unit and there is RUs under the MU is still down and MU is reachable and accessible | There are still active alarms under (RIYB6026_MU2) Master Slave Link Alarm kindly check , the connection between the MU and the RU , SFPs Modules , monitor board for Master unit and there is RUs under the MU is still down and MU is reachable and accessible |  |  |  | API | 08/03/2025 11:14:59 | 08/04/2025 11:07:32 | 08/04/2025 11:07:39 | 08/04/2025 11:07:41 | 08/04/2025 11:07:43 | 08/04/2025 12:56:40 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250803000670 | PCM-20250803-00001065 | TT-20250727-00841 | Telecom | Region_2 | RIYB6058 | RIYB6058 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Ali Raza Abdi Syed Muhammad Taqi Abdi | 08/03/2025 11:51:40 | 09/03/2025 12:12:59 | 08/03/2025 17:51:40 | HC:: Multiple Alarms Active at Site RIYB6058 ¦ FLM Need To Check | 07/27/2025 10:21:51 | Major |  | Health Check-WO to TE FME | 07/27/2025 10:21:51 | P3 | SRAN | riyadh | Sceco | IBS SA | RIYB6058 | FLM_TE |  |  | PCM-20250727-00002156 | Kindly support to check RIYB6058_MU01 as the MU is Flapping and not reachable kindly support to check the Ethernet cable between the MU and Switch | Kindly support to check RIYB6058_MU01 as the MU is Flapping and not reachable kindly support to check the Ethernet cable between the MU and Switch |  |  |  | API | 08/03/2025 11:51:40 | 08/03/2025 12:57:14 | 09/03/2025 09:01:27 | 09/03/2025 09:23:39 | 09/03/2025 10:12:51 | 09/03/2025 12:12:59 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250803000705 | PCM-20250803-00001124 | TT-20250803-01033 | Reference_telecom | Region_5 | ABS0311 | ABS0311 |  |  |  | SAID AHMED HASSAN ABDALLA | 08/03/2025 12:26:02 | 08/31/2025 11:50:50 | 08/04/2025 00:26:02 | LossOfSignal observed in ABS0311_02 towards 10.21.73.163 @ Sceco_STB | 08/03/2025 00:25:59 | Minor |  | LossOfSignal | 08/03/2025 00:25:56 | P2 | 2G | makkah | Sceco_STB | TX NSA | ABS0311 | FLM_TE | [8 empty] | API | 08/03/2025 12:26:02 | 08/07/2025 10:52:54 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250803001112 | PCM-20250803-00001712 | TT-20250803-01579 | Telecom | Region_4 | JED6137 | JED6137 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/03/2025 16:32:02 | 09/24/2025 17:17:09 | 08/03/2025 22:32:02 | HC:: Multiple Alarms Active at Site JED6137 ¦ FLM Need To Check | 08/03/2025 16:31:44 | Major |  | Health Check-WO to TE FME | 08/03/2025 16:31:44 | P3 | 2G | jeddah | Sceco | IBS SA | JED6137 | FLM_TE | [8 empty] | API | 08/03/2025 16:32:02 | 08/03/2025 16:48:48 | 09/24/2025 17:17:03 |  |  | 09/24/2025 17:17:09 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250803001116 | PCM-20250803-00001717 | TT-20250803-01583 | Telecom | Region_4 | JED6010 | JED6010 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/03/2025 16:32:06 | 09/24/2025 17:16:59 | 08/03/2025 22:32:06 | HC:: Multiple Alarms Active at Site JED6010 ¦ FLM Need To Check | 08/03/2025 16:31:44 | Major |  | Health Check-WO to TE FME | 08/03/2025 16:31:44 | P3 | 2G | jeddah | Sceco | IBS SA | JED6010 | FLM_TE | [8 empty] | API | 08/03/2025 16:32:06 | 08/03/2025 16:48:49 | 09/24/2025 17:16:52 |  |  | 09/24/2025 17:16:59 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250803001118 | PCM-20250803-00001719 | TT-20250803-01585 | Telecom | Region_4 | JED6136 | JED6136 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/03/2025 16:32:08 | 09/24/2025 17:17:22 | 08/03/2025 22:32:08 | HC:: Multiple Alarms Active at Site JED6136 ¦ FLM Need To Check | 08/03/2025 16:31:44 | Major |  | Health Check-WO to TE FME | 08/03/2025 16:31:44 | P3 | 2G | jeddah | Sceco | IBS SA | JED6136 | FLM_TE | [8 empty] | API | 08/03/2025 16:32:08 | 08/03/2025 16:48:50 | 09/24/2025 17:17:13 |  |  | 09/24/2025 17:17:22 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250803001203 | PCM-20250803-00001857 | TT-20250803-01703 | Telecom | Region_5 | HA1 | HA1 |  |  |  | Muhammad Zubair | 08/03/2025 17:26:09 | 08/04/2025 01:26:02 | 08/03/2025 23:26:09 | Observing Multiple ALU CIDs flapped and restored B/W MAK HA | 08/03/2025 17:21:48 | Major | 5000003 | Link Down | 08/03/2025 17:21:48 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | HA1 | FLM_TE | [5 empty] | Observing Multiple ALU CIDs flapped and restored B/W MAK HA |  |  | API | 08/03/2025 17:26:09 | 08/04/2025 01:26:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250803001333 | PCM-20250803-00001996 | TT-20250803-01835 | Reference_telecom | Region_3 | MDTB0334 | MDTB0334 |  |  |  | Junaid Eisa | 08/03/2025 17:45:22 | 08/14/2025 04:46:22 | 08/04/2025 05:45:22 | NEC MW Observing Radio Traffic Aggregation Link,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply at MDTB0334(10.75.32.130) | 07/25/2025 17:21:45 | Minor |  | LOF | 07/25/2025 17:21:45 | P1 | SRAN | madinah | Sceco | TX NSA | MDTB0334 | FLM_TE | [8 empty] | API | 08/03/2025 17:45:22 | [7 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250803001341 | PCM-20250803-00002004 | TT-20250803-01843 | Reference_telecom | Region_1 | QTF2866 | QTF2866 |  |  |  | Meraj Husain Idd Baksh | 08/03/2025 17:45:30 | 08/20/2025 11:35:41 | 08/04/2025 05:45:30 | NEC MW Observing ODU CPU / Cable Open,LOF,LOF at QTF2866_IPASO1000#1(10.158.221.163) | 08/01/2025 00:00:19 | Minor |  | LOF | 08/01/2025 00:00:19 | P2 | SRAN | dammam | Sceco | TX NSA | QTF2866_IPASO1000#1 | FLM_TE | [8 empty] | API | 08/03/2025 17:45:30 | 08/03/2025 18:47:52 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250804000083 | PCM-20250804-00000154 | TT-20250804-00199 | Telecom | Region_2 | RIY0078 | RIY0078 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 08/04/2025 01:56:45 | 08/21/2025 09:50:39 | 08/04/2025 05:56:45 | HARD_BAD alarm active at RIY6078_NE_3_SITEA | 08/04/2025 01:51:17 | Critical | 1-236 | HARD_BAD | 08/04/2025 01:51:19 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY6078 | FLM_TE | [8 empty] | API | 08/04/2025 01:56:45 | 08/04/2025 14:43:11 | 08/04/2025 14:48:38 | 08/04/2025 14:48:42 |  | 08/21/2025 09:50:39 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250804000139 | PCM-20250804-00000242 | TT-20250803-00456 | Telecom | Region_4 | SJED1S7012 | SJED0012 | Equipment | SFP_BTS | Clean SFP | MALIK ATIF ZAMAN | 08/04/2025 02:59:24 | 08/06/2025 22:59:01 | 08/04/2025 14:59:24 | PT:: BO need to check Cell state audit alarm under Region 4 for Small Cells | 08/03/2025 06:35:36 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/03/2025 06:35:36 | VIP | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | SJED1S70121 SJED1S73414 SJED1S73411 SJED1S70124 | FLM_TE |  |  | PCM-20250803-00000450 | Audit alarm is clear , please check SJED1S7341 site have LOS alarm | Audit alarm is clear , please check SJED1S7341 site have LOS alarm |  |  |  | API | 08/04/2025 02:59:24 | 08/04/2025 06:24:24 | 08/06/2025 22:58:52 |  |  | 08/06/2025 22:59:01 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250804000950 | PCM-20250804-00001413 | TT-20250804-01533 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 08/04/2025 15:03:11 | 08/06/2025 04:14:45 | 08/04/2025 21:03:11 | Observing Multiple ALU CIDs flapped and restored B/W MAK - TF | 08/04/2025 15:00:09 | Major | 5000003 | Link Down | 08/04/2025 15:00:09 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE | [5 empty] | Observing Multiple ALU CIDs flapped and restored B/W MAK - TF |  |  | API | 08/04/2025 15:03:11 | 08/06/2025 04:14:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250804001181 | PCM-20250804-00001746 | TT-20250804-01810 | MW_HC | Region_1 | JBKH0088 | JBKH0088 |  |  |  | Mohamed Abdelaziz | 08/04/2025 17:16:07 | 08/28/2025 13:46:58 | 08/05/2025 05:16:07 | (As per optimization Team request) NEC MW HC For link JBKH0088--JBKH0113 is counting performance errors | 08/04/2025 17:14:58 | Minor | 1-631 | MW_LOF | 08/04/2025 17:14:58 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH0088--JBKH0113 | FLM_TE | [5 empty] | (As per optimization Team request) NEC MW HC For link JBKH0088--JBKH0113 is counting performance errors |  |  | API | 08/04/2025 17:16:07 | 08/04/2025 17:24:03 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250804001280 | PCM-20250804-00001865 | TT-20250804-01923 | MW_HC | Region_1 | HFBD0010 | HFBD0010 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Muhammad Kashif M M Bashir | 08/04/2025 17:44:18 | 09/03/2025 00:37:28 | 08/05/2025 05:44:18 | NEC MW HC_P0 Observing Performance Issue at HFBD0008(10.154.27.11)--HFBD0010(10.154.27.2) | 08/04/2025 17:42:57 | Minor |  | LOF | 08/04/2025 17:42:57 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFBD0008(10.154.27.11)--HFBD0010(10.154.27.2) | FLM_TE | [8 empty] | API | 08/04/2025 17:44:18 | 08/28/2025 16:43:59 | 09/02/2025 01:30:01 | 09/02/2025 01:30:05 | 09/02/2025 01:31:19 | 09/03/2025 00:37:28 |  | Muhammad Kashif M M Bashir | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250804001390 | PCM-20250804-00002018 | TT-20250804-02084 | Reference_telecom | Region_6 | FIF0045 | FIF0045 |  |  |  | Muhammad Ali | 08/04/2025 19:05:50 | 10/05/2025 13:01:40 | 08/05/2025 07:05:50 | LinkDown observed in FIF0045_01 towards 10.3.86.164 @ Sceco | 08/04/2025 07:06:54 | Minor |  | LinkDown | 08/04/2025 07:05:45 | P2 | 2G | dair | Sceco | TX NSA | FIF0045 | FLM_TE | [8 empty] | API | 08/04/2025 19:05:50 | 08/04/2025 20:02:40 | 10/05/2025 13:01:35 | 10/05/2025 13:01:37 | 10/05/2025 13:01:40 |  |  |  | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250804001407 | PCM-20250804-00002049 | TT-20250804-02126 | Reference_telecom | Region_5 | MAK0645 | MAK0645 | Equipment | BTS_Cable | Reconnect Fiber Cable | Khamis Mosaad Moursy Shaboun | 08/04/2025 19:23:22 | 08/08/2025 16:54:23 | 08/05/2025 01:23:22 | MAK0645-GSM-P2 BASE STATION EXTERNAL ALARM NOTIFICATION(RECTIFIER LOW BATTERY VOLTAGE 46.3 V) (REF TT :: TT-20250728-01016) | 08/04/2025 18:52:53 | Major | 7103 | BASE STATION EXTERNAL ALARM NOTIFICATION | 08/04/2025 18:52:53 | P2 | 2G | makkah | Sceco | 2G SA | MAK0645-GSM-P2 | FLM_TE | [8 empty] | API | 08/04/2025 19:23:22 | 08/08/2025 15:26:03 | 08/08/2025 15:28:19 | 08/08/2025 15:28:22 | 08/08/2025 15:38:39 | 08/08/2025 16:54:23 |  | Khamis Mosaad Moursy Shaboun |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250804001561 | PCM-20250804-00002564 | TT-20250702-02162 | Reference_telecom | Region_6 | TFBH0887 | TFBH0887 | Transsmission | MW_HW_fault | Replace Power Board | SHAH KHALID | 08/04/2025 22:20:11 | 08/09/2025 03:59:18 | 08/05/2025 04:20:11 | MW_IS-IS Adjacency Changed at TFBH0887 to BAH0005 / AB1-ASG-02 // TT-20250320-02435 | 07/02/2025 14:48:49 | Major | 15269 | LOS | 07/02/2025 14:48:49 | P1 | 2G | makhwa | Sceco_STB | IPRAN NSA | MW_IS-IS Adjacency Changed at TFBH0887 to BAH0005 / AB1-ASG-02 // TT-20250320-02435 | FLM_TE |  |  | PCM-20250804-00001779 | Please mention what action done by FLM and close the ticket after checking status with FO | Please mention what action done by FLM and close the ticket after checking status with FO |  |  |  | API | 08/04/2025 22:20:11 | 08/04/2025 22:57:25 | 08/09/2025 03:58:53 |  |  | 08/09/2025 03:59:18 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250805000436 | PCM-20250805-00000655 | TT-20250805-00695 | Reference_telecom | Region_4 | JED0001-ZJe04-CSG-07 | JED0001 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 08/05/2025 08:15:05 | 08/05/2025 10:50:47 | 08/05/2025 20:15:05 | Optical Invalid at JED0001-ZJe04-CSG-07 ¦¦ ref TT-20250722-01419 @ Sceco_STB | 08/04/2025 20:35:18 | Minor | 101-2505224 | Optical Invalid | 08/04/2025 20:35:00 | P1 | IPRAN | jeddah | Sceco_STB | IPRAN NSA | JED0001-ZJe04-CSG-07 | FLM_TE | [8 empty] | API | 08/05/2025 08:15:05 | 08/05/2025 10:50:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250805000809 | PCM-20250805-00001186 | TT-20250805-01287 | EM | Region_3 | MKMD2542 | MKMD2542 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 08/05/2025 14:00:25 | 09/04/2025 04:52:58 | 08/06/2025 02:00:25 | Genset not in auto mode at MKMD2542-P3_SRAN @ Generator_SG | 08/05/2025 13:58:38 | Minor | 65113 | Genset not in auto mode | 08/05/2025 12:11:48 | P3 | 4G | madinah | Generator_SG | 2G NSA | MKMD2542 | FLM_EM | [8 empty] | API | 08/05/2025 14:00:25 | 08/25/2025 01:26:14 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250806000253 | PCM-20250806-00000407 | TT-20250806-00442 | Reference_telecom | Region_1 | HMBY0419 | HMBY0419 |  |  |  | Talha Manzoor | 08/06/2025 05:30:25 | 08/20/2025 11:35:43 | 08/06/2025 17:30:25 | HARD_BAD at HMBY0419_NE_1_SDB @ Generator_SG | 08/06/2025 04:30:18 | Minor | 1-236 | HARD_BAD | 08/06/2025 04:30:08 | P3 | SRAN | dammam | Generator_SG | TX NSA | HMBY0419 | FLM_TE | [8 empty] | API | 08/06/2025 05:30:25 | 08/06/2025 06:41:43 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250806000321 | PCM-20250806-00000501 | TT-20250806-00549 | Reference_telecom | Region_4 | JED0054 | JED0054 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 08/06/2025 06:58:56 | 10/22/2025 10:50:58 | 08/06/2025 10:58:56 | 4(2G) 2(LTE) 4(5G) sites down under JED0054-P2 @ Sceco | 08/06/2025 05:29:35 | Critical | 7706 | BTS O&M LINK FAILURE | 08/06/2025 05:29:35 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0879-P2 2G_5G,JED0054-P2 2G_LTE_5G,JED2857-P3 2G_5G,JED0486-P1-HUB 2G_LTE_5G | FLM_TE | JED0054 | Results: DOWN SITE HUB JED0879-P2 JED0054 JED0054-P2 JED0054 JED2857-P3 JED0054 JED0486-P1-HUB JED0054 Summary: Hub: JED0054, Down Count: 4, Down Sites: JED0879-P2, JED0054-P2, JED2857-P3, JED0486-P1-HUB Alarm Summary: JED0054 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 08/06/2025 06:58:56 | 08/06/2025 10:11:52 | 10/22/2025 10:50:58 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250806000346 | PCM-20250806-00000537 | TT-20250806-00580 | Telecom | Region_4 | JED1U6796 | JED6096 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/06/2025 07:29:00 | 09/10/2025 16:47:04 | 08/06/2025 19:29:00 | BASE STATION ANTENNA LINE PROBLEM at JED1U6796-G9-L18-L21-SBTS-P2 @ Sceco | 08/06/2025 07:12:18 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 08/06/2025 07:12:11 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6796 | FLM_TE |  |  | PCM-20250806-00000527 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 08/06/2025 07:29:00 | 09/04/2025 18:37:57 | 09/10/2025 16:46:56 |  |  | 09/10/2025 16:47:04 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250806000534 | PCM-20250806-00000916 | TT-20250806-00947 | Telecom | Region_4 | MKYL0920 | MKYL0920 |  |  |  | Riasat Ali Allah Baksh | 08/06/2025 11:23:16 | 08/06/2025 19:18:39 | 08/06/2025 17:23:16 | 1(2G) site down under MKYL0920-P2 @ Generator_DG | 08/06/2025 11:16:56 | Major | 7706 | BTS O&M LINK FAILURE | 08/06/2025 11:16:49 | P2 | 2G | jeddah | Generator_DG | 2G SA | MKYL0920 | FLM_TE | MKYL0920 | Results: DOWN SITE HUB MKYL0920 MKYL0920 Summary: Hub: MKYL0920, Down Count: 1, Down Sites: MKYL0920 Alarm Summary: MKYL0920 No Active Alarm on HUB |  |  |  |  | site down |  | API | 08/06/2025 11:23:16 | 08/06/2025 19:18:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250806000673 | PCM-20250806-00001034 | TT-20250724-00680 | Reference_telecom | Region_6 | WBAH0001 | BAH0001 | Transsmission | SFP_Transmission | Reset SFP | SHAH KHALID | 08/06/2025 12:34:17 | 10/14/2025 15:22:29 | 08/07/2025 00:34:17 | WBAH0001 Partial down | 07/24/2025 08:42:40 | Minor | 613007 | Wi-Fi AP Out Of Service | 07/24/2025 08:42:40 | P1 | WIFI | Albaha | Sceco | Wifi SA | WBAH0001_2-3F-AP04 | FLM_TE |  |  | PCM-20250806-00000358 | as per HD WIFI Team; Site is under Access issue , please kindly check once access secured | as per HD WIFI Team; Site is under Access issue , please kindly check once access secured |  |  |  | API | 08/06/2025 12:34:17 | 08/06/2025 13:27:44 | 10/09/2025 01:46:00 |  |  | 10/14/2025 15:22:29 |  | SHAH KHALID | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250806000803 | PCM-20250806-00001228 | TT-20250806-01249 | Reference_telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 08/06/2025 14:04:29 | 09/24/2025 17:17:38 | 08/07/2025 02:04:29 | JED1W6081 Partial Down | 08/06/2025 13:34:50 | Minor | 613007 | Wi-Fi AP Out Of Service | 08/06/2025 13:34:50 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_1-5F-AP04 | FLM_TE | [8 empty] | API | 08/06/2025 14:04:29 | 08/06/2025 16:55:08 | 09/24/2025 17:17:27 |  |  | 09/24/2025 17:17:38 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250806000905 | PCM-20250806-00001458 | TT-20250806-01402 | Telecom | Region_4 | JED6032 | JED6032 | Equipment | BTS_Cable | Re-Tightened Indoor Feeder cable Connector | Mohamed Farag Abdelbary | 08/06/2025 15:14:50 | 09/18/2025 12:33:42 | 08/06/2025 21:14:50 | PT::FLM need to perform HC at JED6032-P3 (LNOC request) | 08/06/2025 15:14:15 | Major | 7604 | BASE STATION OPERATION DEGRADED | 08/06/2025 15:14:15 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED6032 | FLM_TE | [8 empty] | API | 08/06/2025 15:14:50 | 08/06/2025 16:55:08 | 09/15/2025 09:46:40 | 09/15/2025 09:46:52 |  | 09/18/2025 12:33:42 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250806000986 | PCM-20250806-00001584 | TT-20250806-01540 | Reference_telecom | Region_3 | MDHL0374 | MDHL0374 | Transsmission | SFP_Transmission | Reset SFP | Junaid Eisa | 08/06/2025 16:14:01 | 08/15/2025 04:08:12 | 08/07/2025 04:14:01 | MW RTN Observing ETH_LINK_DOWN at MDHL0374_NE_1 | 07/30/2025 16:13:36 | Minor |  | LOF | 07/30/2025 16:13:36 | P3 | SRAN | hail | Sceco_STB | TX NSA | MDHL0374_NE_1 | FLM_TE | [8 empty] | API | 08/06/2025 16:14:01 | [6 empty] | Mohamed Naveed | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250806001088 | PCM-20250806-00001689 | TT-20250806-01646 | Reference_telecom | Region_2 | WRYD0001 | WRYD0001 |  |  |  | Abdelrahim Abdalla Abdelrahim Khairy | 08/06/2025 16:15:53 | 09/13/2025 11:29:21 | 08/07/2025 04:15:53 | Nokia Eband Observing LinkDown-Port 1/1,LossOfSignal-Port 1/2 at WRYD0001-10.3.127.139 | 04/28/2025 11:07:12 | Minor |  | LOF | 04/28/2025 11:07:12 | P3 | WIFI | riyadh | Sceco | TX NSA | WRYD0001-10.3.127.139 | FLM_TE | [8 empty] | API | 08/06/2025 16:15:53 | 09/13/2025 11:29:21 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250807000205 | PCM-20250807-00000335 | TT-20250806-02261 | Reference_EM | Region_4 | HHR0469 | HHR0469 | Equipment | BSS_HW_fault | Replace Air Scale | MALIK ATIF ZAMAN | 08/07/2025 03:09:48 | 08/07/2025 09:27:17 | 08/07/2025 09:09:48 | 1(2G/LTE) sites down under HHR0469-P3 @ Generator_SG (Ref.:: TT-20250806-01174) | 08/06/2025 19:14:50 | Major | 7706 | BTS O&M LINK FAILURE | 08/06/2025 19:14:50 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | HHR0469-P3 | FLM_TE | HHR0469 | Results: DOWN SITE HUB HHR0469-P3 HHR0469 Summary: Hub: HHR0469, Down Count: 1, Down Sites: HHR0469-P3 Alarm Summary: HHR0469 No Active Alarm on HUB | PCM-20250807-00000314 | Please share approval mail with all required details | Please share approval mail with all required details |  | sites down |  | API | 08/07/2025 03:09:48 | 08/07/2025 09:25:14 | 08/07/2025 09:26:41 |  |  | 08/07/2025 09:27:17 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250807000428 | PCM-20250807-00000704 | TT-20250807-00708 | Reference_telecom | Region_3 | YNB2M7675 | YNB0675 |  |  |  | Muhammad Sajjad R3 | 08/07/2025 08:06:32 | 08/19/2025 15:41:37 | 08/07/2025 14:06:32 | Cell Unavailable at YNB2M7675-P1-VIP_AIR @ Sceco_STB) (REF:TT-20250725-00307) | 07/08/2025 13:19:18 | Major | 29240 | Cell Unavailable | 07/08/2025 13:19:18 | VIP | 4G | yanbu | Sceco_STB | 2G_LTE SA | Cell Unavailable at YNB2M7675-P1-VIP_AIR @ Sceco_STB) (REF:TT-20250725-00307) | FLM_TE | [8 empty] | API | 08/07/2025 08:06:32 | 08/07/2025 12:51:27 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250807000693 | PCM-20250807-00001079 | TT-20250807-01538 | Telecom | Region_3 | MDTB0334-ASG-01 | MDTB0334 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 08/07/2025 11:17:35 | 08/19/2025 15:46:25 | 08/07/2025 17:17:35 | Physical Port Down at MDTB0334-ASG-01 @ Generator_DG | 08/07/2025 11:10:07 | Major | 101-2505274 | Physical Port Down | 08/07/2025 11:10:00 | P2 | IPRAN | madinah | Generator_DG | IPRAN NSA | MDTB0334-ASG-01 | FLM_TE | [8 empty] | API | 08/07/2025 11:17:35 | 08/07/2025 17:08:29 | 08/07/2025 19:44:23 | [5 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250807000876 | PCM-20250807-00001322 | TT-20250807-01714 | Telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Muhammad Kashif M M Bashir | 08/07/2025 12:47:06 | 08/12/2025 11:28:55 | 08/07/2025 18:47:06 | BBU CPRI Interface Error at HFF6036-DCU2 @ Sceco | 12/18/2023 02:30:30 | Major | 26234 | BBU CPRI Interface Error | 12/18/2023 02:28:57 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 08/07/2025 12:47:06 | 08/07/2025 19:12:43 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250807001388 | PCM-20250807-00002023 | TT-20250807-02395 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 08/07/2025 17:35:15 | 09/30/2025 00:43:45 | 08/08/2025 05:35:15 | PT::As per Bo request FLM need to perform HC at JED6135 | 08/07/2025 17:35:05 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/07/2025 17:35:05 | P3 | SRAN | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED6135 | FLM_TE | [8 empty] | API | 08/07/2025 17:35:15 | 08/07/2025 18:26:24 | 09/29/2025 16:55:39 | 09/29/2025 16:56:01 | 09/29/2025 16:56:26 | 09/30/2025 00:43:45 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250807001563 | PCM-20250807-00002310 | TT-20250807-02691 | Telecom | Region_1 | DMV0963 | DMV0963 |  |  |  | Muhammad Kashif M M Bashir | 08/07/2025 20:25:48 | 08/12/2025 11:28:56 | 08/08/2025 08:25:48 | RF Unit Maintenance Link Failure at DMV0963-P2_SRAN @ Sceco | 08/07/2025 12:10:17 | Minor | 26235 | RF Unit Maintenance Link Failure | 08/07/2025 18:38:31 | P2 | SRAN | hafouf | Sceco | 2G NSA | DMV0963 | FLM_TE | [8 empty] | API | 08/07/2025 20:25:48 | 08/07/2025 20:31:00 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250809000073 | PCM-20250809-00000121 | TT-20250809-00107 | EM | Region_2 | RYHR0743 | RYHR0743 |  |  |  | Pawan Virdi Santokh Singh | 08/09/2025 01:21:13 | 08/18/2025 12:08:23 | 08/09/2025 13:21:13 | NETECO: AC Failure at RYHR0743 @ Sceco | 08/09/2025 01:14:45 | Minor | 10202 | AC Failure | 08/09/2025 01:14:45 | P2 | SRAN | riyadh | Sceco | 2G NSA | RYHR0743 | FLM_EM | [8 empty] | API | 08/09/2025 01:21:13 | 08/09/2025 08:46:57 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250809000077 | PCM-20250809-00000126 | TT-20250809-00110 | Reference_EM | Region_2 | RYHR0743 | RYHR0743 |  |  |  | Pawan Virdi Santokh Singh | 08/09/2025 01:24:52 | 08/18/2025 12:08:24 | 08/09/2025 13:24:52 | Mains Failure at RYHR0743-P2_SRAN @ Sceco | 08/09/2025 01:14:45 | Minor | 65109 | Mains Failure | 08/09/2025 01:14:42 | P2 | SRAN | riyadh | Sceco | 2G NSA | RYHR0743 | FLM_EM | [8 empty] | API | 08/09/2025 01:24:52 | 08/09/2025 08:46:57 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250809000167 | PCM-20250809-00000271 | TT-20250809-00227 | EM | Region_2 | RYHR2M5743 | RYHR0743 |  |  |  | Pawan Virdi Santokh Singh | 08/09/2025 02:59:33 | 08/18/2025 12:08:24 | 08/09/2025 08:59:33 | 1(2G/3G/LTE) sites down under RYHR0743-P2/R2_RY1_HWBSC01 @ Sceco | 08/09/2025 02:52:30 | Major | 21825 | CSL Fault | 08/09/2025 02:52:29 | P2 | 2G | riyadh | Sceco | 2G_3G_LTE SA | RYHR0743-P2 | FLM_EM | RYHR0743 | Results: DOWN SITE HUB RYHR0743-P2 RYHR0743 Summary: Hub: RYHR0743, Down Count: 1, Down Sites: RYHR0743-P2 Alarm Summary: RYHR0743 Alarm Active on HUB |  |  |  |  | sites down |  | API | 08/09/2025 02:59:33 | 08/09/2025 08:46:58 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250809000231 | PCM-20250809-00000368 | TT-20250808-02206 | Reference_telecom | Region_4 | TAF1MC2108 | TAF2108 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHEHERYAR KHAN MUNAMMAD NAWAZ | 08/09/2025 03:55:53 | 08/17/2025 08:56:08 | 08/09/2025 09:55:53 | 1(5G) site down under TAF2108-P3 (Ref:TT-20250808-01157) | 08/08/2025 15:04:47 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 08/08/2025 15:04:47 | P3 | 5G | taif | Sceco | 5G SA | TAF1MC2108-NR3.5-P2 | FLM_TE | TAF1MC2108 | Results: DOWN SITE HUB TAF1MC2108-NR3.5-P2 TAF1MC2108 Summary: Hub: TAF1MC2108, Down Count: 1, Down Sites: TAF1MC2108-NR3.5-P2 Alarm Summary: TAF1MC2108 No Active Alarm on HUB | PCM-20250809-00000012 | For HW approval kindly share over mail | For HW approval kindly share over mail |  | site down |  | API | 08/09/2025 03:55:53 | 08/09/2025 10:05:28 | 08/17/2025 08:56:01 |  |  | 08/17/2025 08:56:08 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250809000584 | PCM-20250809-00000881 | TT-20250809-00574 | Reference_telecom | Region_6 | MRD1M7101 | MRD0101 | Equipment | BSS_HW_fault | Replace RF Module | Fawad Khan | 08/09/2025 09:09:26 | 08/09/2025 11:13:41 | 08/09/2025 15:09:26 | BASE STATION SERVICE PROBLEM ( No connection to unit ) at MRD1M7101-P2-CA-L800-WBB-G3 REF ( TT-20250808-01101 ) | 08/08/2025 21:43:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 08/08/2025 21:43:39 | P3 | 4G | mohail | Sceco | 2G_3G_LTE SA | MRD1M7101 | FLM_TE |  |  | PCM-20250809-00000732 | For HW approval kindly share over mail | For HW approval kindly share over mail |  |  |  | API | 08/09/2025 09:09:26 | 08/09/2025 10:21:19 | 08/09/2025 10:21:25 | 08/09/2025 10:21:28 | 08/09/2025 11:00:14 | 08/09/2025 11:13:41 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250809001294 | PCM-20250809-00001878 | TT-20250809-01642 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 08/09/2025 16:17:36 | 08/09/2025 19:39:33 | 08/09/2025 22:17:36 | Observing multiple ALU CIDs down B/W MAK - JED - RYD | 08/09/2025 16:13:49 | Major | 5000003 | Link Down | 08/09/2025 16:13:49 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | MK1 | FLM_TE | [5 empty] | Observing multiple ALU CIDs down B/W MAK - JED - RYD |  |  | API | 08/09/2025 16:17:36 | 08/09/2025 19:39:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250810000273 | PCM-20250810-00000458 | TT-20250810-00398 | EM | Region_4 | JED2979 | JED2979 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 08/10/2025 05:27:01 | 09/01/2025 15:24:31 | 08/10/2025 09:27:01 | 1(2G/LTE/5G) sites down under JED2979-P1-VIP/JED2979-P1-VIP @ Generator_SG | 08/10/2025 05:18:31 | Critical | 7706 | BTS O&M LINK FAILURE | 08/10/2025 05:18:27 | VIP | 2G | jeddah | Generator_SG | 2G_LTE SA | JED2979-P1-VIP | FLM_EM | JED2979 | Results: DOWN SITE HUB JED2979-P1-VIP JED2979 Summary: Hub: JED2979, Down Count: 1, Down Sites: JED2979-P1-VIP Alarm Summary: JED2979 Alarm Active on HUB |  |  |  |  | sites down |  | API | 08/10/2025 05:27:01 | 08/31/2025 16:00:32 | 09/01/2025 15:24:21 |  |  | 09/01/2025 15:24:31 |  | Abd EL Azeez EL Sayed Soliman | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250810000593 | PCM-20250810-00000952 | TT-20250808-02131 | Telecom | Region_4 | JED_eSight | JD1 | Transsmission | IPBB Fluctuation | Reset SFP | Muhammad Mustaqeem Irshad Ali | 08/10/2025 10:17:06 | 10/13/2025 05:14:36 | 08/10/2025 22:17:06 | Optical Invalid in JED_eSight towards ED_RN06_EOR | 08/08/2025 22:55:09 | Minor | 3638 | Component Fault | 08/08/2025 22:55:09 | P1 | PS | jeddah | Sceco_STB | CS CORE NSA | JED_eSight | FLM_TE |  |  | PCM-20250810-00000831 | kindly check TX power is high for the port 40GE2-1-0-4 on JED1_vMSE_RN06_NEW_EOR | kindly check TX power is high for the port 40GE2-1-0-4 on JED1_vMSE_RN06_NEW_EOR |  |  |  | API | 08/10/2025 10:17:06 | 08/18/2025 02:04:38 | 10/13/2025 05:14:14 |  |  | 10/13/2025 05:14:36 |  | Muhammad Mustaqeem Irshad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250810000800 | PCM-20250810-00001239 | TT-20250810-01115 | Telecom | Region_4 | JED6071 | JED6071 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 08/10/2025 13:02:36 | 09/24/2025 17:18:08 | 08/10/2025 19:02:36 | PT:: FLM Need to perform HC at JED6071 under R4 (LNOC Request) | 08/10/2025 13:02:16 | Major | 676767671 | Health Check-WO to TE FME | 08/10/2025 13:02:16 | P1 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED6071 | FLM_TE | [8 empty] | API | 08/10/2025 13:02:36 | 08/10/2025 15:37:34 | 09/24/2025 17:18:01 |  |  | 09/24/2025 17:18:08 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250810001250 | PCM-20250810-00001824 | TT-20250810-01683 | Reference_telecom | Region_6 | RTH0601 | RTH0601 |  |  |  | Muhammad Ali | 08/10/2025 15:51:34 | 09/04/2025 18:37:52 | 08/11/2025 03:51:34 | NEC MW Observing LAN Link at RTH0601(10.1.173.115) | 07/20/2025 13:19:01 | Minor |  | LOF | 07/20/2025 13:19:01 | P2 | 2G | raith | Generator_SG | TX NSA | RTH0601(10.1.173.115) | FLM_TE | [8 empty] | API | 08/10/2025 15:51:34 | 08/10/2025 15:52:17 | 08/31/2025 16:20:11 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250810001354 | PCM-20250810-00001958 | TT-20250810-01810 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 08/10/2025 16:21:19 | 08/11/2025 02:57:44 | 08/10/2025 22:21:19 | Observing multiple ALU CIDs down B/W MAK - JED | 08/10/2025 16:16:56 | Major | 5000003 | Link Down | 08/10/2025 16:16:56 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | MK1 | FLM_TE | [5 empty] | Observing multiple ALU CIDs down B/W MAK - JED |  |  | API | 08/10/2025 16:21:19 | 08/11/2025 02:57:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250810001827 | PCM-20250810-00002701 | TT-20250809-02325 | Telecom | Region_6 | BLS0116 | BLS0116 | Transsmission | MW_bad_Weather | Heavy Rain | Fawad Khan | 08/10/2025 21:35:21 | 08/11/2025 00:41:16 | 08/11/2025 03:35:21 | PLR threshold crossed on TWAMP-1 at 20 sites\R6 | 08/09/2025 22:06:55 | Major | 61611 | TWAMP PLR Threshold Crossed | 08/09/2025 22:06:55 | P3 | 2G | namas | Sceco | 2G_3G_LTE_5G NSA | BLS1M7116-L800-P3,TLT1M7752-G9-L9-NL18-SBTS-P3,YAD1M7099-P2,RYAB1M7618-P2-USF,WDS1M7765-P2-USF,AQQ1M7057-G9-NL8-NL18-SBTS-P3,BDN1M7056-G9-L8-NL18-NL21-SBTS-P3,AQQ1M8157-G9-L8-L18-SBTS,GHM1M7452-G9-NL8-NL18-SBTS-P3,KMBS1M7670-G9-L8-L9-L18-SBTS-P3-WBB-G3-P3,KMBS1M7291-G9-NL8-L9-NL18-NL21-SBTS-P3-WBB-G3,BHAB1M7821-G9-L18-SBTS-P2,MKW1M7030-G9-L18-SBTS-P2,MKW1M7031-G9-L8-L18-L21-SBTS-P3,DBY0025-G9-L8-L18-L21-NR2.6-SBTS-P2,MKW0029-G9-NL8-L18-SBTS-P3,BHAB1M8258-G9-L8-L18-L21-SBTS-P3,BHAB1M8259-G9-L8-L18-L21-SBTS-P3,TNM1M8720-CA-L1800-L800-P3,TBL1M7451-G9-L8-L18-L21-SBTS-P3-WBB-G3 | FLM_TE |  |  | PCM-20250810-00002360 | Confirm if links are restored as rain process has been stopped | Confirm if links are restored as rain process has been stopped |  |  |  | API | 08/10/2025 21:35:21 | 08/11/2025 00:29:29 | 08/11/2025 00:39:33 |  |  | 08/11/2025 00:41:16 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250811000497 | PCM-20250811-00000752 | TT-20250811-00778 | Reference_telecom | Region_6 | BHAB0835 | BHAB0835 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamal Khan Abbas Ali | 08/11/2025 07:43:04 | 08/11/2025 15:07:01 | 08/11/2025 13:43:04 | BCCH MISSING at BHAB0835-P3 ( REF : TT-20250810-01466 ) | 08/10/2025 15:41:35 | Major | 7767 | BCCH MISSING | 08/10/2025 15:41:35 | P3 | 2G | mohail | Sceco | 2G_3G_LTE SA | BHAB0835 | FLM_TE | [8 empty] | API | 08/11/2025 07:43:04 | 08/11/2025 15:05:54 | 08/11/2025 15:06:45 |  |  | 08/11/2025 15:07:01 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250811000502 | PCM-20250811-00000762 | TT-20250811-00781 | Reference_telecom | Region_6 | ABBS2107 | ABBS2107 | Equipment | SFP_BTS | Replace SFP | Fawad Khan | 08/11/2025 07:50:05 | 09/03/2025 13:22:37 | 08/11/2025 13:50:05 | D-CHANNEL FAILURE at site ABBS2107 (Ref:TT-20250810-01466) | 08/10/2025 10:55:54 | Major | 7706 | BTS O&M LINK FAILURE | 08/10/2025 10:55:54 | P3 | 2G | namas | Sceco | 2G_3G_LTE SA | ABBS2107 | FLM_TE | ABBS2107 | Results: DOWN SITE HUB ABBS2107 ABBS2107 Summary: Hub: ABBS2107, Down Count: 1, Down Sites: ABBS2107 Alarm Summary: ABBS2107 No Active Alarm on HUB | [6 empty] | API | 08/11/2025 07:50:05 | 08/11/2025 14:49:48 | 08/12/2025 08:19:46 |  |  | 08/12/2025 08:20:29 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250811000778 | PCM-20250811-00001202 | TT-20250811-01189 | Reference_telecom | Region_6 | BLG0041 | BLG0041 | Transsmission | MW_HW_fault | Replace ODU | Muhammad Ali | 08/11/2025 11:26:38 | 09/04/2025 20:25:07 | 08/11/2025 23:26:38 | DialogFailure observed in BLG0041_01 towards 10.74.124.124 @ Sceco | 08/10/2025 23:26:22 | Minor |  | DialogFailure | 08/10/2025 23:26:04 | P2 | 2G | jizan | Sceco | TX NSA | BLG0041 | FLM_TE | [8 empty] | API | 08/11/2025 11:26:38 | 09/04/2025 19:25:44 | 09/04/2025 20:24:58 |  |  | 09/04/2025 20:25:07 |  | Muhammad Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250811000850 | PCM-20250811-00001286 | TT-20250811-01265 | MW_HC | Region_1 | KBR0330 | KBR0330 |  |  |  | Talha Manzoor | 08/11/2025 11:41:33 | 08/28/2025 13:47:04 | 08/11/2025 23:41:33 | NEC MW HC_P2 Observing Modem Down at KBR0330(10.1.221.218)--KBR6043(10.1.221.219) | 08/11/2025 11:40:16 | Minor |  | LOF | 08/11/2025 11:40:16 | VIP | SRAN | dammam | Sceco | TX NSA | KBR0330(10.1.221.218)--KBR6043(10.1.221.219) | FLM_TE | [8 empty] | API | 08/11/2025 11:41:33 | 08/11/2025 18:57:43 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250811000862 | PCM-20250811-00001300 | TT-20250811-01279 | MW_HC | Region_1 | HFF0031 | HFF0031 | Transsmission | MW_HW_fault | Replace ODU | Mohamed Magdy Fouad Zayed | 08/11/2025 11:41:46 | 09/14/2025 19:00:36 | 08/11/2025 23:41:46 | NEC MW HC_P0 Observing Modem Down at HFF0031(10.1.221.154)--HFF6029(10.1.221.155) | 08/11/2025 11:40:16 | Minor |  | LOF | 08/11/2025 11:40:16 | P1 | SRAN | hafouf | Sceco | TX NSA | HFF0031(10.1.221.154)--HFF6029(10.1.221.155) | FLM_TE | [8 empty] | API | 08/11/2025 11:41:46 | 08/11/2025 12:24:12 | 09/14/2025 19:00:13 |  |  | 09/14/2025 19:00:36 |  | Mohamed Magdy Fouad Zayed | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250811000863 | PCM-20250811-00001301 | TT-20250811-01280 | MW_HC | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 08/11/2025 11:41:47 | 08/28/2025 13:47:01 | 08/11/2025 23:41:47 | NEC MW HC_P0 Observing Performance Issue at DMH0104(10.159.105.139)--DMH0606(10.159.105.141) | 08/11/2025 11:40:16 | Minor |  | LOF | 08/11/2025 11:40:16 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104(10.159.105.139)--DMH0606(10.159.105.141) | FLM_TE | [8 empty] | API | 08/11/2025 11:41:47 | 08/11/2025 12:20:45 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250811000956 | PCM-20250811-00001447 | TT-20250811-01415 | MW_HC | Region_6 | BLG0041 | BLG0041 | Transsmission | MW_HW_stuck | Reset ODU | Muhammad Ali | 08/11/2025 12:30:52 | 09/04/2025 20:25:47 | 08/12/2025 00:30:52 | Nokia MW HC_P1 Observing Performance Issue at BLG0041_01-SBBG0045_02 | 08/11/2025 12:30:10 | Minor |  | LOF | 08/11/2025 12:30:10 | P2 | 2G | jizan | Sceco | TX NSA | BLG0041_01-SBBG0045_02 | FLM_TE | [8 empty] | API | 08/11/2025 12:30:52 | 09/04/2025 19:25:43 | 09/04/2025 20:25:37 |  |  | 09/04/2025 20:25:47 |  | Muhammad Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250811001581 | PCM-20250811-00002243 | TT-20250811-02243 | Reference_telecom | Region_1 | YBR0725 | YBR0725 |  |  |  | Mohamed Magdy Fouad Zayed | 08/11/2025 15:49:16 | 08/20/2025 11:35:50 | 08/12/2025 03:49:16 | MW RTN Observing SLAVE_BAD,COMMUN_FAIL at YBR0725_NE_2_N | 11/12/2024 15:08:31 | Minor |  | LOF | 11/12/2024 15:08:31 | P2 | SRAN | hafouf | Power Cube | TX NSA | YBR0725_NE_2_N | FLM_TE | [8 empty] | API | 08/11/2025 15:49:16 | 08/11/2025 16:30:11 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250811001785 | PCM-20250811-00002558 | TT-20250811-02547 | Reference_telecom | Region_2 | RIY2112 | RIY2112 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 08/11/2025 17:02:32 | 10/21/2025 07:50:15 | 08/12/2025 05:02:32 | Nokia Eband Observing DemFail-Channel 1A,DemFail-Channel 1B,LinkDown-Cha at RIY2112-10.89.249.106 | 05/12/2024 14:19:03 | Minor |  | LOF | 05/12/2024 14:19:03 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY2112-10.89.249.106 | FLM_TE | [8 empty] | API | 08/11/2025 17:02:32 | 09/02/2025 08:22:17 | 10/21/2025 07:49:50 |  |  | 10/21/2025 07:50:15 |  | Mubashar Farooq Abdul Majeed | Relocation_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250811001796 | PCM-20250811-00002568 | TT-20250811-02557 | Reference_telecom | Region_2 | RYD0946 | RYD0946 |  |  |  | Touseef Iqbal Mazhar Iqbal | 08/11/2025 17:02:43 | 09/01/2025 11:09:36 | 08/12/2025 05:02:43 | Nokia Eband Observing DemFail-Port 1/1 at RYD0946-10.3.127.138 | 06/06/2025 18:08:22 | Minor |  | LOF | 06/06/2025 18:08:22 | P2 | SRAN | rumah | Sceco | TX NSA | RYD0946-10.3.127.138 | FLM_TE | [8 empty] | API | 08/11/2025 17:02:43 | 08/11/2025 18:33:04 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250812000154 | PCM-20250812-00000273 | TT-20250812-00295 | Reference_EM | Region_1 | DMAP2U6160 | DMAP6060 | Enviroment | Air Condition | Change Fan | Ahmed Abdelfattah Ali Soltan | 08/12/2025 03:05:56 | 10/03/2025 01:55:58 | 08/12/2025 09:05:56 | Air-condition #2 failure alarm at DMAP2U6160-P1-VIP @ Sceco | 08/12/2025 02:55:35 | Major | 65105 | Air-condition #2 failure alarm | 08/12/2025 02:55:28 | VIP | 2G | dammam | Sceco | 2G NSA | DMAP2U6160 | FLM_EM | [8 empty] | API | 08/12/2025 03:05:56 | 08/12/2025 08:35:33 | 10/03/2025 01:55:50 |  |  | 10/03/2025 01:55:58 |  | Ahmed Abdelfattah Ali Soltan | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250812000158 | PCM-20250812-00000278 | TT-20250812-00298 | EM | Region_4 | JED1U6740 | JED6040 |  |  |  | Ahmed Gamal Mohamed Farag | 08/12/2025 03:09:33 | 09/17/2025 12:29:02 | 08/12/2025 15:09:33 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at JED1U6740-G9-L18-SBTS-P3 @ Sceco | 08/12/2025 03:01:14 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 08/12/2025 03:01:08 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6740 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 08/12/2025 03:09:33 | 09/17/2025 12:29:02 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250812000194 | PCM-20250812-00000327 | TT-20250812-00344 | Reference_EM | Region_5 | YAQ0345 | YAQ0345 |  |  |  | SAID AHMED HASSAN ABDALLA | 08/12/2025 03:47:31 | 10/01/2025 09:24:08 | 08/12/2025 09:47:31 | 1(2G/LTE) Site down under YAQ0345-P3 (ref. TT-20250802-00189) | 08/03/2025 01:01:12 | Major | 7706 | BTS O&M LINK FAILURE | 08/03/2025 01:01:12 | P2 | 2G | makkah | Sceco_STB | 2G_LTE SA | YAQ0345-P3 | FLM_EM | YAQ0345 | Results: DOWN SITE HUB YAQ0345-P3 YAQ0345 Summary: Hub: YAQ0345, Down Count: 1, Down Sites: YAQ0345-P3 Alarm Summary: YAQ0345 No Active Alarm on HUB |  |  |  |  | site down |  | API | 08/12/2025 03:47:31 | 10/01/2025 09:24:08 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250812000305 | PCM-20250812-00000497 | TT-20250812-00490 | Telecom | Region_4 | JED1MN0760 | JED0760 | Equipment | SFP_BTS | Clean SFP | Mohammed Altaf Naveed AbdulHakeem | 08/12/2025 06:02:52 | 09/17/2025 21:06:41 | 08/12/2025 12:02:52 | PT:: FLM Need to perform HC at JED1MN0760 under R4. | 08/12/2025 05:44:25 | Major | 676767671 | Health Check-WO to TE FME | 08/12/2025 05:44:25 | P2 | 5G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED1MN0760 | FLM_TE |  | Approved | PCM-20250812-00000493 | Approved | Approved |  |  |  | API | 08/12/2025 06:02:52 | 08/12/2025 08:05:28 | 09/17/2025 21:06:35 |  |  | 09/17/2025 21:06:41 |  | Mohammed Altaf Naveed AbdulHakeem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250812000323 | PCM-20250812-00000520 | TT-20250812-00541 | Telecom | Region_2 | RIY0453-ZRi04-3-CSG-04 | RIY0453 | Equipment | SFP_BTS | Clean SFP | Muhammad Naeem Muhammad Gulzar | 08/12/2025 06:14:12 | 10/12/2025 12:10:01 | 08/12/2025 10:14:12 | Physical Port Down at RIY0453-ZRi04-3-CSG-04 @ Generator_SG | 08/12/2025 06:11:36 | Critical | 101-2505274 | Physical Port Down | 08/12/2025 06:11:12 | VIP | IPRAN | riyadh | Generator_SG | IPRAN SA | RIY0453-ZRi04-3-CSG-04 | FLM_TE | [8 empty] | API | 08/12/2025 06:14:12 | 08/12/2025 08:22:29 | 10/12/2025 12:09:49 |  |  | 10/12/2025 12:10:01 |  | Muhammad Naeem Muhammad Gulzar | STC |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250812000390 | PCM-20250812-00000617 | TT-20250812-00641 | Telecom | Region_6 | MHL0720 | MHL0720 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamal Khan Abbas Ali | 08/12/2025 07:27:48 | 08/12/2025 10:32:37 | 08/12/2025 13:27:48 | BCCH MISSING down at site MHL0720-P3 | 08/12/2025 07:16:38 | Major | 7706 | BTS O&M LINK FAILURE | 08/12/2025 07:16:38 | P3 | 2G | mohail | Sceco | 2G_3G_LTE SA | MHL0720 | FLM_TE | MHL0720 | Results: DOWN SITE HUB MHL0720 MHL0720 Summary: Hub: MHL0720, Down Count: 1, Down Sites: MHL0720 Alarm Summary: MHL0720 No Active Alarm on HUB | [6 empty] | API | 08/12/2025 07:27:48 | 08/12/2025 10:31:57 | 08/12/2025 10:32:24 |  |  | 08/12/2025 10:32:37 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250812001372 | PCM-20250812-00002050 | TT-20250812-02007 | Reference_telecom | Region_6 | RTH9007 | RTH9007 | Transsmission | MW_HW_stuck | Reset IDU | Muhammad Ali | 08/12/2025 16:46:39 | 10/05/2025 14:20:30 | 08/13/2025 04:46:39 | NEC MW Observing Communication FAIL at RTH9007-2(10.157.248.68) | 07/20/2025 13:18:59 | Minor |  | LOF | 07/20/2025 13:18:59 | P1 | Repeater | raith | Sceco_STB | TX NSA | RTH9007-2(10.157.248.68) | FLM_TE | [8 empty] | API | 08/12/2025 16:46:39 | 09/30/2025 11:52:07 | 10/05/2025 14:20:21 |  |  | 10/05/2025 14:20:30 |  | Muhammad Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250812001893 | PCM-20250812-00002878 | TT-20250812-02737 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 08/12/2025 22:01:48 | 08/17/2025 03:35:06 | 08/13/2025 04:01:48 | Observing multiple ALU CIDs down B/W MAK - KMS | 08/12/2025 21:58:34 | Major | 5000003 | Link Down | 08/12/2025 21:58:34 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE | [5 empty] | Observing multiple ALU CIDs down B/W MAK - KMS |  |  | API | 08/12/2025 22:01:48 | 08/17/2025 03:35:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250813000190 | PCM-20250813-00000300 | TT-20250813-00286 | EM | Region_4 | JED1U6760 | JED6060 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 08/13/2025 02:40:33 | 09/06/2025 13:35:21 | 08/13/2025 14:40:33 | AIRCON 2 FAILURE at JED1U6760-G9-L18-SBTS-P3 @ Sceco | 08/13/2025 02:32:31 | Minor | 7103 | AIRCON 2 FAILURE | 08/13/2025 02:32:22 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6760 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/13/2025 02:40:33 | 08/13/2025 13:05:30 | [6 empty] | ZAIN O-M |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250813000192 | PCM-20250813-00000303 | TT-20250813-00288 | EM | Region_4 | JED1U6829 | JED6129 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 08/13/2025 02:41:04 | 08/31/2025 11:51:33 | 08/13/2025 14:41:04 | AIRCON 1 FAILURE at JED1U6829-G9-L18-L21-SBTS-P3 @ Sceco | 08/13/2025 02:33:26 | Minor | 7103 | AIRCON 1 FAILURE | 08/13/2025 02:32:55 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6829 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/13/2025 02:41:04 | 08/13/2025 13:05:31 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250813000443 | PCM-20250813-00000711 | TT-20250813-00695 | EM | Region_3 | RSP0036 | RSP0036 |  |  |  | Sayed Satoor | 08/13/2025 07:59:51 | 09/04/2025 04:09:12 | 08/13/2025 13:59:51 | Door opening alarm at RSP0036-P1-VIP_SRAN @ Generator_SG | 08/13/2025 07:59:19 | Major | 65101 | Door opening alarm | 08/13/2025 07:59:15 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0036 | FLM_EM | [8 empty] | API | 08/13/2025 07:59:51 | 08/13/2025 19:33:04 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250813000955 | PCM-20250813-00001491 | TT-20250813-01504 | EM | Region_3 | RSP0037 | RSP0037 |  |  |  | Sayed Satoor | 08/13/2025 14:04:34 | 09/03/2025 17:49:48 | 08/14/2025 02:04:34 | NETECO: Rectifier Power Failure at RSP0037 @ Generator_SG | 08/13/2025 13:58:14 | Minor | 1607 | Rectifier Power Failure | 08/13/2025 13:58:14 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0037 | FLM_EM | [8 empty] | API | 08/13/2025 14:04:34 | 08/13/2025 19:33:08 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250813001285 | PCM-20250813-00001951 | TT-20250813-01940 | Reference_telecom | Region_2 | RIY2496 | RIY2496 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Farmanullah Akbar Jan | 08/13/2025 16:45:49 | 09/29/2025 12:07:08 | 08/14/2025 04:45:49 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RIY2496_NE_3_SDB | 08/11/2025 16:03:22 | Minor |  | LOF | 08/11/2025 16:03:22 | P3 | SRAN | riyadh | Sceco | TX NSA | RIY2496_NE_3_SDB | FLM_TE | [8 empty] | API | 08/13/2025 16:45:49 | 09/29/2025 12:07:08 | [5 empty] | Farmanullah Akbar Jan | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250813001471 | PCM-20250813-00002196 | TT-20250813-02182 | Telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 08/13/2025 18:32:41 | 09/24/2025 17:18:26 | 08/14/2025 06:32:41 | JED1W6081 Partial Down | 08/13/2025 18:28:41 | Minor | 613007 | Wi-Fi AP Out Of Service | 08/13/2025 18:28:41 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081 | FLM_TE | [8 empty] | API | 08/13/2025 18:32:41 | 08/14/2025 10:39:01 | 09/24/2025 17:18:17 |  |  | 09/24/2025 17:18:26 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250814000594 | PCM-20250814-00000956 | TT-20250814-01064 | Telecom | Region_4 | JED1M8059 | JED2059 |  |  |  | Ahmed Adel Abdelaziz elkholy | 08/14/2025 10:18:57 | 08/14/2025 10:45:55 | 08/14/2025 16:18:57 | PT::FLM need to check FSP subunit lost at JED1M8059-L800-CA-P3-SBTS (Bo request) | 08/14/2025 10:18:46 | Major | 7604 | BASE STATION OPERATION DEGRADED | 08/14/2025 10:18:46 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1M8059-L800-CA-P3-SBTS | FLM_TE | [8 empty] | API | 08/14/2025 10:18:57 | 08/14/2025 10:45:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250814000927 | PCM-20250814-00001431 | TT-20250814-00833 | Telecom | Region_2 | RY1-R1-0212-LL-CSG-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 08/14/2025 13:34:45 | 09/07/2025 14:13:52 | 08/14/2025 19:34:45 | MW Link Down at RY1-R1-0212-LL-CSG-01 @ Sceco | 08/13/2025 23:43:37 | Major | 101-1102218 | Alarm of failed LAG negotiation | 08/13/2025 23:43:30 | P1 | IPRAN | riyadh | Sceco | IPRAN SA | RY1-R1-0212-LL-CSG-01 | FLM_TE |  | It is a new link still under RO as NNN suffix. kindly check with IPRAN. | PCM-20250814-00001355 | It is a new link still under RO as NNN suffix. kindly check with IPRAN. | It is a new link still under RO as NNN suffix. kindly check with IPRAN. |  |  |  | API | 08/14/2025 13:34:45 | [7 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250814001596 | PCM-20250814-00002440 | TT-20250814-02315 | Reference_telecom | Region_2 | RYQ0965 | RYQ0965 | Equipment | BTS_Cable | Reconnect GPS Cable | Muhammad Tahir Abdulrazzaq | 08/14/2025 18:57:12 | 10/12/2025 10:37:21 | 08/15/2025 06:57:12 | External Clock Reference Problem at RYQ0965-P2_SRAN @ Generator_SG | 08/14/2025 15:33:05 | Minor | 26262 | External Clock Reference Problem | 08/14/2025 15:25:53 | P2 | SRAN | majma | Generator_SG | 2G NSA | RYQ0965 | FLM_TE |  |  | PCM-20250814-00002405 | PM Errors and RSL degradation observed on MW link MJM0490-MJM0488 FLM Team please perform health check for the suspected MW link | PM Errors and RSL degradation observed on MW link MJM0490-MJM0488 FLM Team please perform health check for the suspected MW link |  |  |  | API | 08/14/2025 18:57:12 | 08/15/2025 17:36:06 | 10/12/2025 10:36:33 |  |  | 10/12/2025 10:37:21 |  | Muhammad Tahir Abdulrazzaq | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20250814001803 | PCM-20250814-00002748 | TT-20250814-02697 | Reference_telecom | Region_4 | TF1-ASG-02 | TF1 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 08/14/2025 21:44:16 | 08/17/2025 08:50:16 | 08/15/2025 09:44:16 | Optical Invalid at TF1-ASG-02 ¦¦ ref TT-20250605-02098 @ Sceco_STB | 08/13/2025 19:40:43 | Minor | 101-2505224 | Optical Invalid | 08/13/2025 19:40:25 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | TF1-ASG-02 | FLM_TE | [8 empty] | API | 08/14/2025 21:44:16 | 08/15/2025 20:17:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250815000189 | PCM-20250815-00000305 | TT-20250815-00119 | Reference_EM | Region_5 | ASF0727 | ASF0727 | Transsmission | SFP_Transmission | Replace SFP | Zakir Hossan | 08/15/2025 05:20:20 | 09/18/2025 21:44:25 | 08/15/2025 11:20:20 | 1(2G/3G/LTE) Site down under ASF0727-P2-USF(REF: TT-20250814-02415) | 08/15/2025 01:05:20 | Major | 7706 | BTS O&M LINK FAILURE | 08/15/2025 01:05:20 | P2 | 2G | makkah | Generator_SG | 2G_3G_LTE SA | ASF0727 | FLM_TE | ASF0727 | Results: DOWN SITE HUB ASF0727 ASF0727 Summary: Hub: ASF0727, Down Count: 1, Down Sites: ASF0727 Alarm Summary: ASF0727 No Active Alarm on HUB | PCM-20250815-00000123 | TE issue | TE issue |  | site down |  | API | 08/15/2025 05:20:20 | 09/01/2025 11:12:45 | 09/18/2025 21:43:57 |  |  | 09/18/2025 21:44:25 |  | Zakir Hossan | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250816000150 | PCM-20250816-00000237 | TT-20250816-00249 | Reference_telecom | Region_4 | SJED0664 | SJED0664 |  |  |  | Ahmed Adel Abdelaziz elkholy | 08/16/2025 04:06:06 | 08/18/2025 09:42:54 | 08/16/2025 10:06:06 | 3(LTE) sites down under SJED0664-CA-P3,SJED0666-CA-P3,SJED0665-CA-P3(Ref:TT-20250814-01613) | 08/14/2025 14:18:23 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 08/14/2025 14:18:23 | P3 | SRAN | jeddah | Sceco | LTE SA | SJED1S7665-CA-P3 SJED1S7666-CA-P3 SJED1S7664-CA-P3 | FLM_EM | SJED0664 | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20250816-00000232 | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 08/16/2025 04:06:06 | 08/18/2025 09:42:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Reject_FME | CM20250816000620 | PCM-20250816-00000960 | TT-20250816-00958 | Telecom | Region_4 | QUZ1MN0739 | QUZ0739 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 08/16/2025 12:27:51 | 08/24/2025 08:48:10 | 08/16/2025 18:27:51 | PT::FLM need to perform HC at QUZ1MN0739 (BO request) | 08/16/2025 12:27:40 | Major | 676767671 | Health Check-WO to TE FME | 08/16/2025 12:27:40 | P3 | 5G | alaith | Sceco | 2G_3G_LTE_5G NSA | QUZ1MN0739 | FLM_TE | [8 empty] | API | 08/16/2025 12:27:51 | 08/16/2025 13:08:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250816000758 | PCM-20250816-00001143 | TT-20250816-01130 | Reference_telecom | Region_2 | RIY2928 | RIY2928 | Enviroment | SCECO_Failure | SCECO auto restored | Farmanullah Akbar Jan | 08/16/2025 14:04:14 | 09/27/2025 01:10:06 | 08/16/2025 18:04:14 | 1(2G) 3(LTE) sites down under RIY2928-P1-VIP 2G_LTE,RIY2973-CA-L800-P3 LTE,RIY2638-CA-L800-P3 LTE/R2_RY2_HWBSC01 @ Sceco(ref:TT-20250816-00843) | 08/16/2025 13:45:10 | Critical | 301 | NE Is Disconnected | 08/16/2025 13:45:10 | P1 | SRAN | riyadh | Sceco | 2G_LTE SA | RIY2928-P1-VIP 2G_LTE RIY2973-CA-L800-P3 LTE RIY2638-CA-L800-P3 LTE | FLM_TE | RIY2928 | Results: DOWN SITE HUB RIY2928-P1-VIP RIY2928 RIY2973-CA-L800-P3 RIY2638 RIY2638-CA-L800-P3 RIY2638 Summary: Hub: RIY2928, Down Count: 1, Down Sites: RIY2928-P1-VIP Hub: RIY2638, Down Count: 2, Down Sites: RIY2973-CA-L800-P3, RIY2638-CA-L800-P3 Alarm Summary: RIY2928 Alarm Active on HUB RIY2638 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 08/16/2025 14:04:14 | 08/16/2025 14:46:19 | 09/27/2025 01:09:31 |  |  | 09/27/2025 01:10:06 |  | Farmanullah Akbar Jan | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250817000638 | PCM-20250817-00001036 | TT-20250817-00953 | Telecom | Region_2 | RYQS2573 | RYQS2573 |  |  |  | Azmat Ali Madad | 08/17/2025 10:41:52 | 09/07/2025 14:13:53 | 08/17/2025 22:41:52 | MW_LOF at RYQS2573_NE_13 @ Generator_DG | 08/17/2025 10:39:58 | Minor | 1-631 | MW_LOF | 04/30/2025 20:37:26 | P1 | SRAN | riyadh | Generator_DG | TX NSA | RYQS2573 | FLM_TE | [8 empty] | API | 08/17/2025 10:41:52 | 08/18/2025 19:16:52 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250817000714 | PCM-20250817-00001141 | TT-20250817-01060 | Reference_telecom | Region_5 | MAK0552 | MAK0552 |  |  |  | Sohail Ashraf Muhammad Ashraf | 08/17/2025 11:34:00 | 08/31/2025 11:51:51 | 08/17/2025 17:34:00 | BASE STATION SERVICE PROBLEM(No connection to unit) at MAK0552-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2-USF (ref. TT-20250813-01793) | 08/14/2025 05:03:33 | Major | 7116 | BASE STATION SERVICE PROBLEM | 08/14/2025 05:03:33 | P2 | 2G | makkah | Sceco | LTE SA | MAK0552-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2-USF | FLM_TE | [8 empty] | API | 08/17/2025 11:34:00 | 08/17/2025 22:35:51 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250817000722 | PCM-20250817-00001152 | TT-20250817-01071 | Reference_telecom | Region_4 | TAF0175 | TAF0175 | Enviroment | Rectifier Module | Change rectifer module | Rashid Shafique | 08/17/2025 11:43:05 | 08/19/2025 11:50:23 | 08/17/2025 17:43:05 | BASE STATION SERVICE PROBLEM(RSSI difference between main and diversity paths exceed the threshold) at TAF0175-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1 (ref. TT-20250816-00483) | 08/16/2025 22:35:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 08/16/2025 22:35:27 | P1 | 2G | taif | Sceco | LTE SA | TAF0175-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1 | FLM_TE | [8 empty] | API | 08/17/2025 11:43:05 | 08/17/2025 11:58:14 | 08/19/2025 11:50:16 |  |  | 08/19/2025 11:50:23 |  | Rashid Shafique |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250817000772 | PCM-20250817-00001229 | TT-20250817-01142 | Telecom | Region_1 | HFF0031 | HFF0031 | Transsmission | MW_HW_fault | Replace ODU | Mohamed Magdy Fouad Zayed | 08/17/2025 12:18:27 | 09/14/2025 18:59:50 | 08/18/2025 00:18:27 | ODU CPU / Cable Open at HFF0031 on 10.1.221.154 @ Sceco | 08/17/2025 12:15:57 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 08/17/2025 12:17:10 | P1 | SRAN | hafouf | Sceco | TX NSA | HFF0031 | FLM_TE | [8 empty] | API | 08/17/2025 12:18:27 | 08/17/2025 19:47:43 | 09/14/2025 18:59:43 |  |  | 09/14/2025 18:59:50 |  | Mohamed Magdy Fouad Zayed | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250817000774 | PCM-20250817-00001231 | TT-20250811-01264 | MW_HC | Region_1 | KBR6021 | KBR6021 | Transsmission | MW_HW_fault | Replace ODU | Meraj Husain Idd Baksh | 08/17/2025 12:19:50 | 08/28/2025 13:47:09 | 08/18/2025 00:19:50 | NEC MW HC_P0 Observing Modem Down at KBR6021(10.154.12.57)--KBR6090(10.154.12.56) | 08/11/2025 11:40:16 | Minor |  | LOF | 08/11/2025 11:40:16 | P3 | SRAN | dammam | Sceco | TX NSA | KBR6021(10.154.12.57)--KBR6090(10.154.12.56) | FLM_TE |  | Link still count errors | PCM-20250817-00001177 | Link still count errors | Link still count errors |  |  |  | API | 08/17/2025 12:19:50 | 08/28/2025 13:16:17 | [5 empty] | Meraj Husain Idd Baksh | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250817001358 | PCM-20250817-00002047 | TT-20250817-01945 | Reference_telecom | Region_1 | DMAP2153 | DMAP2153 |  |  |  | Meraj Husain Idd Baksh | 08/17/2025 18:08:41 | 08/28/2025 13:47:06 | 08/18/2025 06:08:41 | MW RTN Observing HARD_BAD at DMAP2153_NE_1_V | 08/04/2025 14:06:06 | Minor |  | LOF | 08/04/2025 14:06:06 | P2 | SRAN | dammam | Sceco | TX NSA | DMAP2153_NE_1_V | FLM_TE | [8 empty] | API | 08/17/2025 18:08:41 | 08/17/2025 18:41:33 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250817001639 | PCM-20250817-00002439 | TT-20250817-01946 | Reference_telecom | Region_1 | DRN0129 | DRN0129 |  |  |  | Imran Ali Yousaf | 08/17/2025 21:28:30 | 09/08/2025 11:45:14 | 08/18/2025 09:28:30 | MW RTN Observing COMMUN_FAIL at DRN0129_NE_29_SDB | 08/15/2025 20:10:38 | Minor |  | LOF | 08/15/2025 20:10:38 | P1 | SRAN | dammam | Sceco | TX NSA | DRN0129_NE_29_SDB | FLM_TE |  |  | PCM-20250817-00002340 | Need to check hardware locally | Need to check hardware locally |  |  |  | API | 08/17/2025 21:28:30 | 08/17/2025 23:13:47 | [6 empty] | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250818000037 | PCM-20250818-00000056 | TT-20250818-00028 | Reference_telecom | Region_4 | JED0063 | JED0063 | Equipment | BSS_HW_fault | Replace Controller Card | Mohammed Ramadan A Abu Abid | 08/18/2025 00:41:49 | 08/18/2025 12:50:37 | 08/18/2025 06:41:49 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0063-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 (Ref::TT-20250817-02213) | 08/17/2025 19:42:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 08/17/2025 19:42:37 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE SA | JED0063-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE |  |  | PCM-20250818-00000023 | Approved. | Approved. |  |  |  | API | 08/18/2025 00:41:49 | 08/18/2025 11:07:21 | 08/18/2025 11:08:00 | 08/18/2025 11:14:11 | 08/18/2025 11:24:56 | 08/18/2025 12:50:37 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250818000050 | PCM-20250818-00000081 | TT-20250817-02170 | Reference_telecom | Region_6 | MKW0035 | MKW0035 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | SHAH KHALID | 08/18/2025 00:58:41 | 08/18/2025 02:51:22 | 08/18/2025 06:58:41 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at MKW1M7035-G9-NL8-NL18-NL21-SBTS-P3 (Ref:TT-20250806-02357) | 08/14/2025 01:49:09 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 08/14/2025 01:49:09 | P3 | 2G | makhwa | Sceco | LTE SA | MKW0035 | FLM_TE |  |  | PCM-20250817-00002665 | TX path clear from our side | TX path clear from our side |  |  |  | API | 08/18/2025 00:58:41 | 08/18/2025 02:50:35 | 08/18/2025 02:51:02 |  |  | 08/18/2025 02:51:22 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250818000066 | PCM-20250818-00000105 | TT-20250818-00113 | Reference_telecom | Region_6 | BHAB0824 | BHAB0824 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Manzoor Ahmed | 08/18/2025 01:26:19 | 10/09/2025 16:26:14 | 08/18/2025 13:26:19 | InternalCommunicationProblem observed in BHAB0824_01 towards 10.221.243.2 @ Sceco | 08/17/2025 13:26:41 | Minor |  | InternalCommunicationProblem | 08/17/2025 13:25:45 | P2 | 2G | makhwa | Sceco | TX NSA | BHAB0824 | FLM_TE | [8 empty] | API | 08/18/2025 01:26:19 | 10/09/2025 16:25:40 | 10/09/2025 16:26:04 |  |  | 10/09/2025 16:26:14 |  | Manzoor Ahmed | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250818000081 | PCM-20250818-00000127 | TT-20250818-00107 | Reference_telecom | Region_2 | SRIY2S7069 | SRIY0069 |  |  |  | Azmat Ali Madad | 08/18/2025 01:40:29 | 09/01/2025 11:09:38 | 08/18/2025 13:40:29 | External Clock Reference Problem at SRIY2S7069-P3 @ Sceco | 08/17/2025 22:25:37 | Minor | 26262 | External Clock Reference Problem | 08/17/2025 22:22:14 | P3 | 4G | riyadh | Sceco | 2G NSA | SRIY2S7069 | FLM_TE |  |  | PCM-20250818-00000099 | need to check GNSS | need to check GNSS |  |  |  | API | 08/18/2025 01:40:29 | 08/18/2025 19:16:53 | [6 empty] | SCECO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250818000815 | PCM-20250818-00001336 | TT-20250818-01385 | Reference_telecom | Region_6 | ULY0106 | ULY0106 |  |  |  | Saddam Hussain Shah Nawaz Khan | 08/18/2025 13:41:00 | 10/09/2025 14:32:23 | 08/19/2025 01:41:00 | Degrade observed in ULY0106_2 towards 10.221.240.35 @ Sceco_STB | 08/18/2025 01:41:30 | Minor |  | Degrade | 08/18/2025 01:40:41 | P1 | 2G | bisha | Sceco_STB | TX NSA | ULY0106 | FLM_TE | [8 empty] | API | 08/18/2025 13:41:00 | 08/18/2025 15:00:39 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250818001061 | PCM-20250818-00001716 | TT-20250818-01747 | Telecom | Region_1 | KKM2168 | KKM2168 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 08/18/2025 16:15:14 | 09/16/2025 19:14:07 | 08/19/2025 04:15:14 | Health check for KKM2168 | 08/18/2025 16:14:06 | Minor | 676767672 | Health Check-WO to TE FME | 08/18/2025 16:14:06 | P3 | SRAN | hafr | Sceco | 2G NSA | KKM2168 | FLM_TE | [8 empty] | API | 08/18/2025 16:15:14 | 08/18/2025 16:19:09 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250818001198 | PCM-20250818-00001899 | TT-20250818-01926 | Reference_telecom | Region_6 | DMD0325 | DMD0325 |  |  |  | Khurram Nawaz Muhammad Akram | 08/18/2025 17:30:20 | 09/01/2025 14:51:07 | 08/18/2025 23:30:20 | BCCH MISSING at DMD0325-P3 (Ref:TT-20250818-01459) | 08/18/2025 14:10:11 | Major | 7767 | BCCH MISSING | 08/18/2025 14:10:11 | P3 | 2G | jizan | Generator_SG | 2G SA | DMD0325-P3 | FLM_TE | [8 empty] | API | 08/18/2025 17:30:20 | 08/18/2025 22:37:07 | 09/01/2025 14:51:07 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250818001271 | PCM-20250818-00001998 | TT-20250818-00428 | Telecom | Region_4 | JED1M7728 | JED0728 |  |  |  | Nazeer Mohammed | 08/18/2025 18:15:20 | 08/19/2025 11:04:51 | 08/19/2025 00:15:20 | BASE STATION OPERATION DEGRADED (Reference clock missing in startup) at JED1M7728-CA-L900 @ Sceco | 08/18/2025 04:22:08 | Major | 7651 | BASE STATION OPERATION DEGRADED | 08/18/2025 04:21:57 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7728 | FLM_TE |  |  | PCM-20250818-00001715 | Dear FLM, Thanks to rectify JED0338-JDMD0859 | Dear FLM, Thanks to rectify JED0338-JDMD0859 |  |  |  | API | 08/18/2025 18:15:20 | 08/19/2025 11:04:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250819000374 | PCM-20250819-00000673 | TT-20250819-00704 | Reference_telecom | Region_2 | RIYA6097 | RIYA6097 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ali Raza Abdi Syed Muhammad Taqi Abdi | 08/19/2025 06:35:45 | 08/26/2025 12:00:15 | 08/19/2025 10:35:45 | 1(LTE) sites down under RIYA6097-P1-VIP_SRAN LTE/R2_RY1_HWBSC01 @ Sceco(REF:TT-20250819-00558) | 08/19/2025 05:10:04 | Critical | 301 | NE Is Disconnected | 08/19/2025 05:10:04 | VIP | SRAN | riyadh | Sceco | LTE SA | RIYA6097 | FLM_TE | RIYA6097 | Results: DOWN SITE HUB RIYA6097 RIYA6097 Summary: Hub: RIYA6097, Down Count: 1, Down Sites: RIYA6097 Alarm Summary: RIYA6097 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 08/19/2025 06:35:45 | 08/26/2025 12:00:15 | [5 empty] | Ali Raza Abdi Syed Muhammad Taqi Abdi | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250819000524 | PCM-20250819-00000897 | TT-20250819-00914 | EM | Region_2 | AFL9024 | AFL9024 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Danish Ahsan Ahsan Ullah | 08/19/2025 08:45:02 | 08/29/2025 23:40:03 | 08/19/2025 12:45:02 | RELAY_ALARM_CRITICAL at AfL9024_NE_1 | 08/17/2025 08:32:15 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 08/19/2025 08:36:58 | P3 | Repeater | aflaj | Sceco | TX NSA | AfL9024_NE_1 | FLM_EM | [5 empty] | RELAY_ALARM_CRITICAL at AfL9024_NE_1 |  |  | API | 08/19/2025 08:45:02 | 08/19/2025 09:30:51 | 08/29/2025 23:39:58 |  |  | 08/29/2025 23:40:03 |  | Danish Ahsan Ahsan Ullah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250819000684 | PCM-20250819-00001150 | TT-20250819-01132 | EM | Region_3 | MDN2188 | MDN2188 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 08/19/2025 10:56:37 | 09/03/2025 18:10:50 | 08/19/2025 22:56:37 | NETECO: Communication Fail at MDN2188 @ Generator_SG | 08/19/2025 10:50:27 | Minor | 20001 | Communication Fail | 08/19/2025 10:50:27 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDN2188 | FLM_EM | [8 empty] | API | 08/19/2025 10:56:37 | 08/21/2025 17:49:23 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250819000810 | PCM-20250819-00001336 | TT-20250819-01296 | Reference_EM | Region_4 | JED0410 | JED0410 | Equipment | SW | Issue was solved after softaware configuration | Bilal hassan shaukat ali | 08/19/2025 12:25:52 | 09/08/2025 04:34:43 | 08/19/2025 16:25:52 | 1(2G/LTE) sites down under JED0410-P1-HUB @ Sceco (Ref.:: TT-20250819-00903) | 08/19/2025 08:39:22 | Critical | 7706 | BTS O&M LINK FAILURE | 08/19/2025 08:39:22 | P1 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0410-P1-HUB | FLM_TE | JED0410 | Results: DOWN SITE HUB JED0410-P1-HUB JED0410 Summary: Hub: JED0410, Down Count: 1, Down Sites: JED0410-P1-HUB Alarm Summary: JED0410 No Active Alarm on HUB | PCM-20250819-00001332 | FLM need to check and restore the site. | FLM need to check and restore the site. |  | sites down |  | API | 08/19/2025 12:25:52 | 09/06/2025 03:53:09 | 09/08/2025 04:34:25 |  |  | 09/08/2025 04:34:43 |  | Bilal hassan shaukat ali | NSN_Care |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250819000882 | PCM-20250819-00001454 | TT-20250819-01426 | Telecom | Region_1 | ARR6002 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 08/19/2025 13:39:52 | 08/25/2025 10:23:12 | 08/20/2025 01:39:52 | RF Unit Maintenance Link Failure at ARR6002-P3_SRAN @ Sceco | 08/19/2025 13:36:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 08/19/2025 13:34:19 | P3 | SRAN | arar | Sceco | 2G NSA | ARR6002 | FLM_TE | [8 empty] | API | 08/19/2025 13:39:52 | 08/23/2025 15:35:22 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250819000885 | PCM-20250819-00001458 | TT-20250819-01430 | Telecom | Region_1 | ARR6002 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 08/19/2025 13:41:26 | 08/25/2025 10:23:12 | 08/19/2025 19:41:26 | BBU CPRI Interface Error at ARR6002-P3_SRAN @ Sceco | 08/19/2025 13:36:49 | Major | 26234 | BBU CPRI Interface Error | 08/19/2025 13:34:14 | P3 | SRAN | arar | Sceco | 2G NSA | ARR6002 | FLM_TE | [8 empty] | API | 08/19/2025 13:41:26 | 08/23/2025 15:35:43 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250819000886 | PCM-20250819-00001461 | TT-20250819-01432 | Telecom | Region_1 | JBRK0914 | JBRK0914 |  |  |  | Mohamed Abdelaziz | 08/19/2025 13:41:55 | 08/28/2025 13:47:11 | 08/20/2025 01:41:55 | ODU CPU / Cable Open at JBRK0914 on 10.76.113.211 @ Sceco | 08/19/2025 13:40:56 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 08/19/2025 13:40:02 | P2 | SRAN | jubail | Sceco | TX NSA | JBRK0914 | FLM_TE | [8 empty] | API | 08/19/2025 13:41:55 | 08/19/2025 18:47:26 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250820000023 | PCM-20250820-00000040 | TT-20250819-02717 | Telecom | Region_4 | QUN0335 | QUN0335 | Transsmission | MW_LOW_RSL | Link Alignment Issue | Mudassar Bashir Bashir Ahmad | 08/20/2025 00:35:13 | 08/24/2025 09:42:22 | 08/20/2025 06:35:13 | PT:: BO_TRM Need to perform HC at QUN0335 under R4 (BO_BSS Request) | 08/19/2025 21:58:49 | Major | 676767671 | Health Check-WO to TE FME | 08/19/2025 21:58:49 | P2 | 2G | qunfuddah | Sceco | 2G_3G_LTE_5G SA | QUN0335 | FLM_TE |  |  | PCM-20250819-00002921 | Dear @Shabakkat_FLM_R4 Thanks to rectify QUN0336-JDJZ0776 | Dear @Shabakkat_FLM_R4 Thanks to rectify QUN0336-JDJZ0776 |  |  |  | API | 08/20/2025 00:35:13 | 08/20/2025 01:21:07 | 08/24/2025 09:42:12 |  |  | 08/24/2025 09:42:22 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250820000455 | PCM-20250820-00000749 | TT-20250820-00769 | Reference_telecom | Region_6 | ABBS0165 | ABBS0165 | Equipment | SFP_BTS | Replace SFP | Fawad Khan | 08/20/2025 07:54:48 | 08/25/2025 11:27:51 | 08/20/2025 13:54:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABBS0165-G9-L8-NL18-NL21-NNR2.6-SBTS-P3-WBB-G3 (Ref:TT-20250817-00600) | 08/14/2025 14:18:48 | Major | 7116 | BASE STATION SERVICE PROBLEM | 08/14/2025 14:18:48 | P3 | 2G | namas | Sceco | LTE SA | ABBS0165-G9-L8-NL18-NL21-NNR2.6-SBTS-P3-WBB-G3 | FLM_TE | [8 empty] | API | 08/20/2025 07:54:48 | 08/20/2025 10:04:34 | 08/25/2025 11:26:55 |  |  | 08/25/2025 11:27:51 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250820000489 | PCM-20250820-00000797 | TT-20250820-00745 | Reference_telecom | Region_6 | AQQ0841 | AQQ0841 | Equipment | SFP_BTS | Replace SFP | Manzoor Ahmed | 08/20/2025 08:32:16 | 08/20/2025 13:40:17 | 08/20/2025 14:32:16 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at AQQ1M7841-G9-NL8-SBTS-P3 (Ref:TT-20250812-02082) | 08/18/2025 05:53:48 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 08/18/2025 05:53:48 | P3 | 2G | Albaha | Sceco | LTE SA | AQQ1M7841 | FLM_TE |  |  | PCM-20250820-00000725 | pls check PLR | pls check PLR |  |  |  | API | 08/20/2025 08:32:16 | 08/20/2025 11:13:01 | 08/20/2025 13:40:00 |  |  | 08/20/2025 13:40:17 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250820000500 | PCM-20250820-00000813 | TT-20250820-00828 | Reference_telecom | Region_4 | TAF0314 | TAF0314 | Enviroment | SCECO_Failure | SCECO auto restored | Rashid Shafique | 08/20/2025 08:40:28 | 08/21/2025 01:10:52 | 08/20/2025 14:40:28 | 2(2G) 2(3G) 2(LTE) 1(5G) sites down under TAF0314-P2,TAF0143-P2 (REF: TT-20250820-00793) | 08/20/2025 08:08:23 | Major | 7706 | BTS O&M LINK FAILURE | 08/20/2025 08:08:23 | P2 | 2G | taif | Sceco | 2G_3G_LTE_5G SA | TAF0314-P2,TAF0143-P2 | FLM_TE | TAF0143 | Results: DOWN SITE HUB TAF0314-P2 TAF0143 TAF0143-P2 TAF0143 Summary: Hub: TAF0143, Down Count: 2, Down Sites: TAF0314-P2, TAF0143-P2 Alarm Summary: TAF0143 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 08/20/2025 08:40:28 | 08/20/2025 12:42:21 | 08/21/2025 01:10:33 |  |  | 08/21/2025 01:10:52 |  | Rashid Shafique |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250820000703 | PCM-20250820-00001147 | TT-20250820-01096 | Reference_telecom | Region_3 | MDTB0610 | MDTB0610 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 08/20/2025 10:49:14 | 09/04/2025 04:59:12 | 08/20/2025 22:49:14 | External Clock Reference Problem at MDTB2M5610-P1-WDM-HUB @ Generator_DG | 08/20/2025 07:33:28 | Minor | 26262 | External Clock Reference Problem | 08/20/2025 07:30:04 | P1 | SRAN | madinah | Generator_DG | 2G NSA | MDTB2M5610 | FLM_TE | MDTB0610 | Dear FLM Team, hub site is MDTB0610 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. | PCM-20250820-00001138 | Dear FLM Team, hub site is MDTB0610 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. | Dear FLM Team, hub site is MDTB0610 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. |  |  |  | API | 08/20/2025 10:49:14 | 08/20/2025 15:37:19 | 08/21/2025 17:47:41 | [5 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250820001287 | PCM-20250820-00002026 | TT-20250820-01968 | Reference_telecom | Region_1 | SLW2996 | SLW2996 | Transsmission | MW_LOW_RSL | Link Alignment Issue | Muhammad Kashif M M Bashir | 08/20/2025 17:22:58 | 09/23/2025 09:14:15 | 08/21/2025 05:22:58 | MW_LOF at SLW2996_NE_2_H @ Generator_SG | 08/20/2025 13:21:50 | Minor | 1-631 | MW_LOF | 08/20/2025 13:22:33 | P3 | SRAN | hafouf | Generator_SG | TX NSA | SLW2996 | FLM_TE | [8 empty] | API | 08/20/2025 17:22:58 | 08/20/2025 18:51:48 | 09/23/2025 09:13:53 |  |  | 09/23/2025 09:14:15 |  | Muhammad Kashif M M Bashir | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250821000819 | PCM-20250821-00001167 | TT-20250821-01283 | MW_HC | Region_1 | ARR0518 | ARR0518 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Muhammad Zubair Guilzar | 08/21/2025 10:37:20 | 09/29/2025 01:24:49 | 08/21/2025 22:37:20 | Huawei MW HC_P2 Observing Errors at ARR0518-ARR0625 | 08/21/2025 10:31:06 | Minor |  | LOF | 08/21/2025 10:31:06 | P1 | SRAN | arar | Sceco_STB | TX NSA | ARR0518-ARR0625 | FLM_TE | [8 empty] | API | 08/21/2025 10:37:20 | 08/23/2025 15:34:01 | 09/29/2025 00:09:00 | 09/29/2025 00:09:03 | 09/29/2025 00:09:07 | 09/29/2025 01:24:49 |  | Muhammad Zubair Guilzar | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250821000820 | PCM-20250821-00001168 | TT-20250821-01284 | MW_HC | Region_3 | AWJ0538 | AWJ0538 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Hossam Ali Ahmed Ali | 08/21/2025 10:37:22 | 09/10/2025 01:14:31 | 08/21/2025 22:37:22 | Huawei MW HC_P2 Observing Errors at AWJ0538-AWJ0975 | 08/21/2025 10:31:06 | Minor |  | LOF | 08/21/2025 10:31:06 | P3 | SRAN | tabouk | Sceco | TX NSA | AWJ0538-AWJ0975 | FLM_TE | [8 empty] | API | 08/21/2025 10:37:22 | 09/04/2025 10:02:38 | 09/10/2025 01:14:21 |  |  | 09/10/2025 01:14:31 |  | Hossam Ali Ahmed Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250821001569 | PCM-20250821-00002265 | TT-20250821-02279 | Reference_telecom | Region_6 | BLC9224 | BLC9224 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Manzoor Ahmed | 08/21/2025 17:45:51 | 10/23/2025 23:01:54 | 08/22/2025 05:45:51 | NEC MW Observing Communication FAIL at BLC9224_1(10.154.161.2) | 08/05/2025 06:04:53 | Minor |  | LOF | 08/05/2025 06:04:53 | P1 | Repeater | Albaha | Sceco | TX NSA | BLC9224_1(10.154.161.2) | FLM_TE | [8 empty] | API | 08/21/2025 17:45:51 | 08/21/2025 19:09:04 | 10/23/2025 23:01:37 |  |  | 10/23/2025 23:01:54 |  | Manzoor Ahmed | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250822000146 | PCM-20250822-00000221 | TT-20250822-00212 | Reference_telecom | Region_1 | ARR6002 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 08/22/2025 03:03:42 | 09/06/2025 06:07:51 | 08/22/2025 09:03:42 | Local Cell Unusable at ARR6002-P3_SRAN ref:TT-20250814-00340 @ Sceco | 08/19/2025 13:35:58 | Major | 28203 | Local Cell Unusable | 08/19/2025 13:34:22 | P3 | SRAN | arar | Sceco | 3G SA | ARR6002 | FLM_TE | [8 empty] | API | 08/22/2025 03:03:42 | 08/23/2025 15:34:00 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250822001174 | PCM-20250822-00001819 | TT-20250822-01653 | Reference_telecom | Region_4 | MAS2223 | MAS2223 |  |  |  | Farag Ahmed Taha Mohamed | 08/22/2025 20:00:05 | 09/06/2025 13:35:24 | 08/23/2025 02:00:05 | 3(2G) 2(3G) 1(LTE) 2(5G) sites down under MAS2223-P3,MAS0031-P3,MAS0030-P2-USF/MAS0030-P2-USF @ Generator_SG (Ref::TT-20250821-02789) | 08/22/2025 17:13:36 | Major | 7706 | BTS O&M LINK FAILURE | 08/22/2025 17:13:36 | P3 | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G SA | MAS2223-P3,MAS0031-P3,MAS0030-P2-USF/MAS0030-P2-USF | FLM_EM | MAS2223 | Results: DOWN SITE HUB MAS2223-P3 MAS2223 MAS0031-P3 MAS0030 MAS0030-P2-USF/MAS0030-P2-USF MAS0030 Summary: Hub: MAS2223, Down Count: 1, Down Sites: MAS2223-P3 Hub: MAS0030, Down Count: 2, Down Sites: MAS0031-P3, MAS0030-P2-USF/MAS0030-P2-USF Alarm Summary: MAS2223 No Active Alarm on HUB MAS0030 No Active Alarm on HUB | PCM-20250822-00001777 | power issue | power issue |  | sites down |  | API | 08/22/2025 20:00:05 | 08/23/2025 05:46:40 | [6 empty] | NSN_RO |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20250823000524 | PCM-20250823-00000773 | TT-20250823-00774 | Reference_telecom | Region_4 | JED0028 | JED0028 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 08/23/2025 10:28:07 | 08/23/2025 21:57:47 | 08/23/2025 14:28:07 | 1(2G) site down under JED0028-P1-DIA (Ref::TT-20250823-00637) | 08/23/2025 09:02:32 | Critical | 7706 | BTS O&M LINK FAILURE | 08/23/2025 09:02:32 | P1 | 2G | jeddah | Sceco | 2G SA | JED0028-P1-DIA | FLM_TE | JED0028 | Results: DOWN SITE HUB JED0028-P1-DIA JED0028 Summary: Hub: JED0028, Down Count: 1, Down Sites: JED0028-P1-DIA Alarm Summary: JED0028 No Active Alarm on HUB |  |  |  |  | site down |  | API | 08/23/2025 10:28:07 | 08/23/2025 16:19:51 | 08/23/2025 16:21:07 | 08/23/2025 16:21:26 | 08/23/2025 16:21:51 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250823001646 | PCM-20250823-00002541 | TT-20250823-02278 | Reference_EM | Region_4 | RYMK0544 | RYMK0544 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 08/23/2025 22:02:39 | 10/02/2025 13:44:05 | 08/24/2025 04:02:39 | 1(2G/LTE) Site down under RYMK2231 (REF: TT-20250823-01620) | 08/23/2025 17:09:01 | Major | 7706 | BTS O&M LINK FAILURE | 08/23/2025 17:09:01 | P2 | 2G | taif | Sceco | 2G_3G_LTE SA | RYMK2231 | FLM_EM | RYMK0544 | Hub: RYMK0544 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20250823-00002409 | Hub: RYMK0544 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: RYMK0544 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | site down |  | API | 08/23/2025 22:02:39 | 09/06/2025 16:29:47 | 10/02/2025 13:43:56 |  |  | 10/02/2025 13:44:05 |  | Farghal Ashour Hassan Farghal | Force_Majeure |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250823001743 | PCM-20250823-00002650 | TT-20250823-01772 | Reference_telecom | Region_2 | RIYB2U6721 | RIYB6021 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 08/23/2025 22:33:28 | 09/04/2025 15:18:04 | 08/24/2025 10:33:28 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6721-CA-P3 @ Sceco | 08/23/2025 14:20:57 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 08/23/2025 14:20:52 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6721 | FLM_TE |  |  | PCM-20250823-00001834 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 08/23/2025 22:33:28 | 08/24/2025 15:38:50 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250824000459 | PCM-20250824-00000699 | TT-20250824-00752 | Telecom | Region_1 | DMV0098 | DMV0098 |  |  |  | Mohamed Magdy Fouad Zayed | 08/24/2025 06:49:44 | 08/30/2025 17:50:34 | 08/24/2025 18:49:44 | BD_STATUS at DMV0098_NE_2 @ Sceco_STB | 08/24/2025 02:58:14 | Minor | 1-119 | BD_STATUS | 08/24/2025 02:49:17 | P1 | SRAN | hafouf | Sceco_STB | TX NSA | DMV0098 | FLM_TE | [8 empty] | API | 08/24/2025 06:49:44 | 08/24/2025 07:26:13 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250824001163 | PCM-20250824-00001822 | TT-20250824-01635 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/24/2025 14:10:38 | 09/24/2025 17:18:38 | 08/24/2025 20:10:38 | HC:: Multiple Alarms Active at Site JED6008 ¦ FLM Need To Check | 08/24/2025 14:10:16 | Major |  | Health Check-WO to TE FME | 08/24/2025 14:10:16 | P3 | 2G | jeddah | Sceco | IBS SA | JED6008 | FLM_TE | [8 empty] | API | 08/24/2025 14:10:38 | 08/24/2025 17:05:12 | 09/24/2025 17:18:32 |  |  | 09/24/2025 17:18:38 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250824001284 | PCM-20250824-00001949 | TT-20250824-01764 | Reference_telecom | Region_3 | YNB0675 | YNB0675 |  |  |  | Muhammad Sajjad R3 | 08/24/2025 14:15:05 | 09/04/2025 04:45:41 | 08/25/2025 02:15:05 | NEC MW Observing SBY TX Bus Error at YNB0675(10.159.106.34) | 08/20/2025 19:34:35 | Minor |  | LOF | 08/20/2025 19:34:35 | VIP | SRAN | yanbu | Sceco_STB | TX NSA | YNB0675(10.159.106.34) | FLM_TE | [8 empty] | API | 08/24/2025 14:15:05 | 08/25/2025 11:27:52 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250824001464 | PCM-20250824-00002213 | TT-20250824-02002 | Reference_telecom | Region_4 | JDJZ0776-LL-CSG-01 | JDJZ0776 | Transsmission | Fiber CUT | Mobily LL cut | Mudassar Bashir Bashir Ahmad | 08/24/2025 15:51:48 | 08/29/2025 11:26:36 | 08/25/2025 03:51:48 | MW_LINK DOWN at JDJZ0776-LL-CSG-01 TO JDJZ0778-LL-CSG-01 ¦¦ ref TT-20250702-00384 | 08/24/2025 15:04:13 | Minor | 15269 | LOS | 08/24/2025 15:04:17 | P2 | IPRAN | qunfuddah | Sceco_STB | IPRAN NSA | JDJZ0776 | FLM_TE | [8 empty] | API | 08/24/2025 15:51:48 | 08/24/2025 16:14:54 | 08/29/2025 11:26:26 |  |  | 08/29/2025 11:26:36 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250825000873 | PCM-20250825-00001342 | TT-20250825-01365 | Reference_telecom | Region_4 | JED1U6781 | JED6081 | Equipment | SFP_BTS | Replace SFP | Mohamed Farag Abdelbary | 08/25/2025 14:51:42 | 09/18/2025 12:33:25 | 08/25/2025 20:51:42 | BASE STATION ANTENNA LINE PROBLEM (VSWR upper threshold exceeded) at JED1U6781-G9-L18-L21-P3-CA (REF_TT-20250809-00946) | 08/10/2025 09:19:52 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 08/10/2025 09:19:52 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE SA | JED1U6781 | FLM_TE | [8 empty] | API | 08/25/2025 14:51:42 | 08/25/2025 15:37:04 | 09/10/2025 16:40:38 |  |  | 09/18/2025 12:33:25 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250825001510 | PCM-20250825-00002600 | TT-20250825-02659 | Telecom | Region_1 | JBL2108 | JBL2108 |  |  |  | Tahir Mahmood Hafiz Yar | 08/25/2025 22:50:08 | 09/04/2025 18:37:47 | 08/26/2025 10:50:08 | HARD_BAD at JBL2108_NE_18_H @ Generator_DG | 08/25/2025 22:48:17 | Minor | 1-236 | HARD_BAD | 08/25/2025 19:48:41 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBL2108 | FLM_TE | [8 empty] | API | 08/25/2025 22:50:08 | 08/25/2025 22:50:19 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250826000584 | PCM-20250826-00001590 | TT-20250826-01402 | Telecom | Region_2 | AFF2484 | AFF2484 |  |  |  | Zakir Muhammad Yar Muhammad | 08/26/2025 08:12:13 | 09/07/2025 14:13:53 | 08/26/2025 14:12:13 | BBU CPRI Interface Error at AFF2484-P3_SRAN-PC @ Sceco | 08/26/2025 08:09:29 | Major | 26234 | BBU CPRI Interface Error | 08/26/2025 08:06:55 | P3 | SRAN | dawadmi | Sceco | 2G NSA | AFF2484 | FLM_TE | [8 empty] | API | 08/26/2025 08:12:13 | 08/26/2025 09:15:49 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250826000587 | PCM-20250826-00001594 | TT-20250826-01407 | Telecom | Region_2 | AFF2484 | AFF2484 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Zakir Muhammad Yar Muhammad | 08/26/2025 08:15:20 | 09/08/2025 10:08:55 | 08/26/2025 14:15:20 | NR Cell Unavailable at AFF2484-P3_SRAN-PC @ Sceco | 08/26/2025 08:08:27 | Major | 29841 | NR Cell Unavailable | 08/26/2025 08:06:55 | P3 | SRAN | dawadmi | Sceco | 5G SA | AFF2484 | FLM_TE | [8 empty] | API | 08/26/2025 08:15:20 | 09/08/2025 10:08:55 | [5 empty] | Zakir Muhammad Yar Muhammad | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250826001518 | PCM-20250826-00002939 | TT-20250826-02633 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 08/26/2025 17:40:49 | 09/06/2025 13:03:50 | 08/26/2025 23:40:49 | Observing Multiple ALU CIDs flapped and restored on MAK - HM | 08/26/2025 17:36:01 | Major | 5000003 | Link Down | 08/26/2025 17:36:01 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE | [5 empty] | Observing Multiple ALU CIDs flapped and restored on MAK - HM |  |  | API | 08/26/2025 17:40:49 | 09/06/2025 13:03:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250826001825 | PCM-20250826-00003432 | TT-20250826-03122 | Reference_telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 08/26/2025 22:02:49 | 09/24/2025 17:18:54 | 08/27/2025 10:02:49 | JED1W6081 Partial down | 08/26/2025 21:38:58 | Minor | 613007 | Wi-Fi AP Out Of Service | 08/26/2025 21:38:58 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_3-6F-AP04 | FLM_TE | [8 empty] | API | 08/26/2025 22:02:49 | 08/27/2025 15:33:58 | 09/24/2025 17:18:45 |  |  | 09/24/2025 17:18:54 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250827000439 | PCM-20250827-00001783 | TT-20250827-01899 | Reference_EM | Region_2 | RIYA2U6760B | RIYA6060 |  |  |  | Tanveer Ahmad Fateh Muhammad | 08/27/2025 06:21:37 | 09/06/2025 13:35:25 | 08/27/2025 12:21:37 | eNodeB Out of Service at RIYA2U6760B-P3 @ Sceco(ref:TT-20250727-00697) | 08/21/2025 12:10:51 | Major | 29249 | eNodeB Out of Service | 08/21/2025 12:10:51 | P3 | 4G | riyadh | Sceco | 5G SA | RIYA2U6760B | FLM_EM | [8 empty] | API | 08/27/2025 06:21:37 | 08/27/2025 11:32:41 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Reject_FME | CM20250827001634 | PCM-20250827-00003467 | TT-20250827-03506 | Telecom | Region_6 | SABYA-SEC0014 | SEC0014 |  |  |  | Farhan Ali Khan | 08/27/2025 18:41:47 | 10/07/2025 18:04:13 | 08/28/2025 06:41:47 | Civil snags clearance for the new STC dark fiber | 08/27/2025 18:41:02 | Minor | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 08/27/2025 18:41:02 | P1 | DWDM | jizan | Sceco | DWDM NSA | SABYA-SEC0014 | FLM_TE | [8 empty] | API | 08/27/2025 18:41:47 | 09/04/2025 17:51:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250827001641 | PCM-20250827-00003476 | TT-20250827-03512 | Telecom | Region_6 | ARS0017 | ARS0017 | Transsmission | Fiber CUT | STC LL cut | Farhan Ali Khan | 08/27/2025 18:43:23 | 09/02/2025 15:57:37 | 08/28/2025 06:43:23 | Civil snags clearance for the new STC dark fiber | 08/27/2025 18:42:49 | Minor | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 08/27/2025 18:42:49 | P1 | 2G | jizan | Sceco | DWDM NSA | ARS0017 | FLM_TE | [8 empty] | API | 08/27/2025 18:43:23 | 09/02/2025 15:04:01 | 09/02/2025 15:17:21 | 09/02/2025 15:17:25 | 09/02/2025 15:17:31 | 09/02/2025 15:57:37 |  | Farhan Ali Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20250828000086 | PCM-20250828-00000128 | TT-20250828-00111 | EM | [7 empty] | 08/28/2025 01:29:33 | 08/28/2025 01:29:33 | 08/28/2025 05:29:33 | NE_COMMU_GNE_SWITCH at PEACE CLS @ | 08/28/2025 01:27:42 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 08/28/2025 01:27:39 | P1 | DWDM |  |  | DWDM NSA | PEACE CLS | FLM_EM | [5 empty] | NE PCLS0001_ELC_2's current GNE has been switched to standby GNE |  |  | API | 08/28/2025 01:29:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20250828000238 | PCM-20250828-00000415 | TT-20250828-00463 | Telecom | Region_2 | RIYA6042 | RIYA6042 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 08/28/2025 05:15:50 | 09/06/2025 13:04:46 | 08/28/2025 17:15:50 | RF Unit Maintenance Link Failure at RIYA6042-DCU-3 @ Sceco | 08/28/2025 05:13:46 | Minor | 26235 | RF Unit Maintenance Link Failure | 08/28/2025 05:10:41 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6042 | FLM_TE | [8 empty] | API | 08/28/2025 05:15:50 | 09/06/2025 13:04:46 | [5 empty] | Muhammad Waqas Ashraf Muhammad Ashraf | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250828000776 | PCM-20250828-00001198 | TT-20250828-01215 | Telecom | Region_4 | JED2171 | JED2171 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 08/28/2025 12:50:29 | 08/28/2025 13:00:19 | 08/29/2025 00:50:29 | PT::FLM need to perform HC at JED2171-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 (Bo request) | 08/28/2025 12:50:14 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/28/2025 12:50:14 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED2171-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 | FLM_TE | [8 empty] | API | 08/28/2025 12:50:29 | 08/28/2025 13:00:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250828001094 | PCM-20250828-00001660 | TT-20250828-01667 | EM | Region_6 | TBL9723 | TBL9723 |  |  |  | Asad Saddiq | 08/28/2025 16:20:41 | 09/02/2025 13:58:38 | 08/29/2025 04:20:41 | NSP MW Observing AC, fire alarm at TBL9723 | 08/28/2025 16:18:47 | Minor | MAIN AC + GEN FAILURE (Input-4) | MAIN AC + GEN FAILURE (Input-4) | 08/28/2025 16:18:47 | P3 | Repeater | bisha | Sceco | TX NSA | TBL9723 | FLM_EM | [5 empty] | NSP MW Observing AC, fire alarm at TBL9723 |  |  | API | 08/28/2025 16:20:41 | 08/30/2025 12:08:42 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250828001142 | PCM-20250828-00001719 | TT-20250828-01264 | Telecom | Region_1 | ARM0714 | ARM0714 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 08/28/2025 16:50:24 | 09/29/2025 02:32:30 | 08/29/2025 04:50:24 | ODU CPU / Cable Open at DRN0129_1 on 10.158.154.129 @ Sceco | 08/28/2025 13:10:52 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 08/28/2025 13:11:14 | P1 | SRAN | dammam | Generator_SG | TX NSA | DRN0129 | FLM_EM | ARM0714 | Dear Team, Hub:- ARM0714 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250828-00001651 | Dear Team, Hub:- ARM0714 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- ARM0714 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 08/28/2025 16:50:24 | 09/29/2025 02:20:11 | 09/29/2025 02:32:22 |  |  | 09/29/2025 02:32:30 |  | Ahmed AbdELmoaz Ibrahim | MW_Spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250828001202 | PCM-20250828-00001824 | TT-20250828-01831 | Reference_telecom | Region_1 | ARM0717 | ARM0717 |  |  |  | Talha Manzoor | 08/28/2025 17:34:39 | 09/01/2025 11:09:54 | 08/28/2025 23:34:39 | RF Unit VSWR Threshold Crossed at ARM0717-P3_SRAN @ Sceco | 08/28/2025 14:34:28 | Major | 26529 | RF Unit VSWR Threshold Crossed | 08/28/2025 14:34:15 | P3 | SRAN | dammam | Sceco | 2G NSA | ARM0717 | FLM_TE | [8 empty] | API | 08/28/2025 17:34:39 | 08/28/2025 19:08:56 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250828001220 | PCM-20250828-00001855 | TT-20250828-01855 | Telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Replace Indoor Feeder Cable Connector | Mohamed Farag Abdelbary | 08/28/2025 17:45:43 | 09/24/2025 17:19:07 | 08/29/2025 05:45:43 | JED1W6081 is partial down | 08/28/2025 17:36:55 | Minor | 613007 | Wi-Fi AP Out Of Service | 08/28/2025 17:36:55 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_3-6F-AP04 | FLM_TE | [8 empty] | API | 08/28/2025 17:45:43 | 08/30/2025 12:55:47 | 09/24/2025 17:18:59 |  |  | 09/24/2025 17:19:07 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250828001487 | PCM-20250828-00002263 | TT-20250828-02266 | Telecom | Region_1 | ARM0714 | ARM0714 |  |  |  | Talha Manzoor | 08/28/2025 21:09:02 | 09/04/2025 18:37:51 | 08/29/2025 09:09:02 | ODU CPU / Cable Open at ARM0714 on 10.158.154.132 @ Generator_SG | 08/28/2025 12:31:35 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 08/28/2025 12:23:52 | P1 | SRAN | dammam | Generator_SG | TX NSA | ARM0714 | FLM_TE | [8 empty] | API | 08/28/2025 21:09:02 | 08/29/2025 01:08:44 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250829000267 | PCM-20250829-00000450 | TT-20250829-00499 | Reference_telecom | Region_4 | TURY0646 | TURY0646 | Equipment | SFP_BTS | Replace SFP | Rashid Shafique | 08/29/2025 06:56:03 | 08/29/2025 13:59:47 | 08/29/2025 12:56:03 | TRX OPERATION DEGRADED at TURY0646-P1-HUB (ref. TT-20250828-02074) @ Sceco | 08/28/2025 19:22:33 | Major | 7607 | TRX OPERATION DEGRADED | 08/28/2025 19:22:30 | P1 | 2G | taif | Sceco | 2G SA | TURY0646 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 08/29/2025 06:56:03 | 08/29/2025 13:55:49 | 08/29/2025 13:59:40 |  |  | 08/29/2025 13:59:47 |  | Rashid Shafique |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250829001003 | PCM-20250829-00001506 | TT-20250829-01615 | Telecom | Region_4 | JED2189 | JED2189 |  |  |  | BARKAT ALI MAIN HILAL | 08/29/2025 21:37:55 | 08/30/2025 16:28:33 | 08/30/2025 09:37:55 | PT:: BO TRM need to Check PLR/GTP-U at JED2189/R4 | 08/29/2025 21:36:07 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/29/2025 21:36:09 | P3 | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G NSA | JED2189-G9 | FLM_TE | JED2189 | Dear FLM , kindly rectify link JED2189-JED0368 | PCM-20250829-00001502 | Dear FLM , kindly rectify link JED2189-JED0368 | Dear FLM , kindly rectify link JED2189-JED0368 |  |  |  | API | 08/29/2025 21:37:55 | 08/30/2025 16:28:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250830000271 | PCM-20250830-00000433 | TT-20250830-00438 | Telecom | Region_1 | DAM2M3631 | DAM0631 |  |  |  | Imran Ali Yousaf | 08/30/2025 06:06:32 | 09/03/2025 14:31:02 | 08/30/2025 12:06:32 | Outage-20250829-0004 : 1(LTE) sites down under DAM0631-P3 @ Sceco | 08/30/2025 06:01:30 | Major | 301 | NE Is Disconnected | 08/30/2025 01:12:53 | P3 | 3G | dammam | Sceco | LTE SA | DAM0631-P3 | FLM_TE | DAM0631 | Results: DOWN SITE HUB DAM0631-P3 DAM0631 Summary: Hub: DAM0631, Down Count: 1, Down Sites: DAM0631-P3 Alarm Summary: DAM0631 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 08/30/2025 06:06:32 | 08/30/2025 08:27:03 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250830000369 | PCM-20250830-00000565 | TT-20250830-00576 | Reference_telecom | Region_4 | JED1U6795_1 | JED6095 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 08/30/2025 07:57:19 | 09/24/2025 17:19:22 | 08/30/2025 13:57:19 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6795-P3-CA (Ref.:: TT-20250611-01890) @ Sceco | 08/29/2025 18:40:25 | Major | 7654 | CELL OPERATION DEGRADED | 08/29/2025 18:40:17 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6795 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 08/30/2025 07:57:19 | 08/30/2025 12:55:53 | 09/24/2025 17:19:16 |  |  | 09/24/2025 17:19:22 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250830001137 | PCM-20250830-00001730 | TT-20250830-01649 | Reference_telecom | Region_1 | HFF6030 | HFF6030 |  |  |  | Muhammad Kashif M M Bashir | 08/30/2025 18:50:58 | 09/01/2025 11:10:02 | 08/31/2025 00:50:58 | Capability Inconsistent at HFF6030-DCU2 @ Sceco | 08/30/2025 10:09:28 | Major | 29800 | Capability Inconsistent | 08/30/2025 10:13:19 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6030 | FLM_TE | [8 empty] | API | 08/30/2025 18:50:58 | 08/30/2025 19:53:32 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250830001288 | PCM-20250830-00001953 | TT-20250830-01864 | Reference_telecom | Region_2 | RIY_Flagship | RIY_Flagship | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Muhammad Naeem Muhammad Gulzar | 08/30/2025 20:54:27 | 10/12/2025 12:11:41 | 08/31/2025 02:54:27 | RF Unit VSWR Threshold Crossed at RIY_Flagship-VIP @ Sceco_STB | 08/30/2025 17:54:14 | Major | 26529 | RF Unit VSWR Threshold Crossed | 08/30/2025 17:54:02 | VIP | 4G | riyadh | Sceco_STB | 2G NSA | RIY_Flagship | FLM_TE | [8 empty] | API | 08/30/2025 20:54:27 | 08/31/2025 13:31:30 | 10/12/2025 12:11:19 |  |  | 10/12/2025 12:11:41 |  | Muhammad Naeem Muhammad Gulzar | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250830001449 | PCM-20250830-00002247 | TT-20250830-00927 | Reference_telecom | Region_2 | RIYA2U6269 | RIYA6169 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 08/30/2025 23:58:32 | 09/07/2025 14:13:56 | 08/31/2025 11:58:32 | External Clock Reference Problem at RIYA2U6269-P3-Tech @ Sceco | 08/30/2025 09:10:02 | Minor | 26262 | External Clock Reference Problem | 08/30/2025 09:06:37 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYA2U6269 | FLM_TE |  | Dear Team , Site is restored , observing no issue | PCM-20250830-00002216 | Dear Team , Site is restored , observing no issue | Dear Team , Site is restored , observing no issue |  |  |  | API | 08/30/2025 23:58:32 | 08/31/2025 12:13:43 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831000406 | PCM-20250831-00000704 | TT-20250831-00745 | Telecom | Region_1 | HFF6029 | HFF6029 |  |  |  | Muhammad Kashif M M Bashir | 08/31/2025 09:11:10 | 09/03/2025 14:31:05 | 08/31/2025 21:11:10 | RF Unit Maintenance Link Failure at HFF6029-DCU4 @ Sceco | 08/31/2025 09:03:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 08/31/2025 09:05:38 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 08/31/2025 09:11:10 | 08/31/2025 14:34:07 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831000791 | PCM-20250831-00001236 | TT-20250831-01254 | Reference_telecom | Region_2 | SSHG2S7028 | SSHG0028 |  |  |  | Touseef Iqbal Mazhar Iqbal | 08/31/2025 13:31:59 | 09/04/2025 15:18:21 | 09/01/2025 01:31:59 | External Clock Reference Problem at SSHG2S7028-P3(Ref::TT-20250821-00590) @ Sceco | 08/21/2025 11:35:16 | Minor | 26262 | External Clock Reference Problem | 08/21/2025 11:31:53 | P3 | 4G | muzamiah | Sceco | 2G NSA | SSHG2S7028 | FLM_TE | [8 empty] | API | 08/31/2025 13:31:59 | 08/31/2025 15:48:32 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831000794 | PCM-20250831-00001239 | TT-20250831-01256 | Reference_telecom | Region_2 | SSHG2S7029 | SSHG0029 |  |  |  | Touseef Iqbal Mazhar Iqbal | 08/31/2025 13:32:58 | 09/04/2025 15:18:22 | 09/01/2025 01:32:58 | External Clock Reference Problem at SSHG2S7029-P3(Ref::TT-20250821-00591) @ Sceco | 08/21/2025 11:35:22 | Minor | 26262 | External Clock Reference Problem | 08/21/2025 11:32:00 | P3 | 4G | muzamiah | Sceco | 2G NSA | SSHG2S7029 | FLM_TE | [8 empty] | API | 08/31/2025 13:32:58 | 08/31/2025 15:48:33 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001289 | PCM-20250831-00001985 | TT-20250831-01892 | MW_HC | Region_6 | DRB0165 | DRB0165 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 08/31/2025 18:00:39 | 09/10/2025 05:29:01 | 09/01/2025 06:00:39 | NEC MW HC_P2 Observing Modem Down at DRB0165(10.154.170.178)--JDJZ0785(10.154.170.186) | 08/31/2025 17:59:21 | Minor |  | LOF | 08/31/2025 17:59:21 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0165(10.154.170.178)--JDJZ0785(10.154.170.186) | FLM_TE | [8 empty] | API | 08/31/2025 18:00:39 | 09/10/2025 05:29:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001314 | PCM-20250831-00002009 | TT-20250831-01916 | MW_HC | Region_1 | DMJB0086 | DMJB0086 | Transsmission | MW_LOW_RSL | Link Alignment Issue | Meraj Husain Idd Baksh | 08/31/2025 18:01:06 | 09/17/2025 00:26:01 | 09/01/2025 06:01:06 | NEC MW HC_P1 Observing Performance + RSL Issue at DMJB0086(10.248.32.55)--DMJB0975(10.248.32.43) | 08/31/2025 17:59:21 | Minor |  | LOF | 08/31/2025 17:59:21 | P1 | SRAN | dammam | Generator_SG | TX NSA | DMJB0086(10.248.32.55)--DMJB0975(10.248.32.43) | FLM_TE | [8 empty] | API | 08/31/2025 18:01:06 | 09/17/2025 00:26:01 | [5 empty] | Meraj Husain Idd Baksh | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001376 | PCM-20250831-00002071 | TT-20250831-01978 | Reference_telecom | Region_6 | RTH0608 | RTH0608 |  |  |  | Muhammad Ali | 08/31/2025 18:02:09 | 10/09/2025 14:32:24 | 09/01/2025 06:02:09 | Nokia Eband Observing LagPortDown-Port 4/1,DemFail-Port 4/1,DemFail-Port at RTH0608_01-10.221.241.82 | 08/20/2024 13:13:09 | Minor |  | LOF | 08/20/2024 13:13:09 | P2 | 2G | raith | Generator_DG | TX NSA | RTH0608_01-10.221.241.82 | FLM_TE | [8 empty] | API | 08/31/2025 18:02:09 | 08/31/2025 18:38:08 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001448 | PCM-20250831-00002144 | TT-20250831-02052 | Reference_telecom | Region_6 | MHL0123 | MHL0123 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Muhammad Jamal Khan Abbas Ali | 08/31/2025 18:03:27 | 09/30/2025 11:57:26 | 09/01/2025 06:03:27 | NEC MW Observing MODEM Power Supply Alarm,XIF,MODEM Power Supply Alarm,XIF at MHL0123-3(10.154.171.241) | 08/22/2025 19:21:42 | Minor |  | LOF | 08/22/2025 19:21:42 | P1 | 2G | mohail | Sceco | TX NSA | MHL0123-3(10.154.171.241) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:27 | 09/30/2025 11:57:26 | [5 empty] | Muhammad Jamal Khan Abbas Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001451 | PCM-20250831-00002146 | TT-20250831-02054 | Reference_telecom | Region_6 | MHL0136 | MHL0136 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Muhammad Jamal Khan Abbas Ali | 08/31/2025 18:03:31 | 09/30/2025 11:57:25 | 09/01/2025 06:03:31 | NEC MW Observing XIF,XIF,MODEM Power Supply Alarm,MODEM Power Supply Alarm at MHL0136-MHL9722(10.157.250.22) | 08/22/2025 19:30:14 | Minor |  | LOF | 08/22/2025 19:30:14 | P3 | 2G | mohail | Sceco | TX NSA | MHL0136-MHL9722(10.157.250.22) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:31 | 09/30/2025 11:57:25 | [5 empty] | Muhammad Jamal Khan Abbas Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001450 | PCM-20250831-00002147 | TT-20250831-02055 | Reference_telecom | Region_6 | MHL0137 | MHL0137 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Muhammad Jamal Khan Abbas Ali | 08/31/2025 18:03:31 | 09/30/2025 11:57:26 | 09/01/2025 06:03:31 | NEC MW Observing High BER,RX Level,LOF,Frame ID at MHL0137-2(10.157.250.26) | 08/22/2025 19:23:18 | Minor |  | LOF | 08/22/2025 19:23:18 | P1 | 2G | mohail | Generator_DG | TX NSA | MHL0137-2(10.157.250.26) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:31 | 09/30/2025 11:57:26 | [5 empty] | Muhammad Jamal Khan Abbas Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001454 | PCM-20250831-00002150 | TT-20250831-02058 | Reference_telecom | Region_6 | MHL0256 | MHL0256 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Muhammad Jamal Khan Abbas Ali | 08/31/2025 18:03:34 | 09/30/2025 11:57:24 | 09/01/2025 06:03:34 | NEC MW Observing MODEM Power Supply Alarm,XIF,XIF,MODEM Power Supply Alarm at MHL0256_1(10.154.171.242) | 08/22/2025 19:23:07 | Minor |  | LOF | 08/22/2025 19:23:07 | P2 | 2G | mohail | Sceco | TX NSA | MHL0256_1(10.154.171.242) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:34 | 09/30/2025 11:57:24 | [5 empty] | Muhammad Jamal Khan Abbas Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001452 | PCM-20250831-00002149 | TT-20250831-02057 | Reference_telecom | Region_6 | MHL2007 | MHL2007 | Transsmission | MW_Problematic | Fading Issue | Muhammad Jamal Khan Abbas Ali | 08/31/2025 18:03:34 | 09/30/2025 11:57:25 | 09/01/2025 06:03:34 | NEC MW Observing ODU Power Supply,LOF,ODU CPU / Cable Open at MHL2007(10.157.250.27) | 08/22/2025 19:25:36 | Minor |  | LOF | 08/22/2025 19:25:36 | P2 | 2G | mohail | Sceco | TX NSA | MHL2007(10.157.250.27) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:34 | 09/30/2025 11:57:25 | [5 empty] | Muhammad Jamal Khan Abbas Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250831001463 | PCM-20250831-00002159 | TT-20250831-02067 | Reference_telecom | Region_6 | RTH9007 | RTH9007 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Ali | 08/31/2025 18:03:42 | 10/05/2025 13:57:54 | 09/01/2025 06:03:42 | NEC MW Observing LOF,RX Level,LOF,RX Level at RTH9007-1(10.157.248.65) | 11/06/2024 10:47:40 | Minor |  | LOF | 11/06/2024 10:47:40 | P1 | Repeater | raith | Sceco_STB | TX NSA | RTH9007-1(10.157.248.65) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:42 | 09/30/2025 11:52:07 | 10/05/2025 13:57:47 |  |  | 10/05/2025 13:57:54 |  | Muhammad Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250831001477 | PCM-20250831-00002173 | TT-20250831-02081 | Reference_telecom | Region_6 | SUL9467 | SUL9467 |  |  |  | Mustafa Mohamed Abdelghani Elagami | 08/31/2025 18:03:57 | 09/30/2025 11:12:08 | 09/01/2025 06:03:57 | NEC MW Observing LAN Link at SUL9467(10.89.222.115) | 08/22/2025 19:36:38 | Minor |  | LOF | 08/22/2025 19:36:38 | P3 | Repeater | wadi dawasar | Generator_SG | TX NSA | SUL9467(10.89.222.115) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:57 | 08/31/2025 21:47:44 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250831001478 | PCM-20250831-00002174 | TT-20250831-02082 | Reference_telecom | Region_6 | TFBH0814 | TFBH0814 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SHAH KHALID | 08/31/2025 18:03:58 | 10/20/2025 13:09:22 | 09/01/2025 06:03:58 | NEC MW Observing Radio Traffic Aggregation Link at TFBH0814-2(10.154.162.78) | 08/20/2025 15:10:55 | Minor |  | LOF | 08/20/2025 15:10:55 | P3 | 2G | makhwa | Sceco | TX NSA | TFBH0814-2(10.154.162.78) | FLM_TE | [8 empty] | API | 08/31/2025 18:03:58 | 10/09/2025 15:13:34 | 10/20/2025 13:09:22 |  |  |  |  | SHAH KHALID | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250831001499 | PCM-20250831-00002198 | TT-20250831-02104 | Reference_telecom | Region_2 | RIY2925 | RIY2925 | Transsmission | MW_RSL_fading | Bad Weather | Farmanullah Akbar Jan | 08/31/2025 18:04:20 | 09/27/2025 01:11:19 | 09/01/2025 06:04:20 | MW RTN Observing PG_PRT_DEGRADED at RIY2925_NE_14 | 08/27/2025 06:31:12 | Minor |  | LOF | 08/27/2025 06:31:12 | VIP | SRAN | al kharj | Generator_DG | TX NSA | RIY2925_NE_14 | FLM_TE | [8 empty] | API | 08/31/2025 18:04:20 | 08/31/2025 22:34:12 | 09/27/2025 01:10:57 |  |  | 09/27/2025 01:11:19 |  | Farmanullah Akbar Jan | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000205 | PCM-20250901-00000351 | TT-20250901-00377 | Reference_telecom | Region_6 | MRD0108 | MRD0108 |  |  |  | Fawad Khan | 09/01/2025 04:58:24 | 10/09/2025 14:32:25 | 09/01/2025 16:58:24 | DemFail observed in MRD0108_02 towards 10.221.243.100 @ Sceco | 08/31/2025 16:59:14 | Minor |  | DemFail | 08/31/2025 16:58:12 | P2 | 2G | mohail | Sceco | TX NSA | MRD0108 | FLM_TE | [8 empty] | API | 09/01/2025 04:58:24 | 09/01/2025 09:01:11 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250901000542 | PCM-20250901-00000882 | TT-20250901-00939 | Telecom | Region_2 | RIY0822-ZRi04-1-CSG-06 | RIY0822 | Transsmission | MW_Visibilty | Reconnect ETH Cable | Ejaz Hussain Muhammad Sharif | 09/01/2025 11:25:36 | 09/16/2025 16:03:30 | 09/01/2025 23:25:36 | HC TT at RIY0822-ZRi04-1-CSG-06 | 09/01/2025 11:24:34 | Minor | 15269 | LOS | 09/01/2025 11:24:37 | P1 | IPRAN | riyadh | Sceco | IPRAN NSA | RIY0822 | FLM_TE | [8 empty] | API | 09/01/2025 11:25:36 |  | 09/16/2025 12:32:16 | 09/16/2025 12:32:29 | 09/16/2025 13:16:54 | 09/16/2025 16:03:30 |  | Ejaz Hussain Muhammad Sharif | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250901000543 | PCM-20250901-00000884 | TT-20250901-00941 | Telecom | Region_2 | RIY0278-ZRi04-4-CSG-01 | RIY0278 | Equipment | SFP_BTS | Clean SFP | Muhammad Naeem Muhammad Gulzar | 09/01/2025 11:27:00 | 09/16/2025 15:59:39 | 09/01/2025 23:27:00 | HC TT at RIY0278-ZRi04-4-CSG-01 | 09/01/2025 11:26:31 | Minor | 15269 | LOS | 09/01/2025 11:26:34 | VIP | IPRAN | riyadh | Sceco | IPRAN NSA | RIY0278-ZRi04-4-CSG-01 | FLM_TE | [8 empty] | API | 09/01/2025 11:27:00 | 09/16/2025 12:41:26 | 09/16/2025 12:42:38 | 09/16/2025 12:42:41 | 09/16/2025 13:12:46 | 09/16/2025 15:59:39 |  | Muhammad Naeem Muhammad Gulzar | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000725 | PCM-20250901-00001144 | TT-20250901-01185 | Telecom | Region_2 | RIYA6042 | RIYA6042 | Equipment | BSS_HW_fault | Replace RF Module | Muhammad Waqas Ashraf Muhammad Ashraf | 09/01/2025 13:49:36 | 09/06/2025 16:17:54 | 09/02/2025 01:49:36 | HC for RIYA6042 | 09/01/2025 13:29:42 | Minor | 676767672 | Health Check-WO to TE FME | 09/01/2025 13:29:43 | P1 | SRAN | riyadh | Sceco | 3G NSA | RIYA6042 | FLM_TE |  |  | PCM-20250901-00001130 | Dear mohamed, Approved to replace faulty as passive item but only for the same item as before | Dear mohamed, Approved to replace faulty as passive item but only for the same item as before |  |  |  | API | 09/01/2025 13:49:36 | 09/06/2025 16:17:54 | [5 empty] | Muhammad Waqas Ashraf Muhammad Ashraf | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000830 | PCM-20250901-00001294 | TT-20250730-01323 | MW_HC | Region_1 | RSK2932 | RSK2932 |  |  |  | Mohamed Abdelaziz | 09/01/2025 14:52:23 | 09/08/2025 11:45:20 | 09/02/2025 02:52:23 | Huawei HC_P0 Observing Errors at JBKH2929-RSK2932 | 07/30/2025 11:03:13 | Minor |  | LOF | 07/30/2025 11:03:13 | P3 | SRAN | jubail | Generator_DG | TX NSA | JBKH2929-RSK2932 | FLM_TE | RSK2932 | Link still count BBE | PCM-20250901-00001285 | Link still count BBE | Link still count BBE |  |  |  | API | 09/01/2025 14:52:23 | 09/01/2025 21:34:54 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000844 | PCM-20250901-00001320 | TT-20250826-00376 | MW_HC | Region_1 | NRY0537 | NRY0537 |  |  |  | Mohamed Abdelaziz | 09/01/2025 15:00:06 | 09/22/2025 10:43:05 | 09/02/2025 03:00:06 | MW alarms, PM Errors and RSL degradation observed on MW NRY0537-DMH2098 ( As per BO request ) | 08/26/2025 03:25:42 | Minor | 1-631 | MW_LOF | 08/26/2025 03:25:42 | P3 | SRAN | hafr | Sceco | TX NSA | NRY0537 DMH2098 | FLM_TE | NRY0537 | link count BBE last 24 H | PCM-20250901-00001297 | link count BBE last 24 H | link count BBE last 24 H |  |  |  | API | 09/01/2025 15:00:06 | 09/01/2025 21:34:55 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000918 | PCM-20250901-00001415 | TT-20250821-01077 | MW_HC | Region_1 | JBKH0069 | JBKH0069 |  |  |  | Tahir Mahmood Hafiz Yar | 09/01/2025 15:35:17 | 09/22/2025 10:43:03 | 09/02/2025 03:35:17 | NEC MW HC_P1 Observing Performance Issue at ARM0663(10.76.111.235)--JBKH0069(10.76.111.233) | 08/21/2025 10:31:07 | Minor |  | LOF | 08/21/2025 10:31:07 | P1 | SRAN | jubail | Generator_DG | TX NSA | ARM0663(10.76.111.235)--JBKH0069(10.76.111.233) | FLM_TE | JBKH0069 | Link still count BBE | PCM-20250901-00001364 | Link still count BBE | Link still count BBE |  |  |  | API | 09/01/2025 15:35:17 | 09/01/2025 17:00:55 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000947 | PCM-20250901-00001459 | TT-20250811-01275 | MW_HC | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/01/2025 15:57:08 | 09/08/2025 11:45:18 | 09/02/2025 03:57:08 | NEC MW HC_P0 Observing Modem Down at DMH0104(10.159.105.101)--DMH0105(10.159.105.100) | 08/11/2025 11:40:16 | Minor |  | LOF | 08/11/2025 11:40:16 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104(10.159.105.101)--DMH0105(10.159.105.100) | FLM_TE | DMH0104 | BBE count on MW link last 24 H | PCM-20250901-00001247 | BBE count on MW link last 24 H | BBE count on MW link last 24 H |  |  |  | API | 09/01/2025 15:57:08 | 09/01/2025 17:44:00 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901000956 | PCM-20250901-00001469 | TT-20250804-01823 | MW_HC | Region_1 | JBL0998 | JBL0998 |  |  |  | Tahir Mahmood Hafiz Yar | 09/01/2025 16:01:30 | 09/22/2025 10:43:05 | 09/02/2025 04:01:30 | (As per optimization team Request) NEC MW HC For performance at link JBL0998--JBL2109 is counting performance errors | 08/04/2025 17:19:55 | Minor | 1-631 | MW_LOF | 08/04/2025 17:19:55 | P3 | SRAN | jubail | Sceco | TX NSA | JBL0998--JBL2109 | FLM_TE | JBL0998 | MW alarms still active at link need HC | PCM-20250901-00001349 | MW alarms still active at link need HC | MW alarms still active at link need HC |  |  |  | API | 09/01/2025 16:01:30 | 09/01/2025 17:00:56 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250901001160 | PCM-20250901-00001758 | TT-20250901-01701 | Reference_telecom | Region_3 | AHT0971 | AHT0971 |  |  |  | Junaid Eisa | 09/01/2025 17:55:05 | 09/15/2025 20:08:17 | 09/02/2025 05:55:05 | NEC MW Observing LAN Link at AHT0971-NE2(10.253.0.138) | 08/31/2025 00:17:03 | Minor |  | LOF | 08/31/2025 00:17:03 | P1 | SRAN | hail | Sceco_STB | TX NSA | AHT0971-NE2(10.253.0.138) | FLM_TE | [8 empty] | API | 09/01/2025 17:55:05 | [7 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001166 | PCM-20250901-00001763 | TT-20250901-01706 | Reference_telecom | Region_1 | ARM2755 | ARM2755 |  |  |  | Tahir Mahmood Hafiz Yar | 09/01/2025 17:55:11 | 09/08/2025 11:45:19 | 09/02/2025 05:55:11 | NEC MW Observing MODEM Power Supply Alarm,MODEM Power Supply Alarm at ARM2755 -2(10.76.111.231) | 08/31/2025 07:21:09 | Minor |  | LOF | 08/31/2025 07:21:09 | VIP | SRAN | jubail | Sceco | TX NSA | ARM2755 -2(10.76.111.231) | FLM_TE | [8 empty] | API | 09/01/2025 17:55:11 | 09/01/2025 18:03:01 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001190 | PCM-20250901-00001788 | TT-20250901-01731 | Reference_telecom | Region_1 | HFF6022 | HFF6022 |  |  |  | Muhammad Kashif M M Bashir | 09/01/2025 17:55:37 | 09/11/2025 12:51:56 | 09/02/2025 05:55:37 | NEC MW Observing TX Power,ODU Alarm,LOF at HFF6022(10.74.80.155) | 08/31/2025 00:04:43 | Minor |  | LOF | 08/31/2025 00:04:43 | P3 | SRAN | hafr | Sceco | TX NSA | HFF6022(10.74.80.155) | FLM_TE | [8 empty] | API | 09/01/2025 17:55:37 | 09/02/2025 07:57:32 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001205 | PCM-20250901-00001803 | TT-20250901-01746 | Reference_telecom | Region_6 | KMBS9702 | KMBS9702 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 09/01/2025 17:55:53 | 09/08/2025 15:47:06 | 09/02/2025 05:55:53 | NEC MW Observing Communication FAIL,LOF,Frame ID,XIF at KMBS9702_2(10.154.166.37) | 08/19/2025 02:02:33 | Minor |  | LOF | 08/19/2025 02:02:33 | P1 | Repeater | khamis mushyet | Generator_DG | TX NSA | KMBS9702_2(10.154.166.37) | FLM_TE | [8 empty] | API | 09/01/2025 17:55:53 | 09/08/2025 15:47:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001229 | PCM-20250901-00001827 | TT-20250901-01770 | Reference_telecom | Region_4 | TFBH0798 | TFBH0798 |  |  |  | Ahmad Kamal Abdelmawla | 09/01/2025 17:56:18 | 10/07/2025 13:39:46 | 09/02/2025 05:56:18 | NEC MW Observing ODU Alarm,TX Power at TFBH0798(10.1.175.180) | 08/28/2025 12:33:38 | Minor |  | LOF | 08/28/2025 12:33:38 | P1 | 2G | taif | Sceco_STB | TX NSA | TFBH0798(10.1.175.180) | FLM_TE | [8 empty] | API | 09/01/2025 17:56:18 | 09/02/2025 00:07:16 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001239 | PCM-20250901-00001837 | TT-20250901-01780 | Reference_telecom | Region_6 | WDS9460 | WDS9460 |  |  |  | Mustafa Mohamed Abdelghani Elagami | 09/01/2025 17:56:28 | 09/01/2025 22:36:04 | 09/02/2025 05:56:28 | NEC MW Observing MODEM Power Supply Alarm at WDS9460(10.89.222.146) | 08/23/2025 23:09:38 | Minor |  | LOF | 08/23/2025 23:09:38 | P1 | Repeater | wadi dawasar | Generator_SG | TX NSA | WDS9460(10.89.222.146) | FLM_TE | [8 empty] | API | 09/01/2025 17:56:28 | 09/01/2025 22:36:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250901001243 | PCM-20250901-00001841 | TT-20250901-01784 | Reference_telecom | Region_3 | YBDB0978 | YBDB0978 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Hossam Ali Ahmed Ali | 09/01/2025 17:56:32 | 09/24/2025 12:56:10 | 09/02/2025 05:56:32 | NEC MW Observing LAN Link at YBDB0978-FN356(10.74.87.218) | 08/30/2025 14:05:28 | Minor |  | LOF | 08/30/2025 14:05:28 | P1 | SRAN | tabouk | Sceco_STB | TX NSA | YBDB0978-FN356(10.74.87.218) | FLM_TE | [8 empty] | API | 09/01/2025 17:56:32 | 09/22/2025 11:15:45 | 09/24/2025 12:55:56 |  |  | 09/24/2025 12:56:10 |  | Hossam Ali Ahmed Ali | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001327 | PCM-20250901-00001927 | TT-20250901-01870 | MW_HC | Region_6 | BAH0007 | BAH0007 |  |  |  | SHAH KHALID | 09/01/2025 17:58:01 | 09/02/2025 00:25:22 | 09/02/2025 05:58:01 | Nokia MW HC_P1 Observing Performance Issue at BAH0007_1-BAH0005_04 | 09/01/2025 17:54:02 | Minor |  | LOF | 09/01/2025 17:54:02 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0007_1-BAH0005_04 | FLM_TE | [8 empty] | API | 09/01/2025 17:58:01 | 09/02/2025 00:25:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001383 | PCM-20250901-00001983 | TT-20250901-01925 | MW_HC | Region_6 | WDS0499 | WDS0499 |  |  |  | Mustafa Mohamed Abdelghani Elagami | 09/01/2025 17:58:58 | 09/01/2025 22:36:05 | 09/02/2025 05:58:58 | Nokia MW HC_P0 Observing Performance Issue at WDS0499-WDS0501-3 | 09/01/2025 17:54:02 | Minor |  | LOF | 09/01/2025 17:54:02 | P1 | 2G | wadi dawasar | Sceco | TX NSA | WDS0499-WDS0501-3 | FLM_TE | [8 empty] | API | 09/01/2025 17:58:58 | 09/01/2025 22:36:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001657 | PCM-20250901-00002349 | TT-20250901-02321 | Telecom | Region_4 | JED2007 | JED2007 | Transsmission | SFP_Transmission | Reset SFP | MALIK ATIF ZAMAN | 09/01/2025 22:25:20 | 10/08/2025 09:44:25 | 09/02/2025 10:25:20 | As per BO request NEC MW link JED2007(10.154.153.122) observing visibility down from it self | 09/01/2025 22:19:24 | Minor | 113388 | LOF | 09/01/2025 22:19:27 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED2007 | FLM_TE | [8 empty] | API | 09/01/2025 22:25:20 | 10/08/2025 09:44:25 | [5 empty] | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250901001662 | PCM-20250901-00002359 | TT-20250901-02331 | Telecom | Region_4 | JED0575 | JED0575 | Transsmission | SFP_Transmission | Reset SFP | MALIK ATIF ZAMAN | 09/01/2025 22:37:19 | 10/08/2025 09:44:26 | 09/02/2025 10:37:19 | As per BO request NEC MW link JED0575 (10.154.142.66) observing visibility down due to itself | 09/01/2025 22:33:20 | Minor | 113388 | LOF | 09/01/2025 22:33:28 | P2 | 2G | jeddah | Sceco | TX NSA | JED0575 | FLM_TE | [8 empty] | API | 09/01/2025 22:37:19 | 10/08/2025 09:44:26 | [5 empty] | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902000211 | PCM-20250902-00000362 | TT-20250902-00438 | Telecom | Region_4 | JED0732 | JED0732 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | BARKAT ALI MAIN HILAL | 09/02/2025 04:41:06 | 10/07/2025 16:22:14 | 09/02/2025 16:41:06 | As per BO request NEC MW link JED0732_2(10.1.164.25) observing visibility down from itself SJED0300 (10.1.164.26) is down from hub site | 09/02/2025 04:38:06 | Minor | 113388 | LOF | 09/02/2025 04:38:09 | P2 | 2G | jeddah | Sceco | TX NSA | JED0732_2 | FLM_TE | [8 empty] | API | 09/02/2025 04:41:06 | 10/07/2025 16:22:14 | [5 empty] | BARKAT ALI MAIN HILAL | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250902000232 | PCM-20250902-00000393 | TT-20250902-00476 | Telecom | Region_4 | JED0185 | JED0185 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 09/02/2025 05:12:06 | 10/07/2025 13:39:55 | 09/02/2025 17:12:06 | As per BO request NEC MW link JED0185_3(10.1.169.45) observing visibility down from itself SJED0295(10.1.169.44) is down from hub site | 09/02/2025 05:09:15 | Minor | 113388 | LOF | 09/02/2025 05:09:19 | P3 | 2G | jeddah | Sceco | TX NSA | JED0185_3 | FLM_TE | [8 empty] | API | 09/02/2025 05:12:06 | 09/07/2025 15:07:43 | 09/07/2025 15:22:49 | 09/07/2025 15:22:55 | 09/07/2025 15:22:58 |  |  |  | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902000925 | PCM-20250902-00001729 | TT-20250902-01725 | EM | Region_3 | RSP0034 | RSP0034 | Enviroment | SCECO_Failure | SCECO auto restored | Sayed Satoor | 09/02/2025 15:10:32 | 09/23/2025 17:48:13 | 09/02/2025 21:10:32 | Door opening alarm at RSP0034-P1-VIP_SRAN @ Generator_SG | 09/02/2025 15:09:54 | Major | 65101 | Door opening alarm | 09/02/2025 15:09:49 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0034 | FLM_EM | [8 empty] | API | 09/02/2025 15:10:32 | 09/23/2025 17:48:13 | [5 empty] | Sayed Satoor | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250902001189 | PCM-20250902-00002187 | TT-20250902-02100 | Reference_telecom | Region_6 | TNMW0142 | TNMW0142 |  |  |  | Fawad Khan | 09/02/2025 16:52:56 | 10/09/2025 14:32:25 | 09/03/2025 04:52:56 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A,LagPortDown- at TNMW0142_02-10.221.244.134 | 09/01/2025 17:49:44 | Minor |  | LOF | 09/01/2025 17:49:44 | P3 | 2G | namas | Sceco | TX NSA | TNMW0142_02-10.221.244.134 | FLM_TE | [8 empty] | API | 09/02/2025 16:52:56 | 09/02/2025 19:26:43 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250902001214 | PCM-20250902-00002212 | TT-20250902-02125 | Reference_telecom | Region_3 | RSP2800 | RSP2800 |  |  |  | Junaid Eisa | 09/02/2025 16:53:24 | 09/12/2025 08:06:48 | 09/03/2025 04:53:24 | MW RTN Observing RADIO_MUTE,RADIO_MUTE,RADIO_MUTE,RADIO_MUTE at RSP2800_NE_2 | 07/10/2025 12:47:04 | Minor |  | LOF | 07/10/2025 12:47:04 | VIP | SRAN | yanbu | Sceco | TX NSA | RSP2800_NE_2 | FLM_TE | [8 empty] | API | 09/02/2025 16:53:24 | [7 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902001234 | PCM-20250902-00002232 | TT-20250902-02144 | Reference_telecom | Region_1 | DMJR0662 | DMJR0662 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/02/2025 16:53:44 | 09/11/2025 12:51:57 | 09/03/2025 04:53:44 | NEC MW Observing LOF,RX Level,RX Level,LOF,LOF,RX Level,RX Level,LOF at DMJR0662-2(10.76.116.139) | 08/23/2025 03:53:28 | Minor |  | LOF | 08/23/2025 03:53:28 | P2 | SRAN | hafr | Generator_SG | TX NSA | DMJR0662-2(10.76.116.139) | FLM_TE | [8 empty] | API | 09/02/2025 16:53:44 | 09/02/2025 22:29:07 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250902001235 | PCM-20250902-00002233 | TT-20250902-02145 | Reference_telecom | Region_6 | DRB0903 | DRB0903 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 09/02/2025 16:53:45 | 09/30/2025 17:28:03 | 09/03/2025 04:53:45 | NEC MW Observing MODEM Power Supply Alarm at DRB0903(10.154.170.168) | 08/25/2025 20:05:55 | Minor |  | LOF | 08/25/2025 20:05:55 | P3 | 2G | derb | Generator_SG | TX NSA | DRB0903(10.154.170.168) | FLM_TE | [8 empty] | API | 09/02/2025 16:53:45 | 09/10/2025 05:24:31 | 09/30/2025 17:24:49 | 09/30/2025 17:25:00 | 09/30/2025 17:28:03 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902001275 | PCM-20250902-00002274 | TT-20250902-02186 | Reference_telecom | Region_6 | KHS0561 | KHS0561 |  |  |  | Walid Mohamad Fazil | 09/02/2025 16:54:28 | 09/08/2025 14:21:32 | 09/03/2025 04:54:28 | NEC MW Observing ODU CPU / Cable Open,ODU Power Supply at KHS0561-1(10.89.220.179) | 08/29/2025 05:52:48 | Minor |  | LOF | 08/29/2025 05:52:48 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KHS0561-1(10.89.220.179) | FLM_TE | [8 empty] | API | 09/02/2025 16:54:28 | 09/08/2025 14:21:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902001278 | PCM-20250902-00002277 | TT-20250902-02189 | Reference_telecom | Region_3 | MDN0740 | MDN0740 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 09/02/2025 16:54:32 | 09/16/2025 18:32:54 | 09/03/2025 04:54:32 | NEC MW Observing LOF,RX Level at MDN0740(10.1.222.106) | 08/30/2025 14:05:23 | Minor |  | LOF | 08/30/2025 14:05:23 | P1 | SRAN | madinah | Sceco | TX NSA | MDN0740(10.1.222.106) | FLM_TE | [8 empty] | API | 09/02/2025 16:54:32 | 09/02/2025 17:25:04 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250902001283 | PCM-20250902-00002283 | TT-20250902-02194 | Reference_telecom | Region_6 | NMS0095 | NMS0095 | Transsmission | MW_HW_fault | Replace Ethernet Cable | Fawad Khan | 09/02/2025 16:54:37 | 10/20/2025 00:57:49 | 09/03/2025 04:54:37 | NEC MW Observing LAN Link,LAN Link,ETH LOS,ETH LOS,LAG Link at NMS0095-1(10.154.171.181) | 08/22/2025 21:37:56 | Minor |  | LOF | 08/22/2025 21:37:56 | P1 | 2G | namas | Sceco | TX NSA | NMS0095-1(10.154.171.181) | FLM_TE | [8 empty] | API | 09/02/2025 16:54:37 | 10/09/2025 14:32:43 | 10/20/2025 00:56:57 |  |  | 10/20/2025 00:57:49 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902001289 | PCM-20250902-00002289 | TT-20250902-02200 | Reference_telecom | Region_6 | WDS9464 | WDS9464 |  |  |  | Mustafa Mohamed Abdelghani Elagami | 09/02/2025 16:54:44 | 09/30/2025 11:12:09 | 09/03/2025 04:54:44 | NEC MW Observing LAN Link at WDS9464(10.89.222.118) | 08/26/2025 10:26:30 | Minor |  | LOF | 08/26/2025 10:26:30 | P3 | Repeater | wadi dawasar | Generator_SG | TX NSA | WDS9464(10.89.222.118) | FLM_TE | [8 empty] | API | 09/02/2025 16:54:44 | 09/02/2025 17:09:45 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902001302 | PCM-20250902-00002302 | TT-20250902-02212 | Reference_telecom | Region_6 | WDS9463 | WDS9463 |  |  |  | Mustafa Mohamed Abdelghani Elagami | 09/02/2025 16:54:56 | 09/30/2025 11:12:09 | 09/03/2025 04:54:56 | NEC MW Observing LAN Link at WDS9463-1(10.89.222.119) | 08/22/2025 19:39:54 | Minor |  | LOF | 08/22/2025 19:39:54 | P3 | Repeater | wadi dawasar | Generator_SG | TX NSA | WDS9463-1(10.89.222.119) | FLM_TE | [8 empty] | API | 09/02/2025 16:54:56 | 09/02/2025 17:09:46 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250902001451 | PCM-20250902-00002576 | TT-20250902-02441 | Telecom | Region_1 | DMV0963 | DMV0963 |  |  |  | Muhammad Kashif M M Bashir | 09/02/2025 18:32:35 | 09/07/2025 14:13:58 | 09/03/2025 00:32:35 | BBU CPRI Optical Module or Electrical Port Not Ready at DMV0963-P2_SRAN @ Sceco | 09/02/2025 14:39:42 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 09/02/2025 14:36:34 | P2 | SRAN | hafouf | Sceco | 2G NSA | DMV0963 | FLM_TE | [8 empty] | API | 09/02/2025 18:32:35 | 09/03/2025 00:29:28 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250903000470 | PCM-20250903-00000755 | TT-20250903-00730 | Reference_telecom | Region_6 | TFBH0815 | TFBH0815 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 09/03/2025 08:06:51 | 10/11/2025 17:12:29 | 09/03/2025 20:06:51 | LagPortDown observed in TFBH0815_01 towards 10.10.143.242 @ Sceco | 09/02/2025 20:07:03 | Minor |  | LagPortDown | 09/02/2025 20:06:27 | P3 | 2G | makhwa | Sceco | TX NSA | TFBH0815 | FLM_TE | [8 empty] | API | 09/03/2025 08:06:51 | 09/03/2025 12:31:20 | 10/11/2025 16:32:34 | 10/11/2025 16:33:00 | 10/11/2025 16:33:04 | 10/11/2025 17:12:29 |  | SHAH KHALID | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250903000636 | PCM-20250903-00001036 | TT-20250903-01007 | Reference_telecom | Region_6 | ABH1U6700 | ABH6000 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Amir Sohail | 09/03/2025 10:56:09 | 09/03/2025 11:44:23 | 09/03/2025 16:56:09 | BASE STATION ANTENNA LINE PROBLEM (VSWR upper threshold exceeded) at ABH1U6700-G9-L18-SBTS-P3 (Ref:TT-20250825-01695) | 08/09/2025 21:26:14 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 08/09/2025 21:26:14 | P3 | 4G | abha | Sceco | LTE SA | ABH1U6700-G9-L18-SBTS-P3 | FLM_TE | [8 empty] | API | 09/03/2025 10:56:09 | 09/03/2025 11:42:51 | 09/03/2025 11:44:10 |  |  | 09/03/2025 11:44:23 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250903001256 | PCM-20250903-00002072 | TT-20250902-02139 | Reference_telecom | Region_1 | DAM0259 | DAM0259 |  |  |  | Imran Ali Yousaf | 09/03/2025 19:07:11 | 09/11/2025 12:51:57 | 09/04/2025 07:07:11 | NEC MW Observing MODEM Power Supply Alarm,MODEM Power Supply Alarm,RX Level,XIF,LOF,XIF at DAM0259_2(10.3.147.98) | 08/31/2025 00:02:01 | Minor |  | LOF | 08/31/2025 00:02:01 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0259_2(10.3.147.98) | FLM_TE |  |  | PCM-20250903-00002041 | kindly abort ticket from your side or update it under RO team | kindly abort ticket from your side or update it under RO team |  |  |  | API | 09/03/2025 19:07:11 | 09/03/2025 20:00:13 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250904000184 | PCM-20250904-00000393 | TT-20250904-00440 | Reference_telecom | Region_6 | TLM0131 | TLM0131 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 09/04/2025 04:18:56 | 10/11/2025 02:46:51 | 09/04/2025 16:18:56 | LossOfSignal observed in TLM0131_02 towards 10.10.137.41 @ Sceco | 09/03/2025 16:19:44 | Minor |  | LossOfSignal | 09/03/2025 16:18:52 | P1 | 2G | mohail | Sceco | TX NSA | TLM0131 | FLM_TE | [8 empty] | API | 09/04/2025 04:18:56 | 10/09/2025 15:37:54 | 10/11/2025 02:46:30 |  |  | 10/11/2025 02:46:51 |  | Muhammad Jamal Khan Abbas Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250904000342 | PCM-20250904-00000662 | TT-20250904-00709 | Reference_telecom | Region_6 | BSA2292 | BSA2292 |  |  |  | Saddam Hussain Shah Nawaz Khan | 09/04/2025 07:19:47 | 10/09/2025 14:32:27 | 09/04/2025 19:19:47 | ReplaceableUnitMissing observed in BSA2292_02- towards 10.1.232.60 @ Generator_SG | 09/03/2025 19:19:46 | Minor |  | ReplaceableUnitMissing | 09/03/2025 19:19:19 | P3 | 2G | bisha | Generator_SG | TX NSA | BSA2292 | FLM_TE | [8 empty] | API | 09/04/2025 07:19:47 | 09/04/2025 14:24:37 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250904000416 | PCM-20250904-00000779 | TT-20250904-00827 | Reference_telecom | Region_6 | THR0181 | THR0181 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Manzoor Ahmed | 09/04/2025 08:24:22 | 10/09/2025 16:26:56 | 09/04/2025 20:24:22 | DemFail observed in THR0181_02 towards 10.221.246.67 @ Sceco | 09/03/2025 20:25:57 | Minor |  | DemFail | 09/03/2025 20:24:11 | P3 | 2G | makhwa | Sceco | TX NSA | THR0181 | FLM_TE | [8 empty] | API | 09/04/2025 08:24:22 | 10/09/2025 16:25:40 | 10/09/2025 16:26:48 |  |  | 10/09/2025 16:26:56 |  | Manzoor Ahmed | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250904000661 | PCM-20250904-00001183 | TT-20250904-01188 | Telecom | Region_2 | RIYA6056 | RIYA6056 | Equipment | SFP_BTS | Replace SFP | Muhammad Waqas Ashraf Muhammad Ashraf | 09/04/2025 11:43:48 | 09/29/2025 12:05:35 | 09/04/2025 17:43:48 | RF Unit Optical Module Transmit/Receive Fault at RIYA6056-DCU2 @ Sceco | 09/04/2025 11:34:22 | Major | 26503 | RF Unit Optical Module Transmit/Receive Fault | 09/04/2025 11:37:00 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 09/04/2025 11:43:48 | 09/29/2025 12:05:35 | [5 empty] | Muhammad Waqas Ashraf Muhammad Ashraf | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250904000689 | PCM-20250904-00001226 | TT-20250904-01229 | Reference_EM | Region_1 | DMAP2U6160 | DMAP6060 | Enviroment | Air Condition | Change Fan | Ahmed Abdelfattah Ali Soltan | 09/04/2025 11:57:44 | 10/03/2025 01:56:17 | 09/04/2025 17:57:44 | Air-condition #1 failure alarm at DMAP2U6160-P1-VIP @ Sceco | 09/04/2025 11:47:27 | Major | 65104 | Air-condition #1 failure alarm | 09/04/2025 11:47:22 | VIP | 2G | dammam | Sceco | 2G NSA | DMAP2U6160 | FLM_EM | [8 empty] | API | 09/04/2025 11:57:44 | 09/04/2025 19:34:55 | 10/03/2025 01:56:09 |  |  | 10/03/2025 01:56:17 |  | Ahmed Abdelfattah Ali Soltan | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250904000855 | PCM-20250904-00001478 | TT-20250904-01466 | Telecom | Region_6 | NJR0019 | NJR0019 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Shahid Ali Roshan Ali | 09/04/2025 14:02:14 | 10/09/2025 14:47:35 | 09/05/2025 02:02:14 | ODU CPU / Cable Open at NJR0019-NJR0053 on 10.154.175.211 @ Sceco | 09/04/2025 14:01:37 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 09/04/2025 13:44:30 | P1 | 2G | najran | Sceco | TX NSA | NJR0019 | FLM_TE | [8 empty] | API | 09/04/2025 14:02:14 | 10/09/2025 14:47:35 | [5 empty] | Shahid Ali Roshan Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250904001189 | PCM-20250904-00001993 | TT-20250904-01995 | Reference_telecom | Region_1 | DAM0925 | DAM0925 |  |  |  | Imran Ali Yousaf | 09/04/2025 18:07:10 | 09/16/2025 19:14:10 | 09/05/2025 06:07:10 | NEC MW Observing Radio Traffic Aggregation Link,Radio Traffic Aggregation Link,RX Level,LOF,LOF,RX Level,LOF,RX Level,RX Level,LOF at DAM0925_2(10.158.150.145) | 03/05/2025 10:53:28 | Minor |  | LOF | 03/05/2025 10:53:28 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0925_2(10.158.150.145) | FLM_TE | [8 empty] | API | 09/04/2025 18:07:10 | 09/04/2025 18:08:59 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250904001202 | PCM-20250904-00002006 | TT-20250904-02008 | Reference_telecom | Region_1 | HFR2886 | HFR2886 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/04/2025 18:07:24 | 09/16/2025 19:14:11 | 09/05/2025 06:07:24 | NEC MW Observing LOF,Radio Traffic Aggregation Link,RX Level,LOF,RX Level,RX Level,RX Level,LOF,Radio Traffic Aggregation Link,LOF at HFR2886(10.74.80.178) | 08/02/2025 04:16:16 | Minor |  | LOF | 08/02/2025 04:16:16 | P2 | SRAN | hafr | Sceco | TX NSA | HFR2886(10.74.80.178) | FLM_TE | [8 empty] | API | 09/04/2025 18:07:24 | 09/04/2025 18:48:21 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250904001204 | PCM-20250904-00002008 | TT-20250904-02010 | Reference_telecom | Region_1 | JBKH0113 | JBKH0113 |  |  |  | Mohamed Abdelaziz | 09/04/2025 18:07:27 | 09/16/2025 19:14:11 | 09/05/2025 06:07:27 | NEC MW Observing Radio Traffic Aggregation Link at JBKH0113_3(10.101.186.18) | 08/23/2025 14:14:14 | Minor |  | LOF | 08/23/2025 14:14:14 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH0113_3(10.101.186.18) | FLM_TE | [8 empty] | API | 09/04/2025 18:07:27 | 09/04/2025 19:05:54 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250904001215 | PCM-20250904-00002019 | TT-20250904-02021 | Reference_telecom | Region_4 | JDRS0760 | JDRS0760 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Khizer Hayat | 09/04/2025 18:07:36 | 10/21/2025 21:36:30 | 09/05/2025 06:07:36 | NEC MW Observing TX Input at JDRS0760(10.154.114.6) | 09/03/2025 09:25:18 | Minor |  | LOF | 09/03/2025 09:25:18 | P2 | 2G | jeddah | Sceco | TX NSA | JDRS0760(10.154.114.6) | FLM_TE | [8 empty] | API | 09/04/2025 18:07:36 | 09/05/2025 08:56:43 | 10/21/2025 15:40:33 | 10/21/2025 15:40:36 | 10/21/2025 15:40:39 | 10/21/2025 21:36:30 |  | Khizer Hayat | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250904001230 | PCM-20250904-00002034 | TT-20250904-02036 | Reference_telecom | Region_6 | MHL0136 | MHL0136 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/04/2025 18:07:52 | 09/04/2025 18:09:33 | 09/05/2025 06:07:52 | NEC MW Observing LOF,RX Level,RX Level,LOF at MHL0136-1(10.157.250.21) | 09/03/2025 01:42:51 | Minor |  | LOF | 09/03/2025 01:42:51 | P3 | 2G | mohail | Sceco | TX NSA | MHL0136-1(10.157.250.21) | FLM_TE | [8 empty] | API | 09/04/2025 18:07:52 | 09/04/2025 18:09:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250904001236 | PCM-20250904-00002040 | TT-20250904-02042 | Reference_telecom | Region_6 | NJR0011 | NJR0011 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Shahid Ali Roshan Ali | 09/04/2025 18:07:59 | 10/19/2025 01:59:53 | 09/05/2025 06:07:59 | NEC MW Observing RX Level,LOF,LOF,RX Level at NJR0011_Access1(10.154.164.113) | 09/03/2025 00:19:52 | Minor |  | LOF | 09/03/2025 00:19:52 | P1 | 2G | najran | Sceco | TX NSA | NJR0011_Access1(10.154.164.113) | FLM_TE | [8 empty] | API | 09/04/2025 18:07:59 | 09/05/2025 01:33:34 | 10/19/2025 01:59:37 |  |  | 10/19/2025 01:59:53 |  | Shahid Ali Roshan Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250904001266 | PCM-20250904-00002070 | TT-20250904-02072 | Reference_telecom | Region_6 | WDS0771 | WDS0771 |  |  |  | Mustafa Mohamed Abdelghani Elagami | 09/04/2025 18:08:31 | 09/21/2025 11:31:19 | 09/05/2025 06:08:31 | NEC MW Observing SFP Type Mismatch,LOF,ODU CPU / Cable Open at WDS0771(10.89.222.163) | 09/03/2025 00:42:56 | Minor |  | LOF | 09/03/2025 00:42:56 | P3 | 2G | wadi dawasar | Generator_SG | TX NSA | WDS0771(10.89.222.163) | FLM_TE | [8 empty] | API | 09/04/2025 18:08:31 | 09/04/2025 19:21:23 | 09/21/2025 11:31:12 | 09/21/2025 11:31:15 | 09/21/2025 11:31:19 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250904001502 | PCM-20250904-00002460 | TT-20250904-02506 | Reference_telecom | Region_6 | NJR0213 | NJR0213 | Transsmission | MW_HW_fault | Remade Power Connector | Shahid Ali Roshan Ali | 09/04/2025 23:41:44 | 10/11/2025 16:36:03 | 09/05/2025 11:41:44 | LagPortDown observed in NJR0213_02 towards 10.221.248.5 @ Sceco | 09/04/2025 11:41:22 | Minor |  | LagPortDown | 09/04/2025 11:41:18 | P2 | 2G | najran | Sceco | TX NSA | NJR0213 | FLM_TE | [8 empty] | API | 09/04/2025 23:41:44 | 10/09/2025 14:47:34 | 10/11/2025 16:35:21 |  |  | 10/11/2025 16:36:03 |  | Shahid Ali Roshan Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250905000365 | PCM-20250905-00000565 | TT-20250904-02452 | Reference_telecom | Region_1 | DMJR0176 | DMJR0176 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SARFARAZ MUHAMMAD HUSSAIN | 09/05/2025 08:22:56 | 09/26/2025 13:37:35 | 09/05/2025 20:22:56 | BD_STATUS at DMJR0176_NE_1 @ Sceco_STB | 09/04/2025 16:16:12 | Minor | 1-119 | BD_STATUS | 09/04/2025 16:16:04 | P1 | SRAN | arar | Sceco_STB | TX NSA | DMJR0176 | FLM_TE |  |  | PCM-20250905-00000526 | Approved Item=52414341 | Approved Item=52414341 |  |  |  | API | 09/05/2025 08:22:56 | 09/16/2025 19:43:57 | 09/26/2025 13:33:37 |  |  | 09/26/2025 13:37:35 |  | SARFARAZ MUHAMMAD HUSSAIN | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250905000855 | PCM-20250905-00001353 | TT-20250905-01322 | Reference_telecom | Region_4 | JED2200 | JED2200 |  |  |  | Mohammed Ramadan A Abu Abid | 09/05/2025 17:38:26 | 10/07/2025 13:39:49 | 09/06/2025 05:38:26 | FanFailure observed in JED2200 towards 10.10.191.167 @ Sceco | 09/05/2025 05:39:33 | Minor |  | FanFailure | 09/05/2025 05:38:03 | VIP | 2G | jeddah | Sceco | TX NSA | JED2200 | FLM_TE | [8 empty] | API | 09/05/2025 17:38:26 | 09/05/2025 18:55:03 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250905000896 | PCM-20250905-00001425 | TT-20250905-01404 | MW_HC | Region_1 | KKM2163 | KKM2163 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/05/2025 18:29:56 | 09/22/2025 10:43:06 | 09/06/2025 06:29:56 | (as per BO request) NEC HC for performance issue at link KKM2163-HFR6098 | 09/05/2025 18:29:36 | Minor | 1-631 | MW_LOF | 09/05/2025 18:29:36 | P1 | SRAN | hafr | Sceco | TX NSA | KKM2163-HFR6098 | FLM_TE | [5 empty] | (as per BO request) NEC HC for performance issue at link KKM2163-HFR6098 |  |  | API | 09/05/2025 18:29:56 | 09/05/2025 19:44:13 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250905000898 | PCM-20250905-00001427 | TT-20250905-01407 | Telecom | Region_2 | SRIY0385 | SRIY0385 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 09/05/2025 18:32:52 | 10/21/2025 07:47:08 | 09/06/2025 06:32:52 | (As per BO request) SRIY0385_NE_2_(SRIY0386/SRIY0387) port 1/2 count error need to be changed | 09/05/2025 18:32:00 | Minor | 235 | ETH_LOS | 09/05/2025 18:32:00 | P3 | SRAN | riyadh | Sceco | TX NSA | SRIY0385_NE_2_(SRIY0386/SRIY0387) | FLM_TE | [5 empty] | (As per BO request) SRIY0385_NE_2_(SRIY0386/SRIY0387) port 1/2 count error need to be changed |  |  | API | 09/05/2025 18:32:52 | 09/06/2025 12:29:43 | 10/21/2025 07:46:49 |  |  | 10/21/2025 07:47:08 |  | Mubashar Farooq Abdul Majeed | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250906000046 | PCM-20250906-00000086 | TT-20250906-00074 | Reference_telecom | Region_6 | DUS0058 | DUS0058 | Transsmission | MW_HW_stuck | Reset Control Card | SHAH KHALID | 09/06/2025 01:05:04 | 10/09/2025 15:14:58 | 09/06/2025 13:05:04 | LagPortDown observed in DUS0058_01 towards 10.221.243.158 @ Sceco | 09/05/2025 13:06:30 | Minor |  | LagPortDown | 09/05/2025 13:04:52 | P3 | 2G | Albaha | Sceco | TX NSA | DUS0058 | FLM_TE | [8 empty] | API | 09/06/2025 01:05:04 | 10/09/2025 15:13:33 | 10/09/2025 15:14:14 |  |  | 10/09/2025 15:14:58 |  | SHAH KHALID | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250906000235 | PCM-20250906-00000380 | TT-20250906-00428 | Telecom | Region_2 | RIYB6005 | RIYB6005 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 09/06/2025 07:05:36 | 09/29/2025 11:11:38 | 09/06/2025 13:05:36 | BBU CPRI Interface Error at RIYB6005-P1-SHOP_SRAN @ Sceco | 09/06/2025 07:03:19 | Major | 26234 | BBU CPRI Interface Error | 09/06/2025 07:00:14 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYB6005 | FLM_TE | [8 empty] | API | 09/06/2025 07:05:36 | 09/06/2025 13:04:54 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250906000426 | PCM-20250906-00000687 | TT-20250906-00737 | Reference_telecom | Region_6 | BSA0446 | BSA0446 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Saddam Hussain Shah Nawaz Khan | 09/06/2025 10:51:55 | 10/19/2025 13:52:55 | 09/06/2025 22:51:55 | LossOfSignal observed in BSA0446_05 towards 10.221.245.204 @ Sceco | 09/05/2025 22:52:27 | Minor |  | LossOfSignal | 09/05/2025 22:51:45 | P3 | 2G | bisha | Sceco | TX NSA | BSA0446 | FLM_TE | [8 empty] | API | 09/06/2025 10:51:55 | 09/06/2025 11:43:17 | 10/19/2025 13:52:21 |  |  | 10/19/2025 13:52:55 |  | Saddam Hussain Shah Nawaz Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250906000585 | PCM-20250906-00000944 | TT-20250906-00960 | Reference_telecom | Region_6 | ABBS2235 | ABBS2235 |  |  |  | Fawad Khan | 09/06/2025 12:52:06 | 10/09/2025 14:32:28 | 09/07/2025 00:52:06 | InternalCommunicationProblem observed in ABBS2235 towards 10.74.122.4 @ Sceco | 09/06/2025 00:51:56 | Minor |  | InternalCommunicationProblem | 09/06/2025 00:51:52 | P3 | 2G | Albaha | Sceco | TX NSA | ABBS2235 | FLM_TE | [8 empty] | API | 09/06/2025 12:52:06 | 09/06/2025 15:13:15 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20240526000296 | PCM-20240526-00000411 | TT-20240526-00400 | EM | Region_1 | DAM0229 | DAM0229 | Enviroment | Air Condition | Change Fan | Abdul Malik Shaik | 05/26/2024 02:48:14 | 06/10/2024 03:33:41 | 05/26/2024 06:48:14 | Air condition 3 failure alarm at DAM0229-P1-SHOP-HUB-WDM_SRAN @ Sceco | 05/26/2024 02:46:11 | Critical | 65117 | Air condition 3 failure alarm | 05/26/2024 02:30:02 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0229 | FLM_EM | [8 empty] | API | 05/26/2024 02:48:14 | 06/09/2024 22:36:23 | 06/10/2024 03:21:50 | 06/10/2024 03:21:53 | 06/10/2024 03:21:56 | 06/10/2024 03:33:41 |  | Abdul Malik Shaik | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20240818000575 | PCM-20240818-00000815 | TT-20240818-00958 | EM | Region_4 | RAD9419 | RAD9419 |  |  |  | Mohamed Ibrahim Mohamed Batn | 08/18/2024 08:37:38 | 09/07/2024 15:27:37 | 08/18/2024 12:37:38 | GEN FAILURE+MAIN PWR FAIL (Input-3) at RAD9419 on 10.88.222.146 @ Generator_SG | 08/18/2024 08:32:17 | Critical | GEN FAILURE+MAIN PWR FAIL (Input-3) | GEN FAILURE+MAIN PWR FAIL (Input-3) | 08/18/2024 08:31:59 | P3 | Repeater | alaith | Generator_SG | TX NSA | RAD9419 | FLM_EM | [8 empty] | API | 08/18/2024 08:37:38 | 08/19/2024 08:16:05 | [6 empty] | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20240928001402 | PCM-20240928-00001818 | TT-20240928-01810 | EM | Region_4 | KMMD9063 | KMMD9063 |  |  |  | Muhammad Masoof Zafar Mehmood | 09/28/2024 18:44:55 | 10/04/2024 18:07:56 | 09/28/2024 22:44:55 | gen & Main AC Failure (INPUT-5) (Input-4) at KMMD9063 on 10.154.115.73 @ Sceco_STB | 09/28/2024 18:43:11 | Critical | gen & Main AC Failure (INPUT-5) (Input-4) | gen & Main AC Failure (INPUT-5) (Input-4) | 09/28/2024 18:33:45 | P3 | Repeater | jeddah | Sceco_STB | TX NSA | KMMD9063 | FLM_EM | [8 empty] | API | 09/28/2024 18:44:55 | 09/29/2024 10:56:51 | [6 empty] | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20241116000856 | PCM-20241116-00001077 | TT-20241116-01246 | Reference_EM | Region_1 | HFF0015 | HFF0015 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 11/16/2024 13:40:00 | 11/30/2024 19:30:51 | 11/17/2024 01:40:00 | Air condition 3 failure alarm at HFF0015-P2_SRAN @ Sceco | 11/16/2024 13:29:35 | Minor | 65117 | Air condition 3 failure alarm | 11/16/2024 13:29:31 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0015 | FLM_EM | [8 empty] | API | 11/16/2024 13:40:00 | 11/30/2024 19:29:03 | 11/30/2024 19:30:42 |  |  | 11/30/2024 19:30:51 |  | Shahid Khan Dilawar Khan | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250105001667 | PCM-20250105-00002169 | TT-20250105-02378 | Reference_EM | Region_1 | JBL2138 | JBL2138 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Mossad Tawfik Saad | 01/05/2025 20:48:34 | 01/26/2025 17:19:19 | 01/06/2025 08:48:34 | Low battery voltage at JBL2M2138-P3 @ Generator_SG | 01/05/2025 20:38:11 | Minor | 65110 | Low battery voltage | 01/05/2025 20:38:06 | P3 | 2G | jubail | Generator_SG | 2G NSA | JBL2M2138 | FLM_EM | [8 empty] | API | 01/05/2025 20:48:34 | 01/05/2025 22:04:12 | 01/26/2025 17:19:10 |  |  | 01/26/2025 17:19:19 |  | Mohamed Mossad Tawfik Saad | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250105001747 | PCM-20250105-00002270 | TT-20250105-02466 | EM | Region_1 | JBL2138 | JBL2138 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Mossad Tawfik Saad | 01/05/2025 22:45:44 | 05/03/2025 15:06:53 | 01/06/2025 04:45:44 | 1(2G/3G/LTE) sites down under JBL2138-P3/R1_JB_HWBSC01 @ Generator_SG | 01/05/2025 22:38:37 | Major | 21807 | OML Fault | 01/05/2025 22:38:30 | P3 | 2G | jubail | Generator_SG | 2G_3G_LTE SA | JBL2138-P3 | FLM_EM | [6 empty] | sites down |  | API | 01/05/2025 22:45:44 | 01/06/2025 08:29:58 | 05/03/2025 15:06:47 |  |  | 05/03/2025 15:06:53 |  | Mohamed Mossad Tawfik Saad | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250113000523 | PCM-20250113-00000741 | TT-20250113-00966 | Reference_telecom | Region_4 | JED0609 | JED0609 |  |  |  | Ramadan Mohamed Sabri Mohamed | 01/13/2025 09:09:59 | 01/13/2025 23:27:23 | 01/13/2025 15:09:59 | MW_ Router MW_ JED0189 to JED0245 _ ISIS Adjacency changed REF TT-20241021-00084 | 01/13/2025 08:35:59 | Major | 2738181 | Link down flapping | 01/13/2025 08:35:59 | P2 | 2G | jeddah | Sceco | IPRAN NSA | MW_ Router MW_ JED0189 to JED0245 _ ISIS Adjacency changed REF TT-20241021-00084 | FLM_EM |  | Scattered sites, Site Name HUB REMARK JED2788-P3 JED2037 RSL down and suspected power at HUB, kindly send team to check and fix the issue JED0609-P2 JED0609 RSL down and suspected power at HUB, kindly send team to check and fix the issue JED2037 JED2037 RSL down and suspected power at HUB, kindly send team to check and fix the issue | PCM-20250113-00000729 | Scattered sites, Site Name HUB REMARK JED2788-P3 JED2037 RSL down and suspected power at HUB, kindly send team to check and fix the issue JED0609-P2 JED0609 RSL down and suspected power at HUB, kindly send team to check and fix the issue JED2037 JED2037 RSL down and suspected power at HUB, kindly send team to check and fix the issue | Scattered sites, Site Name HUB REMARK JED2788-P3 JED2037 RSL down and suspected power at HUB, kindly send team to check and fix the issue JED0609-P2 JED0609 RSL down and suspected power at HUB, kindly send team to check and fix the issue JED2037 JED2037 RSL down and suspected power at HUB, kindly send team to check and fix the issue |  |  |  | API | 01/13/2025 09:09:59 | 01/13/2025 23:27:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250203001085 | PCM-20250203-00001398 | TT-20250203-01505 | Reference_EM | Region_2 | RIY2719 | RIY2719 |  |  |  | Hosameldin Mohamed Elzohri Hamed | 02/03/2025 14:44:24 | 03/26/2025 16:08:27 | 02/03/2025 20:44:24 | high temprature 40 at RIY2719-P1-VIP_SRAN @ Generator_SG | 02/03/2025 14:34:07 | Major | 65103 | high temprature 40 | 02/03/2025 14:34:04 | P1 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2719 | FLM_EM | [8 empty] | API | 02/03/2025 14:44:24 | 02/03/2025 16:22:01 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250215000581 | PCM-20250215-00000830 | TT-20250215-00867 | EM | Region_4 | MKJD0649 | MKJD0649 |  |  |  | Muhammad Arqam Muhammad Dawood | 02/15/2025 11:32:14 | 02/16/2025 19:45:19 | 02/15/2025 17:32:14 | 1(2G/LTE) sites down under MKJD0649-P3 @ Sceco | 02/15/2025 11:23:44 | Major | 7706 | BTS O&M LINK FAILURE | 02/15/2025 11:23:40 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | MKJD0649-P3 | FLM_EM | [6 empty] | sites down |  | API | 02/15/2025 11:32:14 | 02/16/2025 19:45:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250320001486 | PCM-20250320-00002168 | TT-20250320-02177 | EM | Region_2 | RYMK9001 | RYMK9001 | Enviroment | SCECO_Failure | SCECO auto restored | Saleem Khan Amir Dost | 03/20/2025 18:40:25 | 04/21/2025 20:37:44 | 03/20/2025 22:40:25 | RELAY_ALARM_CRITICAL AT RYMK9001_NE_3_ExternalAlarms2 | 03/20/2025 18:06:30 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 03/20/2025 18:39:24 | P3 | Repeater | quweyah | Sceco | TX NSA | RYMK9001_NE_3 | FLM_EM | [5 empty] | RELAY_ALARM_CRITICAL AT RYMK9001_NE_3_ExternalAlarms2 10-AUX-DOOR Alarm |  |  | API | 03/20/2025 18:40:25 | 04/20/2025 14:24:50 | 04/21/2025 20:37:36 |  |  | 04/21/2025 20:37:44 |  | Saleem Khan Amir Dost | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250421000713 | PCM-20250421-00001074 | TT-20250421-01118 | Reference_EM | Region_2 | RIY2486 | RIY2486 |  |  |  | Amr Abbas Zaghloul Abbas | 04/21/2025 12:09:04 | 09/19/2025 11:37:57 | 04/21/2025 18:09:04 | 1(2G/LTE) sites down under RIY2486-P3-VIP-RIYSEASON/R2_RY1_HWBSC01 @ Generator_SG (Ref:TT-20240131-00081) | 01/31/2024 01:13:03 | Major | 21825 | CSL Fault | 01/31/2024 01:13:03 | P3 | SRAN | riyadh | Generator_SG | 2G_LTE SA | RIY2486 | FLM_EM |  | Results: DOWN SITE HUB RIY2486 RIY2486 Summary: Hub: RIY2486, Down Count: 1, Down Sites: RIY2486 Alarm Summary: RIY2486 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 04/21/2025 12:09:04 | 04/21/2025 12:49:25 | [6 empty] | Relocation_RO |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250429000618 | PCM-20250429-00000953 | TT-20250429-00952 | EM | Region_1 | KBR0162 | KBR0162 |  |  |  | Ibrahim said mohamed Elmarhoumy | 04/29/2025 10:04:25 | 05/05/2025 12:56:52 | 04/29/2025 22:04:25 | Air condition 3 failure alarm at KBR0162-P3_SRAN @ Sceco | 04/29/2025 09:57:42 | Minor | 65117 | Air condition 3 failure alarm | 04/29/2025 09:53:44 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0162 | FLM_EM | [8 empty] | API | 04/29/2025 10:04:25 | 04/29/2025 21:53:45 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250512001513 | PCM-20250512-00002237 | TT-20250512-02076 | EM | Region_3 | HAL0922 | HAL0922 | Enviroment | SCECO_Failure | SCECO auto restored | Sami Mohammed Jad Shahatah | 05/12/2025 15:52:26 | 05/16/2025 17:23:24 | 05/13/2025 03:52:26 | Air condition 2 failure alarm at HAL0922-P3_SRAN @ Sceco | 05/12/2025 15:44:33 | Minor | 65105 | Air condition 2 failure alarm | 05/12/2025 15:41:52 | P3 | SRAN | hail | Sceco | 2G NSA | HAL0922 | FLM_EM | [8 empty] | API | 05/12/2025 15:52:26 | 05/16/2025 17:22:24 | 05/16/2025 17:23:18 |  |  | 05/16/2025 17:23:24 |  | Sami Mohammed Jad Shahatah | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250518000022 | PCM-20250518-00000026 | TT-20250518-00024 | EM | Region_1 | HFF0008 | HFF0008 |  |  |  | Ibrahim said mohamed Elmarhoumy | 05/18/2025 00:06:02 | 05/29/2025 10:40:03 | 05/18/2025 12:06:02 | Air condition 3 failure alarm at HFF0008-P2_SRAN @ Sceco | 05/18/2025 00:03:57 | Minor | 65117 | Air condition 3 failure alarm | 11/03/2024 07:03:25 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0008 | FLM_EM | [8 empty] | API | 05/18/2025 00:06:02 | 05/19/2025 12:11:00 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250518000023 | PCM-20250518-00000027 | TT-20250518-00025 | EM | Region_1 | HFF0016 | HFF0016 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 05/18/2025 00:06:02 | 05/31/2025 10:27:10 | 05/18/2025 06:06:02 | Air condition 3 failure alarm at HFF0016-P1-HUB_SRAN @ Sceco | 05/18/2025 00:03:40 | Major | 65117 | Air condition 3 failure alarm | 01/22/2025 17:01:04 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFF0016 | FLM_EM | [8 empty] | API | 05/18/2025 00:06:02 | 05/29/2025 13:20:13 | 05/31/2025 10:27:01 |  |  | 05/31/2025 10:27:10 |  | Shahid Khan Dilawar Khan | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250518000024 | PCM-20250518-00000025 | TT-20250518-00023 | EM | Region_1 | HFF0021 | HFF0021 | Transsmission | MW_loop | Remote action done by BO by removing VLAN loop | Shahid Khan Dilawar Khan | 05/18/2025 00:06:03 | 05/31/2025 10:27:22 | 05/18/2025 12:06:03 | Air condition 3 failure alarm at HFF0021-P2_SRAN @ Sceco | 05/18/2025 00:03:40 | Minor | 65117 | Air condition 3 failure alarm | 01/20/2025 22:34:10 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0021 | FLM_EM | [8 empty] | API | 05/18/2025 00:06:03 | 05/29/2025 13:20:13 | 05/31/2025 10:27:15 |  |  | 05/31/2025 10:27:22 |  | Shahid Khan Dilawar Khan | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250518000025 | PCM-20250518-00000033 | TT-20250518-00031 | EM | Region_1 | DRN0129 | DRN0129 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 05/18/2025 00:06:05 | 05/31/2025 23:02:30 | 05/18/2025 04:06:05 | Air condition 3 failure alarm at DRN0129-P1-HUB-WDM_SRAN-FON @ Sceco | 05/18/2025 00:03:40 | Critical | 65117 | Air condition 3 failure alarm | 01/14/2025 02:23:53 | P1 | SRAN | dammam | Sceco | 2G NSA | DRN0129 | FLM_EM | [8 empty] | API | 05/18/2025 00:06:05 | 05/31/2025 22:55:51 | 05/31/2025 23:02:18 |  |  | 05/31/2025 23:02:30 |  | Ahmed AbdELmoaz Ibrahim | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Reject_FME | CM20250604000654 | PCM-20250604-00000992 | TT-20250604-01264 | EM | Region_1 | JBKH0132 | JBKH0132 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 06/04/2025 12:26:01 | 07/14/2025 05:17:41 | 06/05/2025 00:26:01 | NETECO: Maintenance Reminder at JBKH0132 @ Generator_SG | 06/04/2025 12:19:24 | Minor | 40563 | Maintenance Reminder | 06/04/2025 12:19:24 | P3 | SRAN | khafji | Generator_SG | 2G NSA | JBKH0132 | FLM_EM | [8 empty] | API | 06/04/2025 12:26:01 | 07/02/2025 03:07:45 | [6 empty] | Huawei_RO |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250616001880 | PCM-20250616-00002606 | TT-20250616-02819 | Reference_EM | Region_2 | RIY0274 | RIY0274 |  |  |  | RANJEET KUMAR YADAV | 06/16/2025 21:05:06 | 06/30/2025 13:08:22 | 06/17/2025 09:05:06 | Mains Failure at RIY0274-P3_SRAN @ Generator_SG | 06/16/2025 20:54:52 | Minor | 65109 | Mains Failure | 06/16/2025 20:54:48 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0274 | FLM_EM | [8 empty] | API | 06/16/2025 21:05:06 | 06/17/2025 14:36:17 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250616002062 | PCM-20250616-00002875 | TT-20250616-03062 | EM | Region_2 | RIY0274 | RIY0274 |  |  |  | RANJEET KUMAR YADAV | 06/16/2025 23:59:10 | 06/17/2025 14:36:18 | 06/17/2025 05:59:10 | 1(2G/LTE) sites down under RIY0274-P3/R2_RY1_HWBSC01 @ Generator_SG | 06/16/2025 23:50:46 | Major | 21825 | CSL Fault | 06/16/2025 23:50:43 | P3 | 2G | riyadh | Generator_SG | 2G_LTE SA | RIY0274-P3 | FLM_EM |  | Results: DOWN SITE HUB RIY0274-P3 RIY0274 Summary: Hub: RIY0274, Down Count: 1, Down Sites: RIY0274-P3 Alarm Summary: RIY0274 Alarm Active on HUB |  |  |  |  | sites down |  | API | 06/16/2025 23:59:10 | 06/17/2025 14:36:18 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250625000979 | PCM-20250625-00001495 | TT-20250625-01592 | EM | Region_2 | MSJ0147 | MSJ0147 | Enviroment | SCECO_Failure | SCECO auto restored | Shahid Ahmed Shah Nawaz | 06/25/2025 14:37:25 | 10/03/2025 23:10:51 | 06/26/2025 02:37:25 | ( AS PER BO REQUSET ) Huawei HC for observing bad performance at link MSJ0147 - LYM0202 | 06/25/2025 14:34:40 | Minor | 1-631 | MW_LOF | 06/25/2025 14:34:42 | P3 | SRAN | al rass | Sceco | TX NSA | MSJ0147 - LYM0202 | FLM_EM | [5 empty] | ( AS PER BO REQUSET ) Huawei HC for observing bad performance at link MSJ0147 - LYM0202 |  |  | API | 06/25/2025 14:37:25 | 10/03/2025 10:46:56 | 10/03/2025 10:54:52 | 10/03/2025 10:54:54 |  | 10/03/2025 23:10:51 |  | Shahid Ahmed Shah Nawaz |  |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250707000031 | PCM-20250707-00000045 | TT-20250707-00051 | EM | Region_3 | MDN0876 | MDN0876 |  |  |  | Arslan Mustafa Ghulam Mustafa | 07/07/2025 00:39:30 | 07/14/2025 12:49:05 | 07/07/2025 12:39:30 | Air condition 1 failure alarm at MDN0876-P2_SRAN @ Sceco | 07/07/2025 00:32:22 | Minor | 65104 | Air condition 1 failure alarm | 07/07/2025 00:29:08 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0876 | FLM_EM | [8 empty] | API | 07/07/2025 00:39:30 | 07/07/2025 00:39:37 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250708001115 | PCM-20250708-00001755 | TT-20250708-01784 | Reference_EM | Region_3 | MKMD0318 | MKMD0318 |  |  |  | Muhamad Hanif Ahmad | 07/08/2025 13:12:25 | 07/14/2025 12:49:11 | 07/08/2025 19:12:25 | Air condition 1 failure alarm at MKMD0318-P1-HUB_SRAN @ Sceco | 07/08/2025 13:01:47 | Major | 65104 | Air condition 1 failure alarm | 07/08/2025 13:01:41 | P1 | SRAN | madinah | Sceco | 2G NSA | MKMD0318 | FLM_EM | [8 empty] | API | 07/08/2025 13:12:25 | 07/08/2025 21:46:12 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250709001259 | PCM-20250709-00001758 | TT-20250709-01890 | EM | Region_3 | MDN0802 | MDN0802 |  |  |  | Muhamad Hanif Ahmad | 07/09/2025 17:21:20 | 07/14/2025 12:49:16 | 07/09/2025 21:21:20 | Air condition 2 failure alarm at MDN0802-P1-HUB-WDM_SRAN-FON @ Sceco | 07/09/2025 17:19:16 | Critical | 65105 | Air condition 2 failure alarm | 07/09/2025 17:19:11 | P1 | SRAN | madinah | Sceco | 2G NSA | MDN0802 | FLM_EM | [8 empty] | API | 07/09/2025 17:21:20 | 07/09/2025 19:07:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250710001285 | PCM-20250710-00001793 | TT-20250710-01824 | Reference_EM | Region_3 | MDN0748 | MDN0748 | Enviroment | Rectifier Module | Change rectifer module | Muhamad Hanif Ahmad | 07/10/2025 18:55:14 | 07/14/2025 14:57:23 | 07/11/2025 06:55:14 | Air condition 2 failure alarm at MDN0748-P2_SRAN @ Sceco | 07/10/2025 18:44:28 | Minor | 65105 | Air condition 2 failure alarm | 07/10/2025 18:44:24 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0748 | FLM_EM | [8 empty] | API | 07/10/2025 18:55:14 | 07/14/2025 14:57:23 | [5 empty] | Muhamad Hanif Ahmad | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250713000140 | PCM-20250713-00000217 | TT-20250713-00229 | EM | Region_4 | TAF0138 | TAF0138 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 07/13/2025 02:40:40 | 08/30/2025 00:49:58 | 07/13/2025 14:40:40 | RECTIFIER LOW/HIGH BATTERY VOLTAGE at TAF1M7138-CA-L800-P3 @ Sceco | 07/13/2025 02:34:46 | Minor | 7103 | RECTIFIER LOW/HIGH BATTERY VOLTAGE | 07/13/2025 02:31:52 | P2 | 4G | taif | Sceco | LTE NSA | TAF1M7138 | FLM_EM | [5 empty] | RECTIFIER LOW/HIGH BATTERY VOLTAGE |  |  | API | 07/13/2025 02:40:40 | 07/13/2025 10:10:23 | 08/30/2025 00:49:51 |  |  | 08/30/2025 00:49:58 |  | Farghal Ashour Hassan Farghal | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250713000173 | PCM-20250713-00000273 | TT-20250713-00274 | EM | Region_4 | TAF0142 | TAF0142 |  |  |  | Walid Magdy Tawfik Elbana | 07/13/2025 03:15:51 | 08/06/2025 11:52:51 | 07/13/2025 15:15:51 | AIRCON 1 FAILURE at TAF0142-GSM-P3 @ Sceco | 07/13/2025 03:07:15 | Minor | 7103 | AIRCON 1 FAILURE | 07/13/2025 03:07:07 | P3 | 2G | taif | Sceco | 2G NSA | TAF0142 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 07/13/2025 03:15:51 | 07/13/2025 04:44:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Preparation | CM20250715000683 | PCM-20250715-00000988 | TT-20250715-00958 | EM | Region_4 | JED0603 | JED0603 |  |  |  | Muhammad Arqam Muhammad Dawood | 07/15/2025 11:19:11 | 08/05/2025 12:36:30 | 07/15/2025 23:19:11 | SHELTER DOOR OPEN at JED1M7603-CA-L900-L800-SBTS @ Sceco | 07/15/2025 11:18:40 | Minor | 7103 | SHELTER DOOR OPEN | 07/15/2025 11:18:29 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7603 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 07/15/2025 11:19:11 | 08/01/2025 10:37:16 | 08/01/2025 13:19:14 | 08/01/2025 13:19:16 | 08/01/2025 13:19:18 |  |  |  | SCECO |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250720000571 | PCM-20250720-00000853 | TT-20250720-00846 | EM | Region_4 | AQA9452 | AQA9452 |  |  |  | Mohamed Ahmed Kassem Embarak | 07/20/2025 09:52:45 | 08/03/2025 09:28:38 | 07/20/2025 13:52:45 | AIR condition failure(Input) and GEN FAIL+REC MAIN POWER(Input) AQA9452 http:(10.88.221.6) | 07/20/2025 08:20:11 | Critical | MAIN AC + GEN FAILURE (Input-4) | MAIN AC + GEN FAILURE (Input-4) | 07/20/2025 08:10:11 | P1 | Repeater | taif | Generator_DG | TX NSA | RYAB9008 | FLM_EM | [5 empty] | AIR condition failure(Input) and GEN FAIL+REC MAIN POWER(Input) AQA9452 http:(10.88.221.6) |  |  | API | 07/20/2025 09:52:45 | 07/21/2025 12:28:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250721001454 | PCM-20250721-00002373 | TT-20250721-02301 | EM | Region_1 | KBR0173 | KBR0173 |  |  |  | Abdul Malik Shaik | 07/21/2025 19:57:25 | 08/05/2025 12:36:20 | 07/22/2025 07:57:25 | Air condition 3 failure alarm at KBR0173-P3_SRAN @ Sceco | 07/21/2025 19:51:23 | Minor | 65117 | Air condition 3 failure alarm | 07/21/2025 19:47:09 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0173 | FLM_EM | [8 empty] | API | 07/21/2025 19:57:25 | 07/30/2025 02:22:03 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250722000083 | PCM-20250722-00000130 | TT-20250722-00160 | EM | Region_3 | MDTB0339 | MDTB0339 | Enviroment | SCECO_Failure | SCECO auto restored | Muhamed Ismail Muhamed Daoud | 07/22/2025 01:43:45 | 08/10/2025 13:08:15 | 07/22/2025 05:43:45 | INTRUDER ALARM (INPUT-1) Observed at rep(4780-4781)-MDTB2M53 | 07/22/2025 01:37:24 | Critical | 1-631 | MW_LOF | 07/22/2025 01:37:24 | P1 | 2G | madinah | Sceco_STB | TX NSA | MDTB2M5339 | FLM_EM | [5 empty] | INTRUDER ALARM (INPUT-1) Observed at rep(4780-4781)-MDTB2M5339 |  |  | API | 07/22/2025 01:43:45 | 08/09/2025 15:56:59 | 08/10/2025 13:07:57 |  |  | 08/10/2025 13:08:15 |  | Muhamed Ismail Muhamed Daoud | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250723000884 | PCM-20250723-00001379 | TT-20250723-01405 | EM | Region_6 | TLT9478 | TLT9478 | Enviroment | SCECO_Failure | SCECO auto restored | Amir Arif Ali | 07/23/2025 14:23:30 | 09/08/2025 14:46:31 | 07/23/2025 18:23:30 | NEC Eband observing Door open & AC alarm at TLT9478 | 07/23/2025 14:12:25 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 07/23/2025 14:12:25 | P1 | Repeater | turaib | Generator_DG | TX NSA | TLT9478 | FLM_EM | [5 empty] | NEC Eband observing Door open & AC alarm at TLT9478 |  |  | API | 07/23/2025 14:23:30 | 07/23/2025 19:56:18 | 09/08/2025 14:46:16 |  |  | 09/08/2025 14:46:31 |  | Amir Arif Ali | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250726000789 | PCM-20250726-00001083 | TT-20250726-01161 | EM | Region_4 | JZMA9072 | JZMA9072 | Enviroment | Rectifier Module | Adding module due to load issue | Subair Mannayath Moidutty Mannayath | 07/26/2025 13:56:05 | 07/26/2025 14:54:52 | 07/26/2025 17:56:05 | Door Open (Input-2) at JZMA9072 on 10.154.125.178 @ Sceco_STB | 07/26/2025 13:54:10 | Critical | Door Open (Input-2) | Door Open (Input-2) | 07/26/2025 13:48:14 | P3 | Repeater | qunfuddah | Sceco_STB | TX NSA | JZMA9072 | FLM_EM | [8 empty] | API | 07/26/2025 13:56:05 | 07/26/2025 14:18:38 | 07/26/2025 14:18:43 | 07/26/2025 14:18:47 |  | 07/26/2025 14:54:52 |  | Subair Mannayath Moidutty Mannayath |  |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250727000287 | PCM-20250727-00000414 | TT-20250727-00424 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 07/27/2025 06:01:46 | 08/05/2025 18:47:18 | 07/27/2025 18:01:46 | NETECO: Maintenance Reminder at JBK9910 @ Generator_SG | 07/27/2025 05:55:10 | Minor | 40563 | Maintenance Reminder | 07/27/2025 05:55:10 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 07/27/2025 06:01:46 | 08/05/2025 15:01:49 | 08/05/2025 18:47:06 |  |  | 08/05/2025 18:47:18 |  | Imran Qamar Ghulam Qamar | Huawei_RO |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250727001092 | PCM-20250727-00001484 | TT-20250727-01448 | EM | Region_4 | JZMA9072 | JZMA9072 |  |  |  | Subair Mannayath Moidutty Mannayath | 07/27/2025 14:51:16 | 07/27/2025 23:12:45 | 07/27/2025 18:51:16 | High Temp 32 + High Temp 40 (Input-5) at JZMA9072 on 10.154.125.178 @ Sceco_STB | 07/27/2025 14:49:27 | Critical | High Temp 32 + High Temp 40 (Input-5) | High Temp 32 + High Temp 40 (Input-5) | 07/27/2025 14:43:31 | P3 | Repeater | qunfuddah | Sceco_STB | TX NSA | JZMA9072 | FLM_EM | [8 empty] | API | 07/27/2025 14:51:16 | 07/27/2025 23:12:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur
Preparation | CM20250731001226 | PCM-20250731-00001773 | TT-20250731-01770 | EM | Region_4 | JZMA9072 | JZMA9072 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 07/31/2025 15:56:15 | 08/05/2025 12:36:48 | 07/31/2025 19:56:15 | Low Battery + Voltage Alarm (Input-6) at JZMA9072 on 10.154.125.178 @ Sceco_STB | 07/31/2025 15:54:23 | Critical | Low Battery + Voltage Alarm (Input-6) | Low Battery + Voltage Alarm (Input-6) | 07/31/2025 15:48:26 | P3 | Repeater | qunfuddah | Sceco_STB | TX NSA | JZMA9072 | FLM_EM | [8 empty] | API | 07/31/2025 15:56:15 | 08/03/2025 13:37:11 | 08/03/2025 13:38:51 | 08/03/2025 13:38:55 | 08/03/2025 13:54:11 |  |  |  | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250803000132 | PCM-20250803-00000204 | TT-20250803-00203 | EM | Region_5 | MAK0100 | MAK0100 |  |  |  | Ibrahim Ibrahim Mohamed Ismail | 08/03/2025 03:01:00 | 08/04/2025 13:28:17 | 08/03/2025 09:01:00 | AIRCON 1 FAILURE at MAK0100-G9-L800-L18-L21-NR2.6-SBTS-P1-HUB-NEW @ Sceco_STB | 08/03/2025 02:53:01 | Major | 7103 | AIRCON 1 FAILURE | 08/03/2025 02:52:39 | P1 | 2G | makkah | Sceco_STB | 2G NSA | MAK0100 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/03/2025 03:01:00 | 08/03/2025 17:14:48 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250803000144 | PCM-20250803-00000222 | TT-20250803-00221 | EM | Region_5 | MAK0085 | MAK0085 |  |  |  | Atif Javed Javed Hussain | 08/03/2025 03:15:01 | 08/04/2025 13:28:09 | 08/03/2025 15:15:01 | AIRCON 2 FAILURE at MAK1M9085-CA-L800-SBTS @ Sceco | 08/03/2025 03:07:19 | Minor | 7103 | AIRCON 2 FAILURE | 08/03/2025 03:06:15 | P3 | 4G | makkah | Sceco | LTE NSA | MAK1M9085 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/03/2025 03:15:01 | 08/03/2025 09:52:57 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250803000166 | PCM-20250803-00000249 | TT-20250803-00248 | EM | Region_5 | MAK0241 | MAK0241 |  |  |  | Ezz Ismaeal Mahmoud Sayed | 08/03/2025 03:31:31 | 08/04/2025 13:28:06 | 08/03/2025 15:31:31 | AIRCON 1 FAILURE at MAK0241-G9-NL8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 08/03/2025 03:23:24 | Minor | 7103 | AIRCON 1 FAILURE | 08/03/2025 03:23:00 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0241 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/03/2025 03:31:31 | 08/03/2025 03:31:54 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250804000121 | PCM-20250804-00000215 | TT-20250804-00260 | EM | Region_4 | TUR0681 | TUR0681 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 08/04/2025 02:36:11 | 08/22/2025 14:22:37 | 08/04/2025 14:36:11 | RECTIFIER MODULE FAILURE at TUR1M7681-NCA-L800-SBTS @ Sceco | 08/04/2025 02:30:55 | Minor | 7103 | RECTIFIER MODULE FAILURE | 08/04/2025 02:27:38 | P3 | 4G | taif | Sceco | LTE NSA | TUR1M7681 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 08/04/2025 02:36:11 | 08/05/2025 08:40:58 | 08/22/2025 14:22:28 |  |  | 08/22/2025 14:22:37 |  | Afzal Hussain Anwar Ul Haq | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250804000129 | PCM-20250804-00000230 | TT-20250804-00278 | EM | Region_5 | MAK0184 | MAK0184 |  |  |  | Sarwar Saheb Kolkar Muhammad | 08/04/2025 02:52:06 | 08/05/2025 12:36:56 | 08/04/2025 14:52:06 | AIRCON 2 FAILURE at MAK1M9184-G9-L8-L18-L21-SBTS-P3 @ Sceco | 08/04/2025 02:45:04 | Minor | 7103 | AIRCON 2 FAILURE | 08/04/2025 02:43:23 | P3 | 4G | makkah | Sceco | LTE NSA | MAK1M9184 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/04/2025 02:52:06 | 08/04/2025 13:39:10 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Reject_FME | CM20250805000158 | PCM-20250805-00000237 | TT-20250805-00273 | EM | Region_5 | USMD0768 | USMD0768 |  |  |  | Mohammad Naseer Raja Mohammed | 08/05/2025 02:42:16 | 08/06/2025 11:53:12 | 08/05/2025 14:42:16 | AIRCON 1 FAILURE at USMD1M7768-USF-P3_NCA-L800-SBTS @ Sceco_STB | 08/05/2025 02:35:42 | Minor | 7103 | AIRCON 1 FAILURE | 08/05/2025 02:33:28 | P3 | 4G | makkah | Sceco_STB | LTE NSA | USMD1M7768 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/05/2025 02:42:16 | 08/05/2025 11:49:07 | [6 empty] | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250806000146 | PCM-20250806-00000235 | TT-20250806-00210 | EM | Region_5 | MKMD0551 | MKMD0551 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Hamza Ahmed Aly Sawy | 08/06/2025 02:31:56 | 08/29/2025 11:16:26 | 08/06/2025 14:31:56 | AIRCON 2 FAILURE at MKMD1M7551-L800-SBTS @ Generator_DG | 08/06/2025 02:23:50 | Minor | 7103 | AIRCON 2 FAILURE | 08/06/2025 02:23:06 | P2 | 4G | makkah | Generator_DG | LTE NSA | MKMD1M7551 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/06/2025 02:31:56 |  | 08/29/2025 09:55:56 | 08/29/2025 09:56:06 |  | 08/29/2025 11:16:26 |  | Hamza Ahmed Aly Sawy | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250808000794 | PCM-20250808-00001140 | TT-20250808-01190 | EM | Region_1 | DAM0267 | DAM0267 |  |  |  | Gamal Hasan Farag Ali Khalifa | 08/08/2025 15:14:20 | 08/14/2025 12:29:04 | 08/09/2025 03:14:20 | Air condition 3 failure alarm at DAM0267-P2_SRAN @ Sceco | 08/08/2025 15:12:04 | Minor | 65117 | Air condition 3 failure alarm | 08/08/2025 14:55:04 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0267 | FLM_EM | [8 empty] | API | 08/08/2025 15:14:20 | 08/09/2025 12:04:40 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250808001326 | PCM-20250808-00001977 | TT-20250808-02032 | EM | Region_6 | MHL9707 | MHL9707 |  |  |  | Zia Ur Rahamn | 08/08/2025 21:48:35 | 08/14/2025 12:29:03 | 08/09/2025 01:48:35 | AC1 at MHL9707-2 on 10.154.172.2 @ Sceco | 08/08/2025 21:44:00 | Critical | AC1 | AC1 | 08/08/2025 21:43:03 | P3 | Repeater | mohail | Sceco | TX NSA | MHL9707 | FLM_EM | [8 empty] | API | 08/08/2025 21:48:35 | 08/09/2025 04:28:35 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Request_Resolved | CM20250810001843 | PCM-20250810-00002723 | TT-20250810-02521 | Reference_EM | Region_1 | HFR0504 | HFR0504 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Ibrahim Musa | 08/10/2025 21:48:25 | 08/13/2025 21:19:59 | 08/11/2025 09:48:25 | Air condition 2 failure alarm at HFR0504-P2_SRAN @ Sceco | 08/10/2025 21:37:56 | Minor | 65105 | Air condition 2 failure alarm | 08/10/2025 21:37:52 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR0504 | FLM_EM | [8 empty] | API | 08/10/2025 21:48:25 | 08/13/2025 21:03:54 | 08/13/2025 21:19:50 |  |  | 08/13/2025 21:19:59 |  | Ahmed Ibrahim Musa | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur
Stuck | CM20250812000026 | PCM-20250812-0099999 | TT-20250812-00032 | EM | [7 empty] | 08/12/2025 00:37:05 | 08/12/2025 00:37:05 | 08/12/2025 04:37:05 | DC power fail at DAM0363-P1-HUB-WDM_SRAN-FON @ Sceco | 08/12/2025 00:21:52 | Critical | 65106 | DC power fail | 08/12/2025 00:21:48 | P1 | SRAN |  | Sceco | 2G NSA | DAM0363 | FLM_EM | [8 empty] | API | 08/12/2025 00:37:05 | [10 empty] | EM | LATIS |  | Running |  | Inspur
Stuck | CM20250812000031 | PCM-20250812-0099998 | TT-20250812-00032 | EM | [7 empty] | 08/12/2025 00:42:16 | 08/12/2025 00:42:16 | 08/12/2025 04:42:16 | DC power fail at DAM0363-P1-HUB-WDM_SRAN-FON @ Sceco | 08/12/2025 00:21:52 | Critical | 65106 | DC power fail | 08/12/2025 00:21:48 | P1 | SRAN |  | Sceco | 2G NSA | DAM0363 | FLM_EM | [8 empty] | API | 08/12/2025 00:42:16 | [10 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20250812000953 | PCM-20250812-00001443 | TT-20250812-01461 | EM | Region_4 | TAF0150 | TAF0150 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 08/12/2025 14:34:50 | 08/30/2025 00:51:22 | 08/13/2025 02:34:50 | AIRCON1 FAILURE at TAF1M7150-G9-L8-L18-L21-SBTS-P2 @ Sceco | 08/12/2025 14:26:29 | Minor | 7103 | AIRCON1 FAILURE | 08/12/2025 14:26:23 | P2 | 4G | taif | Sceco | LTE NSA | TAF1M7150 | FLM_EM | [5 empty] | AIRCON1 FAILURE |  |  | API | 08/12/2025 14:34:50 | 08/12/2025 17:39:50 | 08/30/2025 00:51:13 |  |  | 08/30/2025 00:51:22 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250813000193 | PCM-20250813-00000305 | TT-20250813-00290 | EM | Region_4 | JED0080 | JED0080 |  |  |  | Muhammad Arqam Muhammad Dawood | 08/13/2025 02:42:51 | 09/02/2025 13:58:12 | 08/13/2025 08:42:51 | AIRCON 1 FAILURE at JED1M7080-P1-DIA-CA-L900-L800-SBTS @ Sceco | 08/13/2025 02:40:35 | Major | 7103 | AIRCON 1 FAILURE | 08/13/2025 02:15:07 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7080 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/13/2025 02:42:51 | 08/13/2025 15:14:17 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250814000149 | PCM-20250814-00000252 | TT-20250814-00296 | EM | Region_4 | JED0185 | JED0185 |  |  |  | Sajid Nazir Muhammad Nazir | 08/14/2025 02:49:31 | 09/02/2025 13:58:13 | 08/14/2025 14:49:31 | AIRCON 2 FAILURE at JED1M7185-CA-L900-L800-SBTS @ Sceco | 08/14/2025 02:42:27 | Minor | 7103 | AIRCON 2 FAILURE | 08/14/2025 02:41:06 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7185 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/14/2025 02:49:31 | 08/14/2025 05:51:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250814000153 | PCM-20250814-00000257 | TT-20250814-00301 | EM | Region_4 | JED0190 | JED0190 |  |  |  | Amer Attallah Awadallah | 08/14/2025 02:50:31 | 08/20/2025 11:35:11 | 08/14/2025 08:50:31 | AIRCON 2 FAILURE at JED1M7190-P1-HUB-WDM-CA-L900-L800-SBTS @ Sceco | 08/14/2025 02:44:31 | Major | 7103 | AIRCON 2 FAILURE | 08/14/2025 02:41:47 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7190 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/14/2025 02:50:31 | 08/14/2025 14:43:01 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20250815000054 | PCM-20250815-00000083 | TT-20250815-00071 | EM | Region_4 | MLJI9438 | MLJI9438 |  |  |  | Faiz Muhammad Ghulam Sarwar | 08/15/2025 00:54:21 | 08/18/2025 19:46:22 | 08/15/2025 06:54:21 | NEC Eband observing Air Cond Fail at MLJI9438 | 08/15/2025 00:09:29 | Major | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 08/15/2025 00:09:29 | P3 | Repeater | adam | Generator_SG | TX NSA | MLJI9438 | FLM_EM | [5 empty] | NEC Eband observing Air Cond Fail at MLJI9438 |  |  | API | 08/15/2025 00:54:21 | 08/18/2025 19:46:22 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250816000953 | PCM-20250816-00001409 | TT-20250816-01416 | Reference_EM | Region_1 | HFF0064 | HFF0064 |  |  |  | Ahmed Bashir Sahib Rahman | 08/16/2025 16:34:30 | 09/08/2025 11:45:01 | 08/17/2025 04:34:30 | Air condition 3 failure alarm at HFF0064-P2_SRAN @ Sceco | 08/16/2025 16:24:01 | Minor | 65117 | Air condition 3 failure alarm | 08/16/2025 16:23:57 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0064 | FLM_EM | [8 empty] | API | 08/16/2025 16:34:30 | 08/17/2025 14:00:40 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250817000126 | PCM-20250817-00000212 | TT-20250817-00215 | EM | Region_4 | JED0535 | JED0535 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 08/17/2025 02:55:01 | 09/02/2025 13:58:10 | 08/17/2025 14:55:01 | AIRCON 1 FAILURE at JED1M7535-CA-L900-L800-SBTS @ Sceco | 08/17/2025 02:46:57 | Minor | 7103 | AIRCON 1 FAILURE | 08/17/2025 02:46:23 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7535 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/17/2025 02:55:01 | 08/17/2025 14:31:57 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250817000136 | PCM-20250817-00000226 | TT-20250817-00229 | EM | Region_4 | JED0564 | JED0564 | Enviroment | Genset failure_Fan Belt | Change Fan Belt | Anas Mohamedelamin Abbas Mustafa | 08/17/2025 03:00:41 | 08/20/2025 07:17:50 | 08/17/2025 09:00:41 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M7564-P1-VIP-CA-L900-L800-SBTS @ Generator_SG | 08/17/2025 02:52:11 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 08/17/2025 02:52:01 | VIP | 4G | jeddah | Generator_SG | LTE NSA | JED1M7564 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 08/17/2025 03:00:41 | 08/20/2025 06:22:10 | 08/20/2025 06:23:14 | 08/20/2025 06:28:12 | 08/20/2025 07:17:29 | 08/20/2025 07:17:50 |  | Anas Mohamedelamin Abbas Mustafa |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20250818000503 | PCM-20250818-00000863 | TT-20250818-00926 | EM | Region_2 | RYMK9001 | RYMK9001 | Enviroment | SCECO_Failure | SCECO auto restored | Saleem Khan Amir Dost | 08/18/2025 09:55:45 | 08/31/2025 21:53:04 | 08/18/2025 13:55:45 | RELAY_ALARM_CRITICAL at RYMK9001_NE_3_ExternalAlarms2 | 08/18/2025 09:49:42 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 08/18/2025 09:49:42 | P3 | Repeater | quweyah | Sceco | TX NSA | RYMK9001_NE_3_ExternalAlarms2 | FLM_EM | [8 empty] | API | 08/18/2025 09:55:45 | 08/18/2025 12:00:22 | 08/31/2025 21:52:56 |  |  | 08/31/2025 21:53:04 |  | Saleem Khan Amir Dost |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20250819000802 | PCM-20250819-00001320 | TT-20250819-01303 | EM | Region_5 | MAK0264 | MAK0264 |  |  |  | Ezz Ismaeal Mahmoud Sayed | 08/19/2025 12:19:01 | 08/21/2025 14:11:10 | 08/20/2025 00:19:01 | AIRCON 2 FAILURE at MAK0264-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 08/19/2025 12:11:02 | Minor | 7103 | AIRCON 2 FAILURE | 08/19/2025 12:10:40 | P3 | 2G | makkah | Sceco | 2G NSA | MAK0264 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 08/19/2025 12:19:01 | [7 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250819000934 | PCM-20250819-00001526 | TT-20250819-01496 | EM | Region_4 | TAF0326 | TAF0326 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 08/19/2025 14:02:20 | 08/30/2025 00:52:14 | 08/19/2025 20:02:20 | AIRCON 1 FAILURE at TAF0326-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB @ Sceco | 08/19/2025 13:53:40 | Major | 7103 | AIRCON 1 FAILURE | 08/19/2025 13:53:47 | P1 | 2G | taif | Sceco | 2G NSA | TAF0326 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/19/2025 14:02:20 | 08/19/2025 22:53:59 | 08/30/2025 00:52:07 |  |  | 08/30/2025 00:52:14 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250822001171 | PCM-20250822-00001816 | TT-20250822-01600 | Telecom | Region_5 | AKR0339 | AKR0339 |  |  |  | Hosini Saeed Hassn Saeed | 08/22/2025 19:57:47 | 09/05/2025 01:41:21 | 08/22/2025 23:57:47 | 5(2G) 5(3G) 3(LTE) 3(5G) sites down under MSE0624-P2-USF,AKR0339-P2-USF, AKR0971-P3,MDQ0970-P3,MDQ2367-P2-USF/MDQ2367-P2-USF @ Generator_SG | 08/22/2025 18:58:10 | Critical | 7706 | BTS O&M LINK FAILURE | 08/22/2025 18:58:05 | P2 | 2G | makkah | Generator_SG | 2G_3G_LTE_5G SA | MSE0624-P2-USF 3G_LTE,MDQ2367-P2-USF 2G_3G_5G,AKR0971-P3 2G_3G,MDQ0970-P3 2G_3G | FLM_EM |  | Hub: AKR0339, MDQ2367, MSE0624 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20250822-00001797 | Hub: AKR0339, MDQ2367, MSE0624 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: AKR0339, MDQ2367, MSE0624 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 08/22/2025 19:57:47 | 08/28/2025 23:06:41 | [6 empty] | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250824001688 | PCM-20250824-00002554 | TT-20250824-02301 | EM | Region_5 | MAK0256 | MAK0256 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 08/24/2025 17:57:30 | 08/26/2025 11:24:55 | 08/25/2025 05:57:30 | AIRCON 1 FAILURE at MAK1M9256-NCA-L800-SBTS @ Sceco | 08/24/2025 17:49:13 | Minor | 7103 | AIRCON 1 FAILURE | 08/24/2025 17:49:06 | P2 | 4G | makkah | Sceco | LTE NSA | MAK1M9256 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 08/24/2025 17:57:30 | 08/24/2025 21:26:18 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250825000438 | PCM-20250825-00000723 | TT-20250825-00775 | EM | Region_4 | MLJI9425 | MLJI9425 | Enviroment | Genset failure_MCU | Change Generator controller | Muhammad Rizwan Basharat Hussain | 08/25/2025 09:07:55 | 09/24/2025 12:03:00 | 08/25/2025 13:07:55 | NEC Eband observing air Conditioning Failure at MLJI9425 | 08/25/2025 08:57:43 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 08/25/2025 09:06:38 | P3 | Repeater | alaith | Generator_DG | TX NSA | MLJI9425 | FLM_EM | [5 empty] | NEC Eband observing air Conditioning Failure at MLJI9425 |  |  | API | 08/25/2025 09:07:55 | 09/24/2025 11:45:07 | 09/24/2025 11:45:21 | 09/24/2025 11:45:25 | 09/24/2025 11:45:36 | 09/24/2025 12:03:00 |  | Muhammad Rizwan Basharat Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250826000593 | PCM-20250826-00001606 | TT-20250826-01423 | EM | Region_2 | BUR0001 | BUR0001 |  |  |  | Farman Ullah Muhammad Nazir | 08/26/2025 08:21:45 | 09/03/2025 14:30:40 | 08/26/2025 20:21:45 | Air condition 2 failure alarm at BUR0001-P2_SRAN @ Sceco | 08/26/2025 08:13:25 | Minor | 65105 | Air condition 2 failure alarm | 08/26/2025 08:11:05 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0001 | FLM_EM | [8 empty] | API | 08/26/2025 08:21:45 | 08/26/2025 08:58:05 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250826001188 | PCM-20250826-00002459 | TT-20250826-02184 | EM | Region_1 | HFF0048 | HFF0048 |  |  |  | Ahmed Bashir Sahib Rahman | 08/26/2025 14:27:01 | 09/08/2025 11:45:02 | 08/27/2025 02:27:01 | Door opening alarm at HFF0048-P2_SRAN @ Sceco | 08/26/2025 14:26:30 | Minor | 65101 | Door opening alarm | 08/26/2025 14:23:59 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0048 | FLM_EM | [8 empty] | API | 08/26/2025 14:27:01 | 08/26/2025 16:34:35 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250826001202 | PCM-20250826-00002479 | TT-20250826-02197 | EM | Region_1 | HFF0048 | HFF0048 |  |  |  | Ahmed Bashir Sahib Rahman | 08/26/2025 14:34:46 | 08/28/2025 13:46:52 | 08/27/2025 02:34:46 | high temprature 32 at HFF0048-P2_SRAN @ Sceco | 08/26/2025 14:26:30 | Minor | 65102 | high temprature 32 | 08/26/2025 14:23:59 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0048 | FLM_EM | [8 empty] | API | 08/26/2025 14:34:46 | 08/26/2025 16:34:35 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250826001822 | PCM-20250826-00003428 | TT-20250826-03119 | EM | Region_4 | TFBH9401 | TFBH9401 |  |  |  | Mohamed Ahmed Kassem Embarak | 08/26/2025 22:00:16 | 08/27/2025 09:42:51 | 08/27/2025 02:00:16 | NEC Eband observing Rectifier Fault alarm at site TFBH9401 | 08/26/2025 21:09:14 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 08/26/2025 21:09:14 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9401 | FLM_EM | [5 empty] | NEC Eband observing Rectifier Fault alarm at site TFBH9401 |  |  | API | 08/26/2025 22:00:16 | 08/27/2025 09:42:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20250828001008 | PCM-20250828-00001525 | TT-20250828-01146 | Telecom | Region_2 | RIY0311 | RIY0311 | Enviroment | Air Condition | Welding condenser & adding Freon | Kadri Jalal Mohammed Asmail | 08/28/2025 15:22:00 | 09/30/2025 14:56:49 | 08/29/2025 03:22:00 | HC For RIY0311 | 08/28/2025 12:17:51 | Minor | 676767672 | Health Check-WO to TE FME | 08/28/2025 12:17:52 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY0311 | FLM_EM |  |  | PCM-20250828-00001506 | Site has repeated power issue and EM to check issue | Site has repeated power issue and EM to check issue |  |  |  | API | 08/28/2025 15:22:00 | 09/30/2025 13:34:05 | 09/30/2025 14:07:20 | 09/30/2025 14:07:25 | 09/30/2025 14:07:29 | 09/30/2025 14:56:49 |  | Kadri Jalal Mohammed Asmail |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250901000871 | PCM-20250901-00001355 | TT-20250901-00260 | Telecom | Region_2 | RIY2700 | RIY2700 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 09/01/2025 15:12:35 | 09/02/2025 01:13:27 | 09/02/2025 03:12:35 | HC TT for RIY2237,RIY2917,RIY2700 | 09/01/2025 03:32:00 | Minor | 676767672 | Health Check-WO to TE FME | 09/01/2025 03:32:00 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2237,RIY2917,RIY2700 | FLM_EM |  |  | PCM-20250901-00001280 | power issue at site | power issue at site |  |  |  | API | 09/01/2025 15:12:35 | 09/02/2025 01:13:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250902000693 | PCM-20250902-00001104 | TT-20250902-01259 | EM | Region_4 | AQA9452 | AQA9452 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Ahmed Kassem Embarak | 09/02/2025 12:20:17 | 09/02/2025 13:32:44 | 09/02/2025 16:20:17 | NEC Eband observing GEN LOW FUEL(Input) at AQA9452-2 | 09/02/2025 12:10:56 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 09/02/2025 12:18:13 | P1 | Repeater | taif | Generator_DG | TX NSA | AQA9452 | FLM_EM | [5 empty] | NEC Eband observing GEN LOW FUEL(Input) at AQA9452-2 |  |  | API | 09/02/2025 12:20:17 | 09/02/2025 12:25:09 | 09/02/2025 13:17:55 | 09/02/2025 13:18:08 | 09/02/2025 13:18:11 | 09/02/2025 13:32:44 |  | Mohamed Ahmed Kassem Embarak |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Accept | CM20250903000980 | PCM-20250903-00001589 | TT-20250903-01532 | EM | Region_2 | RYRN0633 | RYRN0633 |  |  |  | Saleem Khan Amir Dost | 09/03/2025 15:19:02 | 10/01/2025 10:14:19 | 09/04/2025 03:19:02 | Mains Failure at RYRN2M5633-P3 @ Sceco | 09/03/2025 15:09:05 | Minor | 65109 | Mains Failure | 09/03/2025 15:08:55 | P3 | 2G | quweyah | Sceco | 2G NSA | RYRN2M5633 | FLM_EM | [8 empty] | API | 09/03/2025 15:19:02 | 09/03/2025 17:00:53 | 10/01/2025 10:14:19 | [5 empty] | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20250903001202 | PCM-20250903-00001971 | TT-20250903-01863 | EM | Region_1 | HFF0042 | HFF0042 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 09/03/2025 18:13:40 | 10/07/2025 05:57:27 | 09/04/2025 06:13:40 | Low battery voltage at HFF0042-P2_SRAN @ Sceco | 09/03/2025 18:07:06 | Minor | 65110 | Low battery voltage | 09/03/2025 18:03:20 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0042 | FLM_EM | [8 empty] | API | 09/03/2025 18:13:40 | 10/07/2025 03:43:17 | 10/07/2025 05:57:21 |  |  | 10/07/2025 05:57:27 |  | Shahid Khan Dilawar Khan | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250906000708 | PCM-20250906-00001135 | TT-20250906-01127 | Telecom | Region_2 | RIYA6042 | RIYA6042 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 09/06/2025 14:03:18 | 10/07/2025 13:39:49 | 09/07/2025 02:03:18 | RF Unit Maintenance Link Failure at RIYA6042-DCU-3 @ Sceco | 09/06/2025 14:01:16 | Minor | 26235 | RF Unit Maintenance Link Failure | 09/06/2025 13:58:02 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6042 | FLM_TE | [8 empty] | API | 09/06/2025 14:03:18 | 09/06/2025 16:17:56 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907000583 | PCM-20250907-00000959 | TT-20250907-00963 | EM | Region_3 | TBK9046 | TBK9046 |  |  |  | Moustafa Samir Omar | 09/07/2025 11:49:09 | 10/05/2025 15:43:16 | 09/07/2025 15:49:09 | NEC MW observing LOW BATTERY (INPUT-4) At TBK9046_EAS | 09/07/2025 11:46:43 | Critical | 383 | POWER_ALM | 09/07/2025 11:46:43 | P3 | Repeater | tabouk | Generator_DG | TX NSA | TBK9046_EAS | FLM_EM | [5 empty] | NEC MW observing LOW BATTERY (INPUT-4) At TBK9046_EAS |  |  | API | 09/07/2025 11:49:09 | 10/05/2025 15:43:16 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250907001098 | PCM-20250907-00001708 | TT-20250907-01676 | MW_HC | Region_2 | RIY2384 | RIY2384 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Muhammad Naeem Muhammad Gulzar | 09/07/2025 17:04:18 | 09/29/2025 12:03:37 | 09/08/2025 05:04:18 | Huawei MW HC_P2 Observing Errors at RIY2384-RIY2425 | 09/07/2025 17:02:01 | Minor |  | LOF | 09/07/2025 17:02:01 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY2384-RIY2425 | FLM_TE | [8 empty] | API | 09/07/2025 17:04:18 | 09/29/2025 09:28:47 | 09/29/2025 09:42:27 | 09/29/2025 09:42:30 | 09/29/2025 10:54:16 | 09/29/2025 12:03:37 |  | Muhammad Naeem Muhammad Gulzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907001171 | PCM-20250907-00001781 | TT-20250907-01749 | Reference_telecom | Region_6 | JDS0797 | JDS0797 |  |  |  | Osama Hadi | 09/07/2025 17:05:35 | 09/08/2025 00:31:28 | 09/08/2025 05:05:35 | NEC MW Observing SFP Type Mismatch,Low BER at JDS0797_1(10.1.170.185) | 09/03/2025 07:08:15 | Minor |  | LOF | 09/03/2025 07:08:15 | P2 | 2G | jizan | Sceco | TX NSA | JDS0797_1(10.1.170.185) | FLM_TE | [8 empty] | API | 09/07/2025 17:05:35 | 09/08/2025 00:31:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907001177 | PCM-20250907-00001787 | TT-20250907-01755 | Reference_telecom | Region_6 | JIZ0086 | JIZ0086 |  |  |  | Osama Hadi | 09/07/2025 17:05:42 | 09/08/2025 00:31:30 | 09/08/2025 05:05:42 | NEC MW Observing LOF,XIF at JIZ0086(10.157.253.138) | 02/12/2025 00:45:24 | Minor |  | LOF | 02/12/2025 00:45:24 | P1 | 2G | jizan | Generator_SG | TX NSA | JIZ0086(10.157.253.138) | FLM_TE | [8 empty] | API | 09/07/2025 17:05:42 | 09/08/2025 00:31:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907001184 | PCM-20250907-00001794 | TT-20250907-01762 | Reference_telecom | Region_1 | KFJ2004 | KFJ2004 |  |  |  | Mohamed Abdelaziz | 09/07/2025 17:05:48 | 09/16/2025 19:14:13 | 09/08/2025 05:05:48 | NEC MW Observing Radio Traffic Aggregation Link,Radio Traffic Aggregation Link at KFJ2004_1(10.248.33.146) | 09/03/2025 08:12:12 | Minor |  | LOF | 09/03/2025 08:12:12 | P2 | SRAN | khafji | Sceco | TX NSA | KFJ2004_1(10.248.33.146) | FLM_TE | [8 empty] | API | 09/07/2025 17:05:48 | 09/07/2025 17:55:00 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250907001190 | PCM-20250907-00001800 | TT-20250907-01768 | Reference_telecom | Region_3 | MDN0732 | MDN0732 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 09/07/2025 17:05:55 | 09/24/2025 22:12:58 | 09/08/2025 05:05:55 | NEC MW Observing Power Supply,Radio Traffic Aggregation Link at MDN0732(10.154.79.49) | 07/15/2025 20:50:16 | Minor |  | LOF | 07/15/2025 20:50:16 | P1 | SRAN | madinah | Sceco | TX NSA | MDN0732(10.154.79.49) | FLM_TE | [8 empty] | API | 09/07/2025 17:05:55 | 09/07/2025 19:02:42 | 09/24/2025 22:12:58 | [5 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907001209 | PCM-20250907-00001819 | TT-20250907-01787 | Reference_telecom | Region_1 | RST0351 | RST0351 |  |  |  | Tahir Mahmood Hafiz Yar | 09/07/2025 17:06:15 | 09/16/2025 19:14:15 | 09/08/2025 05:06:15 | NEC MW Observing LOF,Frame ID at RST0351-1(10.74.80.162) | 09/01/2025 07:22:52 | Minor |  | LOF | 09/01/2025 07:22:52 | P1 | SRAN | jubail | Sceco | TX NSA | RST0351-1(10.74.80.162) | FLM_TE | [8 empty] | API | 09/07/2025 17:06:15 | 09/07/2025 18:34:31 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907001210 | PCM-20250907-00001820 | TT-20250907-01788 | Reference_telecom | Region_1 | RST0949 | RST0949 |  |  |  | Meraj Husain Idd Baksh | 09/07/2025 17:06:17 | 09/16/2025 19:14:14 | 09/08/2025 05:06:17 | NEC MW Observing XIF,MODEM Power Supply Alarm at RST0949(10.74.80.163) | 08/31/2025 00:03:52 | Minor |  | LOF | 08/31/2025 00:03:52 | P3 | SRAN | dammam | Sceco | TX NSA | RST0949(10.74.80.163) | FLM_TE | [8 empty] | API | 09/07/2025 17:06:17 | 09/07/2025 18:04:27 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20250907001225 | PCM-20250907-00001835 | TT-20250907-01803 | Reference_telecom | Region_3 | YNB0670 | YNB0670 |  |  |  | Muhammad Sajjad R3 | 09/07/2025 17:06:32 | 09/17/2025 16:34:10 | 09/08/2025 05:06:32 | NEC MW Observing LAN Link,ETH LOS,IF Cable Short at YNB0670_1(10.248.39.5) | 07/09/2025 12:22:17 | Minor |  | LOF | 07/09/2025 12:22:17 | P1 | SRAN | yanbu | Sceco | TX NSA | YNB0670_1(10.248.39.5) | FLM_TE | [8 empty] | API | 09/07/2025 17:06:32 | 09/07/2025 23:17:33 | 09/17/2025 16:34:05 | 09/17/2025 16:34:10 |  |  |  |  | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250907001606 | PCM-20250907-00002416 | TT-20250907-02207 | Reference_telecom | Region_5 | MAK1MN0326 | MAK0326 |  |  |  | Atif Javed Javed Hussain | 09/07/2025 21:53:58 | 09/28/2025 17:45:04 | 09/08/2025 03:53:58 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0326-NR2.6-VIP @ Sceco | 09/07/2025 16:34:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 09/07/2025 16:34:11 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0326 | FLM_TE |  |  | PCM-20250907-00002310 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 09/07/2025 21:53:58 | 09/15/2025 14:16:29 | [6 empty] | Force_Majeure |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250908000234 | PCM-20250908-00000503 | TT-20250908-00627 | Reference_telecom | Region_6 | ABBS0163 | ABBS0163 | Transsmission | MW_HW_fault | Replace ODU | Fawad Khan | 09/08/2025 06:39:46 | 10/20/2025 00:53:25 | 09/08/2025 18:39:46 | LossOfSignal observed in ABBS0163_03 towards 10.221.245.11 @ Sceco | 09/07/2025 18:39:38 | Minor |  | LossOfSignal | 09/07/2025 18:39:34 | P3 | 2G | namas | Sceco | TX NSA | ABBS0163 | FLM_TE | [8 empty] | API | 09/08/2025 06:39:46 | 09/08/2025 11:23:15 | 10/20/2025 00:52:49 |  |  | 10/20/2025 00:53:25 |  | Fawad Khan | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908000814 | PCM-20250908-00001567 | TT-20250731-01109 | Reference_telecom | Region_1 | HFF0041 | HFF0041 |  |  |  | Muhammad Kashif M M Bashir | 09/08/2025 14:29:06 | 10/06/2025 16:48:45 | 09/08/2025 20:29:06 | 1(2G/3G/LTE) sites down under HFF0041-P2/R1_HF_HWBSC01 @ Sceco (Ref:TT-20250730-00871) | 07/30/2025 09:51:57 | Major | 21825 | CSL Fault | 07/30/2025 09:51:57 | P2 | SRAN | hafouf | Sceco | 2G_3G_5G SA | HFF0041 | FLM_TE | HFF0041 | Results: DOWN SITE HUB HFF0041 HFF0041 Summary: Hub: HFF0041, Down Count: 1, Down Sites: HFF0041 Alarm Summary: HFF0041 No Active Alarm on HUB | PCM-20250908-00001100 | Site Dismantled, Need approve to cancel TT | Site Dismantled, Need approve to cancel TT |  | sites down |  | API | 09/08/2025 14:29:06 | 09/08/2025 23:34:05 | [6 empty] | Relocation_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001246 | PCM-20250908-00002281 | TT-20250908-02136 | MW_HC | Region_6 | MKW2347 | MKW2347 |  |  |  | SHAH KHALID | 09/08/2025 17:55:05 | 09/08/2025 20:21:05 | 09/09/2025 05:55:05 | Nokia MW HC_P0 Observing RSL Issue at MKW2347-MKW2346_01 | 09/08/2025 17:52:05 | Minor |  | LOF | 09/08/2025 17:52:05 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2347-MKW2346_01 | FLM_TE | [8 empty] | API | 09/08/2025 17:55:05 | 09/08/2025 20:21:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250908001251 | PCM-20250908-00002285 | TT-20250908-02141 | MW_HC | Region_6 | BHAB2442 | BHAB2442 | Transsmission | SFP_Transmission | Replace SFP | SHAH KHALID | 09/08/2025 17:55:10 | 10/15/2025 07:22:17 | 09/09/2025 05:55:10 | Nokia MW HC_P0 Observing Performance Issue at BHAB2442_01-BHAB2005_02 | 09/08/2025 17:52:05 | Minor |  | LOF | 09/08/2025 17:52:05 | P3 | 2G | Albaha | Generator_SG | TX NSA | BHAB2442_01-BHAB2005_02 | FLM_TE | [8 empty] | API | 09/08/2025 17:55:10 | 09/08/2025 20:21:05 | 10/14/2025 11:09:03 |  |  | 10/15/2025 07:22:17 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001397 | PCM-20250908-00002432 | TT-20250908-02285 | MW_HC | Region_6 | JIZ0151 | JIZ0151 |  |  |  | Osama Hadi | 09/08/2025 17:57:38 | 09/08/2025 18:36:00 | 09/09/2025 05:57:38 | Nokia MW HC_P1 Observing Performance Issue at JIZ0151-JIZ0276_Single BOX2 | 09/08/2025 17:52:04 | Minor |  | LOF | 09/08/2025 17:52:04 | P2 | 2G | jizan | Sceco | TX NSA | JIZ0151-JIZ0276_Single BOX2 | FLM_TE | [8 empty] | API | 09/08/2025 17:57:38 | 09/08/2025 18:36:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001425 | PCM-20250908-00002461 | TT-20250908-02313 | MW_HC | Region_6 | BAH0540 | BAH0540 |  |  |  | SHAH KHALID | 09/08/2025 17:58:07 | 09/08/2025 20:21:07 | 09/09/2025 05:58:07 | Nokia MW HC_P2 Observing Modem Down at BAH0540-BAH0007-2 SB | 09/08/2025 17:52:04 | Minor |  | LOF | 09/08/2025 17:52:04 | VIP | 2G | Albaha | Sceco | TX NSA | BAH0540-BAH0007-2 SB | FLM_TE | [8 empty] | API | 09/08/2025 17:58:07 | 09/08/2025 20:21:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20250908001469 | PCM-20250908-00002505 | TT-20250908-02358 | MW_HC | Region_6 | SDA0295 | SDA0295 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 09/08/2025 17:58:53 | 10/01/2025 12:54:22 | 09/09/2025 05:58:53 | NEC MW HC_P2 Observing Modem Down at SDA0295(10.154.163.202)--SDA2294(10.154.163.196) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P3 | 2G | abha | Generator_SG | TX NSA | SDA0295(10.154.163.202)--SDA2294(10.154.163.196) | FLM_TE | [8 empty] | API | 09/08/2025 17:58:53 | 09/08/2025 21:17:56 | 10/01/2025 12:54:22 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20250908001472 | PCM-20250908-00002508 | TT-20250908-02361 | MW_HC | Region_6 | NJR0012 | NJR0012 |  |  |  | Shahid Ali Roshan Ali | 09/08/2025 17:58:55 | 10/19/2025 02:00:46 | 09/09/2025 05:58:55 | NEC MW HC_P0 Observing Modem Down at NJR0012(10.154.164.117)--NJR0074(10.154.164.122) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P3 | 2G | najran | Sceco | TX NSA | NJR0012(10.154.164.117)--NJR0074(10.154.164.122) | FLM_TE | [8 empty] | API | 09/08/2025 17:58:55 | 09/08/2025 18:50:25 | 10/19/2025 02:00:46 | [5 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001473 | PCM-20250908-00002509 | TT-20250908-02362 | MW_HC | Region_6 | MHL0136 | MHL0136 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/08/2025 17:58:57 | 09/08/2025 19:35:26 | 09/09/2025 05:58:57 | NEC MW HC_P0 Observing Modem Down at MHL0136(10.157.250.21)--MHL9712(10.157.250.20) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P3 | 2G | mohail | Sceco | TX NSA | MHL0136(10.157.250.21)--MHL9712(10.157.250.20) | FLM_TE | [8 empty] | API | 09/08/2025 17:58:57 | 09/08/2025 19:35:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001495 | PCM-20250908-00002532 | TT-20250908-02383 | MW_HC | Region_3 | MDHL0379 | MDHL0379 |  |  |  | Mohamed Naveed | 09/08/2025 17:59:19 | 09/08/2025 18:24:07 | 09/09/2025 05:59:19 | NEC MW HC_P0 Observing Modem Down at MDHL0379(10.253.0.133)--MDHL0380(10.253.0.134) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P1 | SRAN | hail | Sceco_STB | TX NSA | MDHL0379(10.253.0.133)--MDHL0380(10.253.0.134) | FLM_TE | [8 empty] | API | 09/08/2025 17:59:19 | 09/08/2025 18:24:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001496 | PCM-20250908-00002533 | TT-20250908-02384 | MW_HC | Region_3 | YBDB0279 | YBDB0279 |  |  |  | Muhammad Sajjad R3 | 09/08/2025 17:59:20 | 09/16/2025 18:35:16 | 09/09/2025 05:59:20 | NEC MW HC_P0 Observing Performance Issue at YBDB0279(10.154.80.3)--YBDB0280(10.154.80.5) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P1 | SRAN | yanbu | Generator_DG | TX NSA | YBDB0279(10.154.80.3)--YBDB0280(10.154.80.5) | FLM_TE | [8 empty] | API | 09/08/2025 17:59:20 | 09/10/2025 08:12:21 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001507 | PCM-20250908-00002545 | TT-20250908-02396 | MW_HC | Region_1 | JBRK0923 | JBRK0923 |  |  |  | Tahir Mahmood Hafiz Yar | 09/08/2025 17:59:32 | 09/19/2025 11:38:02 | 09/09/2025 05:59:32 | NEC MW HC_P0 Observing Modem Down at JBRK0923(10.76.111.234)--JBRK0924(10.76.111.231) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P3 | SRAN | jubail | Generator_DG | TX NSA | JBRK0923(10.76.111.234)--JBRK0924(10.76.111.231) | FLM_TE | [8 empty] | API | 09/08/2025 17:59:32 | 09/08/2025 18:39:42 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001576 | PCM-20250908-00002669 | TT-20250908-02521 | Reference_telecom | Region_1 | KB1 | KB1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 09/08/2025 18:59:02 | 09/16/2025 15:30:58 | 09/09/2025 00:59:02 | RFC Port Underpower at KBR6056-DCU2 @ Sceco_STB | 09/08/2025 12:17:33 | Major | 29803 | RFC Port Underpower | 09/08/2025 12:17:45 | P1 | BSC | dammam | Sceco_STB | LTE NSA | KBR6056 | FLM_TE | [8 empty] | API | 09/08/2025 18:59:02 | 09/16/2025 15:30:58 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250908001577 | PCM-20250908-00002672 | TT-20250908-02525 | Telecom | Region_1 | DJL0551 | DJL0551 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Syed Fawad Ali | 09/08/2025 19:00:19 | 09/16/2025 21:01:58 | 09/09/2025 07:00:19 | ODU CPU / Cable Open at DJL0551-5 on 10.147.4.50 @ Sceco_STB | 09/08/2025 11:38:34 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 09/08/2025 11:45:29 | P2 | SRAN | sakaka | Sceco_STB | TX NSA | DJL0551 | FLM_TE | [8 empty] | API | 09/08/2025 19:00:19 | 09/16/2025 21:01:58 | [5 empty] | Syed Fawad Ali | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250908001739 | PCM-20250908-00002893 | TT-20250908-02745 | Telecom | Region_6 | KMS0467 | KMS0467 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Muhammad shafiq Muhammad Rasheed | 09/08/2025 21:32:55 | 10/01/2025 16:59:06 | 09/09/2025 09:32:55 | NEC MW observing 2 NES visibility down KMS0467 (10.1.172.33) under cluster KMS0039 | 09/08/2025 21:30:20 | Minor | 113388 | LOF | 09/08/2025 21:30:24 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0467 (10.1.172.33), SKMS0091 (10.1.172.34) | FLM_TE | [8 empty] | API | 09/08/2025 21:32:55 | 09/30/2025 15:02:50 | 10/01/2025 16:57:50 | 10/01/2025 16:57:54 |  | 10/01/2025 16:59:06 |  | Muhammad shafiq Muhammad Rasheed | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250908001744 | PCM-20250908-00002903 | TT-20250908-02757 | Telecom | Region_6 | FS325 | FS325 | Transsmission | MW_HW_stuck | Reset IDU | Ahmed Abdelaziz Hamid Abdelrahman | 09/08/2025 21:53:01 | 09/30/2025 13:14:51 | 09/09/2025 09:53:01 | NEC MW observing visibility down at 2 NES FS325 due to PM error under cluster KMS0039_NOKIA USF | 09/08/2025 21:45:13 | Minor | 113388 | LOF | 09/08/2025 21:45:16 | P3 | Shop | khamis mushyet | Sceco | TX NSA | FS325 (10.89.220.38) , KHS0332 (10.89.220.40) | FLM_TE | [8 empty] | API | 09/08/2025 21:53:01 | 09/30/2025 13:12:24 | 09/30/2025 13:14:25 |  |  | 09/30/2025 13:14:51 |  | Ahmed Abdelaziz Hamid Abdelrahman | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250909001380 | PCM-20250909-00002430 | TT-20250909-02317 | Reference_telecom | Region_1 | HFF0845 | HFF0845 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | Mohamed Magdy Fouad Zayed | 09/09/2025 20:11:51 | 09/16/2025 19:32:42 | 09/10/2025 08:11:51 | MW_LOF at HFF0845_NE_1 @ Power Cube | 09/09/2025 16:11:37 | Minor | 1-631 | MW_LOF | 09/09/2025 16:11:25 | P2 | SRAN | hafouf | Power Cube | TX NSA | HFF0845 | FLM_TE | [8 empty] | API | 09/09/2025 20:11:51 | 09/16/2025 19:32:42 | [5 empty] | Mohamed Magdy Fouad Zayed | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250909001390 | PCM-20250909-00002446 | TT-20250909-02335 | Reference_telecom | Region_1 | KBR6054 | KBR6054 |  |  |  | Meraj Husain Idd Baksh | 09/09/2025 20:21:08 | 09/16/2025 19:14:17 | 09/10/2025 02:21:08 | RF Unit VSWR Threshold Crossed at KBR6054-DCU3 @ Sceco | 09/09/2025 17:18:16 | Major | 26529 | RF Unit VSWR Threshold Crossed | 09/09/2025 17:20:43 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6054 | FLM_TE | [8 empty] | API | 09/09/2025 20:21:08 | 09/09/2025 22:11:30 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250910000098 | PCM-20250910-00000177 | TT-20250910-00176 | Reference_telecom | Region_6 | NJR0019 | NJR0019 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 09/10/2025 02:16:08 | 10/09/2025 14:47:36 | 09/10/2025 14:16:08 | LagPortDown observed in NJR0019_01 towards 10.10.158.162 @ Sceco | 09/09/2025 14:15:57 | Minor |  | LagPortDown | 09/09/2025 14:15:52 | P1 | 2G | najran | Sceco | TX NSA | NJR0019 | FLM_TE | [8 empty] | API | 09/10/2025 02:16:08 | 10/09/2025 14:47:36 | [5 empty] | Shahid Ali Roshan Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250910000097 | PCM-20250910-00000176 | TT-20250910-00175 | Reference_telecom | Region_6 | NJR0030 | NJR0030 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 09/10/2025 02:16:08 | 10/09/2025 14:47:36 | 09/10/2025 14:16:08 | LagPortDown observed in NJR0030_03 towards 10.10.158.161 @ Sceco_STB | 09/09/2025 14:15:57 | Minor |  | LagPortDown | 09/09/2025 14:15:52 | VIP | 2G | najran | Sceco_STB | TX NSA | NJR0030 | FLM_TE | [8 empty] | API | 09/10/2025 02:16:08 | 10/09/2025 14:47:36 | [5 empty] | Shahid Ali Roshan Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250910000588 | PCM-20250910-00001133 | TT-20250910-01003 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | BSS_HW_fault | Replace DRH | Muhammad Waqas Ashraf Muhammad Ashraf | 09/10/2025 11:51:29 | 10/22/2025 11:33:31 | 09/10/2025 23:51:29 | FPGA Processing Error at RIYB6158-DCU2 @ Sceco | 09/10/2025 00:53:16 | Minor | 29801 | FPGA Processing Error | 09/10/2025 00:53:11 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 09/10/2025 11:51:29 | 09/10/2025 13:54:59 | 10/22/2025 11:32:57 | 10/22/2025 11:33:04 | 10/22/2025 11:33:06 | 10/22/2025 11:33:31 |  | Muhammad Waqas Ashraf Muhammad Ashraf | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250910000613 | PCM-20250910-00001170 | TT-20250910-01040 | Reference_telecom | Region_6 | NJR0043 | NJR0043 |  |  |  | TALEH MUHAMMAD | 09/10/2025 12:15:14 | 10/09/2025 14:32:31 | 09/11/2025 00:15:14 | LagPortDown observed in NJR0043_02 towards 10.10.158.165 @ Generator_SG | 09/10/2025 00:15:33 | Minor |  | LagPortDown | 09/10/2025 00:14:59 | P3 | 2G | najran | Generator_SG | TX NSA | NJR0043 | FLM_TE | [8 empty] | API | 09/10/2025 12:15:14 | 09/10/2025 14:42:27 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250910001043 | PCM-20250910-00001828 | TT-20250910-01659 | Telecom | Region_2 | RIY2209 | RIY2209 | Transsmission | SFP_Transmission | Replace SFP | Khan zeb Shah nawaz | 09/10/2025 17:07:59 | 09/22/2025 16:47:09 | 09/10/2025 23:07:59 | As per BO confirm MW RTN Observing PLA_PKT_ERR at RIY2209_NE_3_SDB | 09/10/2025 17:06:14 | Major | 1-13930 | PLA_PKT_ERR | 09/10/2025 17:06:16 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2209 | FLM_TE | [8 empty] | API | 09/10/2025 17:07:59 | 09/22/2025 16:47:09 | [5 empty] | Khan zeb Shah nawaz | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250910001070 | PCM-20250910-00001872 | TT-20250910-01712 | Telecom | Region_5 | HAJ0158 | HAJ0158 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 09/10/2025 17:25:09 | 09/11/2025 04:38:58 | 09/11/2025 05:25:09 | SPLIT_INST_FAIL at multiple sites (HAJ0158 , HAJ0140 , RAB0473 , RIY0212 ) | 09/10/2025 17:24:52 | Minor | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 09/10/2025 17:24:52 | P3 | SRAN | makkah | Sceco | DWDM NSA | (HAJ0158 , HAJ0140 , RAB0473 , RIY0212 ) | FLM_TE | [8 empty] | API | 09/10/2025 17:25:09 | 09/11/2025 04:38:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000260 | PCM-20250911-00000620 | TT-20250911-00716 | Reference_telecom | Region_3 | MDN6072 | MDN6072 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 09/11/2025 06:35:23 | 09/25/2025 17:26:27 | 09/11/2025 12:35:23 | RFC Port Underpower at MDN6072-Sector C-DCU @ Sceco | 09/10/2025 18:44:35 | Major | 29803 | RFC Port Underpower | 09/10/2025 18:49:08 | P3 | SRAN | madinah | Sceco | LTE NSA | MDN6072 | FLM_TE | [8 empty] | API | 09/11/2025 06:35:23 | 09/11/2025 09:10:11 | [6 empty] | Mobily |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250911000264 | PCM-20250911-00000624 | TT-20250911-00720 | Reference_telecom | Region_2 | RIY2M2802 | RIY2802 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 09/11/2025 06:36:19 | 10/16/2025 21:23:51 | 09/11/2025 12:36:19 | GSM Cell out of Service at RIY2M2802-P2 @ Sceco(ref:TT-20250619-00725) | 05/11/2025 10:40:01 | Major | 21801 | GSM Cell out of Service | 05/11/2025 10:40:01 | P2 | 2G | riyadh | Sceco | 2G SA | RIY2M2802 | FLM_TE | [8 empty] | API | 09/11/2025 06:36:19 | 09/11/2025 09:45:57 | 10/16/2025 21:23:40 |  |  | 10/16/2025 21:23:51 |  | Mubashar Farooq Abdul Majeed | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000271 | PCM-20250911-00000635 | TT-20250911-00730 | Reference_telecom | Region_2 | RIY2M8208 | RIY2208 |  |  |  | Ejaz Hussain Muhammad Sharif | 09/11/2025 06:46:06 | 09/29/2025 11:11:52 | 09/11/2025 12:46:06 | Cell Unavailable at RIY2M8208-P1-VIP-L800 @ Generator_SG (Ref:TT-20250424-00401) | 04/04/2025 18:21:05 | Major | 29240 | Cell Unavailable | 04/04/2025 18:21:05 | VIP | 4G | riyadh | Generator_SG | LTE SA | RIY2M8208 | FLM_TE | [8 empty] | API | 09/11/2025 06:46:06 | 09/11/2025 08:53:07 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000331 | PCM-20250911-00000767 | TT-20250911-00722 | Reference_EM | Region_2 | RIY2003 | RIY2003 |  |  |  | Touseef Iqbal Mazhar Iqbal | 09/11/2025 08:10:57 | 09/29/2025 11:11:54 | 09/11/2025 14:10:57 | 1(3G/LTE) site down at RIY2003-P3_SRAN @ Generator_SG(Ref:TT-20240710-00294) | 06/16/2024 03:06:53 | Major | 29249 | eNodeB Out of Service | 06/16/2024 03:06:53 | P3 | SRAN | muzamiah | Generator_SG | 3G_LTE SA | RIY2003 | FLM_TE |  |  | PCM-20250911-00000627 | old case vandalism issue /Zain O-M its fall down site and WL equipment still need to install /Issue escalated Zain | old case vandalism issue /Zain O-M its fall down site and WL equipment still need to install /Issue escalated Zain |  |  |  | API | 09/11/2025 08:10:57 | 09/11/2025 08:16:20 | [6 empty] | ZAIN O-M |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20250911000401 | PCM-20250911-00000881 | TT-20250911-00935 | EM | [7 empty] | 09/11/2025 09:05:36 | 09/11/2025 09:05:36 | 09/11/2025 21:05:36 | NETECO: Door Status Sensor Alarm at HMBY0324 @ Sceco | 09/11/2025 09:05:26 | Minor | 5152 | Door Status Sensor Alarm | 09/11/2025 09:05:26 | P3 | SRAN |  | Sceco | 2G NSA | HMBY0324 | FLM_EM | [8 empty] | API | 09/11/2025 09:05:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20250911000402 | PCM-20250911-00000882 | TT-20250911-00936 | EM | [7 empty] | 09/11/2025 09:06:10 | 09/11/2025 09:06:10 | 09/11/2025 21:06:10 | Door opening alarm at HMBY0324-P3_SRAN @ Sceco | 09/11/2025 09:05:33 | Minor | 65101 | Door opening alarm | 09/11/2025 09:05:30 | P3 | SRAN |  | Sceco | 2G NSA | HMBY0324 | FLM_EM | [8 empty] | API | 09/11/2025 09:06:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20250911000651 | PCM-20250911-00001309 | TT-20250911-01336 | Reference_telecom | Region_2 | RIY2208 | RIY2208 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Ejaz Hussain Muhammad Sharif | 09/11/2025 12:59:26 | 09/29/2025 15:02:55 | 09/12/2025 00:59:26 | RF Unit RX Channel RTWP/RSSI Unbalanced at RIY2208-P1-VIP-SRAN @ Generator_SG | 09/11/2025 09:59:22 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 09/11/2025 09:59:16 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2208 | FLM_TE | [8 empty] | API | 09/11/2025 12:59:26 | 09/29/2025 15:02:55 | [5 empty] | Ejaz Hussain Muhammad Sharif | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000838 | PCM-20250911-00001584 | TT-20250908-02389 | MW_HC | Region_1 | JBKH0095 | JBKH0095 |  |  |  | Mohamed Abdelaziz | 09/11/2025 14:50:05 | 09/16/2025 19:14:21 | 09/12/2025 02:50:05 | NEC MW HC_P1 Observing Performance Issue at JBKH0095(10.76.111.226)--JBKH2094(10.76.111.227) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBKH0095(10.76.111.226)--JBKH2094(10.76.111.227) | FLM_TE |  |  | PCM-20250911-00001493 | put link performance under sufficient monitor period then close ticket | put link performance under sufficient monitor period then close ticket |  |  |  | API | 09/11/2025 14:50:05 | 09/11/2025 18:14:43 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000839 | PCM-20250911-00001585 | TT-20250908-02395 | MW_HC | Region_1 | JBKH0088 | JBKH0088 |  |  |  | Mohamed Abdelaziz | 09/11/2025 14:50:41 | 09/16/2025 19:14:22 | 09/12/2025 02:50:41 | NEC MW HC_P0 Observing Performance Issue at JBKH0088(10.76.118.71)--JBKH0114(10.76.118.78) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH0088(10.76.118.71)--JBKH0114(10.76.118.78) | FLM_TE |  |  | PCM-20250911-00001491 | put link performance under sufficient monitor period then close ticket | put link performance under sufficient monitor period then close ticket |  |  |  | API | 09/11/2025 14:50:41 | 09/11/2025 18:14:43 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000840 | PCM-20250911-00001589 | TT-20250908-02379 | MW_HC | Region_1 | JBKH0110 | JBKH0110 |  |  |  | Mohamed Abdelaziz | 09/11/2025 14:51:08 | 09/16/2025 19:14:23 | 09/12/2025 02:51:08 | NEC MW HC_P0 Observing Performance Issue at JBKH0110(10.159.106.231)--JBKH0111(10.159.106.232) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P1 | SRAN | jubail | Generator_SG | TX NSA | JBKH0110(10.159.106.231)--JBKH0111(10.159.106.232) | FLM_TE |  |  | PCM-20250911-00001495 | put link performance under sufficient monitor period then close ticket | put link performance under sufficient monitor period then close ticket |  |  |  | API | 09/11/2025 14:51:08 | 09/11/2025 18:14:44 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000861 | PCM-20250911-00001610 | TT-20250911-01253 | Reference_telecom | Region_3 | MDN2M1017 | MDN0017 |  |  |  | Hussain Ahmad Sultan Muhammad | 09/11/2025 15:01:52 | 10/01/2025 15:55:31 | 09/12/2025 03:01:52 | External Clock Reference Problem at MDN2M1017-P1-HRMCST @ Sceco | 09/11/2025 09:23:43 | Minor | 26262 | External Clock Reference Problem | 09/11/2025 09:20:19 | P1 | 2G | madinah | Sceco | 2G NSA | MDN2M1017 | FLM_TE |  | Dear TX Team kindly check as IP CLK unavailable DSP BTSIPCLK Link Status Result ------------------------------- Port No. Client IP Server IP Link State Active State NULL 10.150.24.70 10.161.136.137 Unavailable Activated NULL 10.150.24.70 10.161.137.137 Unavailable Not Activated | PCM-20250911-00001364 | kindly check link MDN0016<>MDN0783 suffer MW alarms | kindly check link MDN0016<>MDN0783 suffer MW alarms |  |  |  | API | 09/11/2025 15:01:52 | 09/12/2025 21:57:36 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000915 | PCM-20250911-00001695 | TT-20250911-01668 | Reference_telecom | Region_1 | JBL2108 | JBL2108 |  |  |  | Tahir Mahmood Hafiz Yar | 09/11/2025 15:41:52 | 09/16/2025 19:14:20 | 09/12/2025 03:41:52 | MW RTN Observing MW_LOF,RADIO_RSL_LOW at JBL2108_NE_19_V | 09/06/2025 21:29:52 | Minor |  | LOF | 09/06/2025 21:29:52 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBL2108_NE_19_V | FLM_TE | [8 empty] | API | 09/11/2025 15:41:52 | 09/11/2025 16:39:52 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000938 | PCM-20250911-00001718 | TT-20250911-01691 | Reference_telecom | Region_3 | RSP2801 | RSP2801 |  |  |  | Muhammad Sajjad R3 | 09/11/2025 15:42:18 | 09/16/2025 19:14:20 | 09/12/2025 03:42:18 | MW RTN Observing PG_PRT_DEGRADED at RSP2801_NE_1 | 09/07/2025 18:43:47 | Minor |  | LOF | 09/07/2025 18:43:47 | VIP | SRAN | yanbu | Sceco | TX NSA | RSP2801_NE_1 | FLM_TE | [8 empty] | API | 09/11/2025 15:42:18 | 09/11/2025 16:23:33 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911000940 | PCM-20250911-00001720 | TT-20250911-01693 | Reference_telecom | Region_2 | RIYA6060 | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 09/11/2025 15:42:20 | 09/22/2025 13:00:19 | 09/12/2025 03:42:20 | MW RTN Observing ETH_LOS at RIYA6060_NE_2 | 08/21/2025 12:09:12 | Minor |  | LOF | 08/21/2025 12:09:12 | P3 | SRAN | riyadh | Sceco | TX NSA | RIYA6060_NE_2 | FLM_TE | [8 empty] | API | 09/11/2025 15:42:20 | 09/13/2025 09:43:47 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250911001068 | PCM-20250911-00001933 | TT-20250911-01852 | Reference_telecom | Region_6 | ABH0018 | ABH0018 | Transsmission | MW_Problematic | Fading Issue | Muhammad Jamshaid Muhammad Ashraf | 09/11/2025 17:07:24 | 10/06/2025 22:01:29 | 09/12/2025 05:07:24 | Nokia Eband Observing DemFail-Channel 1A,DemFail-Channel 1B at ABH0018_02-10.10.155.89 | 05/13/2025 00:18:29 | Minor |  | LOF | 05/13/2025 00:18:29 | VIP | 2G | abha | Sceco_STB | TX NSA | ABH0018_02-10.10.155.89 | FLM_TE | [8 empty] | API | 09/11/2025 17:07:24 | 10/06/2025 21:59:13 | 10/06/2025 22:00:25 |  |  | 10/06/2025 22:01:29 |  | Muhammad Jamshaid Muhammad Ashraf | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250911001163 | PCM-20250911-00002027 | TT-20250911-01945 | Reference_telecom | Region_6 | ABDB9019 | ABDB9019 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Amir Sohail | 09/11/2025 17:09:15 | 10/19/2025 17:54:29 | 09/12/2025 05:09:15 | NEC MW Observing RX Level,RX Level,LOF,LOF,MODEM Power Supply Alarm,MODEM Power Supply Alarm at ABDB9019_1(10.154.163.180) | 07/30/2025 17:00:58 | Minor |  | LOF | 07/30/2025 17:00:58 | P1 | Repeater | abha | Sceco_STB | TX NSA | ABDB9019_1(10.154.163.180) | FLM_TE | [8 empty] | API | 09/11/2025 17:09:15 | 09/11/2025 17:22:44 | 09/13/2025 13:44:35 |  |  | 10/19/2025 17:54:29 |  | Amir Sohail | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001165 | PCM-20250911-00002029 | TT-20250911-01947 | Reference_telecom | Region_6 | ABDB9020 | ABDB9020 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/11/2025 17:09:17 | 09/30/2025 11:12:16 | 09/12/2025 05:09:17 | NEC MW Observing Communication FAIL at ABDB9020(10.1.170.225) | 09/02/2025 14:50:05 | Minor |  | LOF | 09/02/2025 14:50:05 | P3 | Repeater | mohail | Sceco | TX NSA | ABDB9020(10.1.170.225) | FLM_TE | [8 empty] | API | 09/11/2025 17:09:17 | 09/11/2025 19:22:17 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001187 | PCM-20250911-00002051 | TT-20250911-01969 | Reference_telecom | Region_1 | DMH0105 | DMH0105 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/11/2025 17:09:43 | 09/16/2025 19:14:25 | 09/12/2025 05:09:43 | NEC MW Observing High BER,High BER,LOF,LOF,Frame ID,Frame ID at DMH0105-2(10.159.105.132) | 09/03/2025 21:07:52 | Minor |  | LOF | 09/03/2025 21:07:52 | P1 | SRAN | hafr | Generator_SG | TX NSA | DMH0105-2(10.159.105.132) | FLM_TE | [8 empty] | API | 09/11/2025 17:09:43 | 09/11/2025 18:27:27 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001200 | PCM-20250911-00002064 | TT-20250911-01982 | Reference_telecom | Region_1 | JBKH0088 | JBKH0088 |  |  |  | Mohamed Abdelaziz | 09/11/2025 17:09:57 | 09/16/2025 19:14:24 | 09/12/2025 05:09:57 | NEC MW Observing Low BER,LOF,LOF,Frame ID,Frame ID at JBKH0088-2(10.76.118.70) | 09/03/2025 20:32:24 | Minor |  | LOF | 09/03/2025 20:32:24 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH0088-2(10.76.118.70) | FLM_TE | [8 empty] | API | 09/11/2025 17:09:57 | 09/11/2025 18:14:44 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001201 | PCM-20250911-00002065 | TT-20250911-01983 | Reference_telecom | Region_1 | JBKH0110 | JBKH0110 |  |  |  | Mohamed Abdelaziz | 09/11/2025 17:09:58 | 09/16/2025 19:14:24 | 09/12/2025 05:09:58 | NEC MW Observing LOF,Frame ID,LOF,Frame ID,Low BER at JBKH0110(10.159.106.230) | 09/03/2025 21:14:09 | Minor |  | LOF | 09/03/2025 21:14:09 | P1 | SRAN | jubail | Generator_SG | TX NSA | JBKH0110(10.159.106.230) | FLM_TE | [8 empty] | API | 09/11/2025 17:09:58 | 09/11/2025 18:14:44 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001207 | PCM-20250911-00002071 | TT-20250911-01989 | Reference_telecom | Region_4 | JED0741 | JED0741 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/11/2025 17:10:05 | 10/07/2025 13:39:52 | 09/12/2025 05:10:05 | NEC MW Observing ODU CPU / Cable Open,LOF at JED0741(10.1.168.225) | 09/03/2025 23:14:09 | Minor |  | LOF | 09/03/2025 23:14:09 | P2 | 2G | jeddah | Sceco | TX NSA | JED0741(10.1.168.225) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:05 | 09/11/2025 17:41:23 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001213 | PCM-20250911-00002077 | TT-20250911-01995 | Reference_telecom | Region_1 | KBR0197 | KBR0197 |  |  |  | Talha Manzoor | 09/11/2025 17:10:11 | 09/16/2025 19:14:28 | 09/12/2025 05:10:11 | NEC MW Observing LOF,LOF,RX Level,RX Level,RX Level,RX Level,LOF,LOF,Radio Traffic Aggregation Link at KBR0197(10.3.202.2) | 09/09/2025 22:01:50 | Minor |  | LOF | 09/09/2025 22:01:50 | P3 | SRAN | dammam | Sceco | TX NSA | KBR0197(10.3.202.2) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:11 | 09/11/2025 20:38:03 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001227 | PCM-20250911-00002091 | TT-20250911-02009 | Reference_telecom | Region_3 | MDN0745 | MDN0745 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Hamayo Din Jalal | 09/11/2025 17:10:26 | 09/16/2025 19:12:16 | 09/12/2025 05:10:26 | NEC MW Observing LOF,LOF,RX Level,Radio Traffic Aggregation Link,LOF,RX Level,LOF,RX Level,RX Level at MDN0745-MDN0720(10.154.83.113) | 09/06/2025 15:00:13 | Minor |  | LOF | 09/06/2025 15:00:13 | P1 | SRAN | madinah | Sceco | TX NSA | MDN0745-MDN0720(10.154.83.113) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:26 | 09/16/2025 19:12:16 | [5 empty] | Hamayo Din Jalal | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001232 | PCM-20250911-00002096 | TT-20250911-02014 | Reference_telecom | Region_5 | MKJD0569 | MKJD0569 |  |  |  | Amjad Ali Muhammad Parves | 09/11/2025 17:10:31 | 09/24/2025 02:28:27 | 09/12/2025 05:10:31 | NEC MW Observing LOF,LOF,Frame ID,High BER at MKJD0569-5(10.99.249.65) | 07/27/2025 13:42:08 | Minor |  | LOF | 07/27/2025 13:42:08 | P1 | 2G | makkah | Sceco_STB | TX NSA | MKJD0569-5(10.99.249.65) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:31 | 09/24/2025 02:28:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001235 | PCM-20250911-00002099 | TT-20250911-02018 | Reference_telecom | Region_5 | MKJD0651 | MKJD0651 |  |  |  | Sohail Ashraf Muhammad Ashraf | 09/11/2025 17:10:35 | 09/28/2025 17:45:03 | 09/12/2025 05:10:35 | NEC MW Observing ODU CPU / Cable Open,LOF at MKJD0651(10.99.249.66) | 07/27/2025 13:42:08 | Minor |  | LOF | 07/27/2025 13:42:08 | P1 | 2G | makkah | Sceco | TX NSA | MKJD0651(10.99.249.66) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:35 | 09/13/2025 07:33:36 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001251 | PCM-20250911-00002115 | TT-20250911-02034 | Reference_telecom | Region_6 | SDA0322 | SDA0322 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 09/11/2025 17:10:52 | 09/11/2025 17:59:58 | 09/12/2025 05:10:52 | NEC MW Observing XIF,ODU CPU / Cable Open,MODEM Power Supply Alarm,ODU Power Supply at SDA0322(10.154.163.200) | 08/30/2025 09:17:24 | Minor |  | LOF | 08/30/2025 09:17:24 | P3 | 2G | abha | Sceco | TX NSA | SDA0322(10.154.163.200) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:52 | 09/11/2025 17:59:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001257 | PCM-20250911-00002121 | TT-20250911-02040 | Reference_telecom | Region_6 | SDA0426 | SDA0426 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 09/11/2025 17:10:58 | 09/11/2025 17:59:59 | 09/12/2025 05:10:58 | NEC MW Observing XIF,XIF,MODEM Power Supply Alarm,MODEM Power Supply Alarm,Power Supply,LOF,RX Level at SDA0426(10.154.163.198) | 08/29/2025 13:46:53 | Minor |  | LOF | 08/29/2025 13:46:53 | P3 | 2G | abha | Sceco | TX NSA | SDA0426(10.154.163.198) | FLM_TE | [8 empty] | API | 09/11/2025 17:10:58 | 09/11/2025 17:59:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250911001260 | PCM-20250911-00002124 | TT-20250911-02043 | Reference_telecom | Region_3 | YBDB0300 | YBDB0300 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Hossam Ali Ahmed Ali | 09/11/2025 17:11:02 | 09/20/2025 20:04:08 | 09/12/2025 05:11:02 | NEC MW Observing Radio Traffic Aggregation Link at YBDB0300(10.159.105.232) | 09/08/2025 03:00:31 | Minor |  | LOF | 09/08/2025 03:00:31 | P3 | SRAN | tabouk | Generator_SG | TX NSA | YBDB0300(10.159.105.232) | FLM_TE | [8 empty] | API | 09/11/2025 17:11:02 | 09/19/2025 11:40:28 | 09/20/2025 20:03:52 |  |  | 09/20/2025 20:04:08 |  | Hossam Ali Ahmed Ali | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250911001261 | PCM-20250911-00002125 | TT-20250911-02044 | Reference_telecom | Region_1 | RYHR0120 | RYHR0120 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Ahsan Ul Haq Amtiaz Ali | 09/11/2025 17:11:03 | 09/17/2025 17:34:45 | 09/12/2025 05:11:03 | NEC MW Observing High BER at RYHR0120(10.147.0.67) | 09/03/2025 21:06:38 | Minor |  | LOF | 09/03/2025 21:06:38 | P1 | SRAN | hafr | Sceco_STB | TX NSA | RYHR0120(10.147.0.67) | FLM_TE | [8 empty] | API | 09/11/2025 17:11:03 | 09/17/2025 13:22:20 | 09/17/2025 14:19:31 | 09/17/2025 14:20:00 | 09/17/2025 16:35:00 | 09/17/2025 17:34:45 |  | Ahsan Ul Haq Amtiaz Ali | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250911001416 | PCM-20250911-00002359 | TT-20250911-02238 | Telecom | Region_4 | JED0102-SF-CSG-01 | JED0102 |  |  |  | BARKAT ALI MAIN HILAL | 09/11/2025 18:49:16 | 09/11/2025 19:18:58 | 09/12/2025 06:49:16 | Visibility down at JED0102-SF-CSG-01 | 09/11/2025 18:47:55 | Minor | 15269 | LOS | 09/11/2025 18:47:55 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0102-SF-CSG-01 | FLM_TE | [8 empty] | API | 09/11/2025 18:49:16 | 09/11/2025 19:18:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250912000433 | PCM-20250912-00000852 | TT-20250912-00224 | Telecom | Region_5 | MAK1U6334 | MAK6034 |  |  |  | Atif Javed Javed Hussain | 09/12/2025 12:14:52 | 09/28/2025 17:45:05 | 09/12/2025 18:14:52 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at MAK1U6334-P2 @ Sceco | 09/12/2025 03:21:05 | Major | 7771 | WCDMA CELL OUT OF USE | 07/22/2025 18:26:45 | P3 | 3G | makkah | Sceco | 3G SA | MAK1U6334 | FLM_TE |  |  | PCM-20250912-00000246 | Please check and close | Please check and close |  |  |  | API | 09/12/2025 12:14:52 | 09/15/2025 14:17:27 | [6 empty] | Mobily |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250912000486 | PCM-20250912-00000931 | TT-20250912-00932 | Reference_telecom | Region_6 | BRQ0414 | BRQ0414 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 09/12/2025 13:22:24 | 10/13/2025 21:01:59 | 09/13/2025 01:22:24 | LossOfSignal observed in BRQ0414_01 towards 10.74.121.101 @ Sceco | 09/12/2025 01:22:27 | Minor |  | LossOfSignal | 09/12/2025 01:22:17 | P2 | 2G | mohail | Sceco | TX NSA | BRQ0414 | FLM_TE | [8 empty] | API | 09/12/2025 13:22:24 | 09/12/2025 14:21:24 | 10/13/2025 21:01:43 |  |  | 10/13/2025 21:01:59 |  | Muhammad Jamal Khan Abbas Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250912000959 | PCM-20250912-00001637 | TT-20250912-00754 | Telecom | Region_1 | HMBY0984 | HMBY0984 |  |  |  | Talha Manzoor | 09/12/2025 21:18:37 | 09/16/2025 19:14:33 | 09/13/2025 09:18:37 | As per visibility report NEC MW Observing Visibility down at 3 NEs under HMBY0984 IP 10.21.217.194 | 09/12/2025 10:49:54 | Minor | 2 | NE_NOT_LOGIN | 09/12/2025 10:49:56 | P3 | SRAN | dammam | Sceco | TX NSA | HMBY0984 10.21.217.194 HMBY2500 10.21.217.195 | FLM_TE |  |  | PCM-20250912-00001566 | need check HMBY0984 locally as down visibility from our side | need check HMBY0984 locally as down visibility from our side |  |  |  | API | 09/12/2025 21:18:37 | 09/13/2025 01:17:02 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913000117 | PCM-20250913-00000211 | TT-20250913-00133 | Reference_telecom | Region_1 | KBR6054 | KBR6054 |  |  |  | Meraj Husain Idd Baksh | 09/13/2025 02:06:17 | 09/16/2025 19:14:34 | 09/13/2025 08:06:17 | RF Unit VSWR Threshold Crossed at KBR6054-DCU2 @ Sceco | 09/12/2025 23:01:59 | Major | 26529 | RF Unit VSWR Threshold Crossed | 09/12/2025 23:05:58 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6054 | FLM_TE | [8 empty] | API | 09/13/2025 02:06:17 | 09/13/2025 06:32:49 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913000241 | PCM-20250913-00000413 | TT-20250913-00305 | Telecom | Region_2 | RIYD6159 | RIYD6159 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 09/13/2025 05:33:59 | 10/07/2025 13:39:52 | 09/13/2025 17:33:59 | DCU Optical Module Transmit/Receive Fault at RIYD6159-DCU2 @ Sceco | 09/13/2025 05:30:57 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 09/13/2025 05:29:25 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYD6159 | FLM_TE | [8 empty] | API | 09/13/2025 05:33:59 | 09/15/2025 14:01:06 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913000605 | PCM-20250913-00001027 | TT-20250913-00815 | Telecom | Region_4 | JED2007 | JED2007 | Transsmission | MW_Connectors | Remade Indoor MW Connector | MALIK ATIF ZAMAN | 09/13/2025 11:52:31 | 10/08/2025 09:44:26 | 09/13/2025 23:52:31 | NEC MW Observing Visibility Issue on 2 Nes under JED2007 010.154.153.122 Cluster JED0190 | 09/13/2025 11:52:04 | Minor | 113388 | LOF | 09/13/2025 11:52:03 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED2007 010.154.153.122, SJED0165 010.154.153.123 | FLM_TE | [5 empty] | NEC MW Observing Visibility Issue on 2 Nes under JED2007 010.154.153.122 Cluster JED0190 |  |  | API | 09/13/2025 11:52:31 | 10/08/2025 09:44:26 | [5 empty] | MALIK ATIF ZAMAN | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913000615 | PCM-20250913-00001049 | TT-20250913-00832 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 09/13/2025 12:01:55 | 09/14/2025 04:20:07 | 09/13/2025 18:01:55 | Observing ALU CIDs flapped and restored | 09/13/2025 11:58:44 | Major | 5000003 | Link Down | 09/13/2025 11:58:44 | P1 | BSC | makkah | Sceco | IPBB NSA | Observing ALU CIDs flapped and restored | FLM_TE | [8 empty] | API | 09/13/2025 12:01:55 | 09/14/2025 04:20:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913000887 | PCM-20250913-00001470 | TT-20250908-02380 | MW_HC | Region_1 | DMJR0137 | DMJR0137 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/13/2025 15:53:01 | 09/24/2025 14:28:57 | 09/14/2025 03:53:01 | NEC MW HC_P1 Observing Performance Issue at DMJR0137(10.76.116.141)--DMJR0137(10.76.116.142) | 09/08/2025 17:52:03 | Minor |  | LOF | 09/08/2025 17:52:03 | P2 | SRAN | hafr | Sceco_STB | TX NSA | DMJR0137(10.76.116.141)--DMJR0137(10.76.116.142) | FLM_TE | DMJR0137 | Dear Team , Link is flapping , kindly check this issue as we observing PM_Error | PCM-20250913-00001433 | Dear Team , Link is flapping , kindly check this issue as we observing PM_Error | Dear Team , Link is flapping , kindly check this issue as we observing PM_Error |  |  |  | API | 09/13/2025 15:53:01 | 09/13/2025 16:38:08 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913001027 | PCM-20250913-00001716 | TT-20250913-01413 | Reference_telecom | Region_1 | JBL2384 | JBL2384 | Transsmission | SFP_Transmission | Reset SFP | Tahir Mahmood Hafiz Yar | 09/13/2025 17:41:23 | 09/14/2025 16:08:24 | 09/14/2025 05:41:23 | ETH_LOS at JBL2384_NE_4_V @ Sceco | 09/13/2025 13:41:20 | Minor | 1-235 | ETH_LOS | 09/13/2025 13:41:11 | P3 | SRAN | jubail | Sceco | TX NSA | JBL2384 | FLM_TE | [8 empty] | API | 09/13/2025 17:41:23 | 09/14/2025 16:08:24 | [5 empty] | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250913001041 | PCM-20250913-00001736 | TT-20250913-01433 | EM | Region_3 | RUSF9040 | RUSF9040 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 09/13/2025 17:52:07 | 09/25/2025 17:45:05 | 09/13/2025 21:52:07 | RELAY_ALARM_CRITICAL at RUSF9040_NE_1 @ Power cube | 09/11/2025 18:10:16 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 09/13/2025 17:47:08 | P3 | Repeater | madinah | Sceco_STB | TX NSA | RUSF9040_NE_1 | FLM_EM | [5 empty] | RELAY_ALARM_CRITICAL at RUSF9040_NE_1 @ Power cube |  |  | API | 09/13/2025 17:52:07 | 09/21/2025 12:33:20 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250914000019 | PCM-20250914-00000024 | TT-20250914-00021 | Telecom | Region_6 | DRB0901 | DRB0901 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 09/14/2025 00:17:07 | 09/14/2025 03:20:08 | 09/14/2025 12:17:07 | ODU CPU / Cable Open at DRB0901 on 10.154.170.167 @ Generator_SG | 09/14/2025 00:16:23 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 09/14/2025 00:10:52 | P3 | 2G | derb | Generator_SG | TX NSA | DRB0901 | FLM_TE | [8 empty] | API | 09/14/2025 00:17:07 | 09/14/2025 03:20:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250914000057 | PCM-20250914-00000138 | TT-20250914-00087 | EM | Region_2 | RIYA2U6192b | RIYA6092 |  |  |  | Tanveer Ahmad Fateh Muhammad | 09/14/2025 01:11:23 | 09/28/2025 11:46:06 | 09/14/2025 07:11:23 | Door opening alarm at RIYA2U6192B-P1-VIP-SHOP @ Sceco | 09/14/2025 01:11:06 | Major | 65101 | Door opening alarm | 09/14/2025 01:11:04 | VIP | 2G | riyadh | Sceco | 2G NSA | RIYA2U6192B | FLM_EM | [8 empty] | API | 09/14/2025 01:11:23 | 09/14/2025 16:27:12 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250914000065 | PCM-20250914-00000150 | TT-20250914-00104 | Reference_EM | Region_2 | RIYA2U6192b | RIYA6092 |  |  |  | Tanveer Ahmad Fateh Muhammad | 09/14/2025 01:21:11 | 09/28/2025 11:46:07 | 09/14/2025 07:21:11 | Minor Rec. alarm at RIYA2U6192B-P1-VIP-SHOP @ Sceco | 09/14/2025 01:11:10 | Major | 65108 | Minor Rec. alarm | 09/14/2025 01:11:04 | VIP | 2G | riyadh | Sceco | 2G NSA | RIYA2U6192B | FLM_EM | [8 empty] | API | 09/14/2025 01:21:11 | 09/14/2025 16:27:13 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250914000066 | PCM-20250914-00000151 | TT-20250914-00105 | Reference_EM | Region_2 | RIYA2U6192a | RIYA6092 |  |  |  | Tanveer Ahmad Fateh Muhammad | 09/14/2025 01:21:42 | 09/28/2025 11:46:08 | 09/14/2025 07:21:42 | Major Rec. alarm at RIYA2U6192A-P1-VIP-SHOP @ Sceco | 09/14/2025 01:11:17 | Major | 65107 | Major Rec. alarm | 09/14/2025 01:11:14 | VIP | 2G | riyadh | Sceco | 2G NSA | RIYA2U6192A | FLM_EM | [8 empty] | API | 09/14/2025 01:21:42 | 09/14/2025 16:27:14 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20250914000118 | PCM-20250914-00000294 | TT-20250914-00238 | Reference_telecom | Region_2 | RY4 | RY4 |  |  |  | Saddam hussain muhammad khan | 09/14/2025 03:22:34 | 09/22/2025 13:00:21 | 09/14/2025 15:22:34 | POWER_ABNORMAL at RY4_NE_11 @ Sceco_STB | 09/14/2025 01:52:33 | Minor | 1-412 | POWER_ABNORMAL | 09/14/2025 01:52:21 | P1 | BSC | riyadh | Sceco_STB | TX NSA | RY4 | FLM_TE | [8 empty] | API | 09/14/2025 03:22:34 | [7 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250914000181 | PCM-20250914-00000429 | TT-20250914-00319 | Reference_telecom | Region_2 | RIY2M8304 | RIY2304 |  |  |  | Azmat Ali Madad | 09/14/2025 04:56:14 | 09/29/2025 11:12:01 | 09/14/2025 16:56:14 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M8304-CA-L800-P3 @ Generator_SG | 09/14/2025 01:20:06 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 09/14/2025 01:20:02 | P3 | 4G | riyadh | Generator_SG | 2G NSA | RIY2M8304 | FLM_TE |  | Dears Kindly check HW | PCM-20250914-00000387 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 09/14/2025 04:56:14 | 09/14/2025 12:24:48 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250914000490 | PCM-20250914-00000955 | TT-20250914-00781 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 09/14/2025 10:31:29 | 09/14/2025 10:31:29 | 09/14/2025 16:31:29 | Observing ALU CIDs flapped and restored | 09/14/2025 10:29:02 | Major | 5000003 | Link Down | 09/14/2025 10:29:02 | P1 | BSC | makkah | Sceco | IPBB NSA | Observing ALU CIDs flapped and restored | FLM_TE | [8 empty] | API | 09/14/2025 10:31:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250914000595 | PCM-20250914-00001132 | TT-20250914-00968 | EM | Region_4 | JED1U6786 | JED6086 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 09/14/2025 12:09:59 | 10/07/2025 19:01:05 | 09/15/2025 00:09:59 | RECTIFIER MAINS POWER FAILURE at JED1U6786-G9-L18-L21-SBTS-P3 @ Sceco | 09/14/2025 12:01:57 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 09/14/2025 12:01:43 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6786 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 09/14/2025 12:09:59 | 10/07/2025 19:01:05 | [5 empty] | Mohamed Farag Abdelbary | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250914000796 | PCM-20250914-00001499 | TT-20250914-01344 | EM | Region_2 | RIYA2U6180 | RIYA6080 |  |  |  | Tanveer Ahmad Fateh Muhammad | 09/14/2025 14:53:45 | 09/16/2025 19:14:41 | 09/14/2025 20:53:45 | High temperature 32C alarm at RIYA2U6180-P1-VIP @ Sceco | 09/14/2025 14:43:46 | Major | 65102 | High temperature 32C alarm | 09/14/2025 14:43:40 | VIP | 2G | riyadh | Sceco | 2G NSA | RIYA2U6180 | FLM_EM | [8 empty] | API | 09/14/2025 14:53:45 | 09/14/2025 16:27:18 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250914001153 | PCM-20250914-00002078 | TT-20250914-01922 | MW_HC | Region_2 | RIY0671 | RIY0671 |  |  |  | Ejaz Hussain Muhammad Sharif | 09/14/2025 18:55:55 | 09/14/2025 18:56:15 | 09/15/2025 06:55:55 | Huawei MW HC_P2 Observing Errors at RIY0671-RIY2513 | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0671-RIY2513 | FLM_TE | [8 empty] | API | 09/14/2025 18:55:55 | 09/14/2025 18:56:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250914001154 | PCM-20250914-00002079 | TT-20250914-01923 | MW_HC | Region_2 | RIY0317 | RIY0317 |  |  |  | Khan zeb Shah nawaz | 09/14/2025 18:55:56 | 09/15/2025 09:08:33 | 09/15/2025 06:55:56 | Huawei MW HC_P2 Observing Errors at RIY0317-RIY0200 | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P3 | SRAN | riyadh | Sceco | TX NSA | RIY0317-RIY0200 | FLM_TE | [8 empty] | API | 09/14/2025 18:55:56 | 09/15/2025 09:08:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250914001157 | PCM-20250914-00002082 | TT-20250914-01927 | MW_HC | Region_2 | KHJ0001 | KHJ0001 | Transsmission | MW_RSL_fading | Fading issue | Hakim Ullah Raif Ullah Jan | 09/14/2025 18:56:00 | 10/06/2025 05:24:58 | 09/15/2025 06:56:00 | Huawei MW HC_P2 Observing Errors at KHJ0001-KHJ0003 | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P2 | SRAN | al kharj | Power Cube | TX NSA | KHJ0001-KHJ0003 | FLM_TE | [8 empty] | API | 09/14/2025 18:56:00 | 09/29/2025 13:15:18 | 10/06/2025 05:23:58 |  |  | 10/06/2025 05:24:58 |  | Hakim Ullah Raif Ullah Jan | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250914001186 | PCM-20250914-00002111 | TT-20250914-01957 | MW_HC | Region_6 | SDA0322 | SDA0322 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 09/14/2025 18:56:32 | 09/17/2025 20:14:44 | 09/15/2025 06:56:32 | NEC MW HC_P2 Observing Modem Down at SDA0322(10.154.163.200)--SDA2294(10.154.163.199) | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P3 | 2G | abha | Sceco | TX NSA | SDA0322(10.154.163.200)--SDA2294(10.154.163.199) | FLM_TE | [8 empty] | API | 09/14/2025 18:56:32 | 09/14/2025 21:34:54 | 09/17/2025 20:14:44 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250914001187 | PCM-20250914-00002112 | TT-20250914-01958 | MW_HC | Region_6 | RYAB0627 | RYAB0627 |  |  |  | Ahmed Mamdouh Helal Helal | 09/14/2025 18:56:34 | 09/14/2025 18:58:39 | 09/15/2025 06:56:34 | NEC MW HC_P0 VIP Observing Performance Issue at RYAB0627(10.89.222.6)--WDS0725(10.89.222.4) | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P1 | 2G | wadi dawasar | Sceco_STB | TX NSA | RYAB0627(10.89.222.6)--WDS0725(10.89.222.4) | FLM_TE | [8 empty] | API | 09/14/2025 18:56:34 | 09/14/2025 18:58:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250914001189 | PCM-20250914-00002114 | TT-20250914-01960 | MW_HC | Region_6 | MHL0180 | MHL0180 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/14/2025 18:56:36 | 09/14/2025 19:11:31 | 09/15/2025 06:56:36 | NEC MW HC_P0 Observing Modem Down at MHL0180(10.154.172.3)--MHL9707(10.154.172.2) | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P2 | 2G | mohail | Sceco | TX NSA | MHL0180(10.154.172.3)--MHL9707(10.154.172.2) | FLM_TE | [8 empty] | API | 09/14/2025 18:56:36 | 09/14/2025 19:11:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250914001195 | PCM-20250914-00002120 | TT-20250914-01966 | MW_HC | Region_6 | DRB0908 | DRB0908 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 09/14/2025 18:56:42 | 10/23/2025 18:11:36 | 09/15/2025 06:56:42 | NEC MW HC_P0 Observing Performance Issue at DRB0908(10.154.164.50)--SHQ0048(10.154.164.51) | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P3 | 2G | derb | Sceco | TX NSA | DRB0908(10.154.164.50)--SHQ0048(10.154.164.51) | FLM_TE | [8 empty] | API | 09/14/2025 18:56:42 | 09/14/2025 19:19:51 | 10/23/2025 18:11:31 | 10/23/2025 18:11:34 | 10/23/2025 18:11:36 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250915000009 | PCM-20250915-00000017 | TT-20250915-00010 | Telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Muhammad Kashif M M Bashir | 09/15/2025 00:09:06 | 09/19/2025 11:38:08 | 09/15/2025 06:09:06 | RF Unit Optical Module Transmit/Receive Fault at HFF6036-DCU1 @ Sceco | 09/15/2025 00:07:14 | Major | 26503 | RF Unit Optical Module Transmit/Receive Fault | 08/25/2005 21:01:35 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 09/15/2025 00:09:06 | 09/15/2025 09:35:00 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250915000010 | PCM-20250915-00000016 | TT-20250915-00011 | Telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Muhammad Kashif M M Bashir | 09/15/2025 00:09:06 | 09/19/2025 11:38:09 | 09/15/2025 12:09:06 | RF Unit Maintenance Link Failure at HFF6036-DCU1 @ Sceco | 09/15/2025 00:07:14 | Minor | 26235 | RF Unit Maintenance Link Failure | 08/25/2005 20:18:57 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 09/15/2025 00:09:06 | 09/15/2025 09:35:00 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250915000232 | PCM-20250915-00000415 | TT-20250915-00461 | Reference_telecom | Region_2 | SAR0329 | SAR0329 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Raise Ahmed Nisar Ahmed | 09/15/2025 06:00:23 | 10/06/2025 11:10:11 | 09/15/2025 18:00:23 | POWER_ABNORMAL at SAR0329_NE_1 @ Generator_SG | 09/15/2025 05:24:14 | Minor | 1-412 | POWER_ABNORMAL | 09/15/2025 05:24:01 | P3 | SRAN | buraidah | Generator_SG | TX NSA | SAR0329 | FLM_TE | [8 empty] | API | 09/15/2025 06:00:23 | 09/15/2025 14:01:25 | 10/06/2025 11:08:49 |  |  | 10/06/2025 11:10:11 |  | Raise Ahmed Nisar Ahmed | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250915000324 | PCM-20250915-00000589 | TT-20250915-00603 | Telecom | Region_6 | BAH0005 | BAH0005 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SHAH KHALID | 09/15/2025 07:52:31 | 10/20/2025 11:00:10 | 09/15/2025 19:52:31 | NEC MW Observing Visibility Issue on 2 Nes under BAH0005010.154.160.193 Cluster BAH0005 | 09/15/2025 07:52:22 | Minor | 321339 | Demodulator Fail | 09/15/2025 07:52:20 | VIP | 2G | Albaha | Sceco | TX NSA | BAH0005010.154.160.193 , FS0017010.154.160.196 | FLM_TE | [5 empty] | NEC MW Observing Visibility Issue on 2 Nes under BAH0005010.154.160.193 Cluster BAH0005 |  |  | API | 09/15/2025 07:52:31 | 09/15/2025 16:57:26 | 10/20/2025 10:59:52 |  |  | 10/20/2025 11:00:10 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250915000643 | PCM-20250915-00001114 | TT-20250915-01070 | Telecom | Region_4 | HAW1M7298 | HAW0298 | Equipment | SFP_BTS | Clean SFP | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/15/2025 11:42:17 | 10/19/2025 08:46:14 | 09/15/2025 23:42:17 | PT::FLM need to perform HC at HAW1M7298 (Bo request) | 09/15/2025 11:41:57 | Minor | 676767671 | Health Check-WO to TE FME | 09/15/2025 11:41:57 | P2 | 4G | taif | Sceco | 2G_3G_LTE_5G NSA | HAW1M7298 | FLM_TE | [8 empty] | API | 09/15/2025 11:42:17 | 09/16/2025 12:23:49 | 10/19/2025 08:46:04 |  |  | 10/19/2025 08:46:14 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250915000738 | PCM-20250915-00001273 | TT-20250915-01242 | Telecom | Region_1 | DRN0769 | DRN0769 |  |  |  | Talha Manzoor | 09/15/2025 12:50:34 | 09/22/2025 10:43:09 | 09/16/2025 00:50:34 | ETH_LINK_DOWN at DRN0769_NE_6 @ Generator_SG | 09/15/2025 12:48:45 | Minor | 1-12793 | ETH_LINK_DOWN | 09/08/2025 03:30:01 | P3 | SRAN | dammam | Generator_SG | TX NSA | DRN0769 | FLM_TE | [8 empty] | API | 09/15/2025 12:50:34 | 09/15/2025 14:23:39 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250915000739 | PCM-20250915-00001272 | TT-20250915-01241 | Telecom | Region_1 | ARM0716 | ARM0716 |  |  |  | Talha Manzoor | 09/15/2025 12:50:34 | 09/22/2025 10:43:10 | 09/16/2025 00:50:34 | ETH_LINK_DOWN at ARM0716_RTN380_V @ Sceco | 09/15/2025 12:48:51 | Minor | 1-12793 | ETH_LINK_DOWN | 09/04/2025 18:48:45 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0716 | FLM_TE | [8 empty] | API | 09/15/2025 12:50:34 | 09/15/2025 14:23:40 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20250915000900 | PCM-20250915-00001530 | TT-20250912-00516 | Reference_telecom | [7 empty] | 09/15/2025 14:39:37 | 09/15/2025 14:39:37 | 09/15/2025 18:39:37 | observed alarm DualMaster at RIY at 12/9/2025 7:00 | 09/12/2025 07:00:15 | Critical | 987654321 | Complaint-No WO NSN | 09/12/2025 07:00:15 | P1 | BNG |  | Sceco_STB | BNG SA | N7750-SR12-RIY-BNG | FLM_TE |  |  | PCM-20250912-00000537 | these alarms created due to the IPBB board failure hardware reset and replacement from FLM Side | these alarms created due to the IPBB board failure hardware reset and replacement from FLM Side |  |  |  | API | 09/15/2025 14:39:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20250915001048 | PCM-20250915-00001795 | TT-20250915-00984 | Telecom | [7 empty] | 09/15/2025 16:20:55 | 09/15/2025 16:20:55 | 09/15/2025 22:20:55 | PT::: ONTs down at OLT-1 Slot-1 | 09/15/2025 11:04:00 | Major | 987654321 | Complaint-No WO NSN | 09/15/2025 11:04:00 | P3 | WIFI |  | Sceco | Wifi SA | FTTH OLT-1 | FLM_TE |  |  | PCM-20250915-00001033 | OLT-1 SLot-1 is down , 289 ONTs are down escalate to FLM to check the issue on location | OLT-1 SLot-1 is down , 289 ONTs are down escalate to FLM to check the issue on location |  |  |  | API | 09/15/2025 16:20:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250915001298 | PCM-20250915-00002218 | TT-20250915-00231 | Reference_telecom | Region_4 | JDJZ0773 | JDJZ0773 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 09/15/2025 18:27:39 | 10/16/2025 11:21:06 | 09/16/2025 06:27:39 | DemFail observed in JDJZ0773_01 towards 10.3.234.2 @ Sceco_STB | 09/14/2025 15:11:12 | Minor |  | DemFail | 09/14/2025 15:10:07 | P2 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0773 | FLM_TE |  |  | PCM-20250915-00002200 | Approved | Approved |  |  |  | API | 09/15/2025 18:27:39 | 10/07/2025 14:18:56 | 10/16/2025 11:21:01 |  |  | 10/16/2025 11:21:06 |  | Mudassar Bashir Bashir Ahmad | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250915001354 | PCM-20250915-00002311 | TT-20250915-02107 | Telecom | Region_4 | RYMK0665 | RYMK0665 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ehab Ali Mohamed Abdou | 09/15/2025 19:11:29 | 09/23/2025 01:00:30 | 09/16/2025 07:11:29 | WRYMK0001 Complete Down | 09/15/2025 18:53:45 | Minor | 613007 | Wi-Fi AP Out Of Service | 09/15/2025 18:53:45 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250915-00002291 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 09/15/2025 19:11:29 | 09/21/2025 18:14:40 | 09/23/2025 01:00:22 |  |  | 09/23/2025 01:00:30 |  | Ehab Ali Mohamed Abdou |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250915001608 | PCM-20250915-00002797 | TT-20250911-01253 | Reference_telecom | Region_3 | MDN2M1017 | MDN0017 |  |  |  | Hussain Ahmad Sultan Muhammad | 09/15/2025 23:39:57 | 10/01/2025 16:01:08 | 09/16/2025 11:39:57 | External Clock Reference Problem at MDN2M1017-P1-HRMCST @ Sceco | 09/11/2025 09:23:43 | Minor | 26262 | External Clock Reference Problem | 09/11/2025 09:20:19 | P1 | 2G | madinah | Sceco | 2G NSA | MDN2M1017 | FLM_TE |  | Dear TX Team kindly check as IP CLK unavailable DSP BTSIPCLK Link Status Result ------------------------------- Port No. Client IP Server IP Link State Active State NULL 10.150.24.70 10.161.136.137 Unavailable Activated NULL 10.150.24.70 10.161.137.137 Unavailable Not Activated | PCM-20250915-00002706 | Kindly be noted that the PTP clock configuration has been erased from this route . The needed action to make HC on link MDN0016<>MDN0783 as counting error in daily manner | Kindly be noted that the PTP clock configuration has been erased from this route . The needed action to make HC on link MDN0016<>MDN0783 as counting error in daily manner |  |  |  | API | 09/15/2025 23:39:57 | 09/16/2025 09:10:35 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000086 | PCM-20250916-00000200 | TT-20250916-00204 | Reference_telecom | Region_4 | JED0261 | JED0261 |  |  |  | BARKAT ALI MAIN HILAL | 09/16/2025 02:02:27 | 10/07/2025 13:39:53 | 09/16/2025 14:02:27 | LossOfSignal observed in JED0261_3 towards 10.10.154.137 @ Sceco | 09/15/2025 14:02:58 | Minor |  | LossOfSignal | 09/15/2025 14:02:04 | P2 | 2G | jeddah | Sceco | TX NSA | JED0261 | FLM_TE | [8 empty] | API | 09/16/2025 02:02:27 | 09/17/2025 11:12:32 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000142 | PCM-20250916-00000310 | TT-20250916-00307 | Telecom | Region_1 | HFR-PE-02 | HFR0502 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/16/2025 03:08:36 | 10/06/2025 13:45:01 | 09/16/2025 07:08:36 | The Device is offline at HFR-PE-02 @ Sceco_STB | 09/16/2025 03:08:09 | Critical | 101-7 | The Device is offline | 09/16/2025 03:08:07 | P1 | IPBB | hafr | Sceco_STB | IPRAN SA | HFR-PE-02 | FLM_TE | [8 empty] | Manual | 09/16/2025 03:08:36 | 10/06/2025 13:45:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000634 | PCM-20250916-00001251 | TT-20250916-01136 | Telecom | Region_4 | JED0190-SF-CSG-01 | JED0190 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/16/2025 10:51:41 | 09/23/2025 13:19:48 | 09/16/2025 16:51:41 | Link Down at JED0190-SF-CSG-01 @ Sceco | 09/16/2025 10:47:24 | Major | 101-2505274 | Physical Port Down | 09/16/2025 10:47:17 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0190-SF-CSG-01 | FLM_TE | [8 empty] | API | 09/16/2025 10:51:41 | 09/23/2025 13:19:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000903 | PCM-20250916-00001618 | TT-20250916-01505 | MW_HC | Region_6 | AQQ0039 | AQQ0039 |  |  |  | Manzoor Ahmed | 09/16/2025 12:44:55 | 09/16/2025 13:02:03 | 09/17/2025 00:44:55 | Nokia MW HC_P1 Observing Performance Issue at AQQ0039_01-AQQ0040_01 | 09/16/2025 12:44:20 | Minor |  | LOF | 09/16/2025 12:44:20 | P3 | 2G | Albaha | Sceco | TX NSA | AQQ0039_01-AQQ0040_01 | FLM_TE | [8 empty] | API | 09/16/2025 12:44:55 | 09/16/2025 13:02:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000912 | PCM-20250916-00001627 | TT-20250916-01514 | MW_HC | Region_6 | BLJ0050 | BLJ0050 |  |  |  | Manzoor Ahmed | 09/16/2025 12:45:07 | 09/16/2025 13:02:04 | 09/17/2025 00:45:07 | Nokia MW HC_P0 Observing Performance Issue at BLJ0050_01-BLJ0046_011 | 09/16/2025 12:44:20 | Minor |  | LOF | 09/16/2025 12:44:20 | P2 | 2G | Albaha | Sceco | TX NSA | BLJ0050_01-BLJ0046_011 | FLM_TE | [8 empty] | API | 09/16/2025 12:45:07 | 09/16/2025 13:02:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000913 | PCM-20250916-00001628 | TT-20250916-01516 | MW_HC | Region_6 | MKW2051 | MKW2051 |  |  |  | SHAH KHALID | 09/16/2025 12:45:08 | 09/16/2025 17:21:28 | 09/17/2025 00:45:08 | Nokia MW HC_P2 Observing Performance Issue at MKW2051_01-BHAB2442_02 | 09/16/2025 12:44:20 | Minor |  | LOF | 09/16/2025 12:44:20 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2051_01-BHAB2442_02 | FLM_TE | [8 empty] | API | 09/16/2025 12:45:08 | 09/16/2025 17:21:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000970 | PCM-20250916-00001685 | TT-20250916-01574 | MW_HC | Region_6 | NJR0213 | NJR0213 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 09/16/2025 12:46:14 | 10/09/2025 14:47:36 | 09/17/2025 00:46:14 | Nokia MW HC_P0 Observing Performance Issue at NJR0213_01-NJR0043_02 | 09/16/2025 12:44:20 | Minor |  | LOF | 09/16/2025 12:44:20 | P2 | 2G | najran | Sceco | TX NSA | NJR0213_01-NJR0043_02 | FLM_TE | [8 empty] | API | 09/16/2025 12:46:14 | 10/09/2025 14:47:36 | [5 empty] | Shahid Ali Roshan Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916000971 | PCM-20250916-00001686 | TT-20250916-01575 | MW_HC | Region_6 | NJR0019 | NJR0019 | Transsmission | MW_HW_fault | Remade Power Connector | Shahid Ali Roshan Ali | 09/16/2025 12:46:15 | 10/09/2025 14:47:35 | 09/17/2025 00:46:15 | Nokia MW HC_P0 Observing Performance + RSL Issue at NJR0019_01-NJR0030_03 | 09/16/2025 12:44:20 | Minor |  | LOF | 09/16/2025 12:44:20 | P1 | 2G | najran | Sceco | TX NSA | NJR0019_01-NJR0030_03 | FLM_TE | [8 empty] | API | 09/16/2025 12:46:15 | 10/09/2025 14:47:35 | [5 empty] | Shahid Ali Roshan Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916001591 | PCM-20250916-00002712 | TT-20250916-02462 | Telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Imran Ali Yousaf | 09/16/2025 19:33:49 | 09/22/2025 10:43:10 | 09/17/2025 07:33:49 | Temperature at DAM2066 on 10.74.82.58 @ Sceco | 09/16/2025 19:33:05 | Minor | Temperature | Temperature | 09/16/2025 19:29:37 | P1 | SRAN | dammam | Sceco | TX NSA | DAM2066 | FLM_TE | [8 empty] | API | 09/16/2025 19:33:49 | 09/17/2025 15:08:32 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250916001716 | PCM-20250916-00002915 | TT-20250916-02659 | Reference_telecom | Region_1 | JBL2106 | JBL2106 |  |  |  | Tahir Mahmood Hafiz Yar | 09/16/2025 21:43:30 | 09/24/2025 14:28:59 | 09/17/2025 09:43:30 | ETH_LINK_DOWN at JBL2106_NE_33_H @ Sceco | 09/16/2025 17:55:51 | Minor | 1-12793 | ETH_LINK_DOWN | 09/16/2025 17:55:48 | P1 | SRAN | jubail | Sceco | TX NSA | JBL2106 | FLM_TE | [8 empty] | API | 09/16/2025 21:43:30 | 09/16/2025 22:47:53 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250917000521 | PCM-20250917-00000876 | TT-20250917-00804 | Telecom | Region_4 | JED0007 | JED0007 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 09/17/2025 10:28:39 | 10/17/2025 18:03:37 | 09/17/2025 22:28:39 | PT::FLM need to perform HC at JED0007 (Bo request) | 09/17/2025 10:28:31 | Minor | 676767671 | Health Check-WO to TE FME | 09/17/2025 10:28:31 | P1 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0007 | FLM_TE | [8 empty] | API | 09/17/2025 10:28:39 | 10/17/2025 18:03:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250917000628 | PCM-20250917-00001034 | TT-20250917-00938 | Telecom | Region_4 | JED0993 | JED0993 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/17/2025 11:46:02 | 09/23/2025 13:19:59 | 09/17/2025 23:46:02 | PT::FLM need to perform HC at JED0993 (Bo request) | 09/17/2025 11:45:55 | Minor | 676767671 | Health Check-WO to TE FME | 09/17/2025 11:45:55 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0993 | FLM_TE | [8 empty] | API | 09/17/2025 11:46:02 | 09/23/2025 13:19:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250917000991 | PCM-20250917-00001614 | TT-20250917-00671 | Telecom | Region_6 | DAR0901-LL-CSG-01 | DAR0901 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Ali | 09/17/2025 16:22:30 | 09/17/2025 23:22:40 | 09/17/2025 22:22:30 | MW: Link down at DAR0901-LL-CSG-01 | 09/17/2025 09:19:12 | Major | 15269 | LOS | 09/17/2025 09:26:53 | P3 | IPRAN | raith | Generator_DG | IPRAN NSA | MW: Link down at DAR0901-LL-CSG-01 | FLM_TE |  |  | PCM-20250917-00001365 | Kindly check | Kindly check |  |  |  | API | 09/17/2025 16:22:30 | 09/17/2025 16:40:21 | 09/17/2025 20:11:47 | 09/17/2025 23:22:28 |  | 09/17/2025 23:22:40 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250917001012 | PCM-20250917-00001678 | TT-20250917-01570 | EM | Region_4 | JED6125 | JED6125 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 09/17/2025 16:43:44 | 10/06/2025 17:59:39 | 09/18/2025 04:43:44 | Unknown at JED6125-P3 @ Sceco | 09/17/2025 16:35:16 | Minor | 7408 | Unknown | 09/17/2025 16:35:12 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6125 | FLM_EM | [8 empty] | API | 09/17/2025 16:43:44 | 09/18/2025 19:21:22 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250917001022 | PCM-20250917-00001694 | TT-20250917-01583 | Telecom | Region_1 | KBR6002 | KBR6002 |  |  |  | Meraj Husain Idd Baksh | 09/17/2025 16:51:29 | 09/24/2025 14:29:00 | 09/18/2025 04:51:29 | ODU CPU / Cable Open at KBR6002 on 10.1.218.171 @ Sceco | 09/17/2025 16:50:51 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 09/17/2025 16:41:29 | P3 | SRAN | dammam | Sceco | TX NSA | KBR6002 | FLM_TE | [8 empty] | API | 09/17/2025 16:51:29 | 09/18/2025 04:32:28 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250917001314 | PCM-20250917-00002177 | TT-20250917-02055 | Telecom | Region_4 | RNY1M8245 | RNY2245 | Transsmission | MW_HW_stuck | Reset ODU | Ahmad Kamal Abdelmawla | 09/17/2025 20:55:02 | 09/18/2025 21:30:21 | 09/18/2025 02:55:02 | PT:: BO need to check PLR issue at RNY1M8245/R5 | 09/17/2025 20:52:05 | Major | 61611 | TWAMP PLR Threshold Crossed | 09/17/2025 20:52:05 | P3 | 4G | taif | Sceco | LTE NSA | RNY1M8245-CA-L800-SBTS-P3 | FLM_TE |  |  | PCM-20250917-00002173 | Dear @Shabakkat_FLM_R4 Thanks to confirm with us once RFC finished to confirm sites status as RFC planned tonight | Dear @Shabakkat_FLM_R4 Thanks to confirm with us once RFC finished to confirm sites status as RFC planned tonight |  |  |  | API | 09/17/2025 20:55:02 | 09/17/2025 23:13:39 | 09/18/2025 21:30:10 |  |  | 09/18/2025 21:30:21 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250918000158 | PCM-20250918-00000314 | TT-20250918-00321 | Telecom | Region_4 | JED1MN2200 | JED2200 |  |  |  | Mohammed Ramadan A Abu Abid | 09/18/2025 03:27:32 | 09/29/2025 11:12:19 | 09/18/2025 09:27:32 | PT::FLM need to perform HC at JED1MN2200-NR2.6-P1-VIP (Bo request) | 09/18/2025 03:26:52 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/18/2025 03:26:52 | VIP | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1MN2200-NR2.6-P1-VIP | FLM_TE | [8 empty] | API | 09/18/2025 03:27:32 | 09/18/2025 05:49:21 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250918000193 | PCM-20250918-00000389 | TT-20250918-00403 | Reference_telecom | Region_4 | MKJD1M7922 | MKJD0922 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/18/2025 04:32:07 | 09/29/2025 11:12:21 | 09/18/2025 10:32:07 | 1(LTE) sites down under MKJD0922-P2(Ref:TT-20250215-00149) | 02/15/2025 02:06:37 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 02/15/2025 02:06:37 | P2 | 4G | jeddah | Sceco | LTE SA | MKJD1M7922-USF-P3-L800-SBTS | FLM_TE | MKJD1M7922 | Results: DOWN SITE HUB MKJD1M7922-USF-P3-L800-SBTS MKJD1M7922 Summary: Hub: MKJD1M7922, Down Count: 1, Down Sites: MKJD1M7922-USF-P3-L800-SBTS Alarm Summary: MKJD1M7922 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 09/18/2025 04:32:07 | 09/18/2025 11:19:02 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250918000284 | PCM-20250918-00000564 | TT-20250918-00577 | Reference_telecom | Region_1 | DAM2M3250 | DAM0250 |  |  |  | Imran Ali Yousaf | 09/18/2025 06:57:22 | 09/25/2025 16:57:57 | 09/18/2025 12:57:22 | Inter-Board CANBUS Communication Failure at DAM2M3250-P2 @ Sceco | 09/17/2025 22:17:08 | Major | 26101 | Inter-Board CANBUS Communication Failure | 09/17/2025 22:14:14 | P2 | 3G | dammam | Sceco | 2G NSA | DAM2M3250 | FLM_TE |  |  | PCM-20250918-00000554 | please check Cabinet No.=1, Subrack No.=0, Slot No.=16, Board Type=FAN Board Name FAN Board Type WD2E1FANC BOM Code 02120577 SN(Bar Code) 21021205776TBA904811 | please check Cabinet No.=1, Subrack No.=0, Slot No.=16, Board Type=FAN Board Name FAN Board Type WD2E1FANC BOM Code 02120577 SN(Bar Code) 21021205776TBA904811 |  |  |  | API | 09/18/2025 06:57:22 | 09/18/2025 08:26:40 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250918000969 | PCM-20250918-00001665 | TT-20250918-01566 | Telecom | Region_1 | KBR0163 | KBR0163 |  |  |  | Talha Manzoor | 09/18/2025 14:36:23 | 09/24/2025 14:29:00 | 09/19/2025 02:36:23 | ODU CPU / Cable Open at KBR0163_1 on 10.154.2.225 @ Sceco_STB | 09/18/2025 14:35:32 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 09/18/2025 14:30:26 | P1 | SRAN | dammam | Sceco_STB | TX NSA | KBR0163 | FLM_TE | [8 empty] | API | 09/18/2025 14:36:23 | 09/18/2025 17:08:37 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250918001086 | PCM-20250918-00001836 | TT-20250918-01733 | EM | Region_1 | DAM0471 | DAM0471 |  |  |  | Gamal Hasan Farag Ali Khalifa | 09/18/2025 15:54:23 | 09/25/2025 16:57:58 | 09/19/2025 03:54:23 | NETECO: Door Open Alarm at DAM0471 @ Sceco | 09/18/2025 15:54:15 | Minor | 5152 | Door Open Alarm | 09/18/2025 15:54:15 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0471 | FLM_EM | [8 empty] | API | 09/18/2025 15:54:23 | 09/18/2025 17:04:25 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250918001092 | PCM-20250918-00001849 | TT-20250918-01747 | EM | Region_1 | DAM0471 | DAM0471 |  |  |  | Gamal Hasan Farag Ali Khalifa | 09/18/2025 16:00:36 | 09/25/2025 16:57:59 | 09/19/2025 04:00:36 | NETECO: BMU Missing at DAM0471 @ Sceco | 09/18/2025 15:54:15 | Minor | 13821 | BMU Missing | 09/18/2025 15:54:15 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0471 | FLM_EM | [8 empty] | API | 09/18/2025 16:00:36 | 09/18/2025 17:04:26 | [6 empty] | Huawei_RO |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250918001412 | PCM-20250918-00002370 | TT-20250918-02249 | MW_HC | Region_5 | MAK6035 | MAK6035 |  |  |  | Atif Javed Javed Hussain | 09/18/2025 20:31:25 | 09/21/2025 15:49:20 | 09/19/2025 00:31:25 | As per BO request NOKIA MW Link need to check MAK0021-MK3 | 09/18/2025 20:27:39 | Critical | 113388 | LOF | 09/18/2025 20:27:41 | VIP | 2G | makkah | Sceco | TX NSA | MAK6035 | FLM_TE | [8 empty] | API | 09/18/2025 20:31:25 | 09/21/2025 15:49:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250919000136 | PCM-20250919-00000216 | TT-20250919-00259 | EM | Region_4 | JED6149 | JED6149 |  |  |  | Muhammad Javed Muhammad Anwar | 09/19/2025 04:42:24 | 10/06/2025 17:59:39 | 09/19/2025 16:42:24 | HIGH TEMPERATURE 32 DEGREE C at JED6149-GSM-P3 @ Sceco | 09/19/2025 04:34:09 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 09/19/2025 04:34:03 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6149 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 09/19/2025 04:42:24 | 09/19/2025 18:28:14 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250919000433 | PCM-20250919-00000749 | TT-20250919-00774 | Reference_telecom | Region_1 | DRN0129 | DRN0129 | Transsmission | MW_HW_fault | Replace Control Card | AbdalHafiz Sirageldin Mohamed Yasin | 09/19/2025 12:14:25 | 10/02/2025 04:34:02 | 09/20/2025 00:14:25 | COMMUN_FAIL at DRN0129_NE_29_SDB @ Sceco | 09/19/2025 11:14:12 | Minor | 1-199 | COMMUN_FAIL | 09/19/2025 11:14:04 | P1 | SRAN | dammam | Sceco | TX NSA | DRN0129 | FLM_TE | [8 empty] | API | 09/19/2025 12:14:25 | 10/01/2025 23:47:38 | 10/02/2025 01:04:41 | 10/02/2025 01:05:52 | 10/02/2025 04:32:28 | 10/02/2025 04:34:02 |  | AbdalHafiz Sirageldin Mohamed Yasin | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250919000439 | PCM-20250919-00000759 | TT-20250919-00781 | Telecom | Region_2 | RIY1-PE-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 09/19/2025 12:17:07 | 09/19/2025 12:17:07 | 09/19/2025 18:17:07 | Observing links down flapped and restored on RIY1-PE-01 connected to WIFI WLC1 | 09/19/2025 12:16:48 | Major | 676767671 | Health Check-WO to TE FME | 09/19/2025 12:16:48 | P1 | IPBB | riyadh | Sceco_STB | Wifi SA | RIY1-PE-01 | FLM_TE | [8 empty] | API | 09/19/2025 12:17:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250920000203 | PCM-20250920-00000411 | TT-20250920-00396 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 09/20/2025 05:03:11 | 09/20/2025 05:03:11 | 09/20/2025 11:03:11 | Observing Multiple ALU CIDs flapped and restored B/W MAK - TAF | 09/20/2025 04:59:26 | Major | 5000003 | Link Down | 09/20/2025 04:59:26 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE | [5 empty] | Observing Multiple ALU CIDs flapped and restored B/W MAK - TAF |  |  | API | 09/20/2025 05:03:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250920000207 | PCM-20250920-00000416 | TT-20250920-00402 | Telecom | Region_4 | TF1-ASG-02 | TF1 |  |  |  | Rashid Shafique | 09/20/2025 05:06:36 | 10/14/2025 10:12:14 | 09/20/2025 11:06:36 | DWDM: Link down at TF1-ASG-02 | 09/20/2025 04:59:26 | Major | 15269 | LOS | 09/20/2025 04:59:26 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | DWDM: Link down at TF1-ASG-02 | FLM_TE | [8 empty] | API | 09/20/2025 05:06:36 | 10/14/2025 10:12:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250920000861 | PCM-20250920-00001471 | TT-20250920-01339 | Reference_telecom | Region_4 | RYMK0665 | RYMK0665 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ehab Ali Mohamed Abdou | 09/20/2025 14:32:46 | 09/23/2025 01:00:51 | 09/21/2025 02:32:46 | WRYMK0001 is complete down | 09/20/2025 14:08:09 | Minor | 613007 | Wi-Fi AP Out Of Service | 09/20/2025 14:08:09 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250920-00001400 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 09/20/2025 14:32:46 | 09/20/2025 22:31:44 | 09/23/2025 01:00:42 |  |  | 09/23/2025 01:00:51 |  | Ehab Ali Mohamed Abdou |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250920000925 | PCM-20250920-00001568 | TT-20250920-00887 | Reference_telecom | Region_2 | RIY0625 | RIY0625 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 09/20/2025 15:02:56 | 10/16/2025 20:32:13 | 09/21/2025 03:02:56 | IP Clock Link Failure at RIY0625-P2_SRAN @ Sceco | 09/20/2025 07:33:31 | Minor | 26263 | IP Clock Link Failure | 09/20/2025 07:29:47 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0625 | FLM_TE | RIY0625 | Dear Team, Hub:- RIY0625 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250920-00000992 | Related to TE | Related to TE |  |  |  | API | 09/20/2025 15:02:56 | 09/20/2025 15:15:50 | 10/16/2025 20:32:02 |  |  | 10/16/2025 20:32:13 |  | Mubashar Farooq Abdul Majeed | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250920000941 | PCM-20250920-00001593 | TT-20250920-01510 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 09/20/2025 15:09:24 | 09/20/2025 15:09:24 | 09/20/2025 21:09:24 | observing BFD session down On MAK4-PE Connected to IPRAN | 09/20/2025 15:02:36 | Major | 16165 | BfdSessDown | 09/20/2025 15:02:36 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | observing BFD session down On MAK4-PE Connected to IPRAN | FLM_TE | [5 empty] | observing BFD session down On MAK4-PE Connected to IPRAN |  |  | API | 09/20/2025 15:09:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250920001277 | PCM-20250920-00002109 | TT-20250920-01927 | Reference_telecom | Region_2 | QSDH0706 | QSDH0706 |  |  |  | Touseef Iqbal Mazhar Iqbal | 09/20/2025 17:50:09 | 09/29/2025 11:12:25 | 09/21/2025 05:50:09 | External Clock Reference Problem at SAJ2M1138-P2 @ Sceco | 09/20/2025 14:29:27 | Minor | 26262 | External Clock Reference Problem | 09/20/2025 14:25:51 | P2 | SRAN | buraidah | Sceco | 2G NSA | SAJ2M1138 | FLM_TE | QSDH0706 | Dear Team , We observing MW_BER_SD Alarm at QSDH0706 DIR TO QSDH2707 , Kindly visit the site and check this issue | PCM-20250920-00002098 | Dear Team , We observing MW_BER_SD Alarm at QSDH0706 DIR TO QSDH2707 , Kindly visit the site and check this issue | Dear Team , We observing MW_BER_SD Alarm at QSDH0706 DIR TO QSDH2707 , Kindly visit the site and check this issue |  |  |  | API | 09/20/2025 17:50:09 | 09/21/2025 05:53:19 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250921000573 | PCM-20250921-00001019 | TT-20250921-00782 | Reference_telecom | Region_6 | WDS0499 | WDS0499 |  |  |  | Ahmed Mamdouh Helal Helal | 09/21/2025 10:13:56 | 10/01/2025 20:17:27 | 09/21/2025 16:13:56 | MW Link down at WDS0499-LL-CSG-01 // TT-20250721-02113 // TT-20250817-00807 | 09/20/2025 23:59:29 | Major | 15269 | LOS | 09/20/2025 23:59:29 | P1 | 2G | wadi dawasar | Sceco | IPRAN NSA | MW Link down at WDS0499-LL-CSG-01 // TT-20250721-02113 // TT-20250817-00807 | FLM_TE |  |  | PCM-20250921-00000888 | Thanks to update Status for WDS0501-WDS0499 re-routing action | Thanks to update Status for WDS0501-WDS0499 re-routing action |  |  |  | API | 09/21/2025 10:13:56 | 09/21/2025 11:23:17 | 10/01/2025 20:17:22 | 10/01/2025 20:17:25 | 10/01/2025 20:17:27 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250921000619 | PCM-20250921-00001083 | TT-20250921-00962 | Telecom | Region_4 | KMMD0726 | KMMD0726 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Nazeer Mohammed | 09/21/2025 10:30:41 | 10/01/2025 17:05:55 | 09/21/2025 22:30:41 | PT:: FLM need to do HC at KMMD0726-P3/R4 (LNOC Request) | 09/21/2025 10:30:34 | Minor | 676767671 | Health Check-WO to TE FME | 09/21/2025 10:30:35 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | KMMD0726-P3 | FLM_TE | [8 empty] | API | 09/21/2025 10:30:41 | 09/21/2025 10:45:33 | 10/01/2025 17:05:30 |  |  | 10/01/2025 17:05:55 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250921000623 | PCM-20250921-00001089 | TT-20250921-00967 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 09/21/2025 10:32:10 | 09/21/2025 10:32:10 | 09/21/2025 16:32:10 | Observing Multiple ALU CIDs down B/W MAK & HM | 09/21/2025 10:30:40 | Major | 5000003 | Link Down | 09/21/2025 10:30:40 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | Observing Multiple ALU CIDs down B/W MAK & HM | FLM_TE | [5 empty] | Observing Multiple ALU CIDs down B/W MAK & HM |  |  | API | 09/21/2025 10:32:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921000687 | PCM-20250921-00001173 | TT-20250921-00734 | Reference_telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 09/21/2025 11:18:53 | 09/28/2025 17:45:06 | 09/21/2025 15:18:53 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 09/21/2025 05:02:09 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 09/21/2025 05:02:01 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE |  |  | PCM-20250921-00000847 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 09/21/2025 11:18:53 | 09/21/2025 15:49:28 | [6 empty] | NSN_Care |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921000749 | PCM-20250921-00001241 | TT-20250921-01108 | Reference_telecom | Region_6 | JIZ0184 | JIZ0184 |  |  |  | Osama Hadi | 09/21/2025 11:28:09 | 09/21/2025 21:16:42 | 09/21/2025 23:28:09 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JIZ0184_1-10.10.157.66 | 09/10/2025 10:06:27 | Minor |  | LOF | 09/10/2025 10:06:27 | P2 | 2G | jizan | Sceco | TX NSA | JIZ0184_1-10.10.157.66 | FLM_TE | [8 empty] | API | 09/21/2025 11:28:09 | 09/21/2025 21:16:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921000861 | PCM-20250921-00001429 | TT-20250921-01297 | Telecom | Region_1 | ARM2M7872 | ARM0872 |  |  |  | Talha Manzoor | 09/21/2025 12:41:12 | 09/23/2025 11:47:08 | 09/22/2025 00:41:12 | RF Unit Maintenance Link Failure at ARM2M7872-P3 @ Sceco | 09/21/2025 12:39:23 | Minor | 26235 | RF Unit Maintenance Link Failure | 09/21/2025 12:35:38 | P3 | 4G | dammam | Sceco | LTE NSA | ARM2M7872 | FLM_TE | [8 empty] | API | 09/21/2025 12:41:12 | 09/21/2025 15:53:27 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921000866 | PCM-20250921-00001435 | TT-20250921-01305 | Telecom | Region_1 | ARM2M7872 | ARM0872 |  |  |  | Talha Manzoor | 09/21/2025 12:42:44 | 09/23/2025 11:47:09 | 09/21/2025 18:42:44 | BBU CPRI Interface Error at ARM2M7872-P3 @ Sceco | 09/21/2025 12:39:24 | Major | 26234 | BBU CPRI Interface Error | 09/21/2025 12:35:38 | P3 | 4G | dammam | Sceco | LTE NSA | ARM2M7872 | FLM_TE | [8 empty] | API | 09/21/2025 12:42:44 | 09/21/2025 15:53:28 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250921000872 | PCM-20250921-00001443 | TT-20250921-01311 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 09/21/2025 12:45:24 | 09/21/2025 12:45:24 | 09/21/2025 18:45:24 | Observing Multiple ALU CIDs Down Flapped and restored B/W JD & MAK | 09/21/2025 12:43:17 | Major | 5000003 | Link Down | 09/21/2025 12:43:17 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | Observing Multiple ALU CIDs Down Flapped and restored B/W JD & MAK | FLM_TE | [5 empty] | Observing Multiple ALU CIDs Down Flapped and restored B/W JD & MAK |  |  | API | 09/21/2025 12:45:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001207 | PCM-20250921-00001968 | TT-20250921-01740 | Reference_telecom | Region_1 | ARM2M1872 | ARM0872 |  |  |  | Talha Manzoor | 09/21/2025 15:46:08 | 09/23/2025 11:47:09 | 09/21/2025 21:46:08 | RF Unit VSWR Threshold Crossed at ARM2M1872-P3 @ Sceco | 09/21/2025 12:45:58 | Major | 26529 | RF Unit VSWR Threshold Crossed | 09/21/2025 12:45:55 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1872 | FLM_TE | [8 empty] | API | 09/21/2025 15:46:08 | 09/21/2025 15:53:32 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250921001370 | PCM-20250921-00002260 | TT-20250921-02022 | Telecom | Region_4 | JED6132 | JED6132 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Mohamed Farag Abdelbary | 09/21/2025 17:26:04 | 09/29/2025 17:07:17 | 09/22/2025 05:26:04 | JV arrangment with Mobilty Team to check JED6132 | 09/21/2025 17:21:44 | Minor | 676767681 | Health Check-WO to TE FME | 09/21/2025 17:21:44 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6132 | FLM_TE | [5 empty] | JV arrangment with Mobilty Team to check JED6132 as per Mobily experiencing a coverage issue in specific area of Building 2, Level 0. As shown below, there is currently no signal at all in the affected area. The coverage issue has now expanded to both Building 2 and Building 3. Users are experiencing frequent call drops and poor cellular connectivity, which is causing significant disruption. |  |  | API | 09/21/2025 17:26:04 | 09/21/2025 17:39:58 | 09/28/2025 11:39:16 | 09/28/2025 11:39:19 | 09/28/2025 11:41:25 | 09/29/2025 17:07:17 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001430 | PCM-20250921-00002348 | TT-20250921-02102 | Reference_telecom | Region_6 | BHAB9038 | BHAB9038 |  |  |  | Fawad Khan | 09/21/2025 18:07:30 | 09/22/2025 00:08:50 | 09/22/2025 06:07:30 | NEC MW Observing Radio Traffic Aggregation Link,Radio Traffic Aggregation Link at BHAB9038_3(10.154.168.148) | 09/19/2025 14:29:28 | Minor |  | LOF | 09/19/2025 14:29:28 | P1 | Repeater | namas | Generator_SG | TX NSA | BHAB9038_3(10.154.168.148) | FLM_TE | [8 empty] | API | 09/21/2025 18:07:30 | 09/22/2025 00:08:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001456 | PCM-20250921-00002375 | TT-20250921-02126 | Reference_telecom | Region_1 | JBKH0088 | JBKH0088 |  |  |  | Mohamed Abdelaziz | 09/21/2025 18:07:56 | 10/01/2025 12:58:15 | 09/22/2025 06:07:56 | NEC MW Observing LOF,Frame ID,LOF,Frame ID,High BER at JBKH0088-1(10.76.118.71) | 09/14/2025 22:16:39 | Minor |  | LOF | 09/14/2025 22:16:39 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH0088-1(10.76.118.71) | FLM_TE | [8 empty] | API | 09/21/2025 18:07:56 | 09/21/2025 19:42:01 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001457 | PCM-20250921-00002376 | TT-20250921-02127 | Reference_telecom | Region_1 | JBKH0088 | JBKH0088 |  |  |  | Mohamed Abdelaziz | 09/21/2025 18:07:57 | 10/07/2025 13:39:54 | 09/22/2025 06:07:57 | NEC MW Observing LOF,Frame ID,High BER,RX Level,RX Level,LOF,Frame ID,LOF,Frame ID,High BER,High BER at JBKH0088-3(10.76.118.77) | 09/14/2025 22:41:40 | Minor |  | LOF | 09/14/2025 22:41:40 | P1 | SRAN | khafji | Generator_DG | TX NSA | JBKH0088-3(10.76.118.77) | FLM_TE | [8 empty] | API | 09/21/2025 18:07:57 | 09/21/2025 19:42:01 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001459 | PCM-20250921-00002378 | TT-20250921-02129 | Reference_telecom | Region_1 | JBKH0601 | JBKH0601 |  |  |  | Tahir Mahmood Hafiz Yar | 09/21/2025 18:07:59 | 10/01/2025 12:58:17 | 09/22/2025 06:07:59 | NEC MW Observing MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm, at JBKH0601 NEW(10.154.13.7) | 09/10/2025 13:29:11 | Minor |  | LOF | 09/10/2025 13:29:11 | P1 | SRAN | jubail | Sceco | TX NSA | JBKH0601 NEW(10.154.13.7) | FLM_TE | [8 empty] | API | 09/21/2025 18:07:59 | 09/22/2025 05:11:20 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001460 | PCM-20250921-00002379 | TT-20250921-02130 | Reference_telecom | Region_1 | JBKH0601 | JBKH0601 |  |  |  | Tahir Mahmood Hafiz Yar | 09/21/2025 18:08:01 | 10/01/2025 12:58:17 | 09/22/2025 06:08:01 | NEC MW Observing Radio Traffic Aggregation Link at JBKH0601_2(10.76.111.194) | 09/18/2025 10:31:36 | Minor |  | LOF | 09/18/2025 10:31:36 | P1 | SRAN | jubail | Sceco | TX NSA | JBKH0601_2(10.76.111.194) | FLM_TE | [8 empty] | API | 09/21/2025 18:08:01 | 09/22/2025 05:11:20 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001462 | PCM-20250921-00002381 | TT-20250921-02132 | Reference_telecom | Region_1 | JBL0457 | JBL0457 | Transsmission | MW_HW_fault | Replace ODU | Imran Ali Yousaf | 09/21/2025 18:08:03 | 10/04/2025 03:47:26 | 09/22/2025 06:08:03 | NEC MW Observing TX Power,ODU Alarm,LOF,ODU CPU / Cable Open at JBL0457(10.154.26.162) | 09/18/2025 10:34:08 | Minor |  | LOF | 09/18/2025 10:34:08 | P3 | SRAN | jubail | Generator_SG | TX NSA | JBL0457(10.154.26.162) | FLM_TE | [8 empty] | API | 09/21/2025 18:08:03 | 10/01/2025 14:35:20 | [5 empty] | Imran Ali Yousaf | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001465 | PCM-20250921-00002384 | TT-20250921-02135 | Reference_telecom | Region_1 | JBL2377 | JBL2377 | Transsmission | MW_HW_fault | Replace ODU | Tahir Mahmood Hafiz Yar | 09/21/2025 18:08:06 | 10/04/2025 03:47:27 | 09/22/2025 06:08:06 | NEC MW Observing TX Power,ODU Alarm at JBL2377(10.248.33.27) | 09/18/2025 10:34:07 | Minor |  | LOF | 09/18/2025 10:34:07 | P2 | SRAN | jubail | Sceco | TX NSA | JBL2377(10.248.33.27) | FLM_TE | [8 empty] | API | 09/21/2025 18:08:06 | 10/01/2025 15:54:25 | [5 empty] | Tahir Mahmood Hafiz Yar | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250921001494 | PCM-20250921-00002414 | TT-20250921-02164 | Reference_telecom | Region_6 | RYAB0627 | RYAB0627 |  |  |  | Ahmed Mamdouh Helal Helal | 09/21/2025 18:08:38 | 10/21/2025 23:37:53 | 09/22/2025 06:08:38 | NEC MW Observing LOF,LOF,LOF,LOF,Frame ID,Frame ID,Frame ID at RYAB0627(10.89.222.3) | 09/16/2025 00:00:10 | Minor |  | LOF | 09/16/2025 00:00:10 | P1 | 2G | wadi dawasar | Sceco_STB | TX NSA | RYAB0627(10.89.222.3) | FLM_TE | [8 empty] | API | 09/21/2025 18:08:38 | 09/21/2025 19:26:26 | 10/21/2025 23:37:45 | 10/21/2025 23:37:49 | 10/21/2025 23:37:53 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001506 | PCM-20250921-00002426 | TT-20250921-02177 | Reference_telecom | Region_6 | WDS9471 | WDS9471 |  |  |  | Ahmed Mamdouh Helal Helal | 09/21/2025 18:08:51 | 09/21/2025 19:26:27 | 09/22/2025 06:08:51 | NEC MW Observing ODU CPU / Cable Open,High BER at WDS9471-2(10.89.222.40) | 09/15/2025 23:01:37 | Minor |  | LOF | 09/15/2025 23:01:37 | P1 | Repeater | wadi dawasar | Generator_SG | TX NSA | WDS9471-2(10.89.222.40) | FLM_TE | [8 empty] | API | 09/21/2025 18:08:51 | 09/21/2025 19:26:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250921001517 | PCM-20250921-00002437 | TT-20250921-02188 | Reference_telecom | Region_6 | WDS9509 | WDS9509 |  |  |  | Ahmed Mamdouh Helal Helal | 09/21/2025 18:09:03 | 09/21/2025 19:26:28 | 09/22/2025 06:09:03 | NEC MW Observing LAN Link at WDS9509-1(10.89.222.162) | 09/15/2025 04:32:10 | Minor |  | LOF | 09/15/2025 04:32:10 | P3 | Repeater | wadi dawasar | Generator_SG | TX NSA | WDS9509-1(10.89.222.162) | FLM_TE | [8 empty] | API | 09/21/2025 18:09:03 | 09/21/2025 19:26:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000019 | PCM-20250922-00000041 | TT-20250921-02591 | Reference_telecom | Region_2 | NIF2M1583 | NIF0583 |  |  |  | Zakir Muhammad Yar Muhammad | 09/22/2025 00:40:59 | 09/29/2025 11:12:47 | 09/22/2025 12:40:59 | External Clock Reference Problem at NIF2M1583-P3 @ Sceco | 09/21/2025 19:56:28 | Minor | 26262 | External Clock Reference Problem | 09/21/2025 19:53:02 | P3 | 2G | dawadmi | Sceco | 2G NSA | NIF2M1583 | FLM_TE |  |  | PCM-20250922-00000015 | PM Errors and RSL degradation observed on NIF0583-NIF0584 FLM Team please perform health check for the mentioned MW link | PM Errors and RSL degradation observed on NIF0583-NIF0584 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 09/22/2025 00:40:59 | 09/24/2025 18:45:28 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000020 | PCM-20250922-00000044 | TT-20250921-02593 | Reference_telecom | Region_2 | NIF2M1571 | NIF0571 |  |  |  | Zakir Muhammad Yar Muhammad | 09/22/2025 00:41:31 | 09/29/2025 11:12:47 | 09/22/2025 12:41:31 | External Clock Reference Problem at NIF2M1571-P2 @ Sceco | 09/21/2025 19:57:32 | Minor | 26262 | External Clock Reference Problem | 09/21/2025 19:54:05 | P2 | 2G | dawadmi | Sceco | 2G NSA | NIF2M1571 | FLM_TE |  |  | PCM-20250922-00000019 | PM Errors and RSL degradation observed on NIF0583-NIF0584 FLM Team please perform health check for the mentioned MW link | PM Errors and RSL degradation observed on NIF0583-NIF0584 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 09/22/2025 00:41:31 | 09/24/2025 18:45:29 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000025 | PCM-20250922-00000051 | TT-20250921-02595 | Reference_telecom | Region_2 | NIF2M1584 | NIF0584 |  |  |  | Zakir Muhammad Yar Muhammad | 09/22/2025 00:45:18 | 09/29/2025 11:12:48 | 09/22/2025 12:45:18 | External Clock Reference Problem at NIF2M1584-P3 @ Generator_SG | 09/21/2025 19:58:24 | Minor | 26262 | External Clock Reference Problem | 09/21/2025 19:55:02 | P3 | 2G | dawadmi | Generator_SG | 2G NSA | NIF2M1584 | FLM_TE |  |  | PCM-20250922-00000023 | PM Errors and RSL degradation observed on NIF0583-NIF0584 FLM Team please perform health check for the mentioned MW link | PM Errors and RSL degradation observed on NIF0583-NIF0584 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 09/22/2025 00:45:18 | 09/24/2025 18:45:29 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250922000498 | PCM-20250922-00000863 | TT-20250922-00857 | Telecom | Region_2 | RIY0861 | RIY0861 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 09/22/2025 11:15:43 | 10/16/2025 20:30:34 | 09/22/2025 17:15:43 | SPAN_LOSS_LOWER_GAIN at RIY0861-OCS1 @ Sceco | 09/22/2025 11:11:21 | Major | 1-13650 | SPAN_LOSS_LOWER_GAIN | 09/22/2025 11:11:12 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0861 | FLM_TE | [5 empty] | 0-1-C-8-F1DSFIU-4(ELINE1/ELINE2(FROM RIY0394))-OTS:1 |  |  | API | 09/22/2025 11:15:43 | 09/22/2025 13:55:53 | 10/16/2025 20:30:26 |  |  | 10/16/2025 20:30:34 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000564 | PCM-20250922-00000981 | TT-20250922-00953 | Telecom | Region_4 | JED1MN0800 | JED0800 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/22/2025 12:00:10 | 09/23/2025 13:20:57 | 09/22/2025 18:00:10 | PT::FLM need to perform HC at JED1MN0800-NR2.6-P1-VIP | 09/22/2025 12:00:02 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/22/2025 12:00:02 | VIP | 5G | jeddah | Generator_SG | 2G_3G_LTE_5G NSA | JED1MN0800-NR2.6-P1-VIP | FLM_TE | [8 empty] | API | 09/22/2025 12:00:10 | 09/23/2025 13:20:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250922000565 | PCM-20250922-00000982 | TT-20250922-00954 | Telecom | Region_4 | JED1M7286 | JED0286 | AutoRecovery | Clear_Before_Investigation | Auto Clear | MALIK ATIF ZAMAN | 09/22/2025 12:00:30 | 09/29/2025 14:40:41 | 09/22/2025 18:00:30 | PT::FLM need to perform HC at JED1M7286-P1-HUB-CA-L900-L800-SBTS | 09/22/2025 12:00:22 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/22/2025 12:00:22 | P1 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1M7286-P1-HUB-CA-L900-L800-SBTS | FLM_TE | [8 empty] | API | 09/22/2025 12:00:30 | 09/23/2025 16:43:43 | 09/29/2025 14:40:30 |  |  | 09/29/2025 14:40:41 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000567 | PCM-20250922-00000984 | TT-20250922-00956 | Telecom | Region_4 | JED1MN0629 | JED0629 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/22/2025 12:00:46 | 09/23/2025 13:20:58 | 09/22/2025 18:00:46 | PT::FLM need to perform HC at JED1MN0629-NR2.6-P3 | 09/22/2025 12:00:32 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/22/2025 12:00:32 | P3 | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1MN0629-NR2.6-P3 | FLM_TE | [8 empty] | API | 09/22/2025 12:00:46 | 09/23/2025 13:20:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000573 | PCM-20250922-00000991 | TT-20250922-00963 | Telecom | Region_4 | JED2591 | JED2591 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/22/2025 12:02:54 | 09/22/2025 16:24:48 | 09/22/2025 18:02:54 | PT::FLM need to perform HC at JED2591-G9-L8-L18-L21-NR2.6-P3-SBTS | 09/22/2025 12:02:47 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/22/2025 12:02:47 | P3 | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G NSA | JED2591-G9-L8-L18-L21-NR2.6-P3-SBTS | FLM_TE | [8 empty] | API | 09/22/2025 12:02:54 | 09/22/2025 16:24:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000590 | PCM-20250922-00001016 | TT-20250922-00981 | MW_HC | Region_6 | TLT0387 | TLT0387 |  |  |  | Muhammad Afzal Muhammad Aslam | 09/22/2025 12:11:00 | 09/22/2025 12:25:34 | 09/23/2025 00:11:00 | As per BO request NEC MW link TLT0387-TLT0862 | 09/22/2025 12:09:51 | Minor | 113388 | LOF | 09/22/2025 12:09:54 | P1 | 2G | turaib | Sceco_STB | TX NSA | TLT0387-TLT0862 | FLM_TE | [8 empty] | API | 09/22/2025 12:11:00 | 09/22/2025 12:25:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000593 | PCM-20250922-00001019 | TT-20250922-00984 | Telecom | Region_4 | TAF1MN2106 | TAF2106 |  |  |  | Rashid Shafique | 09/22/2025 12:12:18 | 09/22/2025 16:37:41 | 09/22/2025 18:12:18 | PT::FLM need to perform HC at TAF1MN2106-NR2.6-P2 | 09/22/2025 12:11:48 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/22/2025 12:11:48 | P2 | 5G | taif | Sceco | 2G_3G_LTE_5G NSA | TAF1MN2106-NR2.6-P2 | FLM_TE | [8 empty] | API | 09/22/2025 12:12:18 | 09/22/2025 16:37:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000717 | PCM-20250922-00001219 | TT-20250922-01198 | Telecom | Region_2 | RIYB6025 | RIYB6025 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 09/22/2025 13:56:03 | 10/07/2025 13:39:56 | 09/23/2025 01:56:03 | HC::: FLM need to do health check under RIYB6025 | 09/22/2025 13:48:11 | Minor | 676767681 | Health Check-WO to TE FME | 09/22/2025 13:48:12 | P3 | SRAN | riyadh | Sceco | 2G_3G_LTE_5G NSA | RIYB6025 | FLM_TE | [8 empty] | API | 09/22/2025 13:56:03 | 09/23/2025 11:16:00 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000788 | PCM-20250922-00001343 | TT-20250922-01337 | Telecom | Region_4 | JED2059 | JED2059 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/22/2025 15:08:02 | 09/23/2025 13:21:00 | 09/22/2025 21:08:02 | PT::FLM need to perform HC at JED2059 (Bo request) | 09/22/2025 15:07:52 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/22/2025 15:07:52 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED2059 | FLM_TE | [8 empty] | API | 09/22/2025 15:08:02 | 09/23/2025 13:21:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922000990 | PCM-20250922-00001679 | TT-20250922-01665 | MW_HC | Region_6 | BLC9224 | BLC9224 |  |  |  | Manzoor Ahmed | 09/22/2025 17:08:00 | 09/22/2025 18:08:48 | 09/23/2025 05:08:00 | Nokia MW HC_P0 Observing Performance Issue at BLC9224_01-BLJ0046-8 | 09/22/2025 17:07:37 | Minor |  | LOF | 09/22/2025 17:07:37 | P1 | Repeater | Albaha | Sceco | TX NSA | BLC9224_01-BLJ0046-8 | FLM_TE | [8 empty] | API | 09/22/2025 17:08:00 | 09/22/2025 18:08:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922001108 | PCM-20250922-00001800 | TT-20250922-01785 | MW_HC | Region_2 | UNZ0092 | UNZ0092 |  |  |  | Muhammad Mohsin Raza | 09/22/2025 17:10:07 | 09/23/2025 04:52:36 | 09/23/2025 05:10:07 | Huawei MW HC_P2 Observing Errors at UNZ0092-UNZ0084 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P1 | SRAN | buraidah | Sceco | TX NSA | UNZ0092-UNZ0084 | FLM_TE | [8 empty] | API | 09/22/2025 17:10:07 | 09/23/2025 04:52:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250922001109 | PCM-20250922-00001801 | TT-20250922-01786 | MW_HC | Region_2 | SRIY0394 | SRIY0394 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Naseer Muhammad Nazir | 09/22/2025 17:10:08 | 10/06/2025 22:47:54 | 09/23/2025 05:10:08 | Huawei MW HC_P2 Observing Errors at SRIY0394/SRIY0395/SRIY0396-RIY0759 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P3 | SRAN | riyadh | Sceco | TX NSA | SRIY0394/SRIY0395/SRIY0396-RIY0759 | FLM_TE | [8 empty] | API | 09/22/2025 17:10:08 | 09/23/2025 23:34:39 | 10/06/2025 22:47:04 |  |  | 10/06/2025 22:47:54 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250922001125 | PCM-20250922-00001817 | TT-20250922-01801 | MW_HC | Region_2 | RIY0459 | RIY0459 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Farmanullah Akbar Jan | 09/22/2025 17:10:25 | 09/27/2025 19:15:02 | 09/23/2025 05:10:25 | Huawei MW HC_P2 Observing Errors at RIY0459-RIY0283 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0459-RIY0283 | FLM_TE | [8 empty] | API | 09/22/2025 17:10:25 | 09/22/2025 17:53:05 | 09/27/2025 19:14:48 |  |  | 09/27/2025 19:15:02 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922001200 | PCM-20250922-00001893 | TT-20250922-01880 | MW_HC | Region_1 | JBL2377 | JBL2377 |  |  |  | Tahir Mahmood Hafiz Yar | 09/22/2025 17:11:51 | 10/07/2025 13:39:55 | 09/23/2025 05:11:51 | NEC MW HC_P0 Observing Modem Down at JBL2377(10.248.33.27)--JBL2380(10.248.33.26) | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P2 | SRAN | jubail | Sceco | TX NSA | JBL2377(10.248.33.27)--JBL2380(10.248.33.26) | FLM_TE | [8 empty] | API | 09/22/2025 17:11:51 | 09/22/2025 20:20:19 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250922001277 | PCM-20250922-00002012 | TT-20250922-01980 | Telecom | Region_1 | SAK0586 | SAK0586 |  |  |  | Syed Fawad Ali | 09/22/2025 18:11:34 | 09/30/2025 11:04:16 | 09/23/2025 06:11:34 | RF Unit Maintenance Link Failure at SAK0586-P1-SHOP_SRAN @ Sceco | 09/22/2025 18:07:53 | Minor | 26235 | RF Unit Maintenance Link Failure | 09/22/2025 18:06:10 | P1 | SRAN | sakaka | Sceco | 2G NSA | SAK0586 | FLM_TE | [8 empty] | API | 09/22/2025 18:11:34 | 09/23/2025 01:05:52 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250922001398 | PCM-20250922-00002205 | TT-20250922-02136 | EM | Region_6 | AQQ2230 | AQQ2230 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 09/22/2025 20:00:08 | 10/23/2025 23:01:04 | 09/23/2025 08:00:08 | As per BO request NEC MW link AQQ2230-AQQ0041 as UBT-T odu down AQQ0041 port 1.6 | 09/22/2025 19:58:50 | Minor | 113388 | LOF | 09/22/2025 19:58:53 | P3 | 2G | Albaha | Generator_DG | TX NSA | AQQ2230-AQQ0041 | FLM_EM | [8 empty] | API | 09/22/2025 20:00:08 | 09/29/2025 18:15:08 | 10/23/2025 23:00:19 |  |  | 10/23/2025 23:01:04 |  | Manzoor Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250922001402 | PCM-20250922-00002209 | TT-20250922-02142 | MW_HC | Region_6 | NMR2062 | NMR2062 |  |  |  | SHAH KHALID | 09/22/2025 20:03:52 | 09/22/2025 22:17:23 | 09/23/2025 08:03:52 | As per BO request NOKIA MW link NMR2062-NMR2057 as RSL LOW | 09/22/2025 20:02:42 | Minor | 113388 | LOF | 09/22/2025 20:02:44 | P3 | 2G | Baha | Generator_SG | TX NSA | NMR2062-NMR2057 | FLM_TE | [8 empty] | API | 09/22/2025 20:03:52 | 09/22/2025 22:17:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250923000123 | PCM-20250923-00000188 | TT-20250923-00188 | EM | Region_3 | TBK9046 | TBK9046 |  |  |  | Moustafa Samir Omar | 09/23/2025 03:00:20 | 10/05/2025 15:43:18 | 09/23/2025 07:00:20 | NEC MW observing LOW BATTERY (INPUT-4) At TBK9046_EAS | 09/23/2025 02:59:36 | Critical | 383 | POWER_ALM | 09/23/2025 02:59:36 | P3 | Repeater | tabouk | Generator_DG | TX NSA | TBK9046_EAS | FLM_EM | [5 empty] | NEC MW observing LOW BATTERY (INPUT-4) At TBK9046_EAS |  |  | API | 09/23/2025 03:00:20 | 10/05/2025 15:43:18 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250923000296 | PCM-20250923-00000445 | TT-20250923-00473 | Reference_telecom | Region_6 | ABBS0164 | ABBS0164 | Transsmission | SFP_Transmission | Replace SFP | Fawad Khan | 09/23/2025 07:18:53 | 10/20/2025 00:54:35 | 09/23/2025 19:18:53 | ReplaceableUnitMissing observed in ABBS0164_01 towards 10.221.245.7 @ Sceco | 09/22/2025 19:18:30 | Minor |  | ReplaceableUnitMissing | 09/22/2025 19:18:26 | P3 | 2G | namas | Sceco | TX NSA | ABBS0164 | FLM_TE | [8 empty] | API | 09/23/2025 07:18:53 | 09/23/2025 08:45:52 | 10/20/2025 00:53:51 |  |  | 10/20/2025 00:54:35 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250923000524 | PCM-20250923-00000804 | TT-20250922-02280 | Telecom | Region_1 | HFR2U6199 | HFR6099 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/23/2025 12:28:56 | 09/30/2025 11:04:44 | 09/24/2025 00:28:56 | Radio Link Failure at HFR2U6199-P3 @ Sceco | 09/22/2025 22:02:05 | Minor | 28008 | Radio Link Failure | 09/22/2025 22:00:30 | P3 | 2G | hafr | Sceco | 2G NSA | HFR2U6199 | FLM_TE |  | Dear FLM, stop ping pong TT, pls. need HC at the site to check the Radio link alarm due to path imbalance between UP & DL , we need to check the path from RRU till antenna.. 1-Jumpers. 2-Connectors. 3-Antenna & RRU ports for damage. 4-Change antenna port if any free port available. 5-Remake connectors. GSM - Sector A - Cell 0 | PCM-20250923-00000771 | Dear FLM, stop ping pong TT, pls. need HC at the site to check the Radio link alarm due to path imbalance between UP & DL , we need to check the path from RRU till antenna.. Need to make RF path HC for RRU 60 , 2102310MNS6TEC411083 1-Jumpers. 2-Connectors. 3-Antenna & RRU ports for damage. 4-Change antenna port if any free port available. 5-Remake connectors. GSM - Sector A - Cell 0 | Dear FLM, stop ping pong TT, pls. need HC at the site to check the Radio link alarm due to path imbalance between UP & DL , we need to check the path from RRU till antenna.. Need to make RF path HC for RRU 60 , 2102310MNS6TEC411083 1-Jumpers. 2-Connectors. 3-Antenna & RRU ports for damage. 4-Change antenna port if any free port available. 5-Remake connectors. GSM - Sector A - Cell 0 |  |  |  | API | 09/23/2025 12:28:56 | 09/23/2025 13:06:01 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250923000537 | PCM-20250923-00000827 | TT-20250923-00944 | Telecom | Region_2 | RYMK0509 | RYMK0509 | Enviroment | Circuit Breaker/Sceco | Change SCECO circuit breaker | Nawaz Sharif Muhammad Iqbal | 09/23/2025 12:40:25 | 10/07/2025 20:52:28 | 09/24/2025 00:40:25 | JV with STC team to check power issue on RYMK0509 | 09/23/2025 12:39:05 | Minor | 676767681 | Health Check-WO to TE FME | 09/23/2025 12:39:07 | P1 | SRAN | quweyah | Sceco_STB | 2G_3G_LTE_5G NSA | RYMK0509 | FLM_TE | [8 empty] | API | 09/23/2025 12:40:25 | 10/07/2025 20:52:28 | [5 empty] | Nawaz Sharif Muhammad Iqbal | STC |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250923000866 | PCM-20250923-00001378 | TT-20250922-01808 | MW_HC | Region_1 | KFJ2485 | KFJ2485 |  |  |  | Mohamed Abdelaziz | 09/23/2025 17:02:51 | 10/07/2025 13:39:57 | 09/24/2025 05:02:51 | Huawei MW HC_P2 Observing Errors at KFJ2485-KFJ2003 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P2 | SRAN | khafji | Sceco | TX NSA | KFJ2485-KFJ2003 | FLM_TE |  | link not cleared | PCM-20250923-00001343 | link not cleared | link not cleared |  |  |  | API | 09/23/2025 17:02:51 | 09/24/2025 10:52:06 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250923000947 | PCM-20250923-00001514 | TT-20250923-01536 | Reference_telecom | Region_6 | BRQ9005 | BRQ9005 | Transsmission | MW_HW_fault | Replace XPIC Cable | Muhammad Jamal Khan Abbas Ali | 09/23/2025 17:51:38 | 10/19/2025 15:32:35 | 09/24/2025 05:51:38 | DemFail observed in BRQ9005_01 towards 10.221.246.114 @ Generator_SG | 09/23/2025 05:51:20 | Minor |  | DemFail | 09/23/2025 05:51:16 | P3 | Repeater | mohail | Generator_SG | TX NSA | BRQ9005 | FLM_TE | [8 empty] | API | 09/23/2025 17:51:38 | 10/09/2025 15:37:55 | 10/19/2025 15:32:17 |  |  | 10/19/2025 15:32:35 |  | Muhammad Jamal Khan Abbas Ali | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250923001070 | PCM-20250923-00001745 | TT-20250923-01738 | Reference_telecom | Region_4 | RYMK0665 | RYMK0665 |  |  |  | Ehab Ali Mohamed Abdou | 09/23/2025 19:40:57 | 09/23/2025 20:13:42 | 09/24/2025 07:40:57 | WRYMK0001 complete down | 09/23/2025 19:19:50 | Minor | 613007 | Wi-Fi AP Out Of Service | 09/23/2025 19:19:50 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20250923-00001723 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 09/23/2025 19:40:57 | 09/23/2025 20:13:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250923001078 | PCM-20250923-00001759 | TT-20250923-01768 | Telecom | Region_4 | JED1U6941 | JED6041 | Equipment | BTS_Cable | Replace Indoor Feeder Cable Connector | Mohamed Farag Abdelbary | 09/23/2025 19:46:03 | 09/24/2025 16:50:24 | 09/24/2025 01:46:03 | PT::FLM need to perform HC at JED1U6941-P1-CA-VIP (Bo request) | 09/23/2025 19:45:55 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/23/2025 19:45:55 | VIP | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1U6941-P1-CA-VIP | FLM_TE | [8 empty] | API | 09/23/2025 19:46:03 | 09/24/2025 16:45:29 | 09/24/2025 16:50:18 |  |  | 09/24/2025 16:50:24 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250924000260 | PCM-20250924-00000477 | TT-20250924-00459 | Reference_telecom | Region_6 | WABH0017 | ABH0017 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 09/24/2025 07:01:00 | 09/24/2025 08:22:00 | 09/24/2025 19:01:00 | DemFail observed in WABH0017 towards 10.3.86.219 @ Sceco | 09/23/2025 19:01:06 | Minor |  | DemFail | 09/23/2025 19:00:39 | P2 | WIFI | abha | Sceco | TX NSA | WABH0017 | FLM_TE | [8 empty] | API | 09/24/2025 07:01:00 | 09/24/2025 08:22:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250924000292 | PCM-20250924-00000535 | TT-20250924-00292 | Reference_telecom | Region_3 | MDTB0610 | MDTB0610 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 09/24/2025 07:34:31 | 10/01/2025 16:09:30 | 09/24/2025 19:34:31 | IP Clock Link Failure at MDTB2M5610-P1-WDM-HUB @ Generator_DG | 09/24/2025 02:03:17 | Minor | 26263 | IP Clock Link Failure | 09/24/2025 02:03:03 | P1 | SRAN | madinah | Generator_DG | 2G NSA | MDTB2M5610 | FLM_TE | MDTB0610 | Dear FLM Team, hub site is MDTB0610 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. | PCM-20250924-00000525 | Dear FLM Team, hub site is MDTB0610 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. | Dear FLM Team, hub site is MDTB0610 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. |  |  |  | API | 09/24/2025 07:34:31 | 09/24/2025 07:36:42 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250924000294 | PCM-20250924-00000537 | TT-20250924-00291 | Reference_telecom | Region_3 | MDTB0330 | MDTB0330 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 09/24/2025 07:35:22 | 10/01/2025 16:10:06 | 09/24/2025 19:35:22 | IP Clock Link Failure at MDTB0330-P1-HUB_SRAN @ Sceco_STB | 09/24/2025 02:05:47 | Minor | 26263 | IP Clock Link Failure | 09/24/2025 02:03:08 | P1 | SRAN | madinah | Sceco_STB | 2G NSA | MDTB0330 | FLM_TE | MDTB0330 | Dear FLM Team, hub site is MDTB0330 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. | PCM-20250924-00000526 | Dear FLM Team, hub site is MDTB0330 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. | Dear FLM Team, hub site is MDTB0330 We are observing visibility down at both ends . Kindly visit the site and check the issue locally. |  |  |  | API | 09/24/2025 07:35:22 | 09/24/2025 07:36:44 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250924001292 | PCM-20250924-00002218 | TT-20250924-02000 | Telecom | Region_4 | JED0086 | JED0086 | Transsmission | DWDM_SW | Alarm Cleared | Mohammed Altaf Naveed AbdulHakeem | 09/24/2025 18:34:29 | 09/24/2025 23:06:55 | 09/24/2025 22:34:29 | STC :: LINK DOWN B/W JED0086-JD3 | 09/24/2025 18:31:17 | Critical | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 09/24/2025 18:31:17 | VIP | 2G | jeddah | Sceco | DWDM NSA | JED0086-JD3 | FLM_TE | [8 empty] | API | 09/24/2025 18:34:29 | 09/24/2025 19:15:12 | 09/24/2025 19:26:31 | 09/24/2025 19:26:35 | 09/24/2025 19:55:15 | 09/24/2025 23:06:55 |  | Mohammed Altaf Naveed AbdulHakeem |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250924001325 | PCM-20250924-00002276 | TT-20250924-02049 | Reference_telecom | Region_4 | TUR0694 | TUR0694 |  |  |  | Rashid Shafique | 09/24/2025 19:00:00 | 09/25/2025 14:13:04 | 09/25/2025 01:00:00 | TRX OPERATION DEGRADED (SBTS TRX object degraded, see details from NetAct FM) at TUR0694-P2 (Ref:TT-20250922-00538) @ Sceco | 09/22/2025 09:54:35 | Major | 7607 | TRX OPERATION DEGRADED | 09/22/2025 09:54:32 | P2 | 2G | taif | Sceco | 2G NSA | TUR0694 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 09/24/2025 19:00:00 | 09/25/2025 14:13:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925000129 | PCM-20250925-00000444 | TT-20250925-00624 | Telecom | Region_1 | KBR6054 | KBR6054 |  |  |  | Meraj Husain Idd Baksh | 09/25/2025 03:31:59 | 09/30/2025 11:05:12 | 09/25/2025 15:31:59 | DCU Optical Module Transmit/Receive Fault at KBR6054-DCU1 @ Sceco | 09/25/2025 03:27:42 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 09/25/2025 03:26:23 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6054 | FLM_TE | [8 empty] | API | 09/25/2025 03:31:59 | 09/25/2025 06:34:24 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925000344 | PCM-20250925-00000802 | TT-20250925-01040 | Reference_EM | Region_2 | RIY2353 | RIY2353 |  |  |  | Ajmal Hafeez Hafeez Ahmed Awan | 09/25/2025 08:48:09 | 10/07/2025 13:39:58 | 09/25/2025 20:48:09 | Mains Failure at RIY2353-P2_SRAN @ Sceco | 09/25/2025 08:37:58 | Minor | 65109 | Mains Failure | 09/25/2025 08:37:54 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2353 | FLM_EM | [8 empty] | API | 09/25/2025 08:48:09 | 09/25/2025 10:02:46 | [6 empty] | Relocation_RO |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250925000412 | PCM-20250925-00000928 | TT-20250925-01143 | Telecom | Region_4 | RAB0473 | RAB0473 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Khizer Hayat | 09/25/2025 10:00:28 | 09/27/2025 16:06:33 | 09/25/2025 16:00:28 | BD_NOT_INSTALLED at RAB0473_OCS @ Sceco | 09/25/2025 08:15:03 | Major | 1-625 | BD_NOT_INSTALLED | 09/25/2025 08:15:00 | P1 | 2G | jeddah | Sceco | DWDM NSA | RAB0473 | FLM_TE | [5 empty] | - |  |  | API | 09/25/2025 10:00:28 | 09/25/2025 16:20:21 | 09/27/2025 13:04:13 | 09/27/2025 13:04:16 | 09/27/2025 13:04:24 | 09/27/2025 16:06:33 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925000465 | PCM-20250925-00001019 | TT-20250925-01227 | EM | Region_2 | RIY2M2353 | RIY2353 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Mohamed Ibrahim Elnagar | 09/25/2025 10:46:01 | 10/07/2025 13:43:16 | 09/25/2025 16:46:01 | 1(2G/LTE) sites down under RIY2353-P2/R2_RY4_HWBSC01 @ Sceco | 09/25/2025 10:37:31 | Major | 21825 | CSL Fault | 09/25/2025 10:37:28 | P2 | 2G | riyadh | Sceco | 2G_LTE SA | RIY2353-P2 | FLM_EM | RIY2353 | Results: DOWN SITE HUB RIY2353-P2 RIY2353 Summary: Hub: RIY2353, Down Count: 1, Down Sites: RIY2353-P2 Alarm Summary: RIY2353 Alarm Active on HUB |  |  |  |  | sites down |  | API | 09/25/2025 10:46:01 | 10/07/2025 13:43:16 | [5 empty] | Ahmed Mohamed Ibrahim Elnagar | Relocation_RO |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250925000685 | PCM-20250925-00001341 | TT-20250925-01568 | Telecom | Region_4 | KHU2654 | KHU2654 | Equipment | SFP_BTS | Replace SFP | Ahmad Kamal Abdelmawla | 09/25/2025 13:20:54 | 09/29/2025 16:03:19 | 09/26/2025 01:20:54 | PT:: FLM need to perform HC at KHU2654/R5 (BO request) | 09/25/2025 13:20:43 | Minor | 7115 | BASE STATION INFORMATION | 09/25/2025 13:20:43 | P2 | 2G | taif | Sceco | 2G_3G_LTE_5G NSA | KHU2654 | FLM_TE | [8 empty] | API | 09/25/2025 13:20:54 | 09/25/2025 15:22:38 | 09/29/2025 13:12:13 | 09/29/2025 13:12:15 | 09/29/2025 13:26:02 | 09/29/2025 16:03:19 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250925001129 | PCM-20250925-00002025 | TT-20250925-02206 | Reference_telecom | Region_1 | HFF2718 | HFF2718 |  |  |  | Muhammad Kashif M M Bashir | 09/25/2025 17:23:02 | 10/07/2025 13:40:04 | 09/26/2025 05:23:02 | NEC MW Observing TX Power,ODU Alarm at HFF2718-1(10.147.13.81) | 09/18/2025 10:28:33 | Minor |  | LOF | 09/18/2025 10:28:33 | P1 | SRAN | hafouf | Sceco | TX NSA | HFF2718-1(10.147.13.81) | FLM_TE | [8 empty] | API | 09/25/2025 17:23:02 | 09/28/2025 03:29:39 | 09/28/2025 04:13:47 | 09/28/2025 04:13:50 | 09/28/2025 04:14:37 |  |  |  | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001131 | PCM-20250925-00002027 | TT-20250925-02208 | Reference_telecom | Region_1 | HFS2024 | HFS2024 |  |  |  | Muhammad Kashif M M Bashir | 09/25/2025 17:23:03 | 10/07/2025 13:40:00 | 09/26/2025 05:23:03 | NEC MW Observing LOF,Frame ID,High BER at HFS2024-West(10.154.27.22) | 09/19/2025 08:15:35 | Minor |  | LOF | 09/19/2025 08:15:35 | P3 | SRAN | hafouf | Sceco | TX NSA | HFS2024-West(10.154.27.22) | FLM_TE | [8 empty] | API | 09/25/2025 17:23:03 | 09/26/2025 13:38:55 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001136 | PCM-20250925-00002032 | TT-20250925-02213 | Reference_telecom | Region_1 | JBKH0069 | JBKH0069 |  |  |  | Tahir Mahmood Hafiz Yar | 09/25/2025 17:23:09 | 10/04/2025 03:47:24 | 09/26/2025 05:23:09 | NEC MW Observing RX Level,LOF,LOF,Radio Traffic Aggregation Link,RX Level,LOF,LOF,LOF,RX Level,LOF,LOF,LOF,RX Level,RX Level,RX Level,RX Level,RX Level at JBKH0069(10.76.111.236) | 09/19/2025 08:46:55 | Minor |  | LOF | 09/19/2025 08:46:55 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBKH0069(10.76.111.236) | FLM_TE | [8 empty] | API | 09/25/2025 17:23:09 | 09/25/2025 18:01:20 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001138 | PCM-20250925-00002034 | TT-20250925-02215 | Reference_telecom | Region_1 | JBKH0601 | JBKH0601 |  |  |  | Tahir Mahmood Hafiz Yar | 09/25/2025 17:23:11 | 10/04/2025 03:47:25 | 09/26/2025 05:23:11 | NEC MW Observing Radio Traffic Aggregation Link,Radio Traffic Aggregation Link,Radio Traffic Aggregation Link,LAG Link at JBKH0601_3(10.76.111.197) | 08/27/2024 19:22:05 | Minor |  | LOF | 08/27/2024 19:22:05 | P1 | SRAN | jubail | Sceco | TX NSA | JBKH0601_3(10.76.111.197) | FLM_TE | [8 empty] | API | 09/25/2025 17:23:11 | 09/25/2025 18:01:21 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001154 | PCM-20250925-00002050 | TT-20250925-02231 | Reference_telecom | Region_6 | MHL9707 | MHL9707 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/25/2025 17:23:29 | 09/25/2025 19:17:20 | 09/26/2025 05:23:29 | NEC MW Observing Module,LOF,Frame ID,Low BER at MHL9707-2(10.154.172.2) | 09/16/2025 14:16:50 | Minor |  | LOF | 09/16/2025 14:16:50 | P3 | Repeater | mohail | Sceco | TX NSA | MHL9707-2(10.154.172.2) | FLM_TE | [8 empty] | API | 09/25/2025 17:23:29 | 09/25/2025 19:17:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001188 | PCM-20250925-00002086 | TT-20250925-02266 | Reference_telecom | Region_6 | TNMS0713 | TNMS0713 |  |  |  | Fawad Khan | 09/25/2025 17:24:02 | 09/25/2025 19:15:33 | 09/26/2025 05:24:02 | NEC MW Observing LOF,LOF,RX Level,LOF,Radio Traffic Aggregation Link,LOF,RX Level at TNMS0713_1(10.154.163.148) | 09/16/2025 14:12:14 | Minor |  | LOF | 09/16/2025 14:12:14 | P1 | 2G | namas | Sceco_STB | TX NSA | TNMS0713_1(10.154.163.148) | FLM_TE | [8 empty] | API | 09/25/2025 17:24:02 | 09/25/2025 19:15:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001203 | PCM-20250925-00002101 | TT-20250925-02285 | Reference_telecom | Region_3 | YBYN0305 | YBYN0305 |  |  |  | Muhammad Sajjad R3 | 09/25/2025 17:24:18 | 10/01/2025 16:05:12 | 09/26/2025 05:24:18 | NEC MW Observing Radio Traffic Aggregation Link at YBYN0305_1(10.159.106.41) | 09/15/2025 17:24:07 | Minor |  | LOF | 09/15/2025 17:24:07 | P3 | SRAN | yanbu | Generator_SG | TX NSA | YBYN0305_1(10.159.106.41) | FLM_TE | [8 empty] | API | 09/25/2025 17:24:18 | 09/27/2025 10:28:27 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250925001204 | PCM-20250925-00002102 | TT-20250925-02286 | Reference_telecom | Region_3 | YNB0155 | YNB0155 |  |  |  | Muhammad Sajjad R3 | 09/25/2025 17:24:19 | 10/01/2025 16:05:46 | 09/26/2025 05:24:19 | NEC MW Observing RX Level,LOF,LOF,RX Level,LOF,RX Level,LOF,RX Level,RX Level,LOF,LOF,LOF,RX Level,Radio Traffic Aggregation Link,LOF,RX Level,RX Level at YNB0155-YBDB0280_2(10.154.80.114) | 09/20/2025 03:22:11 | Minor |  | LOF | 09/20/2025 03:22:11 | P1 | SRAN | yanbu | Sceco_STB | TX NSA | YNB0155-YBDB0280_2(10.154.80.114) | FLM_TE | [8 empty] | API | 09/25/2025 17:24:19 | 09/27/2025 10:28:28 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250925001486 | PCM-20250925-00002536 | TT-20250727-00977 | Reference_telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 09/25/2025 21:35:45 | 09/25/2025 21:35:45 | 09/26/2025 03:35:45 | Observing Optical invalid On RYD-SR-02 GigabitEthernet11/1/3 FaultCause=Input Optical Power Too Low If Alias=<< Qwilt_ARA_Server_TenGigE0/8 ¦¦ CT08231852 | 07/27/2025 11:26:08 | Major | 2505224 | Optical Invalid | 07/27/2025 11:26:08 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | RYD | FLM_TE |  |  | PCM-20250925-00001553 | Dear Team - Please check. | Dear Team - Please check. |  |  |  | API | 09/25/2025 21:35:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250926000430 | PCM-20250926-00000678 | TT-20250926-00696 | Telecom | Region_3 | RSP0092 | RSP0092 |  |  |  | Muhammad Sajjad R3 | 09/26/2025 11:28:31 | 10/01/2025 16:06:59 | 09/26/2025 23:28:31 | RF Unit Maintenance Link Failure at RSP0092-P1-VIP_SRAN @ Generator_SG | 09/26/2025 11:24:55 | Minor | 26235 | RF Unit Maintenance Link Failure | 09/26/2025 11:23:12 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0092 | FLM_TE | [8 empty] | API | 09/26/2025 11:28:31 | 09/27/2025 10:28:30 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250927000254 | PCM-20250927-00000476 | TT-20250927-00398 | Reference_telecom | Region_2 | RIY2M1573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 09/27/2025 06:20:30 | 10/07/2025 13:40:07 | 09/27/2025 12:20:30 | (RFC Violation of RFC Time Exceed ) 1GSM Local Cell Unusable at RIY2M1573-P1-FON @ Sceco (Ref: CRQ000000534245) | 09/27/2025 06:19:03 | Major | 28016 | GSM Local Cell Unusable | 09/27/2025 06:18:41 | P1 | 2G | muzamiah | Sceco | 2G SA | RIY2M1573 | FLM_TE | [8 empty] | API | 09/27/2025 06:20:30 | 09/28/2025 12:43:26 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250927000640 | PCM-20250927-00001217 | TT-20250927-01035 | EM | Region_4 | JED1M7521 | JED0521 |  |  |  | Muhammad Arqam Muhammad Dawood | 09/27/2025 12:15:19 | 10/06/2025 17:59:46 | 09/28/2025 00:15:19 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at JED1M7521-CA-L900-L800-SBTS @ Sceco | 09/27/2025 12:07:00 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 09/27/2025 12:06:50 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7521 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 09/27/2025 12:15:19 | [7 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250927000715 | PCM-20250927-00001345 | TT-20250927-01017 | Reference_telecom | Region_2 | RIYA2U6269 | RIYA6169 |  |  |  | Tanveer Ahmad Fateh Muhammad | 09/27/2025 13:06:21 | 10/07/2025 13:40:04 | 09/28/2025 01:06:21 | External Clock Reference Problem at RIYA2U6269-P3-Tech @ Sceco | 09/27/2025 09:11:05 | Minor | 26262 | External Clock Reference Problem | 09/27/2025 09:07:38 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYA2U6269 | FLM_EM |  |  | PCM-20250927-00001257 | kindly check site was down suspected power issue RIYA2U6269 | kindly check site was down suspected power issue RIYA2U6269 |  |  |  | API | 09/27/2025 13:06:21 | 09/28/2025 11:13:59 | [6 empty] | ZAIN Planning |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250927000975 | PCM-20250927-00001728 | TT-20250927-01510 | Reference_telecom | Region_2 | RIYB6038 | RIYB6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 09/27/2025 15:53:50 | 10/07/2025 13:40:02 | 09/27/2025 21:53:50 | RF Unit VSWR Threshold Crossed at RIYB6038-P3_SRAN @ Sceco | 09/27/2025 12:53:28 | Major | 26529 | RF Unit VSWR Threshold Crossed | 09/27/2025 12:53:16 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6038 | FLM_TE | [8 empty] | API | 09/27/2025 15:53:50 | 09/27/2025 16:57:12 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250927001171 | PCM-20250927-00002001 | TT-20250927-01757 | MW_HC | Region_5 | MKJD0651 | MKJD0651 |  |  |  | Sohail Ashraf Muhammad Ashraf | 09/27/2025 18:05:13 | 10/21/2025 19:56:49 | 09/28/2025 06:05:13 | As BO Requested MW Nokia Observing modem 1 down and link counting PM errors MKJD0651-MKJD0569 | 09/27/2025 18:04:14 | Minor | 113388 | LOF | 09/27/2025 18:04:16 | P1 | 2G | makkah | Sceco | TX NSA | MKJD0651-MKJD0569 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing modem 1 down and link counting PM errors MKJD0651-MKJD0569 |  |  | API | 09/27/2025 18:05:13 | 10/21/2025 19:56:49 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250927001198 | PCM-20250927-00002036 | TT-20250927-01801 | Telecom | Region_2 | RIYC2U6713A | RIYC6013 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 09/27/2025 18:29:19 | 10/07/2025 13:40:03 | 09/28/2025 00:29:19 | RF Out of Service at RIYC2U6713A-P3 @ Sceco | 09/27/2025 18:24:43 | Major | 29248 | RF Out of Service | 09/27/2025 18:23:10 | P3 | 4G | riyadh | Sceco | 2G SA | RIYC2U6713A | FLM_TE | [8 empty] | API | 09/27/2025 18:29:19 | 09/27/2025 18:36:50 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250927001251 | PCM-20250927-00002116 | TT-20250927-01888 | MW_HC | Region_6 | KMBS9501 | KMBS9501 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 09/27/2025 19:26:35 | 09/27/2025 23:45:51 | 09/28/2025 07:26:35 | As BO Requested MW Nokia Observing Performance issue For MW Link KMBS9501-KMBS9702 | 09/27/2025 19:25:44 | Minor | 113388 | LOF | 09/27/2025 19:25:46 | P1 | Repeater | khamis mushyet | Generator_DG | TX NSA | KMBS9501-KMBS9702 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing Performance issue For MW Link KMBS9501-KMBS9702 |  |  | API | 09/27/2025 19:26:35 | 09/27/2025 23:45:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250927001291 | PCM-20250927-00002184 | TT-20250927-01965 | Telecom | Region_2 | RIYC2U6713B | RIYC6013 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 09/27/2025 20:45:12 | 10/07/2025 13:40:05 | 09/28/2025 08:45:12 | RF Unit Temperature Unacceptable at RIYC2U6713B-P3 @ Sceco | 09/27/2025 20:38:15 | Minor | 26525 | RF Unit Temperature Unacceptable | 09/27/2025 20:38:11 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYC2U6713B | FLM_TE | [8 empty] | API | 09/27/2025 20:45:12 | 09/28/2025 12:29:36 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250927001325 | PCM-20250927-00002248 | TT-20250927-02038 | Telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 09/27/2025 21:41:21 | 10/07/2025 13:40:06 | 09/28/2025 03:41:21 | Cell Unavailable at RIYB2U6778-P3 @ Sceco | 09/27/2025 21:38:11 | Major | 29240 | Cell Unavailable | 09/27/2025 21:36:37 | P3 | 4G | riyadh | Sceco | LTE SA | RIYB2U6778 | FLM_TE | [8 empty] | API | 09/27/2025 21:41:21 | 09/28/2025 12:29:37 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250928000118 | PCM-20250928-00000249 | TT-20250928-00227 | EM | Region_4 | JED1M8200 | JED2200 |  |  |  | Nabil Nazih Mohamoud Ahmed | 09/28/2025 03:19:54 | 10/06/2025 17:59:51 | 09/28/2025 09:19:54 | RECTIFIER MODULE FAILURE at JED1M8200-CA-L800-P1-VIP-SBTS @ Sceco | 09/28/2025 03:14:42 | Major | 7103 | RECTIFIER MODULE FAILURE | 09/28/2025 03:11:29 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M8200 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/28/2025 03:19:54 | 09/28/2025 19:05:42 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20250928000151 | PCM-20250928-00000299 | TT-20250928-00269 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 09/28/2025 03:55:27 | 09/28/2025 03:55:27 | 09/28/2025 09:55:27 | Observing 2*100G ALU CIDs flapped and restored B/W MAK | 09/28/2025 03:49:41 | Major | 5000003 | Link Down | 09/28/2025 03:49:41 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | MK1 | FLM_TE | [5 empty] | Observing 2*100G ALU CIDs flapped and restored B/W MAK |  |  | API | 09/28/2025 03:55:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250928000256 | PCM-20250928-00000485 | TT-20250928-00461 | Telecom | Region_1 | KBR6005 | KBR6005 |  |  |  | Meraj Husain Idd Baksh | 09/28/2025 06:37:46 | 10/06/2025 16:48:47 | 09/28/2025 12:37:46 | BBU CPRI Interface Error at KBR6005-P3_SRAN @ Sceco | 09/28/2025 06:35:20 | Major | 26234 | BBU CPRI Interface Error | 09/28/2025 06:32:17 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6005 | FLM_TE | [8 empty] | API | 09/28/2025 06:37:46 | 09/28/2025 07:32:42 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250928000259 | PCM-20250928-00000489 | TT-20250928-00464 | Telecom | Region_1 | KBR2U6705 | KBR6005 |  |  |  | Meraj Husain Idd Baksh | 09/28/2025 06:40:20 | 10/06/2025 16:48:48 | 09/28/2025 12:40:20 | RF Out of Service at KBR2U6705-P3 @ Sceco | 09/28/2025 06:35:26 | Major | 29248 | RF Out of Service | 09/28/2025 06:33:54 | P3 | 4G | dammam | Sceco | 2G SA | KBR2U6705 | FLM_TE | [8 empty] | API | 09/28/2025 06:40:20 | 09/28/2025 07:32:43 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250928000485 | PCM-20250928-00000909 | TT-20250928-00817 | Telecom | Region_2 | WTUM0001 | WTUM0001 | Equipment | CB_BTS | Switch on CB on Rectifier | Muhammad Tahir Abdulrazzaq | 09/28/2025 09:50:58 | 10/12/2025 10:35:47 | 09/28/2025 21:50:58 | WTUM0001 Complete down | 09/28/2025 09:41:52 | Minor | 613007 | Wi-Fi AP Out Of Service | 09/28/2025 09:41:52 | P3 | WIFI | Tumair | Sceco | Wifi SA | WTUM0001 | FLM_TE |  | Not observing any issue from our end kindly check site locally. | PCM-20250928-00000902 | Not observing any issue from our end kindly check site locally. | Not observing any issue from our end kindly check site locally. |  |  |  | API | 09/28/2025 09:50:58 | 09/29/2025 13:41:11 | 10/12/2025 10:35:11 |  |  | 10/12/2025 10:35:47 |  | Muhammad Tahir Abdulrazzaq | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250928000500 | PCM-20250928-00000933 | TT-20250928-00692 | Reference_telecom | Region_2 | KJHD0750 | KJHD0750 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hakim Ullah Raif Ullah Jan | 09/28/2025 10:00:20 | 10/09/2025 09:01:02 | 09/28/2025 22:00:20 | IP Clock Link Failure at KJHD0750-P2_SRAN @ Sceco | 09/28/2025 05:45:57 | Minor | 26263 | IP Clock Link Failure | 09/28/2025 05:44:24 | P2 | SRAN | al kharj | Sceco | 2G NSA | KJHD0750 | FLM_TE |  |  | PCM-20250928-00000829 | Need HC on link KJHD0750-KJHD2749 as LOF alarms exist during this time | Need HC on link KJHD0750-KJHD2749 as LOF alarms exist during this time |  |  |  | API | 09/28/2025 10:00:20 | 10/07/2025 15:44:13 | 10/09/2025 09:00:47 |  |  | 10/09/2025 09:01:02 |  | Hakim Ullah Raif Ullah Jan | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250928000549 | PCM-20250928-00001009 | TT-20250928-00920 | Telecom | Region_5 | MK1 | MK1 |  |  |  | Muhammad Zubair | 09/28/2025 10:32:37 | 10/05/2025 12:50:32 | 09/28/2025 16:32:37 | Observing Multiple ALU CIDs Down B/W MK & RY | 09/28/2025 10:30:21 | Major | 5000003 | Link Down | 09/28/2025 10:30:21 | P1 | BSC | makkah | Sceco_STB | IPBB NSA | Observing Multiple ALU CIDs Down B/W MK & RY | FLM_TE | [5 empty] | Observing Multiple ALU CIDs Down B/W MK & RY |  |  | API | 09/28/2025 10:32:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250928000705 | PCM-20250928-00001273 | TT-20250925-02560 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 09/28/2025 12:16:45 | 09/28/2025 12:16:45 | 09/28/2025 18:16:45 | Observing Multiple ALU CIDs Down B/W MAK - HA | 09/25/2025 19:17:32 | Major | 5000003 | Link Down | 09/25/2025 19:17:32 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE |  |  | PCM-20250928-00001010 | Please check and confirm alarm status with FO | Please check and confirm alarm status with FO |  |  |  | API | 09/28/2025 12:16:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250928001212 | PCM-20250928-00002086 | TT-20250928-01939 | Reference_telecom | Region_5 | MAK1MN0320 | MAK0320 |  |  |  | Atif Javed Javed Hussain | 09/28/2025 17:28:07 | 10/06/2025 16:48:51 | 09/28/2025 21:28:07 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 09/28/2025 12:59:32 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 09/28/2025 12:59:27 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0320 | FLM_TE |  |  | PCM-20250928-00002023 | kindly check and confirm no dust or air blockage | kindly check and confirm no dust or air blockage |  |  |  | API | 09/28/2025 17:28:07 | 10/01/2025 16:32:02 | [6 empty] | NSN_Care |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250928001306 | PCM-20250928-00002251 | TT-20250928-02143 | Reference_telecom | Region_5 | BIK0788 | BIK0788 |  |  |  | Hazem Ali Moustafa Ali | 09/28/2025 19:04:46 | 09/30/2025 01:49:50 | 09/29/2025 01:04:46 | TRX OPERATION DEGRADED at BIK0788-P3(REF: TT-20250925-01675) | 09/26/2025 07:47:37 | Major | 7607 | TRX OPERATION DEGRADED | 09/26/2025 07:47:37 | P3 | 2G | makkah | Generator_SG | 2G NSA | BIK0788 | FLM_TE | [8 empty] | API | 09/28/2025 19:04:46 | 09/30/2025 01:49:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250928001529 | PCM-20250928-00002587 | TT-20250928-02517 | MW_HC | Region_6 | NJR0074 | NJR0074 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Shahid Ali Roshan Ali | 09/28/2025 23:24:44 | 10/19/2025 02:00:31 | 09/29/2025 11:24:44 | As BO Requested MW Nokia Observing modem 4 down and link counting PM errors NJR0074-NJR0011 | 09/28/2025 23:23:36 | Minor | 113388 | LOF | 09/28/2025 23:23:38 | P2 | 2G | najran | Sceco | TX NSA | NJR0074-NJR0011 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing modem 4 down and link counting PM errors NJR0074-NJR0011 |  |  | API | 09/28/2025 23:24:44 | 09/29/2025 00:38:13 | 10/19/2025 02:00:14 |  |  | 10/19/2025 02:00:31 |  | Shahid Ali Roshan Ali | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929000043 | PCM-20250929-00000093 | TT-20250929-00099 | EM | Region_4 | HHR0494 | HHR0494 |  |  |  | Anas Mohamedelamin Abbas Mustafa | 09/29/2025 00:55:58 | 09/29/2025 01:35:39 | 09/29/2025 06:55:58 | RECTIFIER MODULE FAILURE at HHR0494-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 09/29/2025 00:47:34 | Major | 7103 | RECTIFIER MODULE FAILURE | 09/29/2025 00:47:25 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0494 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/29/2025 00:55:58 | 09/29/2025 01:35:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20250929000266 | PCM-20250929-00000697 | TT-20250929-00902 | Telecom | Region_4 | YLM1M7876 | YLM0876 |  |  |  | Riasat Ali Allah Baksh | 09/29/2025 07:05:43 | 09/29/2025 13:49:20 | 09/29/2025 13:05:43 | PLR Issue at 30 sites under R4 | 09/29/2025 06:04:25 | Major | 61611 | TWAMP PLR Threshold Crossed | 09/29/2025 06:04:25 | P1 | 4G | alaith | Generator_DG | 2G_3G_LTE SA | YLM1M7876-L800-SBTS-P1 YLM1M7789-L800-P3 DGB1M8169-USF-P3 SDY1M7163-G9-U9-NL8-SBTS-P3 HAM1M7025-G9-U9-NL8-SBTS-P2-USF SDY1M7766-L800-SBTS-P3 JDJZ1M7870-G9-NL8-L18-SBTS-P3 YLM1M7740-USF-P3 YLM1M7391-L800-P1-SBTS DKA1M7347-G9-L8-L18-SBTS-P3 YLM1M8369-L800-P1-SBTS YLM1M7756-L800-P1 JDJZ1M7773-P2-L800 YLM1M7752-P1-L800-SBTS HHR1M7815-P1-VIP-HHR-L800 MKYL1M7908-P2 JDRS1M7757-G9-NL8-SBTS-P3 MTB1M7021-G9-U9-NL8-SBTS-P2-USF_NNN HHR1M7874-P1-VIP-HHR-L800 MKMD1M8252-P3-L800 JED1M8119-CA-L800-P3 SQR1M7074-G9-L8-L9-SBTS-P2-USF SQR1M7080-G9-L9-P2-USF SQR1M7162-G9-L8-L18-L21-SBTS-P2-USF SQR1M7161-G9-NL8-L18-SBTS-P2-USF SIR1M7160-USF-P3 UKZ1M7072-USF-P3-CA-L900-L800-SBTS UKZ1M7073-USF-P3 UKZ1M7211-USF-P3 SQR1M7078-USF-P3 | FLM_TE |  |  | PCM-20250929-00000632 | Site TRM feedback YLM1M7876-L800-SBTS-P1 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 YLM1M7789-L800-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 DGB1M8169-USF-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 SDY1M7163-G9-U9-NL8-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 HAM1M7025-G9-U9-NL8-SBTS-P2-USF PM errors ,RSL degraded on MW JDJZ0770-BLH0044 SDY1M7766-L800-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 JDJZ1M7870-G9-NL8-L18-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0770-BLH0044 YLM1M7740-USF-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 YLM1M7391-L800-P1-SBTS PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 DKA1M7347-G9-L8-L18-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0770-BLH0044 YLM1M8369-L800-P1-SBTS PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 YLM1M7756-L800-P1 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 JDJZ1M7773-P2-L800 PM errors ,RSL degraded on MW JDJZ0770-BLH0044 YLM1M7752-P1-L800-SBTS PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 HHR1M7815-P1-VIP-HHR-L800 PM errors ,RSL degraded on MW JDRS0757-RAB0473 MKYL1M7908-P2 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 JDRS1M7757-G9-NL8-SBTS-P3 PM errors ,RSL degraded on MW JDRS0757-RAB0473 MTB1M7021-G9-U9-NL8-SBTS-P2-USF_NNN PM errors ,RSL degraded on MW JDJZ0770-BLH0044 HHR1M7874-P1-VIP-HHR-L800 PM errors ,RSL degraded on MW JDRS0757-RAB0473 JED1M8119-CA-L800-P3 HC for JED2119-JED0011 SQR1M7074-G9-L8-L9-SBTS-P2-USF HC for TFBH9401- TFBH9443 SQR1M7080-G9-L9-P2-USF HC for TFBH9401- TFBH9444 SQR1M7162-G9-L8-L18-L21-SBTS-P2-USF HC for TFBH9401- TFBH9445 SQR1M7161-G9-NL8-L18-SBTS-P2-USF HC for TFBH9401- TFBH9446 SIR1M7160-USF-P3 HC for TFBH9401- TFBH9447 UKZ1M7072-USF-P3-CA-L900-L800-SBTS HC for TFBH9401- TFBH9448 UKZ1M7073-USF-P3 HC for TFBH9401- TFBH9449 UKZ1M7211-USF-P3 HC for TFBH9401- TFBH9450 SQR1M7078-USF-P3 HC for TFBH9401- TFBH9451 | Site TRM feedback YLM1M7876-L800-SBTS-P1 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 YLM1M7789-L800-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 DGB1M8169-USF-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 SDY1M7163-G9-U9-NL8-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 HAM1M7025-G9-U9-NL8-SBTS-P2-USF PM errors ,RSL degraded on MW JDJZ0770-BLH0044 SDY1M7766-L800-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 JDJZ1M7870-G9-NL8-L18-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0770-BLH0044 YLM1M7740-USF-P3 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 YLM1M7391-L800-P1-SBTS PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 DKA1M7347-G9-L8-L18-SBTS-P3 PM errors ,RSL degraded on MW JDJZ0770-BLH0044 YLM1M8369-L800-P1-SBTS PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 YLM1M7756-L800-P1 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 JDJZ1M7773-P2-L800 PM errors ,RSL degraded on MW JDJZ0770-BLH0044 YLM1M7752-P1-L800-SBTS PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 HHR1M7815-P1-VIP-HHR-L800 PM errors ,RSL degraded on MW JDRS0757-RAB0473 MKYL1M7908-P2 PM errors ,RSL degraded on MW JDJZ0766-JDJZ0767 JDRS1M7757-G9-NL8-SBTS-P3 PM errors ,RSL degraded on MW JDRS0757-RAB0473 MTB1M7021-G9-U9-NL8-SBTS-P2-USF_NNN PM errors ,RSL degraded on MW JDJZ0770-BLH0044 HHR1M7874-P1-VIP-HHR-L800 PM errors ,RSL degraded on MW JDRS0757-RAB0473 JED1M8119-CA-L800-P3 HC for JED2119-JED0011 SQR1M7074-G9-L8-L9-SBTS-P2-USF HC for TFBH9401- TFBH9443 SQR1M7080-G9-L9-P2-USF HC for TFBH9401- TFBH9444 SQR1M7162-G9-L8-L18-L21-SBTS-P2-USF HC for TFBH9401- TFBH9445 SQR1M7161-G9-NL8-L18-SBTS-P2-USF HC for TFBH9401- TFBH9446 SIR1M7160-USF-P3 HC for TFBH9401- TFBH9447 UKZ1M7072-USF-P3-CA-L900-L800-SBTS HC for TFBH9401- TFBH9448 UKZ1M7073-USF-P3 HC for TFBH9401- TFBH9449 UKZ1M7211-USF-P3 HC for TFBH9401- TFBH9450 SQR1M7078-USF-P3 HC for TFBH9401- TFBH9451 |  |  |  | API | 09/29/2025 07:05:43 | 09/29/2025 13:49:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929000691 | PCM-20250929-00001356 | TT-20250929-01590 | Reference_telecom | Region_4 | HAW1M8422 | HAW2422 | Equipment | SFP_BTS | Replace SFP | Rashid Shafique | 09/29/2025 12:55:22 | 10/06/2025 15:18:36 | 09/29/2025 18:55:22 | BASE STATION NOTIFICATION(RET Antenna control failure) at HAW1M8422-P3(REF. TT-20250928-01783) | 09/28/2025 18:41:53 | Major | 7652 | BASE STATION NOTIFICATION | 09/28/2025 18:41:53 | P2 | 4G | taif | Generator_SG | LTE NSA | HAW1M8422 | FLM_TE | [8 empty] | API | 09/29/2025 12:55:22 | 10/04/2025 18:46:02 | 10/04/2025 18:51:18 | 10/04/2025 18:51:32 | 10/04/2025 18:51:36 | 10/06/2025 15:18:36 |  | Rashid Shafique |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929000956 | PCM-20250929-00001754 | TT-20250929-01974 | Telecom | Region_4 | TAF1M7167 | TAF0167 | Equipment | SFP_BTS | Clean SFP | Ahmad Kamal Abdelmawla | 09/29/2025 15:53:37 | 10/14/2025 20:55:13 | 09/30/2025 03:53:37 | PT::FLM need to check FSP overheating and Unit temperature flapping at TAF1M7167-CA-L800-P2 at 28th Sep | 09/29/2025 15:52:00 | Minor | 676767671 | Health Check-WO to TE FME | 09/29/2025 15:52:00 | P2 | 4G | taif | Sceco | 2G_3G_LTE_5G NSA | TAF1M7167 | FLM_TE | [8 empty] | API | 09/29/2025 15:53:37 | 09/29/2025 15:58:28 | 10/14/2025 20:55:04 |  |  | 10/14/2025 20:55:13 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20250929000973 | PCM-20250929-00001783 | TT-20250929-02008 | Reference_telecom | Region_3 | MDN1W6072 | MDN1W6072 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 09/29/2025 16:09:49 | 10/03/2025 23:10:53 | 09/30/2025 04:09:49 | MDN1W6072 is partial down (REF :: TT-20250918-02263) | 09/29/2025 15:38:04 | Minor | 613007 | Wi-Fi AP Out Of Service | 09/29/2025 15:38:04 | P1 | WIFI | madinah | Sceco | Wifi SA | MDN1W6072_1-GF-AP11 | FLM_TE | [8 empty] | API | 09/29/2025 16:09:49 | 09/29/2025 17:06:54 | 10/03/2025 23:10:53 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929000994 | PCM-20250929-00001819 | TT-20250929-02046 | Telecom | Region_4 | SJED1S7332 | SJED0332 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 09/29/2025 16:27:26 | 10/04/2025 17:50:37 | 09/30/2025 04:27:26 | PT:: BO need to check Difference between BTS master clock and reference frequency at SJED1S7332-CA-P3 | 09/29/2025 16:25:37 | Minor | 676767671 | Health Check-WO to TE FME | 09/29/2025 16:25:39 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | SJED1S7332-CA-P3 | FLM_TE | [8 empty] | API | 09/29/2025 16:27:26 | 10/02/2025 12:16:49 | 10/04/2025 17:50:30 |  |  | 10/04/2025 17:50:37 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001012 | PCM-20250929-00001845 | TT-20250929-02108 | MW_HC | Region_2 | RYQS2662 | RYQS2662 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 09/29/2025 16:38:13 | 10/16/2025 20:25:03 | 09/30/2025 04:38:13 | Huawei MW HC_P2 Observing Errors at RYQS2662-SRIY0230/SRIY0231/SWRIY0230(wifi) | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P2 | SRAN | riyadh | Power Cube | TX NSA | RYQS2662-SRIY0230/SRIY0231/SWRIY0230(wifi) | FLM_TE | [8 empty] | API | 09/29/2025 16:38:13 | 09/29/2025 16:50:39 | 10/16/2025 20:24:52 |  |  | 10/16/2025 20:25:03 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001017 | PCM-20250929-00001850 | TT-20250929-02114 | MW_HC | Region_2 | RIYB6100 | RIYB6100 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 09/29/2025 16:38:20 | 09/30/2025 05:54:36 | 09/30/2025 04:38:20 | Huawei MW HC_P2 Observing Errors at RIYB6100/RoyalTerminalAirportSite-RIY0227 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P1 | SRAN | riyadh | Sceco | TX NSA | RIYB6100/RoyalTerminalAirportSite-RIY0227 | FLM_TE | [8 empty] | API | 09/29/2025 16:38:20 | 09/30/2025 05:54:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001039 | PCM-20250929-00001872 | TT-20250929-02143 | MW_HC | Region_2 | BAD0106 | BAD0106 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 09/29/2025 16:39:00 | 09/29/2025 18:05:49 | 09/30/2025 04:39:00 | Huawei MW HC_P1 Observing Errors at BAD0106-HIL0117 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P1 | SRAN | al rass | Sceco_STB | TX NSA | BAD0106-HIL0117 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:00 | 09/29/2025 18:05:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001043 | PCM-20250929-00001876 | TT-20250929-02147 | MW_HC | Region_4 | JDMK2400 | JDMK2400 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:39:05 | 09/29/2025 16:44:27 | 09/30/2025 04:39:05 | Nokia MW HC_P0 Observing Performance Issue at JDMK2400_01-JED0843_01 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | jeddah | Sceco | TX NSA | JDMK2400_01-JED0843_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:05 | 09/29/2025 16:44:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001046 | PCM-20250929-00001879 | TT-20250929-02150 | MW_HC | Region_4 | JED2342 | JED2342 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:39:09 | 10/02/2025 00:02:36 | 09/30/2025 04:39:09 | Nokia MW HC_P0 Observing Performance Issue at JED2342-JED0814_01 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2342-JED0814_01 | FLM_TE | [8 empty] | Manual | 09/29/2025 16:39:09 | 10/02/2025 00:02:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001052 | PCM-20250929-00001885 | TT-20250929-02156 | MW_HC | Region_4 | HJR0231 | HJR0231 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Khizer Hayat | 09/29/2025 16:39:15 | 10/08/2025 08:56:16 | 09/30/2025 04:39:15 | Nokia MW HC_P0 Observing Performance Issue at HJR0231_01-HJR0233_01 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P2 | 2G | jeddah | Sceco | TX NSA | HJR0231_01-HJR0233_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:15 | 09/29/2025 17:49:08 | 10/08/2025 08:55:31 |  |  | 10/08/2025 08:56:16 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001057 | PCM-20250929-00001890 | TT-20250929-02161 | MW_HC | Region_4 | JED2189 | JED2189 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:39:20 | 09/29/2025 16:45:17 | 09/30/2025 04:39:20 | Nokia MW HC_P1 Observing Performance Issue at JED2189_01-JED0368_02 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2189_01-JED0368_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:20 | 09/29/2025 16:45:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001059 | PCM-20250929-00001893 | TT-20250929-02163 | MW_HC | Region_6 | BHAB2334 | BHAB2334 |  |  |  | SHAH KHALID | 09/29/2025 16:39:22 | 09/29/2025 17:02:50 | 09/30/2025 04:39:22 | Nokia MW HC_P0 Observing Performance Issue at BHAB2334_01-BHAB2009_02 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | Albaha | Generator_SG | TX NSA | BHAB2334_01-BHAB2009_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:22 | 09/29/2025 17:02:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001061 | PCM-20250929-00001895 | TT-20250929-02165 | MW_HC | Region_4 | MUMA0772 | MUMA0772 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:39:24 | 09/29/2025 17:50:50 | 09/30/2025 04:39:24 | Nokia MW HC_P0 Observing Performance Issue at MUMA0772_01-JDJZ0776_11 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | qunfuddah | Sceco | TX NSA | MUMA0772_01-JDJZ0776_11 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:24 | 09/29/2025 17:50:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001063 | PCM-20250929-00001897 | TT-20250929-02167 | MW_HC | Region_6 | BHAB2052 | BHAB2052 |  |  |  | SHAH KHALID | 09/29/2025 16:39:27 | 09/29/2025 17:02:51 | 09/30/2025 04:39:27 | Nokia MW HC_P0 Observing Performance Issue at BHAB2052_01-NMR0133_03 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | Baha | Generator_SG | TX NSA | BHAB2052_01-NMR0133_03 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:27 | 09/29/2025 17:02:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001064 | PCM-20250929-00001898 | TT-20250929-02168 | MW_HC | Region_6 | NMR2044 | NMR2044 |  |  |  | SHAH KHALID | 09/29/2025 16:39:27 | 09/29/2025 17:02:51 | 09/30/2025 04:39:27 | Nokia MW HC_P0 Observing Performance Issue at NMR2044_01-NMR2024_01 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | 2G | Baha | Generator_SG | TX NSA | NMR2044_01-NMR2024_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:27 | 09/29/2025 17:02:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001066 | PCM-20250929-00001900 | TT-20250929-02170 | MW_HC | Region_4 | JED2128 | JED2128 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:39:29 | 09/29/2025 16:39:29 | 09/30/2025 04:39:29 | Nokia MW HC_P1 Observing Performance Issue at JED2128-JED0086_6 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | VIP | 2G | jeddah | Sceco | TX NSA | JED2128-JED0086_6 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001067 | PCM-20250929-00001901 | TT-20250929-02171 | MW_HC | Region_4 | JED2005 | JED2005 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:39:31 | 09/29/2025 18:12:51 | 09/30/2025 04:39:31 | Nokia MW HC_P2 Observing Modem Down at JED2005-MKJD0572_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2005-MKJD0572_03 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:31 | 09/29/2025 18:12:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001071 | PCM-20250929-00001905 | TT-20250929-02175 | MW_HC | Region_4 | FAT2363 | FAT2363 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 09/29/2025 16:39:35 | 10/02/2025 11:20:24 | 09/30/2025 04:39:35 | Nokia MW HC_P1 Observing Performance Issue at FAT2363-FAT0348 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | FAT2363-FAT0348 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:35 | 09/29/2025 17:02:55 | 10/02/2025 11:20:01 |  |  | 10/02/2025 11:20:24 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001072 | PCM-20250929-00001906 | TT-20250929-02176 | MW_HC | Region_4 | RYMK0754 | RYMK0754 | Transsmission | MW_HW_fault | Replace ODU | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:39:35 | 10/13/2025 16:09:27 | 09/30/2025 04:39:35 | Nokia MW HC_P0 Observing Performance Issue at RYMK0754_01-RYMK0534_01 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | taif | Sceco | TX NSA | RYMK0754_01-RYMK0534_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:35 | 09/29/2025 17:33:36 | 10/13/2025 12:23:38 | 10/13/2025 13:27:30 | 10/13/2025 13:27:33 | 10/13/2025 16:09:27 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001073 | PCM-20250929-00001907 | TT-20250929-02177 | MW_HC | Region_4 | RAB0966 | RAB0966 | Transsmission | MW_HW_stuck | Reset FAN | Khizer Hayat | 09/29/2025 16:39:36 | 10/08/2025 08:55:16 | 09/30/2025 04:39:36 | Nokia MW HC_P0 Observing Performance Issue at RAB0966_01-RAB0475_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | RAB0966_01-RAB0475_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:36 | 09/29/2025 17:49:09 | 10/08/2025 08:54:50 |  |  | 10/08/2025 08:55:16 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001080 | PCM-20250929-00001916 | TT-20250929-02186 | MW_HC | Region_4 | JED2629 | JED2629 |  |  |  | Nazeer Mohammed | 09/29/2025 16:39:45 | 10/01/2025 11:45:29 | 09/30/2025 04:39:45 | Nokia MW HC_P1 Observing Performance Issue at JED2629_XE-JED0580 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2629_XE-JED0580 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:45 | 10/01/2025 11:45:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20250929001082 | PCM-20250929-00001915 | TT-20250929-02185 | MW_HC | Region_4 | RYMK0549 | RYMK0549 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:39:45 | 10/23/2025 12:55:03 | 09/30/2025 04:39:45 | As per bo request Nokia MW HC FLM to Check Link RYMK0549-TAF0170 Radio Traffic Agg active alarms | 09/29/2025 16:39:38 | Minor | 113388 | LOF | 09/29/2025 16:39:36 | P1 | 2G | taif | Generator_SG | TX NSA | RYMK0549-TAF0170 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM to Check Link RYMK0549-TAF0170 Radio Traffic Agg active alarms |  |  | API | 09/29/2025 16:39:45 | 09/29/2025 17:33:37 | 10/23/2025 12:55:03 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001085 | PCM-20250929-00001919 | TT-20250929-02189 | MW_HC | Region_6 | MHL0533 | MHL0533 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/29/2025 16:39:48 | 09/29/2025 17:16:48 | 09/30/2025 04:39:48 | Nokia MW HC_P1 Observing Performance Issue at MHL0533-MHL0123-05 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | mohail | Generator_SG | TX NSA | MHL0533-MHL0123-05 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:48 | 09/29/2025 17:16:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001086 | PCM-20250929-00001920 | TT-20250929-02190 | MW_HC | Region_4 | HAW2335 | HAW2335 |  |  |  | Rashid Shafique | 09/29/2025 16:39:49 | 09/30/2025 14:46:05 | 09/30/2025 04:39:49 | Nokia MW HC_P2 Observing Performance Issue at HAW2335-HAW2118_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | HAW2335-HAW2118_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:49 | 09/30/2025 14:46:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001088 | PCM-20250929-00001922 | TT-20250929-02192 | MW_HC | Region_4 | JED2574 | JED2574 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:39:51 | 10/20/2025 10:43:26 | 09/30/2025 04:39:51 | Nokia MW HC_P1 Observing Performance Issue at JED2574-JED0532 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED2574-JED0532 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:51 | 10/20/2025 10:34:28 | 10/20/2025 10:35:02 | 10/20/2025 10:35:04 | 10/20/2025 10:43:26 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001089 | PCM-20250929-00001923 | TT-20250929-02193 | MW_HC | Region_4 | JED2388 | JED2388 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:39:52 | 09/29/2025 16:39:52 | 09/30/2025 04:39:52 | Nokia MW HC_P0 Observing Performance Issue at JED2388-JED0449_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2388-JED0449_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001090 | PCM-20250929-00001924 | TT-20250929-02194 | MW_HC | Region_4 | JED0957 | JED0957 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:39:53 | 09/29/2025 18:12:52 | 09/30/2025 04:39:53 | Nokia MW HC_P1 Observing Performance Issue at JED0957 -SH1-JED0008-9 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED0957 -SH1-JED0008-9 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:53 | 09/29/2025 18:12:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001091 | PCM-20250929-00001925 | TT-20250929-02195 | MW_HC | Region_4 | JED0550 | JED0550 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Abd Elrahman Suliman Mohmed Suliman | 09/29/2025 16:39:56 | 10/01/2025 13:17:34 | 09/30/2025 04:39:56 | Nokia MW HC_P2 Observing Modem Down at JED0550_01-JED0011-5 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0550_01-JED0011-5 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:56 | 09/30/2025 12:50:17 | 09/30/2025 13:09:52 | 09/30/2025 13:09:55 | 09/30/2025 13:09:58 | 10/01/2025 13:17:34 |  | Abd Elrahman Suliman Mohmed Suliman |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001094 | PCM-20250929-00001928 | TT-20250929-02198 | MW_HC | Region_4 | JED0699 | JED0699 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:39:58 | 09/29/2025 16:39:58 | 09/30/2025 04:39:58 | Nokia MW HC_P0 Observing Performance Issue at JED0699-JED0164_07 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0699-JED0164_07 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001095 | PCM-20250929-00001929 | TT-20250929-02199 | MW_HC | Region_4 | JED2001 | JED2001 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:39:59 | 09/29/2025 16:44:28 | 09/30/2025 04:39:59 | Nokia MW HC_P2 Observing Performance Issue at JED2001_01-JED0431 -7 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2001_01-JED0431 -7 | FLM_TE | [8 empty] | API | 09/29/2025 16:39:59 | 09/29/2025 16:44:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001096 | PCM-20250929-00001930 | TT-20250929-02200 | MW_HC | Region_4 | JED0881 | JED0881 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 16:40:00 | 09/29/2025 17:40:59 | 09/30/2025 04:40:00 | Nokia MW HC_P0 Observing Performance Issue at JED0881_01-JED0600 -7 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0881_01-JED0600 -7 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:00 | 09/29/2025 17:40:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001097 | PCM-20250929-00001931 | TT-20250929-02201 | MW_HC | Region_4 | RYMK0729 | RYMK0729 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:40:02 | 10/13/2025 16:09:48 | 09/30/2025 04:40:02 | Nokia MW HC_P0 Observing Performance Issue at RYMK0729_01-RYMK0754_01 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | RYMK0729_01-RYMK0754_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:02 | 09/29/2025 17:33:37 | 10/13/2025 16:09:41 |  |  | 10/13/2025 16:09:48 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001098 | PCM-20250929-00001932 | TT-20250929-02202 | MW_HC | Region_4 | BLH0044 | BLH0044 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:40:03 | 09/29/2025 17:50:51 | 09/30/2025 04:40:03 | Nokia MW HC_P2 Observing Performance Issue at BLH0044_03-LTH0330_12 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | qunfuddah | Generator_DG | TX NSA | BLH0044_03-LTH0330_12 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:03 | 09/29/2025 17:50:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001100 | PCM-20250929-00001934 | TT-20250929-02204 | MW_HC | Region_4 | TAF2418 | TAF2418 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 09/29/2025 16:40:05 | 09/30/2025 22:55:58 | 09/30/2025 04:40:05 | Nokia MW HC_P1 Observing Performance Issue at TAF2418-TAF0149_01 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF2418-TAF0149_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:05 | 09/29/2025 17:02:56 | 09/30/2025 22:55:50 |  |  | 09/30/2025 22:55:58 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001107 | PCM-20250929-00001941 | TT-20250929-02211 | MW_HC | Region_4 | JED0580 | JED0580 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 16:40:13 | 09/29/2025 17:40:59 | 09/30/2025 04:40:13 | Nokia MW HC_P2 Observing Performance Issue at JED0580-JED0540_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0580-JED0540_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:13 | 09/29/2025 17:40:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001108 | PCM-20250929-00001942 | TT-20250929-02212 | MW_HC | Region_4 | JED0476 | JED0476 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:40:13 | 09/29/2025 16:40:13 | 09/30/2025 04:40:13 | Nokia MW HC_P0 Observing Performance Issue at JED0476_02-JED0162_12 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0476_02-JED0162_12 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001111 | PCM-20250929-00001945 | TT-20250929-02215 | MW_HC | Region_4 | FRJ0043 | FRJ0043 |  |  |  | Riasat Ali Allah Baksh | 09/29/2025 16:40:17 | 10/02/2025 15:06:08 | 09/30/2025 04:40:17 | Nokia MW HC_P0 Observing Performance Issue at FRJ0043_01-LTH0330 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | qunfuddah | Generator_DG | TX NSA | FRJ0043_01-LTH0330 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:17 | 10/02/2025 15:06:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001113 | PCM-20250929-00001947 | TT-20250929-02217 | MW_HC | Region_4 | JED2119 | JED2119 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 09/29/2025 16:40:19 | 09/29/2025 17:19:26 | 09/30/2025 04:40:19 | Nokia MW HC_P2 Observing Modem Down at JED2119-JED0011-7 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2119-JED0011-7 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:19 | 09/29/2025 17:19:07 | 09/29/2025 17:19:20 | 09/29/2025 17:19:23 | 09/29/2025 17:19:26 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001114 | PCM-20250929-00001948 | TT-20250929-02218 | MW_HC | Region_4 | BLH0044 | BLH0044 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:40:20 | 09/29/2025 17:50:51 | 09/30/2025 04:40:20 | Nokia MW HC_P2 Observing Performance Issue at BLH0044_1-LTH0330_11 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | qunfuddah | Generator_DG | TX NSA | BLH0044_1-LTH0330_11 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:20 | 09/29/2025 17:50:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001115 | PCM-20250929-00001949 | TT-20250929-02219 | MW_HC | Region_4 | RAB0675 | RAB0675 |  |  |  | Khizer Hayat | 09/29/2025 16:40:22 | 09/29/2025 17:49:10 | 09/30/2025 04:40:22 | Nokia MW HC_P0 Observing Performance Issue at RAB0675_02-RAB0655_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | RAB0675_02-RAB0655_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:22 | 09/29/2025 17:49:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001117 | PCM-20250929-00001951 | TT-20250929-02221 | MW_HC | Region_4 | RAB2153 | RAB2153 |  |  |  | Khizer Hayat | 09/29/2025 16:40:24 | 09/29/2025 17:49:11 | 09/30/2025 04:40:24 | Nokia MW HC_P2 Observing Modem Down at RAB2153_01-RAB0966 _02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | RAB2153_01-RAB0966 _02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:24 | 09/29/2025 17:49:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001118 | PCM-20250929-00001952 | TT-20250929-02222 | MW_HC | Region_4 | JED2622 | JED2622 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:40:25 | 09/29/2025 16:44:28 | 09/30/2025 04:40:25 | Nokia MW HC_P0 Observing Performance Issue at JED2622-JED0181_12 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2622-JED0181_12 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:25 | 09/29/2025 16:44:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001119 | PCM-20250929-00001953 | TT-20250929-02223 | MW_HC | Region_4 | JED2129 | JED2129 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Fawzi Muneer Fawzi Mahmoud | 09/29/2025 16:40:26 | 10/06/2025 15:17:29 | 09/30/2025 04:40:26 | Nokia MW HC_P0 Observing Performance Issue at JED2129-JED0775-02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2129-JED0775-02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:26 | 10/06/2025 15:08:41 | 10/06/2025 15:17:21 | 10/06/2025 15:17:25 | 10/06/2025 15:17:29 |  |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001121 | PCM-20250929-00001955 | TT-20250929-02225 | MW_HC | Region_4 | JED2812 | JED2812 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:40:29 | 09/29/2025 16:40:29 | 09/30/2025 04:40:29 | Nokia MW HC_P0 Observing Performance Issue at JED2812-JED2010_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2812-JED2010_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001122 | PCM-20250929-00001956 | TT-20250929-02226 | MW_HC | Region_4 | JED2116 | JED2116 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:40:30 | 09/29/2025 18:12:53 | 09/30/2025 04:40:30 | Nokia MW HC_P2 Observing Performance Issue at JED2116-JED0080_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2116-JED0080_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:30 | 09/29/2025 18:12:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001124 | PCM-20250929-00001958 | TT-20250929-02228 | MW_HC | Region_4 | JED2595 | JED2595 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:40:32 | 09/29/2025 16:45:18 | 09/30/2025 04:40:32 | Nokia MW HC_P1 Observing Performance Issue at JED2595-JED2047-04 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2595-JED2047-04 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:32 | 09/29/2025 16:45:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001126 | PCM-20250929-00001960 | TT-20250929-02230 | MW_HC | Region_4 | JDJZ0771 | JDJZ0771 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:40:34 | 09/29/2025 17:50:52 | 09/30/2025 04:40:34 | Nokia MW HC_P0 Observing Performance Issue at JDJZ0771_01-HAM0357_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0771_01-HAM0357_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:34 | 09/29/2025 17:50:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001128 | PCM-20250929-00001962 | TT-20250929-02232 | MW_HC | Region_4 | JED2130 | JED2130 | Equipment | Power Cable_RRU_BTS | Replace Power Cable | Abdullah Ahmad Mohammad Abdelsheekh | 09/29/2025 16:40:36 | 10/10/2025 10:46:46 | 09/30/2025 04:40:36 | Nokia MW HC_P0 Observing Performance Issue at JED2130-JED0412 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2130-JED0412 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:36 | 10/10/2025 10:46:46 | [5 empty] | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001129 | PCM-20250929-00001963 | TT-20250929-02233 | MW_HC | Region_4 | JED0020 | JED0020 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:40:37 | 09/29/2025 16:45:19 | 09/30/2025 04:40:37 | Nokia MW HC_P0 Observing Performance Issue at JED0020 _09-JED0183_04 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0020 _09-JED0183_04 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:37 | 09/29/2025 16:45:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001131 | PCM-20250929-00001965 | TT-20250929-02235 | MW_HC | Region_4 | JZMA0825 | JZMA0825 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:40:40 | 10/22/2025 16:16:11 | 09/30/2025 04:40:40 | Nokia MW HC_P0 Observing Performance Issue at JZMA0825-JDJZ0778-3 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | qunfuddah | Sceco | TX NSA | JZMA0825-JDJZ0778-3 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:40 | 09/29/2025 17:50:53 | 10/22/2025 16:16:03 | 10/22/2025 16:16:08 | 10/22/2025 16:16:11 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001134 | PCM-20250929-00001968 | TT-20250929-02238 | MW_HC | Region_4 | JED0888 | JED0888 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 16:40:42 | 09/29/2025 17:41:00 | 09/30/2025 04:40:42 | Nokia MW HC_P2 Observing Modem Down at JED0888-3 -JED0880_01 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0888-3 -JED0880_01 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:42 | 09/29/2025 17:41:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001135 | PCM-20250929-00001969 | TT-20250929-02239 | MW_HC | Region_4 | JED0769 | JED0769 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:40:43 | 09/29/2025 16:45:19 | 09/30/2025 04:40:43 | Nokia MW HC_P2 Observing Modem Down at JED0769-JED0123_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0769-JED0123_03 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:43 | 09/29/2025 16:45:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001136 | PCM-20250929-00001970 | TT-20250929-02240 | MW_HC | Region_4 | MAS0721 | MAS0721 |  |  |  | Khizer Hayat | 09/29/2025 16:40:45 | 09/29/2025 17:49:13 | 09/30/2025 04:40:45 | Nokia MW HC_P0 Observing Performance Issue at MAS0721-MAS0653 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | MAS0721-MAS0653 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:45 | 09/29/2025 17:49:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001139 | PCM-20250929-00001973 | TT-20250929-02243 | MW_HC | Region_4 | JED2628 | JED2628 |  |  |  | Nazeer Mohammed | 09/29/2025 16:40:48 | 10/01/2025 11:45:29 | 09/30/2025 04:40:48 | Nokia MW HC_P0 Observing Performance Issue at JED2628_01-JED2025_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED2628_01-JED2025_03 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:48 | 10/01/2025 11:45:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001142 | PCM-20250929-00001976 | TT-20250929-02246 | MW_HC | Region_4 | USF0237 | USF0237 |  |  |  | Nazeer Mohammed | 09/29/2025 16:40:52 | 10/01/2025 11:45:30 | 09/30/2025 04:40:52 | Nokia MW HC_P2 Observing Modem Down at USF0237-JDUS0651 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Generator_SG | TX NSA | USF0237-JDUS0651 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:52 | 10/01/2025 11:45:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001143 | PCM-20250929-00001977 | TT-20250929-02247 | MW_HC | Region_4 | JED0676 | JED0676 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 09/29/2025 16:40:53 | 10/05/2025 15:07:35 | 09/30/2025 04:40:53 | Nokia MW HC_P1 Observing Performance Issue at JED0676_18-JED0126_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0676_18-JED0126_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:53 | 10/05/2025 14:58:04 | 10/05/2025 14:58:10 | 10/05/2025 15:07:32 | 10/05/2025 15:07:35 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001144 | PCM-20250929-00001978 | TT-20250929-02248 | MW_HC | Region_4 | JED2642 | JED2642 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 16:40:54 | 09/29/2025 17:41:01 | 09/30/2025 04:40:54 | Nokia MW HC_P2 Observing Modem Down at JED2642-JED2182 _02 FTK | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2642-JED2182 _02 FTK | FLM_TE | [8 empty] | API | 09/29/2025 16:40:54 | 09/29/2025 17:41:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001145 | PCM-20250929-00001979 | TT-20250929-02249 | MW_HC | Region_4 | JED0961 | JED0961 |  |  |  | Nazeer Mohammed | 09/29/2025 16:40:55 | 10/01/2025 11:45:31 | 09/30/2025 04:40:55 | Nokia MW HC_P2 Observing Modem Down at JED0961-JED0062_2 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0961-JED0062_2 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:55 | 10/01/2025 11:45:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001147 | PCM-20250929-00001981 | TT-20250929-02251 | MW_HC | Region_4 | JED6154 | JED6154 |  |  |  | Mohamed Farag Abdelbary | 09/29/2025 16:40:57 | 10/02/2025 12:16:50 | 09/30/2025 04:40:57 | Nokia MW HC_P2 Observing Modem Down at JED6154-JED0803_2 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED6154-JED0803_2 | FLM_TE | [8 empty] | API | 09/29/2025 16:40:57 | 10/02/2025 12:16:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001151 | PCM-20250929-00001985 | TT-20250929-02255 | MW_HC | Region_4 | JED0123 | JED0123 | Transsmission | SFP_Transmission | Replace SFP | Abdulraqib Abdo Saif Abdulaleem | 09/29/2025 16:41:02 | 10/07/2025 08:44:00 | 09/30/2025 04:41:02 | Nokia MW HC_P0 Observing Performance Issue at JED0123_01-JED0381-12 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0123_01-JED0381-12 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:02 | 10/06/2025 14:26:58 | 10/06/2025 14:27:15 | 10/06/2025 14:27:17 | 10/06/2025 14:27:20 | 10/07/2025 08:44:00 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001152 | PCM-20250929-00001986 | TT-20250929-02256 | MW_HC | Region_4 | MKJD0239 | MKJD0239 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:41:03 | 09/29/2025 18:12:53 | 09/30/2025 04:41:03 | Nokia MW HC_P2 Observing Modem Down at MKJD0239-MKJD0571_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Generator_SG | TX NSA | MKJD0239-MKJD0571_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:03 | 09/29/2025 18:12:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001155 | PCM-20250929-00001989 | TT-20250929-02259 | MW_HC | Region_4 | TAF0339 | TAF0339 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:41:06 | 09/29/2025 17:33:38 | 09/30/2025 04:41:06 | Nokia MW HC_P1 Observing Performance Issue at TAF0339-TAF0161-14 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF0339-TAF0161-14 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:06 | 09/29/2025 17:33:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001156 | PCM-20250929-00001990 | TT-20250929-02260 | MW_HC | Region_4 | TAF0281 | TAF0281 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:41:07 | 09/29/2025 17:33:38 | 09/30/2025 04:41:07 | Nokia MW HC_P1 Observing Performance Issue at TAF0281-TAF0137-4 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | taif | Sceco | TX NSA | TAF0281-TAF0137-4 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:07 | 09/29/2025 17:33:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001157 | PCM-20250929-00001991 | TT-20250929-02261 | MW_HC | Region_4 | TAF0279 | TAF0279 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:41:09 | 09/29/2025 17:33:39 | 09/30/2025 04:41:09 | Nokia MW HC_P1 Observing Performance Issue at TAF0279-TAF0134-3 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF0279-TAF0134-3 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:09 | 09/29/2025 17:33:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001158 | PCM-20250929-00001992 | TT-20250929-02262 | MW_HC | Region_4 | TAF0277 | TAF0277 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:41:10 | 09/29/2025 17:33:39 | 09/30/2025 04:41:10 | Nokia MW HC_P2 Observing Performance Issue at TAF0277-TAF0170-15 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF0277-TAF0170-15 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:10 | 09/29/2025 17:33:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001159 | PCM-20250929-00001993 | TT-20250929-02263 | MW_HC | Region_4 | TAF0270 | TAF0270 |  |  |  | Rashid Shafique | 09/29/2025 16:41:11 | 09/30/2025 14:46:06 | 09/30/2025 04:41:11 | Nokia MW HC_P1 Observing Performance Issue at TAF0270-TAF0276 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF0270-TAF0276 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:11 | 09/30/2025 14:46:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001160 | PCM-20250929-00001994 | TT-20250929-02264 | MW_HC | Region_4 | TAF0171 | TAF0171 |  |  |  | Ahmad Kamal Abdelmawla | 09/29/2025 16:41:13 | 09/29/2025 17:02:57 | 09/30/2025 04:41:13 | Nokia MW HC_P1 Observing Performance Issue at TAF0171-TAF0154-NE5 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF0171-TAF0154-NE5 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:13 | 09/29/2025 17:02:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001161 | PCM-20250929-00001995 | TT-20250929-02265 | MW_HC | Region_4 | TAF0170 | TAF0170 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 09/29/2025 16:41:14 | 10/05/2025 17:24:15 | 09/30/2025 04:41:14 | Nokia MW HC_P1 Observing Performance Issue at TAF0170 _20-TAF0174_2 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | taif | Sceco_STB | TX NSA | TAF0170 _20-TAF0174_2 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:14 | 09/29/2025 17:02:57 | 10/03/2025 21:29:34 |  |  | 10/05/2025 17:24:15 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001163 | PCM-20250929-00001997 | TT-20250929-02267 | MW_HC | Region_4 | TAF0156 | TAF0156 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:41:16 | 09/29/2025 17:33:41 | 09/30/2025 04:41:16 | Nokia MW HC_P0 Observing Performance Issue at TAF0156-TAF0154 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | taif | Sceco | TX NSA | TAF0156-TAF0154 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:16 | 09/29/2025 17:33:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001164 | PCM-20250929-00001998 | TT-20250929-02268 | MW_HC | Region_4 | TAF0139 | TAF0139 | Transsmission | MW_HW_stuck | Reset IDU | Ahmad Kamal Abdelmawla | 09/29/2025 16:41:17 | 09/30/2025 22:55:44 | 09/30/2025 04:41:17 | Nokia MW HC_P1 Observing Performance Issue at TAF0139-TAF0280-6 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | TAF0139-TAF0280-6 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:17 | 09/29/2025 17:02:58 | 09/30/2025 22:55:36 |  |  | 09/30/2025 22:55:44 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001192 | PCM-20250929-00002026 | TT-20250929-02296 | MW_HC | Region_4 | KAC0453 | KAC0453 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Khizer Hayat | 09/29/2025 16:41:46 | 09/30/2025 18:17:40 | 09/30/2025 04:41:46 | Nokia MW HC_P0 Observing Performance Issue at KAC0453-KAC0461_02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Generator_SG | TX NSA | KAC0453-KAC0461_02 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:46 | 09/29/2025 17:49:14 | 09/30/2025 17:43:37 | 09/30/2025 17:43:39 | 09/30/2025 17:43:42 | 09/30/2025 18:17:40 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001196 | PCM-20250929-00002030 | TT-20250929-02300 | MW_HC | Region_4 | JED2057 | JED2057 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:41:50 | 09/29/2025 16:44:30 | 09/30/2025 04:41:50 | Nokia MW HC_P2 Observing Performance Issue at JED2057-JED0868-3 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2057-JED0868-3 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:50 | 09/29/2025 16:44:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001197 | PCM-20250929-00002031 | TT-20250929-02301 | MW_HC | Region_4 | JED2015 | JED2015 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:41:52 | 09/29/2025 16:45:21 | 09/30/2025 04:41:52 | Nokia MW HC_P1 Observing Performance Issue at JED2015 FTK-JED0381-7 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED2015 FTK-JED0381-7 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:52 | 09/29/2025 16:45:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001198 | PCM-20250929-00002032 | TT-20250929-02302 | MW_HC | Region_4 | JED2007 | JED2007 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 09/29/2025 16:41:53 | 10/16/2025 14:07:45 | 09/30/2025 04:41:53 | Nokia MW HC_P2 Observing Modem Down at JED2007_01-JED0485 _02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED2007_01-JED0485 _02 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:53 | 10/16/2025 13:52:07 | 10/16/2025 14:07:27 | 10/16/2025 14:07:33 | 10/16/2025 14:07:45 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001199 | PCM-20250929-00002033 | TT-20250929-02303 | MW_HC | Region_4 | JED0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 16:41:54 | 09/29/2025 17:41:03 | 09/30/2025 04:41:54 | Nokia MW HC_P2 Observing Modem Down at JED0901-JED0676-16 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0901-JED0676-16 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:54 | 09/29/2025 17:41:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001201 | PCM-20250929-00002035 | TT-20250929-02305 | MW_HC | Region_4 | JED0807 | JED0807 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:41:55 | 09/29/2025 16:41:55 | 09/30/2025 04:41:55 | Nokia MW HC_P1 Observing Performance Issue at JED0807-JED0639 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0807-JED0639 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001200 | PCM-20250929-00002034 | TT-20250929-02304 | MW_HC | Region_4 | JED0891 | JED0891 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 09/29/2025 16:41:55 | 09/30/2025 10:58:00 | 09/30/2025 04:41:55 | Nokia MW HC_P2 Observing Modem Down at JED0891 -JED0487 _02 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0891 -JED0487 _02 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:55 | 09/30/2025 10:47:45 | 09/30/2025 10:57:38 | 09/30/2025 10:57:42 | 09/30/2025 10:58:00 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20250929001202 | PCM-20250929-00002036 | TT-20250929-02306 | MW_HC | Region_4 | JED0805 | JED0805 |  |  |  | Ahmed Adel Abdelaziz elkholy | 09/29/2025 16:41:57 | 09/29/2025 16:41:57 | 09/30/2025 04:41:57 | Nokia MW HC_P1 Observing Performance Issue at JED0805-JED0365-11 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0805-JED0365-11 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001203 | PCM-20250929-00002037 | TT-20250929-02307 | MW_HC | Region_4 | JED0800 | JED0800 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 09/29/2025 16:41:58 | 10/22/2025 19:04:11 | 09/30/2025 04:41:58 | Nokia MW HC_P2 Observing Performance Issue at JED0800-JED0184-13 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED0800-JED0184-13 | FLM_TE | [8 empty] | API | 09/29/2025 16:41:58 | 10/22/2025 18:36:45 | 10/22/2025 19:04:03 | 10/22/2025 19:04:05 | 10/22/2025 19:04:11 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001206 | PCM-20250929-00002040 | TT-20250929-02310 | MW_HC | Region_4 | JED0676 | JED0676 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 16:42:01 | 09/29/2025 17:41:04 | 09/30/2025 04:42:01 | Nokia MW HC_P0 Observing Performance Issue at JED0676_17-JED0536 _ 01 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0676_17-JED0536 _ 01 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:01 | 09/29/2025 17:41:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001207 | PCM-20250929-00002041 | TT-20250929-02311 | MW_HC | Region_4 | JED0547 | JED0547 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:42:03 | 09/29/2025 16:44:31 | 09/30/2025 04:42:03 | Nokia MW HC_P0 Observing Performance Issue at JED0547-JED0095-7 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0547-JED0095-7 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:03 | 09/29/2025 16:44:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001208 | PCM-20250929-00002043 | TT-20250929-02312 | MW_HC | Region_4 | JED0514 | JED0514 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 09/29/2025 16:42:04 | 10/16/2025 20:17:48 | 09/30/2025 04:42:04 | Nokia MW HC_P2 Observing Modem Down at JED0514-JED0276-NE9 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0514-JED0276-NE9 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:04 | 10/16/2025 18:42:47 | 10/16/2025 20:15:57 | 10/16/2025 20:17:24 | 10/16/2025 20:17:48 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001209 | PCM-20250929-00002044 | TT-20250929-02313 | MW_HC | Region_4 | JED0408 | JED0408 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:42:05 | 09/29/2025 16:44:32 | 09/30/2025 04:42:05 | Nokia MW HC_P1 Observing Performance Issue at JED0408_15-JED0150_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0408_15-JED0150_03 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:05 | 09/29/2025 16:44:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001210 | PCM-20250929-00002045 | TT-20250929-02314 | MW_HC | Region_4 | JED0336 | JED0336 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Abd Elrahman Suliman Mohmed Suliman | 09/29/2025 16:42:06 | 10/01/2025 13:17:54 | 09/30/2025 04:42:06 | Nokia MW HC_P0 Observing Performance Issue at JED0336 _01-JED0330-9 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0336 _01-JED0330-9 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:06 | 09/29/2025 16:56:17 | 09/29/2025 17:15:02 | 09/29/2025 17:15:12 | 09/29/2025 17:15:16 | 10/01/2025 13:17:54 |  | Abd Elrahman Suliman Mohmed Suliman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001211 | PCM-20250929-00002046 | TT-20250929-02315 | MW_HC | Region_4 | JED0333 | JED0333 |  |  |  | Mohammed Ramadan A Abu Abid | 09/29/2025 16:42:07 | 09/29/2025 17:02:40 | 09/30/2025 04:42:07 | Nokia MW HC_P2 Observing Performance Issue at JED0333-JED0285-9 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0333-JED0285-9 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:07 | 09/29/2025 17:02:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001212 | PCM-20250929-00002047 | TT-20250929-02316 | MW_HC | Region_4 | JED0332 | JED0332 | Transsmission | SFP_Transmission | Replace SFP | Abdulraqib Abdo Saif Abdulaleem | 09/29/2025 16:42:08 | 10/01/2025 12:09:18 | 09/30/2025 04:42:08 | Nokia MW HC_P2 Observing Modem Down at JED0332-12-JED0065-11 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0332-12-JED0065-11 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:08 | 10/01/2025 10:23:31 | 10/01/2025 10:24:48 | 10/01/2025 10:25:09 | 10/01/2025 10:25:30 | 10/01/2025 12:09:18 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001213 | PCM-20250929-00002048 | TT-20250929-02317 | MW_HC | Region_4 | JED0326 | JED0326 | Transsmission | MW_Connectors | Remade Indoor MW Connector | BARKAT ALI MAIN HILAL | 09/29/2025 16:42:10 | 10/04/2025 19:40:47 | 09/30/2025 04:42:10 | Nokia MW HC_P0 Observing Performance Issue at JED0326-JED0168 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0326-JED0168 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:10 | 10/03/2025 16:43:04 | 10/03/2025 16:43:14 | 10/03/2025 17:04:01 | 10/03/2025 17:28:34 | 10/04/2025 19:40:47 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001214 | PCM-20250929-00002049 | TT-20250929-02318 | MW_HC | Region_4 | JED0321 | JED0321 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:42:11 | 09/29/2025 16:45:21 | 09/30/2025 04:42:11 | Nokia MW HC_P1 Observing Performance Issue at JED0321-JED0038-11 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0321-JED0038-11 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:11 | 09/29/2025 16:45:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001215 | PCM-20250929-00002051 | TT-20250929-02319 | MW_HC | Region_4 | JED0275 | JED0275 |  |  |  | Mohammed Ramadan A Abu Abid | 09/29/2025 16:42:12 | 09/29/2025 17:02:41 | 09/30/2025 04:42:12 | Nokia MW HC_P2 Observing Modem Down at JED0275-JED0031_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0275-JED0031_03 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:12 | 09/29/2025 17:02:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001217 | PCM-20250929-00002053 | TT-20250929-02321 | MW_HC | Region_4 | JED0121 | JED0121 | Transsmission | DWDM_HW | Alarm Cleared | Fawzi Muneer Fawzi Mahmoud | 09/29/2025 16:42:13 | 10/06/2025 13:10:19 | 09/30/2025 04:42:13 | Nokia MW HC_P2 Observing Performance Issue at JED0121-JD3_31 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0121-JD3_31 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:13 | 10/06/2025 11:45:30 | 10/06/2025 11:57:26 | 10/06/2025 11:57:28 | 10/06/2025 11:57:31 | 10/06/2025 13:10:19 |  | Fawzi Muneer Fawzi Mahmoud |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001218 | PCM-20250929-00002054 | TT-20250929-02322 | MW_HC | Region_4 | JED0066 | JED0066 |  |  |  | Mohammed Ramadan A Abu Abid | 09/29/2025 16:42:15 | 10/13/2025 11:50:28 | 09/30/2025 04:42:15 | Nokia MW HC_P2 Observing Modem Down at JED0066-JED0148-7 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0066-JED0148-7 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:15 | 10/13/2025 11:23:01 | 10/13/2025 11:23:43 | 10/13/2025 11:23:49 | 10/13/2025 11:50:28 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001220 | PCM-20250929-00002055 | TT-20250929-02323 | MW_HC | Region_4 | HAW0333 | HAW0333 |  |  |  | Rashid Shafique | 09/29/2025 16:42:16 | 09/30/2025 14:46:07 | 09/30/2025 04:42:16 | Nokia MW HC_P2 Observing Performance Issue at HAW0333_14-HAW0298 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | taif | Sceco | TX NSA | HAW0333_14-HAW0298 | FLM_TE | [8 empty] | API | 09/29/2025 16:42:16 | 09/30/2025 14:46:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001224 | PCM-20250929-00002059 | TT-20250929-02327 | MW_HC | Region_4 | UKHA0028 | UKHA0028 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:42:21 | 10/16/2025 11:17:37 | 09/30/2025 04:42:21 | NEC MW HC_P2 Observing Modem Down at UKHA0028(10.154.113.59)--UKHA0645(10.154.113.50) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | adam | Generator_SG | TX NSA | UKHA0028(10.154.113.59)--UKHA0645(10.154.113.50) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:21 | 09/29/2025 17:50:53 | 10/16/2025 11:16:50 |  |  | 10/16/2025 11:17:37 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001225 | PCM-20250929-00002060 | TT-20250929-02328 | MW_HC | Region_4 | UKHA0028 | UKHA0028 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:42:21 | 10/16/2025 11:18:19 | 09/30/2025 04:42:21 | NEC MW HC_P2 Observing Modem Down at UKHA0028(10.154.113.38)--UKHA0645(10.154.113.40) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | adam | Generator_SG | TX NSA | UKHA0028(10.154.113.38)--UKHA0645(10.154.113.40) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:21 | 09/29/2025 17:50:54 | 10/16/2025 11:17:47 |  |  | 10/16/2025 11:18:19 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001226 | PCM-20250929-00002061 | TT-20250929-02329 | MW_HC | Region_4 | TFBH9446 | TFBH9446 |  |  |  | Ahmad Kamal Abdelmawla | 09/29/2025 16:42:22 | 09/29/2025 17:02:58 | 09/30/2025 04:42:22 | NEC MW HC_P0 Observing RSL Issue at TFBH9446(10.88.221.35)--UKZ0179(10.88.221.36) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9446(10.88.221.35)--UKZ0179(10.88.221.36) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:22 | 09/29/2025 17:02:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001228 | PCM-20250929-00002063 | TT-20250929-02331 | MW_HC | Region_4 | SHF2364 | SHF2364 |  |  |  | Rashid Shafique | 09/29/2025 16:42:25 | 09/30/2025 14:46:10 | 09/30/2025 04:42:25 | NEC MW HC_P0 Observing Performance Issue at SHF2364(10.154.150.51)--TFSH9069(10.154.150.50) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | taif | Sceco | TX NSA | SHF2364(10.154.150.51)--TFSH9069(10.154.150.50) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:25 | 09/30/2025 14:46:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001229 | PCM-20250929-00002064 | TT-20250929-02332 | MW_HC | Region_4 | RYMK0543 | RYMK0543 |  |  |  | Rashid Shafique | 09/29/2025 16:42:26 | 09/30/2025 14:46:12 | 09/30/2025 04:42:26 | NEC MW HC_P0 Observing Modem Down at RYMK0543(10.1.164.237)--SAQF0003(10.1.164.238) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | taif | Sceco | TX NSA | RYMK0543(10.1.164.237)--SAQF0003(10.1.164.238) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:26 | 09/30/2025 14:46:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001231 | PCM-20250929-00002066 | TT-20250929-02334 | MW_HC | Region_4 | MKMD0562 | MKMD0562 |  |  |  | Khizer Hayat | 09/29/2025 16:42:28 | 09/29/2025 17:49:15 | 09/30/2025 04:42:28 | NEC MW HC_P0 Observing Performance Issue at MKMD0562(10.154.113.119)--MKMD9011(10.154.113.118) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0562(10.154.113.119)--MKMD9011(10.154.113.118) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:28 | 09/29/2025 17:49:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001233 | PCM-20250929-00002068 | TT-20250929-02336 | MW_HC | Region_4 | KMMD0736 | KMMD0736 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 09/29/2025 16:42:30 | 10/07/2025 16:14:56 | 09/30/2025 04:42:30 | NEC MW HC_P0 Observing Modem Down at KMMD0736(10.154.115.114)--KMMD9075(10.154.115.115) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | KMMD0736(10.154.115.114)--KMMD9075(10.154.115.115) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:30 | 10/07/2025 16:14:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001234 | PCM-20250929-00002069 | TT-20250929-02337 | MW_HC | Region_4 | KMMD0723 | KMMD0723 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Nazeer Mohammed | 09/29/2025 16:42:32 | 10/09/2025 12:54:04 | 09/30/2025 04:42:32 | NEC MW HC_P0 Observing Modem Down at KMMD0723(10.154.115.86)--KMMD9076(10.154.115.85) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | KMMD0723(10.154.115.86)--KMMD9076(10.154.115.85) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:32 | 10/01/2025 11:45:32 | 10/09/2025 12:11:27 | 10/09/2025 12:11:29 | 10/09/2025 12:11:32 | 10/09/2025 12:54:04 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001235 | PCM-20250929-00002070 | TT-20250929-02338 | MW_HC | Region_4 | KMMD0637 | KMMD0637 |  |  |  | Nazeer Mohammed | 09/29/2025 16:42:32 | 10/16/2025 11:50:30 | 09/30/2025 04:42:32 | NEC MW HC_P0 Observing Modem Down at KMMD0637(10.154.115.89)--KMMD0761(10.154.115.90) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | KMMD0637(10.154.115.89)--KMMD0761(10.154.115.90) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:32 | 10/16/2025 11:50:01 | 10/16/2025 11:50:24 | 10/16/2025 11:50:27 | 10/16/2025 11:50:30 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001236 | PCM-20250929-00002071 | TT-20250929-02339 | MW_HC | Region_4 | JED0885 | JED0885 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:42:34 | 09/29/2025 18:12:55 | 09/30/2025 04:42:34 | NEC MW HC_P0 Observing Performance Issue at JED0885(10.1.169.177)--JED0890(10.1.169.178) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0885(10.1.169.177)--JED0890(10.1.169.178) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:34 | 09/29/2025 18:12:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001237 | PCM-20250929-00002072 | TT-20250929-02340 | MW_HC | Region_4 | JED6132 | JED6132 |  |  |  | Mohamed Farag Abdelbary | 09/29/2025 16:42:35 | 10/02/2025 12:16:51 | 09/30/2025 04:42:35 | NEC MW HC_P0 Observing Modem Down at JED6132(10.154.126.23)--THO0369(10.154.126.22) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED6132(10.154.126.23)--THO0369(10.154.126.22) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:35 | 10/02/2025 12:16:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001238 | PCM-20250929-00002073 | TT-20250929-02341 | MW_HC | Region_4 | JED0568 | JED0568 |  |  |  | Nazeer Mohammed | 09/29/2025 16:42:36 | 10/01/2025 11:45:33 | 09/30/2025 04:42:36 | NEC MW HC_P0 VIP Observing Performance Issue at JED0568(10.154.126.85)--JED0839(10.154.126.86) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED0568(10.154.126.85)--JED0839(10.154.126.86) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:36 | 10/01/2025 11:45:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001239 | PCM-20250929-00002074 | TT-20250929-02342 | MW_HC | Region_4 | JED0416 | JED0416 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 16:42:36 | 09/29/2025 16:45:22 | 09/30/2025 04:42:36 | NEC MW HC_P0 Observing Performance Issue at JED0416(10.1.174.97)--JED6072(10.1.174.98) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED0416(10.1.174.97)--JED6072(10.1.174.98) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:36 | 09/29/2025 16:45:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20250929001240 | PCM-20250929-00002075 | TT-20250929-02343 | MW_HC | Region_4 | JDMD0861 | JDMD0861 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 09/29/2025 16:42:38 | 10/04/2025 12:24:55 | 09/30/2025 04:42:38 | NEC MW HC_P0 Observing Modem Down at JDMD0861(10.154.115.2)--MKMD0555(10.154.115.18) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Generator_DG | TX NSA | JDMD0861(10.154.115.2)--MKMD0555(10.154.115.18) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:38 | 10/04/2025 12:24:25 | 10/04/2025 12:24:35 | 10/04/2025 12:24:41 | 10/04/2025 12:24:55 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001241 | PCM-20250929-00002076 | TT-20250929-02344 | MW_HC | Region_4 | JED0155 | JED0155 | Transsmission | MW_Connectors | Replace Indoor MW Connector | BARKAT ALI MAIN HILAL | 09/29/2025 16:42:39 | 10/03/2025 14:56:29 | 09/30/2025 04:42:39 | NEC MW HC_P2 Observing Modem Down at JED0155(10.1.165.84)--JED6116(10.1.165.85) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0155(10.1.165.84)--JED6116(10.1.165.85) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:39 |  | 10/03/2025 11:37:10 | 10/03/2025 11:37:19 | 10/03/2025 12:23:56 | 10/03/2025 14:56:29 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001242 | PCM-20250929-00002077 | TT-20250929-02345 | MW_HC | Region_4 | JED0129 | JED0129 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/29/2025 16:42:41 | 09/29/2025 16:44:34 | 09/30/2025 04:42:41 | NEC MW HC_P0 VIP Observing RSL Issue at JED0129(10.99.254.9)--JED6039(10.99.254.11) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0129(10.99.254.9)--JED6039(10.99.254.11) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:41 | 09/29/2025 16:44:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001243 | PCM-20250929-00002078 | TT-20250929-02346 | MW_HC | Region_4 | JED0079 | JED0079 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 09/29/2025 16:42:42 | 09/29/2025 18:12:56 | 09/30/2025 04:42:42 | NEC MW HC_P0 Observing Performance Issue at JED0079(10.1.166.225)--JED6113(10.1.166.226) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0079(10.1.166.225)--JED6113(10.1.166.226) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:42 | 09/29/2025 18:12:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001244 | PCM-20250929-00002079 | TT-20250929-02347 | MW_HC | Region_4 | JDJZ0776 | JDJZ0776 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:42:42 | 10/07/2025 20:30:48 | 09/30/2025 04:42:42 | NEC MW HC_P2 Observing Modem Down at JDJZ0776(10.157.105.228)--JDJZ9048(10.157.105.227) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0776(10.157.105.228)--JDJZ9048(10.157.105.227) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:42 | 09/29/2025 17:50:55 | 10/07/2025 20:30:19 |  |  | 10/07/2025 20:30:48 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001245 | PCM-20250929-00002081 | TT-20250929-02349 | MW_HC | Region_4 | JDJZ0773 | JDJZ0773 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:42:43 | 09/29/2025 17:50:55 | 09/30/2025 04:42:43 | NEC MW HC_P0 VIP Observing Performance Issue at JDJZ0773(10.154.113.22)--JDJZ0774(10.154.113.18) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0773(10.154.113.22)--JDJZ0774(10.154.113.18) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:43 | 09/29/2025 17:50:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001247 | PCM-20250929-00002082 | TT-20250929-02350 | MW_HC | Region_4 | JDJZ0771 | JDJZ0771 |  |  |  | Mudassar Bashir Bashir Ahmad | 09/29/2025 16:42:45 | 09/29/2025 17:50:56 | 09/30/2025 04:42:45 | NEC MW HC_P0 Observing Performance Issue at JDJZ0771(10.154.113.10)--JDJZ0772(10.154.113.12) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0771(10.154.113.10)--JDJZ0772(10.154.113.12) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:45 | 09/29/2025 17:50:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001248 | PCM-20250929-00002083 | TT-20250929-02351 | MW_HC | Region_4 | JDJZ0762 | JDJZ0762 |  |  |  | Riasat Ali Allah Baksh | 09/29/2025 16:42:45 | 10/02/2025 15:06:09 | 09/30/2025 04:42:45 | NEC MW HC_P0 Observing Performance Issue at JDJZ0762(10.154.140.66)--JDJZ0763(10.154.140.67) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JDJZ0762(10.154.140.66)--JDJZ0763(10.154.140.67) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:45 | 10/02/2025 15:06:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001249 | PCM-20250929-00002084 | TT-20250929-02352 | MW_HC | Region_4 | HHR0444 | HHR0444 |  |  |  | Mohammed Ramadan A Abu Abid | 09/29/2025 16:42:47 | 09/29/2025 17:02:43 | 09/30/2025 04:42:47 | NEC MW HC_P0 VIP Observing Performance Issue at HHR0444(10.154.96.182)--JED0745(10.154.96.178) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | jeddah | Generator_SG | TX NSA | HHR0444(10.154.96.182)--JED0745(10.154.96.178) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:47 | 09/29/2025 17:02:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001251 | PCM-20250929-00002086 | TT-20250929-02354 | MW_HC | Region_4 | FAT0348 | FAT0348 |  |  |  | Ahmad Kamal Abdelmawla | 09/29/2025 16:42:49 | 09/29/2025 17:02:59 | 09/30/2025 04:42:49 | NEC MW HC_P0 Observing Modem Down at FAT0348(10.1.175.181)--TFBH0798(10.1.175.180) | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | taif | Generator_DG | TX NSA | FAT0348(10.1.175.181)--TFBH0798(10.1.175.180) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:49 | 09/29/2025 17:02:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001253 | PCM-20250929-00002088 | TT-20250929-02356 | MW_HC | Region_4 | TFBH9446 | TFBH9446 |  |  |  | Ahmad Kamal Abdelmawla | 09/29/2025 16:42:51 | 09/29/2025 17:03:00 | 09/30/2025 04:42:51 | NEC MW HC_P0 Observing RSL Issue at TFBH9446(10.88.221.35)--UKZ0179(10.88.221.36) | 09/29/2025 16:35:36 | Minor |  | LOF | 09/29/2025 16:35:36 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9446(10.88.221.35)--UKZ0179(10.88.221.36) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:51 | 09/29/2025 17:03:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001260 | PCM-20250929-00002095 | TT-20250929-02363 | MW_HC | Region_6 | MHL0136 | MHL0136 |  |  |  | Muhammad Jamal Khan Abbas Ali | 09/29/2025 16:42:58 | 09/29/2025 17:16:50 | 09/30/2025 04:42:58 | NEC MW HC_P0 Observing Modem Down at MHL0136(10.157.250.22)--MHL9722(10.157.250.23) | 09/29/2025 16:35:36 | Minor |  | LOF | 09/29/2025 16:35:36 | P3 | 2G | mohail | Sceco | TX NSA | MHL0136(10.157.250.22)--MHL9722(10.157.250.23) | FLM_TE | [8 empty] | API | 09/29/2025 16:42:58 | 09/29/2025 17:16:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001270 | PCM-20250929-00002105 | TT-20250929-02373 | MW_HC | Region_6 | JDS0797 | JDS0797 |  |  |  | Osama Hadi | 09/29/2025 16:43:11 | 09/29/2025 18:13:03 | 09/30/2025 04:43:11 | NEC MW HC_P0 Observing Modem Down at JDS0797(10.1.170.185)--JDS0798(10.1.170.183) | 09/29/2025 16:35:36 | Minor |  | LOF | 09/29/2025 16:35:36 | P2 | 2G | jizan | Sceco | TX NSA | JDS0797(10.1.170.185)--JDS0798(10.1.170.183) | FLM_TE | [8 empty] | API | 09/29/2025 16:43:11 | 09/29/2025 18:13:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001271 | PCM-20250929-00002106 | TT-20250929-02374 | MW_HC | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 09/29/2025 16:43:12 | 09/29/2025 17:36:30 | 09/30/2025 04:43:12 | NEC MW HC_P0 Observing Performance Issue at JDJZ0785(10.154.170.172)--SHQ0037(10.154.170.171) | 09/29/2025 16:35:36 | Minor |  | LOF | 09/29/2025 16:35:36 | P1 | 2G | derb | Sceco_STB | TX NSA | JDJZ0785(10.154.170.172)--SHQ0037(10.154.170.171) | FLM_TE | [8 empty] | API | 09/29/2025 16:43:12 | 09/29/2025 17:36:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001289 | PCM-20250929-00002125 | TT-20250929-02393 | MW_HC | Region_1 | DMH0106 | DMH0106 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/29/2025 16:43:33 | 10/07/2025 13:40:07 | 09/30/2025 04:43:33 | NEC MW HC_P0 Observing Performance Issue at DMH0106(10.159.105.164)--DMH0107(10.159.105.165) | 09/29/2025 16:35:36 | Minor |  | LOF | 09/29/2025 16:35:36 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0106(10.159.105.164)--DMH0107(10.159.105.165) | FLM_TE | [8 empty] | API | 09/29/2025 16:43:33 | 09/29/2025 17:28:58 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001306 | PCM-20250929-00002142 | TT-20250929-02409 | Reference_telecom | Region_6 | FUR0050 | FUR0050 |  |  |  | Mohammed Sideag Mohammed Ali | 09/29/2025 16:43:51 | 09/29/2025 17:18:47 | 09/30/2025 04:43:51 | NEC MW Observing LOF,ODU CPU / Cable Open at FUR0050-3(10.1.172.199) | 09/24/2025 14:02:33 | Minor |  | LOF | 09/24/2025 14:02:33 | P3 | 2G | jizan | Sceco_STB | TX NSA | FUR0050-3(10.1.172.199) | FLM_TE | [8 empty] | API | 09/29/2025 16:43:51 | 09/29/2025 17:18:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001307 | PCM-20250929-00002143 | TT-20250929-02410 | Reference_telecom | Region_1 | HFF0944 | HFF0944 |  |  |  | Mohamed Magdy Fouad Zayed | 09/29/2025 16:43:52 | 10/06/2025 16:48:49 | 09/30/2025 04:43:52 | NEC MW Observing Radio Traffic Aggregation Link at HFF0944-2_1(10.158.149.129) | 04/16/2025 00:59:32 | Minor |  | LOF | 04/16/2025 00:59:32 | P1 | SRAN | hafouf | Sceco | TX NSA | HFF0944-2_1(10.158.149.129) | FLM_TE | [8 empty] | API | 09/29/2025 16:43:52 | 09/29/2025 17:40:25 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001323 | PCM-20250929-00002159 | TT-20250929-02426 | Reference_telecom | Region_4 | JED6095 | JED6095 |  |  |  | Mohamed Farag Abdelbary | 09/29/2025 16:44:07 | 10/07/2025 13:40:08 | 09/30/2025 04:44:07 | NEC MW Observing LOF,Frame ID,RX Level at JED6095(10.99.254.66) | 09/18/2025 05:57:00 | Minor |  | LOF | 09/18/2025 05:57:00 | VIP | 2G | jeddah | Sceco | TX NSA | JED6095(10.99.254.66) | FLM_TE | [8 empty] | API | 09/29/2025 16:44:07 | 10/02/2025 12:16:51 | [6 empty] | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001364 | PCM-20250929-00002201 | TT-20250929-02468 | MW_HC | Region_4 | RYMK0535 | RYMK0535 | Transsmission | MW_Connectors | Remade Indoor MW Connector | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 16:44:51 | 10/19/2025 08:44:34 | 09/30/2025 04:44:51 | As per bo request Nokia MW HC Link RYMK0535-RYMK0671 Early Warring alarm continuous without Errors | 09/29/2025 16:44:39 | Minor | 113388 | LOF | 09/29/2025 16:44:37 | P1 | 2G | taif | Generator_DG | TX NSA | RYMK0535-RYMK0671 | FLM_TE | [5 empty] | As per bo request Nokia MW HC Link RYMK0535-RYMK0671 Early Warring alarm continuous without Errors |  |  | API | 09/29/2025 16:44:51 | 09/29/2025 17:33:43 | 10/19/2025 08:44:27 |  |  | 10/19/2025 08:44:34 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001404 | PCM-20250929-00002251 | TT-20250929-02530 | MW_HC | Region_4 | RYMK0549 | RYMK0549 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 09/29/2025 17:05:21 | 09/29/2025 17:33:43 | 09/30/2025 05:05:21 | As per bo request Nokia MW HC FLM to check RYMK0549-RYMK0539 counting error please create TT | 09/29/2025 17:05:16 | Minor | 113388 | LOF | 09/29/2025 17:05:14 | P1 | 2G | taif | Generator_SG | TX NSA | RYMK0549-RYMK0539 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM to check RYMK0549-RYMK0539 counting error please create TT |  |  | API | 09/29/2025 17:05:21 | 09/29/2025 17:33:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001509 | PCM-20250929-00002429 | TT-20250929-02736 | MW_HC | Region_4 | JED6113 | JED6113 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohamed Farag Abdelbary | 09/29/2025 18:45:14 | 10/14/2025 20:54:32 | 09/30/2025 06:45:14 | As per bo request Nokia MW HC FLM need to check link JED6113-JED0079 | 09/29/2025 18:45:09 | Minor | 113388 | LOF | 09/29/2025 18:45:07 | P3 | 2G | jeddah | Sceco | TX NSA | JED6113-JED0079 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check link JED6113-JED0079 |  |  | API | 09/29/2025 18:45:14 | 10/14/2025 20:54:32 | [5 empty] | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001511 | PCM-20250929-00002431 | TT-20250929-02739 | MW_HC | Region_4 | JED0582 | JED0582 |  |  |  | MALIK ATIF ZAMAN | 09/29/2025 18:46:11 | 09/29/2025 18:53:43 | 09/30/2025 06:46:11 | As per bo request Nokia MW HC FLM need to check link JED0582-JED0221 counting PM errors and Modem 1 down | 09/29/2025 18:45:44 | Minor | 113388 | LOF | 09/29/2025 18:45:42 | VIP | 2G | jeddah | Sceco | TX NSA | ED0582-JED0221 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check link JED0582-JED0221 counting PM errors and Modem 1 down |  |  | API | 09/29/2025 18:46:11 | 09/29/2025 18:53:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001514 | PCM-20250929-00002435 | TT-20250929-02741 | MW_HC | Region_4 | JED1M8045 | JED2045 | Equipment | BTS_Cable | Replace Fiber Cable | BARKAT ALI MAIN HILAL | 09/29/2025 18:46:57 | 09/30/2025 15:22:35 | 09/30/2025 06:46:57 | FLM need to check with access BO locally as TX path clear | 09/29/2025 18:46:52 | Minor | 113388 | LOF | 09/29/2025 18:46:50 | P3 | 4G | jeddah | Sceco | TX NSA | JED1M8045 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check with access BO locally as TX path clear |  |  | API | 09/29/2025 18:46:57 | 09/30/2025 12:34:56 | 09/30/2025 12:36:12 | 09/30/2025 12:36:20 | 09/30/2025 13:08:25 | 09/30/2025 15:22:35 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001516 | PCM-20250929-00002437 | TT-20250929-02743 | MW_HC | Region_4 | JED0069 | JED0069 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 18:48:03 | 09/30/2025 12:34:58 | 09/30/2025 06:48:03 | As per bo request Nokia MW HC FLM need to check link JED0069-JED0125 as ACM degraded on H | 09/29/2025 18:47:53 | Minor | 113388 | LOF | 09/29/2025 18:47:51 | P3 | 2G | jeddah | Sceco | TX NSA | JED0069-JED012 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check link JED0069-JED0125 as ACM degraded on H |  |  | API | 09/29/2025 18:48:03 | 09/30/2025 12:34:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250929001527 | PCM-20250929-00002451 | TT-20250929-02756 | MW_HC | Region_4 | JED2175 | JED2175 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Abd Elrahman Suliman Mohmed Suliman | 09/29/2025 18:55:32 | 10/08/2025 13:13:26 | 09/30/2025 06:55:32 | As per bo request Nokia MW HC FLM need to check link JED2175-JED2075 as H part down | 09/29/2025 18:55:27 | Minor | 113388 | LOF | 09/29/2025 18:55:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2175-JED2075 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check link JED2175-JED2075 as H part down |  |  | API | 09/29/2025 18:55:32 | 10/01/2025 18:02:12 | 10/01/2025 18:02:37 | 10/01/2025 18:02:45 | 10/01/2025 18:02:47 | 10/08/2025 13:13:26 |  | Abd Elrahman Suliman Mohmed Suliman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001528 | PCM-20250929-00002452 | TT-20250929-02758 | MW_HC | Region_4 | JED0769 | JED0769 |  |  |  | BARKAT ALI MAIN HILAL | 09/29/2025 18:57:31 | 09/30/2025 12:34:59 | 09/30/2025 06:57:31 | As per bo request Nokia MW HC FLM need to check link JED0769-JED0123 | 09/29/2025 18:57:20 | Minor | 113388 | LOF | 09/29/2025 18:57:18 | VIP | 2G | jeddah | Sceco | TX NSA | JED0769-JED0123 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check link JED0769-JED0123 |  |  | API | 09/29/2025 18:57:31 | 09/30/2025 12:34:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001531 | PCM-20250929-00002456 | TT-20250929-02761 | MW_HC | Region_4 | JED2684 | JED2684 |  |  |  | Nazeer Mohammed | 09/29/2025 18:59:29 | 10/01/2025 11:45:36 | 09/30/2025 06:59:29 | As per bo request Nokia MW HC FLM need to check link JED2684-JED0540 as H flapping with low RSL | 09/29/2025 18:59:16 | Minor | 113388 | LOF | 09/29/2025 18:59:14 | P3 | 2G | jeddah | Sceco | TX NSA | JED2684-JED0540 | FLM_TE | [5 empty] | As per bo request Nokia MW HC FLM need to check link JED2684-JED0540 as H flapping with low RSL |  |  | API | 09/29/2025 18:59:29 | 10/01/2025 11:45:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250929001614 | PCM-20250929-00002578 | TT-20250929-02905 | Reference_telecom | Region_2 | RIYA2U6174b | RIYA6074 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 09/29/2025 20:44:42 | 09/30/2025 09:20:23 | 09/30/2025 02:44:42 | 1(2G) Site down at RIYA2U6174B-P3 (Ref:TT-20250929-02715) | 09/29/2025 18:30:33 | Major | 21807 | OML Fault | 09/29/2025 20:30:33 | P3 | 2G | riyadh | Sceco | 2G_LTE SA | RIYA2U6174B | FLM_TE | RIYA2U6174B | Results: DOWN SITE HUB RIYA2U6174B RIYA2U6174B Summary: Hub: RIYA2U6174B, Down Count: 1, Down Sites: RIYA2U6174B Alarm Summary: RIYA2U6174B No Active Alarm on HUB |  |  |  |  | site down |  | API | 09/29/2025 20:44:42 | 09/30/2025 09:20:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250930000103 | PCM-20250930-00000206 | TT-20250930-00074 | Telecom | Region_4 | JED1M7668 | JED0668 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 09/30/2025 03:08:23 | 09/30/2025 08:05:55 | 09/30/2025 09:08:23 | BASE STATION ANTENNA LINE PROBLEM at JED1M7668-CA-L800-P1-VIP-SBTS @ Sceco | 09/30/2025 00:46:36 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 09/30/2025 00:46:30 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M7668 | FLM_TE |  |  | PCM-20250930-00000054 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 09/30/2025 03:08:23 | 09/30/2025 08:05:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250930000123 | PCM-20250930-00000229 | TT-20250930-00353 | EM | Region_4 | JED6171 | JED6171 |  |  |  | Muhammad Javed Muhammad Anwar | 09/30/2025 03:29:42 | 10/06/2025 17:59:55 | 09/30/2025 15:29:42 | RECTIFIER MAINS POWER FAILURE at JED6171-GSM-P3 @ Sceco | 09/30/2025 03:22:25 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 09/30/2025 03:21:20 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6171 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 09/30/2025 03:29:42 | 09/30/2025 12:09:14 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250930000172 | PCM-20250930-00000306 | TT-20250930-00458 | EM | Region_4 | JDAP1M7969 | JDAP0969 |  |  |  | Ramadan Mohamed Sabri Mohamed | 09/30/2025 04:20:18 | 10/06/2025 17:59:56 | 09/30/2025 10:20:18 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JDAP1M7969-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 09/30/2025 04:13:32 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/30/2025 04:12:08 | VIP | 4G | jeddah | Sceco | LTE NSA | JDAP1M7969 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/30/2025 04:20:18 | 09/30/2025 13:20:24 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20250930000337 | PCM-20250930-00000701 | TT-20250930-00812 | EM | Region_4 | JED1M7901 | JED0901 |  |  |  | Ramadan Mohamed Sabri Mohamed | 09/30/2025 08:20:03 | 10/06/2025 17:59:56 | 09/30/2025 14:20:03 | AIRCON 1 FAILURE at JED1M7901-CA-L800-P1-VIP-SBTS @ Sceco | 09/30/2025 08:11:51 | Major | 7103 | AIRCON 1 FAILURE | 09/30/2025 08:11:45 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M7901 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 09/30/2025 08:20:03 | 09/30/2025 13:20:25 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20250930000382 | PCM-20250930-00000772 | TT-20250907-01691 | MW_HC | Region_2 | KHJ0303 | KHJ0303 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Hakim Ullah Raif Ullah Jan | 09/30/2025 08:45:52 | 10/02/2025 16:09:20 | 09/30/2025 20:45:52 | Huawei MW HC_P1 Observing Errors at KHJ0303-KHJ0010 | 09/07/2025 17:02:01 | Minor |  | LOF | 09/07/2025 17:02:01 | P1 | SRAN | al kharj | Sceco | TX NSA | KHJ0303-KHJ0010 | FLM_TE |  | STILL COUNTING ERRORS | PCM-20250930-00000735 | STILL COUNTING ERRORS | STILL COUNTING ERRORS |  |  |  | API | 09/30/2025 08:45:52 | 10/02/2025 15:51:18 | 10/02/2025 15:51:23 | 10/02/2025 15:51:26 | 10/02/2025 15:51:33 | 10/02/2025 16:09:20 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250930000390 | PCM-20250930-00000785 | TT-20250922-01800 | MW_HC | Region_2 | RIY0641 | RIY0641 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 09/30/2025 08:50:54 | 10/16/2025 20:23:37 | 09/30/2025 20:50:54 | Huawei MW HC_P2 Observing Errors at RIY0641-RIY2878 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0641-RIY2878 | FLM_TE |  | STILL COUNTING ERRORS | PCM-20250930-00000741 | STILL COUNTING ERRORS | STILL COUNTING ERRORS |  |  |  | API | 09/30/2025 08:50:54 | 09/30/2025 10:50:56 | 10/16/2025 20:23:27 |  |  | 10/16/2025 20:23:37 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20250930000498 | PCM-20250930-00000976 | TT-20250930-01065 | MW_HC | Region_4 | JED0571 | JED0571 | Transsmission | MW_HW_fault | Reconnect Fiber Cable | Fawzi Muneer Fawzi Mahmoud | 09/30/2025 10:48:32 | 09/30/2025 16:16:12 | 09/30/2025 22:48:32 | As per BO request NOKIA MW link JED0571-JED0250 | 09/30/2025 10:47:29 | Minor | 113388 | LOF | 09/30/2025 10:47:31 | P2 | 2G | jeddah | Sceco | TX NSA | JED0571-JED0250 | FLM_TE | [8 empty] | API | 09/30/2025 10:48:32 | 09/30/2025 11:52:55 | 09/30/2025 11:53:19 | 09/30/2025 11:53:22 | 09/30/2025 11:53:25 | 09/30/2025 16:16:12 |  | Fawzi Muneer Fawzi Mahmoud |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250930000659 | PCM-20250930-00001229 | TT-20250930-01209 | Reference_telecom | Region_4 | HHR1M7834 | HHR0834 |  |  |  | Khizer Hayat | 09/30/2025 12:43:22 | 09/30/2025 15:15:04 | 09/30/2025 16:43:22 | CELL OPERATION DEGRADED (RET Antenna control failure) at HHR1M7834-P1-VIP-HHR-L800 @ Generator_SG | 09/30/2025 11:41:57 | Critical | 7654 | CELL OPERATION DEGRADED | 09/30/2025 11:41:45 | VIP | 4G | jeddah | Generator_SG | LTE_Cell SA | HHR1M7834 | FLM_TE |  |  | PCM-20250930-00001123 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 09/30/2025 12:43:22 | 09/30/2025 15:15:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250930000785 | PCM-20250930-00001420 | TT-20250929-02748 | Reference_telecom | Region_1 | RYH-0119-NE40E-X2-M8-PE-01 | RYHR0119 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 09/30/2025 14:06:51 | 10/05/2025 08:05:47 | 09/30/2025 20:06:51 | MW_IS-IS Adjacency Changed at RYH-0119-NE40E-X2-M8-PE-01 //TT-20250518-00677 | 09/29/2025 17:09:02 | Major | 15269 | LOS | 09/29/2025 17:09:02 | P3 | IPRAN | hafr | Generator_DG | IPRAN_NSA | MW_IS-IS Adjacency Changed at RYH-0119-NE40E-X2-M8-PE-01 //TT-20250518-00677 | FLM_TE |  |  | PCM-20250930-00001411 | check with TRM BO | check with TRM BO |  |  |  | API | 09/30/2025 14:06:51 | 09/30/2025 18:14:38 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250930001123 | PCM-20250930-00001978 | TT-20250930-02064 | EM | Region_4 | BHMF2137 | BHMF2137 |  |  |  | Khizer Hayat | 09/30/2025 18:02:01 | 10/09/2025 16:52:57 | 10/01/2025 00:02:01 | 1(2G/LTE) sites down under BHMF2137-P3-CAP/BHMF2137-P3-CAP @ Generator_SG | 09/30/2025 17:53:56 | Major | 7706 | BTS O&M LINK FAILURE | 09/30/2025 17:53:50 | P3 | 2G | jeddah | Generator_SG | 2G SA | BHMF2137-P3-CAP | FLM_TE | BHMF2137 | Results: DOWN SITE HUB BHMF2137-P3-CAP BHMF2137 Summary: Hub: BHMF2137, Down Count: 1, Down Sites: BHMF2137-P3-CAP Alarm Summary: BHMF2137 No Active Alarm on HUB |  |  |  |  | sites down |  | Manual | 09/30/2025 18:02:01 | 10/09/2025 16:52:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250930001239 | PCM-20250930-00002142 | TT-20250930-01006 | Telecom | Region_4 | JED1U6837 | JED6137 |  |  |  | Mohamed Farag Abdelbary | 09/30/2025 20:07:05 | 10/02/2025 12:17:00 | 10/01/2025 02:07:05 | PT::BO need to check minor flapping of GTP-U Path Failure at JED1U6837-P3 | 09/30/2025 10:14:33 | Major | 7604 | BASE STATION OPERATION DEGRADED | 09/30/2025 10:14:33 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1U6837-P3 | FLM_TE |  | Thanks to check JED6113-JED0079 | PCM-20250930-00001854 | Thanks to check JED6113-JED0079 | Thanks to check JED6113-JED0079 |  |  |  | API | 09/30/2025 20:07:05 | 10/02/2025 12:17:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000021 | PCM-20251001-00000028 | TT-20250930-02318 | Telecom | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/01/2025 00:30:05 | 10/01/2025 05:47:09 | 10/01/2025 06:30:05 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TURY0688-P3 @ Sceco | 09/30/2025 20:30:58 | Major | 7607 | TRX OPERATION DEGRADED | 09/30/2025 20:30:55 | P3 | 2G | taif | Sceco | 2G_TRX NSA | TURY0688 | FLM_TE |  |  | PCM-20250930-00002177 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/01/2025 00:30:05 | 10/01/2025 05:47:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000024 | PCM-20251001-00000033 | TT-20251001-00048 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/01/2025 00:36:51 | 10/01/2025 10:26:50 | 10/01/2025 04:36:51 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/01/2025 00:36:32 | Critical | 65334 | Door open Alarm Equipment room | 10/01/2025 00:36:27 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/01/2025 00:36:51 | 10/01/2025 10:26:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251001000139 | PCM-20251001-00000251 | TT-20251001-00208 | Reference_telecom | Region_1 | HFF2U6708 | HFF6008 |  |  |  | Mohamed Magdy Fouad Zayed | 10/01/2025 03:13:10 | 10/01/2025 09:05:41 | 10/01/2025 15:13:10 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6708-P1-SHOP @ Sceco | 09/30/2025 23:33:12 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 09/30/2025 23:33:07 | P1 | 4G | hafouf | Sceco | 2G NSA | HFF2U6708 | FLM_TE |  |  | PCM-20251001-00000217 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/01/2025 03:13:10 | 10/01/2025 09:05:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251001000150 | PCM-20251001-00000280 | TT-20251001-00292 | EM | Region_4 | UKZ0073 | UKZ0073 |  |  |  | Faiz Muhammad Ghulam Sarwar | 10/01/2025 03:37:40 | 10/01/2025 03:37:40 | 10/01/2025 15:37:40 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at UKZ0073-GSM-P2-USF @ Sceco | 10/01/2025 03:29:17 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/01/2025 03:29:11 | P2 | 2G | adam | Sceco | 2G NSA | UKZ0073 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/01/2025 03:37:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251001000162 | PCM-20251001-00000299 | TT-20251001-00316 | EM | Region_6 | ABBS1M8181 | ABBS2181 |  |  |  | Muhammad Naeem Taj Din | 10/01/2025 03:49:02 | 10/01/2025 07:39:36 | 10/01/2025 15:49:02 | RECTIFIER MODULE FAILURE at ABBS1M8181-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/01/2025 03:41:58 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/01/2025 03:40:48 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8181 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/01/2025 03:49:02 | 10/01/2025 07:39:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251001000164 | PCM-20251001-00000301 | TT-20251001-00318 | EM | Region_6 | BSA1M8320 | BSA2320 |  |  |  | Asad Saddiq | 10/01/2025 03:49:04 | 10/01/2025 06:42:01 | 10/01/2025 15:49:04 | SMOKE ALARM at BSA1M8320-L800-P3-SBTS @ Generator_SG | 10/01/2025 03:41:48 | Minor | 7103 | SMOKE ALARM | 10/01/2025 03:40:37 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8320 | FLM_EM | [5 empty] | SMOKE ALARM |  |  | API | 10/01/2025 03:49:04 | 10/01/2025 06:42:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251001000165 | PCM-20251001-00000303 | TT-20251001-00320 | EM | Region_6 | ABBS1M8180 | ABBS2180 |  |  |  | Muhammad Naeem Taj Din | 10/01/2025 03:49:05 | 10/01/2025 07:39:37 | 10/01/2025 15:49:05 | RECTIFIER MAINS POWER FAILURE at ABBS1M8180-G9-L800-L1800-SBTS-P3-WBB-G3 @ Generator_SG | 10/01/2025 03:41:03 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/01/2025 03:40:45 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8180 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/01/2025 03:49:05 | 10/01/2025 07:39:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251001000174 | PCM-20251001-00000316 | TT-20251001-00307 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/01/2025 03:57:00 | 10/20/2025 12:32:16 | 10/01/2025 07:57:00 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 09/30/2025 23:45:41 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 09/30/2025 23:45:29 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251001-00000292 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/01/2025 03:57:00 | 10/01/2025 10:45:19 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000207 | PCM-20251001-00000368 | TT-20251001-00376 | Reference_telecom | Region_4 | JED1MN0865 | JED0865 |  |  |  | MALIK ATIF ZAMAN | 10/01/2025 04:39:56 | 10/01/2025 10:45:19 | 10/01/2025 16:39:56 | Fronthaul loop back connectivity check failure at JED1MN0865-NR2.6-P3 @ Sceco | 10/01/2025 04:05:09 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/01/2025 04:05:05 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0865 | FLM_TE |  |  | PCM-20251001-00000363 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/01/2025 04:39:56 | 10/01/2025 10:45:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000312 | PCM-20251001-00000557 | TT-20251001-00483 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/01/2025 07:08:23 | 10/20/2025 12:32:23 | 10/01/2025 13:08:23 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MKYL0914-GSM-UMTS-P3 @ Sceco | 10/01/2025 05:56:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/01/2025 05:56:36 | P3 | 2G | alaith | Sceco | 5G_Cell SA | MKYL0914 | FLM_TE |  |  | PCM-20251001-00000478 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/01/2025 07:08:23 | 10/02/2025 15:06:19 | [6 empty] | Force_Majeure |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000318 | PCM-20251001-00000573 | TT-20250929-02224 | MW_HC | Region_4 | JED0226 | JED0226 |  |  |  | MALIK ATIF ZAMAN | 10/01/2025 07:15:58 | 10/01/2025 10:45:21 | 10/01/2025 19:15:58 | Nokia MW HC_P1 Observing Performance Issue at JED0226 -1-JED0178_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0226 -1-JED0178_03 | FLM_TE |  |  | PCM-20251001-00000507 | Dear FLM team approved | Dear FLM team approved |  |  |  | API | 10/01/2025 07:15:58 | 10/01/2025 10:45:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251001000320 | PCM-20251001-00000581 | TT-20251001-00575 | Telecom | Region_4 | JDAP1M7940 | JDAP0940 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/01/2025 07:20:10 | 10/21/2025 18:15:02 | 10/01/2025 13:20:10 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/01/2025 07:13:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/01/2025 07:13:16 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JDAP1M7940 | FLM_TE |  |  | PCM-20251001-00000578 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/01/2025 07:20:10 | 10/20/2025 14:29:26 | 10/21/2025 18:14:57 |  |  | 10/21/2025 18:15:02 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000325 | PCM-20251001-00000593 | TT-20251001-00584 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/01/2025 07:31:11 | 10/20/2025 12:32:17 | 10/01/2025 19:31:11 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/01/2025 07:23:01 | Minor | 7115 | BASE STATION INFORMATION | 10/01/2025 07:22:55 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/01/2025 07:31:11 | 10/01/2025 10:45:21 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000362 | PCM-20251001-00000670 | TT-20251001-00648 | Telecom | Region_6 | NAMARA-SEC0016 | SEC0016 |  |  |  | Sohail Nasir Mir Afzal | 10/01/2025 08:11:43 | 10/02/2025 13:07:55 | 10/01/2025 14:11:43 | SPAN_LOSS_EXCEED_EOL at NAMARA-SEC0016_OCS @ Sceco | 10/01/2025 07:45:15 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/01/2025 07:45:05 | P1 | DWDM | abha | Sceco | DWDM NSA | NAMARA | FLM_TE | [8 empty] | API | 10/01/2025 08:11:43 | 10/02/2025 13:07:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000377 | PCM-20251001-00000698 | TT-20251001-00679 | EM | Region_4 | MAS1M7358 | MAS0358 |  |  |  | Walid Magdy Tawfik Elbana | 10/01/2025 08:34:44 | 10/01/2025 09:27:47 | 10/01/2025 20:34:44 | RECTIFIER MAINS POWER FAILURE at MAS1M7358-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/01/2025 08:26:42 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/01/2025 08:26:30 | P3 | 4G | taif | Sceco | LTE NSA | MAS1M7358 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/01/2025 08:34:44 | 10/01/2025 09:27:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251001000393 | PCM-20251001-00000725 | TT-20251001-00700 | Reference_telecom | Region_4 | MLJI0201 | MLJI0201 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/01/2025 08:45:37 | 10/03/2025 19:51:31 | 10/01/2025 14:45:37 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MLJI1M7201-G9-U9-NL8-SBTS-P2-USF @ Generator_SG | 10/01/2025 05:40:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/01/2025 05:40:51 | P2 | 2G | alaith | Generator_SG | 5G_Cell SA | MLJI1M7201 | FLM_TE | [5 empty] | Rx signal level failure |  |  | API | 10/01/2025 08:45:37 | 10/01/2025 09:10:49 | 10/03/2025 15:33:30 |  |  | 10/03/2025 19:51:31 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000396 | PCM-20251001-00000731 | TT-20251001-00705 | Reference_EM | Region_2 | RYDM2654 | RYDM2654 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/01/2025 08:47:40 | 10/21/2025 23:22:25 | 10/01/2025 14:47:40 | low fuel alarm at RYDM2654-P1-HUB_SRAN @ Generator_DG | 10/01/2025 08:37:25 | Major | 65115 | low fuel alarm | 10/01/2025 08:37:22 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM2654 | FLM_EM | [8 empty] | API | 10/01/2025 08:47:40 | 10/21/2025 23:22:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251001000449 | PCM-20251001-00000845 | TT-20251001-00801 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/01/2025 09:34:38 | 10/20/2025 12:32:18 | 10/01/2025 13:34:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/01/2025 09:33:38 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/01/2025 09:33:33 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/01/2025 09:34:38 | 10/01/2025 10:45:22 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251001000452 | PCM-20251001-00000850 | TT-20251001-00806 | Telecom | Region_4 | BHR0332 | BHR0332 | Equipment | BSS_HW_fault | Replace GPS Antenna | Moustafa Mahmoud Ahmed Fathelbab | 10/01/2025 09:38:04 | 10/02/2025 11:10:57 | 10/01/2025 21:38:04 | PT::FLM need to perform HC at BHR0332 (Bo request) | 10/01/2025 09:37:56 | Minor | 676767671 | Health Check-WO to TE FME | 10/01/2025 09:37:56 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | BHR0332 | FLM_TE | [8 empty] | API | 10/01/2025 09:38:04 | 10/01/2025 11:27:45 | 10/01/2025 11:29:25 | 10/01/2025 11:29:30 | 10/01/2025 11:29:53 | 10/02/2025 11:10:57 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251001000489 | PCM-20251001-00000903 | TT-20251001-00786 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/01/2025 10:15:23 | 10/21/2025 18:15:35 | 10/01/2025 16:15:23 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/01/2025 09:18:45 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/01/2025 09:18:39 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251001-00000835 | please check connection between JED1U6720 and JED1U6920 | please check connection between JED1U6720 and JED1U6920 |  |  |  | API | 10/01/2025 10:15:23 | 10/20/2025 14:29:25 | 10/21/2025 18:15:29 |  |  | 10/21/2025 18:15:35 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000545 | PCM-20251001-00000997 | TT-20251001-00938 | EM | Region_1 | DAM2M3636 | DAM0636 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/01/2025 10:56:47 | 10/01/2025 11:47:00 | 10/01/2025 22:56:47 | Low battery voltage at DAM2M3636-P2 @ Sceco | 10/01/2025 10:55:03 | Minor | 65110 | Low battery voltage | 10/01/2025 10:37:00 | P2 | 3G | dammam | Sceco | 3G NSA | DAM2M3636 | FLM_EM | [8 empty] | API | 10/01/2025 10:56:47 | 10/01/2025 11:47:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251001000555 | PCM-20251001-00001010 | TT-20251001-00944 | Telecom | Region_4 | JED0341 | JED0341 | Transsmission | DWDM_HW | Replaced HW Fault | Khaled Mohammad Abdallah | 10/01/2025 11:01:53 | 10/09/2025 03:15:12 | 10/01/2025 17:01:53 | IN_PWR_HIGH ALARM AT JED0341 | 10/01/2025 10:54:42 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/01/2025 10:54:42 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0341 | FLM_TE | [8 empty] | API | 10/01/2025 11:01:53 | 10/09/2025 00:39:29 | 10/09/2025 00:48:01 | 10/09/2025 00:48:03 | 10/09/2025 00:48:04 | 10/09/2025 03:15:12 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000559 | PCM-20251001-00001014 | TT-20251001-00947 | Reference_telecom | Region_2 | RIY2208 | RIY2208 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/01/2025 11:02:59 | 10/01/2025 21:02:08 | 10/01/2025 23:02:59 | RF Unit RX Channel RTWP/RSSI Unbalanced at RIY2208-P1-VIP-SRAN @ Generator_SG | 10/01/2025 08:02:47 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/01/2025 08:02:45 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2208 | FLM_TE | [8 empty] | API | 10/01/2025 11:02:59 | 10/01/2025 21:02:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000721 | PCM-20251001-00001265 | TT-20251001-01219 | MW_HC | Region_4 | HHR0505 | HHR0505 |  |  |  | Nazeer Mohammed | 10/01/2025 13:36:02 | 10/01/2025 13:59:58 | 10/02/2025 01:36:02 | As per BO request NEC MW link HHR0505-HHR0507 | 10/01/2025 13:34:59 | Minor | 113388 | LOF | 10/01/2025 13:35:01 | VIP | 2G | jeddah | Generator_SG | TX NSA | HHR0505-HHR0507 | FLM_TE | [8 empty] | API | 10/01/2025 13:36:02 | 10/01/2025 13:59:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000947 | PCM-20251001-00001592 | TT-20251001-01534 | Telecom | Region_4 | KMMD0736 | KMMD0736 |  |  |  | Nazeer Mohammed | 10/01/2025 16:13:25 | 10/01/2025 17:01:32 | 10/02/2025 04:13:25 | ODU CPU / Cable Open at KMMD0736_1 on 10.154.115.114 @ Sceco | 10/01/2025 16:12:25 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/01/2025 16:11:25 | P1 | 2G | jeddah | Sceco | TX NSA | KMMD0736 | FLM_TE | [8 empty] | API | 10/01/2025 16:13:25 | 10/01/2025 17:01:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001000985 | PCM-20251001-00001649 | TT-20251001-01593 | Reference_telecom | Region_4 | MKTF1M8797 | MKTF2797 |  |  |  | Rashid Shafique | 10/01/2025 16:49:06 | 10/01/2025 17:41:15 | 10/02/2025 04:49:06 | BASE STATION NOTIFICATION (Fan failure) at MKTF1M8797-CA-P3 @ Generator_SG | 10/01/2025 16:19:11 | Minor | 7652 | BASE STATION NOTIFICATION | 10/01/2025 16:18:57 | P3 | 4G | jeddah | Generator_SG | LTE NSA | MKTF1M8797 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/01/2025 16:49:06 | 10/01/2025 17:41:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251001001026 | PCM-20251001-00001715 | TT-20251001-01033 | Reference_telecom | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Saddam hussain muhammad khan | 10/01/2025 17:23:19 | 10/01/2025 17:23:19 | 10/01/2025 21:23:19 | IP PM Activation Failure at R2_RY2_HWBSC01 @ Sceco_STB | 10/01/2025 08:54:14 | Critical | 21341 | IP PM Activation Failure | 10/01/2025 08:53:39 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_TE |  |  | PCM-20251001-00001109 | check with Access BO for the site impact | check with Access BO for the site impact |  |  |  | API | 10/01/2025 17:23:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251001001097 | PCM-20251001-00001831 | TT-20251001-01757 | Telecom | Region_4 | TAF1M7279 | TAF0279 | Equipment | BTS_Cable | Reconnect Fiber Cable | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/01/2025 18:08:08 | 10/21/2025 17:12:31 | 10/02/2025 00:08:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF1M7279-G9-L18-L21-SBTS-P2 @ Sceco | 10/01/2025 18:07:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/01/2025 18:07:19 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7279 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/01/2025 18:08:08 | 10/01/2025 18:56:53 | 10/19/2025 08:46:48 |  |  | 10/19/2025 08:47:01 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251001001108 | PCM-20251001-00001847 | TT-20251001-01788 | EM | Region_1 | HFR0502 | HFR0502 | Enviroment | Bill | SCECO was restored after Bill was paid by the owner | Emad Mahmoud Ahmed Mohamed | 10/01/2025 18:17:57 | 10/01/2025 20:50:55 | 10/01/2025 22:17:57 | Door opening alarm at HFR0502-P1-Core-HUB-WDM_SRAN-FON @ Sceco_STB | 10/01/2025 18:17:38 | Critical | 65101 | Door opening alarm | 10/01/2025 18:17:35 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | HFR0502 | FLM_EM | [8 empty] | API | 10/01/2025 18:17:57 | 10/01/2025 20:48:08 | 10/01/2025 20:50:34 |  |  | 10/01/2025 20:50:55 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251001001194 | PCM-20251001-00001969 | TT-20251001-01911 | EM | Region_4 | TAF1M7317 | TAF0317 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | Ragb Ahmed Mohamed Abdelazim | 10/01/2025 19:30:15 | 10/23/2025 15:53:27 | 10/02/2025 07:30:15 | COMMERCIAL POWER FAILURE at TAF1M7317-NCA-L800-SBTS @ Generator_SG | 10/01/2025 19:22:04 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/01/2025 19:21:55 | P2 | 4G | taif | Generator_SG | LTE NSA | TAF1M7317 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/01/2025 19:30:15 | 10/04/2025 22:32:08 | 10/23/2025 15:37:59 | 10/23/2025 15:38:02 | 10/23/2025 15:38:04 | 10/23/2025 15:53:27 |  | Ragb Ahmed Mohamed Abdelazim |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251001001215 | PCM-20251001-00002013 | TT-20251001-01968 | Telecom | Region_4 | JDJZ0774 | JDJZ0774 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/01/2025 19:55:34 | 10/03/2025 14:03:56 | 10/02/2025 07:55:34 | Power Supply at JDJZ0774_4 on 10.154.113.18 @ Sceco | 10/01/2025 19:54:45 | Minor | Power Supply | Power Supply | 10/01/2025 19:46:16 | VIP | 2G | qunfuddah | Sceco | TX NSA | JDJZ0774 | FLM_TE | [8 empty] | API | 10/01/2025 19:55:34 | 10/01/2025 21:15:14 | 10/03/2025 14:03:50 |  |  | 10/03/2025 14:03:56 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001001223 | PCM-20251001-00002028 | TT-20251001-01995 | Telecom | Region_4 | THO0371 | THO0371 |  |  |  | Alaa Hassan Mohammed Gad | 10/01/2025 20:11:35 | 10/19/2025 17:44:00 | 10/02/2025 02:11:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/01/2025 20:10:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/01/2025 20:10:34 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | THO0371 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/01/2025 20:11:35 | 10/01/2025 21:23:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251001001271 | PCM-20251001-00002102 | TT-20251001-01843 | Reference_telecom | Region_4 | SJED1S7482 | SJED0482 |  |  |  | Mohammed Ramadan A Abu Abid | 10/01/2025 21:30:13 | 10/02/2025 06:53:09 | 10/02/2025 03:30:13 | BASE STATION OPERATION DEGRADED (Inter-Site CA X2 link unavailability) at SJED1S7482-P1-VIP (Ref::TT-20250927-01050) @ Sceco | 09/27/2025 18:01:16 | Major | 7651 | BASE STATION OPERATION DEGRADED | 09/27/2025 17:55:12 | VIP | 4G | jeddah | Sceco | LTE NSA | SJED1S7482 | FLM_TE |  |  | PCM-20251001-00001886 | FLM need to check Inter CA site status and SRIO cable between them | FLM need to check Inter CA site status and SRIO cable between them |  |  |  | API | 10/01/2025 21:30:13 | 10/01/2025 23:46:44 | 10/02/2025 06:53:09 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251001001274 | PCM-20251001-00002106 | TT-20251001-01792 | Reference_telecom | Region_4 | JED0152 | JED0152 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/01/2025 21:36:26 | 10/02/2025 10:57:55 | 10/02/2025 09:36:26 | JED1W0152 Complete Down | 10/01/2025 18:08:40 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/01/2025 18:08:40 | VIP | 2G | jeddah | Sceco | Wifi SA | JED1W0152 | FLM_TE | JED0152 | Hub: JED0152 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0109 scattered site observing LOS TO AIRSCALE Kindly update TT under EM, FLM | PCM-20251001-00001866 | No power issue | No power issue |  |  |  | API | 10/01/2025 21:36:26 | 10/02/2025 10:57:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251001001292 | PCM-20251001-00002135 | TT-20251001-02128 | EM | Region_6 | RYAB0630 | RYAB0630 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Aslam Abdul Salam | 10/01/2025 22:15:05 | 10/10/2025 12:26:45 | 10/02/2025 04:15:05 | AIRCON 1 FAILURE at RYAB0630-GSM-UMTS-P1-HUB-USF @ Sceco | 10/01/2025 22:07:07 | Major | 7103 | AIRCON 1 FAILURE | 10/01/2025 22:06:50 | P1 | 2G | wadi dawasar | Sceco | 2G NSA | RYAB0630 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/01/2025 22:15:05 | 10/01/2025 22:17:20 | 10/10/2025 12:26:26 |  |  | 10/10/2025 12:26:45 |  | Muhammad Aslam Abdul Salam |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251001001323 | PCM-20251001-00002204 | TT-20251001-02197 | Reference_telecom | Region_5 | MAK0382 | MAK0382 |  |  |  | IJAZ ALI | 10/01/2025 22:58:57 | 10/23/2025 17:11:42 | 10/02/2025 10:58:57 | Degrade observed in MAK0382 towards 10.10.178.244 @ Sceco | 10/01/2025 11:00:41 | Minor |  | Degrade | 10/01/2025 10:58:25 | VIP | 2G | makkah | Sceco | TX NSA | MAK0382 | FLM_TE | [8 empty] | API | 10/01/2025 22:58:57 | 10/23/2025 16:24:00 | 10/23/2025 17:10:55 | 10/23/2025 17:11:21 | 10/23/2025 17:11:42 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000002 | PCM-20251002-00000002 | TT-20251001-02241 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/02/2025 00:03:49 | 10/20/2025 12:32:19 | 10/02/2025 06:03:49 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/01/2025 23:35:21 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/01/2025 23:35:15 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251001-00002245 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/02/2025 00:03:49 | 10/02/2025 08:31:53 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000013 | PCM-20251002-00000022 | TT-20251002-00016 | Reference_telecom | Region_1 | KBR6010 | KBR6010 |  |  |  | Meraj Husain Idd Baksh | 10/02/2025 00:17:30 | 10/15/2025 11:52:32 | 10/02/2025 12:17:30 | RF Unit RX Channel RTWP/RSSI Too Low at KBR6010-P3_SRAN @ Sceco | 10/01/2025 21:17:09 | Minor | 26521 | RF Unit RX Channel RTWP/RSSI Too Low | 10/01/2025 21:17:07 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6010 | FLM_TE | [8 empty] | API | 10/02/2025 00:17:30 | 10/02/2025 02:19:15 | [6 empty] | STC |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251002000028 | PCM-20251002-00000040 | TT-20251001-00324 | Reference_telecom | Region_2 | R2_RY1_HWBSC01 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/02/2025 00:31:19 | 10/02/2025 00:31:19 | 10/02/2025 04:31:19 | IP PM Activation Failure at R2_RY1_HWBSC01 @ Sceco_STB | 10/01/2025 00:52:41 | Critical | 21341 | IP PM Activation Failure | 10/01/2025 00:52:03 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY1_HWBSC01 | FLM_EM |  |  | PCM-20251001-00002254 | We are observing RSL -90 at hub site RYQS2014 ,Suspected power issue, Dear EM FLM please check issue and solve | We are observing RSL -90 at hub site RYQS2014 ,Suspected power issue, Dear EM FLM please check issue and solve |  |  |  | API | 10/02/2025 00:31:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000067 | PCM-20251002-00000102 | TT-20251002-00124 | EM | Region_1 | Sk1 | SK1 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/02/2025 01:24:40 | 10/02/2025 02:18:06 | 10/02/2025 05:24:40 | Door opening alarm at SK1-Shelter 1-WDM-HUB-Core-P1 @ Sceco_STB | 10/02/2025 01:24:11 | Critical | 65101 | Door opening alarm | 10/02/2025 01:23:27 | P1 | BSC | sakaka | Sceco_STB | 2G NSA | SK1 | FLM_EM | [8 empty] | API | 10/02/2025 01:24:40 | 10/02/2025 02:18:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000079 | PCM-20251002-00000117 | TT-20251002-00141 | EM | Region_1 | Sk1 | SK1 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/02/2025 01:32:25 | 10/02/2025 02:18:08 | 10/02/2025 05:32:25 | Genset not in auto mode at SK1-Shelter 1-WDM-HUB-Core-P1 @ Sceco_STB | 10/02/2025 01:30:32 | Critical | 65113 | Genset not in auto mode | 10/02/2025 01:29:49 | P1 | BSC | sakaka | Sceco_STB | 2G NSA | SK1 | FLM_EM | [8 empty] | API | 10/02/2025 01:32:25 | 10/02/2025 02:18:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000091 | PCM-20251002-00000133 | TT-20251002-00160 | EM | Region_4 | HBI1M8412 | HBI2412 | Enviroment | Outdoor_Temperature | Change Fan | AbdAllah Mohammad abd Elgawad Fath Elbab | 10/02/2025 01:46:53 | 10/14/2025 19:29:57 | 10/02/2025 13:46:53 | SHELTER DOOR OPEN at HBI1M8412-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/02/2025 01:46:33 | Minor | 7103 | SHELTER DOOR OPEN | 10/02/2025 01:45:04 | P3 | 4G | jeddah | Generator_DG | LTE NSA | HBI1M8412 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/02/2025 01:46:53 | 10/14/2025 17:33:14 | 10/14/2025 17:37:44 | 10/14/2025 17:40:19 | 10/14/2025 18:57:06 | 10/14/2025 19:29:57 |  | AbdAllah Mohammad abd Elgawad Fath Elbab |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000113 | PCM-20251002-00000165 | TT-20251002-00197 | Reference_telecom | Region_4 | MKMD0559 | MKMD0559 |  |  |  | Khizer Hayat | 10/02/2025 02:15:49 | 10/02/2025 13:04:48 | 10/02/2025 14:15:49 | LossOfSignal observed in MKMD0559_02 towards 10.10.178.71 @ Sceco_STB | 10/01/2025 14:16:43 | Minor |  | LossOfSignal | 10/01/2025 14:15:41 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKMD0559 | FLM_TE | [8 empty] | API | 10/02/2025 02:15:49 | 10/02/2025 13:04:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000114 | PCM-20251002-00000168 | TT-20251002-00204 | EM | Region_1 | SAK0585 | SAK0585 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/02/2025 02:18:55 | 10/06/2025 16:35:13 | 10/02/2025 06:18:55 | Door opening alarm at SAK0585-P1-Core-SHOP-HUB-WDM_SRAN-FON @ Sceco | 10/02/2025 02:18:45 | Critical | 65101 | Door opening alarm | 10/02/2025 02:18:42 | P1 | SRAN | sakaka | Sceco | 2G NSA | SAK0585 | FLM_EM | [8 empty] | API | 10/02/2025 02:18:55 | 10/06/2025 16:35:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000125 | PCM-20251002-00000179 | TT-20251002-00214 | EM | Region_4 | HHR0613 | HHR0613 | Enviroment | Air Condition | Change indoor motor | Rami Mohamed Abubakr Ibrahim | 10/02/2025 02:29:46 | 10/21/2025 14:26:35 | 10/02/2025 08:29:46 | GENERATOR LOW FUEL at HHR0613-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/02/2025 02:21:33 | Major | 7103 | GENERATOR LOW FUEL | 10/02/2025 02:21:16 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0613 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/02/2025 02:29:46 | 10/21/2025 13:35:44 | 10/21/2025 13:35:49 | 10/21/2025 13:35:52 | 10/21/2025 13:35:55 | 10/21/2025 14:26:35 |  | Rami Mohamed Abubakr Ibrahim |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000126 | PCM-20251002-00000180 | TT-20251002-00216 | EM | Region_4 | HHR0834 | HHR0834 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/02/2025 02:30:17 | 10/20/2025 14:35:54 | 10/02/2025 08:30:17 | AIRCON 1 FAILURE at HHR0834-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/02/2025 02:21:57 | Major | 7103 | AIRCON 1 FAILURE | 10/02/2025 02:21:51 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0834 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/02/2025 02:30:17 | 10/20/2025 14:35:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000135 | PCM-20251002-00000194 | TT-20251002-00250 | EM | Region_6 | BSA1M8291 | BSA2291 |  |  |  | Asad Saddiq | 10/02/2025 02:41:08 | 10/02/2025 10:01:57 | 10/02/2025 14:41:08 | SHELTER DOOR OPEN at BSA1M8291-G9-L8-L18-SBTS-P3 @ Sceco | 10/02/2025 02:40:34 | Minor | 7103 | SHELTER DOOR OPEN | 10/02/2025 02:39:26 | P3 | 4G | bisha | Sceco | LTE NSA | BSA1M8291 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/02/2025 02:41:08 | 10/02/2025 10:01:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000136 | PCM-20251002-00000197 | TT-20251002-00255 | EM | Region_6 | ABBS1M8182 | ABBS2182 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/02/2025 02:46:17 | 10/02/2025 07:04:10 | 10/02/2025 14:46:17 | Tower light Alarm at ABBS1M8182-G9-L800-SBTS-P3 @ Generator_SG | 10/02/2025 02:39:16 | Minor | 7103 | Tower light Alarm | 10/02/2025 02:38:07 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8182 | FLM_EM | [5 empty] | Tower light Alarm |  |  | API | 10/02/2025 02:46:17 | 10/02/2025 07:04:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000138 | PCM-20251002-00000199 | TT-20251002-00257 | EM | Region_6 | BSA1M8291 | BSA2291 |  |  |  | Asad Saddiq | 10/02/2025 02:47:51 | 10/02/2025 10:01:57 | 10/02/2025 14:47:51 | AIRCON 1 FAILURE at BSA1M8291-G9-L8-L18-SBTS-P3 @ Sceco | 10/02/2025 02:40:33 | Minor | 7103 | AIRCON 1 FAILURE | 10/02/2025 02:39:26 | P3 | 4G | bisha | Sceco | LTE NSA | BSA1M8291 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/02/2025 02:47:51 | 10/02/2025 10:01:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000196 | PCM-20251002-00000300 | TT-20251002-00632 | Reference_telecom | Region_4 | MKMD0560 | MKMD0560 |  |  |  | Khizer Hayat | 10/02/2025 04:30:39 | 10/02/2025 13:04:49 | 10/02/2025 16:30:39 | Degrade observed in MKMD0560_01 towards 10.10.178.72 @ Sceco | 10/01/2025 16:30:47 | Minor |  | Degrade | 10/01/2025 16:30:23 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0560 | FLM_TE | [8 empty] | API | 10/02/2025 04:30:39 | 10/02/2025 13:04:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000227 | PCM-20251002-00000344 | TT-20251002-00683 | Telecom | Region_4 | SQSH0023 | SQSH0023 | Equipment | BSS_HW_Stuck | Reset System Module | Mudassar Bashir Bashir Ahmad | 10/02/2025 05:24:44 | 10/04/2025 09:08:36 | 10/02/2025 11:24:44 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at SQSH0023-GSM-UMTS-P2-USF @ Generator_DG | 10/02/2025 05:19:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 05:19:09 | P2 | 2G | qunfuddah | Generator_DG | 5G_Cell SA | SQSH0023 | FLM_TE |  |  | PCM-20251002-00000343 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/02/2025 05:24:44 | 10/02/2025 07:27:55 | 10/04/2025 09:08:13 |  |  | 10/04/2025 09:08:36 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000235 | PCM-20251002-00000361 | TT-20251002-00704 | Reference_telecom | Region_4 | JED0954 | JED0954 |  |  |  | Nazeer Mohammed | 10/02/2025 05:36:15 | 10/02/2025 11:15:31 | 10/02/2025 17:36:15 | FanFailure observed in JED0954_02 towards 10.10.179.163 @ Sceco | 10/01/2025 17:36:56 | Minor |  | FanFailure | 10/01/2025 17:35:45 | P3 | 2G | jeddah | Sceco | TX NSA | JED0954 | FLM_TE | [8 empty] | API | 10/02/2025 05:36:15 | 10/02/2025 11:15:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000242 | PCM-20251002-00000376 | TT-20251002-00701 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/02/2025 05:51:52 | 10/20/2025 12:32:21 | 10/02/2025 09:51:52 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/02/2025 01:33:57 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 01:33:46 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251002-00000357 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/02/2025 05:51:52 | 10/02/2025 08:31:54 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000300 | PCM-20251002-00000475 | TT-20251002-00728 | Telecom | Region_1 | DRN2M8328 | DRN2328 |  |  |  | Imran Ali Yousaf | 10/02/2025 07:09:11 | 10/15/2025 11:52:33 | 10/02/2025 19:09:11 | Cell Capability Degraded at DRN2M8328-L800-P3 @ Sceco | 10/02/2025 02:40:15 | Minor | 29243 | Cell Capability Degraded | 10/02/2025 02:38:42 | P3 | 4G | dammam | Sceco | 2G NSA | DRN2M8328 | FLM_TE |  |  | PCM-20251002-00000386 | pls check UBBP:0-0-4 Port:1 Subport:0 | pls check UBBP:0-0-4 Port:1 Subport:0 |  |  |  | API | 10/02/2025 07:09:11 | 10/02/2025 13:03:57 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000307 | PCM-20251002-00000487 | TT-20251002-00801 | Telecom | Region_1 | DRN2328 | DRN2328 |  |  |  | Imran Ali Yousaf | 10/02/2025 07:15:33 | 10/15/2025 11:52:34 | 10/02/2025 13:15:33 | BBU CPRI Line Rate Negotiation Abnormal at DRN2328-P3_SRAN @ Sceco | 10/02/2025 02:44:39 | Major | 26246 | BBU CPRI Line Rate Negotiation Abnormal | 10/02/2025 02:43:06 | P3 | SRAN | dammam | Sceco | 2G NSA | DRN2328 | FLM_TE |  |  | PCM-20251002-00000479 | pls check RRU Chain Description=UBBP:0-0-4 Port:1 Subport:0 | pls check RRU Chain Description=UBBP:0-0-4 Port:1 Subport:0 |  |  |  | API | 10/02/2025 07:15:33 | 10/02/2025 13:03:57 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000316 | PCM-20251002-00000503 | TT-20251002-00840 | EM | Region_6 | BHAB1M8041 | BHAB2041 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/02/2025 07:29:23 | 10/02/2025 09:21:57 | 10/02/2025 19:29:23 | COMMERCIAL POWER FAILURE at BHAB1M8041-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/02/2025 07:21:14 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/02/2025 07:21:03 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8041 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/02/2025 07:29:23 | 10/02/2025 09:21:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000348 | PCM-20251002-00000550 | TT-20250929-03146 | MW_HC | Region_4 | JED2072 | JED2072 |  |  |  | MALIK ATIF ZAMAN | 10/02/2025 07:55:41 | 10/02/2025 08:31:55 | 10/02/2025 19:55:41 | As BO Requested MW Nokia Observing PM errors and ACM flapping for MW link JED0783-JDJZ0761 | 09/29/2025 23:46:55 | Minor | 113388 | LOF | 09/29/2025 23:46:57 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED2072-JED0435 | FLM_TE |  |  | PCM-20251002-00000410 | Shared with Mr Hazem for approval | Shared with Mr Hazem for approval |  |  |  | API | 10/02/2025 07:55:41 | 10/02/2025 08:31:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000397 | PCM-20251002-00000630 | TT-20251002-00896 | Telecom | Region_1 | KBR2W6015 | KBR2W6015 | Equipment | BTS_Cable | Replace Ethernet Cable | Meraj Husain Idd Baksh | 10/02/2025 08:49:12 | 10/04/2025 16:31:05 | 10/02/2025 20:49:12 | HC TT For KBR2W6015 | 10/02/2025 08:08:27 | Minor | 676767672 | Health Check-WO to TE FME | 10/02/2025 08:08:29 | P3 | WIFI | Khobar | Sceco | 2G NSA | KBR2W6015 | FLM_TE |  |  | PCM-20251002-00000568 | please arrange FLM to the Site to check locally AP is flapping | please arrange FLM to the Site to check locally AP is flapping |  |  |  | API | 10/02/2025 08:49:12 | 10/02/2025 10:59:37 | 10/04/2025 16:30:39 |  |  | 10/04/2025 16:31:05 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251002000423 | PCM-20251002-00000679 | TT-20251002-01000 | EM | Region_4 | JDMK2408 | JDMK2408 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/02/2025 09:16:09 | 10/02/2025 09:24:32 | 10/02/2025 15:16:09 | 1(2G/LTE) sites down under JDMK2408-P3/JDMK2408-P3 @ Generator_SG | 10/02/2025 09:07:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/02/2025 09:07:41 | P3 | 2G | makkah | Generator_SG | 2G SA | JDMK2408-P3 | FLM_TE | JDMK2408 | Results: DOWN SITE HUB JDMK2408-P3 JDMK2408 Summary: Hub: JDMK2408, Down Count: 1, Down Sites: JDMK2408-P3 Alarm Summary: JDMK2408 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/02/2025 09:16:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000463 | PCM-20251002-00000748 | TT-20251002-01066 | Reference_telecom | Region_6 | BAH0173 | BAH0173 |  |  |  | Manzoor Ahmed | 10/02/2025 09:49:05 | 10/02/2025 10:01:41 | 10/02/2025 21:49:05 | Nokia Eband Observing ReplaceableUnitProblem-Card - 3,ReplaceableUnitPro at BAH0173_01-10.221.240.105 | 09/04/2025 13:54:08 | Minor |  | LOF | 09/04/2025 13:54:08 | P2 | 2G | Albaha | Sceco | TX NSA | BAH0173_01-10.221.240.105 | FLM_TE | [8 empty] | API | 10/02/2025 09:49:05 | 10/02/2025 10:01:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000512 | PCM-20251002-00000797 | TT-20251002-01116 | Reference_telecom | Region_5 | AHS9409 | AHS9409 |  |  |  | Hosini Saeed Hassn Saeed | 10/02/2025 09:50:03 | 10/05/2025 06:41:49 | 10/02/2025 21:50:03 | NEC MW Observing RX Level,LOF at AHS9409(10.88.225.82) | 09/29/2025 06:02:35 | Minor |  | LOF | 09/29/2025 06:02:35 | P1 | Repeater | makkah | Generator_DG | TX NSA | AHS9409(10.88.225.82) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:03 | 10/05/2025 06:41:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000513 | PCM-20251002-00000798 | TT-20251002-01117 | Reference_telecom | Region_1 | ARM0872 | ARM0872 |  |  |  | Imran Ali Yousaf | 10/02/2025 09:50:04 | 10/22/2025 11:33:32 | 10/02/2025 21:50:04 | NEC MW Observing TX Power,ODU Alarm at ARM0872(10.21.217.171) | 09/21/2025 12:29:41 | Minor |  | LOF | 09/21/2025 12:29:41 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0872(10.21.217.171) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:04 | 10/02/2025 13:03:58 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000522 | PCM-20251002-00000807 | TT-20251002-01126 | Reference_telecom | Region_1 | HFF2244 | HFF2244 |  |  |  | Mohamed Magdy Fouad Zayed | 10/02/2025 09:50:15 | 10/19/2025 11:08:04 | 10/02/2025 21:50:15 | NEC MW Observing ODU CPU / Cable Open,LOF,Frame ID at HFF2244(10.147.13.82) | 09/28/2025 12:51:35 | Minor |  | LOF | 09/28/2025 12:51:35 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF2244(10.147.13.82) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:15 | 10/02/2025 10:11:59 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000526 | PCM-20251002-00000811 | TT-20251002-01130 | Reference_telecom | Region_1 | HMBY2434 | HMBY2434 |  |  |  | Imran Ali Yousaf | 10/02/2025 09:50:20 | 10/22/2025 11:33:33 | 10/02/2025 21:50:20 | NEC MW Observing LOF,RX Level,RX Level,LOF at HMBY2434(10.154.6.166) | 09/28/2025 05:56:52 | Minor |  | LOF | 09/28/2025 05:56:52 | VIP | SRAN | dammam | Sceco | TX NSA | HMBY2434(10.154.6.166) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:20 | 10/02/2025 13:03:58 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000532 | PCM-20251002-00000817 | TT-20251002-01136 | Reference_telecom | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/02/2025 09:50:26 | 10/02/2025 13:10:43 | 10/02/2025 21:50:26 | NEC MW Observing LOF,Frame ID at JDJZ0785-2(10.154.170.162) | 09/17/2025 10:28:05 | Minor |  | LOF | 09/17/2025 10:28:05 | P1 | 2G | derb | Sceco_STB | TX NSA | JDJZ0785-2(10.154.170.162) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:26 | 10/02/2025 13:10:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000537 | PCM-20251002-00000822 | TT-20251002-01141 | Reference_telecom | Region_1 | KBR0330 | KBR0330 |  |  |  | Imran Ali Yousaf | 10/02/2025 09:50:33 | 10/22/2025 11:33:34 | 10/02/2025 21:50:33 | NEC MW Observing LOF,Frame ID at KBR0330(10.1.221.218) | 09/28/2025 12:52:59 | Minor |  | LOF | 09/28/2025 12:52:59 | VIP | SRAN | dammam | Sceco | TX NSA | KBR0330(10.1.221.218) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:33 | 10/02/2025 13:04:00 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000538 | PCM-20251002-00000823 | TT-20251002-01142 | Reference_telecom | Region_1 | KBR6021 | KBR6021 |  |  |  | Meraj Husain Idd Baksh | 10/02/2025 09:50:34 | 10/22/2025 11:33:28 | 10/02/2025 21:50:34 | NEC MW Observing ODU CPU / Cable Open,LOF,LOF at KBR6021(10.154.12.57) | 09/28/2025 05:56:01 | Minor |  | LOF | 09/28/2025 05:56:01 | P3 | SRAN | dammam | Sceco | TX NSA | KBR6021(10.154.12.57) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:34 | 10/02/2025 10:59:38 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000539 | PCM-20251002-00000824 | TT-20251002-01143 | Reference_telecom | Region_1 | KBR6043 | KBR6043 |  |  |  | Meraj Husain Idd Baksh | 10/02/2025 09:50:35 | 10/22/2025 11:33:30 | 10/02/2025 21:50:35 | NEC MW Observing ODU CPU / Cable Open,LOF at KBR6043(10.1.221.219) | 09/28/2025 05:54:26 | Minor |  | LOF | 09/28/2025 05:54:26 | VIP | SRAN | dammam | Sceco | TX NSA | KBR6043(10.1.221.219) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:35 | 10/02/2025 10:59:39 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000540 | PCM-20251002-00000825 | TT-20251002-01144 | Reference_telecom | Region_1 | KBR6086 | KBR6086 |  |  |  | Meraj Husain Idd Baksh | 10/02/2025 09:50:37 | 10/02/2025 10:59:40 | 10/02/2025 21:50:37 | NEC MW Observing LOF,LOF,Radio Traffic Aggregation Link,LOF,RX Level,LOF,RX Level,RX Level,ODU CPU / Cable Open,RX Level,LOF,Frame ID at KBR6086(10.154.12.58) | 09/28/2025 12:39:39 | Minor |  | LOF | 09/28/2025 12:39:39 | P3 | SRAN | dammam | Sceco | TX NSA | KBR6086(10.154.12.58) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:37 | 10/02/2025 10:59:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000542 | PCM-20251002-00000827 | TT-20251002-01146 | Reference_telecom | Region_1 | KBR6090 | KBR6090 |  |  |  | Meraj Husain Idd Baksh | 10/02/2025 09:50:39 | 10/22/2025 11:33:31 | 10/02/2025 21:50:39 | NEC MW Observing LOF,Frame ID at KBR6090(10.154.12.56) | 09/28/2025 05:55:08 | Minor |  | LOF | 09/28/2025 05:55:08 | P3 | SRAN | dammam | Sceco | TX NSA | KBR6090(10.154.12.56) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:39 | 10/02/2025 10:59:41 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000551 | PCM-20251002-00000837 | TT-20251002-01156 | Reference_telecom | Region_3 | MDN6030 | MDN6030 |  |  |  | TAUSEEF ILYAS | 10/02/2025 09:50:50 | 10/02/2025 13:58:39 | 10/02/2025 21:50:50 | NEC MW Observing MODEM Power Supply Alarm,MODEM Power Supply Alarm at NODE2 RING18 - MDN6030(10.154.89.129) | 07/18/2024 02:10:37 | Minor |  | LOF | 07/18/2024 02:10:37 | P1 | SRAN | madinah | Sceco | TX NSA | NODE2 RING18 - MDN6030(10.154.89.129) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:50 | 10/02/2025 13:58:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000553 | PCM-20251002-00000839 | TT-20251002-01158 | Reference_telecom | Region_4 | TFBH0891 | TFBH0891 |  |  |  | Ahmad Kamal Abdelmawla | 10/02/2025 09:50:52 | 10/02/2025 10:13:33 | 10/02/2025 21:50:52 | NEC MW Observing RX Level,RX Level,RX Level,RX Level,RX Level,RX Level,RX Level,RX Level,LOF,LOF,LOF,LOF,LOF,LOF,LOF,LOF,Radio Traffic Aggregation Link at TFBH_0891(10.154.143.77) | 09/17/2025 10:04:43 | Minor |  | LOF | 09/17/2025 10:04:43 | P1 | 2G | taif | Sceco | TX NSA | TFBH_0891(10.154.143.77) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:52 | 10/02/2025 10:13:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000556 | PCM-20251002-00000841 | TT-20251002-01160 | Reference_telecom | Region_6 | WDS9457 | WDS9457 |  |  |  | Ahmed Mamdouh Helal Helal | 10/02/2025 09:50:56 | 10/02/2025 11:21:16 | 10/02/2025 21:50:56 | NEC MW Observing LAN Link at WDS9457-1(10.89.222.130) | 09/29/2025 11:32:53 | Minor |  | LOF | 09/29/2025 11:32:53 | P1 | Repeater | wadi dawasar | Generator_DG | TX NSA | WDS9457-1(10.89.222.130) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:56 | 10/02/2025 11:21:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000559 | PCM-20251002-00000844 | TT-20251002-01163 | Reference_telecom | Region_4 | THO0369 | THO0369 |  |  |  | Nazeer Mohammed | 10/02/2025 09:50:58 | 10/02/2025 11:15:34 | 10/02/2025 21:50:58 | NEC MW Observing RX Level,LOF,FAN FAIL at THO 0369-3(10.154.126.20) | 09/18/2025 08:42:36 | Minor |  | LOF | 09/18/2025 08:42:36 | P2 | 2G | jeddah | Sceco | TX NSA | THO 0369-3(10.154.126.20) | FLM_TE | [8 empty] | API | 10/02/2025 09:50:58 | 10/02/2025 11:15:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000656 | PCM-20251002-00000981 | TT-20251002-01293 | EM | Region_4 | THO0371 | THO0371 |  |  |  | Hamza Ahmed Aly Sawy | 10/02/2025 11:09:26 | 10/04/2025 23:04:40 | 10/02/2025 23:09:26 | SHELTER DOOR OPEN at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/02/2025 11:09:02 | Minor | 7103 | SHELTER DOOR OPEN | 10/02/2025 11:08:41 | P2 | 2G | jeddah | Sceco | 2G NSA | THO0371 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/02/2025 11:09:26 | 10/04/2025 23:04:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002000660 | PCM-20251002-00000992 | TT-20251002-01305 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/02/2025 11:16:09 | 10/20/2025 12:32:22 | 10/02/2025 23:16:09 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/02/2025 11:08:06 | Minor | 7115 | BASE STATION INFORMATION | 10/02/2025 11:07:58 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/02/2025 11:16:09 | 10/02/2025 11:31:53 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000663 | PCM-20251002-00000995 | TT-20251002-01308 | EM | Region_4 | THO0371 | THO0371 |  |  |  | Hamza Ahmed Aly Sawy | 10/02/2025 11:17:11 | 10/04/2025 23:04:40 | 10/02/2025 23:17:11 | AIRCON1 at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/02/2025 11:09:02 | Minor | 7103 | AIRCON1 | 10/02/2025 11:08:41 | P2 | 2G | jeddah | Sceco | 2G NSA | THO0371 | FLM_EM | [5 empty] | AIRCON1 |  |  | API | 10/02/2025 11:17:11 | 10/04/2025 23:04:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251002000705 | PCM-20251002-00001061 | TT-20251002-01388 | Telecom | Region_4 | JED1M8128 | JED2128 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/02/2025 12:01:35 | 10/02/2025 12:01:35 | 10/02/2025 16:01:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8128-P1-VIP-CA-L800 @ Sceco | 10/02/2025 12:00:58 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 12:00:52 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8128 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/02/2025 12:01:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251002000745 | PCM-20251002-00001122 | TT-20251002-01460 | Reference_EM | Region_1 | RSK2624 | RSK2624 |  |  |  | Dileesh Muringothil Devarajan | 10/02/2025 12:35:10 | 10/02/2025 17:58:16 | 10/03/2025 00:35:10 | Mains Failure at RSK2624-P3_SRAN-PC @ Sceco | 10/02/2025 12:25:03 | Minor | 65109 | Mains Failure | 10/02/2025 12:24:59 | P3 | SRAN | jubail | Sceco | 2G NSA | RSK2624 | FLM_EM | [8 empty] | API | 10/02/2025 12:35:10 | 10/02/2025 12:40:20 | 10/02/2025 17:58:04 | 10/02/2025 17:58:16 | [7 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251002000756 | PCM-20251002-00001136 | TT-20251002-01470 | Telecom | Region_4 | HAW0303 | HAW0303 |  |  |  | Rashid Shafique | 10/02/2025 12:38:29 | 10/02/2025 18:06:10 | 10/03/2025 00:38:29 | PT::FLM need to perform HC at HAW0303 (Bo request) | 10/02/2025 12:38:22 | Minor | 676767671 | Health Check-WO to TE FME | 10/02/2025 12:38:22 | VIP | 2G | taif | Sceco | 2G_3G_LTE_5G NSA | HAW0303 | FLM_TE | [8 empty] | API | 10/02/2025 12:38:29 | 10/02/2025 18:06:00 | 10/02/2025 18:06:05 | 10/02/2025 18:06:07 | 10/02/2025 18:06:10 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251002000758 | PCM-20251002-00001138 | TT-20251002-01472 | Telecom | Region_4 | JED0193 | JED0193 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/02/2025 12:39:17 | 10/02/2025 15:19:13 | 10/03/2025 00:39:17 | PT::FLM need to perform HC at JED0193 (Bo request) | 10/02/2025 12:39:10 | Minor | 676767671 | Health Check-WO to TE FME | 10/02/2025 12:39:10 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0193 | FLM_TE | [8 empty] | API | 10/02/2025 12:39:17 | 10/02/2025 13:00:08 | 10/02/2025 15:04:00 | 10/02/2025 15:04:02 | 10/02/2025 15:19:13 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000813 | PCM-20251002-00001229 | TT-20251002-01394 | Telecom | Region_4 | JED1U6755 | JED6055 | Equipment | BTS_Cable | Replace Indoor Feeder Cable Connector | Mohamed Farag Abdelbary | 10/02/2025 13:35:36 | 10/04/2025 17:43:01 | 10/02/2025 19:35:36 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6755-P3 @ Sceco | 10/02/2025 11:56:08 | Major | 7654 | CELL OPERATION DEGRADED | 10/02/2025 11:55:59 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6755 | FLM_TE |  |  | PCM-20251002-00001070 | please check jumblers, feeders, connectors and ports for RF and antenna | please check jumblers, feeders, connectors and ports for RF and antenna |  |  |  | API | 10/02/2025 13:35:36 | 10/04/2025 17:33:35 | 10/04/2025 17:42:55 |  |  | 10/04/2025 17:43:01 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000816 | PCM-20251002-00001237 | TT-20251002-01392 | Telecom | Region_6 | FIF1M7046 | FIF0046 | Equipment | BSS_HW_Stuck | Reset BBU | Muhammad Ali | 10/02/2025 13:36:39 | 10/02/2025 15:09:10 | 10/03/2025 01:36:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at FIF1M7046-P2-NCA-L800-SBTS @ Sceco | 10/02/2025 12:02:53 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 12:02:44 | P2 | 4G | dair | Sceco | 5G_Cell SA | FIF1M7046 | FLM_TE |  |  | PCM-20251002-00001193 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/02/2025 13:36:39 | 10/02/2025 13:54:27 | 10/02/2025 15:09:03 |  |  | 10/02/2025 15:09:10 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000823 | PCM-20251002-00001249 | TT-20251001-02147 | Reference_EM | Region_5 | HAJ0322 | HAJ0322 |  |  |  | Muhammad Saleem Iqbal | 10/02/2025 13:39:29 | 10/02/2025 19:12:15 | 10/03/2025 01:39:29 | Commercial Power Failure at HAJ0322-P3_SRANRef NetEco: TT-20251001-02133 @ Sceco | 10/01/2025 22:09:41 | Minor | 65037 | Commercial Power Failure | 10/01/2025 22:09:37 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ0322 | FLM_TE |  |  | PCM-20251002-00001198 | Not related to BO | Not related to BO |  |  |  | API | 10/02/2025 13:39:29 | 10/02/2025 19:12:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000859 | PCM-20251002-00001300 | TT-20251002-01630 | EM | Region_1 | KB2 | KB2 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/02/2025 13:57:39 | 10/03/2025 11:20:18 | 10/02/2025 19:57:39 | Door opening alarm at KB2-Main Shelter-Core-P1 @ Sceco_STB | 10/02/2025 13:56:58 | Major | 65101 | Door opening alarm | 10/02/2025 13:56:56 | P1 | BSC | dammam | Sceco_STB | 2G NSA | KB2 | FLM_EM | [8 empty] | API | 10/02/2025 13:57:39 | 10/03/2025 11:20:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251002000909 | PCM-20251002-00001377 | TT-20251002-01711 | Telecom | Region_4 | RAB0721 | RAB0721 | Equipment | BSS_HW_fault | Replace RF Module | Khizer Hayat | 10/02/2025 14:37:57 | 10/17/2025 12:46:59 | 10/03/2025 02:37:57 | BASE STATION SERVICE PROBLEM (TX out of order) at RAB0721-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/02/2025 14:33:04 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 14:32:59 | P2 | 2G | jeddah | Sceco | LTE_Cell SA | RAB0721 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/02/2025 14:37:57 | 10/02/2025 15:59:43 | 10/03/2025 16:38:57 | 10/03/2025 16:39:19 | 10/03/2025 16:39:23 | 10/17/2025 12:46:59 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002000987 | PCM-20251002-00001547 | TT-20251002-01844 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/02/2025 15:34:17 | 10/02/2025 16:30:01 | 10/03/2025 03:34:17 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/02/2025 15:25:53 | Minor | 7103 | AIRCON 2 FAILURE | 10/02/2025 15:25:43 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/02/2025 15:34:17 | 10/02/2025 16:30:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Reject_FME | CM20251002001006 | PCM-20251002-00001575 | TT-20251002-01872 | Telecom | Region_6 | BSA0098 | BSA0098 |  |  |  | Farhan Ali Khan | 10/02/2025 15:50:18 | 10/07/2025 18:04:46 | 10/02/2025 19:50:18 | PORT_MODULE_OFFLINE at BSA0098_ELC @ Sceco | 10/02/2025 03:44:27 | Critical | 1-63629 | PORT_MODULE_OFFLINE | 10/02/2025 03:41:48 | P1 | 2G | bisha | Sceco | DWDM NSA | BSA0098 | FLM_TE | [5 empty] | 0-ELC(1-B)-1-K1LTXMP-3(RX1/TX1)-CLIENT:1 |  |  | API | 10/02/2025 15:50:18 | 10/02/2025 20:40:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002001117 | PCM-20251002-00001753 | TT-20251002-02043 | EM | Region_2 | SEC0024 | SEC0024 | Enviroment | SCECO_Failure | SCECO auto restored | Saleem Khan Amir Dost | 10/02/2025 16:54:22 | 10/06/2025 19:45:12 | 10/02/2025 20:54:22 | NE_COMMU_GNE_SWITCH at SEC0024_ELC @ Sceco | 10/02/2025 16:52:22 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/02/2025 16:52:18 | P1 | DWDM | riyadh | Sceco | DWDM NSA | SEC0024 | FLM_EM | [5 empty] | NE SEC0024_ELC's current GNE has been switched to standby GNE |  |  | API | 10/02/2025 16:54:22 | 10/03/2025 00:46:19 | 10/06/2025 19:45:04 |  |  | 10/06/2025 19:45:12 |  | Saleem Khan Amir Dost |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251002001137 | PCM-20251002-00001787 | TT-20251002-02069 | Telecom | Region_4 | JED0326 | JED0326 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/02/2025 17:09:17 | 10/02/2025 19:18:06 | 10/03/2025 05:09:17 | PT::: as per BO request FLM need to HC at JED0326 | 10/02/2025 17:09:04 | Minor | 676767671 | Health Check-WO to TE FME | 10/02/2025 17:09:04 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0326 | FLM_TE | [8 empty] | API | 10/02/2025 17:09:17 | 10/02/2025 19:18:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001177 | PCM-20251002-00001850 | TT-20251002-02137 | Reference_telecom | Region_2 | SRIY0183 | SRIY0183 | Equipment | SFP_BTS | Clean SFP | Muhammad Naeem Muhammad Gulzar | 10/02/2025 17:47:57 | 10/15/2025 13:56:07 | 10/02/2025 21:47:57 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN/R2_RY3_HWBSC01 @ Sceco(Ref:TT-20251002-02010) | 10/02/2025 16:44:22 | Critical | 301 | NE Is Disconnected | 10/02/2025 16:44:22 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183 | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183 SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183 Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/02/2025 17:47:57 | 10/15/2025 13:56:07 | [5 empty] | Muhammad Naeem Muhammad Gulzar | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001198 | PCM-20251002-00001879 | TT-20251002-02175 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/02/2025 18:02:34 | 10/20/2025 12:32:24 | 10/02/2025 22:02:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/02/2025 18:01:39 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 18:01:31 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/02/2025 18:02:34 | 10/03/2025 10:12:27 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002001202 | PCM-20251002-00001884 | TT-20251002-02181 | Telecom | Region_1 | DAM0358 | DAM0358 | Equipment | SFP_BTS | Replace SFP | AbdalHafiz Sirageldin Mohamed Yasin | 10/02/2025 18:03:06 | 10/04/2025 11:06:20 | 10/03/2025 00:03:06 | BBU CPRI Interface Error at DAM0358-P2_SRAN @ Sceco | 10/02/2025 17:57:35 | Major | 26234 | BBU CPRI Interface Error | 10/02/2025 17:56:02 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0358 | FLM_TE | [8 empty] | API | 10/02/2025 18:03:06 | 10/02/2025 21:54:43 | 10/04/2025 11:05:41 | 10/04/2025 11:05:44 | 10/04/2025 11:05:47 | 10/04/2025 11:06:20 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001224 | PCM-20251002-00001910 | TT-20251002-02199 | EM | Region_6 | BHAB1M7883 | BHAB0883 |  |  |  | Zia Ur Rahamn | 10/02/2025 18:14:27 | 10/03/2025 05:50:16 | 10/03/2025 06:14:27 | AIRCON 2 FAILURE at BHAB1M7883-G9-L8-SBTS-P3 @ Sceco | 10/02/2025 18:06:18 | Minor | 7103 | AIRCON 2 FAILURE | 10/02/2025 18:06:10 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7883 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/02/2025 18:14:27 | 10/03/2025 05:50:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251002001227 | PCM-20251002-00001916 | TT-20251002-02203 | Reference_telecom | Region_5 | BIK0788 | BIK0788 |  |  |  | Hazem Ali Moustafa Ali | 10/02/2025 18:15:33 | 10/18/2025 03:16:06 | 10/03/2025 00:15:33 | TRX OPERATION DEGRADED at BIK0788-P3 (Ref:TT-20250929-01158) @ Generator_SG | 09/30/2025 03:32:22 | Major | 7607 | TRX OPERATION DEGRADED | 09/30/2025 03:32:18 | P3 | 2G | makkah | Generator_SG | 2G NSA | BIK0788 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/02/2025 18:15:33 | 10/18/2025 03:16:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001328 | PCM-20251002-00002074 | TT-20251002-02361 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/02/2025 19:54:10 | 10/04/2025 10:38:39 | 10/03/2025 01:54:10 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/02/2025 16:54:09 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/02/2025 16:53:57 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/02/2025 19:54:10 | 10/04/2025 10:38:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001354 | PCM-20251002-00002113 | TT-20251002-02306 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/02/2025 20:15:49 | 10/20/2025 12:32:25 | 10/03/2025 00:15:49 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP (Ref::TT-20251001-02241) @ Generator_DG | 10/02/2025 18:00:14 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 18:00:07 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251002-00002009 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/02/2025 20:15:49 | 10/03/2025 10:12:28 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251002001358 | PCM-20251002-00002118 | TT-20251002-02285 | Telecom | Region_4 | TAF1M4383 | TAF2383 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/02/2025 20:17:42 | 10/16/2025 00:08:06 | 10/03/2025 02:17:42 | CELL OPERATION DEGRADED (Failure in optical RP3 interface) at TAF1M4383-P2 @ Sceco | 10/02/2025 18:59:24 | Major | 7654 | CELL OPERATION DEGRADED | 09/05/2025 14:28:21 | P2 | 3G | taif | Sceco | LTE_Cell SA | TAF1M4383 | FLM_TE |  |  | PCM-20251002-00001993 | FLM need to check SFP, Fiber and HW at site. | FLM need to check SFP, Fiber and HW at site. |  |  |  | API | 10/02/2025 20:17:42 | 10/04/2025 11:26:19 | 10/16/2025 00:08:01 |  |  | 10/16/2025 00:08:06 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001402 | PCM-20251002-00002178 | TT-20251002-02457 | Reference_telecom | Region_6 | MKW2051 | MKW2051 |  |  |  | SHAH KHALID | 10/02/2025 21:04:55 | 10/02/2025 22:23:57 | 10/03/2025 09:04:55 | LagPortDown observed in MKW2051_01 towards 10.221.243.56 @ Generator_SG | 10/02/2025 09:06:50 | Minor |  | LagPortDown | 10/02/2025 09:04:40 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2051 | FLM_TE | [8 empty] | API | 10/02/2025 21:04:55 | 10/02/2025 22:23:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251002001525 | PCM-20251002-00002363 | TT-20251002-02639 | Telecom | Region_4 | SJED0655 | SJED0655 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/02/2025 23:35:17 | 10/03/2025 15:14:42 | 10/03/2025 11:35:17 | SJED1W0657 Complete Down | 10/02/2025 23:28:08 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/02/2025 23:28:08 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0657 | FLM_EM | SJED0655 | Dear team , Hub: SJED0655 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251002-00002356 | Dear team , Hub: SJED0655 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: SJED0655 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/02/2025 23:35:17 | 10/03/2025 15:14:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251002001534 | PCM-20251002-00002381 | TT-20251002-02668 | Telecom | Region_4 | JED0107 | JED0107 | Equipment | BTS_Cable | Reconnect Sync Cable | Mohammed Ramadan A Abu Abid | 10/02/2025 23:53:54 | 10/19/2025 10:35:45 | 10/03/2025 05:53:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0107-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P1-VIP @ Sceco | 10/02/2025 23:53:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/02/2025 23:52:56 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0107 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/02/2025 23:53:54 | 10/03/2025 09:56:52 | 10/19/2025 10:35:23 |  |  | 10/19/2025 10:35:45 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000028 | PCM-20251003-00000038 | TT-20251003-00039 | EM | Region_6 | MKW1M8121 | MKW2121 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/03/2025 00:43:29 | 10/03/2025 23:09:06 | 10/03/2025 12:43:29 | RECTIFIER MODULE FAILURE at MKW1M8121-L8-L18-SBTS-P3 @ Generator_SG | 10/03/2025 00:35:13 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/03/2025 00:35:03 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8121 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/03/2025 00:43:29 | 10/03/2025 23:09:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Departed | CM20251003000065 | PCM-20251003-00000097 | TT-20251003-00065 | Telecom | Region_4 | JED1M7103 | JED0103 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 10/03/2025 01:30:23 | 10/15/2025 23:48:57 | 10/03/2025 13:30:23 | BASE STATION ANTENNA LINE PROBLEM at JED1M7103-P2-CA-L900-L800-SBTS @ Sceco | 10/03/2025 01:00:39 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/03/2025 01:00:33 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7103 | FLM_TE |  |  | PCM-20251003-00000060 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/03/2025 01:30:23 | 10/05/2025 14:56:55 | 10/15/2025 23:48:34 | 10/15/2025 23:48:57 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251003000073 | PCM-20251003-00000109 | TT-20251003-00111 | EM | Region_2 | U2000 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/03/2025 01:45:59 | 10/03/2025 01:45:59 | 10/03/2025 13:45:59 | Subscription and Support Service Has Expired at U2000 NFV @ Sceco_STB | 10/03/2025 01:36:14 | Minor | 4008 | Subscription and Support Service Has Expired | 10/03/2025 01:35:33 | P1 | Performance | riyadh | Sceco_STB | 2G NSA | U2000 | FLM_EM | [8 empty] | API | 10/03/2025 01:45:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000078 | PCM-20251003-00000125 | TT-20251003-00138 | EM | Region_1 | Sk1 | SK1 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/03/2025 02:04:05 | 10/06/2025 16:35:13 | 10/03/2025 06:04:05 | Door opening alarm at SK1-Shelter 1-WDM-HUB-Core-P1 @ Sceco_STB | 10/03/2025 02:03:30 | Critical | 65101 | Door opening alarm | 10/03/2025 02:02:47 | P1 | BSC | sakaka | Sceco_STB | 2G NSA | SK1 | FLM_EM | [8 empty] | API | 10/03/2025 02:04:05 | 10/06/2025 16:35:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000086 | PCM-20251003-00000136 | TT-20251003-00128 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/03/2025 02:10:17 | 10/20/2025 12:32:26 | 10/03/2025 08:10:17 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/03/2025 01:53:54 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/03/2025 01:53:45 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251003-00000120 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/03/2025 02:10:17 | 10/03/2025 10:12:32 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000089 | PCM-20251003-00000141 | TT-20251003-00152 | EM | Region_1 | R1_HF_HWBSC01 | HF1 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/03/2025 02:18:02 | 10/03/2025 14:07:25 | 10/03/2025 06:18:02 | Intruder Alarm(SH1) at R1_HF_HWBSC01 @ Sceco_STB | 10/03/2025 02:17:40 | Critical | 65334 | Intruder Alarm(SH1) | 10/03/2025 02:17:37 | P1 | BSC | hafouf | Sceco_STB | 2G NSA | R1_HF_HWBSC01 | FLM_EM | [8 empty] | API | 10/03/2025 02:18:02 | 10/03/2025 14:05:21 | 10/03/2025 14:07:17 |  |  | 10/03/2025 14:07:25 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000135 | PCM-20251003-00000244 | TT-20251003-00271 | Reference_telecom | Region_4 | JED0245-ZJe08-CSG-03 | JED0245 |  |  |  | MALIK ATIF ZAMAN | 10/03/2025 03:58:11 | 10/03/2025 10:12:32 | 10/03/2025 15:58:11 | MW Link down at JED0245-ZJe08-CSG-03 to JED0676-ZJe08-CSG-04 REF:TT-20250930-02482 @ Sceco | 09/29/2025 02:09:19 | Minor | 101-2505274 | Physical Port Down | 09/29/2025 02:09:11 | P1 | IPRAN | jeddah | Sceco | IPRAN SA | JED0245-ZJe08-CSG-03 to JED0676-ZJe08-CSG-04 | FLM_TE | [8 empty] | API | 10/03/2025 03:58:11 | 10/03/2025 10:12:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000141 | PCM-20251003-00000254 | TT-20251003-00278 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/03/2025 04:09:02 | 10/04/2025 10:38:40 | 10/03/2025 10:09:02 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/03/2025 01:07:31 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/03/2025 01:08:45 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/03/2025 04:09:02 | 10/04/2025 10:38:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000192 | PCM-20251003-00000355 | TT-20251003-00368 | Reference_telecom | Region_6 | BHAB2091 | BHAB2091 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Manzoor Ahmed | 10/03/2025 05:54:25 | 10/23/2025 23:02:36 | 10/03/2025 17:54:25 | Degrade observed in BHAB2091_01 towards 10.221.242.151 @ Generator_SG | 10/02/2025 17:56:14 | Minor |  | Degrade | 10/02/2025 17:54:13 | P3 | 2G | Baha | Generator_SG | TX NSA | BHAB2091 | FLM_TE | [8 empty] | API | 10/03/2025 05:54:25 | 10/03/2025 12:47:24 | 10/23/2025 23:02:21 |  |  | 10/23/2025 23:02:36 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000221 | PCM-20251003-00000399 | TT-20251003-00417 | Reference_telecom | Region_6 | MHL0123 | MHL0123 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/03/2025 06:53:18 | 10/03/2025 14:02:53 | 10/03/2025 18:53:18 | DemFail observed in MHL0123 towards 10.21.69.184 @ Sceco | 10/02/2025 18:53:19 | Minor |  | DemFail | 10/02/2025 18:53:11 | P1 | 2G | mohail | Sceco | TX NSA | MHL0123 | FLM_TE | [8 empty] | API | 10/03/2025 06:53:18 | 10/03/2025 14:02:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000222 | PCM-20251003-00000402 | TT-20251003-00420 | MW_HC | Region_4 | JED0938 | JED0938 |  |  |  | MALIK ATIF ZAMAN | 10/03/2025 06:55:33 | 10/03/2025 10:12:33 | 10/03/2025 18:55:33 | As BO Requested MW HC For Link JED0938 – JED0536 | 10/03/2025 06:54:38 | Minor | 113388 | LOF | 10/03/2025 06:54:38 | P2 | 2G | jeddah | Sceco | TX NSA | JED0938 – JED0536 | FLM_TE | [5 empty] | As BO Requested MW HC For Link JED0938 – JED0536 |  |  | API | 10/03/2025 06:55:33 | 10/03/2025 10:12:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000245 | PCM-20251003-00000431 | TT-20251003-00456 | Reference_telecom | Region_4 | JED1M7490 | JED0490 | Equipment | SFP_BTS | Replace SFP | Asad Ullah Rahim Said | 10/03/2025 07:17:04 | 10/06/2025 12:47:26 | 10/03/2025 13:17:04 | BASE STATION HARDWARE PROBLEM(Nokia MN BTS SFP validation failure) at JED1M7490-CA-L900-L800-SBTS(Ref:TT-20250919-01691) | 09/20/2025 02:49:57 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 09/20/2025 02:49:57 | P2 | 4G | jeddah | Sceco | LTE SA | JED1M7490-CA-L900-L800-SBTS | FLM_TE | [8 empty] | API | 10/03/2025 07:17:04 | 10/06/2025 11:52:53 | 10/06/2025 12:01:42 | 10/06/2025 12:01:44 | 10/06/2025 12:01:48 | 10/06/2025 12:47:26 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20250906000940 | PCM-20250906-00001515 | TT-20250906-01453 | EM | Region_4 | JED0976 | JED0976 |  |  |  | Ramadan Mohamed Sabri Mohamed | 09/06/2025 16:23:20 | 10/05/2025 15:18:52 | 09/07/2025 04:23:20 | RECTIFIER MODULE FAILURE at JED1M7976-CA-L800-SBTS @ Sceco | 09/06/2025 16:14:53 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/06/2025 16:14:41 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7976 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/06/2025 16:23:20 | 09/06/2025 17:13:26 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250906001073 | PCM-20250906-00001715 | TT-20250906-01654 | EM | Region_4 | JED0412 | JED0412 |  |  |  | Amer Attallah Awadallah | 09/06/2025 18:00:50 | 10/05/2025 15:18:53 | 09/07/2025 06:00:50 | AIRCON 2 FAILURE at JED1M7412-CA-L900-L800-SBTS @ Sceco | 09/06/2025 17:54:09 | Minor | 7103 | AIRCON 2 FAILURE | 09/06/2025 17:52:08 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7412 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 09/06/2025 18:00:50 | 09/06/2025 22:24:51 | [6 empty] | SCECO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250906001109 | PCM-20250906-00001763 | TT-20250906-01696 | EM | Region_6 | MKW9706 | MKW9706 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 09/06/2025 18:27:05 | 09/20/2025 23:40:03 | 09/06/2025 22:27:05 | Input at MKW9706_1 on 10.154.162.17 @ Sceco | 09/06/2025 18:24:48 | Critical | Input | Input | 09/06/2025 18:19:14 | P3 | Repeater | makhwa | Sceco | TX NSA | MKW9706 | FLM_EM | [8 empty] | API | 09/06/2025 18:27:05 | 09/18/2025 01:22:33 | 09/20/2025 23:39:53 |  |  | 09/20/2025 23:40:03 |  | Arif Ullah Shah | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250907001677 | PCM-20250907-00002537 | TT-20250907-02407 | EM | Region_4 | JED0326 | JED0326 |  |  |  | Muhammad Arqam Muhammad Dawood | 09/07/2025 23:43:00 | 10/05/2025 15:18:55 | 09/08/2025 11:43:00 | RECTIFIER MODULE FAILURE at JED1M7326-CA-L900-L800-SBTS @ Sceco | 09/07/2025 23:34:44 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/07/2025 23:34:39 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7326 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/07/2025 23:43:00 | 09/08/2025 13:51:09 | [6 empty] | SCECO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250909000335 | PCM-20250909-00000731 | TT-20250909-00853 | EM | Region_4 | JED0080 | JED0080 |  |  |  | Muhammad Arqam Muhammad Dawood | 09/09/2025 08:17:20 | 09/28/2025 17:44:52 | 09/09/2025 14:17:20 | RECTIFIER MODULE FAILURE at JED1M7080-P1-DIA-CA-L900-L800-SBTS @ Sceco | 09/09/2025 08:08:47 | Major | 7103 | RECTIFIER MODULE FAILURE | 09/09/2025 08:08:39 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7080 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/09/2025 08:17:20 | 09/09/2025 15:11:49 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250909000404 | PCM-20250909-00000888 | TT-20250909-00950 | EM | Region_4 | SQR9447 | SQR9447 |  |  |  | Faiz Muhammad Ghulam Sarwar | 09/09/2025 09:27:10 | 09/09/2025 14:40:37 | 09/09/2025 13:27:10 | NEC Eband GEN Rectifier & AIR COND alarm at site SQR9447 | 09/09/2025 09:15:26 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 09/09/2025 09:15:26 | P3 | Repeater | adam | Generator_DG | TX NSA | SQR9447 | FLM_EM | [5 empty] | NEC Eband GEN Rectifier & AIR COND alarm at site SQR9447 |  |  | API | 09/09/2025 09:27:10 | 09/09/2025 14:40:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250909000427 | PCM-20250909-00000930 | TT-20250828-01389 | Telecom | Region_4 | JED0981 | JED0981 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 09/09/2025 09:42:51 | 09/09/2025 16:29:51 | 09/09/2025 21:42:51 | PT::FLM need to perform HC at JED0981 (Bo request) | 08/28/2025 14:10:34 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/28/2025 14:10:34 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0981 | FLM_EM |  |  | PCM-20250828-00001354 | Load issue | Load issue |  |  |  | API | 09/09/2025 09:42:51 | 09/09/2025 16:29:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250909000433 | PCM-20250909-00000929 | TT-20250824-01451 | Telecom | Region_4 | JED2625 | JED2625 |  |  |  | Sajid Nazir Muhammad Nazir | 09/09/2025 09:43:00 | 09/09/2025 16:00:07 | 09/09/2025 21:43:00 | PT::As per Bo request FLM need to perform HC at JED1MN2625 | 08/24/2025 12:41:08 | Minor | 7604 | BASE STATION OPERATION DEGRADED | 08/24/2025 12:41:08 | P3 | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1MN2625 | FLM_EM |  |  | PCM-20250824-00001530 | Load issue | Load issue |  |  |  | API | 09/09/2025 09:43:00 | 09/09/2025 16:00:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur
Delivered | CM20250909000880 | PCM-20250909-00001597 | TT-20250909-01534 | EM | Region_4 | AQA9452 | AQA9452 |  |  |  | Mohamed Ahmed Kassem Embarak | 09/09/2025 14:14:20 | 09/09/2025 15:46:09 | 09/09/2025 18:14:20 | NEC Eband observing AC Rectifier & LOW Battery alarm at site AQA9452 | 09/09/2025 14:06:24 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 09/09/2025 14:06:24 | P1 | Repeater | taif | Generator_DG | TX NSA | AQA9452 | FLM_EM | [5 empty] | NEC Eband observing AC Rectifier & LOW Battery alarm at site AQA9452 |  |  | API | 09/09/2025 14:14:20 | 09/09/2025 15:46:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20250909001007 | PCM-20250909-00001788 | TT-20250909-01727 | Reference_EM | Region_4 | JED0948 | JED0948 |  |  |  | Nabil Nazih Mohamoud Ahmed | 09/09/2025 15:44:15 | 09/28/2025 17:44:59 | 09/10/2025 03:44:15 | SHELTER DOOR OPEN at JED0948-GSM-P3 (Ref::CRQ000000530570) @ Sceco | 09/09/2025 13:38:23 | Minor | 7103 | SHELTER DOOR OPEN | 09/09/2025 13:17:21 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0948 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 09/09/2025 15:44:15 | 09/09/2025 19:21:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250910000328 | PCM-20250910-00000670 | TT-20250910-00587 | EM | Region_4 | JED0166 | JED0166 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 09/10/2025 08:00:01 | 10/05/2025 15:18:56 | 09/10/2025 20:00:01 | AIRCON 1 FAILURE at JED0166-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 09/10/2025 07:52:12 | Minor | 7103 | AIRCON 1 FAILURE | 09/10/2025 07:51:21 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0166 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 09/10/2025 08:00:01 | 09/11/2025 09:23:23 | [6 empty] | SCECO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250912000607 | PCM-20250912-00001107 | TT-20250912-01117 | EM | Region_4 | TURY0830 | TURY0830 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 09/12/2025 14:58:00 | 10/09/2025 08:20:22 | 09/13/2025 02:58:00 | HIGH TEMPERATURE 32 DEGREE C at TURY0830-GSM-P3 @ Sceco | 09/12/2025 14:51:08 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 09/12/2025 14:49:33 | P3 | 2G | taif | Sceco | 2G NSA | TURY0830 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 09/12/2025 14:58:00 | 10/06/2025 14:46:38 | 10/09/2025 08:20:08 |  |  | 10/09/2025 08:20:22 |  | Afzal Hussain Anwar Ul Haq | SCECO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250912000613 | PCM-20250912-00001113 | TT-20250912-01120 | EM | Region_4 | TURY0829 | TURY0829 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 09/12/2025 14:59:00 | 10/09/2025 08:21:45 | 09/13/2025 02:59:00 | AIRCON 1 FAILURE at TURY0829-GSM-P3 @ Sceco | 09/12/2025 14:50:40 | Minor | 7103 | AIRCON 1 FAILURE | 09/12/2025 14:50:35 | P3 | 2G | taif | Sceco | 2G NSA | TURY0829 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 09/12/2025 14:59:00 | 09/14/2025 08:40:04 | 10/09/2025 08:21:34 |  |  | 10/09/2025 08:21:45 |  | Afzal Hussain Anwar Ul Haq | SCECO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250913000523 | PCM-20250913-00000881 | TT-20250913-00745 | EM | Region_2 | LIQ0551 | LIQ0551 | Enviroment | Air Condition | Change compressor | Mohamed Moustafa Aboelmagd Hefny | 09/13/2025 11:09:30 | 10/19/2025 07:41:35 | 09/13/2025 23:09:30 | Fire Alarm at LIQ0551-P2_SRAN @ Sceco | 09/13/2025 10:59:59 | Minor | 65119 | Fire Alarm | 09/13/2025 10:59:06 | P2 | SRAN | buraidah | Sceco | 2G NSA | LIQ0551 | FLM_EM | [8 empty] | API | 09/13/2025 11:09:30 | 09/13/2025 14:18:34 | 10/19/2025 07:41:20 |  |  | 10/19/2025 07:41:35 |  | Mohamed Moustafa Aboelmagd Hefny | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250913001268 | PCM-20250913-00002089 | TT-20250913-01823 | Reference_EM | Region_1 | HMBY0421 | HMBY0421 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 09/13/2025 22:21:05 | 09/14/2025 14:16:19 | 09/14/2025 10:21:05 | Minor Rec. alarm at HMBY2M1421-P3 @ Sceco | 09/13/2025 22:10:35 | Minor | 65108 | Minor Rec. alarm | 09/13/2025 22:10:31 | P3 | 2G | dammam | Sceco | 2G NSA | HMBY2M1421 | FLM_EM | [8 empty] | API | 09/13/2025 22:21:05 | 09/13/2025 22:38:54 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250914001086 | PCM-20250914-00001982 | TT-20250914-01811 | EM | Region_2 | BUR0034 | BUR0034 |  |  |  | Shahid Ahmed Shah Nawaz | 09/14/2025 18:18:35 | 09/22/2025 08:28:53 | 09/15/2025 06:18:35 | Air condition 1 failure alarm at BUR0034-P2_SRAN @ Sceco | 09/14/2025 18:12:32 | Minor | 65104 | Air condition 1 failure alarm | 09/14/2025 18:08:06 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0034 | FLM_EM | [8 empty] | API | 09/14/2025 18:18:35 | 09/22/2025 08:28:53 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250914001264 | PCM-20250914-00002217 | TT-20250914-02066 | EM | Region_4 | JDJZ0761 | JDJZ0761 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 09/14/2025 19:33:35 | 10/03/2025 22:18:04 | 09/15/2025 07:33:35 | As per BO request NOKIA MW link JDJZ0761 | 09/14/2025 19:32:21 | Minor | 113388 | LOF | 09/14/2025 19:32:24 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDJZ0761 | FLM_EM | [8 empty] | API | 09/14/2025 19:33:35 | 10/03/2025 22:18:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20250916001197 | PCM-20250916-00002045 | TT-20250916-01879 | EM | Region_2 | KHJ0309 | KHJ0309 |  |  |  | Mohamed Talaat Mohamed Tawfik | 09/16/2025 14:45:17 | 09/28/2025 11:46:00 | 09/17/2025 02:45:17 | Fire Alarm at KHJ0309-P2_SRAN @ Sceco | 09/16/2025 14:36:58 | Minor | 65119 | Fire Alarm | 09/16/2025 14:34:43 | P2 | SRAN | al kharj | Sceco | 2G NSA | KHJ0309 | FLM_EM | [8 empty] | API | 09/16/2025 14:45:17 | 09/17/2025 02:36:41 | [6 empty] | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250917000855 | PCM-20250917-00001390 | TT-20250917-01298 | EM | Region_1 | HMBY0426 | HMBY0426 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 09/17/2025 14:37:20 | 10/06/2025 17:59:31 | 09/18/2025 02:37:20 | Door opening alarm at HMBY0426-P3_SRAN @ Sceco | 09/17/2025 14:36:46 | Minor | 65101 | Door opening alarm | 09/17/2025 14:14:09 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY0426 | FLM_EM | [8 empty] | API | 09/17/2025 14:37:20 | 09/17/2025 22:37:01 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250917000858 | PCM-20250917-00001395 | TT-20250917-01300 | EM | Region_1 | HMBY0426 | HMBY0426 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 09/17/2025 14:38:55 | 10/06/2025 17:59:32 | 09/18/2025 02:38:55 | Mains Failure at HMBY0426-P3_SRAN @ Sceco | 09/17/2025 14:36:46 | Minor | 65109 | Mains Failure | 09/17/2025 14:14:09 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY0426 | FLM_EM | [8 empty] | API | 09/17/2025 14:38:55 | 09/17/2025 22:37:01 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20250918000864 | PCM-20250918-00001510 | TT-20250918-01410 | EM | Region_4 | MLJI9438 | MLJI9438 |  |  |  | Faiz Muhammad Ghulam Sarwar | 09/18/2025 13:41:10 | 09/18/2025 13:41:10 | 09/18/2025 17:41:10 | NEC Eband observing AIRCON FAIL at MLJI9438 | 09/18/2025 13:26:19 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 09/18/2025 13:39:52 | P3 | Repeater | adam | Generator_SG | TX NSA | MLJI9438 | FLM_EM | [5 empty] | NEC Eband observing AIRCON FAIL at MLJI9438 |  |  | API | 09/18/2025 13:41:10 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250918001450 | PCM-20250918-00002429 | TT-20250918-02302 | EM | Region_4 | JED0610 | JED0610 |  |  |  | Ahmed Gamal Mohamed Farag | 09/18/2025 21:05:21 | 10/05/2025 15:18:59 | 09/19/2025 09:05:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M7610-CA-L900-L800-SBTS @ Sceco | 09/18/2025 20:57:08 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/18/2025 20:56:55 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7610 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/18/2025 21:05:21 | 09/19/2025 00:56:52 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250918001481 | PCM-20250918-00002484 | TT-20250918-02347 | Reference_EM | Region_1 | RFH0268 | RFH0268 |  |  |  | Elsaid Adel Mohamed Abouhegara | 09/18/2025 21:46:40 | 09/21/2025 11:47:19 | 09/19/2025 09:46:40 | Generator Failure(SH1) at RFH2M7268-P3-PC @ Power Cube | 09/18/2025 21:36:25 | Minor | 65046 | Generator Failure(SH1) | 09/18/2025 21:36:21 | P3 | 4G | quriyat | Power Cube | 2G NSA | RFH2M7268 | FLM_EM | [8 empty] | API | 09/18/2025 21:46:40 | 09/21/2025 11:47:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250920000134 | PCM-20250920-00000234 | TT-20250920-00201 | EM | Region_6 | DAR0916 | DAR0916 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Tayyab | 09/20/2025 03:24:16 | 10/05/2025 13:52:28 | 09/20/2025 15:24:16 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at DAR0916-GSM-UMTS-P2 @ Sceco | 09/20/2025 03:13:35 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 09/20/2025 03:13:28 | P2 | 2G | dair | Sceco | 2G NSA | DAR0916 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 09/20/2025 03:24:16 | 10/04/2025 09:25:04 | 10/05/2025 13:52:13 |  |  | 10/05/2025 13:52:28 |  | Muhammad Tayyab | Latis_Operation |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250920001067 | PCM-20250920-00001788 | TT-20250920-01662 | Reference_EM | Region_2 | QSMD0597 | QSMD0597 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shazlly Mahmoud Abouzied Mahmoud | 09/20/2025 16:02:10 | 10/11/2025 17:57:08 | 09/21/2025 04:02:10 | Generator failure at QSMD0597-P2_SRAN @ Generator_SG | 09/20/2025 15:51:45 | Minor | 65114 | Generator failure | 09/20/2025 15:51:42 | P2 | SRAN | buraidah | Generator_SG | 2G NSA | QSMD0597 | FLM_EM | [8 empty] | API | 09/20/2025 16:02:10 | 09/20/2025 20:55:02 | 10/11/2025 17:56:50 |  |  | 10/11/2025 17:57:08 |  | Shazlly Mahmoud Abouzied Mahmoud | Huawei_RO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250921000874 | PCM-20250921-00001442 | TT-20250921-01310 | EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ibrahim Ù Abdulfttah Ibrahim | 09/21/2025 12:45:35 | 10/06/2025 17:59:34 | 09/22/2025 00:45:35 | Door opening alarm at ARM2M1871-P3 @ Sceco | 09/21/2025 12:44:49 | Minor | 65101 | Door opening alarm | 09/21/2025 12:44:46 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 09/21/2025 12:45:35 | 09/29/2025 23:18:04 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250921000897 | PCM-20250921-00001479 | TT-20250921-01343 | Reference_EM | Region_1 | ARM0873 | ARM0873 |  |  |  | Ibrahim Ù Abdulfttah Ibrahim | 09/21/2025 12:55:56 | 10/06/2025 17:59:35 | 09/22/2025 00:55:56 | Air-condition #2 failure alarm at ARM2M1873-P3 @ Sceco | 09/21/2025 12:45:30 | Minor | 65105 | Air-condition #2 failure alarm | 09/21/2025 12:45:26 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1873 | FLM_EM | [8 empty] | API | 09/21/2025 12:55:56 | 09/29/2025 23:18:05 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250921001373 | PCM-20250921-00002269 | TT-20250921-02032 | EM | Region_4 | JED0023 | JED0023 | Enviroment | SCECO_Failure | SCECO auto restored | Amr Sherif Gabber Ahmed | 09/21/2025 17:33:50 | 09/28/2025 23:37:45 | 09/21/2025 23:33:50 | GENERATOR1 + GENERATOR 2 FAILURE at JED0023-G9-L8-L18-L21-NR2.6-P1-VIP-ARP-DIA-HUB-SBTS @ Sceco_STB | 09/21/2025 17:25:32 | Major | 7103 | GENERATOR1 + GENERATOR 2 FAILURE | 09/21/2025 17:25:22 | VIP | 2G | jeddah | Sceco_STB | 2G NSA | JED0023 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR 2 FAILURE |  |  | API | 09/21/2025 17:33:50 | 09/21/2025 21:35:29 | 09/28/2025 23:37:35 |  |  | 09/28/2025 23:37:45 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250921001529 | PCM-20250921-00002450 | TT-20250921-02068 | Telecom | Region_2 | RIY0336 | RIY0336 |  |  |  | Adham Adham Hassan Farghal | 09/21/2025 18:14:40 | 09/21/2025 20:38:59 | 09/22/2025 06:14:40 | HC for site RIY0336 | 09/21/2025 17:57:51 | Minor | 676767672 | Health Check-WO to TE FME | 09/21/2025 17:57:54 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0336 | FLM_EM |  |  | PCM-20250921-00002334 | Door open , AC not working | Door open , AC not working |  |  |  | API | 09/21/2025 18:14:40 | 09/21/2025 20:38:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250922000899 | PCM-20250922-00001524 | TT-20250922-01519 | EM | Region_4 | MKMD0554 | MKMD0554 |  |  |  | Hamza Ahmed Aly Sawy | 09/22/2025 16:10:55 | 09/28/2025 17:45:01 | 09/23/2025 04:10:55 | HIGH TEMPERATURE 32 DEGREE C at MKMD1M7554-L800-P2-USF @ Sceco | 09/22/2025 16:03:04 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 09/22/2025 16:02:09 | P2 | 4G | jeddah | Sceco | LTE NSA | MKMD1M7554 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 09/22/2025 16:10:55 | 09/23/2025 02:24:26 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20250923000016 | PCM-20250923-00000028 | TT-20250923-00023 | EM | Region_4 | TURY0828 | TURY0828 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 09/23/2025 00:19:05 | 10/24/2025 02:59:58 | 09/23/2025 12:19:05 | HIGH TEMPERATURE 32 DEGREE C at TURY0828-GSM-P3 @ Generator_SG | 09/23/2025 00:10:31 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 09/23/2025 00:10:24 | P3 | 2G | taif | Generator_SG | 2G NSA | TURY0828 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 09/23/2025 00:19:05 | 09/23/2025 01:08:13 | 10/24/2025 02:59:50 |  |  | 10/24/2025 02:59:58 |  | Afzal Hussain Anwar Ul Haq | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250923000471 | PCM-20250923-00000722 | TT-20250923-00837 | EM | Region_4 | JED0609 | JED0609 |  |  |  | Ramadan Mohamed Sabri Mohamed | 09/23/2025 11:33:15 | 10/05/2025 15:19:00 | 09/23/2025 23:33:15 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M7609-P3-CA-L900-L800-SBTS @ Sceco | 09/23/2025 11:25:01 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/23/2025 11:24:54 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7609 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/23/2025 11:33:15 | 09/23/2025 12:30:30 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250923001076 | PCM-20250923-00001758 | TT-20250923-01712 | Telecom | Region_2 | RIY2909 | RIY2909 |  |  |  | Moin Uddin | 09/23/2025 19:45:41 | 09/24/2025 09:35:33 | 09/24/2025 07:45:41 | HC TT for RIY2909,RIY2913 | 09/23/2025 19:19:10 | Minor | 676767672 | Health Check-WO to TE FME | 09/23/2025 19:19:10 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2909,RIY2913 | FLM_EM |  |  | PCM-20250923-00001743 | suspected power issue at site RIY2909 | suspected power issue at site RIY2909 |  |  |  | API | 09/23/2025 19:45:41 | 09/24/2025 09:35:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250923001080 | PCM-20250923-00001762 | TT-20250923-01704 | Telecom | Region_2 | RIY2033 | RIY2033 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 09/23/2025 19:46:50 | 09/23/2025 19:48:29 | 09/24/2025 07:46:50 | HC TT for RIY2033 | 09/23/2025 19:17:20 | Minor | 676767672 | Health Check-WO to TE FME | 09/23/2025 19:17:20 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2033 | FLM_EM |  |  | PCM-20250923-00001746 | suspected power at RIY2135 | suspected power at RIY2135 |  |  |  | API | 09/23/2025 19:46:50 | 09/23/2025 19:48:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250925000143 | PCM-20250925-00000461 | TT-20250925-00648 | EM | Region_4 | JED2064 | JED2064 |  |  |  | Ramadan Mohamed Sabri Mohamed | 09/25/2025 03:36:21 | 10/05/2025 15:19:08 | 09/25/2025 15:36:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8064-L800-CA-SBTS-P3 @ Sceco | 09/25/2025 03:29:31 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/25/2025 03:27:32 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8064 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/25/2025 03:36:21 | 09/27/2025 12:48:35 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20250925000335 | PCM-20250925-00000789 | TT-20250925-01023 | EM | Region_4 | JED0279 | JED0279 |  |  |  | Muhammad Arqam Muhammad Dawood | 09/25/2025 08:38:05 | 10/05/2025 15:19:04 | 09/25/2025 14:38:05 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at JED1M7279-CA-L1800-L800-SBTS-FWA-P1-VIP @ Sceco | 09/25/2025 08:30:03 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 09/25/2025 08:29:41 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7279 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 09/25/2025 08:38:05 | [7 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250925001273 | PCM-20250925-00002194 | TT-20250925-02381 | EM | Region_2 | AFF0521 | AFF0521 |  |  |  | Moustafa Elzaafarany Abdellah | 09/25/2025 17:59:05 | 10/06/2025 13:35:12 | 09/26/2025 05:59:05 | Fire Alarm at AFF0521-P2_SRAN @ Sceco | 09/25/2025 17:49:24 | Minor | 65119 | Fire Alarm | 09/25/2025 17:48:23 | P2 | SRAN | dawadmi | Sceco | 2G NSA | AFF0521 | FLM_EM | [8 empty] | API | 09/25/2025 17:59:05 | 09/26/2025 11:11:54 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250925001362 | PCM-20250925-00002339 | TT-20250925-02532 | EM | Region_2 | BUR0033 | BUR0033 |  |  |  | Farman Ullah Muhammad Nazir | 09/25/2025 19:13:55 | 10/06/2025 13:35:14 | 09/26/2025 07:13:55 | high temprature 32 at BUR0033-P2_SRAN @ Sceco | 09/25/2025 19:07:25 | Minor | 65102 | high temprature 32 | 09/25/2025 19:03:35 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0033 | FLM_EM | [8 empty] | API | 09/25/2025 19:13:55 | 09/28/2025 19:32:35 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250926001190 | PCM-20250926-00001890 | TT-20250926-01754 | EM | Region_4 | AQA9452 | AQA9452 |  |  |  | Mohamed Ahmed Kassem Embarak | 09/26/2025 23:00:01 | 09/26/2025 23:52:53 | 09/27/2025 03:00:01 | NEC Eband observing Low Battery & GEN LOW FUEL alarms at site AQA9452 | 09/26/2025 22:51:22 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 09/26/2025 22:51:22 | P1 | Repeater | taif | Generator_DG | TX NSA | AQA9452 | FLM_EM | [5 empty] | NEC Eband observing Low Battery & GEN LOW FUEL alarms at site AQA9452 |  |  | API | 09/26/2025 23:00:01 | 09/26/2025 23:52:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20250928000094 | PCM-20250928-00000216 | TT-20250928-00195 | EM | Region_4 | JED2299 | JED2299 |  |  |  | Sajid Nazir Muhammad Nazir | 09/28/2025 02:55:51 | 10/05/2025 15:19:09 | 09/28/2025 14:55:51 | RECTIFIER MAINS POWER FAILURE at JED1M8299-P3-CA-L800 @ Sceco | 09/28/2025 02:49:50 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 09/28/2025 02:47:28 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8299 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 09/28/2025 02:55:51 | 09/28/2025 07:40:39 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20250928000099 | PCM-20250928-00000221 | TT-20250928-00201 | EM | Region_4 | JED2146 | JED2146 |  |  |  | Mohammed Ramadan A Abu Abid | 09/28/2025 02:57:56 | 10/13/2025 13:28:16 | 09/28/2025 14:57:56 | ac at JED1M8146-P3-CA-L800 @ Sceco | 09/28/2025 02:51:50 | Minor | 7103 | ac | 09/28/2025 02:49:28 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8146 | FLM_EM | [5 empty] | ac |  |  | API | 09/28/2025 02:57:56 | 10/13/2025 12:17:16 | 10/13/2025 13:22:31 | 10/13/2025 13:22:54 | 10/13/2025 13:28:16 |  |  |  | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250928000117 | PCM-20250928-00000245 | TT-20250928-00222 | EM | Region_4 | JED2861 | JED2861 |  |  |  | Sajid Nazir Muhammad Nazir | 09/28/2025 03:19:09 | 10/05/2025 15:19:10 | 09/28/2025 15:19:09 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8861-P3-CA-L800 @ Sceco | 09/28/2025 03:11:08 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/28/2025 03:10:39 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8861 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/28/2025 03:19:09 | 09/28/2025 07:40:40 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250928000119 | PCM-20250928-00000248 | TT-20250928-00226 | EM | Region_4 | JED2137 | JED2137 |  |  |  | Amer Attallah Awadallah | 09/28/2025 03:20:06 | 10/05/2025 15:19:13 | 09/28/2025 15:20:06 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8137-CA-L800-SBTS-P3 @ Sceco | 09/28/2025 03:12:27 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/28/2025 03:11:22 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8137 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/28/2025 03:20:06 | 09/28/2025 11:53:09 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250928000121 | PCM-20250928-00000250 | TT-20250928-00229 | EM | Region_4 | JED2185 | JED2185 |  |  |  | Sajid Nazir Muhammad Nazir | 09/28/2025 03:20:41 | 10/05/2025 15:19:11 | 09/28/2025 15:20:41 | RECTIFIER MODULE FAILURE at JED2185-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 09/28/2025 03:12:31 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/28/2025 03:11:54 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2185 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/28/2025 03:20:41 | 09/28/2025 07:40:40 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250928000122 | PCM-20250928-00000252 | TT-20250928-00231 | EM | Region_4 | JED2999 | JED2999 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 09/28/2025 03:21:07 | 10/05/2025 15:19:30 | 09/28/2025 15:21:07 | RECTIFIER MODULE FAILURE at JED2999-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Generator_SG | 09/28/2025 03:13:19 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/28/2025 03:12:49 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2999 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/28/2025 03:21:07 | 10/03/2025 22:18:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250928000123 | PCM-20250928-00000253 | TT-20250928-00232 | EM | Region_4 | JED2288 | JED2288 |  |  |  | Sajid Nazir Muhammad Nazir | 09/28/2025 03:21:41 | 10/05/2025 15:19:12 | 09/28/2025 15:21:41 | RECTIFIER MODULE FAILURE at JED2288-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 09/28/2025 03:13:20 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/28/2025 03:12:53 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2288 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/28/2025 03:21:41 | 09/28/2025 07:40:40 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250928000171 | PCM-20250928-00000328 | TT-20250928-00292 | EM | Region_4 | JED2506 | JED2506 |  |  |  | Sajid Nazir Muhammad Nazir | 09/28/2025 04:11:16 | 10/05/2025 15:19:12 | 09/28/2025 16:11:16 | RECTIFIER MODULE FAILURE at JED1M8506-P3-CA-L800 @ Sceco | 09/28/2025 04:03:24 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/28/2025 04:02:53 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8506 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/28/2025 04:11:16 | 09/28/2025 07:40:41 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250928001068 | PCM-20250928-00001847 | TT-20250928-01771 | EM | Region_1 | HFR0501 | HFR0501 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Ibrahim Musa | 09/28/2025 15:45:31 | 10/01/2025 18:09:34 | 09/29/2025 03:45:31 | Air condition 2 failure alarm at HFR0501-P2_SRAN @ Sceco | 09/28/2025 15:38:09 | Minor | 65105 | Air condition 2 failure alarm | 09/28/2025 15:35:12 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR0501 | FLM_EM | [8 empty] | API | 09/28/2025 15:45:31 | 09/30/2025 18:17:00 | 10/01/2025 18:09:22 | 10/01/2025 18:09:25 |  | 10/01/2025 18:09:34 |  | Ahmed Ibrahim Musa | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250929000010 | PCM-20250929-00000022 | TT-20250929-00019 | EM | Region_4 | JED0111 | JED0111 |  |  |  | Nabil Nazih Mohamoud Ahmed | 09/29/2025 00:14:20 | 10/05/2025 15:19:23 | 09/29/2025 06:14:20 | SHELTER DOOR OPEN at JED0111-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P1-HUB @ Generator_DG | 09/29/2025 00:13:52 | Major | 7103 | SHELTER DOOR OPEN | 09/29/2025 00:13:22 | P1 | 2G | jeddah | Generator_DG | 2G NSA | JED0111 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 09/29/2025 00:14:20 | 09/29/2025 17:05:44 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250929000015 | PCM-20250929-00000031 | TT-20250929-00030 | EM | Region_4 | JED0111 | JED0111 |  |  |  | Nabil Nazih Mohamoud Ahmed | 09/29/2025 00:22:05 | 10/05/2025 15:19:24 | 09/29/2025 06:22:05 | AIRCON 2 FAILURE at JED0111-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P1-HUB @ Generator_DG | 09/29/2025 00:13:52 | Major | 7103 | AIRCON 2 FAILURE | 09/29/2025 00:13:22 | P1 | 2G | jeddah | Generator_DG | 2G NSA | JED0111 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 09/29/2025 00:22:05 | 09/29/2025 17:05:44 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250929000155 | PCM-20250929-00000495 | TT-20250929-00745 | EM | Region_4 | JED2109 | JED2109 |  |  |  | Muhammad Javed Muhammad Anwar | 09/29/2025 03:59:36 | 10/05/2025 15:19:14 | 09/29/2025 15:59:36 | RECTIFIER MODULE FAILURE at JED1M8109-P3-CA-L800 @ Sceco | 09/29/2025 03:55:20 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/29/2025 03:51:10 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8109 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/29/2025 03:59:36 | 09/29/2025 11:21:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250929000160 | PCM-20250929-00000500 | TT-20250929-00750 | EM | Region_4 | JED2186 | JED2186 | Enviroment | SCECO_Failure | SCECO auto restored | Amr Sherif Gabber Ahmed | 09/29/2025 04:01:13 | 09/29/2025 11:32:47 | 09/29/2025 16:01:13 | Tower Light at JED2186-G9-L8-L18-L21-NR2.6-P3-SBTS @ Generator_SG | 09/29/2025 03:54:09 | Minor | 7103 | Tower Light | 09/29/2025 03:52:42 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2186 | FLM_EM | [5 empty] | Tower Light |  |  | API | 09/29/2025 04:01:13 | 09/29/2025 10:51:52 | 09/29/2025 11:32:29 |  |  | 09/29/2025 11:32:47 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250929000167 | PCM-20250929-00000513 | TT-20250929-00767 | EM | Region_4 | JED2593 | JED2593 |  |  |  | Nabil Nazih Mohamoud Ahmed | 09/29/2025 04:15:36 | 10/05/2025 15:19:15 | 09/29/2025 16:15:36 | AIRCON 1 FAILURE at JED1M8593-P3-L800-CA @ Sceco | 09/29/2025 04:07:50 | Minor | 7103 | AIRCON 1 FAILURE | 09/29/2025 04:06:53 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8593 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 09/29/2025 04:15:36 | 09/29/2025 17:05:45 | [6 empty] | SCECO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250929001417 | PCM-20250929-00002271 | TT-20250929-02566 | EM | Region_4 | TAF0274 | TAF0274 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 09/29/2025 17:22:25 | 10/17/2025 01:30:16 | 09/30/2025 05:22:25 | SHELTER DOOR OPEN at TAF1M7274-G9-L8-L18-L21-SBTS-P2 @ Sceco | 09/29/2025 17:21:37 | Minor | 7103 | SHELTER DOOR OPEN | 09/29/2025 17:18:57 | P2 | 4G | taif | Sceco | LTE NSA | TAF1M7274 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 09/29/2025 17:22:25 | 10/05/2025 20:34:05 | 10/17/2025 01:30:08 |  |  | 10/17/2025 01:30:16 |  | Farghal Ashour Hassan Farghal | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20250929001425 | PCM-20250929-00002284 | TT-20250929-02580 | EM | Region_4 | TAF0274 | TAF0274 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 09/29/2025 17:27:37 | 10/17/2025 01:31:49 | 09/30/2025 05:27:37 | RECTIFIER MAINS POWER FAILURE at TAF1M7274-G9-L8-L18-L21-SBTS-P2 @ Sceco | 09/29/2025 17:21:37 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 09/29/2025 17:18:57 | P2 | 4G | taif | Sceco | LTE NSA | TAF1M7274 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 09/29/2025 17:27:37 | 10/05/2025 20:34:04 | 10/17/2025 01:31:39 |  |  | 10/17/2025 01:31:49 |  | Farghal Ashour Hassan Farghal | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20250930000128 | PCM-20250930-00000234 | TT-20250930-00360 | EM | Region_4 | SQR0075 | SQR0075 |  |  |  | Faiz Muhammad Ghulam Sarwar | 09/30/2025 03:31:01 | 09/30/2025 03:31:01 | 09/30/2025 15:31:01 | GENERATOR1 + GENERATOR2 2 FAILURE at SQR0075-GSM-UMTS-P2-USF @ Generator_DG | 09/30/2025 03:22:52 | Minor | 7103 | GENERATOR1 + GENERATOR2 2 FAILURE | 09/30/2025 03:22:37 | P2 | 2G | adam | Generator_DG | 2G NSA | SQR0075 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 FAILURE |  |  | API | 09/30/2025 03:31:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250930000130 | PCM-20250930-00000237 | TT-20250930-00363 | EM | Region_4 | KAC0451 | KAC0451 |  |  |  | Rami Mohamed Abubakr Ibrahim | 09/30/2025 03:31:31 | 10/05/2025 15:19:26 | 09/30/2025 15:31:31 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at CKAC0451-GSM-P2 @ Sceco | 09/30/2025 03:22:59 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 09/30/2025 03:22:51 | P2 | 2G | jeddah | Sceco | 2G NSA | CKAC0451 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 09/30/2025 03:31:31 | 10/01/2025 23:45:24 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250930000160 | PCM-20250930-00000282 | TT-20250930-00414 | EM | Region_4 | RAB0659 | RAB0659 |  |  |  | Aly Ahmed Aly Sawy | 09/30/2025 04:00:26 | 10/05/2025 15:19:16 | 09/30/2025 16:00:26 | RECTIFIER MODULE FALIURE at RAB1M7659-CA-L800-P3 @ Sceco | 09/30/2025 03:54:18 | Minor | 7103 | RECTIFIER MODULE FALIURE | 09/30/2025 03:51:47 | P2 | 4G | jeddah | Sceco | LTE NSA | RAB1M7659 | FLM_EM | [5 empty] | RECTIFIER MODULE FALIURE |  |  | API | 09/30/2025 04:00:26 | 09/30/2025 08:46:20 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250930000163 | PCM-20250930-00000283 | TT-20250930-00415 | EM | Region_4 | RAB0675 | RAB0675 |  |  |  | Aly Ahmed Aly Sawy | 09/30/2025 04:00:56 | 10/05/2025 15:19:17 | 09/30/2025 16:00:56 | RECTIFIER MODULE FAILURE at RAB0675-G9-L9-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 09/30/2025 03:53:36 | Minor | 7103 | RECTIFIER MODULE FAILURE | 09/30/2025 03:52:19 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0675 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 09/30/2025 04:00:56 | 09/30/2025 08:46:21 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250930000165 | PCM-20250930-00000292 | TT-20250930-00422 | EM | Region_6 | TLT9478 | TLT9478 |  |  |  | Amir Arif Ali | 09/30/2025 04:08:06 | 10/08/2025 11:10:47 | 09/30/2025 08:08:06 | AC alarm / High temp (Input-6) at TLT9478 on 10.89.223.146 @ Generator_DG | 09/30/2025 04:06:09 | Critical | AC alarm / High temp (Input-6) | AC alarm / High temp (Input-6) | 09/30/2025 03:50:48 | P1 | Repeater | turaib | Generator_DG | TX NSA | TLT9478 | FLM_EM | [8 empty] | API | 09/30/2025 04:08:06 | 09/30/2025 13:24:45 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250930000481 | PCM-20250930-00000954 | TT-20250930-01046 | EM | Region_4 | RYMK0757 | RYMK0757 |  |  |  | Ehab Ali Mohamed Abdou | 09/30/2025 10:35:35 | 09/30/2025 10:42:46 | 09/30/2025 22:35:35 | Commercial Power Failure at RYMK0757-GSM-P2 @ Sceco | 09/30/2025 10:27:15 | Minor | 7103 | Commercial Power Failure | 09/30/2025 10:27:09 | P2 | 2G | taif | Sceco | 2G NSA | RYMK0757 | FLM_EM | [5 empty] | Commercial Power Failure |  |  | API | 09/30/2025 10:35:35 | 09/30/2025 10:42:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250930000510 | PCM-20250930-00000991 | TT-20250930-01085 | EM | Region_4 | MKMD9011 | MKMD9011 |  |  |  | Hamza Ahmed Aly Sawy | 09/30/2025 10:59:20 | 09/30/2025 12:30:42 | 09/30/2025 14:59:20 | Door Open at MKMD9011_1 on 10.154.113.117 @ Generator_SG | 09/30/2025 10:55:45 | Critical | Door Open | Door Open | 09/30/2025 10:54:03 | P3 | Repeater | jeddah | Generator_SG | TX NSA | MKMD9011 | FLM_EM | [8 empty] | API | 09/30/2025 10:59:20 | 09/30/2025 12:30:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20250930000701 | PCM-20250930-00001288 | TT-20250930-01404 | EM | Region_4 | HJR0233 | HJR0233 |  |  |  | Alaa Hassan Mohammed Gad | 09/30/2025 13:22:25 | 10/05/2025 15:19:25 | 10/01/2025 01:22:25 | AIRCON 1 FAILURE at HJR1M7233-L800-USF-P3-WBB-G3 @ Sceco_STB | 09/30/2025 13:14:02 | Minor | 7103 | AIRCON 1 FAILURE | 09/30/2025 13:13:56 | P2 | 4G | jeddah | Sceco_STB | LTE NSA | HJR1M7233 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 09/30/2025 13:22:25 | 10/01/2025 21:23:15 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20250930000848 | PCM-20250930-00001526 | TT-20250929-02478 | Reference_telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 09/30/2025 14:47:35 | 10/06/2025 17:59:36 | 10/01/2025 02:47:35 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at DAM0471_NE_4_V | 09/19/2025 07:48:33 | Minor |  | LOF | 09/19/2025 07:48:33 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0471_NE_4_V | FLM_EM |  | Need to update hub site DAM2066 as down and have access issue | PCM-20250930-00001445 | Need to update hub site DAM2066 as down and have access issue | Need to update hub site DAM2066 as down and have access issue |  |  |  | API | 09/30/2025 14:47:35 | 09/30/2025 18:28:46 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000065 | PCM-20251001-00000114 | TT-20251001-00128 | EM | Region_4 | JED0368 | JED0368 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/01/2025 01:39:06 | 10/03/2025 22:18:14 | 10/01/2025 13:39:06 | SHELTER DOOR OPEN at JED0368-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/01/2025 01:38:18 | Minor | 7103 | SHELTER DOOR OPEN | 10/01/2025 01:37:55 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0368 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/01/2025 01:39:06 | 10/03/2025 22:18:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000073 | PCM-20251001-00000141 | TT-20251001-00136 | EM | Region_4 | JED0368 | JED0368 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/01/2025 01:46:15 | 10/03/2025 22:18:15 | 10/01/2025 13:46:15 | AIRCON 1 FAILURE at JED0368-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/01/2025 01:38:18 | Minor | 7103 | AIRCON 1 FAILURE | 10/01/2025 01:37:55 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0368 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/01/2025 01:46:15 | 10/03/2025 22:18:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001000149 | PCM-20251001-00000277 | TT-20251001-00289 | EM | Region_4 | HJR0040 | HJR0040 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Yassir Omer Ibrahim Mahmoud | 10/01/2025 03:37:21 | 10/04/2025 10:59:30 | 10/01/2025 15:37:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at HJR0040-GSM-P2-USF @ Sceco | 10/01/2025 03:29:02 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/01/2025 03:28:52 | P2 | 2G | adam | Sceco | 2G NSA | HJR0040 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/01/2025 03:37:21 | 10/01/2025 06:27:41 | 10/04/2025 08:27:21 |  |  | 10/04/2025 10:59:30 |  | Yassir Omer Ibrahim Mahmoud |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001000151 | PCM-20251001-00000279 | TT-20251001-00291 | EM | Region_4 | SIR0160 | SIR0160 | Enviroment | Air Condition | Change Fan | Yassir Omer Ibrahim Mahmoud | 10/01/2025 03:37:56 | 10/02/2025 22:44:13 | 10/01/2025 15:37:56 | AIRCON 1 FAILURE at SIR0160-GSM-P2-USF @ Generator_SG | 10/01/2025 03:29:14 | Minor | 7103 | AIRCON 1 FAILURE | 10/01/2025 03:29:08 | P2 | 2G | adam | Generator_SG | 2G NSA | SIR0160 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/01/2025 03:37:56 | 10/01/2025 06:27:41 | 10/02/2025 22:35:58 |  |  | 10/02/2025 22:44:13 |  | Yassir Omer Ibrahim Mahmoud |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000154 | PCM-20251001-00000282 | TT-20251001-00297 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/01/2025 03:41:31 | 10/02/2025 04:30:22 | 10/01/2025 15:41:31 | SHELTER DOOR OPEN at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/01/2025 03:41:04 | Minor | 7103 | SHELTER DOOR OPEN | 10/01/2025 03:39:44 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/01/2025 03:41:31 | 10/02/2025 04:30:22 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000159 | PCM-20251001-00000296 | TT-20251001-00312 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/01/2025 03:48:16 | 10/02/2025 04:30:22 | 10/01/2025 15:48:16 | RECTIFIER MODULE FAILURE at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/01/2025 03:41:04 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/01/2025 03:39:44 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/01/2025 03:48:16 | 10/02/2025 04:30:22 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000177 | PCM-20251001-00000323 | TT-20251001-00338 | EM | Region_4 | KMMD0751 | KMMD0751 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/01/2025 04:03:51 | 10/01/2025 14:53:16 | 10/01/2025 16:03:51 | AIRCON 2 FAILURE at KMMD0751-GSM-P3 @ Sceco | 10/01/2025 03:55:09 | Minor | 7103 | AIRCON 2 FAILURE | 10/01/2025 03:55:02 | P3 | 2G | jeddah | Sceco | 2G NSA | KMMD0751 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/01/2025 04:03:51 | 10/01/2025 14:53:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001000179 | PCM-20251001-00000326 | TT-20251001-00341 | EM | Region_4 | UKHA0345 | UKHA0345 | Equipment | FAN Cleaning | Clean FAN | Hany Mohamed Mahmoud Eldamarany | 10/01/2025 04:03:54 | 10/23/2025 13:32:50 | 10/01/2025 10:03:54 | RECTIFIER MAIN POWER FAILURE at UKHA0345-GSM-P1-HUB @ Sceco | 10/01/2025 03:55:23 | Major | 7103 | RECTIFIER MAIN POWER FAILURE | 10/01/2025 03:55:13 | P1 | 2G | adam | Sceco | 2G NSA | UKHA0345 | FLM_EM | [5 empty] | RECTIFIER MAIN POWER FAILURE |  |  | API | 10/01/2025 04:03:54 | 10/23/2025 13:02:48 | 10/23/2025 13:03:11 | 10/23/2025 13:03:15 | 10/23/2025 13:03:18 | 10/23/2025 13:32:50 |  | Hany Mohamed Mahmoud Eldamarany |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251001000224 | PCM-20251001-00000392 | TT-20251001-00406 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Ibrahim Musa | 10/01/2025 04:59:02 | 10/01/2025 18:08:48 | 10/01/2025 08:59:02 | Air condition 1 failure alarm at DMJR0137-P2-WDM_SRAN @ Sceco_STB | 10/01/2025 04:57:07 | Critical | 65104 | Air condition 1 failure alarm | 10/01/2025 04:57:04 | P2 | SRAN | hafr | Sceco_STB | 2G NSA | DMJR0137 | FLM_EM | [8 empty] | API | 10/01/2025 04:59:02 | 10/01/2025 05:15:47 | 10/01/2025 06:31:03 | 10/01/2025 06:31:06 | 10/01/2025 06:31:15 | 10/01/2025 18:08:48 |  | Ahmed Ibrahim Musa |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251001000226 | PCM-20251001-00000400 | TT-20251001-00411 | EM | Region_4 | JED0974 | JED0974 |  |  |  | Sajid Nazir Muhammad Nazir | 10/01/2025 05:05:47 | 10/15/2025 07:02:45 | 10/01/2025 17:05:47 | RECTIFIER MAINS POWER FAILURE at JED0974-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/01/2025 04:57:25 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/01/2025 04:57:19 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0974 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/01/2025 05:05:47 | 10/15/2025 07:02:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001000278 | PCM-20251001-00000496 | TT-20251001-00500 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/01/2025 06:15:31 | 10/03/2025 20:48:45 | 10/01/2025 10:15:31 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/01/2025 06:13:21 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/01/2025 06:13:16 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 1-(1-B) |  |  | API | 10/01/2025 06:15:31 | 10/01/2025 14:41:33 | 10/03/2025 20:47:37 |  |  | 10/03/2025 20:48:45 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251001000287 | PCM-20251001-00000519 | TT-20251001-00526 | EM | Region_4 | SQR0200 | SQR0200 |  |  |  | Faiz Muhammad Ghulam Sarwar | 10/01/2025 06:33:30 | 10/01/2025 06:33:30 | 10/01/2025 18:33:30 | GENERATOR LOW FUEL at SQR0200-GSM-UMTS-P2-USF @ Generator_SG | 10/01/2025 06:25:03 | Minor | 7103 | GENERATOR LOW FUEL | 10/01/2025 06:24:59 | P2 | 2G | adam | Generator_SG | 2G NSA | SQR0200 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/01/2025 06:33:30 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000360 | PCM-20251001-00000661 | TT-20251001-00429 | Telecom | Region_2 | RIY0216 | RIY0216 |  |  |  | Adham Adham Hassan Farghal | 10/01/2025 08:10:30 | 10/01/2025 17:50:44 | 10/01/2025 12:10:30 | STC : LINK DOWN B/W RIY0216-RIY0241 | 10/01/2025 05:23:02 | Critical | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/01/2025 05:23:02 | VIP | SRAN | riyadh | Sceco | DWDM NSA | RIY0216 | FLM_EM |  |  | PCM-20251001-00000485 | Need FLM to check the power at site | Need FLM to check the power at site |  |  |  | API | 10/01/2025 08:10:30 | 10/01/2025 17:50:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251001000361 | PCM-20251001-00000664 | TT-20251001-00642 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/01/2025 08:10:40 | 10/02/2025 00:02:00 | 10/01/2025 20:10:40 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/01/2025 08:00:13 | Minor | 65102 | high temprature 32 | 10/01/2025 08:00:09 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/01/2025 08:10:40 | 10/02/2025 00:02:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251001000374 | PCM-20251001-00000691 | TT-20251001-00670 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/01/2025 08:28:15 | 10/01/2025 12:58:35 | 10/01/2025 20:28:15 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/01/2025 08:17:43 | Minor | 65102 | high temprature 32 | 10/01/2025 08:17:39 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/01/2025 08:28:15 | 10/01/2025 12:58:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000386 | PCM-20251001-00000713 | TT-20251001-00691 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/01/2025 08:41:40 | 10/01/2025 11:46:59 | 10/01/2025 20:41:40 | high temprature 40 at KBR2223-P3_SRAN @ Sceco | 10/01/2025 08:31:15 | Minor | 65103 | high temprature 40 | 10/01/2025 08:31:10 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/01/2025 08:41:40 | 10/01/2025 11:46:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000412 | PCM-20251001-00000759 | TT-20251001-00729 | EM | Region_4 | JED2024 | JED2024 |  |  |  | Sajid Nazir Muhammad Nazir | 10/01/2025 08:55:40 | 10/01/2025 14:06:29 | 10/01/2025 20:55:40 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8024-L800-CA-SBTS-P2 @ Sceco | 10/01/2025 08:47:22 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/01/2025 08:47:12 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M8024 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/01/2025 08:55:40 | 10/01/2025 14:06:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251001000474 | PCM-20251001-00000877 | TT-20251001-00825 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/01/2025 09:52:25 | 10/01/2025 11:29:33 | 10/01/2025 21:52:25 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/01/2025 09:41:45 | Minor | 65102 | High temperature 32C alarm | 10/01/2025 09:41:42 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/01/2025 09:52:25 | 10/01/2025 11:29:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001000578 | PCM-20251001-00001044 | TT-20251001-00982 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/01/2025 11:23:50 | 10/01/2025 20:17:12 | 10/01/2025 23:23:50 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/01/2025 11:17:09 | Minor | 40564 | Genset Fault | 10/01/2025 11:17:09 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/01/2025 11:23:50 | 10/01/2025 15:10:16 | 10/01/2025 20:16:59 |  |  | 10/01/2025 20:17:12 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251001000619 | PCM-20251001-00001124 | TT-20251001-01046 | EM | Region_4 | JED0786 | JED0786 |  |  |  | Amer Attallah Awadallah | 10/01/2025 12:00:26 | 10/01/2025 12:12:09 | 10/01/2025 18:00:26 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED0786-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-SHOP @ Sceco | 10/01/2025 11:52:24 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/01/2025 11:52:11 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0786 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/01/2025 12:00:26 | 10/01/2025 12:12:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001000655 | PCM-20251001-00001180 | TT-20251001-01120 | Reference_EM | Region_1 | ARR0919 | ARR0919 | Transsmission | MW_loop | Remote action done by BO by removing VLAN loop | Ismail Salah Ismail Elbery | 10/01/2025 12:46:31 | 10/03/2025 08:07:44 | 10/01/2025 18:46:31 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/01/2025 12:35:47 | Major | 65110 | Low battery voltage | 10/01/2025 12:35:46 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/01/2025 12:46:31 | 10/02/2025 03:53:46 | 10/03/2025 08:07:39 |  |  | 10/03/2025 08:07:44 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251001000692 | PCM-20251001-00001224 | TT-20251001-01171 | EM | Region_4 | BHR0307 | BHR0307 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/01/2025 13:12:50 | 10/04/2025 12:56:25 | 10/02/2025 01:12:50 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at BHR1M7307-G9-L8-L18-L21-SBTS-P3 @ Sceco_STB | 10/01/2025 13:07:02 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/01/2025 13:04:11 | P2 | 4G | jeddah | Sceco_STB | LTE NSA | BHR1M7307 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/01/2025 13:12:50 | 10/04/2025 12:56:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000748 | PCM-20251001-00001303 | TT-20251001-01270 | Reference_EM | Region_2 | RYHR0745 | RYHR0745 |  |  |  | Pawan Virdi Santokh Singh | 10/01/2025 14:04:00 | 10/01/2025 16:28:57 | 10/02/2025 02:04:00 | DC power fail at RYHR0745-P2_SRAN @ Sceco | 10/01/2025 13:53:34 | Minor | 65106 | DC power fail | 10/01/2025 13:53:30 | P2 | SRAN | riyadh | Sceco | 2G NSA | RYHR0745 | FLM_EM | [8 empty] | API | 10/01/2025 14:04:00 | 10/01/2025 16:28:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251001000757 | PCM-20251001-00001316 | TT-20251001-01281 | Reference_EM | Region_1 | HFF0096 | HFF0096 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Bashir Sahib Rahman | 10/01/2025 14:11:45 | 10/04/2025 19:57:35 | 10/02/2025 02:11:45 | DC power fail at HFF0096-P2_SRAN @ Sceco | 10/01/2025 14:01:21 | Minor | 65106 | DC power fail | 10/01/2025 14:01:17 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0096 | FLM_EM | [8 empty] | API | 10/01/2025 14:11:45 | 10/04/2025 19:50:36 | 10/04/2025 19:56:40 |  |  | 10/04/2025 19:57:35 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001000935 | PCM-20251001-00001565 | TT-20251001-01503 | EM | Region_4 | JED2298 | JED2298 |  |  |  | Sajid Nazir Muhammad Nazir | 10/01/2025 15:59:45 | 10/01/2025 16:00:41 | 10/02/2025 03:59:45 | RECTIFIER MODULE FAILURE at JED1M8298-CA-L800-P3 @ Sceco | 10/01/2025 15:51:25 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/01/2025 15:51:20 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8298 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/01/2025 15:59:45 | 10/01/2025 16:00:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001001237 | PCM-20251001-00002050 | TT-20251001-02018 | EM | Region_4 | JED2612 | JED2612 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/01/2025 20:29:20 | 10/02/2025 18:18:13 | 10/02/2025 08:29:20 | RECTIFIER MODULE FAILURE at JED1M8612-L800-L1800-CA-P3-SBTS @ Sceco | 10/01/2025 20:20:50 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/01/2025 20:20:40 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8612 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/01/2025 20:29:20 | 10/02/2025 18:18:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001001243 | PCM-20251001-00002058 | TT-20251001-02030 | Reference_EM | Region_1 | DMJ2271 | DMJ2271 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/01/2025 20:40:45 | 10/02/2025 16:28:11 | 10/02/2025 08:40:45 | NETECO: Communication Failure at DMJ2271 @ Generator_SG | 10/01/2025 19:00:50 | Minor | 9354 | Communication Failure | 10/01/2025 19:00:50 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJ2271 | FLM_EM | [8 empty] | API | 10/01/2025 20:40:45 | 10/01/2025 20:58:39 | 10/02/2025 16:27:58 |  |  | 10/02/2025 16:28:11 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001001277 | PCM-20251001-00002112 | TT-20251001-02096 | EM | Region_1 | DAM0274 | DAM0274 | Enviroment | Air Condition | Change Fan | Kenawy Abdalla Tawfik Abdalla | 10/01/2025 21:46:51 | 10/02/2025 00:27:50 | 10/02/2025 01:46:51 | AMBIENT_TEMP_FLUCT at DAM0274_OCS @ Sceco | 10/01/2025 21:44:58 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/01/2025 21:44:49 | P1 | SRAN | dammam | Sceco | DWDM NSA | DAM0274 | FLM_EM | [5 empty] | 2-TO DAM0389(1-A) |  |  | API | 10/01/2025 21:46:51 | 10/01/2025 21:57:32 | 10/01/2025 22:10:47 | 10/01/2025 22:11:22 | 10/01/2025 22:11:33 | 10/02/2025 00:27:50 |  | Kenawy Abdalla Tawfik Abdalla |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251001001333 | PCM-20251001-00002224 | TT-20251001-02219 | EM | Region_1 | ARM0857 | ARM0857 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Omer Elfadoul Mohamed Ibrahim | 10/01/2025 23:16:45 | 10/11/2025 13:19:15 | 10/02/2025 11:16:45 | Door opening alarm at ARM0857-P2_SRAN @ Generator_SG | 10/01/2025 23:16:02 | Minor | 65101 | Door opening alarm | 10/01/2025 23:15:59 | P2 | SRAN | dammam | Generator_SG | 2G NSA | ARM0857 | FLM_EM | [8 empty] | API | 10/01/2025 23:16:45 | 10/02/2025 07:27:11 | 10/11/2025 13:19:00 |  |  | 10/11/2025 13:19:15 |  | Omer Elfadoul Mohamed Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251001001341 | PCM-20251001-00002238 | TT-20251001-02231 | Reference_EM | Region_1 | RSK0990 | RSK0990 |  |  |  | Ali Ahmed Ali Ahmed | 10/01/2025 23:33:50 | 10/04/2025 03:02:19 | 10/02/2025 11:33:50 | Air-condition #1 failure alarm at RSK2M1990-P3 @ Sceco | 10/01/2025 23:23:26 | Minor | 65104 | Air-condition #1 failure alarm | 10/01/2025 23:23:23 | P3 | 2G | jubail | Sceco | 2G NSA | RSK2M1990 | FLM_EM | [8 empty] | API | 10/01/2025 23:33:50 | 10/04/2025 03:02:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251001001360 | PCM-20251001-00002266 | TT-20251001-02253 | EM | Region_2 | AFL9008 | AFL9008 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sher Zamin Nasib Muhammad | 10/01/2025 23:57:35 | 10/21/2025 07:52:28 | 10/02/2025 03:57:35 | RELAY_ALARM_CRITICAL at AFL9008_NE_1 @ Power cube | 09/26/2025 12:11:20 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/01/2025 23:53:08 | P3 | Repeater | aflaj | Power Cube | TX NSA | AFL9008_NE_1 | FLM_EM | [5 empty] | RELAY_ALARM_CRITICAL at AFL9008_NE_1 @ Power cube |  |  | API | 10/01/2025 23:57:35 | 10/03/2025 12:58:15 | 10/21/2025 07:52:02 |  |  | 10/21/2025 07:52:28 |  | Sher Zamin Nasib Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000076 | PCM-20251002-00000113 | TT-20251002-00137 | EM | Region_6 | WDS9470 | WDS9470 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Muhammad Aslam Abdul Salam | 10/02/2025 01:31:06 | 10/10/2025 12:27:27 | 10/02/2025 05:31:06 | Main & Rectifier Failure (Input-2) at WDS9470-1 on 10.89.222.37 @ Generator_DG | 10/02/2025 01:27:45 | Critical | Main & Rectifier Failure (Input-2) | Main & Rectifier Failure (Input-2) | 10/02/2025 01:25:43 | P1 | Repeater | wadi dawasar | Generator_DG | TX NSA | WDS9470 | FLM_EM | [8 empty] | API | 10/02/2025 01:31:06 | 10/02/2025 07:21:58 | 10/10/2025 12:26:51 |  |  | 10/10/2025 12:27:27 |  | Muhammad Aslam Abdul Salam |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002000124 | PCM-20251002-00000178 | TT-20251002-00212 | EM | Region_4 | NOB0225 | NOB0225 |  |  |  | Alaa Hassan Mohammed Gad | 10/02/2025 02:28:56 | 10/02/2025 02:51:12 | 10/02/2025 14:28:56 | GENERATOR1 + GENERATOR2 2 FAILURE at NOB0225-GSM-UMTS-P2-USF @ Generator_SG | 10/02/2025 02:21:11 | Minor | 7103 | GENERATOR1 + GENERATOR2 2 FAILURE | 10/02/2025 02:20:16 | P2 | 2G | jeddah | Generator_SG | 2G NSA | NOB0225 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 FAILURE |  |  | API | 10/02/2025 02:28:56 | 10/02/2025 02:51:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000127 | PCM-20251002-00000183 | TT-20251002-00218 | EM | Region_4 | HHR0866 | HHR0866 |  |  |  | Aly Ahmed Aly Sawy | 10/02/2025 02:30:31 | 10/02/2025 22:51:00 | 10/02/2025 08:30:31 | GENERATOR LOW FUEL at HHR0866-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/02/2025 02:22:00 | Major | 7103 | GENERATOR LOW FUEL | 10/02/2025 02:21:54 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0866 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/02/2025 02:30:31 | 10/02/2025 22:51:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000128 | PCM-20251002-00000181 | TT-20251002-00215 | EM | Region_4 | HHR0867 | HHR0867 |  |  |  | Aly Ahmed Aly Sawy | 10/02/2025 02:30:33 | 10/02/2025 22:51:01 | 10/02/2025 08:30:33 | GENERATOR 1+ GENERATOR 2 FAILURE at HHR0867-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/02/2025 02:22:08 | Major | 7103 | GENERATOR 1+ GENERATOR 2 FAILURE | 10/02/2025 02:22:01 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0867 | FLM_EM | [5 empty] | GENERATOR 1+ GENERATOR 2 FAILURE |  |  | API | 10/02/2025 02:30:33 | 10/02/2025 22:51:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000154 | PCM-20251002-00000225 | TT-20251002-00289 | EM | Region_1 | ARR9807 | ARR9807 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Ismail Salah Ismail Elbery | 10/02/2025 03:23:46 | 10/03/2025 08:07:34 | 10/02/2025 15:23:46 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/02/2025 03:17:19 | Minor | 40564 | Genset Fault | 10/02/2025 03:17:19 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/02/2025 03:23:46 | 10/02/2025 03:53:49 | 10/03/2025 08:07:28 |  |  | 10/03/2025 08:07:34 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000155 | PCM-20251002-00000226 | TT-20251002-00293 | EM | Region_4 | YLM0789 | YLM0789 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Karim Hamdy Mohamed Elashry | 10/02/2025 03:24:46 | 10/02/2025 14:24:13 | 10/02/2025 15:24:46 | GENERATOR LOW FUEL at YLM0789-GSM-UMTS-P3 @ Generator_SG | 10/02/2025 03:16:54 | Minor | 7103 | GENERATOR LOW FUEL | 10/02/2025 03:16:14 | P3 | 2G | alaith | Generator_SG | 2G NSA | YLM0789 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/02/2025 03:24:46 | 10/02/2025 10:42:51 | 10/02/2025 14:23:55 | 10/02/2025 14:24:00 |  | 10/02/2025 14:24:13 |  | Karim Hamdy Mohamed Elashry |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251002000157 | PCM-20251002-00000229 | TT-20251002-00297 | EM | Region_4 | SQR0170 | SQR0170 |  |  |  | Faiz Muhammad Ghulam Sarwar | 10/02/2025 03:25:18 | 10/02/2025 03:25:18 | 10/02/2025 15:25:18 | GENERATOR LOW FUEL at SQR0170-GSM-UMTS-P2-USF @ Generator_DG | 10/02/2025 03:17:11 | Minor | 7103 | GENERATOR LOW FUEL | 10/02/2025 03:16:58 | P2 | 2G | adam | Generator_DG | 2G NSA | SQR0170 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/02/2025 03:25:18 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002000158 | PCM-20251002-00000227 | TT-20251002-00295 | EM | Region_4 | SIR0173 | SIR0173 |  |  |  | Ibrahim Fawzy Mohamed Elbers | 10/02/2025 03:25:19 | 10/04/2025 09:56:21 | 10/02/2025 15:25:19 | RECTIFIER MAINS POWER FAILURE at SIR0173-GSM-UMTS-P2-USF @ Generator_SG | 10/02/2025 03:17:45 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/02/2025 03:16:48 | P2 | 2G | adam | Generator_SG | 2G NSA | SIR0173 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/02/2025 03:25:19 | 10/04/2025 09:56:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000170 | PCM-20251002-00000253 | TT-20251002-00329 | EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/02/2025 03:48:31 | 10/02/2025 11:18:23 | 10/02/2025 09:48:31 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/02/2025 03:43:46 | Major | 65110 | Low battery voltage | 10/02/2025 03:37:58 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/02/2025 03:48:31 | 10/02/2025 11:18:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000208 | PCM-20251002-00000313 | TT-20251002-00647 | EM | Region_4 | JED0935 | JED0935 |  |  |  | AbdAllah Mohammad abd Elgawad Fath Elbab | 10/02/2025 04:47:26 | 10/02/2025 10:52:01 | 10/02/2025 16:47:26 | HIGH TEMPERATURE 32 DEGREE C at JED0935-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Generator_SG | 10/02/2025 04:39:36 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/02/2025 04:39:07 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0935 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/02/2025 04:47:26 | 10/02/2025 10:52:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000211 | PCM-20251002-00000316 | TT-20251002-00650 | EM | Region_4 | JED0183 | JED0183 |  |  |  | Sajid Nazir Muhammad Nazir | 10/02/2025 04:48:25 | 10/02/2025 14:27:31 | 10/02/2025 16:48:25 | RECTIFER MODULE FAILURE at JED0183-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/02/2025 04:40:06 | Minor | 7103 | RECTIFER MODULE FAILURE | 10/02/2025 04:40:00 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0183 | FLM_EM | [5 empty] | RECTIFER MODULE FAILURE |  |  | API | 10/02/2025 04:48:25 | 10/02/2025 14:27:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000215 | PCM-20251002-00000322 | TT-20251002-00657 | EM | Region_4 | MLJI0110 | MLJI0110 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Rizwan Basharat Hussain | 10/02/2025 04:53:36 | 10/04/2025 15:32:13 | 10/02/2025 16:53:36 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at MLJI0110-GSM-UMTS-P3 @ Generator_SG | 10/02/2025 04:45:25 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/02/2025 04:45:16 | P3 | 2G | alaith | Generator_SG | 2G NSA | MLJI0110 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/02/2025 04:53:36 | 10/02/2025 08:25:04 | 10/04/2025 15:31:56 |  |  | 10/04/2025 15:32:13 |  | Muhammad Rizwan Basharat Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000251 | PCM-20251002-00000387 | TT-20251002-00729 | EM | Region_4 | JED0925 | JED0925 | Transsmission | MW_loop | Remote action done by BO by removing VLAN loop | Abd EL Azeez EL Sayed Soliman | 10/02/2025 06:01:16 | 10/04/2025 00:06:20 | 10/02/2025 12:01:16 | SHELTER DOOR OPEN at JED0925-G9-L8-L18-L21-NNR6-SBTS-P1-VIP @ Generator_SG | 10/02/2025 06:00:44 | Major | 7103 | SHELTER DOOR OPEN | 10/02/2025 06:00:11 | VIP | 2G | jeddah | Generator_SG | 2G NSA | JED0925 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/02/2025 06:01:16 | 10/04/2025 00:03:40 | 10/04/2025 00:06:10 |  |  | 10/04/2025 00:06:20 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000255 | PCM-20251002-00000392 | TT-20251002-00735 | EM | Region_4 | JED0925 | JED0925 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/02/2025 06:08:30 | 10/04/2025 00:06:03 | 10/02/2025 12:08:30 | HIGH TEMPERATURE 32 DEGREE C at JED0925-G9-L8-L18-L21-NNR6-SBTS-P1-VIP @ Generator_SG | 10/02/2025 06:00:44 | Major | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/02/2025 06:00:11 | VIP | 2G | jeddah | Generator_SG | 2G NSA | JED0925 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/02/2025 06:08:30 | 10/04/2025 00:03:40 | 10/04/2025 00:05:53 |  |  | 10/04/2025 00:06:03 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000312 | PCM-20251002-00000498 | TT-20251002-00837 | EM | Region_4 | JED0118 | JED0118 |  |  |  | Amer Attallah Awadallah | 10/02/2025 07:25:30 | 10/02/2025 14:23:54 | 10/02/2025 19:25:30 | RECTIFIER MODULE FAILURE at JED1M7118-P2-CA-L900-L800-SBTS @ Sceco | 10/02/2025 07:16:52 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/02/2025 07:16:46 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7118 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/02/2025 07:25:30 | 10/02/2025 14:23:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000334 | PCM-20251002-00000535 | TT-20251002-00870 | EM | Region_1 | DMJR0127 | DMJR0127 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/02/2025 07:49:45 | 10/03/2025 20:49:24 | 10/02/2025 13:49:45 | Air condition 1 failure alarm at DMJR0127-P1-HUB_SRAN @ Sceco_STB | 10/02/2025 07:47:33 | Major | 65104 | Air condition 1 failure alarm | 10/02/2025 07:38:09 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | DMJR0127 | FLM_EM | [8 empty] | API | 10/02/2025 07:49:45 | 10/02/2025 19:46:00 | 10/03/2025 20:48:57 |  |  | 10/03/2025 20:49:24 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002000363 | PCM-20251002-00000572 | TT-20251002-00901 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/02/2025 08:11:30 | 10/03/2025 19:35:51 | 10/02/2025 20:11:30 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/02/2025 08:02:56 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/02/2025 08:02:52 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/02/2025 08:11:30 | 10/03/2025 19:35:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000368 | PCM-20251002-00000577 | TT-20251002-00910 | EM | Region_1 | SMN0806 | SMN0806 | Enviroment | Genset failure_Oil | Site has high oil consumption as site need OH | Rahman Ullah Said Halim | 10/02/2025 08:17:41 | 10/06/2025 21:40:27 | 10/02/2025 20:17:41 | Generator failure at SMN0806-P2_SRAN @ Generator_DG | 10/02/2025 08:15:20 | Minor | 65114 | Generator failure | 10/02/2025 07:55:28 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/02/2025 08:17:41 | 10/03/2025 00:02:33 | 10/06/2025 21:38:24 | 10/06/2025 21:38:27 |  | 10/06/2025 21:40:27 |  | Rahman Ullah Said Halim |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002000381 | PCM-20251002-00000600 | TT-20251002-00895 | Telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/02/2025 08:30:55 | 10/02/2025 11:18:24 | 10/02/2025 20:30:55 | Time Synchronization Failure at DAM2M3636-P2 @ Sceco | 10/02/2025 08:03:21 | Minor | 26266 | Time Synchronization Failure | 10/02/2025 07:59:40 | P1 | SRAN | dammam | Sceco | 3G NSA | DAM2M3636 | FLM_EM |  |  | PCM-20251002-00000593 | suspected power issue at site DAM2066 | suspected power issue at site DAM2066 |  |  |  | API | 10/02/2025 08:30:55 | 10/02/2025 11:18:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002000399 | PCM-20251002-00000634 | TT-20251002-00959 | Reference_EM | Region_2 | RIY2050 | RIY2050 | Enviroment | Genset failure_Oil | Site has high oil consumption as site need OH | Amr Abbas Zaghloul Abbas | 10/02/2025 08:51:15 | 10/02/2025 09:53:07 | 10/02/2025 20:51:15 | Generator failure at RIY2050-P2_SRAN @ Sceco | 10/02/2025 08:40:45 | Minor | 65114 | Generator failure | 10/02/2025 08:40:43 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2050 | FLM_EM | [8 empty] | API | 10/02/2025 08:51:15 | 10/02/2025 09:48:57 | 10/02/2025 09:52:39 |  |  | 10/02/2025 09:53:07 |  | Amr Abbas Zaghloul Abbas |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251002000596 | PCM-20251002-00000895 | TT-20251002-01202 | Reference_EM | Region_2 | RIY2026 | RIY2026 | Enviroment | Genset failure_Oil | Site has high oil consumption as site need OH | Amr Abbas Zaghloul Abbas | 10/02/2025 10:14:55 | 10/02/2025 10:49:56 | 10/02/2025 22:14:55 | Generator failure at RIY2026-P3_SRAN @ Generator_DG | 10/02/2025 10:04:30 | Minor | 65114 | Generator failure | 10/02/2025 10:04:27 | P3 | SRAN | riyadh | Generator_DG | 2G NSA | RIY2026 | FLM_EM | [8 empty] | API | 10/02/2025 10:14:55 | 10/02/2025 10:49:21 | 10/02/2025 10:49:27 | 10/02/2025 10:49:31 | 10/02/2025 10:49:33 | 10/02/2025 10:49:56 |  | Amr Abbas Zaghloul Abbas |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002000615 | PCM-20251002-00000922 | TT-20251002-01226 | EM | Region_4 | JED0086 | JED0086 |  |  |  | Amer Attallah Awadallah | 10/02/2025 10:31:55 | 10/02/2025 14:23:55 | 10/02/2025 16:31:55 | HIGH TEMPERATURE 32 DEGREE C at JED0086-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-SHOP-HUB-WDM-FON @ Sceco | 10/02/2025 10:23:41 | Major | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/02/2025 10:23:29 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0086 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/02/2025 10:31:55 | 10/02/2025 14:23:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251002000793 | PCM-20251002-00001200 | TT-20251002-01530 | EM | Region_6 | ULY0108 | ULY0108 |  |  |  | Asad Saddiq | 10/02/2025 13:21:10 | 10/15/2025 11:51:47 | 10/03/2025 01:21:10 | AIRCON 1 FAILURE at ULY1M7108-G9-L18-L21-SBTS-P2-WBB-G3 @ Sceco | 10/02/2025 13:02:52 | Minor | 7103 | AIRCON 1 FAILURE | 10/02/2025 13:02:44 | P2 | 4G | bisha | Sceco | LTE NSA | ULY1M7108 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/02/2025 13:21:10 | 10/02/2025 13:54:44 | [6 empty] | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000802 | PCM-20251002-00001217 | TT-20251002-01551 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/02/2025 13:30:17 | 10/04/2025 22:31:54 | 10/03/2025 01:30:17 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/02/2025 13:10:49 | Minor | 7103 | AIRCON 1 FAILURE | 10/02/2025 13:10:38 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/02/2025 13:30:17 | 10/04/2025 22:31:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002000853 | PCM-20251002-00001292 | TT-20251002-01620 | EM | Region_4 | GMK0046 | GMK0046 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/02/2025 13:53:15 | 10/03/2025 19:35:52 | 10/03/2025 01:53:15 | rectifier mudule failure at GMK1M7046-G9-NL8-L18-SBTS-P2-USF @ Generator_DG | 10/02/2025 13:45:16 | Minor | 7103 | rectifier mudule failure | 10/02/2025 13:44:56 | P2 | 4G | qunfuddah | Generator_DG | LTE NSA | GMK1M7046 | FLM_EM | [5 empty] | rectifier mudule failure |  |  | API | 10/02/2025 13:53:15 | 10/03/2025 19:35:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002000855 | PCM-20251002-00001294 | TT-20251002-01103 | Reference_telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/02/2025 13:53:45 | 10/02/2025 14:19:51 | 10/03/2025 01:53:45 | MW RTN Observing PLA_MEMBER_DOWN_EXT,PLA_MEMBER_DOWN_EXT at DAM0471_NE_6_SDB | 09/21/2025 12:59:47 | Minor |  | LOF | 09/21/2025 12:59:47 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0471_NE_6_SDB | FLM_EM |  | DAM2066 | PCM-20251002-00001273 | DAM2066 | DAM2066 |  |  |  | API | 10/02/2025 13:53:45 | 10/02/2025 14:19:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251002001107 | PCM-20251002-00001735 | TT-20251002-02031 | Reference_EM | Region_1 | RYHR0116 | RYHR0116 | Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator | Essam Salah Marsa Hassan | 10/02/2025 16:52:30 | 10/02/2025 20:19:51 | 10/03/2025 04:52:30 | Mains Failure at RYHR0116-P3_SRAN @ Generator_SG | 10/02/2025 16:42:10 | Minor | 65109 | Mains Failure | 10/02/2025 16:42:06 | P3 | SRAN | hafr | Generator_SG | 2G NSA | RYHR0116 | FLM_EM | [8 empty] | API | 10/02/2025 16:52:30 | 10/02/2025 16:52:33 | 10/02/2025 19:07:55 | 10/02/2025 19:07:58 | 10/02/2025 20:19:33 | 10/02/2025 20:19:51 |  | Essam Salah Marsa Hassan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251002001114 | PCM-20251002-00001743 | TT-20251002-02037 | EM | Region_2 | MZH0527 | MZH0527 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/02/2025 16:53:35 | 10/03/2025 13:42:01 | 10/02/2025 20:53:35 | NE_COMMU_GNE_SWITCH at MZH0527_ELC @ Sceco_STB | 10/02/2025 16:51:27 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/02/2025 16:51:24 | VIP | SRAN | muzamiah | Sceco_STB | DWDM NSA | MZH0527 | FLM_EM | [5 empty] | NE MZH0527_ELC's current GNE has been switched to standby GNE |  |  | API | 10/02/2025 16:53:35 | 10/03/2025 13:42:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251002001119 | PCM-20251002-00001752 | TT-20251002-02042 | EM | Region_2 | MZH0527 | MZH0527 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/02/2025 16:54:35 | 10/03/2025 13:42:01 | 10/02/2025 20:54:35 | NE_COMMU_GNE_SWITCH at MZH0527_OCS @ Sceco_STB | 10/02/2025 16:52:20 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/02/2025 16:52:18 | VIP | SRAN | muzamiah | Sceco_STB | DWDM NSA | MZH0527 | FLM_EM | [5 empty] | NE MZH0527_OCS's current GNE has been switched to standby GNE |  |  | API | 10/02/2025 16:54:35 | 10/03/2025 13:42:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251002001372 | PCM-20251002-00002136 | TT-20251002-02408 | EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/02/2025 20:34:11 | 10/02/2025 21:14:46 | 10/03/2025 02:34:11 | Door opening alarm at DAM2066-P1-HUB_SRAN @ Sceco | 10/02/2025 20:33:25 | Major | 65101 | Door opening alarm | 10/02/2025 20:32:09 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/02/2025 20:34:11 | 10/02/2025 21:14:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002001413 | PCM-20251002-00002192 | TT-20251002-02487 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/02/2025 21:17:05 | 10/04/2025 11:44:23 | 10/03/2025 09:17:05 | SHELTER DOOR OPEN at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/02/2025 21:16:35 | Minor | 7103 | SHELTER DOOR OPEN | 10/02/2025 19:27:11 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/02/2025 21:17:05 | 10/04/2025 11:44:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002001414 | PCM-20251002-00002195 | TT-20251002-02489 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/02/2025 21:18:35 | 10/04/2025 11:44:24 | 10/03/2025 09:18:35 | AIRCON 1 FAILURE at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/02/2025 21:16:34 | Minor | 7103 | AIRCON 1 FAILURE | 10/02/2025 19:27:11 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/02/2025 21:18:35 | 10/04/2025 11:44:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251002001471 | PCM-20251002-00002278 | TT-20251002-02571 | EM | Region_4 | JED0777 | JED0777 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/02/2025 22:29:55 | 10/03/2025 22:18:16 | 10/03/2025 10:29:55 | RECTIFIER MODULE FAILURE at JED1M7777-P3-CA-L900-L800-SBTS @ Generator_SG | 10/02/2025 22:21:21 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/02/2025 22:21:12 | P2 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7777 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/02/2025 22:29:55 | 10/03/2025 22:18:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000004 | PCM-20251003-00000007 | TT-20251003-00005 | EM | Region_1 | ARM0857 | ARM0857 | Enviroment | Air Condition | Change Fan | Ahmed Abdelfattah Ali Soltan | 10/03/2025 00:07:35 | 10/05/2025 17:44:07 | 10/03/2025 12:07:35 | Door opening alarm at ARM0857-P2_SRAN @ Generator_SG | 10/03/2025 00:06:58 | Minor | 65101 | Door opening alarm | 10/03/2025 00:04:51 | P2 | SRAN | dammam | Generator_SG | 2G NSA | ARM0857 | FLM_EM | [8 empty] | API | 10/03/2025 00:07:35 | 10/05/2025 17:02:18 | 10/05/2025 17:02:41 | 10/05/2025 17:02:46 | 10/05/2025 17:26:31 | 10/05/2025 17:44:07 |  | Ahmed Abdelfattah Ali Soltan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000057 | PCM-20251003-00000085 | TT-20251003-00090 | EM | Region_4 | HAW2301 | HAW2301 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 10/03/2025 01:26:35 | 10/17/2025 01:31:13 | 10/03/2025 13:26:35 | HIGH TEMP ALARM at HAW2301-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/03/2025 01:18:09 | Minor | 7103 | HIGH TEMP ALARM | 10/03/2025 01:18:04 | P3 | 2G | taif | Sceco | 2G NSA | HAW2301 | FLM_EM | [5 empty] | HIGH TEMP ALARM |  |  | API | 10/03/2025 01:26:35 | 10/04/2025 00:01:15 | 10/17/2025 01:31:00 |  |  | 10/17/2025 01:31:13 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000149 | PCM-20251003-00000278 | TT-20251003-00298 | EM | Region_1 | HMBY2429 | HMBY2429 | Enviroment | Genset failure_High Temperature | Change Generator water pump | Khaled Mohamed Abdulla Wahba | 10/03/2025 04:31:00 | 10/03/2025 17:34:36 | 10/03/2025 10:31:00 | Mains Failure at HMBY2429-P1-VIP_SRAN @ Generator_SG | 10/03/2025 04:20:55 | Major | 65109 | Mains Failure | 10/03/2025 04:20:51 | VIP | SRAN | dammam | Generator_SG | 2G NSA | HMBY2429 | FLM_EM | [8 empty] | API | 10/03/2025 04:31:00 | 10/03/2025 04:44:42 | 10/03/2025 04:44:50 | 10/03/2025 04:44:56 | 10/03/2025 05:21:48 | 10/03/2025 17:34:36 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251003000178 | PCM-20251003-00000337 | TT-20251003-00344 | EM | Region_4 | JED0723 | JED0723 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sajid Nazir Muhammad Nazir | 10/03/2025 05:29:50 | 10/03/2025 07:08:39 | 10/03/2025 09:29:50 | POWER_FAIL at JED0723-OCS1 @ Sceco | 10/03/2025 05:28:13 | Critical | 1-125 | POWER_FAIL | 10/03/2025 05:28:02 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0723 | FLM_EM | [5 empty] | 1-1-D-17-F5PIU-OTHER |  |  | API | 10/03/2025 05:29:50 | 10/03/2025 05:39:29 | 10/03/2025 06:57:33 | 10/03/2025 06:57:36 | 10/03/2025 06:57:44 | 10/03/2025 07:08:39 |  | Sajid Nazir Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251003000196 | PCM-20251003-00000364 | TT-20251003-00378 | EM | Region_1 | JBL0531 | JBL0531 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/03/2025 06:07:06 | 10/03/2025 16:33:34 | 10/03/2025 18:07:06 | Door opening alarm at JBL0531-P3_SRAN-PC @ Power Cube | 10/03/2025 06:06:40 | Minor | 65101 | Door opening alarm | 10/03/2025 06:06:35 | P3 | SRAN | jubail | Power Cube | 2G NSA | JBL0531 | FLM_EM | [8 empty] | API | 10/03/2025 06:07:06 | 10/03/2025 16:33:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000205 | PCM-20251003-00000375 | TT-20251003-00388 | Reference_EM | Region_1 | JBL0531 | JBL0531 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/03/2025 06:19:26 | 10/03/2025 16:33:36 | 10/03/2025 18:19:26 | Low battery voltage at JBL0531-P3_SRAN-PC @ Power Cube | 10/03/2025 06:08:50 | Minor | 65110 | Low battery voltage | 10/03/2025 06:08:47 | P3 | SRAN | jubail | Power Cube | 2G NSA | JBL0531 | FLM_EM | [8 empty] | API | 10/03/2025 06:19:26 | 10/03/2025 16:33:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000211 | PCM-20251003-00000386 | TT-20251003-00402 | EM | Region_1 | HMBY2429 | HMBY2429 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/03/2025 06:35:00 | 10/03/2025 21:29:47 | 10/03/2025 12:35:00 | Door opening alarm at HMBY2429-P1-VIP_SRAN @ Generator_SG | 10/03/2025 06:34:30 | Major | 65101 | Door opening alarm | 10/03/2025 06:34:26 | VIP | SRAN | dammam | Generator_SG | 2G NSA | HMBY2429 | FLM_EM | [8 empty] | API | 10/03/2025 06:35:00 | 10/03/2025 17:34:51 | 10/03/2025 21:29:33 |  |  | 10/03/2025 21:29:47 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251003000255 | PCM-20251003-00000446 | TT-20251003-00468 | Reference_telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/03/2025 07:33:03 | 10/03/2025 23:54:17 | 10/03/2025 13:33:03 | BASE STATION SERVICE PROBLEM(No connection to unit) at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2(Ref:TT-20250909-00747) | 09/10/2025 06:33:44 | Major | 7116 | BASE STATION SERVICE PROBLEM | 09/10/2025 06:33:44 | P2 | 2G | jeddah | Sceco | 5G SA | RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 | FLM_TE | [8 empty] | API | 10/03/2025 07:33:03 | 10/03/2025 23:54:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000352 | PCM-20251003-00000600 | TT-20251003-00651 | EM | Region_4 | JED2043 | JED2043 | Enviroment | SCECO_Failure | SCECO auto restored | Amer Attallah Awadallah | 10/03/2025 09:49:29 | 10/10/2025 11:32:19 | 10/03/2025 21:49:29 | AIRCON 1 FAILURE at JED2043-CA-L800-L1800-NR2.6-SBTS-VIP @ Sceco | 10/03/2025 09:40:59 | Minor | 7103 | AIRCON 1 FAILURE | 10/03/2025 09:40:54 | VIP | 2G | jeddah | Sceco | 2G NSA | JED2043 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/03/2025 09:49:29 | 10/10/2025 10:44:06 | 10/10/2025 10:45:51 | 10/10/2025 10:45:53 | 10/10/2025 10:45:56 | 10/10/2025 11:32:19 |  | Amer Attallah Awadallah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000398 | PCM-20251003-00000670 | TT-20251003-00723 | Reference_telecom | Region_4 | HAW1M4360 | HAW2360 |  |  |  | Rashid Shafique | 10/03/2025 11:02:51 | 10/03/2025 13:53:20 | 10/03/2025 23:02:51 | BASE STATION NOTIFICATION (Fan failure) at HAW1M4360-P2 @ Sceco | 10/03/2025 10:32:44 | Minor | 7652 | BASE STATION NOTIFICATION | 10/03/2025 10:32:26 | P2 | 3G | taif | Sceco | 3G NSA | HAW1M4360 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/03/2025 11:02:51 | 10/03/2025 13:53:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000438 | PCM-20251003-00000734 | TT-20251003-00785 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/03/2025 11:49:53 | 10/20/2025 12:32:27 | 10/03/2025 23:49:53 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/03/2025 11:41:50 | Minor | 7115 | BASE STATION INFORMATION | 10/03/2025 11:41:40 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/03/2025 11:49:53 | 10/03/2025 18:36:56 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000484 | PCM-20251003-00000816 | TT-20251002-02079 | Reference_telecom | Region_4 | TUR1M7694 | TUR0694 |  |  |  | Rashid Shafique | 10/03/2025 12:41:40 | 10/03/2025 13:53:21 | 10/03/2025 18:41:40 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TUR1M7694-L800-CA-P2 @ Sceco | 10/02/2025 15:19:39 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/02/2025 15:15:16 | P2 | 4G | taif | Sceco | LTE NSA | TUR1M7694 | FLM_TE |  |  | PCM-20251003-00000761 | Thanks to check | Thanks to check |  |  |  | API | 10/03/2025 12:41:40 | 10/03/2025 13:53:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000525 | PCM-20251003-00000872 | TT-20251003-00889 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/03/2025 13:29:32 | 10/04/2025 11:39:18 | 10/04/2025 01:29:32 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/03/2025 13:21:26 | Minor | 7103 | AIRCON 1 FAILURE | 10/03/2025 13:21:16 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/03/2025 13:29:32 | 10/04/2025 11:39:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000583 | PCM-20251003-00000962 | TT-20251003-00975 | Reference_telecom | Region_4 | HAW1M8292 | HAW2292 | Equipment | SFP_BTS | Clean SFP | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/03/2025 14:35:38 | 10/19/2025 08:48:40 | 10/04/2025 02:35:38 | BASE STATION INFORMATION (Unit temperature is high) at HAW1M8292-P3-CA-L800 @ Generator_SG | 10/03/2025 13:55:38 | Minor | 7115 | BASE STATION INFORMATION | 10/03/2025 13:55:30 | P3 | 4G | taif | Generator_SG | LTE NSA | HAW1M8292 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/03/2025 14:35:38 | 10/04/2025 11:26:21 | 10/19/2025 08:48:33 |  |  | 10/19/2025 08:48:40 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000615 | PCM-20251003-00001014 | TT-20251003-01024 | EM | Region_4 | SIR0069 | SIR0069 |  |  |  | Hamdy Shoueib Salem Ismail | 10/03/2025 15:01:28 | 10/05/2025 18:06:09 | 10/04/2025 03:01:28 | RECTIFIER MAINS POWER FAILURE at SIR0069-GSM-UMTS-P2-USF @ Sceco | 10/03/2025 14:53:27 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/03/2025 14:53:20 | P2 | 2G | adam | Sceco | 2G NSA | SIR0069 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/03/2025 15:01:28 | 10/05/2025 18:06:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000656 | PCM-20251003-00001080 | TT-20251003-00904 | Reference_telecom | Region_1 | DAM2M7270 | DAM0270 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/03/2025 15:32:55 | 10/03/2025 15:37:44 | 10/04/2025 03:32:55 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M7270-P1-SHOP-HUB-WDM-L800 @ Sceco | 10/03/2025 10:41:31 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/03/2025 10:41:26 | P1 | 4G | dammam | Sceco | 2G NSA | DAM2M7270 | FLM_TE |  |  | PCM-20251003-00001015 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/03/2025 15:32:55 | 10/03/2025 15:37:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251003000681 | PCM-20251003-00001124 | TT-20251003-01174 | Reference_telecom | Region_6 | SAB0057 | SAB0057 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/03/2025 16:04:29 | 10/04/2025 20:49:32 | 10/04/2025 04:04:29 | ReplaceableUnitMissing observed in SAB0057_10 towards 10.10.155.129 @ Sceco_STB | 10/03/2025 04:04:07 | Minor |  | ReplaceableUnitMissing | 10/03/2025 04:04:03 | P1 | 2G | baish | Sceco_STB | TX NSA | SAB0057 | FLM_TE | [8 empty] | API | 10/03/2025 16:04:29 | 10/03/2025 23:39:01 | 10/04/2025 20:32:51 | 10/04/2025 20:32:57 | 10/04/2025 20:49:32 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000714 | PCM-20251003-00001172 | TT-20251003-00858 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/03/2025 16:37:29 | 10/21/2025 18:15:58 | 10/03/2025 22:37:29 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/03/2025 12:45:34 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/03/2025 12:45:24 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251003-00000844 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/03/2025 16:37:29 | 10/20/2025 14:29:24 | 10/21/2025 18:15:50 |  |  | 10/21/2025 18:15:58 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000721 | PCM-20251003-00001186 | TT-20251003-01237 | EM | Region_6 | BHAB1M8442 | BHAB2442 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/03/2025 16:48:25 | 10/03/2025 17:24:07 | 10/04/2025 04:48:25 | RECTIFIER MAIN POWER FAILURE at BHAB1M8442-G9-L8-SBTS-P3-WBB-G3 @ Generator_SG | 10/03/2025 16:46:44 | Minor | 7103 | RECTIFIER MAIN POWER FAILURE | 10/03/2025 16:33:30 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8442 | FLM_EM | [5 empty] | RECTIFIER MAIN POWER FAILURE |  |  | API | 10/03/2025 16:48:25 | 10/03/2025 17:24:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000805 | PCM-20251003-00001326 | TT-20251003-01384 | Reference_telecom | Region_2 | BUR6002 | BUR6002 |  |  |  | Raise Ahmed Nisar Ahmed | 10/03/2025 18:14:38 | 10/03/2025 18:58:00 | 10/04/2025 00:14:38 | RFC Port Underpower at BUR6002-DCU1 @ Sceco | 10/03/2025 13:49:15 | Major | 29803 | RFC Port Underpower | 10/03/2025 13:49:10 | VIP | SRAN | buraidah | Sceco | 2G NSA | BUR6002 | FLM_TE | [8 empty] | API | 10/03/2025 18:14:38 | 10/03/2025 18:58:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000808 | PCM-20251003-00001329 | TT-20251003-01388 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/03/2025 18:14:59 | 10/04/2025 17:40:14 | 10/04/2025 06:14:59 | Cell Capability Degraded at JED6008-DCU-P3 @ Sceco | 10/02/2025 19:30:43 | Minor | 28751 | Cell Capability Degraded | 10/02/2025 19:29:10 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/03/2025 18:14:59 | 10/04/2025 17:33:41 | 10/04/2025 17:40:07 |  |  | 10/04/2025 17:40:14 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000818 | PCM-20251003-00001346 | TT-20251003-01408 | EM | Region_6 | BCH1M8321 | BCH2321 |  |  |  | Fathy Mohamed | 10/03/2025 18:24:31 | 10/04/2025 12:29:59 | 10/04/2025 06:24:31 | RECTIFIER MODULE FAILURE at BCH1M8321-G9-L8-SBTS-P3 @ Generator_SG | 10/03/2025 18:16:42 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/03/2025 18:16:07 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8321 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/03/2025 18:24:31 | 10/04/2025 12:29:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251003000833 | PCM-20251003-00001371 | TT-20251003-01444 | Reference_telecom | Region_5 | MAK1M3552 | MAK0552 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/03/2025 18:44:34 | 10/21/2025 19:56:50 | 10/04/2025 00:44:34 | FAILURE IN WCDMA WBTS O&M CONNECTION at MAK1M3552-P2-USF (Ref:TT-20251002-02221) @ Sceco | 10/03/2025 13:54:17 | Major | 7750 | FAILURE IN WCDMA WBTS O&M CONNECTION | 09/30/2025 03:21:49 | P2 | 3G | makkah | Sceco | 3G SA | MAK1M3552 | FLM_TE | [8 empty] | API | 10/03/2025 18:44:34 | 10/21/2025 19:56:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000838 | PCM-20251003-00001382 | TT-20251003-01450 | Reference_telecom | Region_5 | WHT0780 | WHT0780 |  |  |  | Hazem Ali Moustafa Ali | 10/03/2025 18:52:22 | 10/18/2025 03:16:07 | 10/04/2025 00:52:22 | BASE STATION ANTENNA LINE PROBLEM (VSWR lower threshold exceeded) at WHT1M7780-G9-U9-NL8-SBTS-P3 (Re:TT-20251002-01845) @ Generator_SG | 10/03/2025 15:37:49 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/03/2025 15:37:38 | P3 | 2G | makkah | Generator_SG | 2G NSA | WHT1M7780 | FLM_TE | [5 empty] | VSWR lower threshold exceeded |  |  | API | 10/03/2025 18:52:22 | 10/18/2025 03:16:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000843 | PCM-20251003-00001390 | TT-20251003-01415 | Reference_telecom | Region_6 | ALA0021 | ALA0021 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/03/2025 18:56:13 | 10/04/2025 16:10:49 | 10/04/2025 06:56:13 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at ALA0021-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/03/2025 17:58:44 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/03/2025 17:58:34 | P2 | 2G | bisha | Sceco | 2G NSA | ALA0021 | FLM_TE |  |  | PCM-20251003-00001354 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/03/2025 18:56:13 | 10/03/2025 23:43:58 | 10/04/2025 16:10:35 |  |  | 10/04/2025 16:10:49 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000845 | PCM-20251003-00001393 | TT-20251003-01458 | Telecom | Region_1 | SAK2U6705 | SAK6005 |  |  |  | Syed Fawad Ali | 10/03/2025 18:56:33 | 10/15/2025 11:52:36 | 10/04/2025 00:56:33 | RF Out of Service at SAK2U6705-P3 @ Sceco | 10/03/2025 18:51:35 | Major | 29248 | RF Out of Service | 10/03/2025 18:50:02 | P3 | 4G | sakaka | Sceco | 2G SA | SAK2U6705 | FLM_TE | [8 empty] | API | 10/03/2025 18:56:33 | 10/04/2025 09:43:43 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000846 | PCM-20251003-00001394 | TT-20251003-01459 | Reference_telecom | Region_4 | SDY0739 | SDY0739 |  |  |  | Riasat Ali Allah Baksh | 10/03/2025 18:56:47 | 10/04/2025 21:29:53 | 10/04/2025 06:56:47 | BASE STATION INFORMATION (Unit temperature is high) at SDY1M7739-G9-U9-NL8-SBTS-P3 (Ref::TT-20251002-02263) | 10/03/2025 15:38:02 | Minor | 7115 | BASE STATION INFORMATION | 10/03/2025 15:38:02 | P3 | 2G | alaith | Sceco_STB | LTE NSA | SDY1M7739-G9-U9-NL8-SBTS-P3 | FLM_TE | [8 empty] | API | 10/03/2025 18:56:47 | 10/04/2025 21:29:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000852 | PCM-20251003-00001402 | TT-20251003-01465 | Reference_telecom | Region_5 | MAK0884 | MAK0884 | Equipment | FAN Cleaning | Clean FAN | KAMRAN AAMIR | 10/03/2025 18:59:03 | 10/04/2025 12:44:15 | 10/04/2025 06:59:03 | BASE STATION INFORMATION (No module fan detected) at MAK0884-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 (Ref:CM20251003000227) @ Sceco | 10/03/2025 08:13:52 | Minor | 7115 | BASE STATION INFORMATION | 10/03/2025 08:13:42 | P3 | 2G | makkah | Sceco | 5G NSA | MAK0884 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/03/2025 18:59:03 |  | 10/04/2025 11:52:29 | 10/04/2025 11:52:48 | 10/04/2025 12:03:10 | 10/04/2025 12:44:15 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000866 | PCM-20251003-00001430 | TT-20251003-01481 | Telecom | Region_1 | QRY0544 | QRY0544 | Transsmission | MW_LOW_RSL | Reset ODU | SARFARAZ MUHAMMAD HUSSAIN | 10/03/2025 19:09:27 | 10/19/2025 18:20:34 | 10/04/2025 07:09:27 | ODU CPU / Cable Open at QRY0544_1 on 10.154.19.164 @ Sceco | 10/03/2025 19:08:42 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/03/2025 19:03:54 | P1 | SRAN | quriyat | Sceco | TX NSA | QRY0544 | FLM_TE | [8 empty] | API | 10/03/2025 19:09:27 | 10/19/2025 18:20:34 | [5 empty] | SARFARAZ MUHAMMAD HUSSAIN | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251003000882 | PCM-20251003-00001449 | TT-20251003-01493 | Telecom | Region_1 | DAM0358 | DAM0358 | Equipment | SFP_BTS | Replace SFP | AbdalHafiz Sirageldin Mohamed Yasin | 10/03/2025 19:22:23 | 10/04/2025 11:02:01 | 10/04/2025 01:22:23 | BBU CPRI Interface Error at DAM0358-P2_SRAN @ Sceco | 10/03/2025 19:16:52 | Major | 26234 | BBU CPRI Interface Error | 10/03/2025 19:15:19 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0358 | FLM_TE | [8 empty] | API | 10/03/2025 19:22:23 | 10/04/2025 05:50:10 | 10/04/2025 11:00:34 | 10/04/2025 11:00:38 | 10/04/2025 11:00:41 | 10/04/2025 11:02:01 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000887 | PCM-20251003-00001459 | TT-20251003-01504 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/03/2025 19:33:14 | 10/19/2025 17:44:04 | 10/04/2025 01:33:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/03/2025 19:32:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/03/2025 19:32:17 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/03/2025 19:33:14 | 10/05/2025 11:02:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000909 | PCM-20251003-00001509 | TT-20251003-01564 | Telecom | Region_2 | RIY0216 | RIY0216 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Farmanullah Akbar Jan | 10/03/2025 20:18:11 | 10/15/2025 12:00:40 | 10/04/2025 00:18:11 | STC :: LINK DOWN B/W RIY0216--RIY0241 | 10/03/2025 20:12:57 | Critical | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/03/2025 20:12:57 | VIP | SRAN | riyadh | Sceco | DWDM NSA | RIY0216--RIY0241 | FLM_TE | [8 empty] | API | 10/03/2025 20:18:11 | 10/15/2025 12:00:40 | [5 empty] | Farmanullah Akbar Jan | STC |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000915 | PCM-20251003-00001523 | TT-20251003-01577 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/03/2025 20:26:57 | 10/03/2025 23:42:32 | 10/04/2025 08:26:57 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/03/2025 20:18:48 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/03/2025 20:18:39 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/03/2025 20:26:57 | 10/03/2025 23:42:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251003001012 | PCM-20251003-00001686 | TT-20251003-01730 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/03/2025 22:22:40 | 10/20/2025 12:32:31 | 10/04/2025 02:22:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/03/2025 22:22:02 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/03/2025 22:21:54 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/03/2025 22:22:40 | 10/05/2025 11:02:24 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003001024 | PCM-20251003-00001711 | TT-20251003-01752 | Reference_EM | Region_1 | RYDM2059 | RYDM2059 |  |  |  | Ansar Abbas Muhammad Iqbal | 10/03/2025 22:48:31 | 10/04/2025 11:08:45 | 10/04/2025 10:48:31 | Air condition 2 failure alarm at RYDM2059-P2_SRAN @ Sceco_STB | 10/03/2025 22:38:19 | Minor | 65105 | Air condition 2 failure alarm | 10/03/2025 22:38:16 | P2 | SRAN | dammam | Sceco_STB | 2G NSA | RYDM2059 | FLM_EM | [8 empty] | API | 10/03/2025 22:48:31 | 10/04/2025 11:08:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251003001029 | PCM-20251003-00001726 | TT-20251003-01569 | Telecom | Region_2 | RY2-ASG-02 | RY2 |  |  |  | Saddam hussain muhammad khan | 10/03/2025 23:03:07 | 10/15/2025 11:52:35 | 10/04/2025 11:03:07 | DWDM Link down at RY2-ASG-02 | 10/03/2025 20:12:51 | Minor | 15269 | LOS | 10/03/2025 20:12:51 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | DWDM Link down at RY2-ASG-02 | FLM_TE |  |  | PCM-20251003-00001545 | alarm cleared now | alarm cleared now |  |  |  | API | 10/03/2025 23:03:07 | [7 empty] | STC |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000015 | PCM-20251004-00000032 | TT-20251004-00038 | EM | Region_6 | NMR1M8401 | NMR2401 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/04/2025 00:35:57 | 10/06/2025 11:02:59 | 10/04/2025 12:35:57 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at NMR1M8401-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/04/2025 00:27:49 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/04/2025 00:27:45 | P3 | 4G | Baha | Generator_SG | LTE NSA | NMR1M8401 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/04/2025 00:35:57 | 10/06/2025 11:02:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000067 | PCM-20251004-00000133 | TT-20251004-00149 | EM | Region_6 | JDJZ1M7787 | JDJZ0787 |  |  |  | Aziz Ul Haq Umar Gul | 10/04/2025 02:33:45 | 10/04/2025 07:40:04 | 10/04/2025 14:33:45 | SHELTER DOOR OPEN at JDJZ1M7787-L800-P3-SBTS @ Sceco | 10/04/2025 02:33:25 | Minor | 7103 | SHELTER DOOR OPEN | 10/04/2025 02:23:39 | P3 | 4G | derb | Sceco | LTE NSA | JDJZ1M7787 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/04/2025 02:33:45 | 10/04/2025 07:40:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000098 | PCM-20251004-00000187 | TT-20251004-00146 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/04/2025 03:40:12 | 10/20/2025 12:32:31 | 10/04/2025 09:40:12 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/04/2025 02:22:09 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/04/2025 02:21:59 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251004-00000131 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/04/2025 03:40:12 | 10/05/2025 11:02:25 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000131 | PCM-20251004-00000235 | TT-20251004-00267 | Reference_telecom | Region_6 | MKW9711 | MKW9711 |  |  |  | Manzoor Ahmed | 10/04/2025 04:20:42 | 10/04/2025 10:24:41 | 10/04/2025 16:20:42 | LagPortDown observed in MKW9711_02 towards 10.221.244.69 @ Sceco | 10/03/2025 16:22:37 | Minor |  | LagPortDown | 10/03/2025 16:20:26 | P3 | Repeater | makhwa | Sceco | TX NSA | MKW9711 | FLM_TE | [8 empty] | API | 10/04/2025 04:20:42 | 10/04/2025 10:24:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000136 | PCM-20251004-00000241 | TT-20251004-00271 | Reference_telecom | Region_6 | MKW0037 | MKW0037 |  |  |  | Manzoor Ahmed | 10/04/2025 04:24:18 | 10/04/2025 10:24:41 | 10/04/2025 16:24:18 | LagPortDown observed in MKW0037_01 towards 10.221.244.70 @ Sceco | 10/03/2025 16:24:09 | Minor |  | LagPortDown | 10/03/2025 16:24:02 | P3 | 2G | makhwa | Sceco | TX NSA | MKW0037 | FLM_TE | [8 empty] | API | 10/04/2025 04:24:18 | 10/04/2025 10:24:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000208 | PCM-20251004-00000360 | TT-20251004-00411 | Reference_telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/04/2025 06:36:32 | 10/04/2025 16:29:40 | 10/04/2025 12:36:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2(Ref:TT-20250909-00747) | 09/10/2025 06:33:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 09/10/2025 06:33:43 | P2 | 2G | jeddah | Sceco | LTE SA | RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 | FLM_TE | [8 empty] | API | 10/04/2025 06:36:32 | 10/04/2025 16:29:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004000257 | PCM-20251004-00000432 | TT-20251004-00489 | Reference_telecom | Region_4 | JED0887 | JED0887 | Equipment | BSS_HW_fault | Replace System Module | Khaled Mohammad Abdallah | 10/04/2025 07:42:40 | 10/08/2025 09:45:15 | 10/04/2025 19:42:40 | ReplaceableUnitProblem observed in JED0887 towards 10.1.229.163 @ Sceco | 10/03/2025 19:43:19 | Minor |  | ReplaceableUnitProblem | 10/03/2025 19:42:11 | P2 | 2G | jeddah | Sceco | TX NSA | JED0887 | FLM_TE | [8 empty] | API | 10/04/2025 07:42:40 |  | 10/08/2025 07:40:36 | 10/08/2025 07:40:38 | 10/08/2025 07:40:41 | 10/08/2025 09:45:15 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000285 | PCM-20251004-00000477 | TT-20251004-00520 | Reference_telecom | Region_2 | RIYB2U6756 | RIYB6056 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/04/2025 08:11:49 | 10/05/2025 12:01:47 | 10/04/2025 20:11:49 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6756-CA-L800-P3 @ Sceco | 10/04/2025 05:05:12 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/04/2025 05:05:09 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6756 | FLM_TE |  |  | PCM-20251004-00000464 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/04/2025 08:11:49 | 10/05/2025 12:01:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000291 | PCM-20251004-00000486 | TT-20251004-00438 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/04/2025 08:20:15 | 10/20/2025 12:32:32 | 10/04/2025 12:20:15 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/04/2025 03:06:13 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 03:06:04 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251004-00000395 | kindly check and confirm no dust or air blockage | kindly check and confirm no dust or air blockage |  |  |  | API | 10/04/2025 08:20:15 | 10/05/2025 11:02:25 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000344 | PCM-20251004-00000593 | TT-20251004-00642 | EM | Region_6 | ABBS1M8180 | ABBS2180 |  |  |  | Muhammad Naeem Taj Din | 10/04/2025 09:15:10 | 10/04/2025 09:21:07 | 10/04/2025 21:15:10 | RECTIFIER MAINS POWER FAILURE at ABBS1M8180-G9-L800-L1800-SBTS-P3-WBB-G3 @ Generator_SG | 10/04/2025 09:07:37 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/04/2025 09:06:41 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8180 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/04/2025 09:15:10 | 10/04/2025 09:21:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000390 | PCM-20251004-00000662 | TT-20251004-00711 | EM | Region_4 | DGB2169 | DGB2169 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/04/2025 09:58:01 | 10/12/2025 00:01:57 | 10/04/2025 21:58:01 | AIRCON 1 FAILURE at DGB2169-GSM-P3 @ Sceco | 10/04/2025 09:49:39 | Minor | 7103 | AIRCON 1 FAILURE | 10/04/2025 09:49:27 | P3 | 2G | alaith | Sceco | 2G NSA | DGB2169 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/04/2025 09:58:01 | 10/12/2025 00:01:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000396 | PCM-20251004-00000672 | TT-20251004-00721 | EM | Region_6 | BHAB1M8041 | BHAB2041 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/04/2025 10:04:44 | 10/04/2025 10:16:31 | 10/04/2025 22:04:44 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at BHAB1M8041-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/04/2025 09:56:34 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/04/2025 09:56:30 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8041 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/04/2025 10:04:44 | 10/04/2025 10:16:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251004000421 | PCM-20251004-00000711 | TT-20250929-02753 | MW_HC | Region_4 | JED0131 | JED0131 | Transsmission | SFP_Transmission | Reset SFP | Asad Ullah Rahim Said | 10/04/2025 10:24:55 | 10/07/2025 14:09:43 | 10/04/2025 22:24:55 | As per bo request Nokia MW HC need to check B2B port 1.5 at JED0131 10.10.177.183 counting TDF errors | 09/29/2025 18:52:57 | Minor | 113388 | LOF | 09/29/2025 18:52:55 | P2 | 2G | jeddah | Sceco | TX NSA | JED0131 | FLM_TE |  |  | PCM-20251004-00000545 | Dear FLM team, Approved | Dear FLM team, Approved |  |  |  | API | 10/04/2025 10:24:55 | 10/07/2025 13:07:29 | 10/07/2025 13:31:24 | 10/07/2025 13:31:27 | 10/07/2025 13:31:29 | 10/07/2025 14:09:43 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004000431 | PCM-20251004-00000723 | TT-20251004-00766 | Telecom | Region_4 | JED0107 | JED0107 | Equipment | BTS_Cable | Reconnect Sync Cable | Mohammed Ramadan A Abu Abid | 10/04/2025 10:32:37 | 10/19/2025 10:36:06 | 10/04/2025 16:32:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0107-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P1-VIP @ Sceco | 10/04/2025 10:31:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 10:31:43 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0107 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/04/2025 10:32:37 | 10/04/2025 10:48:44 | 10/19/2025 10:35:50 |  |  | 10/19/2025 10:36:06 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000455 | PCM-20251004-00000754 | TT-20251004-00804 | Reference_EM | Region_1 | DRN0109 | DRN0109 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/04/2025 10:53:16 | 10/04/2025 21:23:46 | 10/04/2025 22:53:16 | high temprature 32 at DRN0109-P3_SRAN @ Sceco | 10/04/2025 10:43:02 | Minor | 65102 | high temprature 32 | 10/04/2025 10:42:58 | P3 | SRAN | dammam | Sceco | 2G NSA | DRN0109 | FLM_EM | [8 empty] | API | 10/04/2025 10:53:16 | 10/04/2025 21:23:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000510 | PCM-20251004-00000826 | TT-20251004-00857 | Reference_telecom | Region_4 | HAW1M4360 | HAW2360 |  |  |  | Rashid Shafique | 10/04/2025 11:22:12 | 10/04/2025 11:42:21 | 10/04/2025 23:22:12 | BASE STATION NOTIFICATION (Fan failure) at HAW1M4360-P2 @ Sceco | 10/04/2025 10:52:02 | Minor | 7652 | BASE STATION NOTIFICATION | 10/04/2025 10:51:38 | P2 | 3G | taif | Sceco | 3G NSA | HAW1M4360 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/04/2025 11:22:12 | 10/04/2025 11:42:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004000571 | PCM-20251004-00000929 | TT-20251004-00927 | Telecom | Region_4 | JED0276 | JED0276 | Equipment | SFP_BTS | Clean SFP | Asad Ullah Rahim Said | 10/04/2025 11:56:17 | 10/05/2025 17:34:31 | 10/04/2025 17:56:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0276-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-HUB-WDM-FON @ Sceco | 10/04/2025 11:55:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 11:55:13 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0276 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/04/2025 11:56:17 | 10/05/2025 12:08:17 | 10/05/2025 17:03:09 | 10/05/2025 17:03:12 | 10/05/2025 17:03:14 | 10/05/2025 17:34:31 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251004000603 | PCM-20251004-00000983 | TT-20251004-00614 | Reference_telecom | Region_4 | JED2125 | JED2125 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/04/2025 12:19:07 | 10/04/2025 12:19:07 | 10/05/2025 00:19:07 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2125-CA-L800-NR2.6-SBTS -P3 @ Sceco | 10/04/2025 06:58:47 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/04/2025 06:57:31 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2125 | FLM_TE |  |  | PCM-20251004-00000809 | Dear FLM team, kindly perform HC for MW JED0850-JED0198 | Dear FLM team, kindly perform HC for MW JED0850-JED0198 |  |  |  | API | 10/04/2025 12:19:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004000674 | PCM-20251004-00001094 | TT-20251004-01082 | Reference_EM | Region_1 | JBL0473 | JBL0473 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Salah Abdalgadir Ahmed | 10/04/2025 13:31:19 | 10/04/2025 17:38:01 | 10/05/2025 01:31:19 | high temprature 40 at JBL0473-P2_SRAN @ Sceco | 10/04/2025 13:21:03 | Minor | 65103 | high temprature 40 | 10/04/2025 13:20:59 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0473 | FLM_EM | [8 empty] | API | 10/04/2025 13:31:19 | 10/04/2025 17:26:50 | 10/04/2025 17:37:53 |  |  | 10/04/2025 17:38:01 |  | Ahmed Salah Abdalgadir Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000694 | PCM-20251004-00001121 | TT-20251004-01107 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/04/2025 13:51:28 | 10/04/2025 14:17:55 | 10/05/2025 01:51:28 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/04/2025 13:43:04 | Minor | 7103 | AIRCON 1 FAILURE | 10/04/2025 13:42:58 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/04/2025 13:51:28 | 10/04/2025 14:17:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000705 | PCM-20251004-00001134 | TT-20251004-01125 | Telecom | Region_4 | JDMD0861 | JDMD0861 |  |  |  | Nazeer Mohammed | 10/04/2025 14:00:46 | 10/04/2025 15:42:39 | 10/05/2025 02:00:46 | ODU CPU / Cable Open at JDMD0861_1 on 10.154.115.2 @ Generator_DG | 10/04/2025 13:59:55 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/04/2025 13:55:48 | P1 | 2G | jeddah | Generator_DG | TX NSA | JDMD0861 | FLM_TE | [8 empty] | API | 10/04/2025 14:00:46 | 10/04/2025 15:42:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000743 | PCM-20251004-00001199 | TT-20251004-01191 | EM | Region_4 | MAS1M7358 | MAS0358 |  |  |  | Walid Magdy Tawfik Elbana | 10/04/2025 14:29:42 | 10/05/2025 08:21:13 | 10/05/2025 02:29:42 | RECTIFIER MAINS POWER FAILURE at MAS1M7358-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/04/2025 14:21:22 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/04/2025 14:21:14 | P3 | 4G | taif | Sceco | LTE NSA | MAS1M7358 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/04/2025 14:29:42 | 10/05/2025 08:21:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251004000765 | PCM-20251004-00001236 | TT-20251004-01204 | Telecom | Region_1 | DRN0769 | DRN0769 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/04/2025 14:39:30 | 10/23/2025 11:09:33 | 10/04/2025 20:39:30 | 2(2G) 2(3G) 2(LTE) sites down under DRN2657-P3,DRN0769-P3/DM1MBSCH01 @ Generator_SG | 10/04/2025 14:30:55 | Major | 21825 | CSL Fault | 10/04/2025 14:30:53 | P3 | SRAN | dammam | Generator_SG | 2G_3G_LTE SA | DRN2657-P3 2G_3G_LTE,DRN0769-P3 2G_3G_LTE | FLM_EM | DRN0769 | Hub:- DRN0769 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251004-00001228 | Hub:- DRN0769 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- DRN0769 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/04/2025 14:39:30 | 10/15/2025 14:59:11 | 10/23/2025 11:09:22 |  |  | 10/23/2025 11:09:33 |  | Mohamed Ramadan Mohamed Gomaa | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251004000812 | PCM-20251004-00001306 | TT-20251004-01290 | Telecom | Region_4 | MKJD1M9570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/04/2025 15:14:42 | 10/07/2025 17:45:23 | 10/05/2025 03:14:42 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MKJD1M9570-P3-L800-SBTS @ Generator_DG | 10/04/2025 15:06:27 | Minor | 7115 | BASE STATION INFORMATION | 10/04/2025 15:06:23 | P2 | 4G | jeddah | Generator_DG | LTE NSA | MKJD1M9570 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/04/2025 15:14:42 | 10/07/2025 17:45:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000885 | PCM-20251004-00001423 | TT-20250922-01793 | MW_HC | Region_2 | SAR0325 | SAR0325 |  |  |  | Raise Ahmed Nisar Ahmed | 10/04/2025 16:09:43 | 10/05/2025 15:05:17 | 10/05/2025 04:09:43 | Huawei MW HC_P2 Observing Errors at SAR0325-SAR0324 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P2 | SRAN | buraidah | Generator_SG | TX NSA | SAR0325-SAR0324 | FLM_TE |  |  | PCM-20251004-00001406 | Approved as per FLM TS | Approved as per FLM TS |  |  |  | API | 10/04/2025 16:09:43 | 10/05/2025 15:05:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004000962 | PCM-20251004-00001538 | TT-20251004-01532 | Reference_EM | Region_3 | TBQL2M5233 | TBQL0233 |  |  |  | Moustafa Samir Omar | 10/04/2025 17:13:59 | 10/14/2025 17:30:24 | 10/04/2025 23:13:59 | Mains Failure at TBQL2M5233-P1-HUB @ Generator_DG | 10/04/2025 17:03:50 | Major | 65109 | Mains Failure | 10/04/2025 17:03:46 | P1 | 2G | tabouk | Generator_DG | 2G NSA | TBQL2M5233 | FLM_EM | [8 empty] | API | 10/04/2025 17:13:59 | 10/05/2025 15:43:20 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251004001009 | PCM-20251004-00001622 | TT-20251004-01611 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/04/2025 17:52:12 | 10/07/2025 14:35:15 | 10/04/2025 23:52:12 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/04/2025 14:52:12 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/04/2025 14:51:58 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/04/2025 17:52:12 | 10/07/2025 14:35:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004001020 | PCM-20251004-00001644 | TT-20251004-01029 | Reference_telecom | Region_6 | TLT1M7752 | TLT0752 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/04/2025 17:59:10 | 10/04/2025 18:21:29 | 10/05/2025 05:59:10 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TLT1M7752-G9-L9-NL18-SBTS-P3 @ Generator_SG | 10/04/2025 10:58:30 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/04/2025 10:58:02 | P3 | 4G | tathleeth | Generator_SG | LTE NSA | TLT1M7752 | FLM_TE |  |  | PCM-20251004-00001624 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/04/2025 17:59:10 | 10/04/2025 18:13:46 | 10/04/2025 18:21:21 |  |  | 10/04/2025 18:21:29 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251004001023 | PCM-20251004-00001647 | TT-20251004-01251 | Telecom | Region_4 | JED0791 | JED0791 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/04/2025 17:59:32 | 10/04/2025 17:59:32 | 10/05/2025 05:59:32 | BASE STATION ANTENNA LINE PROBLEM at JED0791-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/04/2025 14:43:34 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/04/2025 14:43:30 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0791 | FLM_TE |  |  | PCM-20251004-00001257 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/04/2025 17:59:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004001054 | PCM-20251004-00001690 | TT-20251004-01486 | Telecom | Region_4 | JDJZ1M7870 | JDJZ0870 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/04/2025 18:16:39 | 10/16/2025 11:18:55 | 10/05/2025 00:16:39 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDJZ1M7870-G9-NL8-L18-SBTS-P3 @ Sceco | 10/04/2025 16:40:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 16:40:26 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JDJZ1M7870 | FLM_TE |  |  | PCM-20251004-00001498 | RSSI alarm active at site, kindly check | RSSI alarm active at site, kindly check |  |  |  | API | 10/04/2025 18:16:39 | 10/04/2025 20:24:19 | 10/16/2025 11:18:49 |  |  | 10/16/2025 11:18:55 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004001082 | PCM-20251004-00001732 | TT-20251004-01587 | Telecom | Region_2 | RIY2949 | RIY2949 | Enviroment | Circuit Breaker/Rectifier | Change rectifier main breaker | Khan zeb Shah nawaz | 10/04/2025 18:53:18 | 10/04/2025 19:12:34 | 10/05/2025 06:53:18 | BO need to do HC for site RIY2949 | 10/04/2025 17:39:00 | Minor | 676767672 | Health Check-WO to TE FME | 10/04/2025 17:39:00 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2949 | FLM_TE | RIY2949 |  | PCM-20251004-00001621 | Related to TE | Related to TE |  |  |  | API | 10/04/2025 18:53:18 | 10/04/2025 19:11:03 | 10/04/2025 19:12:06 |  |  | 10/04/2025 19:12:34 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004001086 | PCM-20251004-00001740 | TT-20251004-01709 | Reference_telecom | Region_6 | RYAB1M7651 | RYAB0651 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/04/2025 19:01:51 | 10/05/2025 02:50:31 | 10/05/2025 01:01:51 | BASE STATION SERVICE PROBLEM (No feedback signal) at RYAB1M7651-G9-L8-L18-L21-SBTS-P2 (Ref:TT-20250929-00960) @ Sceco | 09/29/2025 18:54:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 09/29/2025 18:54:26 | P2 | 4G | abha | Sceco | LTE_Cell SA | RYAB1M7651 | FLM_TE | [5 empty] | No feedback signal |  |  | API | 10/04/2025 19:01:51 | 10/04/2025 23:52:26 | 10/05/2025 02:50:21 |  |  | 10/05/2025 02:50:31 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004001099 | PCM-20251004-00001757 | TT-20251004-01732 | Reference_telecom | Region_6 | ABH1U6700 | ABH6000 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Amir Sohail | 10/04/2025 19:15:22 | 10/05/2025 00:40:09 | 10/05/2025 01:15:22 | BASE STATION ANTENNA LINE PROBLEM (VSWR upper threshold exceeded) at ABH1U6700-G9-L18-SBTS-P3 (Ref:TT-20250908-01429) | 08/09/2025 21:26:14 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 08/09/2025 21:26:14 | P3 | 4G | abha | Sceco | LTE SA | ABH1U6700 | FLM_TE | [8 empty] | API | 10/04/2025 19:15:22 | 10/04/2025 20:08:49 | 10/05/2025 00:39:40 |  |  | 10/05/2025 00:40:09 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251004001120 | PCM-20251004-00001793 | TT-20251004-01774 | Telecom | Region_4 | JED1M7732 | JED0732 | Equipment | BSS_HW_Stuck | Reset ALD | MALIK ATIF ZAMAN | 10/04/2025 19:50:00 | 10/19/2025 17:44:03 | 10/05/2025 01:50:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/04/2025 19:49:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 19:49:10 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/04/2025 19:50:00 | 10/05/2025 11:02:33 | 10/06/2025 15:54:20 | 10/06/2025 15:54:22 | 10/06/2025 16:26:58 | 10/06/2025 17:24:53 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004001202 | PCM-20251004-00001944 | TT-20251004-01952 | Reference_telecom | Region_1 | DMHF2M7081 | DMHF0081 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/04/2025 21:58:48 | 10/04/2025 23:10:33 | 10/05/2025 09:58:48 | Cell RX Channel Interference Noise Power Unbalanced at DMHF2M7081-P1-HUB-L800-CA @ Generator_SG | 10/04/2025 18:46:11 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/04/2025 18:46:07 | P1 | 4G | hafouf | Generator_SG | 2G NSA | DMHF2M7081 | FLM_TE |  |  | PCM-20251004-00001936 | Need FLM to make RF path HC for RRU 121 | Need FLM to make RF path HC for RRU 121 |  |  |  | API | 10/04/2025 21:58:48 | 10/04/2025 23:10:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004001252 | PCM-20251004-00002028 | TT-20251004-01921 | Telecom | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/04/2025 23:07:05 | 10/05/2025 07:46:42 | 10/05/2025 05:07:05 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TURY0688-GSM-P3 @ Sceco | 10/04/2025 21:15:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 21:15:46 | P3 | 2G | taif | Sceco | 5G_Cell SA | TURY0688 | FLM_TE |  |  | PCM-20251004-00001910 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/04/2025 23:07:05 | 10/05/2025 07:46:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004001254 | PCM-20251004-00002030 | TT-20251004-02012 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/04/2025 23:08:09 | 10/20/2025 12:32:37 | 10/05/2025 05:08:09 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MKYL0914-GSM-UMTS-P3 @ Sceco | 10/04/2025 22:44:50 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/04/2025 22:44:39 | P3 | 2G | alaith | Sceco | 5G_Cell SA | MKYL0914 | FLM_TE |  |  | PCM-20251004-00001998 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/04/2025 23:08:09 | 10/06/2025 17:25:49 | [6 empty] | Force_Majeure |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251004001285 | PCM-20251004-00002095 | TT-20251004-02080 | Reference_telecom | Region_1 | SMN0829 | SMN0829 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/04/2025 23:55:23 | 10/05/2025 00:04:32 | 10/05/2025 11:55:23 | RF Unit RX Channel RTWP/RSSI Unbalanced at SMN0829-P3-USF_SRAN @ Sceco | 10/04/2025 20:55:11 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/04/2025 20:55:08 | P3 | SRAN | hafr | Sceco | 2G NSA | SMN0829 | FLM_TE | [8 empty] | API | 10/04/2025 23:55:23 | 10/05/2025 00:04:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000007 | PCM-20251005-00000016 | TT-20251005-00012 | Reference_EM | Region_1 | DAM0311 | DAM0311 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/05/2025 00:11:23 | 10/05/2025 00:47:38 | 10/05/2025 04:11:23 | Violation against FLM as KB2_LH node is isolated while team at site performing the activity under CRQ000000535274 | 10/05/2025 00:11:02 | Critical | 1-12843 | OSC_LOS | 10/05/2025 00:10:46 | VIP | SRAN | dammam | Sceco_STB | DWDM NSA | DAM0311 | FLM_TE | [5 empty] | 0-TO KB2(1-A)-7-G2AST4-1(RM1/TM1(TO KB2, G6WDAPXF(1-A02)-RM2/TM2))-OSC:1 |  |  | API | 10/05/2025 00:11:23 | 10/05/2025 00:47:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000016 | PCM-20251005-00000023 | TT-20251005-00020 | EM | Region_1 | DRN-6034-NE40E-X3-P&PE-01 | DRN6034 |  |  |  | Meraj Husain Idd Baksh | 10/05/2025 00:11:57 | 10/05/2025 13:51:24 | 10/05/2025 04:11:57 | Violation :: The Device is offline at KBR-3137 & DRN-0994 & KB2-ASG-02 & KB2-ASG-01 under CRQ000000535274 | 10/05/2025 00:11:44 | Critical | 101-7 | The Device is offline | 10/05/2025 00:11:43 | VIP | IPRAN | dammam | Sceco | IPRAN SA | DRN-6034-NE40E-X3-P&PE-01 | FLM_TE | [8 empty] | API | 10/05/2025 00:11:57 | 10/05/2025 00:40:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000062 | PCM-20251005-00000105 | TT-20251005-00124 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/05/2025 00:48:35 | 10/20/2025 12:32:33 | 10/05/2025 04:48:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/05/2025 00:47:39 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 00:47:33 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/05/2025 00:48:35 | 10/05/2025 11:02:36 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000070 | PCM-20251005-00000681 | TT-20251005-00710 | Reference_EM | Region_1 | DRN0125 | DRN0125 | Enviroment | Air Condition | Change Fan | Ahmed Abdelfattah Ali Soltan | 10/05/2025 01:05:38 | 10/06/2025 13:52:50 | 10/05/2025 13:05:38 | Low battery voltage at DRN0125-P3_SRAN @ Sceco | 10/05/2025 00:55:29 | Minor | 65110 | Low battery voltage | 10/05/2025 00:55:26 | P3 | SRAN | dammam | Sceco | 2G NSA | DRN0125 | FLM_EM | [8 empty] | API | 10/05/2025 01:05:38 | 10/06/2025 09:24:46 | 10/06/2025 09:32:55 | 10/06/2025 09:32:57 | 10/06/2025 09:44:25 | 10/06/2025 13:52:50 |  | Ahmed Abdelfattah Ali Soltan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251005000095 | PCM-20251005-00000721 | TT-20251005-00767 | Reference_telecom | Region_6 | BAH0018 | BAH0018 |  |  |  | SHAH KHALID | 10/05/2025 01:47:59 | 10/05/2025 07:44:12 | 10/05/2025 13:47:59 | ReplaceableUnitMissing observed in BAH0018_3 towards 10.221.245.123 @ Sceco | 10/04/2025 13:48:07 | Minor |  | ReplaceableUnitMissing | 10/04/2025 13:47:41 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0018 | FLM_TE | [8 empty] | API | 10/05/2025 01:47:59 | 10/05/2025 07:44:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000110 | PCM-20251005-00000746 | TT-20251005-00789 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/05/2025 02:05:03 | 10/20/2025 12:32:34 | 10/05/2025 14:05:03 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/05/2025 01:56:39 | Minor | 7115 | BASE STATION INFORMATION | 10/05/2025 01:56:31 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/05/2025 02:05:03 | 10/05/2025 11:02:37 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000119 | PCM-20251005-00000760 | TT-20251005-00810 | EM | Region_4 | KHY1M8251 | KHY2251 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/05/2025 02:26:45 | 10/06/2025 13:12:08 | 10/05/2025 14:26:45 | GENERATOR LOW FULE ALARM at KHY1M8251-G9-L8-SBTS-P3 @ Generator_SG | 10/05/2025 02:18:39 | Minor | 7103 | GENERATOR LOW FULE ALARM | 10/05/2025 02:18:34 | P3 | 4G | jeddah | Generator_SG | LTE NSA | KHY1M8251 | FLM_EM | [5 empty] | GENERATOR LOW FULE ALARM |  |  | API | 10/05/2025 02:26:45 | 10/06/2025 13:12:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251005000120 | PCM-20251005-00000761 | TT-20251005-00811 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/05/2025 02:29:20 | 10/20/2025 12:32:35 | 10/05/2025 06:29:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/05/2025 02:28:40 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 02:28:29 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/05/2025 02:29:20 | 10/05/2025 11:02:37 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000315 | PCM-20251005-00001050 | TT-20251005-01159 | Reference_telecom | Region_6 | TFBH0814 | TFBH0814 |  |  |  | SHAH KHALID | 10/05/2025 04:50:22 | 10/05/2025 07:44:13 | 10/05/2025 16:50:22 | ReplaceableUnitMissing observed in TFBH0814_01 towards 10.221.243.34 @ Sceco | 10/04/2025 16:50:44 | Minor |  | ReplaceableUnitMissing | 10/04/2025 16:49:50 | P3 | 2G | makhwa | Sceco | TX NSA | TFBH0814 | FLM_TE | [8 empty] | API | 10/05/2025 04:50:22 | 10/05/2025 07:44:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000346 | PCM-20251005-00001109 | TT-20251005-01238 | EM | Region_4 | QIA1M7361 | QIA0361 |  |  |  | Walid Magdy Tawfik Elbana | 10/05/2025 05:51:21 | 10/05/2025 08:21:14 | 10/05/2025 17:51:21 | RECTIFIER MAINS POWER FAILURE at QIA1M7361-L900-L800-P3 @ Sceco | 10/05/2025 05:43:58 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/05/2025 05:43:07 | P3 | 4G | taif | Sceco | LTE NSA | QIA1M7361 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/05/2025 05:51:21 | 10/05/2025 08:21:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000359 | PCM-20251005-00001127 | TT-20251005-01258 | Reference_EM | Region_1 | RAF2581 | RAF2581 | Enviroment | Air Condition | Welding condenser & adding Freon | Emad Mahmoud Ahmed Mohamed | 10/05/2025 06:07:53 | 10/06/2025 19:20:41 | 10/05/2025 12:07:53 | low fuel alarm at RAF2581-P1-USF-HUB_SRAN @ Generator_DG | 10/05/2025 05:57:23 | Major | 65115 | low fuel alarm | 10/05/2025 05:57:19 | P1 | SRAN | hafr | Generator_DG | 2G NSA | RAF2581 | FLM_EM | [8 empty] | API | 10/05/2025 06:07:53 | 10/05/2025 07:10:17 | 10/06/2025 19:20:27 |  |  | 10/06/2025 19:20:41 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251005000391 | PCM-20251005-00001179 | TT-20251005-01311 | Reference_telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/05/2025 06:51:50 | 10/15/2025 11:52:37 | 10/05/2025 12:51:50 | RFC Port Underpower at DAM6027-DCU1 @ Sceco | 10/05/2025 00:40:14 | Major | 29803 | RFC Port Underpower | 10/05/2025 00:40:02 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/05/2025 06:51:50 | 10/05/2025 11:03:14 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000392 | PCM-20251005-00001181 | TT-20251005-01313 | Reference_telecom | Region_1 | KBR6054 | KBR6054 |  |  |  | Meraj Husain Idd Baksh | 10/05/2025 06:52:55 | 10/15/2025 11:52:38 | 10/05/2025 12:52:55 | RFC Port Underpower at KBR6054-DCU1 @ Sceco | 10/05/2025 00:34:42 | Major | 29803 | RFC Port Underpower | 10/05/2025 00:34:35 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6054 | FLM_TE | [8 empty] | API | 10/05/2025 06:52:55 | 10/05/2025 11:03:15 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000396 | PCM-20251005-00001184 | TT-20251005-01317 | Reference_telecom | Region_5 | MAK0131 | MAK0131 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/05/2025 06:56:27 | 10/08/2025 11:33:20 | 10/05/2025 18:56:27 | Degrade observed in MAK0131 towards 10.1.231.226 @ Sceco | 10/04/2025 18:56:30 | Minor |  | Degrade | 10/04/2025 18:56:07 | P2 | 2G | makkah | Sceco | TX NSA | MAK0131 | FLM_TE | [8 empty] | API | 10/05/2025 06:56:27 | 10/08/2025 11:33:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251005000397 | PCM-20251005-00001185 | TT-20251005-01318 | Reference_telecom | Region_1 | KBR6055 | KBR6055 |  |  |  | Meraj Husain Idd Baksh | 10/05/2025 06:57:48 | 10/15/2025 11:52:41 | 10/05/2025 12:57:48 | RFC Port Underpower at KBR6055-DCU2 @ Sceco | 10/05/2025 00:34:40 | Major | 29803 | RFC Port Underpower | 10/05/2025 00:42:45 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6055 | FLM_TE | [8 empty] | API | 10/05/2025 06:57:48 | 10/05/2025 11:03:16 | 10/06/2025 16:36:00 | [5 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251005000437 | PCM-20251005-00001260 | TT-20251005-01392 | Telecom | Region_4 | JED1M7210 | JED0210 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/05/2025 07:58:58 | 10/05/2025 07:58:58 | 10/05/2025 13:58:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7210-CA-L900-L800-SBTS @ Sceco | 10/05/2025 07:58:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 07:57:56 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7210 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/05/2025 07:58:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251005000439 | PCM-20251005-00001263 | TT-20251005-01394 | Telecom | Region_4 | JED1M7103 | JED0103 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/05/2025 08:00:00 | 10/08/2025 18:12:55 | 10/05/2025 14:00:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7103-P2-CA-L900-L800-SBTS @ Sceco | 10/05/2025 07:59:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 07:59:05 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7103 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/05/2025 08:00:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000492 | PCM-20251005-00001353 | TT-20251005-01004 | Telecom | Region_6 | ARF1M7308 | ARF0308 | Transsmission | MW_HW_fault | Replace XPIC Cable | Muhammad shafiq Muhammad Rasheed | 10/05/2025 08:49:53 | 10/05/2025 20:53:56 | 10/05/2025 20:49:53 | BASE STATION HARDWARE PROBLEM (Nokia MN BTS SFP validation failure) at ARF1M7308-CA-L800-P3-SBTS @ Sceco | 10/05/2025 03:10:00 | Minor | 7100 | BASE STATION HARDWARE PROBLEM | 10/05/2025 03:09:51 | P3 | 4G | al harja | Sceco | LTE NSA | ARF1M7308 | FLM_TE |  |  | PCM-20251005-00000946 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/05/2025 08:49:53 | 10/05/2025 14:59:14 | 10/05/2025 15:08:28 | 10/05/2025 15:08:33 | 10/05/2025 19:55:33 | 10/05/2025 20:53:56 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000510 | PCM-20251005-00001380 | TT-20251004-00191 | Reference_telecom | Region_2 | RIY0643 | RIY0643 | Equipment | SFP_BTS | Clean SFP | Mubashar Farooq Abdul Majeed | 10/05/2025 09:04:48 | 10/05/2025 10:38:38 | 10/05/2025 21:04:48 | ETH_LOS at RIY0643_NE_24_H @ Sceco | 10/03/2025 23:24:21 | Minor | 1-235 | ETH_LOS | 10/03/2025 23:23:55 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0643 | FLM_TE |  |  | PCM-20251005-00001359 | approved as FLM ts | approved as FLM ts |  |  |  | API | 10/05/2025 09:04:48 | 10/05/2025 09:26:15 | 10/05/2025 09:31:49 | 10/05/2025 10:12:28 | 10/05/2025 10:12:31 | 10/05/2025 10:38:38 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251005000534 | PCM-20251005-00001418 | TT-20251003-01026 | Telecom | Region_2 | RY1-R1-0212-LL-CSG-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/05/2025 09:22:51 | 10/05/2025 09:22:51 | 10/05/2025 13:22:51 | The Device is offline at RY1-R1-0212-LL-CSG-01 @ Sceco | 10/03/2025 15:02:01 | Critical | 101-7 | The Device is offline | 10/03/2025 15:02:00 | P1 | IPRAN | riyadh | Sceco | IPRAN SA | RY1-R1-0212-LL-CSG-01 | FLM_TE |  |  | PCM-20251003-00001723 | Check alarm status with FO | Check alarm status with FO |  |  |  | API | 10/05/2025 09:22:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000545 | PCM-20251005-00001431 | TT-20251005-01509 | Telecom | Region_4 | MUMA1M8409 | MUMA2409 |  |  |  | Khizer Hayat | 10/05/2025 09:24:36 | 10/09/2025 16:53:07 | 10/05/2025 15:24:36 | 1(LTE) sites down under MUMA2409-G9-L8-L18-SBTS-P3 @ Sceco | 10/05/2025 09:16:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/05/2025 09:16:09 | P3 | 4G | jeddah | Sceco | LTE SA | MUMA2409-G9-L8-L18-SBTS-P3 | FLM_TE |  | Results: DOWN SITE HUB MUMA2409-G9-L8-L18-SBTS-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  | Timeout connecting to [/10.169.93.54:8080] [URL:http://10.169.93.54:8080/NE3S/1.0/] | sites down |  | Manual | 10/05/2025 09:24:36 | 10/09/2025 16:53:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000566 | PCM-20251005-00001453 | TT-20251005-01527 | Reference_telecom | Region_2 | RAS0098 | RAS0098 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/05/2025 09:29:38 | 10/16/2025 12:25:02 | 10/05/2025 21:29:38 | High attenuation B/W RAS0098 - 8809-SEC0004 NCE (REF TT-20250623-00167) | 10/05/2025 09:29:18 | Minor | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/05/2025 09:29:18 | P1 | SRAN | al rass | Sceco_STB | DWDM NSA | RAS0098 - 8809-SEC0004 | FLM_TE | [8 empty] | API | 10/05/2025 09:29:38 | 10/05/2025 14:03:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000581 | PCM-20251005-00001476 | TT-20251005-01558 | EM | Region_4 | RAB2236 | RAB2236 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/05/2025 09:40:45 | 10/06/2025 13:12:09 | 10/05/2025 21:40:45 | GENERATOR FAILURE ALARM at RAB2236-G9-L800-SBTS-P3 @ Generator_SG | 10/05/2025 09:33:41 | Minor | 7103 | GENERATOR FAILURE ALARM | 10/05/2025 09:32:20 | P3 | 2G | jeddah | Generator_SG | 2G NSA | RAB2236 | FLM_EM | [5 empty] | GENERATOR FAILURE ALARM |  |  | API | 10/05/2025 09:40:45 | 10/06/2025 13:12:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251005000674 | PCM-20251005-00001634 | TT-20251005-01712 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/05/2025 10:47:55 | 10/05/2025 10:50:27 | 10/05/2025 22:47:55 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/05/2025 07:47:40 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/05/2025 07:47:38 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/05/2025 10:47:55 | 10/05/2025 10:50:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000699 | PCM-20251005-00001676 | TT-20251005-01695 | Reference_telecom | Region_1 | HFF2U6729 | HFF6029 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/05/2025 11:04:30 | 10/05/2025 13:36:15 | 10/05/2025 23:04:30 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6729-P3 @ Sceco | 10/05/2025 07:39:19 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/05/2025 07:39:15 | P3 | 4G | hafouf | Sceco | 2G NSA | HFF2U6729 | FLM_TE |  | Dears Kindly check HW | PCM-20251005-00001617 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/05/2025 11:04:30 | 10/05/2025 13:36:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000753 | PCM-20251005-00001739 | TT-20251004-01194 | Telecom | Region_6 | JIZ0186 | JIZ0186 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Mohammed Sideag Mohammed Ali | 10/05/2025 11:14:15 | 10/05/2025 17:37:27 | 10/05/2025 17:14:15 | PLR threshold crossed on TWAMP-1 at JIZ0186-P2 sites\R6 | 10/04/2025 14:29:59 | Major | 61611 | TWAMP PLR Threshold Crossed | 10/04/2025 14:30:01 | P2 | 2G | jizan | Sceco | LTE SA | JIZ0186 | FLM_TE |  |  | PCM-20251005-00001622 | need check JIZ0186-JIZ0245 Flapping | need check JIZ0186-JIZ0245 Flapping |  |  |  | API | 10/05/2025 11:14:15 | 10/05/2025 12:38:58 | 10/05/2025 17:37:12 |  |  | 10/05/2025 17:37:27 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000757 | PCM-20251005-00001749 | TT-20250930-02363 | Reference_telecom | Region_4 | JED0919 | JED0919 |  |  |  | Nazeer Mohammed | 10/05/2025 11:17:05 | 10/05/2025 14:16:44 | 10/05/2025 23:17:05 | ReplaceableUnitProblem observed in JED0919_01 towards 10.10.179.166 @ Generator_DG | 09/30/2025 09:09:54 | Minor |  | ReplaceableUnitProblem | 09/30/2025 09:09:50 | VIP | 2G | jeddah | Generator_DG | TX NSA | JED0919 | FLM_TE |  |  | PCM-20251004-00001653 | please check with concern team | please check with concern team |  |  |  | API | 10/05/2025 11:17:05 | 10/05/2025 14:16:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000925 | PCM-20251005-00002026 | TT-20251005-02016 | EM | Region_3 | RUSF9012 | RUSF9012 | Enviroment | SCECO_Failure | SCECO auto restored | Mohammed Ali Mohammed Wafa | 10/05/2025 13:26:59 | 10/06/2025 09:55:20 | 10/06/2025 01:26:59 | NETECO: Maintenance Reminder at RUSF9012 @ Generator_SG | 10/05/2025 13:20:31 | Minor | 40563 | Maintenance Reminder | 10/05/2025 13:20:31 | P3 | Repeater | madinah | Generator_SG | 2G NSA | RUSF9012 | FLM_EM | [8 empty] | API | 10/05/2025 13:26:59 | 10/06/2025 09:53:00 | 10/06/2025 09:55:14 |  |  | 10/06/2025 09:55:20 |  | Mohammed Ali Mohammed Wafa |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251005000930 | PCM-20251005-00002033 | TT-20251005-02022 | MW_HC | Region_4 | JED0221 | JED0221 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/05/2025 13:29:36 | 10/06/2025 17:11:49 | 10/06/2025 01:29:36 | As BO Requested MW Nokia Observing RSL LOW For MW Link JED0221-JED0184 | 10/05/2025 13:27:51 | Minor | 113388 | LOF | 10/05/2025 13:27:53 | P2 | 2G | jeddah | Sceco | TX NSA | JED0221-JED0184 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing RSL LOW For MW Link JED0221-JED0184 |  |  | API | 10/05/2025 13:29:36 | 10/06/2025 16:59:35 | 10/06/2025 17:11:42 | 10/06/2025 17:11:46 | 10/06/2025 17:11:49 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005000932 | PCM-20251005-00002035 | TT-20251005-02024 | Reference_EM | Region_1 | JBL0473 | JBL0473 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Salah Abdalgadir Ahmed | 10/05/2025 13:32:41 | 10/10/2025 17:26:33 | 10/06/2025 01:32:41 | high temprature 40 at JBL0473-P2_SRAN @ Sceco | 10/05/2025 13:22:13 | Minor | 65103 | high temprature 40 | 10/05/2025 13:22:10 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0473 | FLM_EM | [8 empty] | API | 10/05/2025 13:32:41 | 10/05/2025 19:05:22 | 10/10/2025 17:26:26 |  |  | 10/10/2025 17:26:33 |  | Ahmed Salah Abdalgadir Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251005000952 | PCM-20251005-00002076 | TT-20251005-02067 | Reference_telecom | Region_6 | KMBS9501 | KMBS9501 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/05/2025 13:54:53 | 10/05/2025 19:27:31 | 10/06/2025 01:54:53 | LossOfSignal observed in KMBS9501_02 towards 10.74.121.71 @ Generator_DG | 10/05/2025 01:56:21 | Minor |  | LossOfSignal | 10/05/2025 01:54:49 | P1 | Repeater | khamis mushyet | Generator_DG | TX NSA | KMBS9501 | FLM_TE | [8 empty] | API | 10/05/2025 13:54:53 | 10/05/2025 19:27:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005000964 | PCM-20251005-00002093 | TT-20251005-02078 | Reference_telecom | Region_1 | DMJR0138 | DMJR0138 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/05/2025 14:01:37 | 10/05/2025 15:13:36 | 10/06/2025 02:01:37 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR0138-P1-DIA_SRAN @ Sceco_STB | 10/05/2025 11:01:08 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/05/2025 11:01:04 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | DMJR0138 | FLM_TE | [8 empty] | API | 10/05/2025 14:01:37 | 10/05/2025 15:13:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001030 | PCM-20251005-00002214 | TT-20251005-02141 | Telecom | Region_5 | SHU1M7344 | SHU0344 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/05/2025 15:05:49 | 10/08/2025 18:13:20 | 10/05/2025 21:05:49 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at SHU1M7344-G9-L9-SBTS-P2-USF @ Generator_SG | 10/05/2025 14:32:06 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 14:31:58 | P2 | 4G | makkah | Generator_SG | 5G_Cell SA | SHU1M7344 | FLM_TE |  |  | PCM-20251005-00002158 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/05/2025 15:05:49 | 10/08/2025 15:09:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001104 | PCM-20251005-00002331 | TT-20251005-02307 | Reference_telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/05/2025 16:01:29 | 10/17/2025 17:46:18 | 10/06/2025 04:01:29 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6008-DCU-P3 @ Sceco | 10/05/2025 13:01:05 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/05/2025 13:01:02 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/05/2025 16:01:29 | 10/06/2025 12:38:19 | 10/17/2025 17:46:09 |  |  | 10/17/2025 17:46:18 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001159 | PCM-20251005-00002410 | TT-20251005-00995 | Reference_telecom | Region_6 | KHS1M7215 | KHS0215 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/05/2025 16:36:51 | 10/05/2025 19:30:25 | 10/06/2025 04:36:51 | BASE STATION NOTIFICATION (Fan failure) at KHS1M7215-P2-USF @ Sceco | 10/05/2025 02:40:38 | Minor | 7652 | BASE STATION NOTIFICATION | 10/05/2025 02:40:13 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7215 | FLM_TE |  |  | PCM-20251005-00002215 | SMOD_R-1__FAN serial_no=K917296575715 | Need HC as the below SMOD has intermittent alarm SMOD_R-1__FAN serial_no=K917296575715 |  |  |  | API | 10/05/2025 16:36:51 | 10/05/2025 19:27:34 | 10/05/2025 19:30:17 |  |  | 10/05/2025 19:30:25 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001181 | PCM-20251005-00002440 | TT-20251005-02423 | Telecom | Region_4 | JED6058 | JED6058 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/05/2025 16:54:41 | 10/17/2025 17:46:31 | 10/05/2025 22:54:41 | BASE STATION ANTENNA LINE PROBLEM at JED6058-GSM-P3 @ Sceco | 10/05/2025 16:47:21 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/05/2025 16:47:10 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6058 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/05/2025 16:54:41 | 10/06/2025 12:38:19 | 10/17/2025 17:46:24 |  |  | 10/17/2025 17:46:31 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001204 | PCM-20251005-00002489 | TT-20251005-02462 | Telecom | Region_4 | JED0109 | JED0109 | Equipment | BSS_HW_fault | Replace RRU | Mohammed Ramadan A Abu Abid | 10/05/2025 17:26:13 | 10/08/2025 18:13:06 | 10/05/2025 23:26:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/05/2025 17:25:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 17:25:01 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/05/2025 17:26:13 | 10/05/2025 18:21:28 | 10/07/2025 06:30:03 |  |  | 10/07/2025 06:30:28 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001212 | PCM-20251005-00002502 | TT-20251005-02475 | Telecom | Region_2 | MZH-0527-LL-CSG-01 | MZH0527 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nawaz Sharif Muhammad Iqbal | 10/05/2025 17:30:52 | 10/06/2025 06:28:00 | 10/05/2025 23:30:52 | DWDM Link Down at MZH-0527-LL-CSG-01 @ Sceco_STB | 10/05/2025 17:24:32 | Major | 105-1100444 | Interface IPv6 status changed | 10/05/2025 17:24:21 | P1 | IPRAN | muzamiah | Sceco_STB | IPRAN SA | MZH-0527-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/05/2025 17:30:52 | 10/06/2025 06:04:36 | 10/06/2025 06:27:41 |  |  | 10/06/2025 06:28:00 |  | Nawaz Sharif Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001214 | PCM-20251005-00002504 | TT-20251005-02476 | EM | Region_2 | SEC0024 | SEC0024 | Enviroment | SCECO_Failure | SCECO auto restored | Saleem Khan Amir Dost | 10/05/2025 17:31:21 | 10/06/2025 19:46:50 | 10/05/2025 21:31:21 | NE_COMMU_GNE_SWITCH at SEC0024_ELC @ Sceco | 10/05/2025 17:29:28 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/05/2025 17:29:25 | P1 | DWDM | riyadh | Sceco | DWDM NSA | SEC0024 | FLM_EM | [5 empty] | NE SEC0024_ELC's current GNE has been switched to standby GNE |  |  | API | 10/05/2025 17:31:21 | 10/06/2025 02:48:02 | 10/06/2025 19:46:39 |  |  | 10/06/2025 19:46:50 |  | Saleem Khan Amir Dost |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001216 | PCM-20251005-00002507 | TT-20251005-02473 | EM | Region_2 | MZH0527 | MZH0527 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nawaz Sharif Muhammad Iqbal | 10/05/2025 17:32:00 | 10/06/2025 06:28:23 | 10/05/2025 21:32:00 | NE_COMMU_GNE_SWITCH at MZH0527_OCS @ Sceco_STB | 10/05/2025 17:28:08 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/05/2025 17:28:05 | VIP | SRAN | muzamiah | Sceco_STB | DWDM NSA | MZH0527 | FLM_TE |  |  | PCM-20251005-00002498 | Related to TE | Related to TE |  |  |  | API | 10/05/2025 17:32:00 | 10/06/2025 06:04:36 | 10/06/2025 06:28:09 |  |  | 10/06/2025 06:28:23 |  | Nawaz Sharif Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001219 | PCM-20251005-00002510 | TT-20251005-02474 | EM | Region_2 | MZH0527 | MZH0527 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nawaz Sharif Muhammad Iqbal | 10/05/2025 17:32:34 | 10/06/2025 06:28:51 | 10/05/2025 21:32:34 | NE_COMMU_GNE_SWITCH at MZH0527_ELC @ Sceco_STB | 10/05/2025 17:29:14 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/05/2025 17:29:11 | VIP | SRAN | muzamiah | Sceco_STB | DWDM NSA | MZH0527 | FLM_TE |  |  | PCM-20251005-00002501 | Related to TE | Related to TE |  |  |  | API | 10/05/2025 17:32:34 | 10/06/2025 06:04:36 | 10/06/2025 06:28:34 |  |  | 10/06/2025 06:28:51 |  | Nawaz Sharif Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251005001222 | PCM-20251005-00002513 | TT-20251005-02481 | Telecom | Region_2 | R2-RYMK-SEC0028 | SEC0028 |  |  |  | Azmat Ali Madad | 10/05/2025 17:32:45 | 10/05/2025 17:32:45 | 10/05/2025 21:32:45 | SCECO :: LINK DOWN B/W R1-RYMK-SEC0027--R2-RYMK-SEC0028 NCE | 10/05/2025 17:31:23 | Critical | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/05/2025 17:31:23 | P1 | DWDM | quweyah | Sceco_STB | DWDM NSA | R2-RYMK-SEC0028 | FLM_TE | [8 empty] | API | 10/05/2025 17:32:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001244 | PCM-20251005-00002552 | TT-20251005-02437 | Reference_telecom | Region_5 | BIK1M7153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/05/2025 18:02:42 | 10/18/2025 03:16:07 | 10/06/2025 00:02:42 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BIK1M7153-L800-CA-P3 @ Generator_SG | 10/05/2025 15:05:51 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/05/2025 15:05:41 | P3 | 4G | makkah | Generator_SG | LTE NSA | BIK1M7153 | FLM_TE |  |  | PCM-20251005-00002546 | Dear @'Back Office Transmission Team' Please find below last fluctuation 17:21 and PL status till 17:30 . Dear FLM Team, Please check and update ANM on EIF-3. | Dear @'Back Office Transmission Team' Please find below last fluctuation 17:21 and PL status till 17:30 . Dear FLM Team, Please check and update ANM on EIF-3. |  |  |  | API | 10/05/2025 18:02:42 | 10/18/2025 03:16:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001249 | PCM-20251005-00002559 | TT-20251005-02525 | MW_HC | Region_4 | SHB0671 | SHB0671 |  |  |  | Riasat Ali Allah Baksh | 10/05/2025 18:09:45 | 10/06/2025 17:25:54 | 10/06/2025 06:09:45 | As BO Requested MW Nokia Observing counting PM errors For MW Link SHB0671-JDZJ0765 | 10/05/2025 18:08:06 | Minor | 113388 | LOF | 10/05/2025 18:08:08 | P2 | 2G | qunfuddah | Sceco | TX NSA | SHB0671-JDZJ0765 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing counting PM errors For MW Link SHB0671-JDZJ0765 |  |  | API | 10/05/2025 18:09:45 | 10/06/2025 17:25:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001253 | PCM-20251005-00002567 | TT-20251005-02540 | MW_HC | Region_4 | GMK0442 | GMK0442 |  |  |  | Riasat Ali Allah Baksh | 10/05/2025 18:16:13 | 10/06/2025 17:25:55 | 10/06/2025 06:16:13 | As BO Requested MW Nokia Observing RSL flapping and XPD NOK for V ODU For MW Link GMK0442-LTH0330 | 10/05/2025 18:15:39 | Minor | 113388 | LOF | 10/05/2025 18:15:41 | P2 | 2G | qunfuddah | Sceco | TX NSA | GMK0442-LTH0330 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing RSL flapping and XPD NOK for V ODU For MW Link GMK0442-LTH0330 |  |  | API | 10/05/2025 18:16:13 | 10/06/2025 17:25:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251005001261 | PCM-20251005-00002576 | TT-20251005-02551 | MW_HC | Region_4 | SJED0664 | SJED0664 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/05/2025 18:21:01 | 10/05/2025 18:21:01 | 10/06/2025 06:21:01 | As BO Requested MW Nokia Observing counting continuous PM errors SJED0664-JED0363 | 10/05/2025 18:19:54 | Minor | 113388 | LOF | 10/05/2025 18:19:56 | P3 | SRAN | jeddah | Sceco | TX NSA | SJED0664-JED0363 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing counting continuous PM errors SJED0664-JED0363 |  |  | API | 10/05/2025 18:21:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001264 | PCM-20251005-00002580 | TT-20251005-02556 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/05/2025 18:26:07 | 10/07/2025 14:35:18 | 10/06/2025 00:26:07 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/05/2025 15:26:11 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/05/2025 15:25:59 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/05/2025 18:26:07 | 10/07/2025 14:35:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001298 | PCM-20251005-00002636 | TT-20251005-02623 | Telecom | Region_4 | TAF1M7279 | TAF0279 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/05/2025 19:10:01 | 10/21/2025 17:12:31 | 10/06/2025 01:10:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF1M7279-G9-L18-L21-SBTS-P2 @ Sceco | 10/05/2025 19:09:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 19:09:18 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7279 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/05/2025 19:10:01 | 10/05/2025 21:08:51 | 10/19/2025 08:47:18 |  |  | 10/19/2025 08:47:23 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001306 | PCM-20251005-00002657 | TT-20251005-02672 | Telecom | Region_2 | NRR-CRIY0127 | RIY2755 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/05/2025 19:30:41 | 10/16/2025 20:19:52 | 10/06/2025 01:30:41 | REM_SF alarm at NRR-CRIY0127 NCE | 10/05/2025 19:24:45 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/05/2025 19:24:45 | P2 | DWDM | riyadh | Sceco_STB | DWDM NSA | NRR-CRIY0127 | FLM_TE | [8 empty] | API | 10/05/2025 19:30:41 | 10/06/2025 09:00:21 | 10/16/2025 20:19:44 |  |  | 10/16/2025 20:19:52 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001328 | PCM-20251005-00002700 | TT-20251005-02687 | Telecom | Region_4 | SQSH0023 | SQSH0023 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/05/2025 20:07:58 | 10/16/2025 11:19:28 | 10/06/2025 02:07:58 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at SQSH0023-GSM-UMTS-P2-USF @ Generator_DG | 10/05/2025 19:37:16 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 19:37:09 | P2 | 2G | qunfuddah | Generator_DG | 5G_Cell SA | SQSH0023 | FLM_TE |  |  | PCM-20251005-00002676 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/05/2025 20:07:58 | 10/06/2025 07:22:31 | 10/16/2025 11:19:22 |  |  | 10/16/2025 11:19:28 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001334 | PCM-20251005-00002708 | TT-20251005-02699 | Telecom | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/05/2025 20:13:02 | 10/06/2025 11:45:21 | 10/06/2025 02:13:02 | 1(2G) 1(LTE) 2(5G) sites down under RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3,JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/05/2025 19:47:58 | Major | 7706 | BTS O&M LINK FAILURE | 10/05/2025 19:47:53 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3 5G,JED6020-GSM-P3 2G_LTE_5G | FLM_EM | JED6020 | JED6020 Suspected power issue RAB0366 Loss of Signal | PCM-20251005-00002688 | JED6020 Suspected power issue RAB0366 Loss of Signal | JED6020 Suspected power issue RAB0366 Loss of Signal |  | sites down |  | API | 10/05/2025 20:13:02 | 10/06/2025 11:45:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251005001394 | PCM-20251005-00002811 | TT-20251005-02791 | Telecom | Region_4 | JED0252 | JED0252 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Moustafa Mahmoud Ahmed Fathelbab | 10/05/2025 21:45:38 | 10/12/2025 15:44:19 | 10/06/2025 09:45:38 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/05/2025 21:16:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 21:16:43 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251005-00002777 | FLM need to check VSWR and perform HC at site. | FLM need to check VSWR and perform HC at site. |  |  |  | API | 10/05/2025 21:45:38 | 10/06/2025 09:14:30 | 10/08/2025 15:56:14 | 10/08/2025 15:56:16 | 10/08/2025 15:56:18 | 10/12/2025 15:44:19 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001434 | PCM-20251005-00002873 | TT-20251005-02105 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/05/2025 22:21:59 | 10/08/2025 18:13:06 | 10/06/2025 04:21:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/05/2025 14:14:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 14:14:13 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE |  |  | PCM-20251005-00002856 | TE issue | TE issue |  |  |  | API | 10/05/2025 22:21:59 | 10/06/2025 17:25:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001460 | PCM-20251005-00002910 | TT-20251005-02893 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/05/2025 22:53:11 | 10/07/2025 14:35:19 | 10/06/2025 04:53:11 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/05/2025 19:51:33 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/05/2025 19:52:45 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/05/2025 22:53:11 | 10/07/2025 14:35:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251005001490 | PCM-20251005-00002961 | TT-20251005-02935 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/05/2025 23:41:12 | 10/08/2025 18:13:20 | 10/06/2025 05:41:12 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/05/2025 23:33:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/05/2025 23:33:07 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251005-00002957 | Please check the RMOD path and if not clear call BO from site to confirm and send mail for HW replacement | Please check the RMOD path and if not clear call BO from site to confirm and send mail for HW replacement |  |  |  | API | 10/05/2025 23:41:12 | 10/06/2025 12:42:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000039 | PCM-20251006-00000072 | TT-20251006-00065 | Telecom | Region_4 | JDAP1M7940 | JDAP0940 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/06/2025 01:06:22 | 10/21/2025 18:13:24 | 10/06/2025 07:06:22 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/06/2025 00:52:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 00:52:19 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JDAP1M7940 | FLM_TE |  |  | PCM-20251006-00000061 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/06/2025 01:06:22 | 10/20/2025 14:29:29 | 10/21/2025 18:13:18 |  |  | 10/21/2025 18:13:24 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000109 | PCM-20251006-00000217 | TT-20251006-00248 | Telecom | Region_4 | TF1-ASG-01 | TF1 |  |  |  | Rashid Shafique | 10/06/2025 03:07:24 | 10/14/2025 10:15:36 | 10/06/2025 09:07:24 | IS-IS Adjacency Changed at bTF1-ASG-01 | 10/06/2025 01:49:26 | Major | 15269 | LOS | 10/06/2025 01:49:26 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | TF1-ASG-01 | FLM_TE | [8 empty] | API | 10/06/2025 03:07:24 | 10/14/2025 10:15:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000126 | PCM-20251006-00000253 | TT-20251006-00283 | Telecom | Region_6 | BAH1M3019 | BAH0019 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/06/2025 03:26:31 | 10/06/2025 13:34:58 | 10/06/2025 09:26:31 | 1(3G) sites down under BAH0019-P3/BAH1M3019-P3 @ Sceco | 10/06/2025 03:18:57 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/06/2025 03:18:14 | P3 | 3G | Albaha | Sceco | 3G SA | BAH0019-P3 | FLM_TE | BAH0019 | Results: DOWN SITE HUB BAH0019-P3 BAH0019 Summary: Hub: BAH0019, Down Count: 1, Down Sites: BAH0019-P3 Alarm Summary: BAH0019 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/06/2025 03:26:31 | 10/06/2025 03:36:25 | 10/06/2025 13:34:37 |  |  | 10/06/2025 13:34:58 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000140 | PCM-20251006-00000296 | TT-20251006-00354 | Reference_telecom | Region_6 | KHS1M7982 | KHS0982 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/06/2025 03:47:07 | 10/06/2025 20:22:34 | 10/06/2025 15:47:07 | BASE STATION NOTIFICATION (Fan failure) at KHS1M7982-P2-USF @ Sceco | 10/06/2025 03:17:17 | Minor | 7652 | BASE STATION NOTIFICATION | 10/06/2025 03:16:50 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7982 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/06/2025 03:47:07 | 10/06/2025 10:52:33 | 10/06/2025 20:22:27 |  |  | 10/06/2025 20:22:34 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000178 | PCM-20251006-00000363 | TT-20251006-00551 | MW_HC | Region_4 | RNRY0660 | RNRY0660 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Ahmad Kamal Abdelmawla | 10/06/2025 04:51:46 | 10/06/2025 08:19:23 | 10/06/2025 16:51:46 | As BO Requested MW HC For Link RNRY0660-RNRY0659 | 10/06/2025 04:50:57 | Minor | 113388 | LOF | 10/06/2025 04:50:57 | P3 | 2G | taif | Generator_SG | TX NSA | RNRY0660-RNRY0659 | FLM_TE | [5 empty] | As BO Requested MW HC For Link RNRY0660-RNRY0659 |  |  | API | 10/06/2025 04:51:46 | 10/06/2025 05:46:06 | 10/06/2025 05:46:25 |  |  | 10/06/2025 08:19:23 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000249 | PCM-20251006-00000489 | TT-20251006-00678 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/06/2025 06:45:06 | 10/17/2025 17:47:33 | 10/06/2025 18:45:06 | Cell Capability Degraded at JED6008-DCU-P3 @ Sceco | 10/05/2025 20:05:58 | Minor | 28751 | Cell Capability Degraded | 10/05/2025 20:04:24 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/06/2025 06:45:06 | 10/06/2025 12:39:09 | 10/17/2025 17:47:26 |  |  | 10/17/2025 17:47:33 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000288 | PCM-20251006-00000558 | TT-20251006-00656 | Telecom | Region_2 | RIY0810-ZRi03-1-CSG-04 | RIY0810 |  |  |  | Khan zeb Shah nawaz | 10/06/2025 07:45:05 | 10/06/2025 08:02:14 | 10/06/2025 13:45:05 | Physical Port Down at RIY0810-ZRi03-1-CSG-04 @ Sceco | 10/06/2025 01:22:26 | Major | 101-2505274 | Physical Port Down | 10/06/2025 01:22:18 | VIP | IPRAN | riyadh | Sceco | IPRAN NSA | RIY0810-ZRi03-1-CSG-04 | FLM_TE |  |  | PCM-20251006-00000510 | Kindly check port 0-9-0 | Kindly check port 0-9-0 |  |  |  | API | 10/06/2025 07:45:05 | 10/06/2025 08:02:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251006000292 | PCM-20251006-00000562 | TT-20251006-00754 | Reference_telecom | Region_4 | JED0146 | JED0146 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/06/2025 07:47:44 | 10/11/2025 14:48:27 | 10/06/2025 19:47:44 | Degrade observed in JED0146_3 towards 10.1.227.218 @ Sceco | 10/05/2025 19:47:21 | Minor |  | Degrade | 10/05/2025 19:47:17 | P2 | 2G | jeddah | Sceco | TX NSA | JED0146 | FLM_TE | [8 empty] | API | 10/06/2025 07:47:44 | 10/11/2025 14:48:07 | 10/11/2025 14:48:22 | 10/11/2025 14:48:24 | 10/11/2025 14:48:27 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000303 | PCM-20251006-00000580 | TT-20251006-00650 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/06/2025 07:55:47 | 10/20/2025 12:32:36 | 10/06/2025 11:55:47 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/06/2025 02:29:04 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 02:28:59 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251006-00000458 | perform HC | perform HC |  |  |  | API | 10/06/2025 07:55:47 | 10/06/2025 12:42:50 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000343 | PCM-20251006-00000642 | TT-20251006-00714 | Telecom | Region_5 | MAK1M3585 | MAK0585 |  |  |  | Amjad Ali Muhammad Parves | 10/06/2025 08:27:24 | 10/07/2025 17:45:26 | 10/06/2025 14:27:24 | CELL OPERATION DEGRADED (Mast Head Amplifier below current window fault, ANT3) at MAK1M3585-P2 @ Sceco | 10/06/2025 07:07:38 | Major | 7654 | CELL OPERATION DEGRADED | 10/06/2025 07:07:17 | P3 | 3G | makkah | Sceco | LTE_Cell SA | MAK1M3585 | FLM_TE |  |  | PCM-20251006-00000523 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/06/2025 08:27:24 | 10/07/2025 17:45:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251006000346 | PCM-20251006-00000649 | TT-20251006-00582 | Telecom | Region_4 | JED1M8130 | JED2130 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/06/2025 08:30:13 | 10/06/2025 08:30:13 | 10/06/2025 14:30:13 | BASE STATION HARDWARE PROBLEM (Ethernet link unstable) at JED1M8130-CA-L800-P3 @ Sceco | 10/06/2025 05:14:19 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/06/2025 05:14:14 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8130 | FLM_TE |  |  | PCM-20251006-00000394 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/06/2025 08:30:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000413 | PCM-20251006-00000760 | TT-20251006-00928 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/06/2025 09:23:30 | 10/21/2025 18:12:55 | 10/06/2025 15:23:30 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/06/2025 09:13:23 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/06/2025 09:13:14 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251006-00000757 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/06/2025 09:23:30 | 10/20/2025 14:29:30 | 10/21/2025 18:12:49 |  |  | 10/21/2025 18:12:55 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000415 | PCM-20251006-00000763 | TT-20251006-00935 | Telecom | Region_4 | JED1MN0957 | JED0957 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/06/2025 09:24:23 | 10/06/2025 09:33:11 | 10/06/2025 21:24:23 | BASE STATION INFORMATION (No module fan detected) at JED1MN0957-NR2.6-P3 @ Sceco | 10/06/2025 09:16:38 | Minor | 7115 | BASE STATION INFORMATION | 10/06/2025 09:16:08 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN0957 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/06/2025 09:24:23 | 10/06/2025 09:33:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000428 | PCM-20251006-00000784 | TT-20251006-00951 | EM | Region_1 | JBL0477 | JBL0477 | Enviroment | Genset failure_High Temperature | Change Generator radiator | Ahmed Hassan Ahmed Hassanin | 10/06/2025 09:30:35 | 10/07/2025 12:00:12 | 10/06/2025 21:30:35 | Door opening alarm at JBL0477-P2_SRAN @ Sceco | 10/06/2025 09:30:13 | Minor | 65101 | Door opening alarm | 10/06/2025 09:27:15 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0477 | FLM_EM | [8 empty] | API | 10/06/2025 09:30:35 | 10/07/2025 11:47:52 | 10/07/2025 12:00:07 |  |  | 10/07/2025 12:00:12 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000436 | PCM-20251006-00000796 | TT-20251006-00964 | EM | Region_1 | JBL0477 | JBL0477 | Enviroment | Rectifier Module | Adding module due to load issue | Ahmed Hassan Ahmed Hassanin | 10/06/2025 09:37:18 | 10/07/2025 12:00:04 | 10/06/2025 21:37:18 | Mains Failure at JBL0477-P2_SRAN @ Sceco | 10/06/2025 09:30:13 | Minor | 65109 | Mains Failure | 10/06/2025 09:27:15 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0477 | FLM_EM | [8 empty] | API | 10/06/2025 09:37:18 | 10/07/2025 11:47:52 | 10/07/2025 11:59:51 |  |  | 10/07/2025 12:00:04 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251006000454 | PCM-20251006-00000826 | TT-20251006-00905 | Telecom | Region_1 | SAK2596 | SAK2596 |  |  |  | Syed Fawad Ali | 10/06/2025 09:50:02 | 10/06/2025 10:12:36 | 10/06/2025 15:50:02 | 1(3G) 1(LTE) sites down under SAK2596-P3_SRAN,SAK2402-P3/AR1RNCH01 @ Sceco | 10/06/2025 09:05:43 | Major | 22214 | NodeB Unavailable | 10/06/2025 09:05:40 | P3 | SRAN | sakaka | Sceco | 3G_LTE SA | SAK2596-P3_SRAN LTE,SAK2402-P3 3G | FLM_TE | SAK2596 | Dear Team , TRM FB SITES HUB FB SAK2596-P3 SAK2596 observing visibility down SAK2402 SAK2595 suspecting power issue at hub site | PCM-20251006-00000797 | Dear Team , TRM FB SITES HUB FB SAK2596-P3 SAK2596 observing visibility down SAK2402 SAK2595 suspecting power issue at hub site | Dear Team , TRM FB SITES HUB FB SAK2596-P3 SAK2596 observing visibility down SAK2402 SAK2595 suspecting power issue at hub site |  | sites down |  | API | 10/06/2025 09:50:02 | 10/06/2025 10:12:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251006000471 | PCM-20251006-00000849 | TT-20251006-01012 | EM | Region_4 | JED0531 | JED0531 |  |  |  | Hussein Sayed Salama Hussein | 10/06/2025 10:01:34 | 10/06/2025 13:24:38 | 10/06/2025 22:01:34 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at JED0531-G9-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/06/2025 09:53:30 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/06/2025 09:53:06 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0531 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/06/2025 10:01:34 | 10/06/2025 13:24:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251006000474 | PCM-20251006-00000853 | TT-20251006-01014 | Telecom | Region_4 | JED1M7958 | JED0958 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/06/2025 10:03:37 | 10/08/2025 18:13:22 | 10/06/2025 16:03:37 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7958-CA-L800-SBTS-P3 @ Sceco | 10/06/2025 09:58:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 09:58:38 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7958 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/06/2025 10:03:37 | 10/06/2025 12:35:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000498 | PCM-20251006-00000885 | TT-20251006-00999 | Telecom | Region_4 | TAF1M4453 | TAF2453 |  |  |  | Ahmad Kamal Abdelmawla | 10/06/2025 10:19:33 | 10/06/2025 14:50:22 | 10/06/2025 16:19:33 | BASE STATION OPERATION DEGRADED (Rel2 ESM HSPA capability not fully utilized) at TAF1M4453-P3 @ Sceco | 10/06/2025 09:52:13 | Major | 7651 | BASE STATION OPERATION DEGRADED | 09/11/2025 18:29:05 | P3 | 3G | jeddah | Sceco | 3G NSA | TAF1M4453 | FLM_TE |  |  | PCM-20251006-00000837 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/06/2025 10:19:33 | 10/06/2025 14:50:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251006000502 | PCM-20251006-00000891 | TT-20251006-01046 | EM | [7 empty] | 10/06/2025 10:21:32 | 10/06/2025 10:21:32 | 10/06/2025 14:21:32 | RECTIFIER ALARM at SHEDGUN-SEC0034_OCS @ Sceco_STB | 10/06/2025 10:12:36 | Critical | 1-12307 | RECTIFIER ALARM | 10/06/2025 10:12:26 | P1 | DWDM |  | Sceco_STB | DWDM NSA | SHEDGUN | FLM_EM | [8 empty] | API | 10/06/2025 10:21:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251006000507 | PCM-20251006-00000906 | TT-20251006-01059 | Telecom | Region_4 | JDRS1M7623 | JDRS0623 |  |  |  | Khizer Hayat | 10/06/2025 10:28:26 | 10/06/2025 13:02:15 | 10/06/2025 16:28:26 | BASE STATION SERVICE PROBLEM (TX out of order) at JDRS1M7623-USF-P1-VIP-NCA-L800-SBTS-WBB-G3 @ Sceco | 10/06/2025 10:26:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 10:23:04 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JDRS1M7623 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/06/2025 10:28:26 | 10/06/2025 12:53:50 | 10/06/2025 13:02:15 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000569 | PCM-20251006-00000995 | TT-20251006-01141 | MW_HC | Region_4 | RNRY0660 | RNRY0660 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Asad Ullah Rahim Said | 10/06/2025 11:08:22 | 10/14/2025 09:33:04 | 10/06/2025 23:08:22 | As per bo request Nokia MW HC RNRY0660-RNRY0659 currently counting error. | 10/06/2025 11:08:16 | Minor | 113388 | LOF | 10/06/2025 11:08:14 | P3 | 2G | taif | Generator_SG | TX NSA | RNRY0660-RNRY0659 | FLM_TE | [5 empty] | As per bo request Nokia MW HC RNRY0660-RNRY0659 currently counting error. |  |  | API | 10/06/2025 11:08:22 | 10/14/2025 09:33:04 | [5 empty] | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000576 | PCM-20251006-00001007 | TT-20251006-01149 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/06/2025 11:12:49 | 10/06/2025 12:03:07 | 10/06/2025 23:12:49 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/06/2025 08:12:19 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/06/2025 08:12:15 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/06/2025 11:12:49 | 10/06/2025 12:03:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000580 | PCM-20251006-00001013 | TT-20251006-01153 | Telecom | Region_1 | ADR0010 | ADR0010 |  |  |  | Syed Fawad Ali | 10/06/2025 11:14:52 | 10/15/2025 11:52:39 | 10/06/2025 23:14:52 | RF Unit Maintenance Link Failure at ADR0010-P3_SRAN @ Sceco | 10/06/2025 11:13:04 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/06/2025 11:03:33 | P3 | SRAN | sakaka | Sceco | 2G NSA | ADR0010 | FLM_TE | [8 empty] | API | 10/06/2025 11:14:52 | 10/06/2025 11:40:50 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000583 | PCM-20251006-00001017 | TT-20251006-01157 | Telecom | Region_1 | ADR0010 | ADR0010 |  |  |  | Syed Fawad Ali | 10/06/2025 11:16:57 | 10/15/2025 11:52:40 | 10/06/2025 23:16:57 | NR DU Cell TRP Unavailable at ADR0010-P3_SRAN @ Sceco | 10/06/2025 11:13:04 | Minor | 29870 | NR DU Cell TRP Unavailable | 10/06/2025 11:08:48 | P3 | SRAN | sakaka | Sceco | 2G NSA | ADR0010 | FLM_TE | [8 empty] | API | 10/06/2025 11:16:57 | 10/06/2025 11:40:51 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000587 | PCM-20251006-00001022 | TT-20251006-01165 | Telecom | Region_2 | BUR6002 | BUR6002 |  |  |  | Raise Ahmed Nisar Ahmed | 10/06/2025 11:20:33 | 10/06/2025 15:17:16 | 10/06/2025 23:20:33 | DCU Optical Module Transmit/Receive Fault at BUR6002-DCU2 @ Sceco | 10/06/2025 11:16:32 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/06/2025 11:14:59 | VIP | SRAN | buraidah | Sceco | 2G NSA | BUR6002 | FLM_TE | [8 empty] | API | 10/06/2025 11:20:33 | 10/06/2025 15:17:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000614 | PCM-20251006-00001071 | TT-20251006-01231 | Reference_telecom | Region_4 | TF1-ASG-01 | TF1 |  |  |  | Rashid Shafique | 10/06/2025 11:46:27 | 10/14/2025 10:15:36 | 10/06/2025 17:46:27 | DWDM_Physical Port Down at HA1 // TT-20251006-01172 | 10/06/2025 11:25:13 | Major | 15151 | IOC detected but none of them active | 10/06/2025 11:25:13 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | DWDM_Physical Port Down at HA1 // TT-20251006-01172 | FLM_TE | [8 empty] | API | 10/06/2025 11:46:27 | 10/14/2025 10:15:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000675 | PCM-20251006-00001162 | TT-20251006-01322 | EM | Region_4 | HHR1M7448 | HHR0448 |  |  |  | AbdAllah Mohammad abd Elgawad Fath Elbab | 10/06/2025 12:28:45 | 10/06/2025 12:42:55 | 10/06/2025 18:28:45 | RECTIFIRE MAIN FAILURE at HHR1M7448-P1-VIP-HHR-L800-CA @ Generator_SG | 10/06/2025 12:20:23 | Major | 7103 | RECTIFIRE MAIN FAILURE | 10/06/2025 12:20:20 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7448 | FLM_EM | [5 empty] | RECTIFIRE MAIN FAILURE |  |  | API | 10/06/2025 12:28:45 | 10/06/2025 12:42:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251006000697 | PCM-20251006-00001197 | TT-20251006-01348 | Reference_telecom | Region_1 | DMJR2266 | DMJR2266 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/06/2025 12:44:45 | 10/06/2025 13:45:02 | 10/07/2025 00:44:45 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR2266-P3-USF_SRAN @ Sceco | 10/06/2025 09:44:13 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/06/2025 09:44:10 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR2266 | FLM_TE | [8 empty] | API | 10/06/2025 12:44:45 | 10/06/2025 13:45:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000731 | PCM-20251006-00001254 | TT-20251006-01405 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/06/2025 13:14:43 | 10/06/2025 13:22:44 | 10/07/2025 01:14:43 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/06/2025 13:08:02 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/06/2025 13:07:58 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/06/2025 13:14:43 | 10/06/2025 13:22:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000748 | PCM-20251006-00001285 | TT-20251006-01431 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/06/2025 13:28:40 | 10/06/2025 16:35:58 | 10/07/2025 01:28:40 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/06/2025 13:20:43 | Minor | 7103 | AIRCON 1 FAILURE | 10/06/2025 13:20:33 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/06/2025 13:28:40 | 10/06/2025 16:35:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000762 | PCM-20251006-00001301 | TT-20251006-01442 | EM | Region_1 | HFR0502 | HFR0502 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/06/2025 13:32:18 | 10/06/2025 19:47:58 | 10/06/2025 17:32:18 | Door opening alarm at HFR0502-P1-Core-HUB-WDM_SRAN-FON @ Sceco_STB | 10/06/2025 13:31:47 | Critical | 65101 | Door opening alarm | 10/06/2025 13:31:43 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | HFR0502 | FLM_EM | [8 empty] | API | 10/06/2025 13:32:18 | 10/06/2025 19:20:10 | 10/06/2025 19:47:42 |  |  | 10/06/2025 19:47:58 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000818 | PCM-20251006-00001411 | TT-20251006-01540 | Telecom | Region_4 | NSH0138 | NSH0138 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/06/2025 14:24:11 | 10/11/2025 10:28:56 | 10/06/2025 20:24:11 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at NSH0138-GSM-UMTS-P3 @ Generator_DG | 10/06/2025 14:18:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 14:18:42 | P3 | 2G | adam | Generator_DG | 5G_Cell SA | NSH0138 | FLM_TE |  |  | PCM-20251006-00001407 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/06/2025 14:24:11 | 10/06/2025 14:57:20 | 10/11/2025 10:28:48 |  |  | 10/11/2025 10:28:56 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000847 | PCM-20251006-00001469 | TT-20251006-01547 | Reference_telecom | Region_1 | JBKH0146 | JBKH0146 |  |  |  | Mohamed Abdelaziz | 10/06/2025 14:44:04 | 10/06/2025 19:25:44 | 10/07/2025 02:44:04 | External Clock Reference Problem at JBKH0146-P2-USF_SRAN @ Generator_SG | 10/06/2025 11:27:55 | Minor | 26262 | External Clock Reference Problem | 10/06/2025 11:24:30 | P2 | SRAN | khafji | Generator_SG | 2G NSA | JBKH0146 | FLM_TE |  | Dear TX Team kindly check as IP CLK unavailable Link No. = 0 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.180.136 VRF Index = 0 Server IPv4 = 10.161.136.109 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = OFF Clock Server Description = NULL Link No. = 1 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.180.136 VRF Index = 0 Server IPv4 = 10.161.137.109 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = OFF Clock Server Description = NULL (Number of results = 2) | PCM-20251006-00001449 | kindly need Health check for MW link JBKH0112 <> JBKH0113 , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance | JBKH0112 <> JBKH0113 |  |  |  | API | 10/06/2025 14:44:04 | 10/06/2025 19:25:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000848 | PCM-20251006-00001470 | TT-20251006-01546 | Reference_telecom | Region_1 | JBKH0112 | JBKH0112 |  |  |  | Mohamed Abdelaziz | 10/06/2025 14:44:31 | 10/06/2025 19:25:45 | 10/07/2025 02:44:31 | External Clock Reference Problem at JBKH0112-P1-HUB_SRAN @ Sceco | 10/06/2025 11:27:52 | Minor | 26262 | External Clock Reference Problem | 10/06/2025 11:24:29 | P1 | SRAN | khafji | Sceco | 2G NSA | JBKH0112 | FLM_TE |  | Dear TX Team kindly check as IP CLK unavailable Link No. = 0 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.180.135 VRF Index = 0 Server IPv4 = 10.161.136.109 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = OFF Clock Server Description = NULL Link No. = 1 Protocol Type = PTP Device Type = OC_SLAVE Cabinet No. = 0 Subrack No. = 0 Slot No. = 7 Clock Net Mode = Unicast Profile Type = 1588V2 IP mode = IPv4 Client IPv4 = 10.151.180.135 VRF Index = 0 Server IPv4 = 10.161.137.109 Domain = 0 Phase Deviation Report Switch = OFF Phase Deviation Report Interval(s) = NULL Compensation(ns) = 0 Delay Type = E2E Priority = 4 IP Clock Sync Mode = FREQ Continuous Sending Sync Packets Switch = OFF Clock Server Description = NULL (Number of results = 2) | PCM-20251006-00001446 | JBKH0112 <> JBKH0113 | JBKH0112 <> JBKH0113 |  |  |  | API | 10/06/2025 14:44:31 | 10/06/2025 19:25:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000877 | PCM-20251006-00001520 | TT-20251006-01637 | Telecom | Region_2 | RIYC1W6043 | RIYC1W6043 |  |  |  | Abdelrahim Abdalla Abdelrahim Khairy | 10/06/2025 15:11:14 | 10/11/2025 12:36:15 | 10/07/2025 03:11:14 | RIYC1W6043 Partial Down | 10/06/2025 15:03:56 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/06/2025 15:03:56 | P1 | WIFI | riyadh | Sceco | Wifi SA | RIYC1W6043_3-L4-AP11 RIYC1W6043_3-L4-AP16 RIYC1W6043_3-L4-AP21 | FLM_TE | [8 empty] | API | 10/06/2025 15:11:14 | 10/11/2025 12:36:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000879 | PCM-20251006-00001523 | TT-20251006-01624 | Telecom | Region_4 | RYMK0665 | RYMK0665 |  |  |  | Ehab Ali Mohamed Abdou | 10/06/2025 15:12:00 | 10/08/2025 10:54:48 | 10/07/2025 03:12:00 | WRYMK0001 Complete down | 10/06/2025 14:55:13 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/06/2025 14:55:13 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251006-00001508 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/06/2025 15:12:00 | 10/08/2025 10:54:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251006000883 | PCM-20251006-00001531 | TT-20251006-01646 | Telecom | Region_4 | JED1MN2703 | JED2703 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/06/2025 15:14:13 | 10/06/2025 15:14:13 | 10/06/2025 21:14:13 | PT:: Minor Fluctuation of BASE STATION SERVICE PROBLEM (nit synchronization failed) observed at JED1MN2703/R4 | 10/06/2025 15:11:32 | Major | 676767671 | Health Check-WO to TE FME | 10/06/2025 15:11:33 | VIP | 5G | jeddah | Generator_SG | 2G_3G_LTE_5G NSA | JED1MN2703 | FLM_TE | [8 empty] | API | 10/06/2025 15:14:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000888 | PCM-20251006-00001540 | TT-20251006-01652 | Telecom | Region_4 | BHR1MN2112 | BHR2112 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/06/2025 15:17:38 | 10/06/2025 16:36:16 | 10/06/2025 21:17:38 | PT:: Minor Fluctuation of GPS receiver alarm: not tracking satellites observed at BHR1MN2112-NR2.6-P3/R4 | 10/06/2025 15:17:30 | Major | 676767671 | Health Check-WO to TE FME | 10/06/2025 15:17:32 | P3 | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | BHR1MN2112-NR2.6-P3 | FLM_TE | [8 empty] | API | 10/06/2025 15:17:38 | 10/06/2025 16:36:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006000900 | PCM-20251006-00001562 | TT-20251006-01674 | Telecom | Region_4 | JED6175 | JED6075 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/06/2025 15:28:07 | 10/21/2025 18:28:01 | 10/06/2025 21:28:07 | PT:: Minor Fluctuation of BCCH MISSING observed at JED6175-P3/R4 | 10/06/2025 15:28:00 | Major | 676767671 | Health Check-WO to TE FME | 10/06/2025 15:28:02 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED6175-P3 | FLM_TE | [8 empty] | API | 10/06/2025 15:28:07 | 10/07/2025 19:01:04 | 10/21/2025 18:27:55 |  |  | 10/21/2025 18:28:01 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006000994 | PCM-20251006-00001708 | TT-20251006-01727 | Reference_telecom | Region_1 | DMHF2M7081 | DMHF0081 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/06/2025 16:47:09 | 10/06/2025 17:00:10 | 10/07/2025 04:47:09 | Cell RX Channel Interference Noise Power Unbalanced at DMHF2M7081-P1-HUB-L800-CA @ Generator_SG | 10/06/2025 12:59:31 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/06/2025 12:59:27 | P1 | 4G | hafouf | Generator_SG | 2G NSA | DMHF2M7081 | FLM_TE |  | Dears Kindly check HW | PCM-20251006-00001627 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/06/2025 16:47:09 | 10/06/2025 17:00:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001005 | PCM-20251006-00001733 | TT-20251006-01819 | EM | Region_1 | DAM0212 | DAM0212 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/06/2025 16:54:45 | 10/15/2025 11:52:42 | 10/07/2025 04:54:45 | high temprature 32 at DAM0212-P2_SRAN @ Sceco | 10/06/2025 16:48:24 | Minor | 65102 | high temprature 32 | 10/06/2025 16:44:36 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0212 | FLM_EM | [8 empty] | API | 10/06/2025 16:54:45 | 10/06/2025 17:07:38 | [6 empty] | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Departed | CM20251006001053 | PCM-20251006-00001812 | TT-20251006-01908 | Reference_telecom | Region_6 | KMS0039 | KMS0039 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/06/2025 17:26:45 | 10/09/2025 01:15:49 | 10/07/2025 05:26:45 | ReplaceableUnitProblem observed in KMS0039 NE_11 towards 10.10.159.49 @ Sceco_STB | 10/06/2025 05:27:33 | Minor |  | ReplaceableUnitProblem | 10/06/2025 05:26:30 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | KMS0039 | FLM_TE | [8 empty] | API | 10/06/2025 17:26:45 | 10/06/2025 19:21:49 | 10/09/2025 01:15:16 | 10/09/2025 01:15:49 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001095 | PCM-20251006-00001872 | TT-20251006-01963 | MW_HC | Region_4 | JED0783 | JED0783 |  |  |  | BARKAT ALI MAIN HILAL | 10/06/2025 17:54:18 | 10/07/2025 09:49:20 | 10/07/2025 05:54:18 | As per bo request Nokia MW HC E-band flapped for link JED0783-JDJZ0761 | 10/06/2025 17:54:05 | Minor | 113388 | LOF | 10/06/2025 17:54:02 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0783-JDJZ0761 | FLM_TE | [5 empty] | As per bo request Nokia MW HC E-band flapped for link JED0783-JDJZ0761 |  |  | API | 10/06/2025 17:54:18 | 10/07/2025 09:49:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001129 | PCM-20251006-00001928 | TT-20251006-02026 | Telecom | Region_4 | JDJZ0763 | JDJZ0763 |  |  |  | Riasat Ali Allah Baksh | 10/06/2025 18:36:04 | 10/06/2025 18:37:10 | 10/07/2025 00:36:04 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDJZ0763-GSM-P2 @ Generator_SG | 10/06/2025 18:29:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 18:29:18 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JDJZ0763 | FLM_TE |  |  | PCM-20251006-00001924 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/06/2025 18:36:04 | 10/06/2025 18:37:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001131 | PCM-20251006-00001930 | TT-20251006-02029 | Reference_telecom | Region_4 | JDJZ0772 | JDJZ0772 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/06/2025 18:36:31 | 10/07/2025 14:18:42 | 10/07/2025 06:36:31 | DemFail observed in JDJZ0772_01 towards 10.10.183.121 @ Generator_DG | 10/06/2025 06:36:28 | Minor |  | DemFail | 10/06/2025 06:36:22 | P3 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0772 | FLM_TE | [8 empty] | API | 10/06/2025 18:36:31 | 10/07/2025 14:18:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251006001137 | PCM-20251006-00001941 | TT-20251006-02036 | Telecom | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/06/2025 18:50:01 | 10/06/2025 18:50:01 | 10/07/2025 00:50:01 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/06/2025 18:39:33 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 18:39:23 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7558 | FLM_TE |  |  | PCM-20251006-00001938 | FLM Need to perform extensive HC in site for impacted Antenna port. FLM can take support from BO if required while FLM available on site. Pls check all Antenna Line. Perform Cleanup at RFM and Antenna end both. Once issue resolve close the PCM with RCA. | FLM Need to perform extensive HC in site for impacted Antenna port. FLM can take support from BO if required while FLM available on site. Pls check all Antenna Line. Perform Cleanup at RFM and Antenna end both. Once issue resolve close the PCM with RCA. |  |  |  | API | 10/06/2025 18:50:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001143 | PCM-20251006-00001954 | TT-20251006-02051 | EM | Region_6 | ABBS0165 | ABBS0165 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/06/2025 19:00:18 | 10/11/2025 19:36:37 | 10/07/2025 07:00:18 | SHELTER DOOR OPEN at ABBS0165-G9-L8-NL18-NL21-NNR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/06/2025 18:59:50 | Minor | 7103 | SHELTER DOOR OPEN | 10/06/2025 18:59:39 | P3 | 2G | namas | Sceco | 2G NSA | ABBS0165 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/06/2025 19:00:18 | 10/11/2025 19:36:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251006001167 | PCM-20251006-00001993 | TT-20251006-01895 | Reference_telecom | Region_4 | JED0028 | JED0028 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/06/2025 19:32:21 | 10/06/2025 19:32:21 | 10/07/2025 01:32:21 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0028-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/06/2025 15:21:04 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/06/2025 15:20:55 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0028 | FLM_TE |  | Thanks to check | PCM-20251006-00001830 | Thanks to check | Thanks to check |  |  |  | API | 10/06/2025 19:32:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006001168 | PCM-20251006-00001995 | TT-20251006-01868 | Reference_telecom | Region_4 | JED1M7769 | JED0769 | Equipment | BSS_HW_fault | Replace System Module | BARKAT ALI MAIN HILAL | 10/06/2025 19:33:21 | 10/07/2025 16:21:51 | 10/07/2025 01:33:21 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED1M7769-P1-VIP-CA-L900-L800-SBTS @ Sceco | 10/06/2025 15:26:05 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/06/2025 15:12:19 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M7769 | FLM_TE |  | Thanks to check | PCM-20251006-00001829 | Thanks to check | Thanks to check |  |  |  | API | 10/06/2025 19:33:21 | 10/07/2025 09:49:22 | 10/07/2025 09:50:19 | 10/07/2025 09:50:28 | 10/07/2025 10:38:53 | 10/07/2025 16:21:51 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001173 | PCM-20251006-00002004 | TT-20251006-02097 | Telecom | Region_4 | HAW1M7288 | HAW0288 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/06/2025 19:35:49 | 10/08/2025 02:05:44 | 10/07/2025 01:35:49 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at HAW1M7288-G9-L8-L18-L21-SBTS-P1-VIP-ARP @ Sceco | 10/06/2025 19:30:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 19:30:02 | VIP | 4G | taif | Sceco | 5G_Cell SA | HAW1M7288 | FLM_TE |  |  | PCM-20251006-00002002 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/06/2025 19:35:49 | 10/08/2025 02:05:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006001198 | PCM-20251006-00002052 | TT-20251006-02138 | Telecom | Region_4 | JD1 | JD1 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Mustaqeem Irshad Ali | 10/06/2025 20:07:55 | 10/13/2025 04:47:06 | 10/07/2025 02:07:55 | Request for support | 10/06/2025 20:07:18 | Major | 4205 | The interface traffic exceeds the threshold | 10/06/2025 20:07:18 | P1 | BSC | jeddah | Sceco_STB | IPBB NSA | Request for support | FLM_TE | [5 empty] | Request for support |  |  | API | 10/06/2025 20:07:55 | 10/13/2025 04:43:41 | 10/13/2025 04:46:28 |  |  | 10/13/2025 04:47:06 |  | Muhammad Mustaqeem Irshad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006001230 | PCM-20251006-00002097 | TT-20251006-02184 | Reference_telecom | Region_6 | BHAB2103 | BHAB2103 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/06/2025 20:57:13 | 10/14/2025 18:09:44 | 10/07/2025 02:57:13 | 2(2G) 2(LTE) site down under BHAB2091-P3,BHAB2103-P3 ( REF : TT-20251006-01515 ) | 10/06/2025 19:13:18 | Major | 7706 | BTS O&M LINK FAILURE | 10/06/2025 19:13:18 | P3 | 2G | Baha | Generator_DG | 2G_3G_LTE SA | BHAB2091-P3,BHAB2103-P3 | FLM_TE | BHAB2091 | Results: DOWN SITE HUB BHAB2091-P3 BHAB2091 BHAB2103-P3 BHAB2103 Summary: Hub: BHAB2091, Down Count: 1, Down Sites: BHAB2091-P3 Hub: BHAB2103, Down Count: 1, Down Sites: BHAB2103-P3 Alarm Summary: BHAB2091 No Active Alarm on HUB BHAB2103 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/06/2025 20:57:13 | 10/06/2025 20:58:00 | 10/06/2025 21:32:31 |  |  | 10/06/2025 21:32:49 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006001255 | PCM-20251006-00002134 | TT-20251006-02217 | Reference_telecom | Region_6 | DMD1M3043 | DMD0043 | Equipment | BTS_Cable | Replace Ethernet Cable | Zeshan Ali Adnan | 10/06/2025 21:29:50 | 10/06/2025 22:36:37 | 10/07/2025 03:29:50 | 1(3G) site down under DMD1M3043 ( REF : TT-20251006-02185 ) | 10/06/2025 20:52:47 | Major | 7706 | BTS O&M LINK FAILURE | 10/06/2025 20:52:47 | P2 | 3G | jizan | Sceco | 3G SA | DMD1M3043 | FLM_TE | DMD1M3043 | Results: DOWN SITE HUB DMD1M3043 DMD1M3043 Summary: Hub: DMD1M3043, Down Count: 1, Down Sites: DMD1M3043 Alarm Summary: DMD1M3043 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/06/2025 21:29:50 | 10/06/2025 22:35:55 | 10/06/2025 22:36:18 | 10/06/2025 22:36:21 |  | 10/06/2025 22:36:37 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001273 | PCM-20251006-00002174 | TT-20251006-02263 | EM | Region_4 | TURY0685 | TURY0685 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/06/2025 21:54:55 | 10/14/2025 09:01:50 | 10/07/2025 03:54:55 | FIRE ALARM+FIRE ALARM FAILURE at TURY0685-GSM-P1-HUB @ Sceco | 10/06/2025 21:46:35 | Major | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/06/2025 21:46:25 | P1 | 2G | taif | Sceco | 2G NSA | TURY0685 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | API | 10/06/2025 21:54:55 | 10/14/2025 09:01:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251006001276 | PCM-20251006-00002178 | TT-20251006-02265 | Telecom | Region_4 | HAN0441 | HAN0441 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Khizer Hayat | 10/06/2025 21:56:28 | 10/08/2025 18:13:09 | 10/07/2025 03:56:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAN0441-G9-L18-NNR2.6-SBTS-P2 @ Sceco | 10/06/2025 21:55:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 21:55:20 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | HAN0441 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/06/2025 21:56:28 | 10/07/2025 07:39:25 | 10/07/2025 16:20:07 | 10/07/2025 16:20:12 | 10/07/2025 16:20:16 | 10/08/2025 08:58:32 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251006001315 | PCM-20251006-00002243 | TT-20251006-02306 | Telecom | Region_6 | DRB0952 | DRB0952 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | Muhammad Usman Muhammad Zia ul haq | 10/06/2025 22:42:40 | 10/11/2025 14:25:23 | 10/07/2025 04:42:40 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at DRB0952-GSM-UMTS-P3 @ Sceco | 10/06/2025 22:19:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 22:19:25 | P3 | 2G | derb | Sceco | 5G_Cell SA | DRB0952 | FLM_TE |  |  | PCM-20251006-00002218 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/06/2025 22:42:40 | 10/07/2025 01:10:59 | 10/11/2025 14:25:11 |  |  | 10/11/2025 14:25:23 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251006001328 | PCM-20251006-00002260 | TT-20251006-02338 | EM | Region_6 | ABBS2191 | ABBS2191 |  |  |  | ISHFAQ HUSSAIN MUSHTAQ HUSSAIN | 10/06/2025 23:00:33 | 10/07/2025 07:05:41 | 10/07/2025 05:00:33 | 1(2G/5G) sites down under ABBS2191-P3/ABBS2191-P3 @ Sceco | 10/06/2025 22:52:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/06/2025 22:52:00 | P3 | 2G | namas | Sceco | 2G_5G SA | ABBS2191-P3 | FLM_EM | ABBS2191 | Results: DOWN SITE HUB ABBS2191-P3 ABBS2191 Summary: Hub: ABBS2191, Down Count: 1, Down Sites: ABBS2191-P3 Alarm Summary: ABBS2191 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/06/2025 23:00:33 | 10/07/2025 07:05:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000007 | PCM-20251007-00000010 | TT-20251007-00006 | EM | Region_5 | MK2 | MAK2 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/07/2025 00:06:39 | 10/07/2025 22:09:07 | 10/07/2025 04:06:39 | Door Alarm shelter 1(Input) (Input-1) at MK2-8 on 10.154.129.65 @ Sceco_STB | 10/07/2025 00:04:43 | Critical | Door Alarm shelter 1(Input) (Input-1) | Door Alarm shelter 1(Input) (Input-1) | 10/06/2025 23:57:37 | P1 | BSC | makkah | Sceco_STB | TX NSA | MK2 | FLM_EM | [8 empty] | API | 10/07/2025 00:06:39 | 10/07/2025 22:09:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000008 | PCM-20251007-00000011 | TT-20251007-00007 | EM | Region_5 | MK2 | MAK2 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/07/2025 00:06:39 | 10/07/2025 22:09:08 | 10/07/2025 04:06:39 | Door Open(Input) (Input-2) at MK2-14 PROTECTION on 10.154.135.52 @ Sceco_STB | 10/07/2025 00:04:48 | Critical | Door Open(Input) (Input-2) | Door Open(Input) (Input-2) | 10/07/2025 00:01:32 | P1 | BSC | makkah | Sceco_STB | TX NSA | MK2 | FLM_EM | [8 empty] | API | 10/07/2025 00:06:39 | 10/07/2025 22:09:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000040 | PCM-20251007-00000076 | TT-20251007-00068 | Reference_telecom | Region_1 | HFS2M3067 | HFS0067 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/07/2025 00:51:36 | 10/07/2025 02:04:06 | 10/07/2025 12:51:36 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M3067-P3 @ Generator_SG | 10/06/2025 21:51:11 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/06/2025 21:51:07 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M3067 | FLM_TE | [8 empty] | API | 10/07/2025 00:51:36 | 10/07/2025 02:04:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000082 | PCM-20251007-00000166 | TT-20251007-00189 | EM | Region_1 | R1_HF_HWBSC01 | HF1 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/07/2025 02:16:54 | 10/07/2025 05:57:17 | 10/07/2025 06:16:54 | Intruder Alarm(SH1) at R1_HF_HWBSC01 @ Sceco_STB | 10/07/2025 02:16:13 | Critical | 65334 | Intruder Alarm(SH1) | 10/07/2025 02:16:09 | P1 | BSC | hafouf | Sceco_STB | 2G NSA | R1_HF_HWBSC01 | FLM_EM | [8 empty] | API | 10/07/2025 02:16:54 | 10/07/2025 03:43:18 | 10/07/2025 05:57:10 |  |  | 10/07/2025 05:57:17 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000089 | PCM-20251007-00000188 | TT-20251007-00214 | EM | Region_6 | TFBH1M7812 | TFBH0812 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 10/07/2025 02:32:21 | 10/11/2025 10:02:38 | 10/07/2025 14:32:21 | AIRCON 2 FAILURE at TFBH1M7812-G9-L8-SBTS-P3 @ Sceco | 10/07/2025 02:25:35 | Minor | 7103 | AIRCON 2 FAILURE | 10/07/2025 02:24:09 | P3 | 4G | makhwa | Sceco | LTE NSA | TFBH1M7812 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/07/2025 02:32:21 | 10/07/2025 13:09:56 | 10/11/2025 10:02:27 |  |  | 10/11/2025 10:02:38 |  | Arif Ullah Shah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000090 | PCM-20251007-00000190 | TT-20251007-00219 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/07/2025 02:33:23 | 10/20/2025 12:32:38 | 10/07/2025 06:33:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/07/2025 02:32:40 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 02:32:34 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/07/2025 02:33:23 | 10/07/2025 12:30:10 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000097 | PCM-20251007-00000209 | TT-20251007-00245 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/07/2025 02:45:16 | 10/20/2025 12:32:39 | 10/07/2025 14:45:16 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/07/2025 02:36:56 | Minor | 7115 | BASE STATION INFORMATION | 10/07/2025 02:36:49 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/07/2025 02:45:16 | 10/07/2025 12:30:11 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000116 | PCM-20251007-00000243 | TT-20251007-00298 | EM | Region_6 | BHAB1M7819 | BHAB0819 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 10/07/2025 03:02:18 | 10/11/2025 10:03:08 | 10/07/2025 15:02:18 | Smoke Alarm at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/07/2025 02:56:14 | Minor | 7103 | Smoke Alarm | 10/07/2025 02:53:52 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7819 | FLM_EM | [5 empty] | Smoke Alarm |  |  | API | 10/07/2025 03:02:18 | 10/07/2025 13:09:56 | 10/11/2025 10:02:56 |  |  | 10/11/2025 10:03:08 |  | Arif Ullah Shah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000119 | PCM-20251007-00000247 | TT-20251007-00307 | EM | Region_6 | BHAB1M7883 | BHAB0883 |  |  |  | Zia Ur Rahamn | 10/07/2025 03:03:54 | 10/07/2025 15:03:31 | 10/07/2025 15:03:54 | AIRCON 2 FAILURE at BHAB1M7883-G9-L8-SBTS-P3 @ Sceco | 10/07/2025 02:56:30 | Minor | 7103 | AIRCON 2 FAILURE | 10/07/2025 02:55:21 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7883 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/07/2025 03:03:54 | 10/07/2025 15:03:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000122 | PCM-20251007-00000250 | TT-20251007-00310 | EM | Region_6 | QLW1M8354 | QLW2354 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/07/2025 03:05:24 | 10/07/2025 13:43:34 | 10/07/2025 15:05:24 | RECTIFIER MODULE FAILURE at QLW1M8354-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/07/2025 02:57:09 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/07/2025 02:57:00 | P3 | 4G | Albaha | Generator_SG | LTE NSA | QLW1M8354 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/07/2025 03:05:24 | 10/07/2025 13:43:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000128 | PCM-20251007-00000256 | TT-20251007-00254 | EM | Region_2 | RYD0940 | RYD0940 | Equipment | BSS_HW_fault | Replace Controller Card | WAQAR AHMED BASHIR AHMED | 10/07/2025 03:08:28 | 10/07/2025 03:46:07 | 10/07/2025 07:08:28 | 1(2G/3G/LTE) sites down under RYD0940-P1-HUB/RY1BSCH02 @ Generator_DG | 10/07/2025 02:46:37 | Critical | 21825 | CSL Fault | 10/07/2025 02:46:36 | P1 | SRAN | rumah | Generator_DG | 2G_3G SA | RYD0940-P1-HUB | FLM_TE | RYD0940 | Results: DOWN SITE HUB RYD0940-P1-HUB RYD0940 Summary: Hub: RYD0940, Down Count: 1, Down Sites: RYD0940-P1-HUB Alarm Summary: RYD0940 No Active Alarm on HUB | PCM-20251007-00000225 | Telecom team at site TS | Telecom team at site TS |  | sites down |  | API | 10/07/2025 03:08:28 | 10/07/2025 03:09:56 | 10/07/2025 03:38:20 | 10/07/2025 03:38:22 | 10/07/2025 03:38:24 | 10/07/2025 03:46:07 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000130 | PCM-20251007-00000259 | TT-20251007-00319 | EM | Region_1 | HF1 | HF1 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/07/2025 03:09:32 | 10/07/2025 05:57:05 | 10/07/2025 09:09:32 | Door opening alarm BSC New shelter at HF1-Shelter 3-Core-P1 @ Sceco_STB | 10/07/2025 03:08:56 | Major | 65134 | Door opening alarm BSC New shelter | 10/07/2025 03:08:54 | P1 | BSC | hafouf | Sceco_STB | 2G NSA | HF1 | FLM_EM | [8 empty] | API | 10/07/2025 03:09:32 | 10/07/2025 03:43:18 | 10/07/2025 05:56:59 |  |  | 10/07/2025 05:57:05 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000144 | PCM-20251007-00000283 | TT-20251007-00352 | EM | Region_1 | HFF6029 | HFF6029 | Enviroment | Air Condition | Change Fan | Amr Ahmed Gouda | 10/07/2025 03:26:34 | 10/12/2025 13:09:39 | 10/07/2025 15:26:34 | high temprature 40 at HFF6029-P3_SRAN @ Sceco | 10/07/2025 03:20:26 | Minor | 65103 | high temprature 40 | 10/07/2025 03:16:19 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_EM | [8 empty] | API | 10/07/2025 03:26:34 | 10/12/2025 13:07:46 | 10/12/2025 13:09:00 |  |  | 10/12/2025 13:09:39 |  | Amr Ahmed Gouda | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000148 | PCM-20251007-00000305 | TT-20251007-00391 | Telecom | Region_2 | RYD2M7940 | RYD0940 | Equipment | BSS_HW_fault | Replace Controller Card | WAQAR AHMED BASHIR AHMED | 10/07/2025 03:36:42 | 10/07/2025 03:46:40 | 10/07/2025 09:36:42 | Cell Unavailable at RYD2M7940-L800 @ Generator_DG | 10/07/2025 03:33:21 | Major | 29240 | Cell Unavailable | 10/07/2025 03:31:46 | P1 | 4G | rumah | Generator_DG | LTE SA | RYD2M7940 | FLM_TE | [8 empty] | API | 10/07/2025 03:36:42 | 10/07/2025 03:41:45 | 10/07/2025 03:46:15 | 10/07/2025 03:46:18 | 10/07/2025 03:46:20 | 10/07/2025 03:46:40 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000149 | PCM-20251007-00000307 | TT-20251007-00392 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/07/2025 03:37:23 | 10/07/2025 14:35:21 | 10/07/2025 09:37:23 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/07/2025 00:36:00 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/07/2025 00:37:14 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/07/2025 03:37:23 | 10/07/2025 14:35:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000150 | PCM-20251007-00000312 | TT-20251007-00396 | EM | Region_6 | BAH0173 | BAH0173 |  |  |  | Sohail Nasir Mir Afzal | 10/07/2025 03:42:03 | 10/08/2025 11:11:07 | 10/07/2025 15:42:03 | AIRCON 1 FAILURE at BAH0173-L800-CA-NR2.6-SBTS-P2-WBB-G3 @ Sceco | 10/07/2025 03:33:40 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 03:33:36 | P2 | 2G | Albaha | Sceco | 2G NSA | BAH0173 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 03:42:03 | 10/07/2025 07:36:36 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000153 | PCM-20251007-00000316 | TT-20251007-00400 | EM | Region_6 | ARS0125 | ARS0125 |  |  |  | Khurram Nawaz Muhammad Akram | 10/07/2025 03:42:33 | 10/08/2025 11:11:05 | 10/07/2025 15:42:33 | AIRCON 1 FAILURE at ARS0125-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/07/2025 03:34:34 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 03:34:23 | P2 | 2G | jizan | Sceco | 2G NSA | ARS0125 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 03:42:33 | 10/07/2025 03:46:20 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Accept | CM20251007000198 | PCM-20251007-00000418 | TT-20251007-00524 | EM | Region_5 | USMD0770 | USMD0770 |  |  |  | Mohammad Naseer Raja Mohammed | 10/07/2025 04:41:27 | 10/07/2025 08:11:47 | 10/07/2025 16:41:27 | COMMERCIAL POWER FAILURE at USMD0770-GSM-UMTS-P2-USF @ Sceco_STB | 10/07/2025 04:32:58 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/07/2025 04:32:54 | P1 | 2G | makkah | Sceco_STB | 2G NSA | USMD0770 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/07/2025 04:41:27 | 10/07/2025 06:57:21 | 10/07/2025 08:11:47 | [8 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251007000203 | PCM-20251007-00000429 | TT-20251007-00532 | Telecom | Region_4 | JED0253 | JED0253 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 04:45:33 | 10/08/2025 18:13:10 | 10/07/2025 10:45:33 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connector) at JED0253-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/07/2025 04:40:50 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 04:40:44 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0253 | FLM_TE | [5 empty] | Increased BER detected on the optical connector |  |  | API | 10/07/2025 04:45:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000204 | PCM-20251007-00000431 | TT-20251007-00534 | Telecom | Region_2 | RIY0322 | RIY0322 | Equipment | SFP_BTS | Clean SFP | Muhammad Naeem Muhammad Gulzar | 10/07/2025 04:46:36 | 10/12/2025 12:11:03 | 10/07/2025 08:46:36 | PORT_MODULE_OFFLINE at RIY0322 (RY1)_ELC @ Sceco | 10/07/2025 04:45:58 | Critical | 1-63629 | PORT_MODULE_OFFLINE | 10/07/2025 04:45:43 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0322 | FLM_TE | [5 empty] | 5-ELC(2-E)-5-G1M520S-3(RX1/TX1(CID:RY1JD1-100G-23))-CLIENT:1 |  |  | API | 10/07/2025 04:46:36 | 10/08/2025 21:14:08 | 10/12/2025 12:10:50 |  |  | 10/12/2025 12:11:03 |  | Muhammad Naeem Muhammad Gulzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000213 | PCM-20251007-00000440 | TT-20251007-00047 | Reference_telecom | Region_4 | HBI1M7353 | HBI0353 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/07/2025 04:49:57 | 10/16/2025 11:20:31 | 10/07/2025 16:49:57 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at HBI1M7353-G9-NL8-L18-SBTS-P3 @ Sceco | 10/06/2025 22:34:18 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/06/2025 22:32:44 | P3 | 4G | qunfuddah | Sceco | LTE NSA | HBI1M7353 | FLM_TE |  |  | PCM-20251007-00000057 | site down | site down |  |  |  | API | 10/07/2025 04:49:57 | 10/07/2025 14:18:43 | 10/16/2025 11:20:23 |  |  | 10/16/2025 11:20:31 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000235 | PCM-20251007-00000470 | TT-20251007-00554 | Telecom | Region_2 | RIYA6042 | RIYA6042 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/07/2025 05:07:46 | 10/07/2025 12:28:32 | 10/07/2025 17:07:46 | RF Unit Maintenance Link Failure at RIYA6042-DCU-3 @ Sceco | 10/07/2025 05:05:41 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/07/2025 05:02:31 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6042 | FLM_TE | [8 empty] | API | 10/07/2025 05:07:46 | 10/07/2025 12:28:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000252 | PCM-20251007-00000506 | TT-20251007-00202 | Telecom | Region_6 | AQQ0841 | AQQ0841 |  |  |  | Sohail Nasir Mir Afzal | 10/07/2025 05:37:09 | 10/07/2025 11:30:53 | 10/07/2025 09:37:09 | 1(2G) 8(LTE) sites down under AQQ0841-P3 @ Sceco | 10/07/2025 02:22:12 | Critical | 7706 | BTS O&M LINK FAILURE | 10/07/2025 02:22:06 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | AQQ2425-G9-L8-SBTS-P3-CAP LTE,AQQ2331-G9-L8-L18-SBTS-CAP-P3 LTE,UKHA2360-G9-L8-L18-SBTS-P3 LTE,BAH2152-G9-L8-L18-SBTS-P3-CAP LTE,BAH2155-G9-L8-L18-SBTS-P3-CAP LTE,QLW2364-G9-L8-L18-SBTS-P3 LTE,AQQ2433-G9-L800-P3-SBTS LTE,AQQ2431-G9-L8-L18-SBTS-P3 LTE,AQQ0841-P3 2G | FLM_TE | AQQ0841 | kindly check with access as these related to RFC CRQ000000535358 | PCM-20251007-00000184 | kindly check with access as these related to RFC CRQ000000535358 | kindly check with access as these related to RFC CRQ000000535358 |  | sites down |  | API | 10/07/2025 05:37:09 | 10/07/2025 11:30:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000257 | PCM-20251007-00000512 | TT-20251007-00165 | Telecom | Region_4 | JDAP1M7940 | JDAP0940 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/07/2025 05:41:45 | 10/21/2025 18:24:47 | 10/07/2025 11:41:45 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/07/2025 01:48:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 01:48:17 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JDAP1M7940 | FLM_TE |  |  | PCM-20251007-00000149 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/07/2025 05:41:45 | 10/07/2025 19:01:09 | 10/21/2025 18:24:42 |  |  | 10/21/2025 18:24:47 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000265 | PCM-20251007-00000525 | TT-20251006-02056 | Telecom | Region_6 | TNMS0711 | TNMS0711 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Fawad Khan | 10/07/2025 05:49:19 | 10/21/2025 17:12:39 | 10/07/2025 11:49:19 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by transmission path (Tx) failure) at TNMS0711-G9-L8-NR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/06/2025 19:02:31 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/06/2025 19:02:20 | P3 | 2G | namas | Sceco | 5G_Cell SA | TNMS0711 | FLM_TE |  |  | PCM-20251007-00000045 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/07/2025 05:49:19 | 10/07/2025 08:24:16 | 10/07/2025 23:20:52 | 10/07/2025 23:21:09 |  | 10/07/2025 23:22:09 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000304 | PCM-20251007-00000584 | TT-20251007-00645 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/07/2025 06:22:54 | 10/21/2025 18:24:37 | 10/07/2025 18:22:54 | RFC RF Port Input Power Out of Range at JED6008-DCU-P3 @ Sceco | 10/06/2025 19:52:51 | Minor | 28754 | RFC RF Port Input Power Out of Range | 10/06/2025 19:52:17 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/07/2025 06:22:54 | 10/07/2025 19:01:10 | 10/21/2025 18:24:31 |  |  | 10/21/2025 18:24:37 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000324 | PCM-20251007-00000631 | TT-20251007-00690 | Telecom | Region_1 | HFF6028 | HFF6028 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/07/2025 06:54:44 | 10/15/2025 11:52:43 | 10/07/2025 12:54:44 | RF Unit Optical Module Transmit/Receive Fault at HFF6028-DCU2 @ Sceco | 10/07/2025 03:19:07 | Major | 26503 | RF Unit Optical Module Transmit/Receive Fault | 10/07/2025 03:19:02 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/07/2025 06:54:44 | 10/07/2025 07:59:02 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007000344 | PCM-20251007-00000667 | TT-20251007-00719 | Reference_telecom | Region_4 | JDMK2408 | JDMK2408 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/07/2025 07:23:06 | 10/07/2025 07:23:06 | 10/07/2025 19:23:06 | FanFailure observed in JDMK2408 towards 10.3.233.150 @ Generator_SG | 10/06/2025 19:24:54 | Minor |  | FanFailure | 10/06/2025 19:22:37 | P3 | 2G | makkah | Generator_SG | TX NSA | JDMK2408 | FLM_TE | [8 empty] | API | 10/07/2025 07:23:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000383 | PCM-20251007-00000736 | TT-20251007-00788 | Reference_telecom | Region_1 | HFS2M4025 | HFS2025 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/07/2025 08:06:30 | 10/07/2025 09:48:41 | 10/07/2025 20:06:30 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M4025-P3 @ Generator_SG | 10/07/2025 05:06:05 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/07/2025 05:06:01 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M4025 | FLM_TE | [8 empty] | API | 10/07/2025 08:06:30 | 10/07/2025 09:48:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000403 | PCM-20251007-00000774 | TT-20251007-00671 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/07/2025 08:21:27 | 10/20/2025 12:32:40 | 10/07/2025 12:21:27 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/07/2025 02:40:40 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 02:40:33 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251007-00000604 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/07/2025 08:21:27 | 10/07/2025 12:30:13 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000404 | PCM-20251007-00000775 | TT-20251007-00763 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/07/2025 08:21:50 | 10/20/2025 12:32:44 | 10/07/2025 14:21:50 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at MKYL0914-GSM-UMTS-P3 @ Sceco | 10/07/2025 07:48:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 07:48:13 | P3 | 2G | alaith | Sceco | 5G_Cell SA | MKYL0914 | FLM_TE |  |  | PCM-20251007-00000710 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/07/2025 08:21:50 | 10/08/2025 14:44:08 | [6 empty] | Force_Majeure |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000416 | PCM-20251007-00000801 | TT-20251007-00835 | Telecom | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/07/2025 08:30:17 | 10/08/2025 18:13:11 | 10/07/2025 14:30:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/07/2025 08:29:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 08:29:23 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2259 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/07/2025 08:30:17 | 10/07/2025 09:49:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000431 | PCM-20251007-00000834 | TT-20251007-00858 | EM | Region_4 | BHMF2137 | BHMF2137 |  |  |  | Khizer Hayat | 10/07/2025 08:52:32 | 10/09/2025 16:53:13 | 10/07/2025 14:52:32 | 1(2G/LTE) sites down under BHMF2137-P3/BHMF2137-P3 @ Generator_SG | 10/07/2025 08:44:21 | Major | 7706 | BTS O&M LINK FAILURE | 10/07/2025 08:44:15 | P3 | 2G | jeddah | Generator_SG | 2G SA | BHMF2137-P3 | FLM_TE | BHMF2137 | Results: DOWN SITE HUB BHMF2137-P3 BHMF2137 Summary: Hub: BHMF2137, Down Count: 1, Down Sites: BHMF2137-P3 Alarm Summary: BHMF2137 No Active Alarm on HUB |  |  |  |  | sites down |  | Manual | 10/07/2025 08:52:32 | 10/09/2025 16:53:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000437 | PCM-20251007-00000840 | TT-20251007-00873 | Reference_telecom | Region_4 | JED2256 | JED2256 |  |  |  | Nazeer Mohammed | 10/07/2025 08:57:07 | 10/07/2025 10:41:50 | 10/07/2025 20:57:07 | FanFailure observed in JED2256_01 towards 10.21.72.244 @ Generator_SG | 10/06/2025 20:57:50 | Minor |  | FanFailure | 10/06/2025 20:56:54 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED2256 | FLM_TE | [8 empty] | API | 10/07/2025 08:57:07 | 10/07/2025 10:41:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000466 | PCM-20251007-00000888 | TT-20251007-00932 | Reference_EM | Region_1 | JBL0473 | JBL0473 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Salah Abdalgadir Ahmed | 10/07/2025 09:35:21 | 10/10/2025 17:26:19 | 10/07/2025 21:35:21 | high temprature 32 at JBL0473-P2_SRAN @ Sceco | 10/07/2025 09:25:01 | Minor | 65102 | high temprature 32 | 10/07/2025 09:24:58 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0473 | FLM_EM | [8 empty] | API | 10/07/2025 09:35:21 | 10/07/2025 17:26:33 | 10/10/2025 17:26:12 |  |  | 10/10/2025 17:26:19 |  | Ahmed Salah Abdalgadir Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000468 | PCM-20251007-00000891 | TT-20251007-00608 | Telecom | Region_2 | RIY0282 | RIY0282 | Equipment | BTS_Cable | Replace Fiber Cable | Ejaz Hussain Muhammad Sharif | 10/07/2025 09:36:08 | 10/07/2025 12:00:52 | 10/07/2025 15:36:08 | BBU CPRI Interface Error at RIY0282-P2_SRAN @ Sceco | 10/07/2025 05:56:50 | Major | 26234 | BBU CPRI Interface Error | 10/07/2025 05:54:17 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0282 | FLM_TE |  |  | PCM-20251007-00000689 | TE issue at site and access secured | TE issue at site and access secured |  |  |  | API | 10/07/2025 09:36:08 | 10/07/2025 09:36:51 | 10/07/2025 09:37:25 | 10/07/2025 09:37:28 | 10/07/2025 09:37:39 | 10/07/2025 12:00:52 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000503 | PCM-20251007-00000952 | TT-20251007-00995 | Telecom | Region_4 | SHB1M7670 | SHB0670 |  |  |  | Riasat Ali Allah Baksh | 10/07/2025 10:05:50 | 10/08/2025 14:44:09 | 10/07/2025 22:05:50 | BASE STATION INFORMATION (Fan vendor not detected) at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/07/2025 09:57:29 | Minor | 7115 | BASE STATION INFORMATION | 10/07/2025 09:57:22 | P3 | 4G | qunfuddah | Sceco | LTE NSA | SHB1M7670 | FLM_TE | [5 empty] | Fan vendor not detected |  |  | API | 10/07/2025 10:05:50 | 10/08/2025 14:44:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251007000522 | PCM-20251007-00000982 | TT-20251007-01025 | EM | [7 empty] | 10/07/2025 10:21:21 | 10/07/2025 10:21:21 | 10/07/2025 16:21:21 | RECTIFIER MAINS POWER FAILURE at MAK1U6745-G18-L18-L21-SBTS-P1-HRM @ Sceco | 10/07/2025 10:13:09 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/07/2025 10:13:00 | P1 | 4G |  | Sceco | LTE NSA | MAK1U6745 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/07/2025 10:21:21 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000540 | PCM-20251007-00001014 | TT-20251007-00046 | Reference_telecom | Region_4 | JZMA1M7824 | JZMA0824 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/07/2025 10:40:35 | 10/16/2025 11:20:47 | 10/07/2025 22:40:35 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JZMA1M7824-G9-L8-SBTS-P3 @ Sceco | 10/06/2025 22:33:20 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/06/2025 22:32:37 | P3 | 4G | qunfuddah | Sceco | LTE NSA | JZMA1M7824 | FLM_TE |  |  | PCM-20251007-00000666 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/07/2025 10:40:35 | 10/07/2025 14:18:56 | 10/16/2025 11:20:40 |  |  | 10/16/2025 11:20:47 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000558 | PCM-20251007-00001048 | TT-20251007-01084 | Telecom | Region_4 | JED1MN2980 | JED2980 | Equipment | SFP_BTS | Clean SFP | Moustafa Mahmoud Ahmed Fathelbab | 10/07/2025 10:49:29 | 10/12/2025 15:44:32 | 10/07/2025 16:49:29 | PT::FLM need to perform HC at JED1MN2980 (Bo request) | 10/07/2025 10:49:09 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/07/2025 10:49:09 | P3 | 5G | jeddah | Generator_SG | 2G_3G_LTE_5G NSA | JED1MN2980 | FLM_TE | [8 empty] | API | 10/07/2025 10:49:29 | 10/07/2025 11:25:20 | 10/07/2025 19:12:36 | 10/07/2025 19:12:40 | 10/07/2025 19:12:42 | 10/12/2025 15:44:32 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000600 | PCM-20251007-00001128 | TT-20251007-01149 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/07/2025 11:14:32 | 10/07/2025 22:19:34 | 10/07/2025 23:14:32 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/07/2025 08:14:16 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/07/2025 08:14:12 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/07/2025 11:14:32 | 10/07/2025 22:19:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000611 | PCM-20251007-00001141 | TT-20251007-01157 | Telecom | Region_6 | TLT0921 | TLT0921 | Equipment | BSS_HW_fault | Replace FAN | Muhammad Afzal Muhammad Aslam | 10/07/2025 11:18:08 | 10/09/2025 16:23:50 | 10/07/2025 17:18:08 | BASE STATION INFORMATION at TLT0921-GSM-P2 @ Generator_SG | 10/07/2025 11:11:36 | Major | 7115 | BASE STATION INFORMATION | 10/07/2025 11:11:28 | P2 | 2G | turaib | Generator_SG | 2G NSA | TLT0921 | FLM_TE | [5 empty] | Fan vendor not detected |  |  | API | 10/07/2025 11:18:08 | 10/07/2025 12:12:43 | 10/09/2025 16:23:36 |  |  | 10/09/2025 16:23:50 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000615 | PCM-20251007-00001147 | TT-20251007-01161 | Telecom | Region_6 | KMS0515 | KMS0515 | Equipment | BSS_HW_fault | Replace FAN | Muhammad shafiq Muhammad Rasheed | 10/07/2025 11:19:11 | 10/12/2025 17:58:21 | 10/07/2025 17:19:11 | BASE STATION INFORMATION at KMS0515-GSM-P1-VIP-SHOP @ Sceco | 10/07/2025 11:15:32 | Major | 7115 | BASE STATION INFORMATION | 10/07/2025 11:14:35 | VIP | 2G | khamis mushyet | Sceco | 2G NSA | KMS0515 | FLM_TE | [5 empty] | Fan vendor not detected |  |  | API | 10/07/2025 11:19:11 | 10/07/2025 19:22:38 | 10/08/2025 17:53:32 | 10/08/2025 17:53:38 | 10/12/2025 17:26:10 | 10/12/2025 17:58:21 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000664 | PCM-20251007-00001218 | TT-20251007-01206 | Reference_telecom | Region_5 | SHU0331 | SHU0331 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/07/2025 11:50:41 | 10/14/2025 18:13:40 | 10/07/2025 17:50:41 | 1(2G/3G/LTE) sites down under SHU0331-P3 (REF:CRQ000000535027) @ Sceco | 10/07/2025 10:43:24 | Major | 7706 | BTS O&M LINK FAILURE | 10/07/2025 10:43:24 | P3 | 2G | makkah | Generator_SG | 2G_3G SA | SHU0331 | FLM_TE | SHU0331 | Results: DOWN SITE HUB SHU0331 SHU0331 Summary: Hub: SHU0331, Down Count: 1, Down Sites: SHU0331 Alarm Summary: SHU0331 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/07/2025 11:50:41 | 10/08/2025 15:09:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000690 | PCM-20251007-00001254 | TT-20251007-00986 | Telecom | Region_4 | GMK0442 | GMK0442 |  |  |  | Riasat Ali Allah Baksh | 10/07/2025 12:13:50 | 10/08/2025 14:44:09 | 10/07/2025 18:13:50 | BCF NOTIFICATION (FF FF FF FF FF FF) at GMK0442-P2-USF @ Sceco | 10/07/2025 09:53:31 | Major | 7602 | BCF NOTIFICATION | 10/07/2025 09:53:17 | P2 | 2G | qunfuddah | Sceco | 2G NSA | GMK0442 | FLM_TE |  |  | PCM-20251007-00000944 | Kindly check the GPS and it's position at site | Kindly check the GPS and it's position at site |  |  |  | API | 10/07/2025 12:13:50 | 10/08/2025 14:44:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000714 | PCM-20251007-00001288 | TT-20251007-01292 | EM | Region_1 | HFR0502 | HFR0502 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/07/2025 12:33:05 | 10/09/2025 06:01:12 | 10/07/2025 16:33:05 | Door opening alarm at HFR0502-P1-Core-HUB-WDM_SRAN-FON @ Sceco_STB | 10/07/2025 12:32:33 | Critical | 65101 | Door opening alarm | 10/07/2025 12:32:31 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | HFR0502 | FLM_EM | [8 empty] | API | 10/07/2025 12:33:05 | 10/07/2025 16:46:26 | 10/09/2025 06:01:01 |  |  | 10/09/2025 06:01:12 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251007000761 | PCM-20251007-00001365 | TT-20251007-01380 | Telecom | Region_4 | JED1MN2352 | JED2352 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 10/07/2025 13:15:57 | 10/08/2025 18:33:10 | 10/07/2025 19:15:57 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2352-NR2.6-P2 @ Sceco | 10/07/2025 13:15:11 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 13:15:02 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2352 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/07/2025 13:15:57 | 10/08/2025 18:13:14 | 10/08/2025 18:33:06 | 10/08/2025 18:33:08 | 10/08/2025 18:33:10 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000799 | PCM-20251007-00001431 | TT-20251007-01392 | Telecom | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/07/2025 13:44:37 | 10/07/2025 16:57:43 | 10/07/2025 19:44:37 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TURY0688-GSM-P3 @ Sceco | 10/07/2025 13:15:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 13:15:47 | P3 | 2G | taif | Sceco | 5G_Cell SA | TURY0688 | FLM_TE |  |  | PCM-20251007-00001374 | RSSI alarm active at site, kindly check | RSSI alarm active at site, kindly check |  |  |  | API | 10/07/2025 13:44:37 | 10/07/2025 16:57:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000805 | PCM-20251007-00001441 | TT-20251007-01448 | Telecom | Region_4 | JED1M9491 | JED0491 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/07/2025 13:47:01 | 10/07/2025 18:02:56 | 10/07/2025 19:47:01 | BASE STATION OPERATION DEGRADED (GNSS receiver signal inaccurate) at JED1M9491-CA-P2 @ Generator_SG | 10/07/2025 13:37:01 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/07/2025 13:36:55 | P2 | 4G | jeddah | Generator_SG | LTE NSA | JED1M9491 | FLM_TE |  |  | PCM-20251007-00001428 | Kindly check the GPS and it's location at site and perform HC | Kindly check the GPS and it's location at site and perform HC |  |  |  | API | 10/07/2025 13:47:01 | 10/07/2025 14:31:09 | 10/07/2025 18:02:50 |  |  | 10/07/2025 18:02:56 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000823 | PCM-20251007-00001471 | TT-20251007-01460 | Reference_telecom | Region_4 | JED2820 | JED2820 | Equipment | SFP_BTS | Clean SFP | BARKAT ALI MAIN HILAL | 10/07/2025 13:59:16 | 10/17/2025 20:02:26 | 10/08/2025 01:59:16 | Fronthaul loop back connectivity check failure at JED2820-G900-CA-NR2.6-SBTS-P3 @ Generator_SG | 10/07/2025 13:22:41 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/07/2025 13:22:33 | P4 | 2G | jeddah | Generator_SG | 2G NSA | JED2820 | FLM_TE |  |  | PCM-20251007-00001452 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/07/2025 13:59:16 |  | 10/16/2025 18:26:38 | 10/16/2025 18:26:41 | 10/16/2025 18:37:48 | 10/17/2025 20:02:26 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000886 | PCM-20251007-00001558 | TT-20251007-01363 | Telecom | Region_4 | JED0560 | JED0560 |  |  |  | MALIK ATIF ZAMAN | 10/07/2025 14:42:19 | 10/08/2025 09:44:27 | 10/07/2025 20:42:19 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0560-PI-VIP-ARP-SHOP @ Sceco | 10/07/2025 12:57:27 | Major | 7602 | BCF NOTIFICATION | 10/07/2025 12:57:10 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0560 | FLM_TE |  |  | PCM-20251007-00001352 | Kindly check the GPS and its location and perform HC at site | Kindly check the GPS and its location and perform HC at site |  |  |  | API | 10/07/2025 14:42:19 | 10/08/2025 09:44:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007000894 | PCM-20251007-00001565 | TT-20251007-01561 | Telecom | Region_1 | QRH2M8432 | QRH2432 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Imran Ali Yousaf | 10/07/2025 14:44:38 | 10/07/2025 15:05:43 | 10/07/2025 18:44:38 | 1(LTE) sites down under QRH2432-P1-VIP @ Generator_SG | 10/07/2025 14:37:56 | Critical | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/07/2025 14:36:19 | VIP | 4G | dammam | Generator_SG | LTE SA | QRH2432-P1-VIP | FLM_TE | QRH2432 | Results: DOWN SITE HUB QRH2432-P1-VIP QRH2432 Summary: Hub: QRH2432, Down Count: 1, Down Sites: QRH2432-P1-VIP Alarm Summary: QRH2432 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/07/2025 14:44:38 | 10/07/2025 15:04:41 | 10/07/2025 15:05:33 |  |  | 10/07/2025 15:05:43 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000897 | PCM-20251007-00001572 | TT-20251007-01578 | EM | Region_1 | KFKM0786 | KFKM0786 |  |  |  | Rahman Ullah Said Halim | 10/07/2025 14:46:21 | 10/08/2025 15:20:22 | 10/08/2025 02:46:21 | Door opening alarm at KFKM0786-P2_SRAN @ Generator_SG | 10/07/2025 14:45:43 | Minor | 65101 | Door opening alarm | 10/07/2025 14:45:40 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0786 | FLM_EM | [8 empty] | API | 10/07/2025 14:46:21 | 10/08/2025 15:20:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251007000898 | PCM-20251007-00001573 | TT-20251007-01486 | Telecom | [7 empty] | 10/07/2025 14:46:24 | 10/07/2025 14:46:24 | 10/08/2025 02:46:24 | SJED1W0266 Complete Down | 10/07/2025 13:59:15 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/07/2025 13:59:15 | P3 | WIFI |  | Sceco | Wifi SA | SJED1W0266 | FLM_TE | SJED1W0266-NNN |  | PCM-20251007-00001482 | SJED1W0266 | SJED1W0266 |  |  |  | API | 10/07/2025 14:46:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000902 | PCM-20251007-00001575 | TT-20251007-01564 | Reference_telecom | Region_5 | BIK1M7153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/07/2025 14:47:06 | 10/18/2025 03:16:08 | 10/07/2025 20:47:06 | 1(LTE) site down under BIK0153-P3(Ref:TT-20251007-00906) | 10/07/2025 14:33:09 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/07/2025 14:33:09 | P3 | 4G | makkah | Generator_SG | LTE SA | BIK1M7153-L800-CA-P3 | FLM_TE | BIK1M7153 | Results: DOWN SITE HUB BIK1M7153-L800-CA-P3 BIK1M7153 Summary: Hub: BIK1M7153, Down Count: 1, Down Sites: BIK1M7153-L800-CA-P3 Alarm Summary: BIK1M7153 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/07/2025 14:47:06 | 10/18/2025 03:16:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000903 | PCM-20251007-00001577 | TT-20251007-01583 | Telecom | Region_4 | KMMD0736 | KMMD0736 |  |  |  | Nazeer Mohammed | 10/07/2025 14:48:24 | 10/07/2025 14:58:02 | 10/08/2025 02:48:24 | ODU CPU / Cable Open at KMMD0736 on 10.154.115.114 @ Sceco | 10/07/2025 14:47:33 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/07/2025 14:46:32 | P1 | 2G | jeddah | Sceco | TX NSA | KMMD0736 | FLM_TE | [8 empty] | API | 10/07/2025 14:48:24 | 10/07/2025 14:58:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000909 | PCM-20251007-00001586 | TT-20251007-01593 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/07/2025 14:53:34 | 10/08/2025 12:03:48 | 10/08/2025 02:53:34 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/07/2025 14:45:25 | Minor | 7103 | AIRCON 2 FAILURE | 10/07/2025 14:45:14 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/07/2025 14:53:34 | 10/08/2025 12:03:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251007000944 | PCM-20251007-00001647 | TT-20251007-01648 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/07/2025 15:28:41 | 10/07/2025 16:53:29 | 10/08/2025 03:28:41 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/07/2025 15:21:54 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/07/2025 15:21:51 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/07/2025 15:28:41 | 10/07/2025 16:53:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000956 | PCM-20251007-00001661 | TT-20251007-01622 | Reference_telecom | Region_4 | DOM1M3441 | DOM0441 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/07/2025 15:30:56 | 10/08/2025 02:05:49 | 10/07/2025 21:30:56 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at DOM1M3441-P2 @ Sceco | 10/07/2025 14:42:56 | Major | 7771 | WCDMA CELL OUT OF USE | 10/07/2025 14:40:44 | P2 | 3G | taif | Sceco | 3G SA | DOM1M3441 | FLM_TE |  |  | PCM-20251007-00001620 | Kindly check the site locally as cells are down due to degraded connectivity | Kindly check the site locally as cells are down due to degraded connectivity |  |  |  | API | 10/07/2025 15:30:56 | 10/08/2025 02:05:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007000975 | PCM-20251007-00001682 | TT-20251007-01679 | Telecom | Region_5 | MAK0812 | MAK0812 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/07/2025 15:45:20 | 10/21/2025 19:56:50 | 10/07/2025 21:45:20 | PT::: As Per BO request need FLM to do HC in site MAK0812 /R6 | 10/07/2025 15:44:49 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/07/2025 15:44:53 | P2 | 2G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK0812 | FLM_TE | [8 empty] | API | 10/07/2025 15:45:20 | 10/21/2025 19:56:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251007000986 | PCM-20251007-00001700 | TT-20251007-01699 | Reference_EM | Region_2 | RIYB2U6178a | RIYB6078 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/07/2025 15:54:31 | 10/15/2025 11:52:58 | 10/08/2025 03:54:31 | Minor Rec. alarm at RIYB2U6178A-P3 @ Sceco | 10/07/2025 15:44:06 | Minor | 65108 | Minor Rec. alarm | 10/07/2025 15:44:05 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYB2U6178A | FLM_EM | [8 empty] | API | 10/07/2025 15:54:31 | 10/14/2025 14:14:45 | 10/14/2025 14:18:56 | 10/14/2025 14:18:59 | 10/14/2025 15:28:13 |  |  |  | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Accept | CM20251007001051 | PCM-20251007-00001787 | TT-20251007-01801 | Telecom | Region_4 | JED0925 | JED0925 |  |  |  | Mohammed Ramadan A Abu Abid | 10/07/2025 16:39:28 | 10/12/2025 13:16:19 | 10/07/2025 22:39:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0925-G9-L8-L18-L21-NNR6-SBTS-P1-VIP @ Generator_SG | 10/07/2025 16:38:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 16:38:15 | VIP | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0925 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/07/2025 16:39:28 | 10/07/2025 16:40:26 | 10/12/2025 13:16:19 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001063 | PCM-20251007-00001803 | TT-20251007-01815 | Telecom | Region_4 | JED1M7958 | JED0958 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/07/2025 16:46:10 | 10/08/2025 18:13:25 | 10/07/2025 22:46:10 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7958-CA-L800-SBTS-P3 @ Sceco | 10/07/2025 16:41:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 16:41:28 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7958 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/07/2025 16:46:10 | 10/07/2025 16:46:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001133 | PCM-20251007-00001932 | TT-20251007-01902 | Telecom | Region_5 | MAK1M9254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/07/2025 17:41:36 | 10/08/2025 11:33:21 | 10/07/2025 23:41:36 | BASE STATION ANTENNA LINE PROBLEM at MAK1M9254-P1-SHOP-CA-L800-SBTS @ Sceco | 10/07/2025 17:15:27 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/07/2025 17:15:20 | P1 | 4G | makkah | Sceco | LTE NSA | MAK1M9254 | FLM_TE |  |  | PCM-20251007-00001896 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/07/2025 17:41:36 | 10/08/2025 11:33:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001166 | PCM-20251007-00001989 | TT-20251007-01984 | EM | Region_6 | ABBS1M8095 | ABBS2095 |  |  |  | Muhammad Naeem Taj Din | 10/07/2025 18:16:31 | 10/08/2025 14:04:02 | 10/08/2025 06:16:31 | Smoke Alarm at ABBS1M8095-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/07/2025 18:08:18 | Minor | 7103 | Smoke Alarm | 10/07/2025 18:08:08 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8095 | FLM_EM | [5 empty] | Smoke Alarm |  |  | API | 10/07/2025 18:16:31 | 10/08/2025 14:04:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251007001175 | PCM-20251007-00002005 | TT-20251007-00684 | Telecom | Region_1 | JDNR0776 | JDNR0776 |  |  |  | Tahir Mahmood Hafiz Yar | 10/07/2025 18:23:01 | 10/07/2025 18:57:35 | 10/08/2025 06:23:01 | HC for JDNR0776 | 10/07/2025 06:49:09 | Minor | 676767672 | Health Check-WO to TE FME | 10/07/2025 06:49:12 | P1 | SRAN | jubail | Generator_SG | 2G NSA | JDNR0776 | FLM_TE |  |  | PCM-20251007-00001714 | Dear FLM, Kindly check with NOC who opened PCM | Dear FLM, Kindly check with NOC who opened PCM |  |  |  | API | 10/07/2025 18:23:01 | 10/07/2025 18:57:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001186 | PCM-20251007-00002026 | TT-20251007-01920 | Reference_telecom | Region_4 | JED0028 | JED0028 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 18:30:26 | 10/07/2025 18:30:26 | 10/08/2025 00:30:26 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0028-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/07/2025 15:30:25 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/07/2025 15:30:18 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0028 | FLM_TE |  |  | PCM-20251007-00001916 | Please check RF Module filter input power missing [JED0028-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA] MRBTS-417028 EQM_R-1 APEQM_R-1 RMOD_R-7 | Please check RF Module filter input power missing [JED0028-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA] MRBTS-417028 EQM_R-1 APEQM_R-1 RMOD_R-7 |  |  |  | API | 10/07/2025 18:30:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007001190 | PCM-20251007-00002035 | TT-20251007-02005 | Telecom | Region_1 | ARM2M7763 | ARM0763 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Imran Ali Yousaf | 10/07/2025 18:31:31 | 10/07/2025 19:58:15 | 10/08/2025 00:31:31 | 1(LTE) sites down under ARM0763-P3 @ Sceco | 10/07/2025 18:23:24 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/07/2025 18:23:01 | P3 | 4G | dammam | Sceco | LTE SA | ARM0763-P3 | FLM_TE | ARM0763 | Results: DOWN SITE HUB ARM0763-P3 ARM0763 Summary: Hub: ARM0763, Down Count: 1, Down Sites: ARM0763-P3 Alarm Summary: ARM0763 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/07/2025 18:31:31 | 10/07/2025 18:58:37 | 10/07/2025 19:58:03 |  |  | 10/07/2025 19:58:15 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001199 | PCM-20251007-00002051 | TT-20251007-02036 | MW_HC | Region_1 | JBL2108 | JBL2108 |  |  |  | Tahir Mahmood Hafiz Yar | 10/07/2025 18:45:56 | 10/07/2025 18:57:35 | 10/08/2025 06:45:56 | (As per BO Request) Huawei MW HC at link JBL2108-JBL2391 | 10/07/2025 18:45:28 | Minor | 1-631 | MW_LOF | 10/07/2025 18:45:28 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBL2108-JBL2391 | FLM_TE | [5 empty] | (As per BO Request) Huawei MW HC at link JBL2108-JBL2391 |  |  | API | 10/07/2025 18:45:56 | 10/07/2025 18:57:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001207 | PCM-20251007-00002060 | TT-20251007-02047 | Reference_telecom | Region_2 | RIYB2U6178a | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/07/2025 18:55:16 | 10/08/2025 09:24:44 | 10/08/2025 00:55:16 | RF Unit VSWR Threshold Crossed at RIYB2U6178A-P3 @ Sceco | 10/07/2025 15:54:49 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/07/2025 15:54:47 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYB2U6178A | FLM_TE | [8 empty] | API | 10/07/2025 18:55:16 | 10/08/2025 09:24:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001241 | PCM-20251007-00002141 | TT-20250901-02350 | Telecom | Region_4 | KMMD9063 | KMMD9063 |  |  |  | Nazeer Mohammed | 10/07/2025 19:40:48 | 10/08/2025 13:58:20 | 10/08/2025 07:40:48 | NEC MW link KMMD9063(10.154.115.73) observing visibility down from itself | 09/01/2025 22:59:49 | Minor | 113388 | LOF | 09/01/2025 22:59:53 | P3 | Repeater | jeddah | Sceco_STB | TX NSA | KMMD9063 | FLM_TE |  | Thanks to share mail | PCM-20251007-00002101 | Thanks to share mail | Thanks to share mail |  |  |  | API | 10/07/2025 19:40:48 | 10/08/2025 13:58:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251007001242 | PCM-20251007-00002142 | TT-20250901-01726 | Reference_telecom | Region_4 | FAT0348 | FAT0348 |  |  |  | Asad Ullah Rahim Said | 10/07/2025 19:41:48 | 10/21/2025 22:55:54 | 10/08/2025 07:41:48 | NEC MW Observing LOF at FAT0348-IDU#5(10.1.175.181) | 08/28/2025 12:33:38 | Minor |  | LOF | 08/28/2025 12:33:38 | P1 | 2G | taif | Generator_DG | TX NSA | FAT0348-IDU#5(10.1.175.181) | FLM_TE |  | Thanks to share mail | PCM-20251007-00002091 | Thanks to share mail | Thanks to share mail |  |  |  | API | 10/07/2025 19:41:48 | 10/21/2025 22:36:37 | 10/21/2025 22:55:48 | 10/21/2025 22:55:52 | 10/21/2025 22:55:54 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001243 | PCM-20251007-00002143 | TT-20250902-00108 | Telecom | Region_4 | JED0349 | JED0349 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 19:42:55 | 10/07/2025 19:42:55 | 10/08/2025 07:42:55 | NEC MW link JED0349_2(10.1.168.129) observing visibility down from itself | 09/02/2025 01:04:54 | Minor | 113388 | LOF | 09/02/2025 01:04:56 | P2 | 2G | jeddah | Sceco | TX NSA | JED0349_2 | FLM_TE |  | Thanks to share mail | PCM-20251007-00002095 | Thanks to share mail | Thanks to share mail |  |  |  | API | 10/07/2025 19:42:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007001252 | PCM-20251007-00002156 | TT-20250921-02173 | Reference_telecom | Region_4 | TFBH9446 | TFBH9446 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ahmad Kamal Abdelmawla | 10/07/2025 19:54:00 | 10/16/2025 14:40:23 | 10/08/2025 07:54:00 | NEC MW Observing LOF,ODU CPU / Cable Open,LOF,Frame ID at TFBH9446-3(10.88.221.50) | 09/20/2025 10:52:04 | Minor |  | LOF | 09/20/2025 10:52:04 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9446-3(10.88.221.50) | FLM_TE |  |  | PCM-20251007-00002094 | Cleared & under observation 24H | Cleared & under observation 24H |  |  |  | API | 10/07/2025 19:54:00 | 10/07/2025 23:06:05 | 10/16/2025 14:40:08 |  |  | 10/16/2025 14:40:23 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001259 | PCM-20251007-00002169 | TT-20251007-02131 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 19:59:49 | 10/07/2025 19:59:49 | 10/08/2025 01:59:49 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/07/2025 19:59:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 19:58:51 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/07/2025 19:59:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007001263 | PCM-20251007-00002178 | TT-20251007-02082 | Telecom | Region_4 | JED0252 | JED0252 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Moustafa Mahmoud Ahmed Fathelbab | 10/07/2025 20:03:29 | 10/12/2025 15:45:13 | 10/08/2025 08:03:29 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/07/2025 19:16:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 19:16:43 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251007-00002109 | FLM Need to perform extensive HC in site for impacted Antenna port. FLM can take support from BO if required while FLM available on site. Pls check all Antenna Line. Perform Cleanup at RFM and Antenna end both. Once issue resolve close the PCM with RCA. | FLM Need to perform extensive HC in site for impacted Antenna port. FLM can take support from BO if required while FLM available on site. Pls check all Antenna Line. Perform Cleanup at RFM and Antenna end both. Once issue resolve close the PCM with RCA. |  |  |  | API | 10/07/2025 20:03:29 | 10/07/2025 23:14:50 | 10/08/2025 15:38:26 | 10/08/2025 15:38:40 | 10/08/2025 15:55:52 | 10/12/2025 15:45:13 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001285 | PCM-20251007-00002215 | TT-20251007-02169 | EM | Region_4 | JED0791 | JED0791 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/07/2025 20:29:16 | 10/08/2025 15:19:24 | 10/08/2025 08:29:16 | AIRCON 1 FAILURE at JED0791-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/07/2025 20:20:54 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 20:20:43 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0791 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 20:29:16 | 10/08/2025 15:19:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Reject_FME | CM20251007001299 | PCM-20251007-00002235 | TT-20251007-02178 | Reference_telecom | Region_6 | TFBH0887 | TFBH0887 |  |  |  | Farhan Ali Khan | 10/07/2025 20:37:49 | 10/13/2025 10:05:09 | 10/08/2025 08:37:49 | High attenuation b/w TFBH0887-BAH0005-sophia (Ref. TT-20250911-01834) | 10/07/2025 15:47:36 | Minor | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/07/2025 15:47:36 | P1 | 2G | makhwa | Sceco_STB | DWDM NSA | TFBH0887 | FLM_TE | [8 empty] | API | 10/07/2025 20:37:49 | 10/09/2025 10:08:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007001319 | PCM-20251007-00002266 | TT-20251007-02204 | Telecom | Region_4 | JED0109 | JED0109 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/07/2025 20:53:02 | 10/09/2025 06:35:59 | 10/08/2025 02:53:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/07/2025 20:52:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 20:52:11 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/07/2025 20:53:02 | 10/07/2025 21:08:25 | 10/09/2025 06:35:48 |  |  | 10/09/2025 06:35:59 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001322 | PCM-20251007-00002271 | TT-20251007-02189 | Telecom | Region_4 | JED1M8130 | JED2130 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 20:53:55 | 10/07/2025 20:53:55 | 10/08/2025 02:53:55 | BASE STATION HARDWARE PROBLEM (Ethernet link unstable) at JED1M8130-CA-L800-P3 @ Sceco | 10/07/2025 20:39:40 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/07/2025 20:39:31 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8130 | FLM_TE |  |  | PCM-20251007-00002255 | FLM need to check Ethernet link and perform HC at site. | FLM need to check Ethernet link and perform HC at site. |  |  |  | API | 10/07/2025 20:53:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001333 | PCM-20251007-00002289 | TT-20251007-02221 | Reference_telecom | Region_1 | HRBD0123 | HRBD0123 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/07/2025 21:12:09 | 10/07/2025 22:58:36 | 10/08/2025 09:12:09 | RF Unit RX Channel RTWP/RSSI Unbalanced at HRBD0123-P1-HUB_SRAN @ Generator_SG | 10/07/2025 18:12:04 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/07/2025 18:11:59 | P1 | SRAN | hafr | Generator_SG | 2G NSA | HRBD0123 | FLM_TE | [8 empty] | API | 10/07/2025 21:12:09 | 10/07/2025 22:58:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001377 | PCM-20251007-00002358 | TT-20251007-02278 | Reference_telecom | Region_4 | GMK0442 | GMK0442 |  |  |  | Riasat Ali Allah Baksh | 10/07/2025 21:54:30 | 10/08/2025 14:44:10 | 10/08/2025 09:54:30 | ReplaceableUnitMissing observed in GMK0442 towards 10.3.234.210 @ Sceco | 10/07/2025 09:54:19 | Minor |  | ReplaceableUnitMissing | 10/07/2025 09:54:02 | P2 | 2G | qunfuddah | Sceco | TX NSA | GMK0442 | FLM_TE | [8 empty] | API | 10/07/2025 21:54:30 | 10/08/2025 14:44:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001380 | PCM-20251007-00002361 | TT-20250902-00447 | Telecom | Region_4 | JED0361 | JED0361 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 21:57:35 | 10/07/2025 21:57:35 | 10/08/2025 09:57:35 | NEC MW link JED0361_2(10.1.167.241) observing visibility down from itself FSW002 (10.1.167.242) is down from hub site | 09/02/2025 04:42:33 | Minor | 113388 | LOF | 09/02/2025 04:42:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0361_2 | FLM_TE |  | Thanks to check | PCM-20251007-00002097 | Thanks to check | Thanks to check |  |  |  | API | 10/07/2025 21:57:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001384 | PCM-20251007-00002368 | TT-20250901-02345 | Telecom | Region_4 | FSW001 | FSW001 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/07/2025 22:02:57 | 10/07/2025 22:02:57 | 10/08/2025 10:02:57 | NEC MW link FSW001(10.99.254.61) observing visibility down due to hub site | 09/01/2025 22:49:45 | Minor | 113388 | LOF | 09/01/2025 22:49:48 | P3 | Shop | jeddah | Sceco | TX NSA | FSW001 | FLM_TE |  | Thanks to share email | PCM-20251007-00002100 | Thanks to share email | Thanks to share email |  |  |  | API | 10/07/2025 22:02:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001385 | PCM-20251007-00002369 | TT-20250902-00593 | Reference_telecom | Region_4 | JDMD0862 | JDMD0862 |  |  |  | Nazeer Mohammed | 10/07/2025 22:03:46 | 10/08/2025 13:58:20 | 10/08/2025 10:03:46 | NEC MW link JDMD0862-2(10.154.142.194) observing visibility down from itself JED0480 (10.154.142.195) down from JDMD0862 | 09/02/2025 05:53:29 | Minor | 113388 | LOF | 09/02/2025 05:53:32 | P2 | 2G | jeddah | Generator_DG | TX NSA | JDMD0862-2 | FLM_TE |  | Thanks to share email | PCM-20251007-00002102 | Thanks to share email | Thanks to share email |  |  |  | API | 10/07/2025 22:03:46 | 10/08/2025 13:58:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001389 | PCM-20251007-00002374 | TT-20250901-01771 | Reference_telecom | Region_4 | TFBH0840 | TFBH0840 |  |  |  | Ahmad Kamal Abdelmawla | 10/07/2025 22:04:35 | 10/07/2025 23:06:05 | 10/08/2025 10:04:35 | NEC MW Observing LOF,Frame ID at TFBH0840(10.154.143.86) | 08/27/2025 18:09:35 | Minor |  | LOF | 08/27/2025 18:09:35 | P3 | 2G | taif | Generator_SG | TX NSA | TFBH0840(10.154.143.86) | FLM_TE |  | Thanks to share email | PCM-20251007-00002092 | Thanks to share email | Thanks to share email |  |  |  | API | 10/07/2025 22:04:35 | 10/07/2025 23:06:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001401 | PCM-20251007-00002389 | TT-20251007-02257 | Reference_telecom | Region_4 | JED2125 | JED2125 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 22:12:46 | 10/07/2025 22:12:46 | 10/08/2025 10:12:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2125-CA-L800-NR2.6-SBTS -P3 @ Sceco | 10/07/2025 19:34:58 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/07/2025 19:34:51 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2125 | FLM_TE |  | Thanks to share after reroute plan | PCM-20251007-00002344 | Thanks to share after reroute plan | Thanks to share after reroute plan |  |  |  | API | 10/07/2025 22:12:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251007001410 | PCM-20251007-00002399 | TT-20250902-00467 | Telecom | Region_4 | JED0639 | JED0639 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/07/2025 22:17:55 | 10/07/2025 22:17:55 | 10/08/2025 10:17:55 | NEC MW link JED0639 (10.1.165.113) observing visibility down from itself FW057 (10.1.165.114) is down from hub site | 09/02/2025 04:59:59 | Minor | 113388 | LOF | 09/02/2025 05:00:01 | P2 | 2G | jeddah | Sceco | TX NSA | JED0639 | FLM_TE |  | Thanks to share email | PCM-20251007-00002098 | Thanks to share email | Thanks to share email |  |  |  | API | 10/07/2025 22:17:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251007001428 | PCM-20251007-00002434 | TT-20251007-02329 | Reference_telecom | Region_4 | JED1MN0832 | JED0832 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/07/2025 22:48:29 | 10/09/2025 06:36:29 | 10/08/2025 10:48:29 | Fronthaul loop back connectivity check failure at JED1MN0832-NR2.6-P2 @ Sceco | 10/07/2025 22:11:32 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/07/2025 22:11:23 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0832 | FLM_TE |  |  | PCM-20251007-00002429 | FLM need to check RFM and Fronthaul cabling at site. | FLM need to check RFM and Fronthaul cabling at site. |  |  |  | API | 10/07/2025 22:48:29 | 10/07/2025 22:56:27 | 10/09/2025 06:36:14 |  |  | 10/09/2025 06:36:29 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001440 | PCM-20251007-00002451 | TT-20251007-02340 | Telecom | Region_4 | SQSH0023 | SQSH0023 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/07/2025 23:05:23 | 10/08/2025 10:10:29 | 10/08/2025 05:05:23 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at SQSH0023-GSM-UMTS-P2-USF @ Generator_DG | 10/07/2025 22:50:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 22:50:09 | P2 | 2G | qunfuddah | Generator_DG | 5G_Cell SA | SQSH0023 | FLM_TE |  |  | PCM-20251007-00002445 | FLM need to check Rx level and perform HC at site. | FLM need to check Rx level and perform HC at site. |  |  |  | API | 10/07/2025 23:05:23 | 10/08/2025 10:10:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251007001446 | PCM-20251007-00002461 | TT-20251007-02366 | EM | Region_4 | JDUS1M7651 | JDUS0651 |  |  |  | Hamza Ahmed Aly Sawy | 10/07/2025 23:14:04 | 10/08/2025 03:33:03 | 10/08/2025 11:14:04 | RECTIFIER MODULE FAILURE at JDUS1M7651-USF-P3-L800-CA-SBTS @ Generator_SG | 10/07/2025 23:05:59 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/07/2025 23:05:49 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JDUS1M7651 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/07/2025 23:14:04 | 10/08/2025 03:33:03 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000001 | PCM-20251008-00000001 | TT-20251007-02410 | Telecom | Region_4 | TURY0826 | TURY0826 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 00:01:13 | 10/19/2025 08:38:42 | 10/08/2025 06:01:13 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/07/2025 23:46:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/07/2025 23:46:08 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251007-00002509 | FLM need to check RF Module and perform HC at site. | FLM need to check RF Module and perform HC at sit |  |  |  | API | 10/08/2025 00:01:13 | 10/08/2025 02:05:51 | 10/19/2025 08:38:34 |  |  | 10/19/2025 08:38:42 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000017 | PCM-20251008-00000028 | TT-20251007-00005 | Telecom | Region_4 | TUR0694 | TUR0694 |  |  |  | Rashid Shafique | 10/08/2025 00:15:59 | 10/08/2025 00:16:43 | 10/08/2025 06:15:59 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TUR0694-P2 @ Sceco | 10/07/2025 00:00:43 | Major | 7607 | TRX OPERATION DEGRADED | 10/07/2025 00:00:38 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TUR0694 | FLM_TE |  |  | PCM-20251007-00001884 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/08/2025 00:15:59 | 10/08/2025 00:16:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000035 | PCM-20251008-00000062 | TT-20251008-00074 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/08/2025 00:36:39 | 10/08/2025 10:11:24 | 10/08/2025 04:36:39 | Intruder Alarm - DC Floor2 at DM1MBSCH01 @ Generator_DG | 10/08/2025 00:36:01 | Critical | 65365 | Intruder Alarm - DC Floor2 | 10/08/2025 00:35:58 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/08/2025 00:36:39 | 10/08/2025 10:11:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000040 | PCM-20251008-00000071 | TT-20251008-00085 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/08/2025 00:43:23 | 10/08/2025 10:11:24 | 10/08/2025 04:43:23 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/08/2025 00:42:52 | Critical | 65334 | Door open Alarm Equipment room | 10/08/2025 00:42:50 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/08/2025 00:43:23 | 10/08/2025 10:11:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000054 | PCM-20251008-00000262 | TT-20251008-00270 | EM | Region_6 | QLW1M8354 | QLW2354 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/08/2025 00:54:30 | 10/11/2025 08:24:24 | 10/08/2025 12:54:30 | RECTIFIER MAINS POWER FAILURE at QLW1M8354-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/08/2025 00:45:30 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/08/2025 00:45:24 | P3 | 4G | Albaha | Generator_SG | LTE NSA | QLW1M8354 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/08/2025 00:54:30 | 10/11/2025 08:24:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000132 | PCM-20251008-00000413 | TT-20251008-00431 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 02:41:41 | 10/19/2025 17:44:05 | 10/08/2025 08:41:41 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/08/2025 02:40:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 02:40:29 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/08/2025 02:41:41 | 10/08/2025 14:44:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000146 | PCM-20251008-00000436 | TT-20251008-00396 | Telecom | Region_6 | JIZ0124 | JIZ0124 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/08/2025 03:04:31 | 10/08/2025 08:51:39 | 10/08/2025 07:04:31 | 6(2G) 2(3G) 5(LTE) 2(5G) sites down under JIZ0124-P2 @ Sceco | 10/08/2025 02:12:23 | Critical | 7706 | BTS O&M LINK FAILURE | 10/08/2025 02:12:18 | P2 | 2G | jizan | Sceco | 2G_3G_LTE_5G SA | JDSM0791-P1-HUB 2G_LTE,JIZ0124-P2 2G_3G_LTE_5G,JDS0798-P2 2G_LTE,JIZ0168-P3 2G_3G_5G,JDSM0794-P3-CA LTE,JDS0162-P1-CA LTE,SMT2065-P3 2G,HSM0238-P2 2G | FLM_TE | JIZ0124 | DOWN SITE HUB TX FB JDSM0791-P1-HUB 2G_LTE JDSM0791 Link flapping at HUB JDS0798-P2 2G_LTE JDS0798 visibility down at HUB, kindly check locally JDSM0794-P3-CA LTE JDSM0794 LOS to Air Scale JDS0162-P1-CA LTE JDS0162 Observing Eth loss & LAN link flapping at the hub SMT2065-P3 2G SMT2065 Observing Eth loss & LAN link flapping at the hub HSM0238-P2 2G HSM0238 LOS to Air Scale JIZ0168 JIZ0168 LOS to Air Scale JIZ0124 JIZ0124 observing no issue at HUB , kindly check locally | PCM-20251008-00000392 | DOWN SITE HUB TX FB JDSM0791-P1-HUB 2G_LTE JDSM0791 Link flapping at HUB JDS0798-P2 2G_LTE JDS0798 visibility down at HUB, kindly check locally JDSM0794-P3-CA LTE JDSM0794 LOS to Air Scale JDS0162-P1-CA LTE JDS0162 Observing Eth loss & LAN link flapping at the hub SMT2065-P3 2G SMT2065 Observing Eth loss & LAN link flapping at the hub HSM0238-P2 2G HSM0238 LOS to Air Scale JIZ0168 JIZ0168 LOS to Air Scale JIZ0124 JIZ0124 observing no issue at HUB , kindly check locally | DOWN SITE HUB TX FB JDSM0791-P1-HUB 2G_LTE JDSM0791 Link flapping at HUB JDS0798-P2 2G_LTE JDS0798 visibility down at HUB, kindly check locally JDSM0794-P3-CA LTE JDSM0794 LOS to Air Scale JDS0162-P1-CA LTE JDS0162 Observing Eth loss & LAN link flapping at the hub SMT2065-P3 2G SMT2065 Observing Eth loss & LAN link flapping at the hub HSM0238-P2 2G HSM0238 LOS to Air Scale JIZ0168 JIZ0168 LOS to Air Scale JIZ0124 JIZ0124 observing no issue at HUB , kindly check locally |  | sites down |  | API | 10/08/2025 03:04:31 | 10/08/2025 08:32:16 | 10/08/2025 08:51:13 |  |  | 10/08/2025 08:51:39 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000158 | PCM-20251008-00000478 | TT-20251008-00524 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 03:40:33 | 10/20/2025 12:32:42 | 10/08/2025 15:40:33 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/08/2025 03:32:23 | Minor | 7115 | BASE STATION INFORMATION | 10/08/2025 03:32:17 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/08/2025 03:40:33 | 10/08/2025 09:44:32 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000170 | PCM-20251008-00000507 | TT-20251008-00551 | EM | Region_6 | ARS1M7166 | ARS0166 |  |  |  | Khurram Nawaz Muhammad Akram | 10/08/2025 03:57:36 | 10/11/2025 14:47:48 | 10/08/2025 15:57:36 | AIRCON 1 FAILURE at ARS1M7166-P2-NCA-L800-SBTS @ Sceco | 10/08/2025 03:49:25 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 03:49:09 | P2 | 4G | jizan | Sceco | LTE NSA | ARS1M7166 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 03:57:36 | 10/08/2025 10:12:53 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000174 | PCM-20251008-00000513 | TT-20251008-00559 | EM | Region_6 | NJR0213 | NJR0213 |  |  |  | Habib Ahmed | 10/08/2025 04:00:42 | 10/11/2025 14:47:47 | 10/08/2025 16:00:42 | AIRCON 1 FAILURE at NJR0213-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/08/2025 03:52:54 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 03:52:29 | P2 | 2G | najran | Sceco | 2G NSA | NJR0213 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 04:00:42 | 10/08/2025 09:15:07 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251008000183 | PCM-20251008-00000537 | TT-20251008-00581 | Reference_telecom | Region_5 | MAK0118 | MAK0118 |  |  |  | Muhammad Zubair | 10/08/2025 04:11:34 | 10/09/2025 15:00:11 | 10/08/2025 08:11:34 | SCECO:: Link down b/w HAJ0091_MAK0118 (MK1). Under ASON and OLP Switching Test activity | 10/08/2025 04:10:56 | Critical | 1-12843 | OSC_LOS | 10/08/2025 04:10:43 | P1 | 2G | makkah | Sceco_STB | DWDM NSA | MAK0118 | FLM_TE | [5 empty] | 0-TO MAK0106(MK4)(1-A)-6-G2AST4-2(RM2/TM2(TO HAJ0091_HYB,TNG6WDAPXF(1-D02)-RM1/TM1))-OSC:1 |  |  | API | 10/08/2025 04:11:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000186 | PCM-20251008-00000543 | TT-20251007-02261 | Reference_telecom | Region_2 | RIY2M8185 | RIY2185 | Equipment | SFP_BTS | Replace SFP | Muhammad Naseer Muhammad Nazir | 10/08/2025 04:21:06 | 10/08/2025 07:03:02 | 10/08/2025 10:21:06 | Cell Unavailable at RIY2M8185-P2-L900-L800 (REF:TT-20251007-02248) @ Sceco | 10/07/2025 21:26:02 | Major | 29240 | Cell Unavailable | 10/07/2025 21:24:28 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M8185 | FLM_TE |  | Approved as per your TS | PCM-20251008-00000524 | Approved as per your TS | Approved as per your TS |  |  |  | API | 10/08/2025 04:21:06 | 10/08/2025 06:21:12 | 10/08/2025 06:21:33 | 10/08/2025 06:21:38 | 10/08/2025 06:45:26 | 10/08/2025 07:03:02 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000196 | PCM-20251008-00000571 | TT-20251008-00623 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/08/2025 04:52:54 | 10/08/2025 10:11:25 | 10/08/2025 08:52:54 | Intruder Alarm - DC Floor2 at DM1MBSCH01 @ Generator_DG | 10/08/2025 04:52:32 | Critical | 65365 | Intruder Alarm - DC Floor2 | 10/08/2025 04:52:28 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/08/2025 04:52:54 | 10/08/2025 10:11:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000205 | PCM-20251008-00000587 | TT-20251008-00636 | EM | Region_6 | BHS2361 | BHS2361 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/08/2025 05:15:33 | 10/08/2025 15:02:28 | 10/08/2025 11:15:33 | 1(2G/LTE) sites down under BHS2361-P3/BHS2361-P3 @ Sceco | 10/08/2025 05:07:25 | Major | 7706 | BTS O&M LINK FAILURE | 10/08/2025 05:07:21 | P3 | 2G | Baha | Sceco | 2G_LTE SA | BHS2361-P3 | FLM_EM | BHS2361 | Results: DOWN SITE HUB BHS2361-P3 BHS2361 Summary: Hub: BHS2361, Down Count: 1, Down Sites: BHS2361-P3 Alarm Summary: BHS2361 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/08/2025 05:15:33 | 10/08/2025 15:02:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000232 | PCM-20251008-00000636 | TT-20251008-00703 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/08/2025 06:24:06 | 10/17/2025 17:43:35 | 10/08/2025 18:24:06 | Cell Capability Degraded at JED6008-DCU-P3 @ Sceco | 10/07/2025 20:14:56 | Minor | 28751 | Cell Capability Degraded | 10/07/2025 20:13:22 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/08/2025 06:24:06 | 10/09/2025 14:52:43 | 10/17/2025 17:43:27 |  |  | 10/17/2025 17:43:35 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000244 | PCM-20251008-00000665 | TT-20251008-00740 | Reference_telecom | Region_6 | JEC0154 | JEC0154 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/08/2025 06:53:46 | 10/08/2025 20:42:56 | 10/08/2025 12:53:46 | TRX OPERATION DEGRADED at JEC0154-P1-VIP-HUB (Ref:TT-20251002-02122) @ Generator_SG | 10/08/2025 03:59:31 | Major | 7607 | TRX OPERATION DEGRADED | 10/08/2025 03:59:25 | VIP | 2G | baish | Generator_SG | 2G_TRX NSA | JEC0154 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/08/2025 06:53:46 | 10/08/2025 16:02:34 | 10/08/2025 20:42:39 |  |  | 10/08/2025 20:42:56 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000249 | PCM-20251008-00000671 | TT-20251008-00743 | Reference_telecom | Region_6 | JEC0287 | JEC0287 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/08/2025 06:55:43 | 10/08/2025 20:52:06 | 10/08/2025 12:55:43 | TRX OPERATION DEGRADED at JEC0287-P1-VIP (Ref:TT-20251005-01295) @ Generator_SG | 10/08/2025 03:54:50 | Major | 7607 | TRX OPERATION DEGRADED | 10/08/2025 03:54:45 | VIP | 2G | baish | Generator_SG | 2G_TRX NSA | JEC0287 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/08/2025 06:55:43 | 10/08/2025 16:02:42 | 10/08/2025 20:51:55 |  |  | 10/08/2025 20:52:06 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000251 | PCM-20251008-00000673 | TT-20251008-00744 | Reference_telecom | Region_6 | JEC0377 | JEC0377 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/08/2025 06:57:36 | 10/08/2025 20:55:00 | 10/08/2025 12:57:36 | TRX OPERATION DEGRADED at JEC0377-P1-VIP (Ref:TT-20251002-02122) @ Generator_SG | 10/08/2025 02:19:44 | Major | 7607 | TRX OPERATION DEGRADED | 10/08/2025 02:19:40 | VIP | 2G | baish | Generator_SG | 2G_TRX NSA | JEC0377 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/08/2025 06:57:36 | 10/08/2025 16:02:44 | 10/08/2025 20:54:47 |  |  | 10/08/2025 20:55:00 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000275 | PCM-20251008-00000711 | TT-20251008-00775 | Reference_telecom | Region_4 | JED6021 | JED6021 |  |  |  | Mohamed Farag Abdelbary | 10/08/2025 07:23:11 | 10/09/2025 14:52:44 | 10/08/2025 19:23:11 | DemXpicLOS observed in JED6021 towards 10.10.181.68 @ Generator_SG | 10/07/2025 19:24:14 | Minor |  | DemXpicLOS | 10/07/2025 19:22:48 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED6021 | FLM_TE | [8 empty] | API | 10/08/2025 07:23:11 | 10/09/2025 14:52:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000346 | PCM-20251008-00000853 | TT-20251008-00903 | Telecom | Region_4 | TAF1M7267 | TAF0267 |  |  |  | Rashid Shafique | 10/08/2025 08:53:44 | 10/08/2025 16:20:00 | 10/08/2025 20:53:44 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TAF1M7267-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/08/2025 08:47:23 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 08:47:11 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7267 | FLM_TE |  |  | PCM-20251008-00000847 | Kindly check the RSSI alarm active at site | Kindly check the RSSI alarm active at site |  |  |  | API | 10/08/2025 08:53:44 | 10/08/2025 16:20:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000351 | PCM-20251008-00000861 | TT-20251008-00912 | Reference_telecom | Region_6 | ABBS9710 | ABBS9710 |  |  |  | Manzoor Ahmed | 10/08/2025 09:00:17 | 10/08/2025 11:21:00 | 10/08/2025 21:00:17 | LossOfSignal observed in ABBS9710_03 towards 10.221.243.190 @ Sceco | 10/07/2025 21:01:40 | Minor |  | LossOfSignal | 10/07/2025 20:59:46 | P3 | Repeater | Albaha | Sceco | TX NSA | ABBS9710 | FLM_TE | [8 empty] | API | 10/08/2025 09:00:17 | 10/08/2025 11:21:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000371 | PCM-20251008-00000902 | TT-20251008-00941 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/08/2025 09:25:50 | 10/21/2025 18:13:37 | 10/08/2025 15:25:50 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/08/2025 09:14:42 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/08/2025 09:14:36 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251008-00000892 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/08/2025 09:25:50 | 10/20/2025 14:29:28 | 10/21/2025 18:13:31 |  |  | 10/21/2025 18:13:37 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000385 | PCM-20251008-00000924 | TT-20251008-00975 | Reference_telecom | Region_4 | JED0244 | JED0244 | Equipment | BSS_HW_Stuck | Reset RRU | Abdullah Ahmad Mohammad Abdelsheekh | 10/08/2025 09:41:33 | 10/18/2025 13:33:27 | 10/08/2025 21:41:33 | LagPortDown observed in JED0244_04 towards 10.1.224.231 @ Sceco | 10/07/2025 21:42:50 | Minor |  | LagPortDown | 10/07/2025 21:41:06 | P1 | 2G | jeddah | Sceco | TX NSA | JED0244 | FLM_TE | [8 empty] | API | 10/08/2025 09:41:33 | 10/18/2025 13:11:28 | 10/18/2025 13:12:02 | 10/18/2025 13:12:05 | 10/18/2025 13:12:08 | 10/18/2025 13:33:27 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000407 | PCM-20251008-00000954 | TT-20251008-01003 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 10:01:44 | 10/20/2025 12:32:43 | 10/08/2025 14:01:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/08/2025 10:00:50 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 10:00:43 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/08/2025 10:01:44 | 10/08/2025 10:30:09 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000419 | PCM-20251008-00000969 | TT-20251008-00711 | Telecom | Region_6 | SDA0507 | SDA0507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/08/2025 10:07:04 | 10/19/2025 17:44:46 | 10/08/2025 16:07:04 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at SDA0507-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Generator_SG | 10/08/2025 06:25:05 | Major | 7114 | CELL SERVICE PROBLEM | 10/08/2025 06:24:51 | P3 | 2G | abha | Generator_SG | 5G_Cell SA | SDA0507 | FLM_TE |  |  | PCM-20251008-00000644 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/08/2025 10:07:04 | 10/08/2025 12:55:27 | 10/08/2025 15:59:18 |  |  | 10/08/2025 15:59:27 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000433 | PCM-20251008-00000993 | TT-20251008-01023 | Telecom | Region_4 | JED0105 | JED0105 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 10:23:46 | 10/08/2025 11:29:13 | 10/08/2025 22:23:46 | BASE STATION HARDWARE PROBLEM (Nokia MN BTS SFP validation failure) at JED0105-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/08/2025 10:09:42 | Minor | 7100 | BASE STATION HARDWARE PROBLEM | 10/08/2025 10:09:49 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0105 | FLM_TE |  |  | PCM-20251008-00000982 | Kindly check the SFP issue active at site | Kindly check the SFP issue active at site |  |  |  | API | 10/08/2025 10:23:46 | 10/08/2025 11:29:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000442 | PCM-20251008-00001012 | TT-20251008-01053 | Telecom | Region_1 | ARR2U6702 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 10/08/2025 10:30:40 | 10/15/2025 11:52:44 | 10/08/2025 16:30:40 | RF Out of Service at ARR2U6702-P3 @ Sceco | 10/08/2025 10:25:49 | Major | 29248 | RF Out of Service | 10/08/2025 10:24:16 | P3 | 4G | arar | Sceco | 2G SA | ARR2U6702 | FLM_TE | [8 empty] | API | 10/08/2025 10:30:40 | 10/08/2025 12:15:07 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000456 | PCM-20251008-00001039 | TT-20251008-01020 | Telecom | Region_4 | RYMK0671 | RYMK0671 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 10:38:40 | 10/09/2025 10:07:23 | 10/08/2025 16:38:40 | MW_IS-IS Adjacency Changed at KHU0652-LL-CSG-01 to RYMK0671 | 10/08/2025 10:11:08 | Major | 15269 | LOS | 10/08/2025 10:11:08 | P1 | 2G | taif | Sceco_STB | IPRAN_NSA | MW_IS-IS Adjacency Changed at KHU0652-LL-CSG-01 to RYMK0671 | FLM_TE |  |  | PCM-20251008-00000979 | FLM to check RNRY0659-RNRY0660 | FLM to check RNRY0659-RNRY0660 |  |  |  | API | 10/08/2025 10:38:40 | 10/09/2025 10:07:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000496 | PCM-20251008-00001110 | TT-20251008-01148 | Telecom | Region_4 | HJR0041 | HJR0041 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/08/2025 11:13:01 | 10/10/2025 11:38:08 | 10/08/2025 23:13:01 | Power Supply at HJR0041-1 on 10.88.220.130 @ Sceco | 10/08/2025 11:12:05 | Minor | Power Supply | Power Supply | 10/08/2025 10:57:31 | P2 | 2G | adam | Sceco | TX NSA | HJR0041 | FLM_TE | [8 empty] | API | 10/08/2025 11:13:01 | 10/08/2025 16:01:42 | 10/10/2025 11:37:58 |  |  | 10/10/2025 11:38:08 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000507 | PCM-20251008-00001128 | TT-20251008-01052 | Telecom | Region_1 | ARR6002 | ARR6002 |  |  |  | Muhammad Zubair Guilzar | 10/08/2025 11:25:25 | 10/08/2025 12:15:08 | 10/08/2025 17:25:25 | Local Cell Capability Decline at ARR6002-P3_SRAN @ Sceco | 10/08/2025 10:26:43 | Major | 28206 | Local Cell Capability Decline | 10/08/2025 10:25:07 | P3 | SRAN | arar | Sceco | 2G NSA | ARR6002 | FLM_TE |  |  | PCM-20251008-00001011 | Many active hardware alarms on site, Please check for any issue locally. | Many active hardware alarms on site, Please check for any issue locally. |  |  |  | API | 10/08/2025 11:25:25 | 10/08/2025 12:15:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000535 | PCM-20251008-00001173 | TT-20251008-01217 | Reference_EM | Region_1 | JBL0473 | JBL0473 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Salah Abdalgadir Ahmed | 10/08/2025 11:49:43 | 10/10/2025 17:25:34 | 10/08/2025 23:49:43 | high temprature 40 at JBL0473-P2_SRAN @ Sceco | 10/08/2025 11:39:34 | Minor | 65103 | high temprature 40 | 10/08/2025 11:39:29 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0473 | FLM_EM | [8 empty] | API | 10/08/2025 11:49:43 | 10/08/2025 14:41:11 | 10/10/2025 17:25:23 |  |  | 10/10/2025 17:25:34 |  | Ahmed Salah Abdalgadir Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000547 | PCM-20251008-00001190 | TT-20251008-01207 | Reference_telecom | Region_1 | HFF2U6729 | HFF6029 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/08/2025 11:57:35 | 10/08/2025 13:10:17 | 10/08/2025 23:57:35 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6729-P3 @ Sceco | 10/08/2025 08:45:27 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/08/2025 08:45:24 | P3 | 4G | hafouf | Sceco | 2G NSA | HFF2U6729 | FLM_TE |  |  | PCM-20251008-00001167 | This either due to hardware issue or due to interference, so please follow below hardware check first then if issue still persist escalate to quality team. 1.All cable and ports for RRU, Feeder, Jumper, antenna, TMA and ALD should be check and free from any damage and properly terminated (needs to be check single or double jumper, with or without TMA). 2.Perform hardware swap such as RRU, Feeder, Jumper, antenna, TMA and ALD, and monitor status and record result in each and every action. Note: 1. Don't perform all hardware swap in just one shot in order to isolate where exactly is the fault. 3.Please share all details and findings with above actions with clear time stamp. 4. Need to check with Quality for possible interference if alarm still not cleared. | This either due to hardware issue or due to interference, so please follow below hardware check first then if issue still persist escalate to quality team. 1.All cable and ports for RRU, Feeder, Jumper, antenna, TMA and ALD should be check and free from any damage and properly terminated (needs to be check single or double jumper, with or without TMA). 2.Perform hardware swap such as RRU, Feeder, Jumper, antenna, TMA and ALD, and monitor status and record result in each and every action. Note: 1. Don't perform all hardware swap in just one shot in order to isolate where exactly is the fault. 3.Please share all details and findings with above actions with clear time stamp. 4. Need to check with Quality for possible interference if alarm still not cleared. |  |  |  | API | 10/08/2025 11:57:35 | 10/08/2025 13:10:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000560 | PCM-20251008-00001213 | TT-20251008-01259 | EM | Region_2 | RIY2699 | RIY2699 |  |  |  | Adham Adham Hassan Farghal | 10/08/2025 12:05:14 | 10/10/2025 12:36:22 | 10/09/2025 00:05:14 | Door opening alarm at RIY2699-P2_SRAN @ Sceco | 10/08/2025 12:04:45 | Minor | 65101 | Door opening alarm | 10/08/2025 12:04:42 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2699 | FLM_EM | [8 empty] | API | 10/08/2025 12:05:14 | 10/10/2025 12:36:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000586 | PCM-20251008-00001253 | TT-20251008-01287 | Telecom | Region_4 | RNRY0667 | RNRY0667 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable Connector | Asad Ullah Rahim Said | 10/08/2025 12:27:20 | 10/12/2025 14:25:25 | 10/08/2025 18:27:20 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at RNRY0667-P3 @ Sceco | 10/08/2025 12:14:53 | Major | 7607 | TRX OPERATION DEGRADED | 10/08/2025 12:14:50 | P3 | 2G | taif | Sceco | 2G_TRX NSA | RNRY0667 | FLM_TE |  |  | PCM-20251008-00001236 | VSWR alarm active at site, kindly check | VSWR alarm active at site, kindly check |  |  |  | API | 10/08/2025 12:27:20 | 10/08/2025 12:49:23 | 10/08/2025 14:27:39 | 10/08/2025 14:27:42 | 10/12/2025 13:24:46 | 10/12/2025 14:25:25 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000598 | PCM-20251008-00001274 | TT-20251008-01305 | Telecom | Region_4 | BHR0328 | BHR0328 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 12:37:49 | 10/21/2025 13:17:55 | 10/08/2025 16:37:49 | 1(2G) 1(LTE) sites down under JED0769-P1-VIP-CA-L900-L800-SBTS,BHR0328-P3/BHR0328-P3 @ Generator_SG | 10/08/2025 12:28:41 | Critical | 7706 | BTS O&M LINK FAILURE | 10/08/2025 12:28:35 | P2 | 2G | jeddah | Generator_SG | 2G_LTE SA | JED0769-P1-VIP-CA-L900-L800-SBTS LTE,BHR0328-P3 2G | FLM_TE | BHR0328 | Scattered sites: BHR0328 We are observing visibility down from our end kindly send team to check locally JED0769 observing LOS TO AIRSCALE | PCM-20251008-00001268 | Scattered sites: BHR0328 We are observing visibility down from our end kindly send team to check locally JED0769 observing LOS TO AIRSCALE | Scattered sites: BHR0328 We are observing visibility down from our end kindly send team to check locally JED0769 observing LOS TO AIRSCALE |  | sites down |  | Manual | 10/08/2025 12:37:49 | 10/21/2025 13:17:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008000632 | PCM-20251008-00001320 | TT-20251008-01365 | Reference_telecom | Region_6 | WJZ0065 | WJZ0065 |  |  |  | Muhammad Ali | 10/08/2025 13:03:09 | 10/12/2025 09:29:16 | 10/09/2025 01:03:09 | DemFail observed in WJZ0065_04 towards 10.74.121.187 @ Sceco | 10/08/2025 01:03:53 | Minor |  | DemFail | 10/08/2025 01:02:46 | P3 | 2G | jizan | Sceco | TX NSA | WJZ0065 | FLM_TE | [8 empty] | API | 10/08/2025 13:03:09 | 10/08/2025 13:05:08 | 10/12/2025 09:29:10 | 10/12/2025 09:29:14 | 10/12/2025 09:29:16 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000655 | PCM-20251008-00001355 | TT-20251008-01412 | Telecom | Region_6 | DRB1MN0404 | DRB0404 | Equipment | BSS_HW_fault | Replace RRU | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 13:22:43 | 10/12/2025 22:30:52 | 10/08/2025 19:22:43 | BASE STATION SERVICE PROBLEM (RX out of order) at DRB1MN0404-NR2.6-P2 @ Sceco | 10/08/2025 13:17:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 13:17:50 | P2 | 5G | derb | Sceco | LTE_Cell SA | DRB1MN0404 | FLM_TE | [5 empty] | RX out of order |  |  | API | 10/08/2025 13:22:43 | 10/08/2025 18:20:26 | 10/12/2025 18:41:51 | 10/12/2025 18:41:54 | 10/12/2025 19:06:53 | 10/12/2025 22:30:52 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20251008000666 | PCM-20251008-00001369 | TT-20251008-01432 | Reference_telecom | Region_4 | JED0368 | JED0368 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/08/2025 13:32:01 | 10/13/2025 15:48:59 | 10/09/2025 01:32:01 | Degrade observed in JED0368_02 towards 10.21.74.147 @ Generator_SG | 10/08/2025 01:33:45 | Minor |  | Degrade | 10/08/2025 01:31:39 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0368 | FLM_TE | [8 empty] | API | 10/08/2025 13:32:01 | 10/13/2025 15:44:44 | 10/13/2025 15:48:56 | 10/13/2025 15:48:59 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000701 | PCM-20251008-00001414 | TT-20251008-01466 | Reference_telecom | Region_4 | SDY1M3163 | SDY0163 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 13:48:35 | 10/12/2025 09:50:38 | 10/08/2025 19:48:35 | 1(3G) site down under SDY1M3163-P3 | 10/08/2025 11:21:48 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/08/2025 11:21:48 | P3 | 3G | alaith | Generator_SG | 3G SA | SDY1M3163-P3 | FLM_TE | SDY1M3163 | Results: DOWN SITE HUB SDY1M3163-P3 SDY1M3163 Summary: Hub: SDY1M3163, Down Count: 1, Down Sites: SDY1M3163-P3 Alarm Summary: SDY1M3163 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/08/2025 13:48:35 | 10/08/2025 14:44:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000761 | PCM-20251008-00001510 | TT-20251008-01554 | Telecom | Region_1 | HMBY2429 | HMBY2429 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Imran Ali Yousaf | 10/08/2025 14:34:22 | 10/08/2025 23:15:38 | 10/08/2025 18:34:22 | 1(2G) 4(3G) 5(LTE) sites down under HF1RNCH01 @ Sceco | 10/08/2025 14:23:09 | Critical | 22214 | NodeB Unavailable | 10/08/2025 14:23:06 | VIP | SRAN | dammam | Generator_SG | 3G_LTE SA | QRH2431-P1-VIP 3G_LTE,HMBY2429-P1-VIP_SRAN LTE,UQR2313-P3 3G_LTE,UQSW2730-P3_SRAN LTE,QRH2432-P1-VIP 3G,QRH2430-P1-VIP 3G | FLM_TE | HMBY2429 | Dear Team, We are observing MW_BER_SD alarms and HU issue at MW LINK HMBY2429 DIR HMBY2428 | PCM-20251008-00001507 | Dear Team, We are observing MW_BER_SD alarms and HU issue at MW LINK HMBY2429 DIR HMBY2428 | Dear Team, We are observing MW_BER_SD alarms and HU issue at MW LINK HMBY2429 DIR HMBY2428 |  | sites down |  | API | 10/08/2025 14:34:22 | 10/08/2025 16:40:05 | 10/08/2025 23:15:24 |  |  | 10/08/2025 23:15:38 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000783 | PCM-20251008-00001558 | TT-20251008-01614 | Telecom | Region_4 | TAF2405 | TAF2405 | Equipment | BSS_HW_fault | Replace Antenna | Asad Ullah Rahim Said | 10/08/2025 14:51:35 | 10/20/2025 16:25:54 | 10/09/2025 02:51:35 | BASE STATION INFORMATION (No module fan detected) at TAF2405-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/08/2025 14:43:13 | Minor | 7115 | BASE STATION INFORMATION | 10/08/2025 14:43:08 | P2 | 2G | taif | Sceco | 2G NSA | TAF2405 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/08/2025 14:51:35 | 10/20/2025 15:07:50 | 10/20/2025 15:20:54 | 10/20/2025 15:20:59 | 10/20/2025 15:21:11 | 10/20/2025 16:25:54 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000790 | PCM-20251008-00001568 | TT-20251008-01620 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/08/2025 14:53:38 | 10/08/2025 16:21:16 | 10/09/2025 02:53:38 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/08/2025 14:45:36 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 14:45:26 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 14:53:38 | 10/08/2025 16:21:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008000830 | PCM-20251008-00001633 | TT-20251008-01678 | Telecom | Region_5 | MAK6108 | MAK6108 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:17:47 | 10/16/2025 11:25:42 | 10/08/2025 21:17:47 | HC:: Multiple Alarms Active at Site MAK6108 ¦ FLM Need To Check | 10/08/2025 15:17:31 | Major |  | Health Check-WO to TE FME | 10/08/2025 15:17:31 | VIP | 2G | makkah | Sceco | IBS SA | MAK6108 | FLM_TE | [8 empty] | API | 10/08/2025 15:17:47 | 10/16/2025 11:25:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000831 | PCM-20251008-00001634 | TT-20251008-01679 | Telecom | Region_5 | MAK6030 | MAK6030 |  |  |  | Mosab Nasr eldeen Mohamed | 10/08/2025 15:17:48 | 10/09/2025 19:37:44 | 10/08/2025 21:17:48 | HC:: Multiple Alarms Active at Site MAK6030 ¦ FLM Need To Check | 10/08/2025 15:17:31 | Major |  | Health Check-WO to TE FME | 10/08/2025 15:17:31 | P3 | 2G | makkah | Sceco | IBS SA | MAK6030 | FLM_TE | [8 empty] | API | 10/08/2025 15:17:48 | 10/09/2025 19:37:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000832 | PCM-20251008-00001635 | TT-20251008-01680 | Telecom | Region_5 | MAK6091 | MAK6091 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:17:49 | 10/16/2025 11:25:43 | 10/08/2025 21:17:49 | HC:: Multiple Alarms Active at Site MAK6091 ¦ FLM Need To Check | 10/08/2025 15:17:31 | Major |  | Health Check-WO to TE FME | 10/08/2025 15:17:31 | P3 | 2G | makkah | Sceco | IBS SA | MAK6091 | FLM_TE | [8 empty] | API | 10/08/2025 15:17:49 | 10/16/2025 11:25:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000833 | PCM-20251008-00001636 | TT-20251008-01681 | Telecom | Region_5 | MAK6028 | MAK6028 |  |  |  | Mosab Nasr eldeen Mohamed | 10/08/2025 15:17:50 | 10/09/2025 19:37:44 | 10/08/2025 21:17:50 | HC:: Multiple Alarms Active at Site MAK6028 ¦ FLM Need To Check | 10/08/2025 15:17:31 | Major |  | Health Check-WO to TE FME | 10/08/2025 15:17:31 | P3 | 2G | makkah | Sceco | IBS SA | MAK6028 | FLM_TE | [8 empty] | API | 10/08/2025 15:17:50 | 10/09/2025 19:37:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000834 | PCM-20251008-00001637 | TT-20251008-01682 | Telecom | Region_5 | MAK6094 | MAK6094 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:17:51 | 10/16/2025 11:25:43 | 10/08/2025 21:17:51 | HC:: Multiple Alarms Active at Site MAK6094 ¦ FLM Need To Check | 10/08/2025 15:17:31 | Major |  | Health Check-WO to TE FME | 10/08/2025 15:17:31 | VIP | 2G | makkah | Sceco | IBS SA | MAK6094 | FLM_TE | [8 empty] | API | 10/08/2025 15:17:51 | 10/16/2025 11:25:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000844 | PCM-20251008-00001649 | TT-20251008-01693 | Telecom | Region_1 | DRN0134 | DRN0134 |  |  |  | Imran Ali Yousaf | 10/08/2025 15:20:54 | 10/22/2025 11:33:35 | 10/09/2025 03:20:54 | MW RTN Observing RADIO_RSL_LOW,MW_LOF at DRN0134_NE_14_V | 10/14/2025 14:28:50 | Minor |  | LOF | 10/14/2025 14:28:50 | P1 | SRAN | dammam | Sceco | TX NSA | DRN0134_NE_14_V | FLM_TE | [8 empty] | API | 10/08/2025 15:20:54 | 10/08/2025 16:40:08 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000845 | PCM-20251008-00001650 | TT-20251008-01694 | Telecom | Region_1 | DRN0134 | DRN0134 |  |  |  | Imran Ali Yousaf | 10/08/2025 15:20:55 | 10/22/2025 11:33:36 | 10/09/2025 03:20:55 | MW RTN Observing RADIO_RSL_LOW,RADIO_RSL_LOW,PLA_MEMBER_DOWN_EXT,PL at DRN0134_NE_16_SDB | 10/14/2025 14:28:49 | Minor |  | LOF | 10/14/2025 14:28:49 | P1 | SRAN | dammam | Sceco | TX NSA | DRN0134_NE_16_SDB | FLM_TE | [8 empty] | API | 10/08/2025 15:20:55 | 10/08/2025 16:40:09 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000848 | PCM-20251008-00001653 | TT-20251008-01697 | Reference_telecom | Region_1 | HFF2362 | HFF2362 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/08/2025 15:20:58 | 10/08/2025 21:10:21 | 10/09/2025 03:20:58 | MW RTN Observing BD_STATUS at HFF2362_NE_1_V | 07/16/2025 16:23:58 | Minor |  | LOF | 07/16/2025 16:23:58 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF2362_NE_1_V | FLM_TE | [8 empty] | API | 10/08/2025 15:20:58 | 10/08/2025 21:10:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000849 | PCM-20251008-00001654 | TT-20251008-01698 | Reference_telecom | Region_1 | HFF2362 | HFF2362 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/08/2025 15:21:00 | 10/08/2025 21:10:21 | 10/09/2025 03:21:00 | MW RTN Observing HARD_BAD at HFF2362_NE_2_H | 07/04/2025 04:23:07 | Minor |  | LOF | 07/04/2025 04:23:07 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF2362_NE_2_H | FLM_TE | [8 empty] | API | 10/08/2025 15:21:00 | 10/08/2025 21:10:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000875 | PCM-20251008-00001680 | TT-20251008-01729 | Reference_telecom | Region_2 | RIY2920 | RIY2920 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Khan zeb Shah nawaz | 10/08/2025 15:21:35 | 10/23/2025 13:51:35 | 10/09/2025 03:21:35 | MW RTN Observing ETH_LOS,NB_UNREACHABLE at RIY2920_NE_2_H | 07/17/2025 17:05:55 | Minor |  | LOF | 07/17/2025 17:05:55 | P3 | SRAN | riyadh | Sceco | TX NSA | RIY2920_NE_2_H | FLM_TE | [8 empty] | API | 10/08/2025 15:21:35 | 10/08/2025 16:44:58 | 10/23/2025 12:01:35 | 10/23/2025 12:01:37 | 10/23/2025 12:44:12 | 10/23/2025 13:51:35 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000885 | PCM-20251008-00001690 | TT-20251008-01742 | MW_HC | Region_2 | RYQS2575 | RYQS2575 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/08/2025 15:21:51 | 10/16/2025 20:18:03 | 10/09/2025 03:21:51 | Huawei MW HC_P2 Observing Errors at RYQS2575-RYQS2015 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | rumah | Generator_SG | TX NSA | RYQS2575-RYQS2015 | FLM_TE | [8 empty] | API | 10/08/2025 15:21:51 | 10/09/2025 14:31:43 | 10/16/2025 20:17:54 |  |  | 10/16/2025 20:18:03 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000890 | PCM-20251008-00001695 | TT-20251008-01749 | MW_HC | Region_2 | RIY0208 | RIY0208 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Waseem Shahzad Ghulam Rasool | 10/08/2025 15:21:59 | 10/12/2025 10:44:41 | 10/09/2025 03:21:59 | Huawei MW HC_P2 Observing Errors at RIY0208-RIY2474 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0208-RIY2474 | FLM_TE | [8 empty] | API | 10/08/2025 15:21:59 | 10/11/2025 12:41:38 | 10/12/2025 10:44:09 |  |  | 10/12/2025 10:44:41 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000893 | PCM-20251008-00001698 | TT-20251008-01753 | MW_HC | Region_2 | RIY0015 | RIY0015 |  |  |  | Khan zeb Shah nawaz | 10/08/2025 15:22:03 | 10/08/2025 16:44:58 | 10/09/2025 03:22:03 | Huawei MW HC_P2 Observing Errors at RIY0015-RIY0034 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0015-RIY0034 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:03 | 10/08/2025 16:44:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000895 | PCM-20251008-00001700 | TT-20251008-01755 | MW_HC | Region_3 | MDYB0309 | MDYB0309 |  |  |  | Muhammad Sajjad R3 | 10/08/2025 15:22:05 | 10/09/2025 10:58:49 | 10/09/2025 03:22:05 | Huawei MW HC_P2 Observing Errors at MDYB0309-MDYB0503 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | yanbu | Sceco | TX NSA | MDYB0309-MDYB0503 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:05 | 10/09/2025 10:58:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000898 | PCM-20251008-00001703 | TT-20251008-01758 | MW_HC | Region_5 | MAK0115 | MAK0115 | Equipment | BSS_HW_fault | Replace BBU | KAMRAN AAMIR | 10/08/2025 15:22:09 | 10/19/2025 12:54:10 | 10/09/2025 03:22:09 | Huawei MW HC_P2 Observing Errors at MAK0115-HAJ0214 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | 2G | makkah | Sceco | TX NSA | MAK0115-HAJ0214 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:09 |  | 10/19/2025 09:53:56 | 10/19/2025 09:54:01 | 10/19/2025 10:20:11 | 10/19/2025 12:54:10 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000899 | PCM-20251008-00001704 | TT-20251008-01759 | MW_HC | Region_1 | JBL2385 | JBL2385 |  |  |  | Tahir Mahmood Hafiz Yar | 10/08/2025 15:22:10 | 10/08/2025 15:33:04 | 10/09/2025 03:22:10 | Huawei MW HC_P2 Observing Errors at JBL2385-JBL0435 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | jubail | Sceco | TX NSA | JBL2385-JBL0435 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:10 | 10/08/2025 15:33:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000901 | PCM-20251008-00001706 | TT-20251008-01762 | MW_HC | Region_1 | JBL0557 | JBL0557 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Tahir Mahmood Hafiz Yar | 10/08/2025 15:22:14 | 10/22/2025 17:41:18 | 10/09/2025 03:22:14 | Huawei MW HC_P2 Observing Errors at JBL0557-JBL0549 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | SRAN | jubail | Power Cube | TX NSA | JBL0557-JBL0549 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:14 | 10/08/2025 15:33:04 | 10/22/2025 14:18:18 | 10/22/2025 14:18:21 | 10/22/2025 15:23:35 | 10/22/2025 17:41:18 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000906 | PCM-20251008-00001711 | TT-20251008-01768 | MW_HC | Region_1 | HFF0839 | HFF0839 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Shakeel Ahmad Ghulam Murtaza | 10/08/2025 15:22:20 | 10/12/2025 15:29:20 | 10/09/2025 03:22:20 | Huawei MW HC_P2 Observing Errors at HFF0839-HFF0821 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | hafouf | Power Cube | TX NSA | HFF0839-HFF0821 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:20 | 10/08/2025 21:10:22 | 10/12/2025 13:49:31 | 10/12/2025 14:19:10 | 10/12/2025 14:35:26 | 10/12/2025 15:29:20 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000909 | PCM-20251008-00001714 | TT-20251008-01771 | MW_HC | Region_5 | HAJ9903 | HAJ9903 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/08/2025 15:22:23 | 10/24/2025 01:40:08 | 10/09/2025 03:22:23 | Huawei MW HC_P1 Observing Modem Down at HAJ9903-HAJ9902 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | Repeater | makkah | Generator_DG | TX NSA | HAJ9903-HAJ9902 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:23 | 10/24/2025 01:40:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008000910 | PCM-20251008-00001715 | TT-20251008-01772 | MW_HC | Region_5 | HAJ6019 | HAJ6019 |  |  |  | Ahmed Mohamed Soliman Mohamed | 10/08/2025 15:22:24 | 10/08/2025 15:22:24 | 10/09/2025 03:22:24 | Huawei MW HC_P2 Observing Modem Down at HAJ6019-HAJ9903 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ6019-HAJ9903 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000911 | PCM-20251008-00001716 | TT-20251008-01773 | MW_HC | Region_5 | HAJ2921 | HAJ2921 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:25 | 10/08/2025 22:14:44 | 10/09/2025 03:22:25 | Huawei MW HC_P2 Observing Modem Down at HAJ2921-HAJ9903 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Generator_SG | TX NSA | HAJ2921-HAJ9903 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:25 | 10/08/2025 22:14:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000912 | PCM-20251008-00001717 | TT-20251008-01774 | MW_HC | Region_5 | HAJ0332 | HAJ0332 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:26 | 10/08/2025 22:14:44 | 10/09/2025 03:22:26 | Huawei MW HC_P2 Observing Errors at HAJ0332-HAJ0010 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0332-HAJ0010 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:26 | 10/08/2025 22:14:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000913 | PCM-20251008-00001718 | TT-20251008-01775 | MW_HC | Region_5 | HAJ0331 | HAJ0331 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:27 | 10/08/2025 22:14:45 | 10/09/2025 03:22:27 | Huawei MW HC_P2 Observing Errors at HAJ0331-HAJ0362 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0331-HAJ0362 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:27 | 10/08/2025 22:14:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008000914 | PCM-20251008-00001719 | TT-20251008-01776 | MW_HC | Region_5 | HAJ0271 | HAJ0271 |  |  |  | Hassan Ezzelarab Ali Mohamed | 10/08/2025 15:22:28 | 10/08/2025 15:22:28 | 10/09/2025 03:22:28 | Huawei MW HC_P2 Observing Errors at HAJ0271-HAJ0287 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0271-HAJ0287 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000915 | PCM-20251008-00001720 | TT-20251008-01777 | MW_HC | Region_5 | HAJ0235 | HAJ0235 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:29 | 10/08/2025 22:14:46 | 10/09/2025 03:22:29 | Huawei MW HC_P2 Observing Errors at HAJ0235-MAK2063 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0235-MAK2063 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:29 | 10/08/2025 22:14:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000916 | PCM-20251008-00001721 | TT-20251008-01778 | MW_HC | Region_5 | HAJ0226 | HAJ0226 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:31 | 10/08/2025 22:14:46 | 10/09/2025 03:22:31 | Huawei MW HC_P2 Observing Errors at HAJ0226-HAJ0332 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0226-HAJ0332 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:31 | 10/08/2025 22:14:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000917 | PCM-20251008-00001722 | TT-20251008-01780 | MW_HC | Region_5 | HAJ0123 | HAJ0123 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:31 | 10/08/2025 22:14:47 | 10/09/2025 03:22:31 | Huawei MW HC_P2 Observing Errors at HAJ0226-HAJ0123 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0226-HAJ0123 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:31 | 10/08/2025 22:14:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000918 | PCM-20251008-00001723 | TT-20251008-01781 | MW_HC | Region_5 | HAJ0141 | HAJ0141 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:33 | 10/08/2025 22:14:48 | 10/09/2025 03:22:33 | Huawei MW HC_P2 Observing Errors at HAJ0141-HAJ0078 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0141-HAJ0078 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:33 | 10/08/2025 22:14:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000919 | PCM-20251008-00001724 | TT-20251008-01782 | MW_HC | Region_5 | HAJ0140 | HAJ0140 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/08/2025 15:22:33 | 10/24/2025 01:40:09 | 10/09/2025 03:22:33 | Huawei MW HC_P2 Observing Errors at HAJ0140-HAJ0136 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | SRAN | makkah | Sceco | TX NSA | HAJ0140-HAJ0136 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:33 | 10/24/2025 01:40:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000920 | PCM-20251008-00001725 | TT-20251008-01783 | MW_HC | Region_5 | HAJ0127 | HAJ0127 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:22:35 | 10/08/2025 22:14:49 | 10/09/2025 03:22:35 | Huawei MW HC_P2 Observing Errors at HAJ0127-HAJ0136 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0127-HAJ0136 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:35 | 10/08/2025 22:14:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008000921 | PCM-20251008-00001726 | TT-20251008-01784 | MW_HC | Region_5 | HAJ0012 | HAJ0012 |  |  |  | Hyder Ali Muhammad Sabir | 10/08/2025 15:22:36 | 10/08/2025 15:22:36 | 10/09/2025 03:22:36 | Huawei MW HC_P2 Observing Errors at HAJ0012-HAJ0140 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0012-HAJ0140 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000923 | PCM-20251008-00001728 | TT-20251008-01787 | MW_HC | Region_1 | DMH0605 | DMH0605 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Ahsan Ul Haq Amtiaz Ali | 10/08/2025 15:22:38 | 10/11/2025 00:47:45 | 10/09/2025 03:22:38 | Huawei MW HC_P2 Observing Errors at DMH0605-QMAP0226 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | hafr | Sceco | TX NSA | DMH0605-QMAP0226 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:38 | 10/10/2025 22:47:31 | 10/10/2025 22:47:35 | 10/10/2025 22:48:35 | 10/10/2025 23:17:40 | 10/11/2025 00:47:45 |  | Ahsan Ul Haq Amtiaz Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000926 | PCM-20251008-00001731 | TT-20251008-01791 | MW_HC | Region_2 | BUR0214 | BUR0214 |  |  |  | Muhammad Mohsin Raza | 10/08/2025 15:22:42 | 10/08/2025 15:34:12 | 10/09/2025 03:22:42 | Huawei MW HC_P2 Observing Errors at BUR0214-BUR0028 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | buraidah | Sceco | TX NSA | BUR0214-BUR0028 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:42 | 10/08/2025 15:34:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000928 | PCM-20251008-00001733 | TT-20251008-01794 | MW_HC | Region_2 | BUR0021 | BUR0021 | Transsmission | SFP_Transmission | Reset SFP | Raise Ahmed Nisar Ahmed | 10/08/2025 15:22:45 | 10/18/2025 18:13:49 | 10/09/2025 03:22:45 | Huawei MW HC_P2 Observing Errors at BUR0021-BUR0241 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | SRAN | buraidah | Sceco | TX NSA | BUR0021-BUR0241 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:45 | 10/15/2025 17:32:13 | 10/16/2025 15:04:45 | 10/18/2025 16:21:23 | 10/18/2025 16:52:00 | 10/18/2025 18:13:49 |  | Raise Ahmed Nisar Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000933 | PCM-20251008-00001738 | TT-20251008-01799 | Reference_telecom | Region_6 | ABH0015 | ABH0015 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/08/2025 15:22:51 | 10/08/2025 15:58:38 | 10/09/2025 03:22:51 | Nokia Eband Observing LagPortDown-Port 4/1,DemFail-Channel 1A at ABH0015-10.3.86.218 | 09/23/2025 19:00:40 | Minor |  | LOF | 09/23/2025 19:00:40 | VIP | 2G | abha | Sceco | TX NSA | ABH0015-10.3.86.218 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:51 | 10/08/2025 15:58:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251008000938 | PCM-20251008-00001743 | TT-20251008-01804 | Reference_telecom | Region_6 | ARF0695 | ARF0695 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/08/2025 15:22:57 | 10/09/2025 01:33:35 | 10/09/2025 03:22:57 | Nokia Eband Observing SecondaryBatteryFail-ARF0695 at ARF0695-10.74.122.38 | 10/01/2025 03:24:19 | Minor |  | LOF | 10/01/2025 03:24:19 | P2 | 2G | khamis mushyet | Sceco | TX NSA | ARF0695-10.74.122.38 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:57 | 10/08/2025 20:27:53 | 10/09/2025 01:33:28 | 10/09/2025 01:33:35 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000940 | PCM-20251008-00001745 | TT-20251008-01806 | Reference_telecom | Region_6 | BCH2213 | BCH2213 |  |  |  | SHAH KHALID | 10/08/2025 15:22:59 | 10/08/2025 15:28:11 | 10/09/2025 03:22:59 | Nokia Eband Observing DemFail-Channel 1A,DemFail-Channel 1B at BCH2213_01-10.221.244.189 | 10/03/2025 20:22:48 | Minor |  | LOF | 10/03/2025 20:22:48 | P3 | 2G | Baha | Generator_SG | TX NSA | BCH2213_01-10.221.244.189 | FLM_TE | [8 empty] | API | 10/08/2025 15:22:59 | 10/08/2025 15:28:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000947 | PCM-20251008-00001752 | TT-20251008-01814 | Reference_telecom | Region_6 | BHMF0859 | BHMF0859 |  |  |  | SHAH KHALID | 10/08/2025 15:23:06 | 10/08/2025 15:28:13 | 10/09/2025 03:23:06 | Nokia Eband Observing LagPortDown-Port 7/3,DemFail-Channel 1A,DemFail-Ch at BHMF0859_01-10.221.244.84 | 09/02/2025 20:26:28 | Minor |  | LOF | 09/02/2025 20:26:28 | P3 | 2G | makhwa | Sceco | TX NSA | BHMF0859_01-10.221.244.84 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:06 | 10/08/2025 15:28:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000953 | PCM-20251008-00001758 | TT-20251008-01819 | Reference_telecom | Region_5 | EKA0634 | EKA0634 | Transsmission | SFP_Transmission | Reset SFP | Israr Ahmed Muhammad Ghauri | 10/08/2025 15:23:12 | 10/10/2025 22:03:59 | 10/09/2025 03:23:12 | Nokia Eband Observing DemFail-Channel 1A at EKA0634_4-10.221.241.130 | 09/23/2025 17:05:15 | Minor |  | LOF | 09/23/2025 17:05:15 | P2 | 2G | makkah | Sceco | TX NSA | EKA0634_4-10.221.241.130 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:12 | 10/10/2025 20:54:07 | 10/10/2025 21:00:57 | 10/10/2025 21:01:03 | 10/10/2025 21:11:59 | 10/10/2025 22:03:59 |  | Israr Ahmed Muhammad Ghauri |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000956 | PCM-20251008-00001761 | TT-20251008-01822 | Reference_telecom | Region_4 | JDMD0753 | JDMD0753 |  |  |  | Nazeer Mohammed | 10/08/2025 15:23:16 | 10/09/2025 13:22:08 | 10/09/2025 03:23:16 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at JDMD0753-10.3.231.226 | 09/28/2025 16:45:26 | Minor |  | LOF | 09/28/2025 16:45:26 | P2 | 2G | jeddah | Sceco | TX NSA | JDMD0753-10.3.231.226 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:16 | 10/09/2025 13:22:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000962 | PCM-20251008-00001767 | TT-20251008-01828 | Reference_telecom | Region_4 | JED0117 | JED0117 | Transsmission | CB_MW | Switch on CB on Rectifier | MALIK ATIF ZAMAN | 10/08/2025 15:23:24 | 10/12/2025 17:08:09 | 10/09/2025 03:23:24 | Nokia Eband Observing SecondaryBatteryFail-JED0117_02,DemFail-Channel 1B at JED0117_02-10.3.233.225 | 06/10/2025 22:03:27 | Minor |  | LOF | 06/10/2025 22:03:27 | VIP | 2G | jeddah | Sceco | TX NSA | JED0117_02-10.3.233.225 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:24 | 10/08/2025 16:08:59 | 10/08/2025 18:20:27 | 10/12/2025 15:41:02 | 10/12/2025 16:25:23 | 10/12/2025 17:08:09 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000972 | PCM-20251008-00001777 | TT-20251008-01839 | Reference_telecom | Region_4 | JED0686 | JED0686 |  |  |  | Mohammed Ramadan A Abu Abid | 10/08/2025 15:23:37 | 10/08/2025 17:11:43 | 10/09/2025 03:23:37 | Nokia Eband Observing LagPortDown-Port 4/5,Degrade-LAG 2,DemFail-Port 4/ at JED0686_03-10.10.181.70 | 09/12/2025 21:38:39 | Minor |  | LOF | 09/12/2025 21:38:39 | P2 | 2G | jeddah | Sceco | TX NSA | JED0686_03-10.10.181.70 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:37 | 10/08/2025 17:11:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008000975 | PCM-20251008-00001780 | TT-20251008-01842 | Reference_telecom | Region_4 | JED0813 | JED0813 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/08/2025 15:23:40 | 10/11/2025 17:28:38 | 10/09/2025 03:23:40 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at JED0813-02-10.10.148.103 | 10/05/2025 17:46:15 | Minor |  | LOF | 10/05/2025 17:46:15 | P2 | 2G | jeddah | Sceco | TX NSA | JED0813-02-10.10.148.103 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:40 | 10/11/2025 17:28:28 | 10/11/2025 17:28:32 | 10/11/2025 17:28:34 | 10/11/2025 17:28:38 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008000980 | PCM-20251008-00001785 | TT-20251008-01847 | Reference_telecom | Region_4 | JED2016 | JED2016 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:23:46 | 10/08/2025 15:23:46 | 10/09/2025 03:23:46 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at JED2016-10.1.235.210 | 09/16/2025 16:38:28 | Minor |  | LOF | 09/16/2025 16:38:28 | P3 | 2G | jeddah | Sceco | TX NSA | JED2016-10.1.235.210 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000983 | PCM-20251008-00001788 | TT-20251008-01850 | Reference_telecom | Region_6 | JIZ0005 | JIZ0005 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:23:49 | 10/08/2025 15:33:20 | 10/09/2025 03:23:49 | Nokia Eband Observing DemFail-Port 4/5,LagPortDown-Port 4/5,Degrade-LAG at JIZ0005_05-10.10.154.97 | 09/26/2025 02:38:02 | Minor |  | LOF | 09/26/2025 02:38:02 | VIP | 2G | jizan | Sceco | TX NSA | JIZ0005_05-10.10.154.97 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:49 | 10/08/2025 15:33:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000984 | PCM-20251008-00001789 | TT-20251008-01851 | Reference_telecom | Region_6 | JIZ0011 | JIZ0011 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:23:50 | 10/08/2025 15:33:21 | 10/09/2025 03:23:50 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.21. at JIZ0011-Single Box-10.21.71.34 | 08/30/2025 11:31:47 | Minor |  | LOF | 08/30/2025 11:31:47 | P1 | 2G | jizan | Sceco | TX NSA | JIZ0011-Single Box-10.21.71.34 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:50 | 10/08/2025 15:33:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000985 | PCM-20251008-00001790 | TT-20251008-01852 | Reference_telecom | Region_6 | JIZ0025 | JIZ0025 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:23:51 | 10/08/2025 15:33:21 | 10/09/2025 03:23:51 | Nokia Eband Observing DemFail-Port 1/1 at JIZ0025_09-10.3.86.50 | 09/16/2025 03:38:31 | Minor |  | LOF | 09/16/2025 03:38:31 | VIP | 2G | jizan | Sceco | TX NSA | JIZ0025_09-10.3.86.50 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:51 | 10/08/2025 15:33:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000986 | PCM-20251008-00001791 | TT-20251008-01853 | Reference_telecom | Region_6 | JIZ0089 | JIZ0089 |  |  |  | Osama Hadi | 10/08/2025 15:23:52 | 10/08/2025 16:03:17 | 10/09/2025 03:23:52 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JIZ0089_01-10.10.157.18 | 09/30/2025 08:56:27 | Minor |  | LOF | 09/30/2025 08:56:27 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0089_01-10.10.157.18 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:52 | 10/08/2025 16:03:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000987 | PCM-20251008-00001792 | TT-20251008-01854 | Reference_telecom | Region_6 | JIZ0156 | JIZ0156 | Transsmission | MW_HW_fault | Replace Control Card | Mohammed Sideag Mohammed Ali | 10/08/2025 15:23:54 | 10/22/2025 18:17:19 | 10/09/2025 03:23:54 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JIZ0156-1-Single BOX-10.10.157.162 | 09/17/2025 18:56:07 | Minor |  | LOF | 09/17/2025 18:56:07 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0156-1-Single BOX-10.10.157.162 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:54 | 10/08/2025 15:33:22 | 10/22/2025 18:16:25 |  |  | 10/22/2025 18:17:19 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000988 | PCM-20251008-00001793 | TT-20251008-01855 | Reference_telecom | Region_6 | JIZ0226 | JIZ0226 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:23:55 | 10/08/2025 15:33:22 | 10/09/2025 03:23:55 | Nokia Eband Observing DemFail-Channel 1A at JIZ0226_01-10.21.71.18 | 10/05/2025 02:08:02 | Minor |  | LOF | 10/05/2025 02:08:02 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0226_01-10.21.71.18 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:55 | 10/08/2025 15:33:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000989 | PCM-20251008-00001794 | TT-20251008-01856 | Reference_telecom | Region_6 | JIZ0279 | JIZ0279 |  |  |  | Osama Hadi | 10/08/2025 15:23:56 | 10/08/2025 16:03:17 | 10/09/2025 03:23:56 | Nokia Eband Observing DemFail-Port 1/1 at JIZ0279-10.3.86.178 | 07/23/2025 18:33:31 | Minor |  | LOF | 07/23/2025 18:33:31 | P2 | 2G | jizan | Generator_SG | TX NSA | JIZ0279-10.3.86.178 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:56 | 10/08/2025 16:03:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000990 | PCM-20251008-00001795 | TT-20251008-01857 | Reference_telecom | Region_6 | JIZ0296 | JIZ0296 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:23:57 | 10/08/2025 15:33:23 | 10/09/2025 03:23:57 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JIZ0296-10.10.157.35 | 10/05/2025 17:28:58 | Minor |  | LOF | 10/05/2025 17:28:58 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0296-10.10.157.35 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:57 | 10/08/2025 15:33:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000991 | PCM-20251008-00001796 | TT-20251008-01858 | Reference_telecom | Region_5 | JUM0324 | JUM0324 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/08/2025 15:23:57 | 10/21/2025 19:56:51 | 10/09/2025 03:23:57 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at JUM0324-10.221.241.101 | 10/01/2025 14:21:07 | Minor |  | LOF | 10/01/2025 14:21:07 | P2 | 2G | makkah | Sceco | TX NSA | JUM0324-10.221.241.101 | FLM_TE | [8 empty] | API | 10/08/2025 15:23:57 | 10/21/2025 19:56:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008000993 | PCM-20251008-00001798 | TT-20251008-01860 | Reference_telecom | Region_4 | JZMA9072 | JZMA9072 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:24:00 | 10/08/2025 16:02:44 | 10/09/2025 03:24:00 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A at JZMA9072_02-10.74.120.87 | 09/07/2025 12:40:18 | Minor |  | LOF | 09/07/2025 12:40:18 | P3 | Repeater | qunfuddah | Sceco_STB | TX NSA | JZMA9072_02-10.74.120.87 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:00 | 10/08/2025 16:02:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251008000994 | PCM-20251008-00001799 | TT-20251008-01861 | Reference_telecom | Region_6 | KMS0039 | KMS0039 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/08/2025 15:24:01 | 10/09/2025 01:33:09 | 10/09/2025 03:24:01 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at KMS0039_13-10.10.159.193 | 05/17/2025 19:47:39 | Minor |  | LOF | 05/17/2025 19:47:39 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | KMS0039_13-10.10.159.193 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:01 | 10/08/2025 20:27:53 | 10/09/2025 01:33:00 | 10/09/2025 01:33:09 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008000998 | PCM-20251008-00001803 | TT-20251008-01865 | Reference_telecom | Region_6 | KMS0465 | KMS0465 | Transsmission | MW_HW_fault | Replace Control Card | Ahmed Abdelaziz Hamid Abdelrahman | 10/08/2025 15:24:05 | 10/23/2025 15:06:13 | 10/09/2025 03:24:05 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2,ReplaceableUnitMis at KMS0465_10-10.10.159.194 | 07/09/2025 01:03:56 | Minor |  | LOF | 07/09/2025 01:03:56 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | KMS0465_10-10.10.159.194 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:05 | 10/08/2025 15:27:52 | 10/23/2025 15:05:55 |  |  | 10/23/2025 15:06:13 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001002 | PCM-20251008-00001808 | TT-20251008-01870 | Reference_telecom | Region_5 | MAK0053 | MAK0053 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Inam ullah | 10/08/2025 15:24:10 | 10/13/2025 20:17:39 | 10/09/2025 03:24:10 | Nokia Eband Observing InternalCommunicationProblem-Port 4/5,DemXpicLOS-P at MAK0053 -19-10.3.224.17 | 10/01/2025 07:27:10 | Minor |  | LOF | 10/01/2025 07:27:10 | P1 | 2G | makkah | Sceco_STB | TX NSA | MAK0053 -19-10.3.224.17 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:10 | 10/13/2025 17:19:31 | 10/13/2025 18:17:14 | 10/13/2025 18:17:17 | 10/13/2025 18:17:20 | 10/13/2025 20:17:39 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001004 | PCM-20251008-00001810 | TT-20251008-01872 | Reference_telecom | Region_5 | MAK0123 | MAK0123 |  |  |  | Muhammad Shabbir Muhammad | 10/08/2025 15:24:12 | 10/10/2025 19:16:52 | 10/09/2025 03:24:12 | Nokia Eband Observing DemFail-Port 4/5,DemFail-Port 3/5,LagPortDown-Port at MAK0123_SH10-10.10.189.161 | 07/30/2025 11:41:03 | Minor |  | LOF | 07/30/2025 11:41:03 | P1 | 2G | makkah | Sceco_STB | TX NSA | MAK0123_SH10-10.10.189.161 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:12 | 10/10/2025 19:16:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001005 | PCM-20251008-00001811 | TT-20251008-01873 | Reference_telecom | Region_5 | MAK0156 | MAK0156 | Transsmission | MW_Connectors | Remade Indoor MW Connector | IJAZ ALI | 10/08/2025 15:24:13 | 10/21/2025 10:56:16 | 10/09/2025 03:24:13 | Nokia Eband Observing LagPortDown-Port 4/5,Degrade-LAG 1 at MAK0156-10.10.142.242 | 10/07/2025 12:38:22 | Minor |  | LOF | 10/07/2025 12:38:22 | P3 | 2G | makkah | Sceco | TX NSA | MAK0156-10.10.142.242 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:13 | 10/21/2025 09:17:57 | 10/21/2025 09:18:31 | 10/21/2025 09:18:34 | 10/21/2025 10:02:01 | 10/21/2025 10:56:16 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001006 | PCM-20251008-00001812 | TT-20251008-01874 | Reference_telecom | Region_5 | MAK0229 | MAK0229 | Transsmission | MW_HW_fault | Replace ODU | Husain Hassan Ishag Omer | 10/08/2025 15:24:14 | 10/23/2025 12:58:18 | 10/09/2025 03:24:14 | Nokia Eband Observing DemFail-Channel 1A at MAK0229_6-10.221.241.129 | 09/23/2025 17:31:21 | Minor |  | LOF | 09/23/2025 17:31:21 | P1 | 2G | makkah | Sceco | TX NSA | MAK0229_6-10.221.241.129 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:14 | 10/23/2025 10:21:12 | 10/23/2025 10:21:22 | 10/23/2025 10:21:27 | 10/23/2025 10:43:51 | 10/23/2025 12:58:18 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001009 | PCM-20251008-00001815 | TT-20251008-01877 | Reference_telecom | Region_5 | MAK0273 | MAK0273 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/08/2025 15:24:19 | 10/24/2025 01:40:09 | 10/09/2025 03:24:19 | Nokia Eband Observing DemFail-Port 4/5 at MAK0273_01-10.3.224.18 | 10/01/2025 07:27:13 | Minor |  | LOF | 10/01/2025 07:27:13 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK0273_01-10.3.224.18 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:19 | 10/24/2025 01:40:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001011 | PCM-20251008-00001817 | TT-20251008-01879 | Reference_telecom | Region_5 | MAK0380 | MAK0380 | Transsmission | MW_Connectors | Replace Indoor MW Connector | IJAZ ALI | 10/08/2025 15:24:20 | 10/20/2025 14:53:20 | 10/09/2025 03:24:20 | Nokia Eband Observing Degrade-LAG 1,LossOfSignal-Port 5/5,InternalCommun at MAK0380_SH01-10.10.178.243 | 09/21/2025 16:40:12 | Minor |  | LOF | 09/21/2025 16:40:12 | VIP | 2G | makkah | Sceco | TX NSA | MAK0380_SH01-10.10.178.243 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:20 | 10/20/2025 09:13:16 | 10/20/2025 09:13:45 | 10/20/2025 09:13:50 | 10/20/2025 11:49:22 | 10/20/2025 14:53:20 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001013 | PCM-20251008-00001819 | TT-20251008-01881 | Reference_telecom | Region_5 | MAK0538 | MAK0538 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/08/2025 15:24:22 | 10/21/2025 19:56:52 | 10/09/2025 03:24:22 | Nokia Eband Observing DemFail-Port 4/5,DemFail-Port 3/5,Degrade-LAG 1,La at MAK0538-9-10.3.235.49 | 08/13/2025 13:26:28 | Minor |  | LOF | 08/13/2025 13:26:28 | P1 | 2G | makkah | Sceco | TX NSA | MAK0538-9-10.3.235.49 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:22 | 10/21/2025 19:56:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001017 | PCM-20251008-00001823 | TT-20251008-01885 | Reference_telecom | Region_5 | MAK2096 | MAK2096 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/08/2025 15:24:27 | 10/08/2025 17:42:34 | 10/09/2025 03:24:27 | Nokia Eband Observing InternalCommunicationProblem-Port 6/5,InternalComm at MAK2096-10.10.138.74 | 10/04/2025 03:03:47 | Minor |  | LOF | 10/04/2025 03:03:47 | P3 | 2G | makkah | Sceco | TX NSA | MAK2096-10.10.138.74 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:27 | 10/08/2025 17:42:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001018 | PCM-20251008-00001824 | TT-20251008-01886 | Reference_telecom | Region_4 | MKMD0561 | MKMD0561 |  |  |  | Khizer Hayat | 10/08/2025 15:24:28 | 10/09/2025 16:53:14 | 10/09/2025 03:24:28 | Nokia Eband Observing DemFail-Channel 1B (SPARE),DemFail-Channel 1B (MAI at MKMD0561_02-10.10.178.74 | 09/29/2025 17:53:42 | Minor |  | LOF | 09/29/2025 17:53:42 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0561_02-10.10.178.74 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:28 | 10/09/2025 16:53:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001019 | PCM-20251008-00001825 | TT-20251008-01887 | Reference_telecom | Region_6 | MKW2129 | MKW2129 |  |  |  | Manzoor Ahmed | 10/08/2025 15:24:29 | 10/08/2025 17:33:16 | 10/09/2025 03:24:29 | Nokia Eband Observing BatteryFail-MKW2129 at MKW2129-10.221.246.53 | 10/05/2025 02:15:43 | Minor |  | LOF | 10/05/2025 02:15:43 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2129-10.221.246.53 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:29 | 10/08/2025 17:33:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001020 | PCM-20251008-00001826 | TT-20251008-01888 | Reference_telecom | Region_6 | MKW2140 | MKW2140 |  |  |  | Manzoor Ahmed | 10/08/2025 15:24:31 | 10/08/2025 17:33:16 | 10/09/2025 03:24:31 | Nokia Eband Observing Degrade-LAG 1,LossOfSignal-Port 8/3,InternalCommun at MKW2140_01-10.221.246.57 | 09/22/2025 14:30:10 | Minor |  | LOF | 09/22/2025 14:30:10 | P3 | 2G | Baha | Sceco | TX NSA | MKW2140_01-10.221.246.57 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:31 | 10/08/2025 17:33:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001021 | PCM-20251008-00001827 | TT-20251008-01889 | Reference_telecom | Region_6 | NMR9001 | NMR9001 |  |  |  | SHAH KHALID | 10/08/2025 15:24:32 | 10/08/2025 15:28:13 | 10/09/2025 03:24:32 | Nokia Eband Observing HouseKeeping-auxIn-13 at NMR9001_01-10.221.243.50 | 10/05/2025 17:21:30 | Minor |  | LOF | 10/05/2025 17:21:30 | P3 | Repeater | Baha | Generator_SG | TX NSA | NMR9001_01-10.221.243.50 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:32 | 10/08/2025 15:28:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001024 | PCM-20251008-00001830 | TT-20251008-01892 | Reference_telecom | Region_6 | RTH0954 | RTH0954 |  |  |  | Muhammad Ali | 10/08/2025 15:24:36 | 10/08/2025 15:43:13 | 10/09/2025 03:24:36 | Nokia Eband Observing ReplaceableUnitMissing-Card - 1 at RTH0954_01-10.21.79.232 | 06/29/2025 14:29:34 | Minor |  | LOF | 06/29/2025 14:29:34 | P2 | 2G | raith | Sceco | TX NSA | RTH0954_01-10.21.79.232 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:36 | 10/08/2025 15:43:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001026 | PCM-20251008-00001833 | TT-20251008-01895 | Reference_telecom | Region_6 | SMT0063 | SMT0063 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:24:38 | 10/08/2025 15:33:23 | 10/09/2025 03:24:38 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at SMT0063_02-10.3.226.37 | 09/21/2025 19:00:42 | Minor |  | LOF | 09/21/2025 19:00:42 | P1 | 2G | jizan | Sceco | TX NSA | SMT0063_02-10.3.226.37 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:38 | 10/08/2025 15:33:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001028 | PCM-20251008-00001835 | TT-20251008-01897 | Reference_telecom | Region_6 | SAB0146 | SAB0146 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:24:40 | 10/08/2025 16:02:45 | 10/09/2025 03:24:40 | Nokia Eband Observing DemFail-Port 1/1 at SAB0146-10.3.86.186 | 10/01/2025 03:33:32 | Minor |  | LOF | 10/01/2025 03:33:32 | P2 | 2G | baish | Sceco | TX NSA | SAB0146-10.3.86.186 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:40 | 10/08/2025 16:02:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001032 | PCM-20251008-00001839 | TT-20251008-01901 | Reference_telecom | Region_6 | SAB0058 | SAB0058 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:24:45 | 10/10/2025 18:45:50 | 10/09/2025 03:24:45 | Nokia Eband Observing DemFail-Port 1/1 at SAB0058-10.3.86.138 | 08/04/2024 09:10:06 | Minor |  | LOF | 08/04/2024 09:10:06 | P1 | 2G | baish | Sceco | TX NSA | SAB0058-10.3.86.138 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:45 | 10/08/2025 16:02:48 | 10/10/2025 18:45:36 | 10/10/2025 18:45:45 | 10/10/2025 18:45:50 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001033 | PCM-20251008-00001840 | TT-20251008-01902 | Reference_telecom | Region_6 | SAB0057 | SAB0057 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:24:47 | 10/08/2025 16:02:48 | 10/09/2025 03:24:47 | Nokia Eband Observing ReplaceableUnitProblem-Card - 1 at SAB0057_09-10.21.79.209 | 03/16/2025 05:28:02 | Minor |  | LOF | 03/16/2025 05:28:02 | P1 | 2G | baish | Sceco_STB | TX NSA | SAB0057_09-10.21.79.209 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:47 | 10/08/2025 16:02:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001034 | PCM-20251008-00001841 | TT-20251008-01903 | Reference_telecom | Region_4 | TUR0681 | TUR0681 |  |  |  | Rashid Shafique | 10/08/2025 15:24:48 | 10/08/2025 16:20:01 | 10/09/2025 03:24:48 | Nokia Eband Observing DemFail-Port 3/5,LagPortDown-Port 3/5,Degrade-LAG at TUR0681-10.3.236.209 | 09/27/2025 05:07:00 | Minor |  | LOF | 09/27/2025 05:07:00 | P3 | 2G | taif | Sceco | TX NSA | TUR0681-10.3.236.209 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:48 | 10/08/2025 16:20:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001037 | PCM-20251008-00001844 | TT-20251008-01906 | Reference_telecom | Region_6 | SAB0059 | SAB0059 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:24:52 | 10/08/2025 16:02:49 | 10/09/2025 03:24:52 | Nokia Eband Observing DemFail-Port 1/1 at SAB0059-10.3.86.146 | 05/05/2025 16:58:25 | Minor |  | LOF | 05/05/2025 16:58:25 | P2 | 2G | baish | Sceco | TX NSA | SAB0059-10.3.86.146 | FLM_TE | [8 empty] | API | 10/08/2025 15:24:52 | 10/08/2025 16:02:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001040 | PCM-20251008-00001847 | TT-20251008-01909 | MW_HC | Region_4 | UKHA0735 | UKHA0735 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:25:40 | 10/12/2025 12:14:47 | 10/09/2025 03:25:40 | NEC MW HC_P2 Observing Modem Down at UKHA0630(10.154.113.58)--UKHA0735(10.154.111.210) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | adam | Sceco | TX NSA | UKHA0630(10.154.113.58)--UKHA0735(10.154.111.210) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:40 | 10/08/2025 16:02:45 | 10/12/2025 12:14:33 |  |  | 10/12/2025 12:14:47 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001041 | PCM-20251008-00001849 | TT-20251008-01910 | MW_HC | Region_4 | UKHA0731 | UKHA0731 | Transsmission | MW_HW_fault | Replace ODU | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:25:41 | 10/12/2025 12:18:31 | 10/09/2025 03:25:41 | NEC MW HC_P0 Observing Modem Down at UKHA0630(10.154.113.58)--UKHA0731(10.154.113.57) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | adam | Sceco | TX NSA | UKHA0630(10.154.113.58)--UKHA0731(10.154.113.57) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:41 | 10/08/2025 16:02:46 | 10/12/2025 12:17:30 |  |  | 10/12/2025 12:18:31 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001042 | PCM-20251008-00001850 | TT-20251008-01911 | MW_HC | Region_4 | TAF6098 | TAF6098 |  |  |  | Rashid Shafique | 10/08/2025 15:25:42 | 10/08/2025 16:20:02 | 10/09/2025 03:25:42 | NEC MW HC_P0 Observing Modem Down at TAF0270(10.1.166.17)--TAF6098(10.1.166.18) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | SRAN | taif | Sceco | TX NSA | TAF0270(10.1.166.17)--TAF6098(10.1.166.18) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:42 | 10/08/2025 16:20:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001043 | PCM-20251008-00001851 | TT-20251008-01912 | MW_HC | Region_4 | SIR0155 | SIR0155 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:25:43 | 10/08/2025 16:02:46 | 10/09/2025 03:25:43 | NEC MW HC_P0 Observing RSL Issue at SIR0154(10.88.222.55)--SIR0155(10.88.222.56) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | adam | Generator_SG | TX NSA | SIR0154(10.88.222.55)--SIR0155(10.88.222.56) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:43 | 10/08/2025 16:02:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001044 | PCM-20251008-00001852 | TT-20251008-01913 | MW_HC | Region_5 | MKTF0635 | MKTF0635 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/08/2025 15:25:44 | 10/08/2025 23:47:24 | 10/09/2025 03:25:44 | NEC MW HC_P0 Observing RSL Issue at MAK2841(10.154.125.245)--MKTF0635(10.154.125.244) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK2841(10.154.125.245)--MKTF0635(10.154.125.244) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:44 | 10/08/2025 23:47:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001045 | PCM-20251008-00001853 | TT-20251008-01914 | MW_HC | Region_4 | JDMD0863 | JDMD0863 |  |  |  | Nazeer Mohammed | 10/08/2025 15:25:45 | 10/09/2025 13:22:09 | 10/09/2025 03:25:45 | NEC MW HC_P0 Observing Performance Issue at JDMD0861(10.154.115.9)--JDMD0863(10.154.115.12) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDMD0861(10.154.115.9)--JDMD0863(10.154.115.12) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:45 | 10/09/2025 13:22:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001047 | PCM-20251008-00001855 | TT-20251008-01916 | MW_HC | Region_4 | JED0582 | JED0582 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:25:47 | 10/08/2025 16:09:02 | 10/09/2025 03:25:47 | NEC MW HC_P2 Observing Modem Down at JED0221(10.1.165.121)--JED0582(10.1.165.123) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | jeddah | Sceco | TX NSA | JED0221(10.1.165.121)--JED0582(10.1.165.123) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:47 | 10/08/2025 16:09:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001049 | PCM-20251008-00001857 | TT-20251008-01918 | MW_HC | Region_4 | NNL0216 | NNL0216 | Transsmission | MW_HW_fault | Replace IDU | TOSIF AHMED - MUHAMMAD SHARIF | 10/08/2025 15:25:51 | 10/10/2025 11:38:29 | 10/09/2025 03:25:51 | NEC MW HC_P0 Observing Performance Issue at NNL0139(10.88.222.73)--NNL0216(10.88.222.72) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | adam | Generator_SG | TX NSA | NNL0139(10.88.222.73)--NNL0216(10.88.222.72) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:51 | 10/08/2025 16:01:43 | 10/10/2025 11:38:18 |  |  | 10/10/2025 11:38:29 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001050 | PCM-20251008-00001858 | TT-20251008-01919 | MW_HC | Region_4 | MKJD0573 | MKJD0573 |  |  |  | Amjad Ali Muhammad Parves | 10/08/2025 15:25:51 | 10/08/2025 16:42:54 | 10/09/2025 03:25:51 | NEC MW HC_P0 Observing Modem Down at MKJD0570(10.154.128.242)--MKJD0573(10.154.128.249) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Generator_SG | TX NSA | MKJD0570(10.154.128.242)--MKJD0573(10.154.128.249) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:51 | 10/08/2025 16:42:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001051 | PCM-20251008-00001859 | TT-20251008-01920 | MW_HC | Region_4 | JED6095 | JED6095 |  |  |  | Mohamed Farag Abdelbary | 10/08/2025 15:25:52 | 10/09/2025 14:52:45 | 10/09/2025 03:25:52 | NEC MW HC_P0 Observing Modem Down at JED0308(10.99.254.65)--JED6095(10.99.254.66) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | jeddah | Sceco | TX NSA | JED0308(10.99.254.65)--JED6095(10.99.254.66) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:52 | 10/09/2025 14:52:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001053 | PCM-20251008-00001861 | TT-20251008-01922 | MW_HC | Region_4 | JED6125 | JED6125 |  |  |  | Mohamed Farag Abdelbary | 10/08/2025 15:25:54 | 10/09/2025 14:52:45 | 10/09/2025 03:25:54 | NEC MW HC_P0 VIP Observing Modem Down at JED0152(10.1.165.163)--JED6125(10.1.165.164) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED0152(10.1.165.163)--JED6125(10.1.165.164) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:54 | 10/09/2025 14:52:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001054 | PCM-20251008-00001862 | TT-20251008-01923 | MW_HC | Region_4 | NNL0168 | NNL0168 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 15:25:55 | 10/20/2025 21:24:44 | 10/09/2025 03:25:55 | NEC MW HC_P0 Observing Performance Issue at JDJZ0769(10.88.224.34)--NNL0168(10.88.224.36) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0769(10.88.224.34)--NNL0168(10.88.224.36) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:55 | 10/20/2025 21:24:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001056 | PCM-20251008-00001863 | TT-20251008-01924 | MW_HC | Region_4 | QAL0721 | QAL0721 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 15:25:56 | 10/09/2025 15:07:30 | 10/09/2025 03:25:56 | NEC MW HC_P2 Observing Performance Issue at JDJZ0768(10.88.222.23)--QAL0721(10.88.222.20) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | qunfuddah | Sceco | TX NSA | JDJZ0768(10.88.222.23)--QAL0721(10.88.222.20) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:56 | 10/09/2025 15:07:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001057 | PCM-20251008-00001864 | TT-20251008-01925 | MW_HC | Region_4 | SDY2715 | SDY2715 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 15:25:58 | 10/09/2025 15:07:31 | 10/09/2025 03:25:58 | NEC MW HC_P0 Observing Performance Issue at JDJZ0766(10.88.222.114)--SDY2715(10.88.222.116) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | alaith | Sceco_STB | TX NSA | JDJZ0766(10.88.222.114)--SDY2715(10.88.222.116) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:58 | 10/09/2025 15:07:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001058 | PCM-20251008-00001865 | TT-20251008-01926 | MW_HC | Region_4 | SHB0671 | SHB0671 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 15:25:59 | 10/09/2025 15:07:32 | 10/09/2025 03:25:59 | NEC MW HC_P0 Observing Performance Issue at JDJZ0765(10.154.140.84)--SHB0671(10.154.140.103) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | qunfuddah | Sceco | TX NSA | JDJZ0765(10.154.140.84)--SHB0671(10.154.140.103) | FLM_TE | [8 empty] | API | 10/08/2025 15:25:59 | 10/09/2025 15:07:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001059 | PCM-20251008-00001866 | TT-20251008-01927 | MW_HC | Region_4 | JED0713 | JED0713 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 15:26:00 | 10/08/2025 15:36:27 | 10/09/2025 03:26:00 | NEC MW HC_P0 Observing Performance Issue at JDJZ0761(10.99.254.185)--JED0713(10.99.254.186) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Sceco | TX NSA | JDJZ0761(10.99.254.185)--JED0713(10.99.254.186) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:00 | 10/08/2025 15:36:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001060 | PCM-20251008-00001867 | TT-20251008-01928 | MW_HC | Region_4 | JED0920 | JED0920 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:26:01 | 10/08/2025 16:09:03 | 10/09/2025 03:26:01 | NEC MW HC_P0 Observing Modem Down at JDAP0940(10.1.165.130)--JED0920(10.1.165.129) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Sceco | TX NSA | JDAP0940(10.1.165.130)--JED0920(10.1.165.129) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:01 | 10/08/2025 16:09:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001061 | PCM-20251008-00001868 | TT-20251008-01929 | MW_HC | Region_4 | HJR0041 | HJR0041 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/08/2025 15:26:02 | 10/21/2025 19:36:42 | 10/09/2025 03:26:02 | NEC MW HC_P0 Observing Modem Down at HJR0040(10.88.220.132)--HJR0041(10.88.220.130) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | adam | Sceco | TX NSA | HJR0040(10.88.220.132)--HJR0041(10.88.220.130) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:02 | 10/08/2025 16:01:43 | 10/21/2025 19:36:30 |  |  | 10/21/2025 19:36:42 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001063 | PCM-20251008-00001870 | TT-20251008-01931 | MW_HC | Region_6 | RTH0652 | RTH0652 |  |  |  | Muhammad Ali | 10/08/2025 15:26:04 | 10/08/2025 15:43:14 | 10/09/2025 03:26:04 | NEC MW HC_P0 Observing RSL Issue at RTH0603(10.1.173.114)--RTH0652(10.1.173.113) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | raith | Sceco | TX NSA | RTH0603(10.1.173.114)--RTH0652(10.1.173.113) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:04 | 10/08/2025 15:43:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001064 | PCM-20251008-00001871 | TT-20251008-01932 | MW_HC | Region_6 | NJR0074 | NJR0074 |  |  |  | Shahid Ali Roshan Ali | 10/08/2025 15:26:05 | 10/08/2025 18:00:55 | 10/09/2025 03:26:05 | NEC MW HC_P0 Observing Modem Down at NJR0011(10.154.164.113)--NJR0074(10.154.164.122) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | najran | Sceco | TX NSA | NJR0011(10.154.164.113)--NJR0074(10.154.164.122) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:05 | 10/08/2025 18:00:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001066 | PCM-20251008-00001873 | TT-20251008-01934 | MW_HC | Region_6 | MHL9722 | MHL9722 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/08/2025 15:26:08 | 10/08/2025 15:39:33 | 10/09/2025 03:26:08 | NEC MW HC_P0 Observing Modem Down at MHL0182(10.157.250.24)--MHL9722(10.157.250.23) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | Repeater | mohail | Generator_SG | TX NSA | MHL0182(10.157.250.24)--MHL9722(10.157.250.23) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:08 | 10/08/2025 15:39:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001068 | PCM-20251008-00001875 | TT-20251008-01936 | MW_HC | Region_6 | KHS0561 | KHS0561 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/08/2025 15:26:10 | 10/08/2025 15:27:52 | 10/09/2025 03:26:10 | NEC MW HC_P0 Observing Performance Issue at KHS0343(10.89.220.178)--KHS0561(10.89.220.179) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KHS0343(10.89.220.178)--KHS0561(10.89.220.179) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:10 | 10/08/2025 15:27:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001070 | PCM-20251008-00001877 | TT-20251008-01938 | MW_HC | Region_6 | KHS0865 | KHS0865 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/08/2025 15:26:13 | 10/08/2025 15:27:53 | 10/09/2025 03:26:13 | NEC MW HC_P0 Observing Performance Issue at KHS0342(10.89.220.51)--KHS0865(10.89.220.49) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | KHS0342(10.89.220.51)--KHS0865(10.89.220.49) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:13 | 10/08/2025 15:27:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001073 | PCM-20251008-00001880 | TT-20251008-01941 | MW_HC | Region_6 | JEC0313 | JEC0313 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:26:17 | 10/08/2025 16:02:51 | 10/09/2025 03:26:17 | NEC MW HC_P0 VIP Observing Modem Down at JEC0088(10.199.24.88)--JEC0313(10.199.24.90) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | baish | Generator_SG | TX NSA | JEC0088(10.199.24.88)--JEC0313(10.199.24.90) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:17 | 10/08/2025 16:02:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001074 | PCM-20251008-00001881 | TT-20251008-01942 | MW_HC | Region_6 | JEC0287 | JEC0287 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:26:18 | 10/08/2025 16:02:52 | 10/09/2025 03:26:18 | NEC MW HC_P0 VIP Observing Modem Down at JEC0088(10.199.24.88)--JEC0287(10.199.24.89) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | baish | Generator_SG | TX NSA | JEC0088(10.199.24.88)--JEC0287(10.199.24.89) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:18 | 10/08/2025 16:02:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001075 | PCM-20251008-00001882 | TT-20251008-01943 | MW_HC | Region_6 | JIZ0086 | JIZ0086 |  |  |  | Osama Hadi | 10/08/2025 15:26:19 | 10/08/2025 16:03:18 | 10/09/2025 03:26:19 | NEC MW HC_P0 Observing Modem Down at JDSM0791(10.157.253.139)--JIZ0086(10.157.253.138) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | jizan | Generator_SG | TX NSA | JDSM0791(10.157.253.139)--JIZ0086(10.157.253.138) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:19 | 10/08/2025 16:03:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001077 | PCM-20251008-00001884 | TT-20251008-01945 | MW_HC | Region_6 | JDJZ0789 | JDJZ0789 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:26:22 | 10/08/2025 16:02:52 | 10/09/2025 03:26:22 | NEC MW HC_P2 Observing Modem Down at JDJZ0788(10.154.170.55)--JDJZ0789(10.154.170.56) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | baish | Sceco | TX NSA | JDJZ0788(10.154.170.55)--JDJZ0789(10.154.170.56) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:22 | 10/08/2025 16:02:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001078 | PCM-20251008-00001885 | TT-20251008-01946 | MW_HC | Region_6 | SHQ0183 | SHQ0183 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 15:26:23 | 10/11/2025 14:55:49 | 10/09/2025 03:26:23 | NEC MW HC_P0 Observing Performance Issue at JDJZ0785(10.154.170.162)--SHQ0183(10.154.170.163) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | derb | Sceco | TX NSA | JDJZ0785(10.154.170.162)--SHQ0183(10.154.170.163) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:23 | 10/08/2025 18:20:27 | 10/11/2025 14:55:44 | 10/11/2025 14:55:47 | 10/11/2025 14:55:49 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001080 | PCM-20251008-00001887 | TT-20251008-01948 | MW_HC | Region_6 | FIF0150 | FIF0150 |  |  |  | Muhammad Ali | 10/08/2025 15:26:26 | 10/08/2025 15:43:14 | 10/09/2025 03:26:26 | NEC MW HC_P0 Observing Modem Down at FIF0046(10.157.253.170)--FIF0150(10.157.253.171) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | dair | Sceco | TX NSA | FIF0046(10.157.253.170)--FIF0150(10.157.253.171) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:26 | 10/08/2025 15:43:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001081 | PCM-20251008-00001888 | TT-20251008-01949 | MW_HC | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 15:26:26 | 10/08/2025 18:20:28 | 10/09/2025 03:26:26 | NEC MW HC_P2 Observing Modem Down at DRB0908(10.154.164.50)--JDJZ0785(10.154.164.49) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0908(10.154.164.50)--JDJZ0785(10.154.164.49) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:26 | 10/08/2025 18:20:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001082 | PCM-20251008-00001889 | TT-20251008-01950 | MW_HC | Region_6 | DRB0911 | DRB0911 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 15:26:28 | 10/08/2025 18:38:03 | 10/09/2025 03:26:28 | NEC MW HC_P0 Observing Modem Down at DRB0165(10.154.164.54)--DRB0911(10.154.164.55) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0165(10.154.164.54)--DRB0911(10.154.164.55) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:28 | 10/08/2025 18:38:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001083 | PCM-20251008-00001890 | TT-20251008-01951 | MW_HC | Region_6 | DRB0911 | DRB0911 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 15:26:29 | 10/08/2025 18:38:04 | 10/09/2025 03:26:29 | NEC MW HC_P0 Observing Modem Down at DRB0038(10.154.171.3)--DRB0911(10.154.171.1) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0038(10.154.171.3)--DRB0911(10.154.171.1) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:29 | 10/08/2025 18:38:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001084 | PCM-20251008-00001891 | TT-20251008-01952 | MW_HC | Region_6 | RTH9007 | RTH9007 |  |  |  | Muhammad Ali | 10/08/2025 15:26:30 | 10/08/2025 15:43:15 | 10/09/2025 03:26:30 | NEC MW HC_P2 Observing Modem Down at DAR0901(10.157.248.67)--RTH9007(10.157.248.65) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | Repeater | raith | Sceco_STB | TX NSA | DAR0901(10.157.248.67)--RTH9007(10.157.248.65) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:30 | 10/08/2025 15:43:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251003000250 | PCM-20251003-00000440 | TT-20251003-00464 | EM | Region_4 | JED0566 | JED0566 |  |  |  | Sajid Nazir Muhammad Nazir | 10/03/2025 07:24:36 | 10/03/2025 07:32:13 | 10/03/2025 13:24:36 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED0566-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P1-VIP @ Sceco | 10/03/2025 07:16:08 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/03/2025 07:16:00 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0566 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/03/2025 07:24:36 | 10/03/2025 07:32:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000264 | PCM-20251003-00000456 | TT-20251003-00483 | EM | Region_4 | TUR0693 | TUR0693 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/03/2025 07:43:40 | 10/03/2025 09:33:05 | 10/03/2025 19:43:40 | RECTIFIER MAINS POWER FAILURE at TUR0693-GSM-P2 @ Sceco | 10/03/2025 07:35:21 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/03/2025 07:35:10 | P2 | 2G | taif | Sceco | 2G NSA | TUR0693 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/03/2025 07:43:40 | 10/03/2025 09:33:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000265 | PCM-20251003-00000458 | TT-20251003-00484 | EM | Region_1 | DAM0229 | DAM0229 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/03/2025 07:44:10 | 10/04/2025 16:52:49 | 10/03/2025 11:44:10 | AMBIENT_TEMP_FLUCT at DAM0229_HYB @ Sceco | 10/03/2025 07:42:20 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/03/2025 07:42:13 | P1 | SRAN | dammam | Sceco | DWDM NSA | DAM0229 | FLM_EM | [5 empty] | 4-TO DAM0255(2-A) |  |  | API | 10/03/2025 07:44:10 | 10/04/2025 16:52:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251003000280 | PCM-20251003-00000479 | TT-20251003-00501 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/03/2025 08:03:21 | 10/03/2025 19:35:59 | 10/03/2025 20:03:21 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/03/2025 07:54:53 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/03/2025 07:54:49 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/03/2025 08:03:21 | 10/03/2025 19:35:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000288 | PCM-20251003-00000492 | TT-20251003-00517 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/03/2025 08:14:10 | 10/04/2025 00:05:16 | 10/03/2025 20:14:10 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/03/2025 08:05:41 | Minor | 7103 | AIRCON 1 FAILURE | 10/03/2025 08:05:33 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/03/2025 08:14:10 | 10/04/2025 00:03:42 | 10/04/2025 00:05:06 |  |  | 10/04/2025 00:05:16 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251003000307 | PCM-20251003-00000524 | TT-20251003-00359 | Reference_telecom | Region_2 | RYQS2014 | RYQS2014 |  |  |  | Ahmed Mahmoud Mohamed Mahmoud | 10/03/2025 08:50:17 | 10/03/2025 08:50:17 | 10/03/2025 12:50:17 | IP PM Activation Failure at R2_RY1_HWBSC01 @ Sceco_STB | 10/03/2025 02:38:56 | Critical | 21341 | IP PM Activation Failure | 10/03/2025 02:38:23 | P3 | SRAN | buraidah | Power Cube | 2G NSA | R2_RY1_HWBSC01 | FLM_EM |  |  | PCM-20251003-00000508 | Suspected power issue at site | Suspected power issue at site |  |  |  | API | 10/03/2025 08:50:17 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000332 | PCM-20251003-00000568 | TT-20251003-00613 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/03/2025 09:19:45 | 10/03/2025 12:00:53 | 10/03/2025 15:19:45 | high temprature 32 at DAM2066-P1-HUB_SRAN @ Sceco | 10/03/2025 09:07:31 | Major | 65102 | high temprature 32 | 10/03/2025 09:09:03 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/03/2025 09:19:45 | 10/03/2025 12:00:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000356 | PCM-20251003-00000605 | TT-20251003-00655 | EM | Region_4 | QUZ0738 | QUZ0738 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/03/2025 09:55:55 | 10/03/2025 17:24:03 | 10/03/2025 21:55:55 | RECTIFIER MODULE FAILURE at QUZ1M7738-P3-CA-L800 @ Sceco | 10/03/2025 09:47:42 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/03/2025 09:47:36 | P2 | 4G | qunfuddah | Sceco | LTE NSA | QUZ1M7738 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/03/2025 09:55:55 | 10/03/2025 17:24:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000369 | PCM-20251003-00000625 | TT-20251003-00682 | EM | Region_4 | JED0086 | JED0086 |  |  |  | Amer Attallah Awadallah | 10/03/2025 10:26:55 | 10/03/2025 13:38:51 | 10/03/2025 16:26:55 | HIGH TEMPERATURE 32 DEGREE C at JED0086-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-SHOP-HUB-WDM-FON @ Sceco | 10/03/2025 10:18:29 | Major | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/03/2025 10:18:20 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0086 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/03/2025 10:26:55 | 10/03/2025 13:38:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251003000409 | PCM-20251003-00000689 | TT-20251003-00743 | EM | Region_4 | TAF0268 | TAF0268 |  |  |  | Walid Magdy Tawfik Elbana | 10/03/2025 11:16:01 | 10/03/2025 16:17:52 | 10/03/2025 23:16:01 | AIRCON 1 FAILURE at TAF0268-GSM-P3 @ Sceco | 10/03/2025 11:07:44 | Minor | 7103 | AIRCON 1 FAILURE | 10/03/2025 11:07:38 | P3 | 2G | taif | Sceco | 2G NSA | TAF0268 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/03/2025 11:16:01 | 10/03/2025 16:17:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000455 | PCM-20251003-00000776 | TT-20251003-00799 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/03/2025 12:06:05 | 10/03/2025 14:00:15 | 10/04/2025 00:06:05 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/03/2025 11:55:41 | Minor | 65102 | High temperature 32C alarm | 10/03/2025 11:55:39 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/03/2025 12:06:05 | 10/03/2025 14:00:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000542 | PCM-20251003-00000907 | TT-20251003-00916 | EM | Region_4 | JED0713 | JED0713 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/03/2025 13:48:55 | 10/04/2025 11:39:19 | 10/04/2025 01:48:55 | HIGH TEMPERATURE 32 DEGREE C at JED1M7713-P3-CA-L800 @ Sceco | 10/03/2025 13:40:22 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/03/2025 13:40:18 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7713 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/03/2025 13:48:55 | 10/04/2025 11:39:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000601 | PCM-20251003-00000986 | TT-20251003-00998 | EM | Region_4 | TAF2453 | TAF2453 |  |  |  | Walid Magdy Tawfik Elbana | 10/03/2025 14:47:45 | 10/03/2025 16:17:52 | 10/04/2025 02:47:45 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at TAF1M8453-P3-CA-L800-P3 @ Sceco | 10/03/2025 14:39:22 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/03/2025 14:39:10 | P3 | 4G | jeddah | Sceco | LTE NSA | TAF1M8453 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/03/2025 14:47:45 | 10/03/2025 16:17:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000653 | PCM-20251003-00001076 | TT-20251003-01106 | EM | Region_2 | RIY0398 | RIY0398 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/03/2025 15:30:05 | 10/07/2025 17:33:18 | 10/04/2025 03:30:05 | Air condition 1 failure alarm at RIY0398-P2_SRAN @ Sceco | 10/03/2025 15:21:54 | Minor | 65104 | Air condition 1 failure alarm | 10/03/2025 15:19:38 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0398 | FLM_EM | [8 empty] | API | 10/03/2025 15:30:05 | 10/07/2025 17:33:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000702 | PCM-20251003-00001155 | TT-20251003-01206 | EM | Region_6 | RYNJ9701 | RYNJ9701 |  |  |  | Ijaz Ahmad Ali Muhammad | 10/03/2025 16:25:56 | 10/06/2025 09:45:01 | 10/03/2025 20:25:56 | DOOR OPEN (Input-1) at RYNJ9701-2 on 10.157.250.62 @ Generator_SG | 10/03/2025 16:23:44 | Critical | DOOR OPEN (Input-1) | DOOR OPEN (Input-1) | 10/03/2025 16:14:03 | P1 | Repeater | wadi dawasar | Generator_SG | TX NSA | RYNJ9701 | FLM_EM | [8 empty] | API | 10/03/2025 16:25:56 | 10/04/2025 06:32:02 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251003000725 | PCM-20251003-00001192 | TT-20251003-01242 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/03/2025 16:50:17 | 10/04/2025 11:44:25 | 10/04/2025 04:50:17 | RECTIFIER MODULE FAILURE at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/03/2025 16:41:51 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/03/2025 16:41:46 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/03/2025 16:50:17 | 10/04/2025 11:44:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000743 | PCM-20251003-00001222 | TT-20251003-01272 | EM | Region_1 | SKAR0181 | SKAR0181 | Enviroment | Air Condition | Change Fan | Asmat Anwar Sher Ullah Khan | 10/03/2025 17:11:55 | 10/04/2025 22:00:02 | 10/03/2025 21:11:55 | AMBIENT_TEMP_FLUCT at SKAR0181_HYB @ Sceco_STB | 10/03/2025 17:09:48 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/03/2025 17:09:41 | P2 | SRAN | sakaka | Sceco_STB | DWDM NSA | SKAR0181 | FLM_EM | [5 empty] | 0-TO SKAR0177(1-D) |  |  | API | 10/03/2025 17:11:55 | 10/04/2025 21:58:27 | 10/04/2025 21:59:31 |  |  | 10/04/2025 22:00:02 |  | Asmat Anwar Sher Ullah Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Preparation | CM20251003000747 | PCM-20251003-00001233 | TT-20251003-01304 | Reference_EM | Region_1 | NRY0686 | NRY0686 |  |  |  | Dileesh Muringothil Devarajan | 10/03/2025 17:20:40 | 10/03/2025 19:36:38 | 10/04/2025 05:20:40 | high temprature 32 at NRY0686-P3-USF_SRAN-PC @ Sceco | 10/03/2025 17:10:08 | Minor | 65102 | high temprature 32 | 10/03/2025 17:10:04 | P3 | SRAN | jubail | Sceco | 2G NSA | NRY0686 | FLM_EM | [8 empty] | API | 10/03/2025 17:20:40 | 10/03/2025 18:19:24 | 10/03/2025 19:36:33 | 10/03/2025 19:36:35 | 10/03/2025 19:36:38 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251003000842 | PCM-20251003-00001387 | TT-20251003-01456 | EM | Region_6 | MHA0433 | MHA0433 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Waqas Javed Tariq Javed | 10/03/2025 18:55:45 | 10/21/2025 06:13:18 | 10/04/2025 06:55:45 | AIRCON 2 FAILURE at MHA0433-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/03/2025 18:47:05 | Minor | 7103 | AIRCON 2 FAILURE | 10/03/2025 18:47:00 | P2 | 2G | abha | Generator_SG | 2G NSA | MHA0433 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/03/2025 18:55:45 | 10/04/2025 13:23:34 | 10/21/2025 06:13:04 |  |  | 10/21/2025 06:13:18 |  | Muhammad Waqas Javed Tariq Javed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000916 | PCM-20251003-00001524 | TT-20251003-01578 | EM | Region_4 | AQA0244 | AQA0244 |  |  |  | Yassir Omer Ibrahim Mahmoud | 10/03/2025 20:28:16 | 10/04/2025 10:59:09 | 10/04/2025 08:28:16 | AIR CON FAILURE at AQA1M7244-G9-NL8-L9-NL18-NL21-SBTS-P2-USF @ Sceco | 10/03/2025 20:19:45 | Minor | 7103 | AIR CON FAILURE | 10/03/2025 20:19:34 | P2 | 4G | adam | Sceco | LTE NSA | AQA1M7244 | FLM_EM | [5 empty] | AIR CON FAILURE |  |  | API | 10/03/2025 20:28:16 | 10/04/2025 10:59:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000933 | PCM-20251003-00001552 | TT-20251003-01601 | EM | Region_1 | NRY0686 | NRY0686 |  |  |  | Dileesh Muringothil Devarajan | 10/03/2025 20:47:20 | 10/04/2025 00:08:21 | 10/04/2025 08:47:20 | Door opening alarm at NRY0686-P3-USF_SRAN-PC @ Sceco | 10/03/2025 20:46:53 | Minor | 65101 | Door opening alarm | 10/03/2025 20:46:50 | P3 | SRAN | jubail | Sceco | 2G NSA | NRY0686 | FLM_EM | [8 empty] | API | 10/03/2025 20:47:20 | 10/04/2025 00:08:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003000938 | PCM-20251003-00001562 | TT-20251003-01618 | EM | Region_4 | JED0355 | JED0355 |  |  |  | Ahmed Gamal Mohamed Farag | 10/03/2025 20:57:40 | 10/04/2025 17:42:08 | 10/04/2025 08:57:40 | AIRCON 1 FAILURE at JED1M7355-CA-L900-L800-SBTS @ Sceco | 10/03/2025 20:49:17 | Minor | 7103 | AIRCON 1 FAILURE | 10/03/2025 20:49:08 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7355 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/03/2025 20:57:40 | 10/04/2025 17:42:08 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251003001060 | PCM-20251003-00001784 | TT-20251003-01807 | EM | Region_4 | NNL0176 | NNL0176 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/03/2025 23:48:10 | 10/04/2025 08:19:16 | 10/04/2025 11:48:10 | RECTIFIER MAINS POWER FAILURE at NNL0176-GSM-UMTS-P3 @ Generator_SG | 10/03/2025 23:40:01 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/03/2025 23:39:50 | P3 | 2G | qunfuddah | Generator_SG | 2G NSA | NNL0176 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/03/2025 23:48:10 | 10/04/2025 08:19:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000018 | PCM-20251004-00000038 | TT-20251004-00044 | EM | Region_4 | JED2671 | JED2671 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/04/2025 00:46:30 | 10/04/2025 11:39:21 | 10/04/2025 12:46:30 | TOWER LIGHT ALARM at JED2671-G9-L8-L18-L21-NR2.6-P3 @ Generator_SG | 10/04/2025 00:38:11 | Minor | 7103 | TOWER LIGHT ALARM | 10/04/2025 00:38:04 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2671 | FLM_EM | [5 empty] | TOWER LIGHT ALARM |  |  | API | 10/04/2025 00:46:30 | 10/04/2025 11:39:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004000021 | PCM-20251004-00000041 | TT-20251004-00046 | EM | Region_1 | JBKH0601 | JBKH0601 | Enviroment | Fire Alarm | Reset Fire Pannel | Nabawy Salah Ibrahim Loulah | 10/04/2025 00:49:36 | 10/05/2025 23:47:04 | 10/04/2025 04:49:36 | Door opening alarm at JBKH0601-P1-HUB-WDM_SRAN @ Sceco | 10/04/2025 00:48:48 | Critical | 65101 | Door opening alarm | 10/04/2025 00:48:46 | P1 | SRAN | jubail | Sceco | 2G NSA | JBKH0601 | FLM_EM | [8 empty] | API | 10/04/2025 00:49:36 | 10/04/2025 18:45:42 | 10/05/2025 23:41:38 | 10/05/2025 23:41:46 | 10/05/2025 23:41:49 | 10/05/2025 23:47:04 |  | Nabawy Salah Ibrahim Loulah |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251004000084 | PCM-20251004-00000165 | TT-20251004-00198 | EM | Region_4 | JED0368 | JED0368 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/04/2025 03:30:21 | 10/04/2025 17:18:46 | 10/04/2025 15:30:21 | RECTIFIER MAINS POWER FAILURE at JED0368-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/04/2025 03:21:59 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/04/2025 03:21:41 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0368 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/04/2025 03:30:21 | 10/04/2025 17:18:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004000094 | PCM-20251004-00000183 | TT-20251004-00212 | EM | Region_4 | JED0599 | JED0599 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sajid Nazir Muhammad Nazir | 10/04/2025 03:37:01 | 10/04/2025 06:07:48 | 10/04/2025 15:37:01 | RECTIFIER MODULE FAILURE at JED1M7599-CA-L900-L800-SBTS @ Sceco | 10/04/2025 03:28:34 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/04/2025 03:28:23 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7599 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/04/2025 03:37:01 | 10/04/2025 04:48:23 | 10/04/2025 06:01:09 | 10/04/2025 06:01:12 | 10/04/2025 06:01:14 | 10/04/2025 06:07:48 |  | Sajid Nazir Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000201 | PCM-20251004-00000353 | TT-20251004-00403 | EM | Region_4 | FYD0320 | FYD0320 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/04/2025 06:25:55 | 10/04/2025 23:52:51 | 10/04/2025 18:25:55 | AIRCON 1 FAILURE at FYD0320-GSM-P3 @ Sceco | 10/04/2025 06:17:25 | Minor | 7103 | AIRCON 1 FAILURE | 10/04/2025 06:17:20 | P3 | 2G | jeddah | Sceco | 2G NSA | FYD0320 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/04/2025 06:25:55 | 10/04/2025 23:52:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000268 | PCM-20251004-00000445 | TT-20251004-00507 | EM | Region_4 | TUR0693 | TUR0693 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/04/2025 07:52:45 | 10/04/2025 09:39:31 | 10/04/2025 19:52:45 | RECTIFIER MAINS POWER FAILURE at TUR0693-GSM-P2 @ Sceco | 10/04/2025 07:44:17 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/04/2025 07:44:10 | P2 | 2G | taif | Sceco | 2G NSA | TUR0693 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/04/2025 07:52:45 | 10/04/2025 09:39:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004000273 | PCM-20251004-00000451 | TT-20251004-00510 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/04/2025 07:55:51 | 10/05/2025 12:34:07 | 10/04/2025 19:55:51 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/04/2025 07:47:42 | Minor | 7103 | AIRCON 1 FAILURE | 10/04/2025 07:47:31 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/04/2025 07:55:51 | 10/04/2025 17:50:31 | 10/05/2025 12:33:55 |  |  | 10/05/2025 12:34:07 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251004000318 | PCM-20251004-00000548 | TT-20251004-00599 | EM | Region_4 | JED0318 | JED0318 |  |  |  | Sajid Nazir Muhammad Nazir | 10/04/2025 08:49:35 | 10/18/2025 15:56:01 | 10/04/2025 14:49:35 | RECTIFIER MODULE FAILURE at JED1M7318-FWA-P1-VIP-CA-L900-L800-SBTS @ Generator_SG | 10/04/2025 08:41:15 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/04/2025 08:40:57 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7318 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/04/2025 08:49:35 | 10/18/2025 15:53:55 | 10/18/2025 15:55:56 | 10/18/2025 15:55:59 | 10/18/2025 15:56:01 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000391 | PCM-20251004-00000666 | TT-20251004-00716 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/04/2025 10:00:50 | 10/04/2025 13:30:25 | 10/04/2025 16:00:50 | high temprature 32 at DAM2066-P1-HUB_SRAN @ Sceco | 10/04/2025 09:50:19 | Major | 65102 | high temprature 32 | 10/04/2025 09:50:16 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/04/2025 10:00:50 | 10/04/2025 13:30:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004000422 | PCM-20251004-00000710 | TT-20250929-02117 | MW_HC | Region_2 | MUK0190 | MUK0190 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Shahid Ahmed Shah Nawaz | 10/04/2025 10:25:00 | 10/04/2025 14:36:48 | 10/04/2025 22:25:00 | Huawei MW HC_P1 Observing Errors at QSDH0701-MUK0190 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P3 | SRAN | buraidah | Sceco | TX NSA | QSDH0701-MUK0190 | FLM_EM |  | Hub:- MUK0190 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251004-00000664 | Hub:- MUK0190 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- MUK0190 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/04/2025 10:25:00 | 10/04/2025 11:42:28 | 10/04/2025 14:36:31 |  |  | 10/04/2025 14:36:48 |  | Shahid Ahmed Shah Nawaz |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251004000477 | PCM-20251004-00000784 | TT-20251004-00827 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/04/2025 11:06:55 | 10/05/2025 14:37:13 | 10/04/2025 23:06:55 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/04/2025 10:56:18 | Minor | 65102 | high temprature 32 | 10/04/2025 10:56:14 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/04/2025 11:06:55 | 10/05/2025 14:37:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000537 | PCM-20251004-00000861 | TT-20251004-00758 | Reference_telecom | Region_2 | RIY0740 | RIY0740 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/04/2025 11:35:40 | 10/05/2025 20:48:29 | 10/04/2025 23:35:40 | IP PM Activation Failure at RIY0740-P2_SRAN @ Sceco | 10/04/2025 08:07:27 | Minor | 25900 | IP PM Activation Failure | 10/04/2025 10:02:53 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0740 | FLM_EM |  | Dear TX Team kindly check as alarm active with below details Name Alarm Source Last Occurred (NT) Location Information IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 10:02:53 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=232, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.32, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 10:02:53 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=231, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.31, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 10:02:53 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=230, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.30, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 10:02:53 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=21, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.30, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 10:02:53 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=20, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.29, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 07:23:34 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=233, Alarm Cause=Activation timeout, Peer IP Address=10.166.0.33, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 07:23:34 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=229, Alarm Cause=Activation timeout, Peer IP Address=10.166.0.29, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 07:23:34 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=24, Alarm Cause=Activation timeout, Peer IP Address=10.166.0.33, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 07:23:34 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=23, Alarm Cause=Activation timeout, Peer IP Address=10.166.0.32, Specific Problem=Uplink IP PM Activation Failure RIY0740-P2_SRAN 2025-10-04 07:23:34 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=22, Alarm Cause=Activation timeout, Peer IP Address=10.166.0.31, Specific Problem=Uplink | PCM-20251004-00000767 | Suspected power issue at site RIY2376 | Suspected power issue at site RIY2376 |  |  |  | API | 10/04/2025 11:35:40 | 10/05/2025 20:48:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004000614 | PCM-20251004-00001000 | TT-20251004-00303 | Reference_EM | Region_1 | HFF2780 | HFF2780 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Amr Ahmed Gouda | 10/04/2025 12:27:25 | 10/07/2025 20:07:40 | 10/05/2025 00:27:25 | Mains Failure at HFF2780-P3_SRAN-PC @ Sceco | 10/04/2025 04:47:44 | Minor | 65109 | Mains Failure | 10/04/2025 04:47:40 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF2780 | FLM_EM |  |  | PCM-20251004-00000354 | after Telecom team checking found alarm active due to power issue | after Telecom team checking found alarm active due to power issue |  |  |  | API | 10/04/2025 12:27:25 | 10/06/2025 15:59:49 | 10/07/2025 20:07:33 |  |  | 10/07/2025 20:07:40 |  | Amr Ahmed Gouda |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000618 | PCM-20251004-00001005 | TT-20251004-00985 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/04/2025 12:29:35 | 10/04/2025 13:30:25 | 10/05/2025 00:29:35 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/04/2025 12:19:09 | Minor | 65102 | High temperature 32C alarm | 10/04/2025 12:19:07 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/04/2025 12:29:35 | 10/04/2025 13:30:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251004000639 | PCM-20251004-00001040 | TT-20251004-01018 | EM | Region_1 | DAM0229 | DAM0229 |  |  |  | Yasser Mohamed Abdelnabi Ibrahim | 10/04/2025 12:52:50 | 10/04/2025 13:49:11 | 10/04/2025 16:52:50 | AMBIENT_TEMP_FLUCT at DAM0229_HYB @ Sceco | 10/04/2025 12:50:52 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/04/2025 12:50:47 | P1 | SRAN | dammam | Sceco | DWDM NSA | DAM0229 | FLM_EM | [5 empty] | 1-TO DAM0278(1-B) |  |  | API | 10/04/2025 12:52:50 |  | 10/04/2025 13:48:56 | 10/04/2025 13:49:00 | 10/04/2025 13:49:11 | [6 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251004000650 | PCM-20251004-00001056 | TT-20251004-01035 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/04/2025 13:05:45 | 10/04/2025 22:32:01 | 10/05/2025 01:05:45 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/04/2025 12:57:08 | Minor | 7103 | AIRCON 1 FAILURE | 10/04/2025 12:56:59 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/04/2025 13:05:45 | 10/04/2025 22:32:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000687 | PCM-20251004-00001109 | TT-20251004-00421 | Reference_telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/04/2025 13:42:50 | 10/04/2025 13:45:43 | 10/05/2025 01:42:50 | NCE MW Observing Visibility Issue on 2 Nes under DAM2066_NE_1_V Cluster DRN0129 | 10/02/2025 21:27:46 | Minor | 2 | NE_NOT_LOGIN | 10/02/2025 21:27:46 | P1 | SRAN | dammam | Sceco | TX NSA | DAM2066_NE_1_V DAM2066_NE_2_H | FLM_EM |  |  | PCM-20251004-00000375 | site has access issuePCM escalated to EM domain till fixed access issue | site has access issuePCM escalated to EM domain till fixed access issue |  |  |  | API | 10/04/2025 13:42:50 | 10/04/2025 13:45:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000707 | PCM-20251004-00001139 | TT-20251004-01128 | EM | Region_4 | JED2125 | JED2125 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/04/2025 14:02:00 | 10/04/2025 15:58:48 | 10/05/2025 02:02:00 | RECTIFIER MAJOR at JED2125-CA-L800-NR2.6-SBTS -P3 @ Sceco | 10/04/2025 13:53:33 | Minor | 7103 | RECTIFIER MAJOR | 10/04/2025 13:53:25 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2125 | FLM_EM | [5 empty] | RECTIFIER MAJOR |  |  | API | 10/04/2025 14:02:00 | 10/04/2025 15:58:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000746 | PCM-20251004-00001207 | TT-20251004-01196 | EM | Region_4 | JED0200 | JED0200 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/04/2025 14:31:00 | 10/04/2025 15:58:49 | 10/05/2025 02:31:00 | HIGH TEMPERATURE 32 DEGREE C at JED0200-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/04/2025 14:22:15 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/04/2025 14:22:11 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0200 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/04/2025 14:31:00 | 10/04/2025 15:58:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000787 | PCM-20251004-00001270 | TT-20251004-01206 | Reference_telecom | Region_2 | RIY0222 | RIY0222 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/04/2025 14:56:35 | 10/05/2025 14:32:13 | 10/05/2025 02:56:35 | IP PM Activation Failure at RIYA6041-P3_SRAN @ Sceco | 10/04/2025 11:40:18 | Minor | 25900 | IP PM Activation Failure | 10/04/2025 11:32:17 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIYA6041 | FLM_EM |  | Dear TX Team kindly check as alarm active on site Name Alarm Source Last Occurred (NT) Location Information IP PM Activation Failure RIYA6041-P3_SRAN 2025-10-04 11:32:17 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=24, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.33, Specific Problem=Uplink IP PM Activation Failure RIYA6041-P3_SRAN 2025-10-04 11:32:17 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=23, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.32, Specific Problem=Uplink IP PM Activation Failure RIYA6041-P3_SRAN 2025-10-04 11:32:17 Cabinet No.=0, Subrack No.=0, Slot No.=7, Session ID=20, Alarm Cause=long-time without BR frame received, Peer IP Address=10.166.0.29, Specific Problem=Uplink | PCM-20251004-00001260 | suspected power issue at hub site | suspected power issue at hub site |  |  |  | API | 10/04/2025 14:56:35 | 10/05/2025 14:32:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251004000920 | PCM-20251004-00001471 | TT-20251004-01373 | Reference_telecom | Region_2 | RYRN0767 | RYRN0767 | Enviroment | SCECO_Failure | SCECO auto restored | Saleem Khan Amir Dost | 10/04/2025 16:34:20 | 10/06/2025 19:45:26 | 10/05/2025 04:34:20 | IP Clock Link Failure at RYRN2M5761-P3 @ Sceco | 10/04/2025 12:45:52 | Minor | 26263 | IP Clock Link Failure | 10/04/2025 12:45:39 | P2 | SRAN | quweyah | Sceco | 2G NSA | RYRN2M5761 | FLM_EM |  | Dear TX Team kindly check as IP CLK unavailable DSP BTSIPCLK Link Status Result ------------------------------- Port No. Client IP Server IP Link State Active State NULL 10.118.0.241 10.161.136.17 Unavailable Activated NULL 10.118.0.241 10.161.137.17 Unavailable Not Activated | PCM-20251004-00001445 | Suspected power issue at hub site | Suspected power issue at hub site |  |  |  | API | 10/04/2025 16:34:20 | 10/04/2025 18:32:50 | 10/06/2025 19:45:20 |  |  | 10/06/2025 19:45:26 |  | Saleem Khan Amir Dost |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004000921 | PCM-20251004-00001472 | TT-20251004-01369 | Reference_telecom | Region_2 | RYRN0767 | RYRN0767 |  |  |  | Saleem Khan Amir Dost | 10/04/2025 16:34:30 | 10/04/2025 18:32:51 | 10/05/2025 04:34:30 | IP Clock Link Failure at RYRN2M5764-P3 @ Sceco | 10/04/2025 12:44:54 | Minor | 26263 | IP Clock Link Failure | 10/04/2025 12:44:41 | P2 | SRAN | quweyah | Sceco | 2G NSA | RYRN2M5764 | FLM_EM |  | Dear TX Team kindly check as IP CLK unavailable DSP BTSIPCLK Link Status Result ------------------------------- Port No. Client IP Server IP Link State Active State NULL 10.118.0.242 10.161.136.17 Unavailable Activated NULL 10.118.0.242 10.161.137.17 Unavailable Not Activated | PCM-20251004-00001438 | Suspected power issue at hub site | Suspected power issue at hub site |  |  |  | API | 10/04/2025 16:34:30 | 10/04/2025 18:32:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004000936 | PCM-20251004-00001501 | TT-20251004-01490 | EM | Region_4 | YLM0789 | YLM0789 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Karim Hamdy Mohamed Elashry | 10/04/2025 16:47:20 | 10/05/2025 09:56:22 | 10/05/2025 04:47:20 | RECTIFIER MAINS POWER FAILURE at YLM0789-GSM-UMTS-P3 @ Generator_SG | 10/04/2025 16:38:47 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/04/2025 16:38:39 | P3 | 2G | alaith | Generator_SG | 2G NSA | YLM0789 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/04/2025 16:47:20 | 10/05/2025 07:58:37 | 10/05/2025 09:56:13 |  |  | 10/05/2025 09:56:22 |  | Karim Hamdy Mohamed Elashry |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004001014 | PCM-20251004-00001627 | TT-20251004-01481 | Telecom | Region_2 | RIY0969 | RIY0969 |  |  |  | Adham Adham Hassan Farghal | 10/04/2025 17:53:30 | 10/05/2025 09:12:58 | 10/05/2025 05:53:30 | BO need to do HC For site RIY0969 | 10/04/2025 16:40:00 | Minor | 676767672 | Health Check-WO to TE FME | 10/04/2025 16:40:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0969 | FLM_EM |  |  | PCM-20251004-00001510 | power issue at site please check | power issue at site please check |  |  |  | API | 10/04/2025 17:53:30 | 10/05/2025 09:12:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004001062 | PCM-20251004-00001702 | TT-20251004-01653 | Reference_telecom | Region_2 | RYQ0972 | RYQ0972 | Equipment | BSS_HW_fault | Replace Controller Card | Mahmoud Hefny Ali Ahmed | 10/04/2025 18:24:46 | 10/13/2025 10:55:55 | 10/05/2025 06:24:46 | IP Link Performance Measurement Fault at RYQ0955-P2_SRAN @ Generator_DG | 10/04/2025 11:41:49 | Minor | 25904 | IP Link Performance Measurement Fault | 10/04/2025 11:41:17 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0955 | FLM_EM |  |  | PCM-20251004-00001694 | power issue at RYQ0972 | power issue at RYQ0972 |  |  |  | API | 10/04/2025 18:24:46 | 10/05/2025 20:23:10 | 10/10/2025 17:20:34 | 10/13/2025 10:55:23 |  | 10/13/2025 10:55:55 |  | Mahmoud Hefny Ali Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251004001107 | PCM-20251004-00001767 | TT-20251004-01745 | Reference_EM | Region_1 | KBR0608 | KBR0608 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/04/2025 19:27:30 | 10/05/2025 12:11:04 | 10/05/2025 07:27:30 | NETECO: Communication Failure at KBR0608 @ Sceco | 10/04/2025 16:07:57 | Minor | 9354 | Communication Failure | 10/04/2025 16:07:57 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0608 | FLM_EM | [8 empty] | API | 10/04/2025 19:27:30 | 10/05/2025 10:51:42 | 10/05/2025 12:10:40 | 10/05/2025 12:11:02 | 10/05/2025 12:11:04 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251004001162 | PCM-20251004-00001880 | TT-20251004-01864 | EM | Region_4 | JED2929 | JED2929 | Enviroment | SCECO_Failure | SCECO auto restored | Amer Attallah Awadallah | 10/04/2025 20:51:10 | 10/04/2025 23:52:57 | 10/05/2025 08:51:10 | RECTIFIER MODULE FAILURE at JED2929-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2-USF @ Sceco | 10/04/2025 20:42:37 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/04/2025 20:42:25 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2929 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/04/2025 20:51:10 | 10/04/2025 21:29:42 | 10/04/2025 21:47:49 | 10/04/2025 21:48:00 | 10/04/2025 22:26:24 | 10/04/2025 23:52:57 |  | Amer Attallah Awadallah |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251004001190 | PCM-20251004-00001915 | TT-20251004-01927 | EM | Region_4 | JED0430 | JED0430 |  |  |  | Sajid Nazir Muhammad Nazir | 10/04/2025 21:27:50 | 10/04/2025 22:29:47 | 10/05/2025 09:27:50 | COMMERCIAL POWER FAILURE at JED0430-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/04/2025 21:19:34 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/04/2025 21:19:29 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0430 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/04/2025 21:27:50 | 10/04/2025 22:29:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251005000038 | PCM-20251005-00000057 | TT-20251005-00063 | EM | Region_4 | JED0778 | JED0778 | Enviroment | Rectifier Module | Adding module due to load issue | Amr Sherif Gabber Ahmed | 10/05/2025 00:21:55 | 10/07/2025 13:54:00 | 10/05/2025 06:21:55 | RECTIFIER MODULE FAILURE at JED1M7778-CA-L800-P1-VIP-SBTS @ Generator_SG | 10/05/2025 00:13:38 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/05/2025 00:13:28 | VIP | 4G | jeddah | Generator_SG | LTE NSA | JED1M7778 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/05/2025 00:21:55 | 10/05/2025 00:54:46 | 10/07/2025 13:53:33 |  |  | 10/07/2025 13:54:00 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000097 | PCM-20251005-00000722 | TT-20251005-00768 | Reference_EM | Region_2 | RIY0621 | RIY0621 |  |  |  | Pawan Virdi Santokh Singh | 10/05/2025 01:48:16 | 10/05/2025 21:45:40 | 10/05/2025 13:48:16 | Air condition 2 failure alarm at RIY0621-P2_SRAN @ Sceco | 10/05/2025 01:37:49 | Minor | 65105 | Air condition 2 failure alarm | 10/05/2025 01:37:47 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0621 | FLM_EM | [8 empty] | API | 10/05/2025 01:48:16 | 10/05/2025 21:45:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000133 | PCM-20251005-00000787 | TT-20251005-00842 | EM | Region_6 | TRB0269 | TRB0269 |  |  |  | Javad Qadir Bukhsh | 10/05/2025 02:49:11 | 10/15/2025 11:51:49 | 10/05/2025 14:49:11 | AIRCON 1 FAILURE at TRB1M7269-G9-L18-SBTS-P3 @ Sceco | 10/05/2025 02:41:58 | Minor | 7103 | AIRCON 1 FAILURE | 10/05/2025 02:40:26 | P3 | 4G | turaib | Sceco | LTE NSA | TRB1M7269 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/05/2025 02:49:11 | 10/05/2025 06:58:33 | [6 empty] | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251005000135 | PCM-20251005-00000789 | TT-20251005-00843 | EM | Region_6 | KHS0343 | KHS0343 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ezat Mohammed | 10/05/2025 02:49:46 | 10/17/2025 20:48:33 | 10/05/2025 14:49:46 | LOW FUEL at KHS1M7343-P2-USF-L900 @ Sceco_STB | 10/05/2025 02:41:43 | Minor | 7103 | LOW FUEL | 10/05/2025 02:41:17 | P2 | 4G | khamis mushyet | Sceco_STB | LTE NSA | KHS1M7343 | FLM_EM | [5 empty] | LOW FUEL |  |  | API | 10/05/2025 02:49:46 |  | 10/17/2025 20:48:27 |  |  | 10/17/2025 20:48:33 |  | Ezat Mohammed | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251005000321 | PCM-20251005-00001059 | TT-20251005-01166 | EM | Region_1 | RYDM2239 | RYDM2239 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Amr Ahmed Gouda | 10/05/2025 05:02:00 | 10/07/2025 20:07:01 | 10/05/2025 17:02:00 | Mains Failure at RYDM2239-P3_SRAN @ Sceco | 10/05/2025 04:51:52 | Minor | 65109 | Mains Failure | 10/05/2025 04:51:49 | P3 | SRAN | hafouf | Sceco | 2G NSA | RYDM2239 | FLM_EM | [8 empty] | API | 10/05/2025 05:02:00 | 10/06/2025 15:59:51 | 10/07/2025 20:06:53 |  |  | 10/07/2025 20:07:01 |  | Amr Ahmed Gouda |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000334 | PCM-20251005-00001090 | TT-20251005-01209 | EM | Region_4 | JED0355 | JED0355 |  |  |  | Ahmed Gamal Mohamed Farag | 10/05/2025 05:30:55 | 10/06/2025 00:10:05 | 10/05/2025 17:30:55 | AIRCON 1 FAILURE at JED1M7355-CA-L900-L800-SBTS @ Sceco | 10/05/2025 05:22:37 | Minor | 7103 | AIRCON 1 FAILURE | 10/05/2025 05:22:28 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7355 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/05/2025 05:30:55 | 10/06/2025 00:10:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000393 | PCM-20251005-00001180 | TT-20251005-01312 | EM | Region_4 | TAF2104 | TAF2104 |  |  |  | Walid Magdy Tawfik Elbana | 10/05/2025 06:53:05 | 10/05/2025 08:21:15 | 10/05/2025 18:53:05 | DOOR OPEN at TAF2104-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/05/2025 06:52:35 | Minor | 7103 | DOOR OPEN | 10/05/2025 06:52:28 | P3 | 2G | taif | Sceco | 2G NSA | TAF2104 | FLM_EM | [5 empty] | DOOR OPEN |  |  | API | 10/05/2025 06:53:05 | 10/05/2025 08:21:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251005000417 | PCM-20251005-00001225 | TT-20251005-01363 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_loop | Remote action done by BO by removing VLAN loop | Abd EL Azeez EL Sayed Soliman | 10/05/2025 07:29:45 | 10/05/2025 12:31:25 | 10/05/2025 19:29:45 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8333-P3-CA-L800 @ Generator_SG | 10/05/2025 07:21:41 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/05/2025 07:21:11 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/05/2025 07:29:45 | 10/05/2025 12:30:27 | 10/05/2025 12:31:06 |  |  | 10/05/2025 12:31:25 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000433 | PCM-20251005-00001255 | TT-20251005-01389 | EM | Region_4 | TUR0693 | TUR0693 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/05/2025 07:54:30 | 10/05/2025 09:36:36 | 10/05/2025 19:54:30 | RECTIFIER MAINS POWER FAILURE at TUR0693-GSM-P2 @ Sceco | 10/05/2025 07:46:19 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/05/2025 07:46:11 | P2 | 2G | taif | Sceco | 2G NSA | TUR0693 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/05/2025 07:54:30 | 10/05/2025 09:36:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000533 | PCM-20251005-00001417 | TT-20251005-01516 | EM | Region_4 | TAF0268 | TAF0268 |  |  |  | Walid Magdy Tawfik Elbana | 10/05/2025 09:22:20 | 10/05/2025 09:47:37 | 10/05/2025 21:22:20 | AIRCON 1 FAILURE at TAF0268-GSM-P3 @ Sceco | 10/05/2025 09:13:47 | Minor | 7103 | AIRCON 1 FAILURE | 10/05/2025 09:13:39 | P3 | 2G | taif | Sceco | 2G NSA | TAF0268 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/05/2025 09:22:20 | 10/05/2025 09:47:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000585 | PCM-20251005-00001489 | TT-20251005-01569 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/05/2025 09:46:40 | 10/06/2025 01:26:01 | 10/05/2025 21:46:40 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/05/2025 09:36:16 | Minor | 65102 | high temprature 32 | 10/05/2025 09:36:12 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/05/2025 09:46:40 | 10/06/2025 01:26:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251005000634 | PCM-20251005-00001573 | TT-20251004-01908 | Telecom | Region_2 | RIY0496 | RIY0496 | Equipment | SFP_BTS | Replace SFP | Farmanullah Akbar Jan | 10/05/2025 10:20:40 | 10/06/2025 09:47:32 | 10/05/2025 22:20:40 | RF Unit Maintenance Link Failure at RIY0496-P2_SRAN @ Sceco | 10/04/2025 21:03:06 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/04/2025 21:01:24 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0496 | FLM_EM |  |  | PCM-20251004-00001893 | high temp at site and access issue ARAMCO | high temp at site and access issue ARAMCO |  |  |  | API | 10/05/2025 10:20:40 | 10/06/2025 09:34:56 | 10/06/2025 09:41:45 | 10/06/2025 09:41:48 | 10/06/2025 09:46:27 | 10/06/2025 09:47:32 |  | Farmanullah Akbar Jan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251005000636 | PCM-20251005-00001579 | TT-20251004-01911 | Telecom | Region_2 | RIY0496 | RIY0496 | Equipment | SFP_BTS | Replace SFP | Farmanullah Akbar Jan | 10/05/2025 10:21:40 | 10/06/2025 09:41:33 | 10/05/2025 22:21:40 | BBU CPRI Optical Module Fault at RIY0496-P2_SRAN @ Sceco | 10/04/2025 21:03:47 | Minor | 26230 | BBU CPRI Optical Module Fault | 10/04/2025 21:02:15 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0496 | FLM_EM |  |  | PCM-20251004-00001895 | high temp at site and access issue ARAMCO | high temp at site and access issue ARAMCO |  |  |  | API | 10/05/2025 10:21:40 | 10/06/2025 09:34:55 | 10/06/2025 09:40:45 | 10/06/2025 09:40:49 | 10/06/2025 09:40:53 | 10/06/2025 09:41:33 |  | Farmanullah Akbar Jan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000819 | PCM-20251005-00001856 | TT-20251005-01850 | EM | Region_4 | JED0156 | JED0156 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/05/2025 12:00:25 | 10/06/2025 13:21:19 | 10/06/2025 00:00:25 | RECTIFIER MAINS POWER FAILURE at JED1MN0156-NR2.6-P2 @ Sceco | 10/05/2025 11:52:06 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/05/2025 11:51:57 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0156 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/05/2025 12:00:25 | 10/06/2025 13:21:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000862 | PCM-20251005-00001927 | TT-20251005-01915 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/05/2025 12:31:55 | 10/05/2025 19:07:27 | 10/06/2025 00:31:55 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/05/2025 12:21:27 | Minor | 65102 | High temperature 32C alarm | 10/05/2025 12:21:25 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/05/2025 12:31:55 | 10/05/2025 19:07:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251005000869 | PCM-20251005-00001947 | TT-20251005-01930 | Reference_EM | Region_1 | ARR0919 | ARR0919 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Ismail Salah Ismail Elbery | 10/05/2025 12:41:15 | 10/06/2025 18:39:28 | 10/05/2025 18:41:15 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/05/2025 12:30:59 | Major | 65110 | Low battery voltage | 10/05/2025 12:30:55 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/05/2025 12:41:15 | 10/06/2025 13:22:52 | 10/06/2025 18:39:17 | 10/06/2025 18:39:19 |  | 10/06/2025 18:39:28 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251005000885 | PCM-20251005-00001967 | TT-20251005-01952 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/05/2025 12:54:40 | 10/05/2025 19:07:28 | 10/05/2025 18:54:40 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/05/2025 12:44:14 | Major | 65110 | Low battery voltage | 10/05/2025 12:44:11 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/05/2025 12:54:40 | 10/05/2025 19:07:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005000896 | PCM-20251005-00001989 | TT-20251005-01973 | Reference_EM | Region_2 | RIY2037 | RIY2037 |  |  |  | Pawan Virdi Santokh Singh | 10/05/2025 13:08:06 | 10/05/2025 21:45:40 | 10/06/2025 01:08:06 | DC power fail at RIY2037-P2_SRAN @ Sceco | 10/05/2025 12:57:45 | Minor | 65106 | DC power fail | 10/05/2025 12:57:42 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2037 | FLM_EM | [8 empty] | API | 10/05/2025 13:08:06 | 10/05/2025 21:45:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251005001038 | PCM-20251005-00002226 | TT-20251005-02195 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/05/2025 15:11:05 | 10/05/2025 15:50:47 | 10/06/2025 03:11:05 | high temprature 40 at KBR0166-P3_SRAN @ Sceco | 10/05/2025 15:00:26 | Minor | 65103 | high temprature 40 | 10/05/2025 15:00:22 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/05/2025 15:11:05 | 10/05/2025 15:50:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251005001077 | PCM-20251005-00002281 | TT-20251005-02255 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/05/2025 15:32:45 | 10/06/2025 18:39:53 | 10/06/2025 03:32:45 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/05/2025 15:26:00 | Minor | 40564 | Genset Fault | 10/05/2025 15:26:00 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/05/2025 15:32:45 | 10/06/2025 13:22:59 | 10/06/2025 18:39:45 |  |  | 10/06/2025 18:39:53 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005001087 | PCM-20251005-00002300 | TT-20251005-02275 | EM | Region_6 | JEC0088 | JEC0088 |  |  |  | Fizan Ahmed | 10/05/2025 15:46:15 | 10/10/2025 12:30:19 | 10/06/2025 03:46:15 | AIRCON 2 FAILURE at JEC1M7088-G9-L18-L21-SBTS-P2 @ Sceco_STB | 10/05/2025 15:37:55 | Minor | 7103 | AIRCON 2 FAILURE | 10/05/2025 15:37:49 | VIP | 4G | baish | Sceco_STB | LTE NSA | JEC1M7088 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/05/2025 15:46:15 | 10/10/2025 12:30:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251005001090 | PCM-20251005-00002304 | TT-20251005-02279 | EM | Region_4 | NNL0176 | NNL0176 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/05/2025 15:48:50 | 10/06/2025 08:27:46 | 10/06/2025 03:48:50 | RECTIFIER MODULE FAILURE at NNL0176-GSM-UMTS-P3 @ Generator_SG | 10/05/2025 15:40:29 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/05/2025 15:40:17 | P3 | 2G | qunfuddah | Generator_SG | 2G NSA | NNL0176 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/05/2025 15:48:50 | 10/06/2025 08:27:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251005001487 | PCM-20251005-00002953 | TT-20251005-02896 | Telecom | Region_2 | RYQS0584 | RYQS0584 |  |  |  | Ahmed Mahmoud Mohamed Mahmoud | 10/05/2025 23:36:35 | 10/05/2025 23:36:35 | 10/06/2025 05:36:35 | IS-IS Adjacency Changed at ZLF-C-0510-LL-CSG-01 to MJM-C-0495-LL-CSG-01 | 10/05/2025 22:51:35 | Major | 15269 | LOS | 10/05/2025 22:51:35 | P2 | SRAN | majma | Generator_DG | IPRAN NSA | MJM-C-0495-LL-CSG-01 | FLM_EM |  | Dear Team, Hub:- RYQS0584 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | PCM-20251005-00002950 | Dear Team, Hub:- RYQS0584 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | Dear Team, Hub:- RYQS0584 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. |  |  |  | API | 10/05/2025 23:36:35 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251005001493 | PCM-20251005-00002969 | TT-20251005-01533 | Reference_telecom | Region_2 | RYQS0586 | RYQS0586 |  |  |  | Ibrahim Abdou Ibrahim Abdou | 10/05/2025 23:55:00 | 10/06/2025 22:25:58 | 10/06/2025 03:55:00 | IP PM Activation Failure at R2_RY1_HWBSC01 @ Sceco_STB | 10/05/2025 06:31:59 | Critical | 21341 | IP PM Activation Failure | 10/05/2025 06:31:17 | P2 | SRAN | buraidah | Generator_SG | 2G NSA | R2_RY1_HWBSC01 | FLM_EM |  | Dear TRM BO,IPRAN, pls. check if any abnormality related to site RYQS0586-P2_SRAN, the site reported many transport alarms like BFD fault , TWAMP , IPPM , SCTP link ,S1 alarms , also reported DSCP mismatch alarn as shown below. pls. check and confirm QOS configuration for 2G service from your side. BTS Name=RYQS2M1586-P2 IP address of the Site end=10.116.2.238, IP address of the BSC end=10.131.192.89, Alarm Cause=DSCP mismatch , source DSCP=38,, Remarked DSCP=34, | PCM-20251005-00002962 | Suspected power issue at site | Suspected power issue at site |  |  |  | API | 10/05/2025 23:55:00 | 10/06/2025 22:25:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251006000046 | PCM-20251006-00000093 | TT-20251006-00098 | EM | Region_4 | MKJD0239 | MKJD0239 |  |  |  | AbdAllah Mohammad abd Elgawad Fath Elbab | 10/06/2025 01:26:20 | 10/06/2025 12:42:55 | 10/06/2025 13:26:20 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at MKJD1M7239-SBTS-CA-P3 @ Generator_SG | 10/06/2025 01:19:46 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/06/2025 01:17:47 | P2 | 4G | jeddah | Generator_SG | LTE NSA | MKJD1M7239 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/06/2025 01:26:20 | 10/06/2025 12:42:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000050 | PCM-20251006-00000103 | TT-20251006-00105 | Reference_EM | Region_1 | YBR0613 | YBR0613 |  |  |  | Montasir Awadalla Abdalla Bala | 10/06/2025 01:32:31 | 10/06/2025 12:19:25 | 10/06/2025 13:32:31 | Air condition 1 failure alarm at YBR0613-P2-USF_SRAN-PC @ Power Cube | 10/06/2025 01:22:07 | Minor | 65104 | Air condition 1 failure alarm | 10/06/2025 01:22:04 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0613 | FLM_EM | [8 empty] | API | 10/06/2025 01:32:31 | 10/06/2025 12:19:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251006000062 | PCM-20251006-00000125 | TT-20251006-00132 | EM | Region_1 | DMH0108 | DMH0108 | Equipment | Power Cable_RRU_BTS | Replace DCDU Fuse | Mahmoud Youssef Mohamed Ahmed | 10/06/2025 01:54:15 | 10/06/2025 08:04:12 | 10/06/2025 07:54:15 | Mains Failure at DMH0108-P1-HUB_SRAN @ Generator_DG | 10/06/2025 01:44:16 | Major | 65109 | Mains Failure | 10/06/2025 01:44:14 | P1 | SRAN | hafr | Generator_DG | 2G NSA | DMH0108 | FLM_EM | [8 empty] | API | 10/06/2025 01:54:15 | 10/06/2025 02:18:29 | 10/06/2025 02:55:46 | 10/06/2025 02:55:49 | 10/06/2025 02:55:51 | 10/06/2025 08:04:12 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000066 | PCM-20251006-00000129 | TT-20251006-00135 | EM | Region_4 | JED0153 | JED0153 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/06/2025 01:56:45 | 10/06/2025 13:32:49 | 10/06/2025 13:56:45 | COMMERCIAL POWER FAILURE at JED1M7153-CA-L900-L800-SBTS-P3 @ Sceco | 10/06/2025 01:48:04 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/06/2025 01:48:12 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7153 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/06/2025 01:56:45 | 10/06/2025 13:32:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000091 | PCM-20251006-00000172 | TT-20251006-00194 | EM | Region_6 | KMS0164 | KMS0164 |  |  |  | Amir Abbas Arif Raza | 10/06/2025 02:39:42 | 10/08/2025 11:10:50 | 10/06/2025 14:39:42 | AIRCON 1 FAILURE at KMS0164-P3 @ Sceco | 10/06/2025 02:31:09 | Minor | 7103 | AIRCON 1 FAILURE | 10/06/2025 02:31:03 | P3 | 2G | khamis mushyet | Sceco | 2G NSA | KMS0164 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/06/2025 02:39:42 | 10/06/2025 11:44:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000093 | PCM-20251006-00000175 | TT-20251006-00195 | EM | Region_6 | KHS0693 | KHS0693 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/06/2025 02:42:16 | 10/06/2025 13:52:05 | 10/06/2025 14:42:16 | AIRCON 1 FAILURE at KHS1M7693-G9-L9-L18-SBTS-P2 @ Generator_SG | 10/06/2025 02:34:45 | Minor | 7103 | AIRCON 1 FAILURE | 10/06/2025 02:33:33 | P2 | 4G | khamis mushyet | Generator_SG | LTE NSA | KHS1M7693 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/06/2025 02:42:16 | 10/06/2025 13:52:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000137 | PCM-20251006-00000286 | TT-20251006-00345 | EM | Region_6 | ARF0761 | ARF0761 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/06/2025 03:45:20 | 10/06/2025 13:52:07 | 10/06/2025 15:45:20 | AIRCON 1 FAILURE at ARF0761-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/06/2025 03:38:11 | Minor | 7103 | AIRCON 1 FAILURE | 10/06/2025 03:36:52 | P2 | 2G | khamis mushyet | Sceco | 2G NSA | ARF0761 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/06/2025 03:45:20 | 10/06/2025 13:52:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000161 | PCM-20251006-00000334 | TT-20251006-00398 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/06/2025 04:15:47 | 10/06/2025 21:40:49 | 10/06/2025 16:15:47 | Generator failure at SMN0805-P3_SRAN @ Generator_DG | 10/06/2025 04:07:49 | Minor | 65114 | Generator failure | 10/06/2025 04:05:17 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/06/2025 04:15:47 | 10/06/2025 21:40:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000217 | PCM-20251006-00000435 | TT-20251006-00623 | EM | Region_1 | SMN0806 | SMN0806 |  |  |  | Rahman Ullah Said Halim | 10/06/2025 06:13:01 | 10/06/2025 21:40:50 | 10/06/2025 18:13:01 | Genset not in auto mode at SMN0806-P2_SRAN @ Generator_DG | 10/06/2025 06:10:48 | Minor | 65113 | Genset not in auto mode | 10/06/2025 05:50:52 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/06/2025 06:13:01 | 10/06/2025 21:40:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251006000231 | PCM-20251006-00000461 | TT-20251006-00654 | EM | Region_4 | RNRY0835 | RNRY0835 |  |  |  | Mohamed Elsaid Abdou Younes | 10/06/2025 06:30:36 | 10/08/2025 06:26:11 | 10/06/2025 18:30:36 | AIRCON 1 FAILURE at RNRY0835-GSM-P3 @ Sceco | 10/06/2025 06:22:13 | Minor | 7103 | AIRCON 1 FAILURE | 10/06/2025 06:22:08 | P3 | 2G | taif | Sceco | 2G NSA | RNRY0835 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/06/2025 06:30:36 | 10/08/2025 06:26:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000286 | PCM-20251006-00000548 | TT-20251006-00748 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/06/2025 07:40:17 | 10/06/2025 11:29:53 | 10/06/2025 19:40:17 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/06/2025 07:29:44 | Minor | 65102 | high temprature 32 | 10/06/2025 07:29:41 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/06/2025 07:40:17 | 10/06/2025 11:29:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251006000298 | PCM-20251006-00000572 | TT-20251006-00767 | EM | Region_4 | TUR0693 | TUR0693 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 10/06/2025 07:54:41 | 10/09/2025 08:17:36 | 10/06/2025 19:54:41 | RECTIFIER MAINS POWER FAILURE at TUR0693-GSM-P2 @ Sceco | 10/06/2025 07:46:10 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/06/2025 07:46:03 | P2 | 2G | taif | Sceco | 2G NSA | TUR0693 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/06/2025 07:54:41 | 10/06/2025 14:46:41 | 10/09/2025 08:17:26 |  |  | 10/09/2025 08:17:36 |  | Afzal Hussain Anwar Ul Haq |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251006000396 | PCM-20251006-00000734 | TT-20251006-00910 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/06/2025 09:11:10 | 10/06/2025 12:15:36 | 10/06/2025 21:11:10 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/06/2025 09:04:25 | Minor | 40564 | Genset Fault | 10/06/2025 09:04:25 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/06/2025 09:11:10 | 10/06/2025 09:25:23 | 10/06/2025 12:14:39 |  |  | 10/06/2025 12:15:36 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251006000403 | PCM-20251006-00000744 | TT-20251006-00914 | EM | Region_4 | KMMD0721 | KMMD0721 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/06/2025 09:15:20 | 10/06/2025 09:39:57 | 10/06/2025 15:15:20 | AIRCON 2 at KMMD0721-GSM-P1-HUB @ Sceco | 10/06/2025 09:06:57 | Major | 7103 | AIRCON 2 | 10/06/2025 09:06:49 | P1 | 2G | jeddah | Sceco | 2G NSA | KMMD0721 | FLM_EM | [5 empty] | AIRCON 2 |  |  | API | 10/06/2025 09:15:20 | 10/06/2025 09:39:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251006000470 | PCM-20251006-00000848 | TT-20251006-01011 | EM | Region_1 | DRN0123 | DRN0123 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/06/2025 10:01:15 | 10/09/2025 22:53:27 | 10/06/2025 14:01:15 | AMBIENT_TEMP_FLUCT at DRN0123_OCS @ Sceco_STB | 10/06/2025 09:59:31 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/06/2025 09:59:26 | P1 | SRAN | dammam | Sceco_STB | DWDM NSA | DRN0123 | FLM_EM | [5 empty] | 1-LOCAL-2(2-B) |  |  | API | 10/06/2025 10:01:15 | 10/06/2025 15:01:15 | 10/08/2025 13:53:08 | 10/08/2025 13:53:11 |  | 10/09/2025 22:53:27 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251006000708 | PCM-20251006-00001214 | TT-20251006-01363 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/06/2025 12:51:10 | 10/06/2025 16:44:31 | 10/07/2025 00:51:10 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/06/2025 12:40:47 | Minor | 65102 | High temperature 32C alarm | 10/06/2025 12:40:46 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/06/2025 12:51:10 | 10/06/2025 16:44:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251006000717 | PCM-20251006-00001224 | TT-20251006-01373 | Reference_EM | Region_1 | ARR0919 | ARR0919 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ismail Salah Ismail Elbery | 10/06/2025 12:54:15 | 10/06/2025 18:40:16 | 10/06/2025 18:54:15 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/06/2025 12:43:38 | Major | 65110 | Low battery voltage | 10/06/2025 12:43:34 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/06/2025 12:54:15 | 10/06/2025 13:23:06 | 10/06/2025 18:40:09 |  |  | 10/06/2025 18:40:16 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251006000720 | PCM-20251006-00001229 | TT-20251006-01378 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/06/2025 12:55:50 | 10/07/2025 19:33:00 | 10/07/2025 00:55:50 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/06/2025 12:47:34 | Minor | 7103 | AIRCON 1 FAILURE | 10/06/2025 12:47:28 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/06/2025 12:55:50 | 10/07/2025 19:33:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000769 | PCM-20251006-00001313 | TT-20251006-01455 | EM | Region_6 | MHL0133 | MHL0133 |  |  |  | Zia Ur Rahamn | 10/06/2025 13:36:40 | 10/06/2025 16:44:53 | 10/07/2025 01:36:40 | AIRCON 2 FAILURE at MHL0133-GSM-P3 @ Sceco | 10/06/2025 13:28:04 | Minor | 7103 | AIRCON 2 FAILURE | 10/06/2025 13:27:53 | P3 | 2G | mohail | Sceco | 2G NSA | MHL0133 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/06/2025 13:36:40 | 10/06/2025 16:44:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006000859 | PCM-20251006-00001487 | TT-20251006-01602 | EM | Region_4 | JDRS0832 | JDRS0832 |  |  |  | Alaa Hassan Mohammed Gad | 10/06/2025 14:53:35 | 10/07/2025 19:33:01 | 10/07/2025 02:53:35 | AIRCON 2 FAILURE at JDRS1M7832-G9-L8-SBTS-P2 @ Generator_SG | 10/06/2025 14:45:08 | Minor | 7103 | AIRCON 2 FAILURE | 10/06/2025 14:44:59 | P2 | 4G | jeddah | Generator_SG | LTE NSA | JDRS1M7832 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/06/2025 14:53:35 | 10/07/2025 19:33:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251006000953 | PCM-20251006-00001637 | TT-20251006-01734 | Reference_EM | Region_1 | DAM0263 | DAM0263 | Enviroment | Rectifier Module | Change rectifer module | Gamal Hasan Farag Ali Khalifa | 10/06/2025 16:07:30 | 10/07/2025 19:21:22 | 10/07/2025 04:07:30 | Minor Rec alarm at DAM0263-P2_SRAN @ Sceco | 10/06/2025 15:57:09 | Minor | 65108 | Minor Rec alarm | 10/06/2025 15:57:06 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0263 | FLM_EM | [8 empty] | API | 10/06/2025 16:07:30 | 10/07/2025 18:08:40 | 10/07/2025 19:07:04 | 10/07/2025 19:07:06 | 10/07/2025 19:07:08 | 10/07/2025 19:21:22 |  | Gamal Hasan Farag Ali Khalifa |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251006000963 | PCM-20251006-00001652 | TT-20251006-01753 | EM | Region_1 | KFKM0783 | KFKM0783 | Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue | Abu Sufyan Mehfooz Ali | 10/06/2025 16:18:21 | 10/07/2025 15:08:29 | 10/06/2025 20:18:21 | AMBIENT_TEMP_FLUCT at KFKM0783_OCS @ Generator_SG | 10/06/2025 16:16:10 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/06/2025 16:16:04 | P3 | SRAN | khafji | Generator_SG | DWDM NSA | KFKM0783 | FLM_EM | [5 empty] | 1-(1-A) |  |  | API | 10/06/2025 16:18:21 | 10/06/2025 16:34:31 | 10/07/2025 15:07:56 |  |  | 10/07/2025 15:08:29 |  | Abu Sufyan Mehfooz Ali |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251006001161 | PCM-20251006-00001985 | TT-20251006-02084 | EM | Region_4 | JDRS0758 | JDRS0758 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/06/2025 19:30:00 | 10/07/2025 14:13:30 | 10/07/2025 07:30:00 | GENET RUNNING at JDRS0758-GSM-P3-USF @ Generator_DG | 10/06/2025 19:21:42 | Minor | 7103 | GENET RUNNING | 10/06/2025 19:21:37 | P3 | 2G | jeddah | Generator_DG | 2G NSA | JDRS0758 | FLM_EM | [5 empty] | GENET RUNNING |  |  | API | 10/06/2025 19:30:00 | 10/07/2025 14:13:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251006001236 | PCM-20251006-00002108 | TT-20251006-02192 | EM | Region_4 | JED0066 | JED0066 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/06/2025 21:06:05 | 10/07/2025 17:10:38 | 10/07/2025 09:06:05 | RECTIFIER MODULE FAILURE at JED1M7066-P3-CA-L900-L800-SBTS @ Sceco | 10/06/2025 20:57:36 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/06/2025 20:57:30 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7066 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/06/2025 21:06:05 | 10/07/2025 17:10:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006001314 | PCM-20251006-00002241 | TT-20251006-02326 | EM | Region_4 | JED0920 | JED0920 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/06/2025 22:41:40 | 10/07/2025 14:24:23 | 10/07/2025 04:41:40 | RECTIFIER MODULE FAILURE at JED1M7920-CA-L900-L800-SBTS-FWA-P1-VIP @ Sceco | 10/06/2025 22:33:13 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/06/2025 22:33:02 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7920 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/06/2025 22:41:40 | 10/07/2025 14:24:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251006001348 | PCM-20251006-00002304 | TT-20251006-02395 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/06/2025 23:37:55 | 10/07/2025 13:09:06 | 10/07/2025 05:37:55 | Air condition 1 failure alarm at DAM2066-P1-HUB_SRAN @ Sceco | 10/06/2025 23:27:16 | Major | 65104 | Air condition 1 failure alarm | 10/06/2025 23:27:12 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/06/2025 23:37:55 | 10/07/2025 13:09:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000015 | PCM-20251007-00000027 | TT-20251007-00021 | EM | Region_4 | BHR2989 | BHR2989 |  |  |  | Sajid Nazir Muhammad Nazir | 10/07/2025 00:17:15 | 10/07/2025 13:44:26 | 10/07/2025 12:17:15 | ALARM MAJOR at BHR2989-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/07/2025 00:08:40 | Minor | 7103 | ALARM MAJOR | 10/07/2025 00:08:35 | P3 | 2G | jeddah | Sceco | 2G NSA | BHR2989 | FLM_EM | [5 empty] | ALARM MAJOR |  |  | API | 10/07/2025 00:17:15 | 10/07/2025 13:44:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000069 | PCM-20251007-00000138 | TT-20251007-00156 | Reference_EM | Region_2 | RIY2789 | RIY2789 |  |  |  | Pawan Virdi Santokh Singh | 10/07/2025 01:44:31 | 10/07/2025 06:55:51 | 10/07/2025 13:44:31 | Low battery voltage at RIY2789-P2_SRAN @ Sceco | 10/07/2025 01:33:47 | Minor | 65110 | Low battery voltage | 10/07/2025 01:33:44 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2789 | FLM_EM | [8 empty] | API | 10/07/2025 01:44:31 | 10/07/2025 06:55:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000117 | PCM-20251007-00000244 | TT-20251007-00299 | EM | Region_6 | BSA0456 | BSA0456 |  |  |  | Asad Saddiq | 10/07/2025 03:02:54 | 10/15/2025 11:51:54 | 10/07/2025 15:02:54 | AIRCON 1 FAILURE at BSA1M7456-G9-NL8-SBTS-P3 @ Sceco | 10/07/2025 02:56:54 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 02:53:52 | P3 | 4G | bisha | Sceco | LTE NSA | BSA1M7456 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 03:02:54 | 10/07/2025 04:19:40 | [6 empty] | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000154 | PCM-20251007-00000315 | TT-20251007-00399 | EM | Region_6 | TNM0176 | TNM0176 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/07/2025 03:42:46 | 10/15/2025 11:52:02 | 10/07/2025 15:42:46 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at TNM0176-G9-L8-L18-NL21-NNR2.6-SBTS-P3 @ Sceco | 10/07/2025 03:34:34 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/07/2025 03:34:02 | P3 | 2G | namas | Sceco | 2G NSA | TNM0176 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/07/2025 03:42:46 | 10/11/2025 19:36:38 | [6 empty] | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000170 | PCM-20251007-00000349 | TT-20251007-00435 | EM | Region_6 | SBBG0045 | SBBG0045 |  |  |  | Khurram Nawaz Muhammad Akram | 10/07/2025 04:02:57 | 10/08/2025 11:10:53 | 10/07/2025 10:02:57 | AIRCON 1 FAILURE at SBBG1M7045-CA-L800-P1-VIP @ Sceco | 10/07/2025 03:56:20 | Major | 7103 | AIRCON 1 FAILURE | 10/07/2025 03:54:17 | VIP | 4G | jizan | Sceco | LTE NSA | SBBG1M7045 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 04:02:57 | 10/07/2025 04:46:41 | [6 empty] | Vandalism |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251007000207 | PCM-20251007-00000433 | TT-20251007-00537 | Reference_EM | Region_1 | DMBQ0073 | DMBQ0073 | Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator | Abdalla Nazmy Abdelfattah Ahmed | 10/07/2025 04:48:20 | 10/20/2025 16:51:40 | 10/07/2025 16:48:20 | Air-condition #2 failure alarm at DMBQ2M5073-P2 @ Generator_SG | 10/07/2025 04:38:06 | Minor | 65105 | Air-condition #2 failure alarm | 10/07/2025 04:38:04 | P2 | 2G | hafouf | Generator_SG | 2G NSA | DMBQ2M5073 | FLM_EM | [8 empty] | API | 10/07/2025 04:48:20 | 10/08/2025 14:00:42 | 10/20/2025 16:51:18 | 10/20/2025 16:51:21 |  | 10/20/2025 16:51:40 |  | Abdalla Nazmy Abdelfattah Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000242 | PCM-20251007-00000486 | TT-20251007-00566 | EM | Region_4 | JED0368 | JED0368 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/07/2025 05:20:55 | 10/07/2025 07:18:56 | 10/07/2025 17:20:55 | RECTIFIER MODULE FAILURE at JED0368-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/07/2025 05:13:00 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/07/2025 05:12:31 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0368 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/07/2025 05:20:55 | 10/07/2025 07:18:56 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251007000334 | PCM-20251007-00000648 | TT-20251007-00709 | EM | Region_4 | JED0647 | JED0647 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/07/2025 07:07:50 | 10/07/2025 07:07:50 | 10/07/2025 19:07:50 | COMMERCIAL POWER FAILURE at JED0647-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/07/2025 06:59:24 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/07/2025 06:59:19 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0647 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/07/2025 07:07:50 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000373 | PCM-20251007-00000721 | TT-20251007-00770 | EM | Region_4 | TUR0693 | TUR0693 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/07/2025 07:59:30 | 10/14/2025 09:01:50 | 10/07/2025 19:59:30 | RECTIFIER MAINS POWER FAILURE at TUR0693-GSM-P2 @ Sceco | 10/07/2025 07:51:15 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/07/2025 07:51:09 | P2 | 2G | taif | Sceco | 2G NSA | TUR0693 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/07/2025 07:59:30 | 10/14/2025 09:01:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000380 | PCM-20251007-00000731 | TT-20251007-00785 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/07/2025 08:05:06 | 10/09/2025 06:33:13 | 10/07/2025 20:05:06 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/07/2025 07:56:30 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/07/2025 07:56:23 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/07/2025 08:05:06 | 10/09/2025 06:33:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251007000387 | PCM-20251007-00000745 | TT-20251007-00796 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/07/2025 08:10:50 | 10/07/2025 13:25:00 | 10/07/2025 20:10:50 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/07/2025 08:02:35 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 08:02:27 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 08:10:50 | 10/07/2025 09:42:42 | 10/07/2025 13:24:50 |  |  | 10/07/2025 13:25:00 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000511 | PCM-20251007-00000964 | TT-20251007-01004 | EM | Region_1 | DAM0377 | DAM0377 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/07/2025 10:12:15 | 10/07/2025 18:07:21 | 10/07/2025 22:12:15 | high temprature 40 at DAM0377-P2_SRAN @ Sceco | 10/07/2025 10:03:47 | Minor | 65103 | high temprature 40 | 10/07/2025 10:01:37 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0377 | FLM_EM | [8 empty] | API | 10/07/2025 10:12:15 | 10/07/2025 18:07:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000519 | PCM-20251007-00000977 | TT-20251007-01021 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/07/2025 10:19:01 | 10/07/2025 10:35:20 | 10/07/2025 22:19:01 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/07/2025 10:08:25 | Minor | 65102 | high temprature 32 | 10/07/2025 10:08:22 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/07/2025 10:19:01 | 10/07/2025 10:35:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000567 | PCM-20251007-00001070 | TT-20251007-01106 | EM | Region_4 | RNRY0835 | RNRY0835 |  |  |  | Mohamed Elsaid Abdou Younes | 10/07/2025 10:57:10 | 10/08/2025 06:26:14 | 10/07/2025 22:57:10 | AIRCON 1 FAILURE at RNRY0835-GSM-P3 @ Sceco | 10/07/2025 10:48:33 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 10:48:26 | P3 | 2G | taif | Sceco | 2G NSA | RNRY0835 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 10:57:10 | 10/08/2025 06:26:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000570 | PCM-20251007-00001072 | TT-20251007-01111 | EM | Region_4 | TURY0836 | TURY0836 |  |  |  | Mohamed Elsaid Abdou Younes | 10/07/2025 10:57:46 | 10/08/2025 06:26:15 | 10/07/2025 22:57:46 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at TURY0836-GSM-P3 @ Sceco | 10/07/2025 10:49:20 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/07/2025 10:49:16 | P3 | 2G | taif | Sceco | 2G NSA | TURY0836 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/07/2025 10:57:46 | 10/08/2025 06:26:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251007000752 | PCM-20251007-00001349 | TT-20251007-01358 | EM | Region_1 | ARR9807 | ARR9807 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Ismail Salah Ismail Elbery | 10/07/2025 13:01:40 | 10/11/2025 11:00:52 | 10/08/2025 01:01:40 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/07/2025 12:54:54 | Minor | 40564 | Genset Fault | 10/07/2025 12:54:54 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/07/2025 13:01:40 | 10/07/2025 14:42:42 | 10/11/2025 11:00:46 |  |  | 10/11/2025 11:00:52 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000832 | PCM-20251007-00001443 | TT-20251007-01452 | EM | Region_4 | JED0070 | JED0070 |  |  |  | Sajid Nazir Muhammad Nazir | 10/07/2025 14:04:40 | 10/07/2025 15:47:40 | 10/08/2025 02:04:40 | COMMERCIAL POWER FAILURE at JED1M7070-P3-CA-L900-L800-SBTS @ Sceco | 10/07/2025 13:40:06 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/07/2025 13:39:59 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7070 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/07/2025 14:04:40 | 10/07/2025 15:47:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251007000835 | PCM-20251007-00001419 | TT-20251007-01439 | EM | Region_1 | RYHR9915 | RYHR9915 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/07/2025 14:05:20 | 10/08/2025 09:39:22 | 10/08/2025 02:05:20 | NETECO: Maintance Reminder at RYHR9915 @ Generator_SG | 10/07/2025 13:35:42 | Minor | 40563 | Maintance Reminder | 10/07/2025 13:35:42 | P3 | Repeater | hafr | Generator_SG | 2G NSA | RYHR9915 | FLM_EM | [8 empty] | API | 10/07/2025 14:05:20 | 10/07/2025 18:07:03 | 10/08/2025 09:39:11 |  |  | 10/08/2025 09:39:22 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251007000858 | PCM-20251007-00001518 | TT-20251007-01527 | EM | Region_4 | USMD0701 | USMD0701 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 10/07/2025 14:24:55 | 10/24/2025 02:59:03 | 10/08/2025 02:24:55 | AIRCON 1 FAILURE at USMD0701-GSM-P3 @ Sceco | 10/07/2025 14:16:19 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 14:16:10 | P3 | 2G | taif | Sceco | 2G NSA | USMD0701 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 14:24:55 | 10/14/2025 09:01:51 | 10/24/2025 02:58:55 |  |  | 10/24/2025 02:59:03 |  | Afzal Hussain Anwar Ul Haq |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007000873 | PCM-20251007-00001539 | TT-20251007-01551 | EM | Region_6 | TLT9478 | TLT9478 | Enviroment | SCECO_Failure | SCECO auto restored | Amir Arif Ali | 10/07/2025 14:36:16 | 10/15/2025 20:40:25 | 10/07/2025 18:36:16 | AIRCON FAILURE (Input-6) at TLT9478 on 10.89.223.146 @ Generator_DG | 10/07/2025 14:34:23 | Critical | AIRCON FAILURE (Input-6) | AIRCON FAILURE (Input-6) | 10/07/2025 14:18:55 | P1 | Repeater | turaib | Generator_DG | TX NSA | TLT9478 | FLM_EM | [8 empty] | API | 10/07/2025 14:36:16 | 10/15/2025 20:40:25 | [5 empty] | Amir Arif Ali | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251007000875 | PCM-20251007-00001541 | TT-20251007-01552 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/07/2025 14:36:45 | 10/07/2025 16:37:40 | 10/08/2025 02:36:45 | High temperature 40C alarm at ARM2M1871-P3 @ Sceco | 10/07/2025 14:26:27 | Minor | 65103 | High temperature 40C alarm | 10/07/2025 14:26:24 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/07/2025 14:36:45 | 10/07/2025 16:37:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251007001110 | PCM-20251007-00001866 | TT-20251007-01882 | EM | Region_1 | RAF0098 | RAF0098 |  |  |  | Murtada Awad AbdElwahab Ahmed | 10/07/2025 17:13:15 | 10/10/2025 15:41:08 | 10/08/2025 05:13:15 | Door opening alarm at RAF0098-P2_SRAN @ Sceco | 10/07/2025 17:12:38 | Minor | 65101 | Door opening alarm | 10/07/2025 17:12:34 | P2 | SRAN | rafha | Sceco | 2G NSA | RAF0098 | FLM_EM | [8 empty] | API | 10/07/2025 17:13:15 | 10/10/2025 15:41:08 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251007001140 | PCM-20251007-00001941 | TT-20251007-01940 | EM | Region_1 | KFKM0783 | KFKM0783 | Enviroment | Air Condition | Change Fan | Abu Sufyan Mehfooz Ali | 10/07/2025 17:48:51 | 10/22/2025 10:50:22 | 10/07/2025 21:48:51 | AMBIENT_TEMP_FLUCT at KFKM0783_OCS @ Generator_SG | 10/07/2025 17:47:10 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/07/2025 17:47:03 | P3 | SRAN | khafji | Generator_SG | DWDM NSA | KFKM0783 | FLM_EM | [5 empty] | 1-(1-A) |  |  | API | 10/07/2025 17:48:51 | 10/09/2025 08:09:33 | 10/22/2025 10:48:24 |  |  | 10/22/2025 10:50:22 |  | Abu Sufyan Mehfooz Ali |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Dispatched | CM20251007001424 | PCM-20251007-00002425 | TT-20251007-02326 | EM | Region_4 | JED0787 | JED0787 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/07/2025 22:37:05 | 10/07/2025 22:37:05 | 10/08/2025 10:37:05 | AIRCON 1 FAILURE at JED1M7787-CA-L900-L800-SBTS @ Sceco | 10/07/2025 22:28:29 | Minor | 7103 | AIRCON 1 FAILURE | 10/07/2025 22:28:18 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7787 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/07/2025 22:37:05 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000064 | PCM-20251008-00000278 | TT-20251008-00283 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/08/2025 01:03:16 | 10/08/2025 14:00:50 | 10/08/2025 13:03:16 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/08/2025 00:52:46 | Minor | 65102 | high temprature 32 | 10/08/2025 00:52:42 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/08/2025 01:03:16 | 10/08/2025 14:00:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251008000140 | PCM-20251008-00000425 | TT-20251008-00444 | EM | Region_6 | FUR2109 | FUR2109 | Enviroment | Air Condition | Change Fan | Adnan Nadeem Abdul Ghaffar | 10/08/2025 02:50:19 | 10/16/2025 17:37:02 | 10/08/2025 14:50:19 | AIRCON 1 FAILURE at FUR1M8109-G9-L8-L18-L21-P3-SBTS @ Generator_SG | 10/08/2025 02:43:19 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 02:41:39 | P3 | 4G | jizan | Generator_SG | LTE NSA | FUR1M8109 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 02:50:19 | 10/15/2025 17:06:03 | 10/16/2025 17:36:43 | 10/16/2025 17:36:46 |  | 10/16/2025 17:37:02 |  | Adnan Nadeem Abdul Ghaffar | NSN_RO |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000142 | PCM-20251008-00000430 | TT-20251008-00450 | Reference_EM | Region_1 | SAR0073 | SAR0073 |  |  |  | Elsaid Adel Mohamed Abouhegara | 10/08/2025 02:57:56 | 10/11/2025 07:03:07 | 10/08/2025 08:57:56 | Generator failure at SAR0073-P1-USF-HUB_SRAN @ Generator_DG | 10/08/2025 02:47:23 | Major | 65114 | Generator failure | 10/08/2025 02:47:19 | P1 | SRAN | quriyat | Generator_DG | 2G NSA | SAR0073 | FLM_EM | [8 empty] | API | 10/08/2025 02:57:56 | 10/11/2025 07:03:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000144 | PCM-20251008-00000432 | TT-20251008-00451 | EM | Region_4 | JED2783 | JED2380 |  |  |  | Sajid Nazir Muhammad Nazir | 10/08/2025 02:58:26 | 10/08/2025 05:05:17 | 10/08/2025 14:58:26 | LOW FUEL LEVEL at JED2783-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-P3 @ Sceco | 10/08/2025 02:49:58 | Minor | 7103 | LOW FUEL LEVEL | 10/08/2025 02:49:47 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2783 | FLM_EM | [5 empty] | LOW FUEL LEVEL |  |  | API | 10/08/2025 02:58:26 | 10/08/2025 05:05:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000145 | PCM-20251008-00000435 | TT-20251008-00457 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/08/2025 03:03:36 | 10/08/2025 03:17:28 | 10/08/2025 09:03:36 | Air condition 1 failure alarm at DAM2066-P1-HUB_SRAN @ Sceco | 10/08/2025 02:53:00 | Major | 65104 | Air condition 1 failure alarm | 10/08/2025 02:52:57 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/08/2025 03:03:36 | 10/08/2025 03:17:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251008000167 | PCM-20251008-00000492 | TT-20251008-00535 | EM | Region_6 | JIZ0157 | JIZ0157 | Enviroment | Air Condition | Change Fan | Adnan Nadeem Abdul Ghaffar | 10/08/2025 03:48:01 | 10/17/2025 19:30:26 | 10/08/2025 15:48:01 | AIRCON 1 FAILURE at JIZ0157-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/08/2025 03:40:00 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 03:39:34 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0157 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 03:48:01 | 10/11/2025 18:39:37 | 10/13/2025 04:18:46 | 10/17/2025 19:30:04 |  | 10/17/2025 19:30:26 |  | Adnan Nadeem Abdul Ghaffar | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251008000175 | PCM-20251008-00000512 | TT-20251008-00558 | EM | Region_6 | AHM0235 | AHM0235 | Enviroment | Air Condition | Change Fan | Touseef Ahmed | 10/08/2025 04:00:56 | 10/18/2025 09:51:57 | 10/08/2025 16:00:56 | AIRCON 1 FAILURE at AHM1M7235-P3-CA-L800 @ Sceco | 10/08/2025 03:52:41 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 03:52:26 | P2 | 4G | jizan | Sceco | LTE NSA | AHM1M7235 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 04:00:56 | 10/08/2025 09:57:31 | 10/08/2025 16:24:34 | 10/18/2025 09:51:41 |  | 10/18/2025 09:51:57 |  | Touseef Ahmed | Force_Majeure |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000191 | PCM-20251008-00000552 | TT-20251008-00600 | EM | Region_1 | SMN0806 | SMN0806 |  |  |  | Rahman Ullah Said Halim | 10/08/2025 04:30:25 | 10/08/2025 15:20:24 | 10/08/2025 16:30:25 | Genset not in auto mode at SMN0806-P2_SRAN @ Generator_DG | 10/08/2025 04:28:18 | Minor | 65113 | Genset not in auto mode | 10/08/2025 04:08:15 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/08/2025 04:30:25 | 10/08/2025 15:20:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000204 | PCM-20251008-00000586 | TT-20251008-00639 | EM | Region_4 | JED0022 | JED0022 |  |  |  | Ahmed Gamal Mohamed Farag | 10/08/2025 05:13:46 | 10/08/2025 20:19:14 | 10/08/2025 11:13:46 | FIRE ALARM at JED0022-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/08/2025 05:05:44 | Major | 7103 | FIRE ALARM | 10/08/2025 05:05:17 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0022 | FLM_EM | [5 empty] | FIRE ALARM |  |  | API | 10/08/2025 05:13:46 | 10/08/2025 20:19:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000218 | PCM-20251008-00000611 | TT-20251008-00677 | EM | Region_4 | JED0327 | JED0327 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/08/2025 05:52:00 | 10/08/2025 15:19:25 | 10/08/2025 17:52:00 | COMMERCIAL POWER FAILURE at JED0327-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/08/2025 05:44:03 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/08/2025 05:43:11 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0327 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/08/2025 05:52:00 | 10/08/2025 15:19:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251008000235 | PCM-20251008-00000641 | TT-20251008-00708 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/08/2025 06:26:05 | 10/08/2025 09:40:55 | 10/08/2025 18:26:05 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/08/2025 06:19:19 | Minor | 40564 | Genset Fault | 10/08/2025 06:19:19 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/08/2025 06:26:05 | 10/08/2025 09:37:40 | 10/08/2025 09:40:44 |  |  | 10/08/2025 09:40:55 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000264 | PCM-20251008-00000695 | TT-20251008-00763 | Reference_EM | Region_1 | YBR0613 | YBR0613 |  |  |  | Montasir Awadalla Abdalla Bala | 10/08/2025 07:12:05 | 10/08/2025 12:34:17 | 10/08/2025 19:12:05 | Air condition 1 failure alarm at YBR0613-P2-USF_SRAN-PC @ Power Cube | 10/08/2025 07:01:34 | Minor | 65104 | Air condition 1 failure alarm | 10/08/2025 07:01:31 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0613 | FLM_EM | [8 empty] | API | 10/08/2025 07:12:05 | 10/08/2025 12:34:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000281 | PCM-20251008-00000720 | TT-20251008-00786 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/08/2025 07:34:50 | 10/08/2025 16:34:39 | 10/08/2025 19:34:50 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/08/2025 07:24:18 | Minor | 65102 | high temprature 32 | 10/08/2025 07:24:14 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/08/2025 07:34:50 | 10/08/2025 16:34:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000285 | PCM-20251008-00000725 | TT-20251008-00788 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/08/2025 07:37:55 | 10/09/2025 06:33:17 | 10/08/2025 19:37:55 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/08/2025 07:29:10 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/08/2025 07:29:06 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/08/2025 07:37:55 | 10/09/2025 06:33:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251008000312 | PCM-20251008-00000769 | TT-20251008-00839 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/08/2025 08:13:00 | 10/08/2025 20:15:04 | 10/08/2025 20:13:00 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/08/2025 08:04:42 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 08:04:33 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 08:13:00 | 10/08/2025 16:36:40 | 10/08/2025 20:14:53 |  |  | 10/08/2025 20:15:04 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251008000370 | PCM-20251008-00000899 | TT-20251008-00948 | EM | Region_4 | SQR0200 | SQR0200 |  |  |  | Faiz Muhammad Ghulam Sarwar | 10/08/2025 09:24:45 | 10/08/2025 09:24:45 | 10/08/2025 21:24:45 | RECTIFIER MODULE FAILURE at SQR0200-GSM-UMTS-P2-USF @ Generator_SG | 10/08/2025 09:16:23 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/08/2025 09:16:12 | P2 | 2G | adam | Generator_SG | 2G NSA | SQR0200 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/08/2025 09:24:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000416 | PCM-20251008-00000965 | TT-20251008-01010 | EM | Region_1 | JBKH0601 | JBKH0601 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/08/2025 10:05:36 | 10/08/2025 15:03:16 | 10/08/2025 14:05:36 | Door opening alarm at JBKH0601-P1-HUB-WDM_SRAN @ Sceco | 10/08/2025 10:04:42 | Critical | 65101 | Door opening alarm | 10/08/2025 10:04:40 | P1 | SRAN | jubail | Sceco | 2G NSA | JBKH0601 | FLM_EM | [8 empty] | API | 10/08/2025 10:05:36 | 10/08/2025 15:03:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251008000420 | PCM-20251008-00000970 | TT-20251008-01012 | EM | Region_4 | MAS0033 | MAS0033 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/08/2025 10:08:10 | 10/12/2025 22:58:26 | 10/08/2025 22:08:10 | AIRCON 1 FAILURE at MAS0033-GSM-UMTS-P2-USF @ Generator_SG | 10/08/2025 09:59:57 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 09:59:46 | P2 | 2G | jeddah | Generator_SG | 2G NSA | MAS0033 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 10:08:10 | 10/12/2025 22:58:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000428 | PCM-20251008-00000986 | TT-20251008-01028 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/08/2025 10:19:00 | 10/08/2025 12:04:04 | 10/08/2025 22:19:00 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/08/2025 10:08:30 | Minor | 65102 | high temprature 32 | 10/08/2025 10:08:24 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/08/2025 10:19:00 | 10/08/2025 12:04:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000520 | PCM-20251008-00001153 | TT-20251008-00611 | Reference_telecom | Region_2 | RYQS0586 | RYQS0586 |  |  |  | Ibrahim Abdou Ibrahim Abdou | 10/08/2025 11:35:45 | 10/08/2025 22:48:03 | 10/08/2025 15:35:45 | IP PM Activation Failure at R2_RY1_HWBSC01 @ Sceco_STB | 10/08/2025 01:41:10 | Critical | 21341 | IP PM Activation Failure | 10/08/2025 01:40:35 | P2 | SRAN | buraidah | Generator_SG | 2G NSA | R2_RY1_HWBSC01 | FLM_EM |  | issue related to site RYQS2M1586-P2 check IPRAN and TX team | PCM-20251008-00001149 | power issue at site | power issue at site |  |  |  | API | 10/08/2025 11:35:45 | 10/08/2025 22:48:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000602 | PCM-20251008-00001278 | TT-20251008-01321 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/08/2025 12:40:35 | 10/08/2025 21:57:17 | 10/09/2025 00:40:35 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/08/2025 12:31:59 | Minor | 7103 | AIRCON 1 FAILURE | 10/08/2025 12:31:51 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/08/2025 12:40:35 | 10/08/2025 21:57:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251008000618 | PCM-20251008-00001297 | TT-20251008-01340 | Reference_EM | Region_1 | ARR0919 | ARR0919 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/08/2025 12:51:25 | 10/11/2025 11:01:14 | 10/08/2025 18:51:25 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/08/2025 12:40:51 | Major | 65110 | Low battery voltage | 10/08/2025 12:40:47 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/08/2025 12:51:25 | 10/10/2025 03:46:17 | 10/11/2025 11:01:07 |  |  | 10/11/2025 11:01:14 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251008000657 | PCM-20251008-00001359 | TT-20251008-01415 | Reference_EM | Region_1 | JBL0966 | JBL0966 |  |  |  | Hamid Bilal Bashir Ahmed | 10/08/2025 13:24:00 | 10/08/2025 15:49:10 | 10/09/2025 01:24:00 | Mains Failure at JBL2M1966-P2 @ Sceco | 10/08/2025 13:13:39 | Minor | 65109 | Mains Failure | 10/08/2025 13:13:36 | P2 | 2G | jubail | Sceco | 2G NSA | JBL2M1966 | FLM_EM | [8 empty] | API | 10/08/2025 13:24:00 | 10/08/2025 15:49:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000672 | PCM-20251008-00001375 | TT-20251008-01438 | Reference_EM | Region_1 | QRY0542 | QRY0542 |  |  |  | Mabrouk Mohamed Mabrouk Kandil | 10/08/2025 13:34:50 | 10/11/2025 14:47:45 | 10/08/2025 19:34:50 | Air condition 2 failure alarm at QRY0542-P1-SHOP_SRAN @ Sceco | 10/08/2025 13:24:06 | Major | 65105 | Air condition 2 failure alarm | 10/08/2025 13:24:02 | P1 | SRAN | quriyat | Sceco | 2G NSA | QRY0542 | FLM_EM | [8 empty] | API | 10/08/2025 13:34:50 | 10/10/2025 14:16:17 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251008000698 | PCM-20251008-00001411 | TT-20251008-01477 | Reference_EM | Region_2 | ZLF0509 | ZLF0509 |  |  |  | Ahmed Mahmoud Mohamed Mahmoud | 10/08/2025 13:48:15 | 10/20/2025 12:31:54 | 10/09/2025 01:48:15 | Air-condition #2 failure alarm at ZLF2M1509-P3 @ Sceco | 10/08/2025 13:37:35 | Minor | 65105 | Air-condition #2 failure alarm | 10/08/2025 13:37:33 | P3 | 2G | buraidah | Sceco | 2G NSA | ZLF2M1509 | FLM_EM | [8 empty] | API | 10/08/2025 13:48:15 | [7 empty] | Latis_Operation |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008000753 | PCM-20251008-00001494 | TT-20251008-01550 | EM | Region_1 | HFF2359 | HFF2359 |  |  |  | Ahmed Bashir Sahib Rahman | 10/08/2025 14:25:55 | 10/08/2025 19:35:16 | 10/09/2025 02:25:55 | NETECO: Communication Failure at HFF2359 @ Sceco | 10/08/2025 14:19:40 | Minor | 9354 | Communication Failure | 10/08/2025 14:19:40 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2359 | FLM_EM | [8 empty] | API | 10/08/2025 14:25:55 | 10/08/2025 19:35:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251008000772 | PCM-20251008-00001531 | TT-20251008-01588 | EM | Region_4 | YLM0789 | YLM0789 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Karim Hamdy Mohamed Elashry | 10/08/2025 14:42:31 | 10/09/2025 15:27:35 | 10/09/2025 02:42:31 | GENERATOR LOW FUEL at YLM0789-GSM-UMTS-P3 @ Generator_SG | 10/08/2025 14:34:07 | Minor | 7103 | GENERATOR LOW FUEL | 10/08/2025 14:33:58 | P3 | 2G | alaith | Generator_SG | 2G NSA | YLM0789 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/08/2025 14:42:31 | 10/09/2025 15:25:29 | 10/09/2025 15:27:25 |  |  | 10/09/2025 15:27:35 |  | Karim Hamdy Mohamed Elashry |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008001085 | PCM-20251008-00001892 | TT-20251008-01953 | MW_HC | Region_6 | FIF0045 | FIF0045 |  |  |  | Muhammad Ali | 10/08/2025 15:26:31 | 10/08/2025 15:43:16 | 10/09/2025 03:26:31 | NEC MW HC_P0 Observing Performance Issue at BLG0041(10.154.170.20)--FIF0045(10.154.170.19) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | dair | Sceco | TX NSA | BLG0041(10.154.170.20)--FIF0045(10.154.170.19) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:31 | 10/08/2025 15:43:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001086 | PCM-20251008-00001893 | TT-20251008-01954 | MW_HC | Region_6 | ARS0315 | ARS0315 | Transsmission | MW_RSL_fading | Bad Weather | Zeshan Ali Adnan | 10/08/2025 15:26:33 | 10/16/2025 14:28:11 | 10/09/2025 03:26:33 | NEC MW HC_P0 Observing Modem Down at ARS0126(10.1.174.50)--ARS0315(10.1.174.51) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jizan | Sceco | TX NSA | ARS0126(10.1.174.50)--ARS0315(10.1.174.51) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:33 | 10/08/2025 16:03:35 | 10/16/2025 14:27:32 |  |  | 10/16/2025 14:28:11 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001089 | PCM-20251008-00001896 | TT-20251008-01957 | MW_HC | Region_6 | ABH0161 | ABH0161 | Transsmission | MW_HW_fault | Replace ODU | Muhammad Jamshaid Muhammad Ashraf | 10/08/2025 15:26:36 | 10/12/2025 21:56:22 | 10/09/2025 03:26:36 | NEC MW HC_P0 Observing Modem Down at ABH0135(10.154.161.148)--ABH0161(10.154.161.145) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0135(10.154.161.148)--ABH0161(10.154.161.145) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:36 | 10/09/2025 17:47:52 | 10/12/2025 21:56:02 |  |  | 10/12/2025 21:56:22 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001099 | PCM-20251008-00001907 | TT-20251008-01968 | MW_HC | Region_5 | USMD0706 | USMD0706 |  |  |  | Amr Abdulla Ali Othman | 10/08/2025 15:26:47 | 10/08/2025 15:26:47 | 10/09/2025 03:26:47 | NEC MW HC_P0 Observing Modem Down at USMD0705(10.154.140.166)--USMD0706(10.154.140.152) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | makkah | Sceco | TX NSA | USMD0705(10.154.140.166)--USMD0706(10.154.140.152) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001102 | PCM-20251008-00001910 | TT-20251008-01971 | MW_HC | Region_5 | MKTF0635 | MKTF0635 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/08/2025 15:26:51 | 10/08/2025 23:47:25 | 10/09/2025 03:26:51 | NEC MW HC_P2 Observing Modem Down at MAK2841(10.154.125.245)--MKTF0635(10.154.125.244) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK2841(10.154.125.245)--MKTF0635(10.154.125.244) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:51 | 10/08/2025 23:47:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001110 | PCM-20251008-00001918 | TT-20251008-01979 | MW_HC | Region_1 | DMJR2156 | DMJR2156 |  |  |  | Muhammad Zubair Guilzar | 10/08/2025 15:26:59 | 10/22/2025 11:33:37 | 10/09/2025 03:26:59 | NEC MW HC_P0 Observing Performance Issue at DMJ0157(10.76.111.72)--DMJR2156(10.76.111.73) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | SRAN | arar | Generator_DG | TX NSA | DMJ0157(10.76.111.72)--DMJR2156(10.76.111.73) | FLM_TE | [8 empty] | API | 10/08/2025 15:26:59 | 10/08/2025 20:13:14 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001112 | PCM-20251008-00001920 | TT-20251008-01981 | MW_HC | Region_4 | HJR0232 | HJR0232 |  |  |  | Khizer Hayat | 10/08/2025 15:27:01 | 10/09/2025 16:53:15 | 10/09/2025 03:27:01 | Nokia MW HC_P0 Observing Performance Issue at HJR0232_01-HJR0236_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Generator_DG | TX NSA | HJR0232_01-HJR0236_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:01 | 10/09/2025 16:53:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001115 | PCM-20251008-00001923 | TT-20251008-01984 | MW_HC | Region_4 | JED2301 | JED2301 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 15:27:05 | 10/08/2025 15:58:41 | 10/09/2025 03:27:05 | Nokia MW HC_P0 Observing Performance Issue at JED2301-JED0965_09 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2301-JED0965_09 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:05 | 10/08/2025 15:58:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001116 | PCM-20251008-00001924 | TT-20251008-01985 | MW_HC | Region_4 | JED2886 | JED2886 | Transsmission | MW_Connectors | Replace Indoor MW Connector | BARKAT ALI MAIN HILAL | 10/08/2025 15:27:06 | 10/16/2025 10:56:50 | 10/09/2025 03:27:06 | Nokia MW HC_P0 Observing Performance Issue at JED2886-JED0947_03 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2886-JED0947_03 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:06 | 10/08/2025 15:36:27 | 10/08/2025 20:06:51 | 10/08/2025 20:06:55 | 10/08/2025 20:07:49 | 10/16/2025 10:56:50 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001118 | PCM-20251008-00001926 | TT-20251008-01987 | MW_HC | Region_6 | BAH0012 | BAH0012 |  |  |  | SHAH KHALID | 10/08/2025 15:27:08 | 10/08/2025 15:28:14 | 10/09/2025 03:27:08 | Nokia MW HC_P1 Observing Performance Issue at BAH0012-BAH0014_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0012-BAH0014_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:08 | 10/08/2025 15:28:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001119 | PCM-20251008-00001927 | TT-20251008-01988 | MW_HC | Region_4 | JED0686 | JED0686 |  |  |  | Mohammed Ramadan A Abu Abid | 10/08/2025 15:27:09 | 10/08/2025 17:11:44 | 10/09/2025 03:27:09 | Nokia MW HC_P2 Observing Modem Down at JED0686_03-JED6021 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Sceco | TX NSA | JED0686_03-JED6021 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:09 | 10/08/2025 17:11:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001121 | PCM-20251008-00001929 | TT-20251008-01990 | MW_HC | Region_6 | BRQ0414 | BRQ0414 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/08/2025 15:27:11 | 10/08/2025 15:39:36 | 10/09/2025 03:27:11 | Nokia MW HC_P1 Observing Performance Issue at BRQ0414_01-BRQ0084_05 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | mohail | Sceco | TX NSA | BRQ0414_01-BRQ0084_05 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:11 | 10/08/2025 15:39:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001123 | PCM-20251008-00001932 | TT-20251008-01993 | MW_HC | Region_6 | BSA2316 | BSA2316 |  |  |  | Hamid Ullah Muhammad Alam Khan | 10/08/2025 15:27:14 | 10/08/2025 16:54:39 | 10/09/2025 03:27:14 | Nokia MW HC_P1 Observing Performance + RSL Issue at BSA2316-BSA2313_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | bisha | Generator_SG | TX NSA | BSA2316-BSA2313_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:14 | 10/08/2025 16:54:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001125 | PCM-20251008-00001934 | TT-20251008-01995 | MW_HC | Region_4 | JED2235 | JED2235 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:27:16 | 10/08/2025 16:09:03 | 10/09/2025 03:27:16 | Nokia MW HC_P2 Observing Performance Issue at JED2235-JED2142 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2235-JED2142 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:16 | 10/08/2025 16:09:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251008001126 | PCM-20251008-00001935 | TT-20251008-01996 | MW_HC | Region_6 | KMS0591 | KMS0591 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/08/2025 15:27:17 | 10/09/2025 01:31:20 | 10/09/2025 03:27:17 | Nokia MW HC_P0 Observing Performance Issue at KMS0591-ARF0076-3 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0591-ARF0076-3 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:17 | 10/08/2025 20:27:56 | 10/09/2025 01:31:14 | 10/09/2025 01:31:20 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001128 | PCM-20251008-00001937 | TT-20251008-01997 | MW_HC | Region_6 | MKW2340 | MKW2340 |  |  |  | SHAH KHALID | 10/08/2025 15:27:18 | 10/08/2025 15:28:15 | 10/09/2025 03:27:18 | Nokia MW HC_P0 Observing Performance Issue at MKW2340_01-MKW2338_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2340_01-MKW2338_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:18 | 10/08/2025 15:28:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001129 | PCM-20251008-00001938 | TT-20251008-01998 | MW_HC | Region_6 | MHL9707 | MHL9707 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/08/2025 15:27:20 | 10/08/2025 15:39:37 | 10/09/2025 03:27:20 | Nokia MW HC_P0 Observing Performance Issue at MHL9707_01-MHL0132_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | Repeater | mohail | Sceco | TX NSA | MHL9707_01-MHL0132_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:20 | 10/08/2025 15:39:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001130 | PCM-20251008-00001939 | TT-20251008-01999 | MW_HC | Region_6 | MHL0131 | MHL0131 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/08/2025 15:27:21 | 10/12/2025 19:03:45 | 10/09/2025 03:27:21 | Nokia MW HC_P0 Observing Performance Issue at MHL0131_01-MHL9707_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | mohail | Sceco | TX NSA | MHL0131_01-MHL9707_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:21 | 10/08/2025 15:39:38 | 10/12/2025 19:03:33 |  |  | 10/12/2025 19:03:45 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001131 | PCM-20251008-00001940 | TT-20251008-02000 | MW_HC | Region_4 | JED0925 | JED0925 |  |  |  | Mohammed Ramadan A Abu Abid | 10/08/2025 15:27:22 | 10/08/2025 17:11:44 | 10/09/2025 03:27:22 | Nokia MW HC_P2 Observing Modem Down at JED0925-JED0155-06 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED0925-JED0155-06 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:22 | 10/08/2025 17:11:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251008001133 | PCM-20251008-00001942 | TT-20251008-02002 | MW_HC | Region_6 | MKW9711 | MKW9711 |  |  |  | Manzoor Ahmed | 10/08/2025 15:27:24 | 10/08/2025 22:30:18 | 10/09/2025 03:27:24 | Nokia MW HC_P2 Observing Modem Down at MKW9711_01-BHAB0823_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | Repeater | makhwa | Sceco | TX NSA | MKW9711_01-BHAB0823_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:24 | 10/08/2025 17:33:17 | 10/08/2025 22:30:18 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001134 | PCM-20251008-00001943 | TT-20251008-02003 | MW_HC | Region_6 | BHAB0827 | BHAB0827 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/08/2025 15:27:25 | 10/08/2025 15:39:38 | 10/09/2025 03:27:25 | Nokia MW HC_P0 Observing Performance Issue at BHAB0827_01-BHAB9036_09 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | makhwa | Sceco_STB | TX NSA | BHAB0827_01-BHAB9036_09 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:25 | 10/08/2025 15:39:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001136 | PCM-20251008-00001944 | TT-20251008-02004 | MW_HC | Region_4 | JDJZ0777 | JDJZ0777 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/08/2025 15:27:26 | 10/14/2025 10:58:51 | 10/09/2025 03:27:26 | Nokia MW HC_P1 Observing Performance Issue at JDJZ0777_01-JDJZ0778-4 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0777_01-JDJZ0778-4 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:26 | 10/14/2025 10:58:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001137 | PCM-20251008-00001945 | TT-20251008-02005 | MW_HC | Region_6 | NMR2067 | NMR2067 |  |  |  | SHAH KHALID | 10/08/2025 15:27:28 | 10/08/2025 15:28:16 | 10/09/2025 03:27:28 | Nokia MW HC_P0 Observing Performance Issue at NMR2067_01-NMR2044_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | Albaha | Sceco | TX NSA | NMR2067_01-NMR2044_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:28 | 10/08/2025 15:28:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_with_Closed | CM20251008001139 | PCM-20251008-00001947 | TT-20251008-02007 | MW_HC | Region_4 | JED0791 | JED0791 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/08/2025 15:27:30 | 10/13/2025 13:54:33 | 10/09/2025 03:27:30 | Nokia MW HC_P0 Observing Performance Issue at JED0791-JED0159_1 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Sceco | TX NSA | JED0791-JED0159_1 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:30 | 10/13/2025 11:08:58 | 10/13/2025 11:10:18 | 10/13/2025 11:10:20 | 10/13/2025 11:10:22 | 10/13/2025 13:54:33 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001142 | PCM-20251008-00001950 | TT-20251008-02009 | MW_HC | Region_4 | JED2125 | JED2125 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:27:32 | 10/08/2025 15:27:32 | 10/09/2025 03:27:32 | Nokia MW HC_P2 Observing Performance Issue at JED2125-JED0850_4 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2125-JED0850_4 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001144 | PCM-20251008-00001952 | TT-20251008-02011 | MW_HC | Region_4 | JED0220 | JED0220 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:27:34 | 10/08/2025 15:27:34 | 10/09/2025 03:27:34 | Nokia MW HC_P0 Observing Performance Issue at JED0220-02-JED0253_2 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Sceco | TX NSA | JED0220-02-JED0253_2 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001145 | PCM-20251008-00001953 | TT-20251008-02012 | MW_HC | Region_5 | MAK0273 | MAK0273 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/08/2025 15:27:35 | 10/24/2025 01:40:10 | 10/09/2025 03:27:35 | Nokia MW HC_P2 Observing Modem Down at MAK0273_01-MAK0053 -19 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK0273_01-MAK0053 -19 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:35 | 10/24/2025 01:40:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001147 | PCM-20251008-00001955 | TT-20251008-02013 | MW_HC | Region_3 | WHAL0002 | WHAL0002 |  |  |  | Mazin Meshary AlEnzi | 10/08/2025 15:27:37 | 10/08/2025 17:51:25 | 10/09/2025 03:27:37 | Nokia MW HC_P2 Observing Performance Issue at WHAL0002-HAL0117 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | WIFI | hail | Sceco | TX NSA | WHAL0002-HAL0117 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:37 | 10/08/2025 17:51:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001149 | PCM-20251008-00001957 | TT-20251008-02015 | MW_HC | Region_6 | JDJ0406 | JDJ0406 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:27:39 | 10/08/2025 16:02:53 | 10/09/2025 03:27:39 | Nokia MW HC_P1 Observing Performance Issue at JDJ0406-SAB2078_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | bisha | Generator_SG | TX NSA | JDJ0406-SAB2078_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:39 | 10/08/2025 16:02:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001150 | PCM-20251008-00001958 | TT-20251008-02016 | MW_HC | Region_6 | SAB2078 | SAB2078 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:27:40 | 10/14/2025 15:02:16 | 10/09/2025 03:27:40 | Nokia MW HC_P0 Observing Performance Issue at SAB2078_01-SAB0060_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | baish | Sceco | TX NSA | SAB2078_01-SAB0060_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:40 | 10/08/2025 16:02:53 | 10/14/2025 14:36:39 | 10/14/2025 14:36:57 | 10/14/2025 15:02:16 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001151 | PCM-20251008-00001959 | TT-20251008-02017 | MW_HC | Region_5 | MAK2967 | MAK2967 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/08/2025 15:27:41 | 10/08/2025 17:01:34 | 10/09/2025 03:27:41 | Nokia MW HC_P0 Observing Performance Issue at MAK2967-MAK0854_USF-NeW Site_8 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | makkah | Generator_SG | TX NSA | MAK2967-MAK0854_USF-NeW Site_8 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:41 | 10/08/2025 17:01:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001152 | PCM-20251008-00001960 | TT-20251008-02018 | MW_HC | Region_5 | MAK0077 | MAK0077 | Transsmission | SFP_Transmission | Replace SFP | Husain Hassan Ishag Omer | 10/08/2025 15:27:43 | 10/15/2025 19:03:09 | 10/09/2025 03:27:43 | Nokia MW HC_P2 Observing Performance Issue at MAK0077_01-MAK0538 -10 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0077_01-MAK0538 -10 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:43 | 10/15/2025 14:27:27 | 10/15/2025 15:25:18 | 10/15/2025 15:25:37 | 10/15/2025 15:25:46 | 10/15/2025 19:03:09 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001153 | PCM-20251008-00001961 | TT-20251008-02019 | MW_HC | Region_4 | JED2397 | JED2397 |  |  |  | Nazeer Mohammed | 10/08/2025 15:27:44 | 10/09/2025 13:22:10 | 10/09/2025 03:27:44 | Nokia MW HC_P1 Observing Performance Issue at JED2397-JED2288_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2397-JED2288_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:44 | 10/09/2025 13:22:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001154 | PCM-20251008-00001963 | TT-20251008-02020 | MW_HC | Region_6 | JIZ0226 | JIZ0226 |  |  |  | Mohammed Sideag Mohammed Ali | 10/08/2025 15:27:45 | 10/08/2025 15:33:24 | 10/09/2025 03:27:45 | Nokia MW HC_P2 Observing Modem Down at JIZ0226_01-JIZ0025_08 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0226_01-JIZ0025_08 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:45 | 10/08/2025 15:33:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001157 | PCM-20251008-00001966 | TT-20251008-02023 | MW_HC | Region_4 | JED0850 | JED0850 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/08/2025 15:27:49 | 10/21/2025 15:02:25 | 10/09/2025 03:27:49 | Nokia MW HC_P0 Observing Performance Issue at JED0850_01-JED0198-NE6 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | jeddah | Sceco | TX NSA | JED0850_01-JED0198-NE6 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:49 | 10/21/2025 14:40:24 | 10/21/2025 15:02:16 | 10/21/2025 15:02:23 | 10/21/2025 15:02:25 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001159 | PCM-20251008-00001968 | TT-20251008-02025 | MW_HC | Region_4 | JED0979 | JED0979 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 15:27:51 | 10/08/2025 15:58:41 | 10/09/2025 03:27:51 | Nokia MW HC_P2 Observing Modem Down at JED0979-JED0813_03 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0979-JED0813_03 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:51 | 10/08/2025 15:58:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001160 | PCM-20251008-00001969 | TT-20251008-02026 | MW_HC | Region_4 | JED0218 | JED0218 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/08/2025 15:27:52 | 10/15/2025 10:52:22 | 10/09/2025 03:27:52 | Nokia MW HC_P2 Observing Performance Issue at JED0218_3-JED2703 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | jeddah | Sceco | TX NSA | JED0218_3-JED2703 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:52 | 10/15/2025 10:52:10 | 10/15/2025 10:52:18 | 10/15/2025 10:52:20 | 10/15/2025 10:52:22 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001161 | PCM-20251008-00001970 | TT-20251008-02027 | MW_HC | Region_5 | MAK0125 | MAK0125 |  |  |  | Husain Hassan Ishag Omer | 10/08/2025 15:27:54 | 10/09/2025 10:39:44 | 10/09/2025 03:27:54 | Nokia MW HC_P1 Observing Performance Issue at MAK0125-MAK2301_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0125-MAK2301_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:54 | 10/09/2025 10:39:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001164 | PCM-20251008-00001972 | TT-20251008-02029 | MW_HC | Region_5 | MAK0992 | MAK0992 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:27:56 | 10/16/2025 11:25:46 | 10/09/2025 03:27:56 | Nokia MW HC_P0 Observing Performance Issue at MAK0992-MK5_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | VIP | 2G | makkah | Sceco | TX NSA | MAK0992-MK5_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:27:56 | 10/16/2025 11:25:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001167 | PCM-20251008-00001975 | TT-20251008-02032 | MW_HC | Region_6 | JIZ0089 | JIZ0089 |  |  |  | Osama Hadi | 10/08/2025 15:28:00 | 10/08/2025 16:03:20 | 10/09/2025 03:28:00 | Nokia MW HC_P0 Observing Performance Issue at JIZ0089_01-JIZ0025_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0089_01-JIZ0025_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:00 | 10/08/2025 16:03:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001168 | PCM-20251008-00001976 | TT-20251008-02033 | MW_HC | Region_6 | SAB0098 | SAB0098 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:28:01 | 10/08/2025 16:02:54 | 10/09/2025 03:28:01 | Nokia MW HC_P0 Observing Performance Issue at SAB0098-SAB0057_06 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | baish | Sceco | TX NSA | SAB0098-SAB0057_06 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:01 | 10/08/2025 16:02:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001171 | PCM-20251008-00001980 | TT-20251008-02036 | MW_HC | Region_6 | BAH0016 | BAH0016 |  |  |  | SHAH KHALID | 10/08/2025 15:28:04 | 10/08/2025 15:28:17 | 10/09/2025 03:28:04 | Nokia MW HC_P0 Observing Performance Issue at BAH0016_1-BAH0005_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0016_1-BAH0005_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:04 | 10/08/2025 15:28:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001172 | PCM-20251008-00001981 | TT-20251008-02037 | MW_HC | Region_4 | JED0189 | JED0189 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:28:05 | 10/08/2025 16:09:04 | 10/09/2025 03:28:05 | Nokia MW HC_P0 Observing Performance Issue at JED0189_02-JED0609_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | jeddah | Sceco | TX NSA | JED0189_02-JED0609_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:05 | 10/08/2025 16:09:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001175 | PCM-20251008-00001984 | TT-20251008-02040 | MW_HC | Region_4 | JED0202 | JED0202 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:28:09 | 10/08/2025 15:28:09 | 10/09/2025 03:28:09 | Nokia MW HC_P1 Observing Performance Issue at JED0202-JED0097_01 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0202-JED0097_01 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001177 | PCM-20251008-00001986 | TT-20251008-02042 | MW_HC | Region_4 | BHR0312 | BHR0312 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 15:28:11 | 10/08/2025 15:58:42 | 10/09/2025 03:28:11 | Nokia MW HC_P1 Observing Performance Issue at BHR0312_01_-MKJD0568_04 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | BHR0312_01_-MKJD0568_04 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:11 | 10/08/2025 15:58:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251008001179 | PCM-20251008-00001988 | TT-20251008-02044 | MW_HC | Region_6 | ARF0899 | ARF0899 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/08/2025 15:28:13 | 10/09/2025 01:29:50 | 10/09/2025 03:28:13 | Nokia MW HC_P2 Observing Performance Issue at ARF0899-ARF0699 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | khamis mushyet | Sceco | TX NSA | ARF0899-ARF0699 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:13 | 10/08/2025 20:27:57 | 10/09/2025 01:29:39 | 10/09/2025 01:29:50 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001180 | PCM-20251008-00001990 | TT-20251008-02047 | MW_HC | Region_4 | JED2176 | JED2176 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:28:14 | 10/08/2025 16:09:04 | 10/09/2025 03:28:14 | Nokia MW HC_P1 Observing Performance Issue at JED2176-JED0245_13 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2176-JED0245_13 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:14 | 10/08/2025 16:09:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001181 | PCM-20251008-00001991 | TT-20251008-02048 | MW_HC | Region_4 | JED0268 | JED0268 |  |  |  | Mohammed Ramadan A Abu Abid | 10/08/2025 15:28:15 | 10/15/2025 10:10:36 | 10/09/2025 03:28:15 | Nokia MW HC_P2 Observing Performance Issue at JED0268_01-JED0121-12 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0268_01-JED0121-12 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:15 | 10/15/2025 08:59:50 | 10/15/2025 09:53:57 | 10/15/2025 09:54:01 | 10/15/2025 10:10:36 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001184 | PCM-20251008-00001993 | TT-20251008-02050 | MW_HC | Region_5 | MAK2700 | MAK2700 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/08/2025 15:28:18 | 10/08/2025 17:42:36 | 10/09/2025 03:28:18 | Nokia MW HC_P1 Observing Performance Issue at MAK2700-MAK0026 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK2700-MAK0026 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:18 | 10/08/2025 17:42:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001185 | PCM-20251008-00001994 | TT-20251008-02051 | MW_HC | Region_4 | HLA0424 | HLA0424 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:28:19 | 10/08/2025 16:02:47 | 10/09/2025 03:28:19 | Nokia MW HC_P1 Observing Performance Issue at HLA0424_1-HLA0423_04 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | qunfuddah | Sceco | TX NSA | HLA0424_1-HLA0423_04 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:19 | 10/08/2025 16:02:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001187 | PCM-20251008-00001996 | TT-20251008-02053 | MW_HC | Region_4 | JED0379 | JED0379 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:28:21 | 10/08/2025 16:09:04 | 10/09/2025 03:28:21 | Nokia MW HC_P2 Observing Modem Down at JED0379-JED0025 - 3 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | jeddah | Sceco | TX NSA | JED0379-JED0025 - 3 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:21 | 10/08/2025 16:09:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001189 | PCM-20251008-00001998 | TT-20251008-02055 | MW_HC | Region_5 | BIK0151 | BIK0151 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/08/2025 15:28:24 | 10/08/2025 15:28:24 | 10/09/2025 03:28:24 | Nokia MW HC_P2 Observing Modem Down at BIK0151-SHD0164_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | BIK0151-SHD0164_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001190 | PCM-20251008-00001999 | TT-20251008-02056 | MW_HC | Region_4 | QHN0737 | QHN0737 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:28:25 | 10/08/2025 16:02:48 | 10/09/2025 03:28:25 | Nokia MW HC_P1 Observing Performance Issue at QHN0737_01-JDJZ0778-1 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | qunfuddah | Sceco | TX NSA | QHN0737_01-JDJZ0778-1 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:25 | 10/08/2025 16:02:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001192 | PCM-20251008-00002000 | TT-20251008-02057 | MW_HC | Region_4 | JED2023 | JED2023 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 15:28:26 | 10/08/2025 15:36:28 | 10/09/2025 03:28:26 | Nokia MW HC_P1 Observing Performance Issue at JED2023-JED0069_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2023-JED0069_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:26 | 10/08/2025 15:36:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001193 | PCM-20251008-00002001 | TT-20251008-02058 | MW_HC | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 15:28:27 | 10/08/2025 15:36:28 | 10/09/2025 03:28:27 | Nokia MW HC_P0 Observing Performance Issue at JED2259-JED0544 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2259-JED0544 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:27 | 10/08/2025 15:36:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001197 | PCM-20251008-00002005 | TT-20251008-02062 | MW_HC | Region_4 | JED2609 | JED2609 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 15:28:32 | 10/08/2025 15:36:29 | 10/09/2025 03:28:32 | Nokia MW HC_P1 Observing Performance Issue at JED2609-JED2073_2 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2609-JED2073_2 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:32 | 10/08/2025 15:36:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001198 | PCM-20251008-00002006 | TT-20251008-02063 | MW_HC | Region_5 | MAK0763 | MAK0763 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:28:33 | 10/16/2025 11:25:46 | 10/09/2025 03:28:33 | Nokia MW HC_P2 Observing Performance Issue at MAK0763-MAK0991_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | makkah | Sceco | TX NSA | MAK0763-MAK0991_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:33 | 10/16/2025 11:25:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001199 | PCM-20251008-00002008 | TT-20251008-02064 | MW_HC | Region_5 | MAK0753 | MAK0753 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:28:34 | 10/16/2025 11:25:47 | 10/09/2025 03:28:34 | Nokia MW HC_P1 Observing Performance Issue at MAK0753-MAK0995_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | makkah | Sceco | TX NSA | MAK0753-MAK0995_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:34 | 10/16/2025 11:25:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001201 | PCM-20251008-00002010 | TT-20251008-02066 | MW_HC | Region_4 | JED2424 | JED2424 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:28:36 | 10/08/2025 15:28:36 | 10/09/2025 03:28:36 | Nokia MW HC_P2 Observing Performance Issue at JED2424-JED2085 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2424-JED2085 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001202 | PCM-20251008-00002011 | TT-20251008-02067 | MW_HC | Region_6 | ABSD0704 | ABSD0704 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/08/2025 15:28:37 | 10/08/2025 15:58:40 | 10/09/2025 03:28:37 | Nokia MW HC_P1 Observing Performance Issue at ABSD0704_01-ABH0501_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | abha | Sceco | TX NSA | ABSD0704_01-ABH0501_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:37 | 10/08/2025 15:58:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001204 | PCM-20251008-00002013 | TT-20251008-02069 | MW_HC | Region_4 | TUR2323 | TUR2323 |  |  |  | Rashid Shafique | 10/08/2025 15:28:39 | 10/08/2025 16:20:04 | 10/09/2025 03:28:39 | Nokia MW HC_P0 Observing Performance Issue at TUR2323-TUR0681 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | TUR2323-TUR0681 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:39 | 10/08/2025 16:20:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001205 | PCM-20251008-00002014 | TT-20251008-02070 | MW_HC | Region_4 | TAF0326 | TAF0326 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 15:28:41 | 10/09/2025 10:07:26 | 10/09/2025 03:28:41 | Nokia MW HC_P2 Observing Performance Issue at TAF0326-TAF0163 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | taif | Sceco | TX NSA | TAF0326-TAF0163 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:41 | 10/09/2025 10:07:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001206 | PCM-20251008-00002016 | TT-20251008-02071 | MW_HC | Region_6 | SMT0062 | SMT0062 |  |  |  | Osama Hadi | 10/08/2025 15:28:41 | 10/08/2025 16:03:22 | 10/09/2025 03:28:41 | Nokia MW HC_P0 Observing Performance Issue at SMT0062_01-SMT0063_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | jizan | Sceco_STB | TX NSA | SMT0062_01-SMT0063_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:41 | 10/08/2025 16:03:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001207 | PCM-20251008-00002017 | TT-20251008-02072 | MW_HC | Region_6 | SAB0052 | SAB0052 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 15:28:43 | 10/08/2025 16:02:55 | 10/09/2025 03:28:43 | Nokia MW HC_P1 Observing Performance Issue at SAB0052-SAB0053_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | baish | Sceco | TX NSA | SAB0052-SAB0053_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:43 | 10/08/2025 16:02:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001208 | PCM-20251008-00002018 | TT-20251008-02073 | MW_HC | Region_4 | QUN0341 | QUN0341 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mudassar Bashir Bashir Ahmad | 10/08/2025 15:28:44 | 10/09/2025 12:03:51 | 10/09/2025 03:28:44 | Nokia MW HC_P2 Observing Modem Down at QUN0341-QUN0337_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | qunfuddah | Sceco | TX NSA | QUN0341-QUN0337_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:44 | 10/08/2025 16:02:48 | 10/09/2025 10:49:05 | 10/09/2025 10:49:09 | 10/09/2025 10:49:14 | 10/09/2025 12:03:51 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001212 | PCM-20251008-00002021 | TT-20251008-02076 | MW_HC | Region_5 | MAK0928 | MAK0928 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/08/2025 15:28:47 | 10/21/2025 19:56:52 | 10/09/2025 03:28:47 | Nokia MW HC_P2 Observing Modem Down at MAK0928-MAK0047 - 8 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK0928-MAK0047 - 8 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:47 | 10/21/2025 19:56:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001213 | PCM-20251008-00002022 | TT-20251008-02077 | MW_HC | Region_5 | MAK0814 | MAK0814 |  |  |  | Husain Hassan Ishag Omer | 10/08/2025 15:28:48 | 10/09/2025 10:39:44 | 10/09/2025 03:28:48 | Nokia MW HC_P1 Observing Performance Issue at MAK0814-MAK0245-2 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0814-MAK0245-2 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:48 | 10/09/2025 10:39:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001214 | PCM-20251008-00002023 | TT-20251008-02078 | MW_HC | Region_5 | MAK0795 | MAK0795 |  |  |  | Husain Hassan Ishag Omer | 10/08/2025 15:28:49 | 10/09/2025 10:39:45 | 10/09/2025 03:28:49 | Nokia MW HC_P1 Observing Performance Issue at MAK0795-1-MAK0005-11 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0795-1-MAK0005-11 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:49 | 10/09/2025 10:39:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001215 | PCM-20251008-00002024 | TT-20251008-02079 | MW_HC | Region_5 | MAK0765 | MAK0765 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:28:50 | 10/16/2025 11:25:47 | 10/09/2025 03:28:50 | Nokia MW HC_P0 Observing Performance Issue at MAK0765_1-MAK0007_11 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | makkah | Sceco | TX NSA | MAK0765_1-MAK0007_11 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:50 | 10/16/2025 11:25:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001216 | PCM-20251008-00002025 | TT-20251008-02080 | MW_HC | Region_5 | MAK0755 | MAK0755 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Husain Hassan Ishag Omer | 10/08/2025 15:28:52 | 10/22/2025 08:10:30 | 10/09/2025 03:28:52 | Nokia MW HC_P1 Observing Performance Issue at MAK0755-MAK0520 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK0755-MAK0520 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:52 | 10/09/2025 10:39:45 | 10/22/2025 07:01:53 | 10/22/2025 07:01:56 | 10/22/2025 07:02:00 | 10/22/2025 08:10:30 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001217 | PCM-20251008-00002026 | TT-20251008-02081 | MW_HC | Region_5 | MAK0725 | MAK0725 |  |  |  | Muhammad Saleem Iqbal | 10/08/2025 15:28:52 | 10/08/2025 22:14:50 | 10/09/2025 03:28:52 | Nokia MW HC_P1 Observing Performance Issue at MAK0725-MK2-4 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | makkah | Sceco | TX NSA | MAK0725-MK2-4 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:52 | 10/08/2025 22:14:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001219 | PCM-20251008-00002028 | TT-20251008-02083 | MW_HC | Region_5 | MAK0587 | MAK0587 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/08/2025 15:28:55 | 10/08/2025 15:28:55 | 10/09/2025 03:28:55 | Nokia MW HC_P2 Observing Performance Issue at MAK0587-MAK0050_03 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0587-MAK0050_03 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001220 | PCM-20251008-00002029 | TT-20251008-02084 | MW_HC | Region_5 | MAK0583 | MAK0583 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/08/2025 15:28:56 | 10/21/2025 19:56:53 | 10/09/2025 03:28:56 | Nokia MW HC_P0 Observing Performance Issue at MAK0583-MAK0229-10 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | makkah | Sceco | TX NSA | MAK0583-MAK0229-10 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:56 | 10/21/2025 19:56:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001221 | PCM-20251008-00002030 | TT-20251008-02085 | MW_HC | Region_5 | MAK0547 | MAK0547 |  |  |  | Amjad Ali Muhammad Parves | 10/08/2025 15:28:57 | 10/08/2025 16:42:57 | 10/09/2025 03:28:57 | Nokia MW HC_P1 Observing Performance Issue at MAK0547-MAK0527 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK0547-MAK0527 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:57 | 10/08/2025 16:42:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001222 | PCM-20251008-00002031 | TT-20251008-02086 | MW_HC | Region_5 | MAK0546 | MAK0546 |  |  |  | Amr Abdulla Ali Othman | 10/08/2025 15:28:58 | 10/08/2025 15:28:58 | 10/09/2025 03:28:58 | Nokia MW HC_P1 Observing Performance Issue at MAK0546-MAK0544 _02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0546-MAK0544 _02 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001223 | PCM-20251008-00002032 | TT-20251008-02087 | MW_HC | Region_5 | MAK0533 | MAK0533 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/08/2025 15:28:59 | 10/21/2025 19:56:54 | 10/09/2025 03:28:59 | Nokia MW HC_P2 Observing Modem Down at MAK0533-MAK0201 _03 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Generator_SG | TX NSA | MAK0533-MAK0201 _03 | FLM_TE | [8 empty] | API | 10/08/2025 15:28:59 | 10/21/2025 19:56:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001224 | PCM-20251008-00002033 | TT-20251008-02088 | MW_HC | Region_5 | MAK0385 | MAK0385 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:29:00 | 10/16/2025 11:25:48 | 10/09/2025 03:29:00 | Nokia MW HC_P0 Observing Performance Issue at MAK0385-MAK0066-9 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | makkah | Sceco | TX NSA | MAK0385-MAK0066-9 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:00 | 10/16/2025 11:25:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001225 | PCM-20251008-00002034 | TT-20251008-02089 | MW_HC | Region_5 | MAK0325 | MAK0325 |  |  |  | Husain Hassan Ishag Omer | 10/08/2025 15:29:02 | 10/09/2025 10:39:46 | 10/09/2025 03:29:02 | Nokia MW HC_P2 Observing Performance Issue at MAK0325-MAK0620_04 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK0325-MAK0620_04 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:02 | 10/09/2025 10:39:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001226 | PCM-20251008-00002035 | TT-20251008-02090 | MW_HC | Region_5 | MAK0323 | MAK0323 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:29:03 | 10/16/2025 11:25:48 | 10/09/2025 03:29:03 | Nokia MW HC_P1 Observing Performance Issue at MAK0323-MK3-28 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0323-MK3-28 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:03 | 10/16/2025 11:25:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001227 | PCM-20251008-00002036 | TT-20251008-02091 | MW_HC | Region_5 | MAK0312 | MAK0312 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/08/2025 15:29:04 | 10/08/2025 15:29:04 | 10/09/2025 03:29:04 | Nokia MW HC_P0 Observing Performance Issue at MAK0312-MAK0123-NE8 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK0312-MAK0123-NE8 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001228 | PCM-20251008-00002037 | TT-20251008-02092 | MW_HC | Region_5 | MAK0308 | MAK0308 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 15:29:05 | 10/16/2025 11:25:49 | 10/09/2025 03:29:05 | Nokia MW HC_P1 Observing Performance Issue at MAK0308-MAK0385 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | SRAN | makkah | Sceco | TX NSA | MAK0308-MAK0385 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:05 | 10/16/2025 11:25:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001229 | PCM-20251008-00002038 | TT-20251008-02093 | MW_HC | Region_5 | MAK0274 | MAK0274 | Transsmission | MW_LOW_RSL | Link Alignment Issue | Husain Hassan Ishag Omer | 10/08/2025 15:29:06 | 10/09/2025 14:04:03 | 10/09/2025 03:29:06 | Nokia MW HC_P1 Observing Performance Issue at MAK0274-MAK0017-4 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0274-MAK0017-4 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:06 | 10/09/2025 10:39:46 | 10/09/2025 10:40:19 | 10/09/2025 10:40:22 | 10/09/2025 10:40:27 | 10/09/2025 14:04:03 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001230 | PCM-20251008-00002039 | TT-20251008-02094 | MW_HC | Region_5 | MAK0265 | MAK0265 |  |  |  | Husain Hassan Ishag Omer | 10/08/2025 15:29:07 | 10/09/2025 10:39:47 | 10/09/2025 03:29:07 | Nokia MW HC_P1 Observing Performance Issue at MAK0265 - 1-MAK0115-1 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | makkah | Sceco | TX NSA | MAK0265 - 1-MAK0115-1 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:07 | 10/09/2025 10:39:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001232 | PCM-20251008-00002041 | TT-20251008-02096 | MW_HC | Region_5 | MAK0246 | MAK0246 |  |  |  | Amjad Ali Muhammad Parves | 10/08/2025 15:29:09 | 10/08/2025 16:42:57 | 10/09/2025 03:29:09 | Nokia MW HC_P0 Observing Performance Issue at MAK0246-MAK0085-3 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0246-MAK0085-3 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:09 | 10/08/2025 16:42:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001234 | PCM-20251008-00002042 | TT-20251008-02097 | MW_HC | Region_5 | MAK0245 | MAK0245 |  |  |  | Zakir Hossan | 10/08/2025 15:29:12 | 10/18/2025 14:14:03 | 10/09/2025 03:29:12 | Nokia MW HC_P1 Observing Performance Issue at MAK0245-MAK2077 _02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | makkah | Sceco | TX NSA | MAK0245-MAK2077 _02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:12 | 10/18/2025 14:14:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001238 | PCM-20251008-00002047 | TT-20251008-02103 | MW_HC | Region_5 | MAK0078 | MAK0078 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/08/2025 15:29:17 | 10/08/2025 17:01:36 | 10/09/2025 03:29:17 | Nokia MW HC_P1 Observing Performance Issue at MAK0078-MAK0178_10 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | makkah | Sceco_STB | TX NSA | MAK0078-MAK0178_10 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:17 | 10/08/2025 17:01:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001239 | PCM-20251008-00002050 | TT-20251008-02106 | MW_HC | Region_5 | MAK0058 | MAK0058 | Transsmission | MW_Connectors | Replace Indoor MW Connector | IJAZ ALI | 10/08/2025 15:29:17 | 10/23/2025 19:29:37 | 10/09/2025 03:29:17 | Nokia MW HC_P1 Observing Performance Issue at MAK0058-10-MAK0928-RADIO | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | VIP | 2G | makkah | Sceco | TX NSA | MAK0058-10-MAK0928-RADIO | FLM_TE | [8 empty] | API | 10/08/2025 15:29:17 | 10/23/2025 18:16:16 | 10/23/2025 19:29:25 |  |  | 10/23/2025 19:29:37 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001240 | PCM-20251008-00002052 | TT-20251008-02109 | MW_HC | Region_5 | MAK0048 | MAK0048 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/08/2025 15:29:19 | 10/21/2025 19:56:55 | 10/09/2025 03:29:19 | Nokia MW HC_P2 Observing Modem Down at MAK0048-MAK0611_03 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0048-MAK0611_03 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:19 | 10/21/2025 19:56:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001242 | PCM-20251008-00002054 | TT-20251008-02111 | MW_HC | Region_4 | KAU0616 | KAU0616 |  |  |  | Khizer Hayat | 10/08/2025 15:29:21 | 10/09/2025 16:53:16 | 10/09/2025 03:29:21 | Nokia MW HC_P1 Observing Performance Issue at KAU0616-KAU0303-NE2 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | KAU0616-KAU0303-NE2 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:21 | 10/09/2025 16:53:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001243 | PCM-20251008-00002055 | TT-20251008-02112 | MW_HC | Region_5 | JURY0904 | JURY0904 |  |  |  | Amr Abdulla Ali Othman | 10/08/2025 15:29:22 | 10/08/2025 15:29:22 | 10/09/2025 03:29:22 | Nokia MW HC_P1 Observing Performance Issue at JURY0904-ABU0876_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | JURY0904-ABU0876_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001244 | PCM-20251008-00002056 | TT-20251008-02113 | MW_HC | Region_4 | JED6015 | JED6015 |  |  |  | Mohamed Farag Abdelbary | 10/08/2025 15:29:23 | 10/09/2025 14:52:46 | 10/09/2025 03:29:23 | Nokia MW HC_P2 Observing Performance Issue at JED6015-JED0941 _02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED6015-JED0941 _02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:23 | 10/09/2025 14:52:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001245 | PCM-20251008-00002057 | TT-20251008-02114 | MW_HC | Region_4 | JED2137 | JED2137 | Equipment | BSS_HW_fault | Replace RRU | MALIK ATIF ZAMAN | 10/08/2025 15:29:24 | 10/17/2025 16:49:05 | 10/09/2025 03:29:24 | Nokia MW HC_P0 Observing Performance Issue at JED2137-JED0702_4 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2137-JED0702_4 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:24 | 10/08/2025 16:09:05 | 10/17/2025 11:51:01 | 10/17/2025 11:51:03 | 10/17/2025 12:53:53 | 10/17/2025 16:49:05 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001246 | PCM-20251008-00002058 | TT-20251008-02115 | MW_HC | Region_4 | JED2053 | JED2053 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/08/2025 15:29:25 | 10/11/2025 13:44:11 | 10/09/2025 03:29:25 | Nokia MW HC_P2 Observing Performance Issue at JED2053-JD1-32 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED2053-JD1-32 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:25 | 10/11/2025 13:42:40 | 10/11/2025 13:44:07 | 10/11/2025 13:44:09 | 10/11/2025 13:44:11 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001247 | PCM-20251008-00002059 | TT-20251008-02116 | MW_HC | Region_4 | JED0917 | JED0917 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:29:27 | 10/08/2025 16:09:05 | 10/09/2025 03:29:27 | Nokia MW HC_P2 Observing Modem Down at JED0917-JED0676_NE7 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0917-JED0676_NE7 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:27 | 10/08/2025 16:09:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001249 | PCM-20251008-00002061 | TT-20251008-02118 | MW_HC | Region_4 | JED0991 | JED0991 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | BARKAT ALI MAIN HILAL | 10/08/2025 15:29:29 | 10/17/2025 13:18:46 | 10/09/2025 03:29:29 | Nokia MW HC_P2 Observing Performance Issue at JED0991-JED0899_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED0991-JED0899_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:29 | 10/08/2025 15:36:29 | 10/15/2025 10:57:25 | 10/15/2025 10:57:32 | 10/15/2025 11:25:45 | 10/17/2025 13:18:46 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001251 | PCM-20251008-00002063 | TT-20251008-02120 | MW_HC | Region_4 | JED0692 | JED0692 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:29:31 | 10/08/2025 16:09:06 | 10/09/2025 03:29:31 | Nokia MW HC_P1 Observing Performance Issue at JED0692-JED0178 _02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | jeddah | Sceco | TX NSA | JED0692-JED0178 _02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:31 | 10/08/2025 16:09:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001252 | PCM-20251008-00002064 | TT-20251008-02121 | MW_HC | Region_4 | JED0976 | JED0976 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:29:32 | 10/08/2025 15:29:32 | 10/09/2025 03:29:32 | Nokia MW HC_P2 Observing Performance Issue at JED0976-JED0078 - 5 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED0976-JED0078 - 5 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001253 | PCM-20251008-00002065 | TT-20251008-02122 | MW_HC | Region_4 | JED0832 | JED0832 | Equipment | SFP_BTS | Clean SFP | Khaled Mohammad Abdallah | 10/08/2025 15:29:33 | 10/09/2025 00:39:41 | 10/09/2025 03:29:33 | Nokia MW HC_P2 Observing Modem Down at JED0832-JED0071-8 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0832-JED0071-8 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:33 | 10/09/2025 00:39:21 | 10/09/2025 00:39:28 |  |  | 10/09/2025 00:39:41 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001254 | PCM-20251008-00002066 | TT-20251008-02123 | MW_HC | Region_4 | JED0101 | JED0101 |  |  |  | Mohammed Ramadan A Abu Abid | 10/08/2025 15:29:34 | 10/08/2025 17:11:47 | 10/09/2025 03:29:34 | Nokia MW HC_P2 Observing Performance Issue at JED0101-JD3-20 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED0101-JD3-20 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:34 | 10/08/2025 17:11:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001255 | PCM-20251008-00002068 | TT-20251008-02125 | MW_HC | Region_4 | JED2027 | JED2027 |  |  |  | Nazeer Mohammed | 10/08/2025 15:29:36 | 10/09/2025 13:22:11 | 10/09/2025 03:29:36 | Nokia MW HC_P0 Observing Performance Issue at JED2027-JED2025_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED2027-JED2025_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:36 | 10/09/2025 13:22:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001257 | PCM-20251008-00002069 | TT-20251008-02126 | MW_HC | Region_6 | BAH0008 | BAH0008 |  |  |  | SHAH KHALID | 10/08/2025 15:29:37 | 10/09/2025 14:33:34 | 10/09/2025 03:29:37 | Nokia MW HC_P2 Observing Performance Issue at BAH0008 -BAH0009_3 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0008 -BAH0009_3 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:37 | 10/08/2025 15:31:09 | 10/09/2025 14:33:08 | 10/09/2025 14:33:28 | 10/09/2025 14:33:34 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001258 | PCM-20251008-00002070 | TT-20251008-02127 | MW_HC | Region_4 | JED2004 | JED2004 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 15:29:39 | 10/08/2025 15:29:39 | 10/09/2025 03:29:39 | Nokia MW HC_P2 Observing Modem Down at JED2004-JED0184- 11 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED2004-JED0184- 11 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001260 | PCM-20251008-00002072 | TT-20251008-02128 | MW_HC | Region_4 | HAW0298 | HAW0298 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 15:29:40 | 10/09/2025 10:07:26 | 10/09/2025 03:29:40 | Nokia MW HC_P2 Observing Performance Issue at HAW0298-HAW0294 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | taif | Sceco | TX NSA | HAW0298-HAW0294 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:40 | 10/09/2025 10:07:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251008001262 | PCM-20251008-00002074 | TT-20251008-02130 | MW_HC | Region_4 | JED0407 | JED0407 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 10/08/2025 15:29:42 | 10/23/2025 19:34:10 | 10/09/2025 03:29:42 | Nokia MW HC_P1 Observing Performance Issue at JED0407-JED0066 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0407-JED0066 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:42 | 10/19/2025 11:12:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001263 | PCM-20251008-00002075 | TT-20251008-02131 | MW_HC | Region_4 | JED2034 | JED2034 |  |  |  | Nazeer Mohammed | 10/08/2025 15:29:43 | 10/09/2025 13:22:19 | 10/09/2025 03:29:43 | Nokia MW HC_P1 Observing Performance Issue at JED2034-01-JED0189-6 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED2034-01-JED0189-6 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:43 | 10/09/2025 13:22:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001264 | PCM-20251008-00002076 | TT-20251008-02132 | MW_HC | Region_4 | JED0301 | JED0301 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 15:29:44 | 10/08/2025 16:09:07 | 10/09/2025 03:29:44 | Nokia MW HC_P2 Observing Performance Issue at JED0301 _01-JED0869_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0301 _01-JED0869_02 | FLM_TE | [8 empty] | API | 10/08/2025 15:29:44 | 10/08/2025 16:09:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001302 | PCM-20251008-00002139 | TT-20251008-02192 | Telecom | Region_4 | SQR0184 | SQR0184 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/08/2025 16:05:57 | 10/10/2025 11:36:46 | 10/09/2025 04:05:57 | ODU CPU / Cable Open at SQR0184 on 10.88.220.151 @ Generator_DG | 10/08/2025 16:04:33 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/08/2025 16:04:34 | P2 | 2G | alaith | Generator_DG | TX NSA | SQR0184 | FLM_TE | [8 empty] | API | 10/08/2025 16:05:57 | 10/10/2025 11:32:21 | 10/10/2025 11:36:37 |  |  | 10/10/2025 11:36:46 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001314 | PCM-20251008-00002164 | TT-20251008-02223 | EM | Region_2 | KHJ0301 | KJ1 |  |  |  | Ajmal Hafeez Hafeez Ahmed Awan | 10/08/2025 16:22:29 | 10/09/2025 10:38:53 | 10/08/2025 20:22:29 | AMBIENT_TEMP_FLUCT at KHJ0301_OCS @ Sceco_STB | 10/08/2025 16:20:57 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/08/2025 16:20:49 | P1 | SRAN | al kharj | Sceco_STB | DWDM NSA | KHJ0301 | FLM_EM | [5 empty] | 0-TO HAWTA8712-SEC0040(2-A) |  |  | API | 10/08/2025 16:22:29 | 10/09/2025 10:38:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008001338 | PCM-20251008-00002198 | TT-20251008-02244 | EM | Region_4 | BHMF2137 | BHMF2137 |  |  |  | Khizer Hayat | 10/08/2025 16:38:38 | 10/09/2025 16:53:17 | 10/08/2025 22:38:38 | 1(2G/LTE) sites down under BHMF2137-P3/BHMF2137-P3 @ Generator_SG | 10/08/2025 16:30:00 | Major | 7706 | BTS O&M LINK FAILURE | 10/08/2025 16:29:57 | P3 | 2G | jeddah | Generator_SG | 2G SA | BHMF2137-P3 | FLM_TE | BHMF2137 | Results: DOWN SITE HUB BHMF2137-P3 BHMF2137 Summary: Hub: BHMF2137, Down Count: 1, Down Sites: BHMF2137-P3 Alarm Summary: BHMF2137 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/08/2025 16:38:38 | 10/09/2025 16:53:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001348 | PCM-20251008-00002212 | TT-20251008-02190 | Reference_telecom | Region_6 | TLT0743 | TLT0743 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/08/2025 16:42:25 | 10/12/2025 13:26:07 | 10/08/2025 22:42:25 | MW Link Down at TLT0743-LL // TT-20250921-00798-CSG-01 to KHNJ0849-LL-CSG-01 | 10/08/2025 15:47:26 | Major | 15269 | LOS | 10/08/2025 15:47:26 | P1 | 2G | tathleeth | Sceco_STB | IPRAN NSA | MW Link Down at TLT0743-LL // TT-20250921-00798-CSG-01 to KHNJ0849-LL-CSG-01 | FLM_TE |  |  | PCM-20251008-00002137 | Thanks to check local as all chain down visibiity now - ZHR0977 - TLT0743 | Thanks to check local as all chain down visibiity now - ZHR0977 - TLT0743 |  |  |  | API | 10/08/2025 16:42:25 | 10/08/2025 17:08:59 | 10/12/2025 13:26:00 |  |  | 10/12/2025 13:26:07 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001357 | PCM-20251008-00002232 | TT-20251008-02279 | Reference_telecom | Region_2 | RIYD1W6008 | RIYD1W6008 |  |  |  | Abdelrahim Abdalla Abdelrahim Khairy | 10/08/2025 16:46:57 | 10/20/2025 09:53:54 | 10/09/2025 04:46:57 | RIYD1W6008 Partial Down | 10/08/2025 16:34:33 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/08/2025 16:34:33 | P1 | WIFI | riyadh | Sceco | Wifi SA | RIYD1W6008_4-GF-AP04 | FLM_TE | [8 empty] | API | 10/08/2025 16:46:57 | 10/11/2025 12:36:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001382 | PCM-20251008-00002287 | TT-20251008-02316 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/08/2025 17:03:49 | 10/08/2025 17:13:52 | 10/09/2025 05:03:49 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/08/2025 16:57:08 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/08/2025 16:57:04 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/08/2025 17:03:49 | 10/08/2025 17:13:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001405 | PCM-20251008-00002324 | TT-20251005-01890 | MW_HC | Region_5 | MAK2090 | MAK2090 |  |  |  | Husain Hassan Ishag Omer | 10/08/2025 17:24:07 | 10/09/2025 10:39:48 | 10/09/2025 05:24:07 | As BO Requested MW Nokia Observing H flapping MAK2090-MAK2077 | 10/05/2025 12:17:14 | Minor | 113388 | LOF | 10/05/2025 12:17:15 | P2 | 2G | makkah | Sceco | TX NSA | MAK2090-MAK2077 | FLM_TE |  |  | PCM-20251008-00002315 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/08/2025 17:24:07 | 10/09/2025 10:39:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001408 | PCM-20251008-00002328 | TT-20251008-02356 | Reference_telecom | Region_2 | RAS0098 | RAS0098 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/08/2025 17:26:29 | 10/09/2025 01:48:35 | 10/08/2025 23:26:29 | IN_PWR_HIGH ALARM AT RAS0098 ¦¦ REF::TT-20251005-01825 | 10/05/2025 16:09:47 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/05/2025 16:09:47 | P1 | SRAN | al rass | Sceco_STB | DWDM NSA | RAS0098 | FLM_TE | [8 empty] | API | 10/08/2025 17:26:29 | 10/09/2025 01:48:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001409 | PCM-20251008-00002329 | TT-20251006-01583 | MW_HC | Region_1 | UQR0722 | UQR0722 |  |  |  | Mohamed Magdy Fouad Zayed | 10/08/2025 17:26:30 | 10/08/2025 17:29:35 | 10/09/2025 05:26:30 | (As per BO Request) Huawei MW HC Observing PM errors and RSL degradation at MW link UQR0722 dir HFF9016 | 10/06/2025 14:38:38 | Minor | 1-631 | MW_LOF | 10/06/2025 14:38:38 | P3 | SRAN | hafouf | Power Cube | TX NSA | UQR0722 | FLM_TE |  | LINK STILL COUNTING ERRORS | PCM-20251008-00002286 | LINK STILL COUNTING ERRORS | LINK STILL COUNTING ERRORS |  |  |  | API | 10/08/2025 17:26:30 | 10/08/2025 17:29:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001422 | PCM-20251008-00002350 | TT-20251008-02075 | MW_HC | Region_6 | QFL0110 | QFL0110 | Transsmission | SFP_Transmission | Reset SFP | Mohammed Sideag Mohammed Ali | 10/08/2025 17:36:46 | 10/08/2025 19:02:17 | 10/09/2025 05:36:46 | Nokia MW HC_P2 Observing Performance Issue at QFL0110-QFL0032_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jizan | Sceco | TX NSA | QFL0110-QFL0032_02 | FLM_TE |  |  | PCM-20251008-00002297 | Currently link is cleared & under observation | Currently link is cleared & under observation |  |  |  | API | 10/08/2025 17:36:46 | 10/08/2025 19:01:16 | 10/08/2025 19:01:48 |  |  | 10/08/2025 19:02:17 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001426 | PCM-20251008-00002359 | TT-20251008-02384 | Reference_telecom | Region_4 | TF1 | TF1 |  |  |  | Rashid Shafique | 10/08/2025 17:39:08 | 10/14/2025 10:16:58 | 10/08/2025 23:39:08 | SHELF_AREA_POWER_OVER ALARM AT TF1 ¦¦REF :: TT-20250318-01175 | 10/07/2025 18:42:25 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/07/2025 18:42:25 | P1 | BSC | taif | Sceco_STB | DWDM NSA | TF1 | FLM_TE | [8 empty] | API | 10/08/2025 17:39:08 | 10/14/2025 10:16:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001434 | PCM-20251008-00002371 | TT-20250928-02013 | Telecom | Region_4 | USF0717 | USF0717 |  |  |  | Israr Ahmed Muhammad Ghauri | 10/08/2025 17:44:18 | 10/08/2025 19:07:51 | 10/08/2025 23:44:18 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at USF0717-P2-USF @ Generator_SG | 09/28/2025 17:44:25 | Major | 7607 | TRX OPERATION DEGRADED | 09/28/2025 17:44:22 | P2 | 2G | jeddah | Generator_SG | 2G_TRX NSA | USF0717 | FLM_TE |  |  | PCM-20251008-00002213 | Please check the site is down now | Please check the site is down now |  |  |  | API | 10/08/2025 17:44:18 | 10/08/2025 19:07:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001458 | PCM-20251008-00002409 | TT-20251008-02424 | Reference_telecom | Region_6 | ABDB0880 | ABDB0880 | Transsmission | MW_HW_fault | Replace Fiber Cable | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 18:07:53 | 10/21/2025 23:10:36 | 10/09/2025 06:07:53 | NEC MW Observing LAN Link at ABDB0880(10.154.167.58) | 10/02/2025 00:39:54 | Minor |  | LOF | 10/02/2025 00:39:54 | P3 | 2G | derb | Sceco | TX NSA | ABDB0880(10.154.167.58) | FLM_TE | [8 empty] | API | 10/08/2025 18:07:53 | 10/08/2025 18:38:04 | 10/21/2025 23:10:15 |  |  | 10/21/2025 23:10:36 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001470 | PCM-20251008-00002423 | TT-20251008-02437 | Reference_telecom | Region_6 | BHAB9038 | BHAB9038 |  |  |  | Fawad Khan | 10/08/2025 18:08:07 | 10/09/2025 00:34:35 | 10/09/2025 06:08:07 | NEC MW Observing Communication FAIL at BHAB9038_1(10.154.168.166) | 09/27/2025 03:07:08 | Minor |  | LOF | 09/27/2025 03:07:08 | P1 | Repeater | namas | Generator_SG | TX NSA | BHAB9038_1(10.154.168.166) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:07 | 10/09/2025 00:34:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001473 | PCM-20251008-00002426 | TT-20251008-02440 | Reference_telecom | Region_6 | DAR0954 | DAR0954 |  |  |  | Muhammad Ali | 10/08/2025 18:08:10 | 10/08/2025 18:16:33 | 10/09/2025 06:08:10 | NEC MW Observing Power Supply at DAR0954(10.1.173.2) | 10/06/2025 04:29:32 | Minor |  | LOF | 10/06/2025 04:29:32 | P2 | 2G | dair | Sceco | TX NSA | DAR0954(10.1.173.2) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:10 | 10/08/2025 18:16:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001489 | PCM-20251008-00002441 | TT-20251008-02455 | Reference_telecom | Region_6 | DRB0038 | DRB0038 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 18:08:40 | 10/08/2025 18:38:05 | 10/09/2025 06:08:40 | NEC MW Observing LOF,RX Level,Frame ID at DRB0038(10.154.171.3) | 10/01/2025 21:51:13 | Minor |  | LOF | 10/01/2025 21:51:13 | P2 | 2G | derb | Sceco | TX NSA | DRB0038(10.154.171.3) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:40 | 10/08/2025 18:38:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001490 | PCM-20251008-00002442 | TT-20251008-02456 | Reference_telecom | Region_6 | DRB0165 | DRB0165 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 18:08:41 | 10/21/2025 23:22:34 | 10/09/2025 06:08:41 | NEC MW Observing High BER at DRB0165(10.154.164.54) | 10/06/2025 06:27:57 | Minor |  | LOF | 10/06/2025 06:27:57 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0165(10.154.164.54) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:41 | 10/08/2025 18:38:10 | 10/21/2025 23:22:26 |  |  | 10/21/2025 23:22:34 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001494 | PCM-20251008-00002446 | TT-20251008-02460 | Reference_telecom | Region_4 | GMQ0153 | GMQ0153 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/08/2025 18:08:45 | 10/09/2025 00:47:50 | 10/09/2025 06:08:45 | NEC MW Observing IF Cable Short at GMQ0153(10.88.222.53) | 10/02/2025 12:35:02 | Minor |  | LOF | 10/02/2025 12:35:02 | P2 | 2G | adam | Generator_SG | TX NSA | GMQ0153(10.88.222.53) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:45 | 10/09/2025 00:47:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001495 | PCM-20251008-00002447 | TT-20251008-02461 | Reference_telecom | Region_4 | HBM0351 | HBM0351 | Transsmission | SFP_Transmission | Replace SFP | Asad Ullah Rahim Said | 10/08/2025 18:08:46 | 10/22/2025 11:02:28 | 10/09/2025 06:08:46 | NEC MW Observing High BER at HBM0351_1(10.154.143.87) | 10/01/2025 19:45:07 | Minor |  | LOF | 10/01/2025 19:45:07 | P3 | 2G | taif | Sceco | TX NSA | HBM0351_1(10.154.143.87) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:46 | 10/22/2025 11:02:28 | [5 empty] | Asad Ur Rehman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001496 | PCM-20251008-00002448 | TT-20251008-02462 | Reference_telecom | Region_1 | HFB0028 | HFB0028 | Transsmission | MW_HW_fault | Replace IF Cable | Mohamed Magdy Fouad Zayed | 10/08/2025 18:08:47 | 10/22/2025 18:15:54 | 10/09/2025 06:08:47 | NEC MW Observing LOF,Frame ID,High BER at HFB0028(10.74.86.101) | 09/29/2025 13:37:02 | Minor |  | LOF | 09/29/2025 13:37:02 | P3 | SRAN | hafouf | Sceco | TX NSA | HFB0028(10.74.86.101) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:47 | 10/22/2025 18:15:54 | [5 empty] | Mohamed Magdy Fouad Zayed | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001497 | PCM-20251008-00002449 | TT-20251008-02463 | Reference_telecom | Region_1 | HFBD0660 | HFBD0660 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/08/2025 18:08:48 | 10/08/2025 21:10:24 | 10/09/2025 06:08:48 | NEC MW Observing Radio Traffic Aggregation Link at HFBD0660-HFBD0011(10.159.106.134) | 09/28/2025 05:58:28 | Minor |  | LOF | 09/28/2025 05:58:28 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFBD0660-HFBD0011(10.159.106.134) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:48 | 10/08/2025 21:10:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001500 | PCM-20251008-00002452 | TT-20251008-02468 | Reference_telecom | Region_4 | HJR9400 | HJR9400 |  |  |  | Khizer Hayat | 10/08/2025 18:08:51 | 10/09/2025 16:53:18 | 10/09/2025 06:08:51 | NEC MW Observing SFP Type Mismatch at HJR9400(10.88.224.99) | 09/23/2025 22:23:40 | Minor |  | LOF | 09/23/2025 22:23:40 | P1 | Repeater | jeddah | Generator_DG | TX NSA | HJR9400(10.88.224.99) | FLM_TE | [8 empty] | API | 10/08/2025 18:08:51 | 10/09/2025 16:53:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001510 | PCM-20251008-00002462 | TT-20251008-02479 | Reference_telecom | Region_4 | JDAP0940 | JDAP0940 |  |  |  | Mohamed Farag Abdelbary | 10/08/2025 18:09:03 | 10/09/2025 14:52:46 | 10/09/2025 06:09:03 | NEC MW Observing ODU CPU / Cable Open,LOF at JDAP0940(10.1.165.130) | 09/16/2025 08:23:29 | Minor |  | LOF | 09/16/2025 08:23:29 | VIP | 2G | jeddah | Sceco | TX NSA | JDAP0940(10.1.165.130) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:03 | 10/09/2025 14:52:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001515 | PCM-20251008-00002467 | TT-20251008-02484 | Reference_telecom | Region_4 | JDJZ0773 | JDJZ0773 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/08/2025 18:09:21 | 10/09/2025 00:47:51 | 10/09/2025 06:09:21 | NEC MW Observing Radio Traffic Aggregation Link,High BER,LOF,Frame ID,LOF,Frame ID at JDJZ0773_3(10.154.113.22) | 10/01/2025 19:28:44 | Minor |  | LOF | 10/01/2025 19:28:44 | P2 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0773_3(10.154.113.22) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:21 | 10/09/2025 00:47:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001516 | PCM-20251008-00002468 | TT-20251008-02485 | Reference_telecom | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 18:09:22 | 10/08/2025 18:38:10 | 10/09/2025 06:09:22 | NEC MW Observing LOF,LOF at JDJZ0785(10.154.170.186) | 10/01/2025 02:48:37 | Minor |  | LOF | 10/01/2025 02:48:37 | P1 | 2G | derb | Sceco_STB | TX NSA | JDJZ0785(10.154.170.186) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:22 | 10/08/2025 18:38:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001517 | PCM-20251008-00002470 | TT-20251008-02487 | Reference_telecom | Region_6 | JDJZ0785 | JDJZ0785 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 18:09:23 | 10/08/2025 18:38:11 | 10/09/2025 06:09:23 | NEC MW Observing XIF at JDJZ0785-3(10.154.170.180) | 10/02/2025 00:59:07 | Minor |  | LOF | 10/02/2025 00:59:07 | P1 | 2G | derb | Sceco_STB | TX NSA | JDJZ0785-3(10.154.170.180) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:23 | 10/08/2025 18:38:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001518 | PCM-20251008-00002471 | TT-20251008-02488 | Reference_telecom | Region_6 | JDJZ0787 | JDJZ0787 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/08/2025 18:09:25 | 10/08/2025 18:38:12 | 10/09/2025 06:09:25 | NEC MW Observing TX Input at JDJZ0787(10.199.24.26) | 10/01/2025 02:12:48 | Minor |  | LOF | 10/01/2025 02:12:48 | P3 | 2G | derb | Sceco | TX NSA | JDJZ0787(10.199.24.26) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:25 | 10/08/2025 18:38:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001519 | PCM-20251008-00002472 | TT-20251008-02489 | Reference_telecom | Region_6 | JDJZ0788 | JDJZ0788 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:25 | 10/08/2025 19:20:49 | 10/09/2025 06:09:25 | NEC MW Observing MODEM Power Supply Alarm,XIF,High BER at JDJZ0788-1(10.154.170.55) | 10/02/2025 06:09:01 | Minor |  | LOF | 10/02/2025 06:09:01 | P1 | 2G | baish | Sceco_STB | TX NSA | JDJZ0788-1(10.154.170.55) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:25 | 10/08/2025 19:20:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001520 | PCM-20251008-00002473 | TT-20251008-02490 | Reference_telecom | Region_6 | JDJZ0788 | JDJZ0788 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:26 | 10/08/2025 19:20:50 | 10/09/2025 06:09:26 | NEC MW Observing SFP Type Mismatch at JDJZ0788-2(10.199.24.25) | 10/01/2025 02:12:47 | Minor |  | LOF | 10/01/2025 02:12:47 | P1 | 2G | baish | Sceco_STB | TX NSA | JDJZ0788-2(10.199.24.25) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:26 | 10/08/2025 19:20:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001521 | PCM-20251008-00002474 | TT-20251008-02491 | Reference_telecom | Region_6 | JDJZ0789 | JDJZ0789 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:27 | 10/08/2025 19:20:50 | 10/09/2025 06:09:27 | NEC MW Observing RX Level,RX Level,LOF,LOF at JDJZ0789-2(10.154.170.56) | 10/02/2025 00:58:45 | Minor |  | LOF | 10/02/2025 00:58:45 | P1 | 2G | baish | Sceco | TX NSA | JDJZ0789-2(10.154.170.56) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:27 | 10/08/2025 19:20:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001522 | PCM-20251008-00002475 | TT-20251008-02492 | Reference_telecom | Region_4 | JDRS0764 | JDRS0764 |  |  |  | Khizer Hayat | 10/08/2025 18:09:29 | 10/09/2025 16:53:19 | 10/09/2025 06:09:29 | NEC MW Observing ODU CPU / Cable Open,ODU Power Supply at JDRS0764(10.154.114.14) | 09/19/2025 18:29:58 | Minor |  | LOF | 09/19/2025 18:29:58 | P2 | 2G | jeddah | Sceco | TX NSA | JDRS0764(10.154.114.14) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:29 | 10/09/2025 16:53:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001524 | PCM-20251008-00002477 | TT-20251008-02494 | Reference_telecom | Region_6 | JEC0088 | JEC0088 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:31 | 10/21/2025 17:01:17 | 10/09/2025 06:09:31 | NEC MW Observing MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm at JEC0088(10.199.24.88) | 09/30/2025 16:57:00 | Minor |  | LOF | 09/30/2025 16:57:00 | P2 | 2G | baish | Sceco_STB | TX NSA | JEC0088(10.199.24.88) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:31 | 10/08/2025 19:20:51 | 10/21/2025 17:00:36 | 10/21/2025 17:00:40 | 10/21/2025 17:01:17 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001526 | PCM-20251008-00002479 | TT-20251008-02496 | Reference_telecom | Region_6 | JEC0154 | JEC0154 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:33 | 10/08/2025 19:20:53 | 10/09/2025 06:09:33 | NEC MW Observing XIF at JEC0154-1(10.154.172.179) | 09/30/2025 16:41:51 | Minor |  | LOF | 09/30/2025 16:41:51 | VIP | 2G | baish | Generator_SG | TX NSA | JEC0154-1(10.154.172.179) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:33 | 10/08/2025 19:20:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001528 | PCM-20251008-00002481 | TT-20251008-02498 | Reference_telecom | Region_6 | JEC0331 | JEC0331 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:36 | 10/23/2025 21:24:39 | 10/09/2025 06:09:36 | NEC MW Observing MODEM Power Supply Alarm,Module,Module,Radio Traffic Aggregation Link,XIF at JEC0331(10.154.126.6) | 10/06/2025 08:52:19 | Minor |  | LOF | 10/06/2025 08:52:19 | P2 | 2G | baish | Generator_SG | TX NSA | JEC0331(10.154.126.6) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:36 | 10/08/2025 19:20:54 | 10/23/2025 21:24:14 |  |  | 10/23/2025 21:24:39 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001529 | PCM-20251008-00002482 | TT-20251008-02499 | Reference_telecom | Region_6 | JEC0377 | JEC0377 | Transsmission | MW_HW_fault | Replace FAN | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:09:37 | 10/23/2025 21:22:47 | 10/09/2025 06:09:37 | NEC MW Observing FAN FAIL,LOF at JEC0377(10.154.126.8) | 10/02/2025 04:19:34 | Minor |  | LOF | 10/02/2025 04:19:34 | VIP | 2G | baish | Generator_SG | TX NSA | JEC0377(10.154.126.8) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:37 | 10/08/2025 19:20:55 | 10/23/2025 21:22:23 |  |  | 10/23/2025 21:22:47 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001530 | PCM-20251008-00002483 | TT-20251008-02500 | Reference_telecom | Region_4 | JED0125 | JED0125 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 18:09:38 | 10/08/2025 20:16:12 | 10/09/2025 06:09:38 | NEC MW Observing LOF,LOF,Frame ID,Frame ID at JED0125_1(10.154.142.201) | 10/01/2025 19:06:31 | Minor |  | LOF | 10/01/2025 19:06:31 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED0125_1(10.154.142.201) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:38 | 10/08/2025 20:16:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001532 | PCM-20251008-00002485 | TT-20251008-02502 | Reference_telecom | Region_4 | JED0182 | JED0182 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 18:09:40 | 10/08/2025 20:57:13 | 10/09/2025 06:09:40 | NEC MW Observing LAN Link at JED0182(10.154.140.35) | 09/22/2025 14:17:07 | Minor |  | LOF | 09/22/2025 14:17:07 | P2 | 2G | jeddah | Sceco | TX NSA | JED0182(10.154.140.35) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:40 | 10/08/2025 20:57:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001533 | PCM-20251008-00002486 | TT-20251008-02503 | Reference_telecom | Region_4 | JED0221 | JED0221 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 18:09:41 | 10/08/2025 18:09:41 | 10/09/2025 06:09:41 | NEC MW Observing LOF at JED0221-A1(10.1.165.121) | 09/20/2025 16:16:08 | Minor |  | LOF | 09/20/2025 16:16:08 | P2 | 2G | jeddah | Sceco | TX NSA | JED0221-A1(10.1.165.121) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001534 | PCM-20251008-00002487 | TT-20251008-02504 | Reference_telecom | Region_4 | JED0476 | JED0476 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 18:09:42 | 10/08/2025 18:09:42 | 10/09/2025 06:09:42 | NEC MW Observing LOF at JED0476(10.99.254.169) | 09/20/2025 10:55:49 | Minor |  | LOF | 09/20/2025 10:55:49 | P1 | 2G | jeddah | Sceco | TX NSA | JED0476(10.99.254.169) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001535 | PCM-20251008-00002488 | TT-20251008-02505 | Reference_telecom | Region_4 | JED0703 | JED0703 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 18:09:44 | 10/08/2025 20:16:12 | 10/09/2025 06:09:44 | NEC MW Observing ODU Alarm,TX Power,RX Level,RX Level,RX Level,RX Level,LOF,LOF,LOF,LOF,Radio Traffic Aggregation Link at JED0703(10.1.169.241) | 10/01/2025 01:50:20 | Minor |  | LOF | 10/01/2025 01:50:20 | P3 | 2G | jeddah | Sceco | TX NSA | JED0703(10.1.169.241) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:44 | 10/08/2025 20:16:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001537 | PCM-20251008-00002490 | TT-20251008-02507 | Reference_telecom | Region_4 | JED6125 | JED6125 |  |  |  | Mohamed Farag Abdelbary | 10/08/2025 18:09:49 | 10/09/2025 14:52:46 | 10/09/2025 06:09:49 | NEC MW Observing Frame ID,LOF,RX Level at JED6125(10.1.165.164) | 10/02/2025 20:36:48 | Minor |  | LOF | 10/02/2025 20:36:48 | P3 | 2G | jeddah | Sceco | TX NSA | JED6125(10.1.165.164) | FLM_TE | [8 empty] | API | 10/08/2025 18:09:49 | 10/09/2025 14:52:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001544 | PCM-20251008-00002497 | TT-20251008-02514 | Reference_telecom | Region_4 | KHL0711 | KHL0711 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/08/2025 18:10:07 | 10/09/2025 13:26:55 | 10/09/2025 06:10:07 | NEC MW Observing RX Level at KHL0711(10.154.115.5) | 09/18/2025 10:09:51 | Minor |  | LOF | 09/18/2025 10:09:51 | P3 | 2G | jeddah | Sceco | TX NSA | KHL0711(10.154.115.5) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:07 | 10/09/2025 13:22:21 | 10/09/2025 13:26:20 |  |  | 10/09/2025 13:26:55 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001546 | PCM-20251008-00002499 | TT-20251008-02516 | Reference_telecom | Region_4 | KMMD0639 | KMMD0639 |  |  |  | Nazeer Mohammed | 10/08/2025 18:10:09 | 10/09/2025 13:22:21 | 10/09/2025 06:10:09 | NEC MW Observing ODU CPU / Cable Open,ODU Power Supply at KMMD0639(10.154.115.119) | 09/20/2025 05:41:04 | Minor |  | LOF | 09/20/2025 05:41:04 | P2 | 2G | jeddah | Sceco | TX NSA | KMMD0639(10.154.115.119) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:09 | 10/09/2025 13:22:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001547 | PCM-20251008-00002500 | TT-20251008-02517 | Reference_telecom | Region_5 | MAK0099 | MAK0099 |  |  |  | Amjad Ali Muhammad Parves | 10/08/2025 18:10:11 | 10/09/2025 09:34:41 | 10/09/2025 06:10:11 | NEC MW Observing LOF,Frame ID at MAK0099(10.3.251.219) | 10/07/2025 17:25:09 | Minor |  | LOF | 10/07/2025 17:25:09 | P1 | 2G | makkah | Sceco_STB | TX NSA | MAK0099(10.3.251.219) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:11 | 10/09/2025 09:34:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001548 | PCM-20251008-00002501 | TT-20251008-02518 | Reference_telecom | Region_5 | MAK2064 | MAK2064 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 18:10:11 | 10/16/2025 11:25:49 | 10/09/2025 06:10:11 | NEC MW Observing Power Supply at MAK2064(10.248.218.250) | 10/07/2025 11:10:25 | Minor |  | LOF | 10/07/2025 11:10:25 | P3 | SRAN | makkah | Sceco | TX NSA | MAK2064(10.248.218.250) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:11 | 10/16/2025 11:25:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001549 | PCM-20251008-00002502 | TT-20251008-02519 | Reference_telecom | Region_5 | MAK6090 | MAK6090 |  |  |  | Atif Javed Javed Hussain | 10/08/2025 18:10:13 | 10/16/2025 11:25:50 | 10/09/2025 06:10:13 | NEC MW Observing LOF,Frame ID at MAK6090(10.99.249.74) | 10/06/2025 17:03:24 | Minor |  | LOF | 10/06/2025 17:03:24 | P3 | 2G | makkah | Sceco | TX NSA | MAK6090(10.99.249.74) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:13 | 10/16/2025 11:25:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001551 | PCM-20251008-00002504 | TT-20251008-02521 | Reference_telecom | Region_3 | MDHL0379 | MDHL0379 |  |  |  | Mohamed Naveed | 10/08/2025 18:10:15 | 10/08/2025 19:02:03 | 10/09/2025 06:10:15 | NEC MW Observing LOF,LOF,Frame ID,Frame ID,Frame ID,LOF,LOF,Frame ID at MDHL0379-MDHL0380(10.253.0.133) | 10/04/2025 07:08:01 | Minor |  | LOF | 10/04/2025 07:08:01 | P1 | SRAN | hail | Sceco_STB | TX NSA | MDHL0379-MDHL0380(10.253.0.133) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:15 | 10/08/2025 19:02:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001553 | PCM-20251008-00002506 | TT-20251008-02523 | Reference_telecom | Region_6 | MHL0138 | MHL0138 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/08/2025 18:10:17 | 10/08/2025 22:01:32 | 10/09/2025 06:10:17 | NEC MW Observing LAN Link at MHL0138(10.154.171.232) | 09/30/2025 16:37:11 | Minor |  | LOF | 09/30/2025 16:37:11 | P3 | 2G | mohail | Sceco | TX NSA | MHL0138(10.154.171.232) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:17 | 10/08/2025 22:01:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001554 | PCM-20251008-00002507 | TT-20251008-02524 | Reference_telecom | Region_4 | MKJD0570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/08/2025 18:10:18 | 10/09/2025 09:34:42 | 10/09/2025 06:10:18 | NEC MW Observing LOF,Frame ID at MKJD0570(10.154.128.242) | 10/07/2025 17:10:59 | Minor |  | LOF | 10/07/2025 17:10:59 | P2 | 2G | jeddah | Generator_DG | TX NSA | MKJD0570(10.154.128.242) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:18 | 10/09/2025 09:34:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001555 | PCM-20251008-00002508 | TT-20251008-02525 | Reference_telecom | Region_4 | MKJD0571 | MKJD0571 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 18:10:19 | 10/08/2025 20:16:13 | 10/09/2025 06:10:19 | NEC MW Observing ODU CPU / Cable Open,LOF at MKJD0571(10.1.164.121) | 10/01/2025 00:18:20 | Minor |  | LOF | 10/01/2025 00:18:20 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKJD0571(10.1.164.121) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:19 | 10/08/2025 20:16:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001556 | PCM-20251008-00002509 | TT-20251008-02526 | Reference_telecom | Region_4 | MKJD0572 | MKJD0572 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/08/2025 18:10:20 | 10/08/2025 20:16:13 | 10/09/2025 06:10:20 | NEC MW Observing RX Level,RX Level,LOF,Radio Traffic Aggregation Link,RX Level,LOF,LOF,LOF,RX Level,Radio Traffic Aggregation Link at MKJD0572_1(10.1.166.217) | 09/30/2025 16:34:54 | Minor |  | LOF | 09/30/2025 16:34:54 | P1 | 2G | jeddah | Generator_DG | TX NSA | MKJD0572_1(10.1.166.217) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:20 | 10/08/2025 20:16:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001557 | PCM-20251008-00002510 | TT-20251008-02527 | Reference_telecom | Region_4 | MKMD0555 | MKMD0555 |  |  |  | Nazeer Mohammed | 10/08/2025 18:10:21 | 10/09/2025 13:22:22 | 10/09/2025 06:10:21 | NEC MW Observing FAN FAIL at MKMD0555_5(10.154.115.22) | 09/19/2025 12:31:41 | Minor |  | LOF | 09/19/2025 12:31:41 | P1 | 2G | jeddah | Generator_DG | TX NSA | MKMD0555_5(10.154.115.22) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:21 | 10/09/2025 13:22:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001559 | PCM-20251008-00002513 | TT-20251008-02531 | Reference_telecom | Region_4 | MLJI0110 | MLJI0110 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 18:10:24 | 10/09/2025 15:07:38 | 10/09/2025 06:10:24 | NEC MW Observing FAN FAIL at MLJI0110(10.88.223.179) | 10/01/2025 05:49:20 | Minor |  | LOF | 10/01/2025 05:49:20 | P3 | 2G | alaith | Generator_SG | TX NSA | MLJI0110(10.88.223.179) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:24 | 10/09/2025 15:07:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001560 | PCM-20251008-00002514 | TT-20251008-02532 | Reference_telecom | Region_4 | NNL0175 | NNL0175 |  |  |  | Riasat Ali Allah Baksh | 10/08/2025 18:10:25 | 10/09/2025 15:07:39 | 10/09/2025 06:10:25 | NEC MW Observing ODU CPU / Cable Open,ODU Power Supply,SFP Type Mismatch at NNL0175(10.88.223.66) | 10/01/2025 05:46:25 | Minor |  | LOF | 10/01/2025 05:46:25 | P2 | 2G | alaith | Sceco | TX NSA | NNL0175(10.88.223.66) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:25 | 10/09/2025 15:07:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001567 | PCM-20251008-00002521 | TT-20251008-02539 | Reference_telecom | Region_6 | RYAB0646 | RYAB0646 |  |  |  | Umair Abbas Muhammad Abbas | 10/08/2025 18:10:46 | 10/08/2025 18:10:48 | 10/09/2025 06:10:46 | NEC MW Observing Low BER at RYAB0646(10.154.165.34) | 10/03/2025 14:16:06 | Minor |  | LOF | 10/03/2025 14:16:06 | P3 | 2G | turaib | Sceco_STB | TX NSA | RYAB0646(10.154.165.34) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:46 | 10/08/2025 18:10:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001572 | PCM-20251008-00002526 | TT-20251008-02544 | Reference_telecom | Region_4 | RYMK0549 | RYMK0549 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 18:10:52 | 10/09/2025 10:07:28 | 10/09/2025 06:10:52 | NEC MW Observing SBY TX Bus Error at RYMK0549-1(10.154.118.66) | 09/30/2025 16:57:44 | Minor |  | LOF | 09/30/2025 16:57:44 | P1 | 2G | taif | Generator_SG | TX NSA | RYMK0549-1(10.154.118.66) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:52 | 10/09/2025 10:07:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001573 | PCM-20251008-00002527 | TT-20251008-02545 | Reference_telecom | Region_6 | SAB0277 | SAB0277 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/08/2025 18:10:53 | 10/08/2025 19:20:56 | 10/09/2025 06:10:53 | NEC MW Observing RX Level,LOF,Communication FAIL,RX Level,LAN Link,LOF,Frame ID,LOF at SAB0277-SBA2022(10.1.173.20) | 10/02/2025 05:21:59 | Minor |  | LOF | 10/02/2025 05:21:59 | P1 | 2G | baish | Sceco | TX NSA | SAB0277-SBA2022(10.1.173.20) | FLM_TE | [8 empty] | API | 10/08/2025 18:10:53 | 10/08/2025 19:20:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001580 | PCM-20251008-00002534 | TT-20251008-02552 | Reference_telecom | Region_4 | SQR0184 | SQR0184 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/08/2025 18:11:02 | 10/10/2025 11:35:27 | 10/09/2025 06:11:02 | NEC MW Observing Low BER at SQR0184(10.88.220.151) | 10/03/2025 14:11:06 | Minor |  | LOF | 10/03/2025 14:11:06 | P2 | 2G | alaith | Generator_DG | TX NSA | SQR0184(10.88.220.151) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:02 | 10/10/2025 11:32:24 | 10/10/2025 11:35:17 |  |  | 10/10/2025 11:35:27 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001584 | PCM-20251008-00002538 | TT-20251008-02557 | Reference_telecom | Region_6 | TFBH0887 | TFBH0887 |  |  |  | SHAH KHALID | 10/08/2025 18:11:07 | 10/08/2025 18:23:31 | 10/09/2025 06:11:07 | NEC MW Observing SBY TX Bus Error at TFBH0887_1(10.88.221.1) | 09/02/2025 15:09:53 | Minor |  | LOF | 09/02/2025 15:09:53 | P1 | 2G | makhwa | Sceco_STB | TX NSA | TFBH0887_1(10.88.221.1) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:07 | 10/08/2025 18:23:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001589 | PCM-20251008-00002543 | TT-20251008-02562 | Reference_telecom | Region_6 | TFBH0887 | TFBH0887 |  |  |  | SHAH KHALID | 10/08/2025 18:11:15 | 10/08/2025 18:23:32 | 10/09/2025 06:11:15 | NEC MW Observing Low BER,High BER,Low BER at TFBH0887-IDU3(10.154.175.102) | 10/02/2025 06:00:45 | Minor |  | LOF | 10/02/2025 06:00:45 | P1 | 2G | makhwa | Sceco_STB | TX NSA | TFBH0887-IDU3(10.154.175.102) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:15 | 10/08/2025 18:23:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001591 | PCM-20251008-00002545 | TT-20251008-02564 | Reference_telecom | Region_6 | WDS0686 | WDS0686 |  |  |  | Ahmed Mamdouh Helal Helal | 10/08/2025 18:11:27 | 10/09/2025 10:45:21 | 10/09/2025 06:11:27 | NEC MW Observing SFP Type Mismatch at WDS0686(10.89.222.147) | 09/30/2025 17:02:14 | Minor |  | LOF | 09/30/2025 17:02:14 | P2 | 2G | wadi dawasar | Sceco_STB | TX NSA | WDS0686(10.89.222.147) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:27 | 10/09/2025 10:45:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001592 | PCM-20251008-00002546 | TT-20251008-02565 | Reference_telecom | Region_4 | TFSH9069 | TFSH9069 |  |  |  | Rashid Shafique | 10/08/2025 18:11:28 | 10/08/2025 18:53:20 | 10/09/2025 06:11:28 | NEC MW Observing High BER at TFSH9069-1(10.154.143.228) | 10/01/2025 19:32:28 | Minor |  | LOF | 10/01/2025 19:32:28 | P1 | Repeater | taif | Sceco_STB | TX NSA | TFSH9069-1(10.154.143.228) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:28 | 10/08/2025 18:53:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001595 | PCM-20251008-00002549 | TT-20251008-02568 | Reference_telecom | Region_6 | TLT0862 | TLT0862 |  |  |  | Umair Abbas Muhammad Abbas | 10/08/2025 18:11:32 | 10/08/2025 18:11:38 | 10/09/2025 06:11:32 | NEC MW Observing RX Level,RX Level,LOF,LOF at TLT0862(10.89.223.156) | 10/01/2025 13:59:24 | Minor |  | LOF | 10/01/2025 13:59:24 | P1 | 2G | turaib | Sceco_STB | TX NSA | TLT0862(10.89.223.156) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:32 | 10/08/2025 18:11:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251008001596 | PCM-20251008-00002550 | TT-20251008-02569 | Reference_telecom | Region_6 | WDS0740 | WDS0740 |  |  |  | Ahmed Mamdouh Helal Helal | 10/08/2025 18:11:33 | 10/11/2025 12:50:32 | 10/09/2025 06:11:33 | NEC MW Observing High BER at WDS0740(10.89.222.7) | 10/02/2025 06:08:58 | Minor |  | LOF | 10/02/2025 06:08:58 | P1 | 2G | wadi dawasar | Sceco_STB | TX NSA | WDS0740(10.89.222.7) | FLM_TE | [8 empty] | API | 10/08/2025 18:11:33 | 10/09/2025 10:45:22 | 10/11/2025 12:50:04 | 10/11/2025 12:50:27 | 10/11/2025 12:50:32 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001639 | PCM-20251008-00002610 | TT-20251008-02644 | Telecom | Region_4 | JED0984 | JED0984 | Equipment | BSS_HW_fault | Replace FAN | Mohammed Ramadan A Abu Abid | 10/08/2025 18:59:43 | 10/16/2025 13:52:09 | 10/09/2025 06:59:43 | BASE STATION INFORMATION (No module fan detected) at JED0984-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/08/2025 18:51:27 | Minor | 7115 | BASE STATION INFORMATION | 10/08/2025 18:51:18 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0984 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/08/2025 18:59:43 | 10/08/2025 19:00:35 | 10/12/2025 13:16:05 | 10/14/2025 09:52:50 | 10/14/2025 10:22:55 | 10/16/2025 13:52:09 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001643 | PCM-20251008-00002618 | TT-20251008-02626 | Telecom | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/08/2025 19:05:30 | 10/08/2025 20:21:03 | 10/09/2025 01:05:30 | 1(2G) 1(3G) 1(LTE) 2(5G) sites down under JED0984-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3,MAS0063-P3,JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/08/2025 18:45:29 | Major | 7706 | BTS O&M LINK FAILURE | 10/08/2025 18:45:23 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED6020-GSM-P3 2G_LTE,JED0984-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 5G,MAS0063-P3 3G | FLM_EM | JED6020 | Scattered sites: JED6020 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0984, MAS0030 observing no alarm flapped Kindly update TT under EM, FLM | PCM-20251008-00002603 | Scattered sites: JED6020 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0984, MAS0030 observing no alarm flapped Kindly update TT under EM, FLM | Scattered sites: JED6020 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. JED0984, MAS0030 observing no alarm flapped Kindly update TT under EM, FLM |  | sites down |  | API | 10/08/2025 19:05:30 | 10/08/2025 20:21:03 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001644 | PCM-20251008-00002619 | TT-20251008-02654 | Reference_telecom | Region_5 | MAK0206 | MAK0206 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Inam ullah | 10/08/2025 19:05:40 | 10/13/2025 17:09:33 | 10/09/2025 07:05:40 | LossOfSignal observed in MAK0206 -1 towards 10.10.143.98 @ Sceco | 10/08/2025 07:08:03 | Minor |  | LossOfSignal | 10/08/2025 07:05:16 | P2 | 2G | makkah | Sceco | TX NSA | MAK0206 | FLM_TE | [8 empty] | API | 10/08/2025 19:05:40 | 10/13/2025 15:22:31 | 10/13/2025 15:57:00 | 10/13/2025 15:57:11 | 10/13/2025 16:40:01 | 10/13/2025 17:09:33 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001666 | PCM-20251008-00002659 | TT-20251008-02694 | Reference_telecom | Region_4 | JED2577 | JED2577 | Equipment | BSS_HW_Stuck | Reset Interface Card | Abdullah Ahmad Mohammad Abdelsheekh | 10/08/2025 19:30:28 | 10/11/2025 10:35:04 | 10/09/2025 07:30:28 | ReplaceableUnitMissing observed in JED2577 towards 10.21.68.114 @ Sceco | 10/08/2025 07:30:16 | Minor |  | ReplaceableUnitMissing | 10/08/2025 07:30:12 | P3 | 2G | jeddah | Sceco | TX NSA | JED2577 | FLM_TE | [8 empty] | API | 10/08/2025 19:30:28 | 10/11/2025 10:29:28 | 10/11/2025 10:30:05 | 10/11/2025 10:30:33 | 10/11/2025 10:30:40 | 10/11/2025 10:35:04 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001669 | PCM-20251008-00002662 | TT-20251008-01983 | MW_HC | Region_5 | MAK0084 | MAK0084 |  |  |  | Amjad Ali Muhammad Parves | 10/08/2025 19:31:57 | 10/09/2025 09:34:43 | 10/09/2025 07:31:57 | Nokia MW HC_P1 Observing Performance Issue at MAK0084_01-MAK0020-6 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0084_01-MAK0020-6 | FLM_TE |  |  | PCM-20251008-00002627 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/08/2025 19:31:57 | 10/09/2025 09:34:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001675 | PCM-20251008-00002671 | TT-20251008-02703 | Telecom | Region_4 | JED2259 | JED2259 | Equipment | SFP_BTS | Clean SFP | BARKAT ALI MAIN HILAL | 10/08/2025 19:36:10 | 10/19/2025 17:44:08 | 10/09/2025 01:36:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/08/2025 19:35:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 19:35:10 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2259 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/08/2025 19:36:10 | 10/08/2025 20:57:16 | 10/12/2025 19:50:53 | 10/12/2025 19:51:02 | 10/12/2025 19:58:17 | 10/12/2025 22:00:25 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001676 | PCM-20251008-00002673 | TT-20251008-02388 | Telecom | Region_4 | JED1MN0667 | JED0667 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 19:36:35 | 10/09/2025 09:49:46 | 10/09/2025 01:36:35 | PT::BO need to check low availability issue at site JED1MN0667-NR2.6-P3 | 10/08/2025 17:40:54 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/08/2025 17:40:54 | P1 | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1MN0667-NR2.6-P3 | FLM_TE |  |  | PCM-20251008-00002366 | TWAMP alarm is fluctuating at site. JED1M8577-CA-L800-P3 is the TWAMP anchor for this site. | TWAMP alarm is fluctuating at site. JED1M8577-CA-L800-P3 is the TWAMP anchor for this site. |  |  |  | API | 10/08/2025 19:36:35 | 10/09/2025 09:49:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001683 | PCM-20251008-00002684 | TT-20251008-02721 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/08/2025 19:46:30 | 10/10/2025 12:56:44 | 10/09/2025 01:46:30 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/08/2025 16:46:16 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/08/2025 16:46:02 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/08/2025 19:46:30 | 10/10/2025 12:56:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001685 | PCM-20251008-00002687 | TT-20251008-02722 | Reference_telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/08/2025 19:48:33 | 10/16/2025 12:51:13 | 10/09/2025 07:48:33 | RF Unit RX Channel RTWP/RSSI Too Low at RIY0573-P2_SRAN-FON @ Sceco | 10/08/2025 16:48:32 | Minor | 26521 | RF Unit RX Channel RTWP/RSSI Too Low | 10/08/2025 16:48:27 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_TE | [8 empty] | API | 10/08/2025 19:48:33 | 10/10/2025 09:18:22 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001689 | PCM-20251008-00002693 | TT-20251008-02362 | Reference_telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 19:53:05 | 10/08/2025 20:57:16 | 10/09/2025 07:53:05 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/08/2025 15:27:47 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/08/2025 15:27:38 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0296 | FLM_TE |  |  | PCM-20251008-00002685 | Thanks to check related link JED0947-JED0759 | Thanks to check related link JED0947-JED0759 |  |  |  | API | 10/08/2025 19:53:05 | 10/08/2025 20:57:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001699 | PCM-20251008-00002708 | TT-20251008-02210 | Reference_telecom | Region_4 | JED0390 | JED0390 |  |  |  | BARKAT ALI MAIN HILAL | 10/08/2025 20:06:00 | 10/08/2025 20:57:18 | 10/09/2025 08:06:00 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0390-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/08/2025 14:18:58 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/08/2025 14:16:47 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0390 | FLM_TE |  |  | PCM-20251008-00002314 | Alarm Cleared. Please check and close with RCA. | Alarm Cleared. Please check and close with RCA. |  |  |  | API | 10/08/2025 20:06:00 | 10/08/2025 20:57:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001704 | PCM-20251008-00002714 | TT-20251008-02179 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 20:10:22 | 10/09/2025 09:49:47 | 10/09/2025 08:10:22 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/08/2025 15:55:05 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 15:54:59 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251008-00002129 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/08/2025 20:10:22 | 10/09/2025 09:49:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001706 | PCM-20251008-00002718 | TT-20251008-02742 | EM | Region_4 | JED1M7619 | JED0619 |  |  |  | Anas Mohamedelamin Abbas Mustafa | 10/08/2025 20:13:53 | 10/08/2025 21:51:22 | 10/09/2025 02:13:53 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M7619-P1-HUB-CA-L900-L800-SBTS @ Generator_SG | 10/08/2025 20:08:34 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/08/2025 20:05:47 | P1 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7619 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/08/2025 20:13:53 | 10/08/2025 21:51:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008001707 | PCM-20251008-00002719 | TT-20250929-02324 | MW_HC | Region_4 | HAW0299 | HAW0299 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 20:15:08 | 10/09/2025 10:07:30 | 10/09/2025 08:15:08 | Nokia MW HC_P2 Observing Performance Issue at HAW0299_01-HAW0297-03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | VIP | 2G | taif | Sceco | TX NSA | HAW0299_01-HAW0297-03 | FLM_TE |  |  | PCM-20251008-00002690 | Currently is cleared & under observation | Currently is cleared & under observation |  |  |  | API | 10/08/2025 20:15:08 | 10/09/2025 10:07:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001708 | PCM-20251008-00002720 | TT-20251008-02405 | Telecom | Region_4 | USF0717 | USF0717 |  |  |  | Amr Abdulla Ali Othman | 10/08/2025 20:16:58 | 10/08/2025 20:16:58 | 10/09/2025 02:16:58 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at USF0717-P2-USF @ Generator_SG | 10/08/2025 17:48:31 | Major | 7607 | TRX OPERATION DEGRADED | 10/08/2025 17:48:29 | P2 | 2G | jeddah | Generator_SG | 2G_TRX NSA | USF0717 | FLM_TE |  |  | PCM-20251008-00002387 | FLM need to perform HC at site. | FLM need to perform HC at site. |  |  |  | API | 10/08/2025 20:16:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001713 | PCM-20251008-00002727 | TT-20251008-01933 | MW_HC | Region_4 | TFBH9443 | TFBH9443 |  |  |  | Ahmad Kamal Abdelmawla | 10/08/2025 20:20:36 | 10/09/2025 13:03:41 | 10/09/2025 08:20:36 | NEC MW HC_P0 Observing Performance Issue at MLJI9434(10.88.224.57)--TFBH9443(10.88.224.58) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | Repeater | taif | Generator_DG | TX NSA | MLJI9434(10.88.224.57)--TFBH9443(10.88.224.58) | FLM_TE |  |  | PCM-20251008-00002686 | The interference issue escalated to planning team for advice | The interference issue escalated to planning team for advice |  |  |  | API | 10/08/2025 20:20:36 | 10/09/2025 13:03:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001737 | PCM-20251008-00002772 | TT-20251008-02787 | Telecom | Region_4 | JED0109 | JED0109 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/08/2025 21:01:23 | 10/21/2025 17:12:31 | 10/09/2025 03:01:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/08/2025 21:00:44 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 21:00:36 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/08/2025 21:01:23 | 10/08/2025 22:50:36 | 10/09/2025 06:38:24 |  |  | 10/09/2025 06:38:37 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001747 | PCM-20251008-00002794 | TT-20251008-01429 | Telecom | Region_1 | DM1 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/08/2025 21:22:49 | 10/09/2025 04:51:21 | 10/09/2025 03:22:49 | Observing Links Down on DMM-SR-01/02 connected to 100GE2/0/6 && 100GE1/0/3 | 10/08/2025 13:23:27 | Major | 5000003 | Link Down | 10/08/2025 13:23:27 | P1 | BSC | dammam | Sceco_STB | TTImpacISPNSA | Observing Links Down on DMM-SR-01/02 connected to 100GE2/0/6 && 100GE1/0/3 | FLM_TE |  |  | PCM-20251008-00002593 | dear ,kindly escalate this To RO team as they who are owner for this action | dear ,kindly escalate this To RO team as they who are owner for this action |  |  |  | API | 10/08/2025 21:22:49 | 10/09/2025 04:51:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001767 | PCM-20251008-00002821 | TT-20251008-02825 | EM | Region_6 | QLW1M8370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/08/2025 21:43:45 | 10/21/2025 22:25:38 | 10/09/2025 09:43:45 | RECTIFIER MODULE FAILURE at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/08/2025 21:35:31 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/08/2025 21:35:22 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | Manual | 10/08/2025 21:43:45 | 10/21/2025 22:25:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251008001777 | PCM-20251008-00002833 | TT-20251008-02833 | Reference_telecom | Region_1 | DMJR0138 | DMJR0138 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/08/2025 21:50:28 | 10/08/2025 22:27:22 | 10/09/2025 09:50:28 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR0138-P1-DIA_SRAN @ Sceco_STB | 10/08/2025 18:50:20 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/08/2025 18:50:16 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | DMJR0138 | FLM_TE | [8 empty] | API | 10/08/2025 21:50:28 | 10/08/2025 22:27:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001803 | PCM-20251008-00002875 | TT-20251008-00594 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/08/2025 22:15:11 | 10/08/2025 22:15:11 | 10/09/2025 04:15:11 | Observing BGP Peer Connection at at 10.127.216.230 (BGP Peer 10.183.206.194) | 10/08/2025 00:52:28 | Major | 16144 | BGP Peer Status | 10/08/2025 00:52:28 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | Observing BGP Peer Connection at at 10.127.216.230 (BGP Peer 10.183.206.194) | FLM_TE |  |  | PCM-20251008-00000669 | dear , kindly escalate to IPRAN | dear , kindly escalate to IPRAN |  |  |  | API | 10/08/2025 22:15:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251008001829 | PCM-20251008-00002919 | TT-20251008-02763 | Reference_telecom | Region_4 | JED0028 | JED0028 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/08/2025 22:52:59 | 10/08/2025 22:52:59 | 10/09/2025 04:52:59 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0028-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/08/2025 18:34:57 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/08/2025 18:34:49 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0028 | FLM_TE |  | thanks to update case after reroute | PCM-20251008-00002779 | thanks to update case after reroute | thanks to update case after reroute |  |  |  | API | 10/08/2025 22:52:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251008001830 | PCM-20251008-00002920 | TT-20251008-02914 | Telecom | Region_4 | TAF1M7168 | TAF0168 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Ahmad Kamal Abdelmawla | 10/08/2025 22:53:26 | 10/14/2025 20:57:35 | 10/09/2025 04:53:26 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TAF1M7168-NCA-L800-SBTS @ Sceco | 10/08/2025 22:44:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 22:44:47 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7168 | FLM_TE |  |  | PCM-20251008-00002910 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/08/2025 22:53:26 | 10/09/2025 13:03:42 | 10/14/2025 20:57:26 |  |  | 10/14/2025 20:57:35 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001838 | PCM-20251008-00002930 | TT-20251008-02892 | Reference_telecom | Region_1 | DMHF2M7081 | DMHF0081 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/08/2025 23:01:57 | 10/09/2025 03:08:51 | 10/09/2025 11:01:57 | Cell RX Channel Interference Noise Power Unbalanced at DMHF2M7081-P1-HUB-L800-CA @ Generator_SG | 10/08/2025 19:26:11 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/08/2025 19:26:07 | P1 | 4G | hafouf | Generator_SG | 2G NSA | DMHF2M7081 | FLM_TE |  | Dears kindly check HW | PCM-20251008-00002892 | Dears kindly check HW | Dears kindly check HW |  |  |  | API | 10/08/2025 23:01:57 | 10/09/2025 03:08:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001864 | PCM-20251008-00002979 | TT-20251008-02954 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/08/2025 23:39:59 | 10/20/2025 12:32:45 | 10/09/2025 03:39:59 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/08/2025 19:28:18 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 19:28:09 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251008-00002958 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/08/2025 23:39:59 | 10/09/2025 09:49:49 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001878 | PCM-20251008-00002999 | TT-20251008-02982 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/08/2025 23:52:54 | 10/09/2025 10:07:30 | 10/09/2025 05:52:54 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/08/2025 23:46:05 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/08/2025 23:45:55 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251008-00002995 | FLM need to check RF Module and perform HC at site. | FLM need to check RF Module and perform HC at site. |  |  |  | API | 10/08/2025 23:52:54 | 10/09/2025 10:07:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000013 | PCM-20251009-00000017 | TT-20251008-02958 | Reference_telecom | Region_4 | JED0947 | JED0947 | Transsmission | MW_HW_fault | Replace IDU | Khaled Mohammad Abdallah | 10/09/2025 00:08:33 | 10/18/2025 23:04:01 | 10/09/2025 12:08:33 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0947-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/08/2025 21:33:19 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/08/2025 21:31:14 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0947 | FLM_TE |  |  | PCM-20251008-00002963 | TWAMP alarm is active. Please check from your end. | TWAMP alarm is active. Please check from your end. |  |  |  | API | 10/09/2025 00:08:33 |  | 10/17/2025 07:23:53 | 10/17/2025 07:23:56 | 10/17/2025 07:23:58 | 10/18/2025 23:04:01 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000044 | PCM-20251009-00000059 | TT-20251008-01939 | MW_HC | Region_6 | JEC0286 | JEC0286 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/09/2025 00:35:51 | 10/09/2025 00:56:00 | 10/09/2025 12:35:51 | NEC MW HC_P0 VIP Observing Modem Down at JEC0090(10.199.24.84)--JEC0286(10.199.24.85) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | baish | Generator_SG | TX NSA | JEC0090(10.199.24.84)--JEC0286(10.199.24.85) | FLM_TE |  | Thanks to share time for HC and share after complete 24 H | PCM-20251008-00002777 | Thanks to share time for HC and share after complete 24 H | Thanks to share time for HC and share after complete 24 H |  |  |  | API | 10/09/2025 00:35:51 | 10/09/2025 00:56:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251009000052 | PCM-20251009-00000073 | TT-20251009-00077 | MW_HC | Region_4 | SJED0337 | SJED0337 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/09/2025 00:44:31 | 10/09/2025 00:44:31 | 10/09/2025 12:44:31 | As per bo request Nokia MW HC for link SJED0337-JED2063 as link counting continuous PM errors at JED2063 and need to setup AMR for the link | 10/09/2025 00:44:25 | Minor | 113388 | LOF | 10/09/2025 00:44:23 | P3 | SRAN | jeddah | Sceco | TX NSA | SJED0337-JED2063 | FLM_TE | [5 empty] | As per bo request Nokia MW HC for link SJED0337-JED2063 as link counting continuous PM errors at JED2063 and need to setup AMR for the link |  |  | API | 10/09/2025 00:44:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000057 | PCM-20251009-00000086 | TT-20251009-00091 | Reference_telecom | Region_4 | MKYL0918 | MKYL0918 |  |  |  | Riasat Ali Allah Baksh | 10/09/2025 00:58:29 | 10/09/2025 15:07:43 | 10/09/2025 12:58:29 | DemFail observed in MKYL0918 towards 10.253.34.114 @ Generator_SG | 10/08/2025 12:58:22 | Minor |  | DemFail | 10/08/2025 12:58:07 | P2 | 2G | jeddah | Generator_SG | TX NSA | MKYL0918 | FLM_TE | [8 empty] | API | 10/09/2025 00:58:29 | 10/09/2025 15:07:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000067 | PCM-20251009-00000100 | TT-20251009-00079 | Reference_telecom | Region_6 | JDJZ1M3885 | JDJZ0885 | Equipment | BSS_HW_fault | Replace RRU | Muhammad Usman Muhammad Zia ul haq | 10/09/2025 01:13:58 | 10/10/2025 14:58:42 | 10/09/2025 05:13:58 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at JDJZ1M3885-P1-HUB @ Sceco_STB | 10/09/2025 00:16:21 | Critical | 7771 | WCDMA CELL OUT OF USE | 10/09/2025 00:14:09 | P1 | 3G | derb | Sceco_STB | 3G SA | JDJZ1M3885 | FLM_TE |  |  | PCM-20251009-00000074 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/09/2025 01:13:58 | 10/09/2025 02:58:05 | 10/09/2025 16:55:23 | 10/09/2025 16:55:27 | 10/09/2025 16:55:32 | 10/10/2025 14:58:42 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000070 | PCM-20251009-00000103 | TT-20251009-00098 | EM | Region_6 | QLW2370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/09/2025 01:14:03 | 10/21/2025 22:25:40 | 10/09/2025 07:14:03 | 1(2G/LTE) sites down under QLW2370-P3/QLW2370-P3 @ Generator_SG | 10/09/2025 01:05:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/09/2025 01:05:42 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | QLW2370-P3 | FLM_EM | QLW2370 | Results: DOWN SITE HUB QLW2370-P3 QLW2370 Summary: Hub: QLW2370, Down Count: 1, Down Sites: QLW2370-P3 Alarm Summary: QLW2370 No Active Alarm on HUB |  |  |  |  | sites down |  | Manual | 10/09/2025 01:14:03 | 10/21/2025 22:25:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000095 | PCM-20251009-00000145 | TT-20251008-01796 | MW_HC | Region_3 | AHT2061 | AHT2061 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Mohamed Naveed | 10/09/2025 01:43:32 | 10/12/2025 18:14:42 | 10/09/2025 13:43:32 | Huawei MW HC_P2 Observing Errors at AHT2061-AHT2165 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | hail | Generator_SG | TX NSA | AHT2061-AHT2165 | FLM_TE | AHT2061 | Dear Team , Link is flapping , kindly check this issue | PCM-20251009-00000138 | Dear Team , Link is flapping , kindly check this issue | Dear Team , Link is flapping , kindly check this issue |  |  |  | API | 10/09/2025 01:43:32 | 10/09/2025 08:49:29 | 10/12/2025 18:14:31 |  |  | 10/12/2025 18:14:42 |  | Mohamed Naveed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000096 | PCM-20251009-00000146 | TT-20251008-01797 | MW_HC | Region_3 | AHT0972 | AHT0972 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohamed Naveed | 10/09/2025 01:45:21 | 10/12/2025 18:14:26 | 10/09/2025 13:45:21 | Huawei MW HC_P2 Observing Errors at AHT0972-AHT2149 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | SRAN | hail | Sceco | TX NSA | AHT0972-AHT2149 | FLM_TE | AHT0972 | Dear Team , Link is flapping , kindly check locally | PCM-20251009-00000139 | Dear Team , Link is flapping , kindly check locally | Dear Team , Link is flapping , kindly check locally |  |  |  | API | 10/09/2025 01:45:21 | 10/09/2025 08:49:30 | 10/12/2025 18:14:14 | 10/12/2025 18:14:17 |  | 10/12/2025 18:14:26 |  | Mohamed Naveed |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251009000126 | PCM-20251009-00000208 | TT-20251009-00232 | EM | Region_1 | RSK2624 | RSK2624 |  |  |  | Dileesh Muringothil Devarajan | 10/09/2025 02:40:48 | 10/09/2025 13:11:14 | 10/09/2025 14:40:48 | Mains Failure at RSK2624-P3_SRAN-PC @ Sceco | 10/09/2025 02:38:45 | Minor | 65109 | Mains Failure | 10/08/2025 23:36:19 | P3 | SRAN | jubail | Sceco | 2G NSA | RSK2624 | FLM_EM | [8 empty] | API | 10/09/2025 02:40:48 | 10/09/2025 07:27:30 | 10/09/2025 13:11:05 | 10/09/2025 13:11:07 | 10/09/2025 13:11:14 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000167 | PCM-20251009-00000283 | TT-20251009-00336 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/09/2025 03:59:50 | 10/20/2025 12:32:45 | 10/09/2025 15:59:50 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/09/2025 03:51:45 | Minor | 7115 | BASE STATION INFORMATION | 10/09/2025 03:51:37 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/09/2025 03:59:50 | 10/09/2025 09:49:50 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000175 | PCM-20251009-00000299 | TT-20251009-00358 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/09/2025 04:23:36 | 10/09/2025 10:16:42 | 10/09/2025 08:23:36 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/09/2025 04:23:01 | Critical | 65334 | Door open Alarm Equipment room | 10/09/2025 04:22:58 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/09/2025 04:23:36 | 10/09/2025 10:16:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000211 | PCM-20251009-00000350 | TT-20251009-00424 | Reference_telecom | Region_6 | BHAB0827 | BHAB0827 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/09/2025 05:46:47 | 10/09/2025 12:37:31 | 10/09/2025 17:46:47 | DemFail observed in BHAB0827_01 towards 10.221.243.194 @ Sceco_STB | 10/08/2025 17:46:31 | Minor |  | DemFail | 10/08/2025 17:46:26 | P1 | 2G | makhwa | Sceco_STB | TX NSA | BHAB0827 | FLM_TE | [8 empty] | API | 10/09/2025 05:46:47 | 10/09/2025 12:37:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000261 | PCM-20251009-00000431 | TT-20251009-00506 | Reference_telecom | Region_4 | MUMA0772 | MUMA0772 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/09/2025 07:00:40 | 10/09/2025 10:16:14 | 10/09/2025 19:00:40 | ReplaceableUnitProblem observed in MUMA0772_01 towards 10.221.243.242 @ Sceco | 10/08/2025 19:02:21 | Minor |  | ReplaceableUnitProblem | 10/08/2025 19:00:26 | P3 | 2G | qunfuddah | Sceco | TX NSA | MUMA0772 | FLM_TE | [8 empty] | API | 10/09/2025 07:00:40 | 10/09/2025 10:16:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251009000270 | PCM-20251009-00000442 | TT-20251009-00518 | Telecom | Region_4 | JED1MN2352 | JED2352 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/09/2025 07:17:13 | 10/09/2025 07:17:13 | 10/09/2025 13:17:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2352-NR2.6-P2 @ Sceco | 10/09/2025 07:16:09 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 07:16:02 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2352 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 07:17:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000275 | PCM-20251009-00000450 | TT-20251009-00522 | MW_HC | Region_4 | TFBH9401 | TFBH9401 |  |  |  | Ahmad Kamal Abdelmawla | 10/09/2025 07:19:57 | 10/09/2025 13:03:43 | 10/09/2025 19:19:57 | As per bo request Nokia MW HC need to restore visibility for TFBH9401 10.88.224.13 -UKZ9444 10.88.224.2 | 10/09/2025 07:19:51 | Minor | 113388 | LOF | 10/09/2025 07:19:49 | P1 | Repeater | taif | Generator_DG | TX NSA | FBH9401 10.88.224.13 -UKZ9444 10.88.224.2 | FLM_TE | [5 empty] | As per bo request Nokia MW HC need to restore visibility for TFBH9401 10.88.224.13 -UKZ9444 10.88.224.2 |  |  | API | 10/09/2025 07:19:57 | 10/09/2025 13:03:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000310 | PCM-20251009-00000511 | TT-20251009-00624 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/09/2025 08:10:25 | 10/10/2025 12:16:08 | 10/09/2025 20:10:25 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/09/2025 08:04:16 | Minor | 1589 | AC Overfrequency | 10/09/2025 08:04:16 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/09/2025 08:10:25 | 10/09/2025 09:59:06 | 10/10/2025 12:15:59 |  |  | 10/10/2025 12:16:08 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000319 | PCM-20251009-00000526 | TT-20251009-00634 | Reference_telecom | Region_1 | HFS2M4025 | HFS2025 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/09/2025 08:19:12 | 10/09/2025 19:51:07 | 10/09/2025 20:19:12 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M4025-P3 @ Generator_SG | 10/09/2025 05:19:09 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/09/2025 05:19:07 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M4025 | FLM_TE | [8 empty] | API | 10/09/2025 08:19:12 | 10/09/2025 19:51:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000375 | PCM-20251009-00000604 | TT-20251009-00147 | Telecom | Region_4 | JED1M7901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/09/2025 08:40:26 | 10/20/2025 12:32:46 | 10/09/2025 14:40:26 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1M7901-CA-L800-P1-VIP-SBTS @ Sceco | 10/09/2025 01:45:32 | Major | 7114 | CELL SERVICE PROBLEM | 10/09/2025 01:45:22 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7901 | FLM_TE |  |  | PCM-20251009-00000149 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/09/2025 08:40:26 | 10/09/2025 09:49:52 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000393 | PCM-20251009-00000631 | TT-20251009-00429 | Reference_telecom | Region_2 | RIY2970 | RIY2970 |  |  |  | Asad Ali Nadiq Khan | 10/09/2025 08:49:58 | 10/09/2025 09:32:09 | 10/09/2025 12:49:58 | Outage-20251008-0104 : 1(LTE) sites down under RIY2970-FWA-P1-VIP_SRAN @ Generator_SG | 10/09/2025 05:49:30 | Critical | 301 | NE Is Disconnected | 10/09/2025 02:25:44 | P3 | SRAN | riyadh | Generator_SG | LTE SA | RIY2970-FWA-P1-VIP_SRAN | FLM_TE | RIY2970 | Results: DOWN SITE HUB RIY2970-FWA-P1-VIP_SRAN RIY2970 Summary: Hub: RIY2970, Down Count: 1, Down Sites: RIY2970-FWA-P1-VIP_SRAN Alarm Summary: RIY2970 No Active Alarm on HUB | PCM-20251009-00000608 | observing RO operation at site | observing RO operation at site |  | sites down |  | API | 10/09/2025 08:49:58 | 10/09/2025 09:32:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000433 | PCM-20251009-00000691 | TT-20251009-00752 | EM | Region_6 | SRA2355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/09/2025 09:25:04 | 10/21/2025 22:25:41 | 10/09/2025 15:25:04 | 1(2G/LTE) sites down under SRA2355-P3/SRA2355-P3 @ Generator_SG | 10/09/2025 09:16:54 | Major | 7706 | BTS O&M LINK FAILURE | 10/09/2025 09:16:49 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2355-P3 | FLM_EM | SRA2355 | Results: DOWN SITE HUB SRA2355-P3 SRA2355 Summary: Hub: SRA2355, Down Count: 1, Down Sites: SRA2355-P3 Alarm Summary: SRA2355 Alarm Active on HUB |  |  |  |  | sites down |  | Manual | 10/09/2025 09:25:04 | 10/21/2025 22:25:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000444 | PCM-20251009-00000704 | TT-20251009-00770 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/09/2025 09:31:31 | 10/09/2025 12:09:54 | 10/09/2025 21:31:31 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/09/2025 09:23:03 | Minor | 7103 | HIGH TEMP | 10/09/2025 09:22:58 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/09/2025 09:31:31 | 10/09/2025 12:09:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000445 | PCM-20251009-00000705 | TT-20251009-00771 | Telecom | Region_4 | TAF0170 | TAF0170 |  |  |  | Ahmad Kamal Abdelmawla | 10/09/2025 09:31:46 | 10/09/2025 13:03:43 | 10/09/2025 21:31:46 | PT:: as per BO BSS FLM need to perform HC at TAF0170 | 10/09/2025 09:31:00 | Minor | 676767671 | Health Check-WO to TE FME | 10/09/2025 09:31:00 | P1 | 2G | taif | Sceco_STB | 2G_3G_LTE_5G NSA | TAF0170 | FLM_TE | [8 empty] | API | 10/09/2025 09:31:46 | 10/09/2025 13:03:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000453 | PCM-20251009-00000719 | TT-20251009-00785 | EM | Region_4 | THO0371 | THO0371 |  |  |  | Hamza Ahmed Aly Sawy | 10/09/2025 09:42:22 | 10/09/2025 11:27:48 | 10/09/2025 21:42:22 | AIRCON1 at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/09/2025 09:33:57 | Minor | 7103 | AIRCON1 | 10/09/2025 09:33:48 | P2 | 2G | jeddah | Sceco | 2G NSA | THO0371 | FLM_EM | [5 empty] | AIRCON1 |  |  | API | 10/09/2025 09:42:22 | 10/09/2025 11:27:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251009000479 | PCM-20251009-00000758 | TT-20251009-00829 | Telecom | Region_4 | JED0253 | JED0253 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/09/2025 10:01:28 | 10/19/2025 17:44:07 | 10/09/2025 16:01:28 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connector) at JED0253-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/09/2025 09:56:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 09:56:29 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0253 | FLM_TE | [5 empty] | Increased BER detected on the optical connector |  |  | API | 10/09/2025 10:01:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000523 | PCM-20251009-00000822 | TT-20251009-00891 | Telecom | Region_6 | ABBS0165 | ABBS0165 | Equipment | BTS_Cable | Replace CPRI Cable | Fawad Khan | 10/09/2025 10:34:02 | 10/20/2025 00:50:58 | 10/09/2025 16:34:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABBS0165-G9-L8-NL18-NL21-NNR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/09/2025 10:32:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 10:32:54 | P3 | 2G | namas | Sceco | 5G_Cell SA | ABBS0165 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 10:34:02 | 10/09/2025 14:32:41 | 10/20/2025 00:50:23 |  |  | 10/20/2025 00:50:58 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000541 | PCM-20251009-00000848 | TT-20251009-00918 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/09/2025 10:49:31 | 10/09/2025 19:51:09 | 10/09/2025 22:49:31 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/09/2025 07:49:12 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/09/2025 07:49:09 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/09/2025 10:49:31 | 10/09/2025 19:51:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000558 | PCM-20251009-00000868 | TT-20251009-00161 | Reference_telecom | Region_4 | JED0005 | JED0005 |  |  |  | MALIK ATIF ZAMAN | 10/09/2025 11:02:51 | 10/09/2025 14:47:34 | 10/09/2025 23:02:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0005-G9-L8-L18-L21-NR2.6--SBTS-P3 @ Sceco | 10/09/2025 00:13:11 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/08/2025 23:58:54 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0005 | FLM_TE |  |  | PCM-20251009-00000813 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/09/2025 11:02:51 | 10/09/2025 14:47:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000561 | PCM-20251009-00000871 | TT-20251009-00029 | Telecom | Region_4 | JED1M7299 | JED0299 | Equipment | BSS_HW_fault | Replace System Module | Ahmad Mostafa Hamouda Ibrahem | 10/09/2025 11:03:20 | 10/12/2025 11:44:58 | 10/09/2025 23:03:20 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at JED1M7299-P3-CA-L900-L800-SBTS @ Sceco | 10/09/2025 00:13:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/08/2025 03:02:08 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7299 | FLM_TE |  |  | PCM-20251009-00000812 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/09/2025 11:03:20 | 10/12/2025 10:01:32 | 10/12/2025 10:31:21 | 10/12/2025 10:31:30 | 10/12/2025 10:31:33 | 10/12/2025 11:44:58 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000564 | PCM-20251009-00000874 | TT-20251009-00850 | Telecom | Region_6 | SDA0507 | SDA0507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/09/2025 11:04:12 | 10/19/2025 17:44:07 | 10/09/2025 17:04:12 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at SDA0507-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Generator_SG | 10/09/2025 10:10:03 | Major | 7114 | CELL SERVICE PROBLEM | 10/09/2025 10:09:52 | P3 | 2G | abha | Generator_SG | 5G_Cell SA | SDA0507 | FLM_TE |  |  | PCM-20251009-00000783 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/09/2025 11:04:12 | 10/09/2025 12:16:19 | 10/09/2025 14:37:40 |  |  | 10/09/2025 14:37:54 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000566 | PCM-20251009-00000876 | TT-20251009-00940 | EM | Region_6 | NMR1M8401 | NMR2401 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/09/2025 11:04:29 | 10/11/2025 08:24:28 | 10/09/2025 23:04:29 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at NMR1M8401-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/09/2025 10:56:23 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/09/2025 10:56:05 | P3 | 4G | Baha | Generator_SG | LTE NSA | NMR1M8401 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/09/2025 11:04:29 | 10/11/2025 08:24:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000572 | PCM-20251009-00000883 | TT-20251009-00943 | EM | Region_6 | QLW1M8370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/09/2025 11:06:03 | 10/21/2025 22:25:46 | 10/09/2025 23:06:03 | SHELTER DOOR OPEN at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/09/2025 11:05:44 | Minor | 7103 | SHELTER DOOR OPEN | 10/09/2025 11:04:17 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | Manual | 10/09/2025 11:06:03 | 10/21/2025 22:25:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000587 | PCM-20251009-00000904 | TT-20251009-00960 | EM | Region_6 | QLW1M8370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/09/2025 11:12:45 | 10/21/2025 22:25:47 | 10/09/2025 23:12:45 | RECTIFIER MODULE FAILURE at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/09/2025 11:05:44 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/09/2025 11:04:17 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | Manual | 10/09/2025 11:12:45 | 10/21/2025 22:25:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000600 | PCM-20251009-00000921 | TT-20251009-00935 | Telecom | Region_4 | JED0850 | JED0850 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/09/2025 11:19:16 | 10/10/2025 12:42:27 | 10/09/2025 15:19:16 | 3(2G) 3(5G) sites down under JED0850-P2,JED2125-P3,JED0028-P1-DIA/JED0028-P1-DIA @ Sceco | 10/09/2025 10:59:57 | Critical | 7706 | BTS O&M LINK FAILURE | 10/09/2025 10:59:51 | P2 | 2G | jeddah | Sceco | 2G SA | JED0028-P1-DIA 2G,JED2125-P3 2G,JED0850-P2 2G | FLM_TE | JED0850 | Hub: JED0850 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251009-00000901 | no power issue TE team checking | no power issue TE team checking |  | sites down |  | API | 10/09/2025 11:19:16 | 10/10/2025 12:42:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000605 | PCM-20251009-00000927 | TT-20251009-00988 | Telecom | Region_4 | JED1M7029 | JED0029 | Equipment | CB_BTS | Switch on CB on Rectifier | Khaled Mohammad Abdallah | 10/09/2025 11:23:05 | 10/12/2025 05:34:14 | 10/09/2025 17:23:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7029-CA-L900-L800-SBTS @ Sceco | 10/09/2025 11:22:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 11:22:24 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7029 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 11:23:05 | 10/10/2025 01:48:06 | 10/10/2025 02:29:57 | 10/10/2025 02:29:59 | 10/10/2025 02:30:02 | 10/12/2025 05:34:14 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000636 | PCM-20251009-00000974 | TT-20250929-02231 | MW_HC | Region_4 | JED0056 | JED0056 |  |  |  | BARKAT ALI MAIN HILAL | 10/09/2025 11:45:07 | 10/09/2025 13:23:21 | 10/09/2025 23:45:07 | Nokia MW HC_P0 Observing Performance Issue at JED0056-JED0899_SH04 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED0056-JED0899_SH04 | FLM_TE |  |  | PCM-20251009-00000381 | where data | where data |  |  |  | API | 10/09/2025 11:45:07 | 10/09/2025 13:23:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000673 | PCM-20251009-00001029 | TT-20251009-01071 | Reference_telecom | Region_4 | SJED0664 | SJED0664 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Ahmad Mostafa Hamouda Ibrahem | 10/09/2025 12:12:47 | 10/23/2025 11:12:17 | 10/10/2025 00:12:47 | SJED1W0664 complete down | 10/09/2025 11:42:37 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/09/2025 11:42:37 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0664 | FLM_EM | SJED0664 | Hub: SJED0664 We are observing PM error at far end, kindly visit the site and check the issue at site. Kindly update TT under EM, FLM | PCM-20251009-00000999 | Hub: SJED0664 We are observing PM error at far end, kindly visit the site and check the issue at site. Kindly update TT under EM, FLM | Hub: SJED0664 We are observing PM error at far end, kindly visit the site and check the issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/09/2025 12:12:47 | 10/12/2025 11:49:30 | 10/15/2025 23:47:32 | 10/17/2025 14:01:57 | 10/19/2025 17:07:16 | 10/23/2025 11:12:17 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000694 | PCM-20251009-00001066 | TT-20251009-01111 | Telecom | Region_1 | TRT2M7233 | TRT0233 |  |  |  | Meraj Husain Idd Baksh | 10/09/2025 12:28:27 | 10/09/2025 17:37:22 | 10/10/2025 00:28:27 | Cell Capability Degraded at TRT2M7233-P3-L800 @ Sceco | 10/09/2025 12:11:44 | Minor | 29243 | Cell Capability Degraded | 10/09/2025 12:10:12 | P3 | 4G | dammam | Sceco | 2G NSA | TRT2M7233 | FLM_TE |  |  | PCM-20251009-00001040 | Need FLM to check or swap RRU of SEC 4 L1800 , RRU 2102310SSQ4MEC002092 | Need FLM to check or swap RRU of SEC 4 L1800 , RRU 2102310SSQ4MEC002092 |  |  |  | API | 10/09/2025 12:28:27 | 10/09/2025 17:37:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251009000718 | PCM-20251009-00001109 | TT-20251009-01176 | Telecom | Region_4 | TAF0287 | TAF0287 |  |  |  | Asad Ullah Rahim Said | 10/09/2025 12:44:10 | 10/10/2025 13:40:45 | 10/10/2025 00:44:10 | ODU CPU / Cable Open at TAF0287-3 on 10.1.166.25 @ Sceco | 10/09/2025 12:43:34 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/09/2025 12:34:34 | P3 | 2G | taif | Sceco | TX NSA | TAF0287 | FLM_TE | [8 empty] | API | 10/09/2025 12:44:10 | 10/10/2025 12:51:35 | 10/10/2025 13:40:26 | 10/10/2025 13:40:42 | 10/10/2025 13:40:45 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000732 | PCM-20251009-00001128 | TT-20251009-01128 | Telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/09/2025 12:51:20 | 10/09/2025 13:44:06 | 10/10/2025 00:51:20 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/09/2025 12:18:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 12:18:44 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251009-00001055 | RSSI alarm active at site, kindly check | RSSI alarm active at site, kindly check |  |  |  | API | 10/09/2025 12:51:20 | 10/09/2025 13:44:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000735 | PCM-20251009-00001132 | TT-20251009-00572 | Reference_telecom | Region_4 | JZMA1M7822 | JZMA0822 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/09/2025 12:52:10 | 10/16/2025 11:23:40 | 10/10/2025 00:52:10 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JZMA1M7822-G9-L8-NL18-SBTS-P2-WBB-G3 @ Generator_SG | 10/09/2025 05:45:03 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/09/2025 05:44:00 | P2 | 4G | qunfuddah | Generator_SG | LTE NSA | JZMA1M7822 | FLM_TE |  |  | PCM-20251009-00001065 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/09/2025 12:52:10 | 10/10/2025 13:43:02 | 10/16/2025 11:23:32 |  |  | 10/16/2025 11:23:40 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000765 | PCM-20251009-00001176 | TT-20251009-01232 | Reference_telecom | Region_2 | RIYD1W6008 | RIYD1W6008 |  |  |  | Abdelrahim Abdalla Abdelrahim Khairy | 10/09/2025 13:14:49 | 10/20/2025 09:54:13 | 10/10/2025 01:14:49 | RIYD1W6008 Partial down | 10/09/2025 12:56:42 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/09/2025 12:56:42 | P1 | WIFI | riyadh | Sceco | Wifi SA | RIYD1W6008_4-GF-AP01 RIYD1W6008_4-GF-AP03 RIYD1W6008_4-GF-AP06 RIYD1W6008_4-GF-AP08 | FLM_TE | [8 empty] | API | 10/09/2025 13:14:49 | 10/11/2025 12:36:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000806 | PCM-20251009-00001237 | TT-20251005-02553 | MW_HC | Region_5 | BIK0153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/09/2025 13:50:22 | 10/18/2025 03:16:08 | 10/10/2025 01:50:22 | As BO Requested MW Nokia Observing Performance issue at HUB Site BIK0153 | 10/05/2025 18:23:19 | Minor | 113388 | LOF | 10/05/2025 18:23:23 | P3 | 2G | makkah | Generator_SG | TX NSA | BIK0153 | FLM_TE |  |  | PCM-20251009-00001220 | For HW approval kindly share over mail | For HW approval kindly share over mail |  |  |  | API | 10/09/2025 13:50:22 | 10/18/2025 03:16:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000809 | PCM-20251009-00001244 | TT-20251009-01313 | Telecom | Region_4 | MLJI0187 | MLJI0187 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/09/2025 13:52:27 | 10/10/2025 11:32:25 | 10/09/2025 19:52:27 | PT::FLM need to check Sync issue at MLJI0187 (Bo request) | 10/09/2025 13:52:01 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/09/2025 13:52:01 | P2 | 2G | alaith | Sceco | 2G_3G_LTE_5G NSA | MLJI0187 | FLM_TE | [8 empty] | API | 10/09/2025 13:52:27 | 10/10/2025 11:32:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000823 | PCM-20251009-00001265 | TT-20251009-01219 | Telecom | Region_4 | JED3W6071 | JED3W6071 |  |  |  | Mohamed Farag Abdelbary | 10/09/2025 14:03:45 | 10/09/2025 14:52:50 | 10/10/2025 02:03:45 | JED3W6071 partial down | 10/09/2025 13:04:51 | Minor | 676767675 | Health Check-WO to TE FME | 10/09/2025 13:04:51 | P3 | WIFI | jeddah | Sceco | Wifi SA | JED3W6071 | FLM_TE |  |  | PCM-20251009-00001160 | Please check the APs locally JED3W6071_1-1F-AP-15 JED3W6071_1-1F-AP-14 | Please check the APs locally JED3W6071_1-1F-AP-15 JED3W6071_1-1F-AP-14 |  |  |  | API | 10/09/2025 14:03:45 | 10/09/2025 14:52:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000865 | PCM-20251009-00001324 | TT-20251009-01400 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/09/2025 14:24:57 | 10/09/2025 18:05:45 | 10/10/2025 02:24:57 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/09/2025 14:16:31 | Minor | 7103 | AIRCON 1 FAILURE | 10/09/2025 14:16:22 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/09/2025 14:24:57 | 10/09/2025 18:05:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000880 | PCM-20251009-00001348 | TT-20251009-01424 | Reference_telecom | Region_2 | RIYB6038 | RIYB6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/09/2025 14:37:51 | 10/10/2025 12:56:45 | 10/09/2025 20:37:51 | RF Unit VSWR Threshold Crossed at RIYB6038-P3_SRAN @ Sceco | 10/09/2025 11:37:30 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/09/2025 11:37:20 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6038 | FLM_TE | [8 empty] | API | 10/09/2025 14:37:51 | 10/10/2025 12:56:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000890 | PCM-20251009-00001360 | TT-20251009-01438 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/09/2025 14:46:07 | 10/21/2025 22:25:49 | 10/10/2025 02:46:07 | SHELTER DOOR OPEN at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/09/2025 14:45:56 | Minor | 7103 | SHELTER DOOR OPEN | 10/09/2025 14:44:32 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | Manual | 10/09/2025 14:46:07 | 10/21/2025 22:25:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251009000897 | PCM-20251009-00001367 | TT-20251009-01446 | Telecom | Region_4 | JED0198-ZJe08-CSG-04 | JED0198 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/09/2025 14:48:41 | 10/09/2025 14:48:41 | 10/09/2025 20:48:41 | Physical Port Down at JED0198-ZJe08-CSG-04 @ Sceco | 10/09/2025 14:45:47 | Major | 101-2505274 | Physical Port Down | 10/09/2025 14:45:39 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0198-ZJe08-CSG-04 | FLM_TE | [8 empty] | API | 10/09/2025 14:48:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000904 | PCM-20251009-00001377 | TT-20251009-01456 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/09/2025 14:52:50 | 10/21/2025 22:25:52 | 10/10/2025 02:52:50 | RECTIFIRE MAIN FAIL at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/09/2025 14:45:57 | Minor | 7103 | RECTIFIRE MAIN FAIL | 10/09/2025 14:44:32 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | RECTIFIRE MAIN FAIL |  |  | Manual | 10/09/2025 14:52:50 | 10/21/2025 22:25:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000907 | PCM-20251009-00001381 | TT-20251009-01462 | Telecom | Region_1 | DAM2995 | DAM2995 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/09/2025 14:54:23 | 10/09/2025 16:32:15 | 10/10/2025 02:54:23 | RF Unit Temperature Unacceptable at DAM2995-P2_SRAN @ Sceco | 10/09/2025 14:47:23 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/09/2025 14:47:19 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2995 | FLM_TE | [8 empty] | API | 10/09/2025 14:54:23 | 10/09/2025 16:32:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000911 | PCM-20251009-00001389 | TT-20251009-01171 | Telecom | Region_4 | RNRY0667 | RNRY0667 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Ahmad Kamal Abdelmawla | 10/09/2025 14:59:02 | 10/14/2025 20:54:39 | 10/09/2025 20:59:02 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at RNRY0667-P3 @ Sceco | 10/09/2025 12:38:16 | Major | 7607 | TRX OPERATION DEGRADED | 10/09/2025 12:38:14 | P3 | 2G | taif | Sceco | 2G_TRX NSA | RNRY0667 | FLM_TE |  |  | PCM-20251009-00001105 | VSWR alarm active at site, kindly check | VSWR alarm active at site, kindly check |  |  |  | API | 10/09/2025 14:59:02 | 10/09/2025 15:47:57 | 10/14/2025 20:54:29 |  |  | 10/14/2025 20:54:39 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000930 | PCM-20251009-00001422 | TT-20251009-01495 | Telecom | Region_1 | UQSW2M8730 | UQSW2730 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Imran Ali Yousaf | 10/09/2025 15:16:32 | 10/09/2025 15:53:15 | 10/09/2025 21:16:32 | 1(LTE) sites down under UQSW2730-L800-P3 @ Generator_SG | 10/09/2025 15:09:16 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/09/2025 15:07:57 | P3 | 4G | dammam | Generator_SG | LTE SA | UQSW2730-L800-P3 | FLM_TE | UQSW2730 | Results: DOWN SITE HUB UQSW2730-L800-P3 UQSW2730 Summary: Hub: UQSW2730, Down Count: 1, Down Sites: UQSW2730-L800-P3 Alarm Summary: UQSW2730 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/09/2025 15:16:32 | 10/09/2025 15:31:43 | 10/09/2025 15:52:54 |  |  | 10/09/2025 15:53:15 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000935 | PCM-20251009-00001427 | TT-20251009-01481 | Telecom | Region_1 | HMBY2428 | HMBY2428 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Imran Ali Yousaf | 10/09/2025 15:18:25 | 10/23/2025 17:12:18 | 10/09/2025 19:18:25 | 4(3G) 5(LTE) sites down under QRH2431-P1-VIP,QRH2432-P1-VIP @ Generator_SG | 10/09/2025 15:02:45 | Critical | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/09/2025 15:01:06 | P3 | SRAN | dammam | Sceco | LTE SA | QRH2432-P1-VIP LTE,QRH2431-P1-VIP LTE | FLM_TE | HMBY2428 | Dear Team, We are observing MW_BER_SD & MW_LOF alarms and HU issue at MW LINK HMBY2428 DIR HMBY0422 | PCM-20251009-00001407 | Dear Team, We are observing MW_BER_SD & MW_LOF alarms and HU issue at MW LINK HMBY2428 DIR HMBY0422 | Dear Team, We are observing MW_BER_SD & MW_LOF alarms and HU issue at MW LINK HMBY2428 DIR HMBY0422 |  | sites down |  | API | 10/09/2025 15:18:25 | 10/09/2025 15:31:44 | 10/09/2025 15:43:07 |  |  | 10/09/2025 15:43:25 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009000937 | PCM-20251009-00001430 | TT-20251009-01516 | EM | Region_6 | JDJZ1M7787 | JDJZ0787 |  |  |  | Aziz Ul Haq Umar Gul | 10/09/2025 15:18:39 | 10/09/2025 16:53:54 | 10/10/2025 03:18:39 | SHELTER DOOR OPEN at JDJZ1M7787-L800-P3-SBTS @ Sceco | 10/09/2025 15:18:26 | Minor | 7103 | SHELTER DOOR OPEN | 10/09/2025 15:16:29 | P3 | 4G | derb | Sceco | LTE NSA | JDJZ1M7787 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/09/2025 15:18:39 | 10/09/2025 16:53:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009000949 | PCM-20251009-00001448 | TT-20251009-01534 | EM | Region_6 | JDJZ1M7787 | JDJZ0787 |  |  |  | Aziz Ul Haq Umar Gul | 10/09/2025 15:24:51 | 10/09/2025 16:53:54 | 10/10/2025 03:24:51 | AIRCON 1 FAILURE at JDJZ1M7787-L800-P3-SBTS @ Sceco | 10/09/2025 15:18:26 | Minor | 7103 | AIRCON 1 FAILURE | 10/09/2025 15:16:29 | P3 | 4G | derb | Sceco | LTE NSA | JDJZ1M7787 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/09/2025 15:24:51 | 10/09/2025 16:53:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000971 | PCM-20251009-00001476 | TT-20251009-01560 | Telecom | Region_4 | JED0339 | JED0339 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/09/2025 15:37:16 | 10/11/2025 10:48:41 | 10/10/2025 03:37:16 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0339-G9-L18-L21-NR2.6-SBTS-P2-USF @ Generator_SG | 10/09/2025 15:36:22 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 15:36:17 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0339 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 15:37:16 | 10/09/2025 15:39:27 | 10/09/2025 17:24:33 | 10/09/2025 17:24:39 | 10/09/2025 17:24:44 | 10/11/2025 10:48:41 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251009000974 | PCM-20251009-00001480 | TT-20251009-01563 | Reference_EM | [7 empty] | 10/09/2025 15:37:47 | 10/09/2025 15:37:47 | 10/10/2025 03:37:47 | Minor Rec alarm at RIYB6076-P3_SRAN @ Sceco | 10/09/2025 15:27:30 | Minor | 65108 | Minor Rec alarm | 10/09/2025 15:27:26 | P3 | SRAN |  | Sceco | 2G NSA | RIYB6076 | FLM_EM | [8 empty] | API | 10/09/2025 15:37:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251009000995 | PCM-20251009-00001521 | TT-20251009-01599 | Telecom | Region_4 | JED2350 | JED2350 | Equipment | BSS_HW_Stuck | Reset Interface Card | Abdullah Ahmad Mohammad Abdelsheekh | 10/09/2025 15:53:49 | 10/19/2025 17:44:08 | 10/09/2025 21:53:49 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2350-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-FON @ Sceco | 10/09/2025 15:52:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 15:52:53 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED2350 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 15:53:49 | 10/09/2025 16:01:08 | 10/09/2025 16:33:30 | 10/09/2025 16:33:47 | 10/09/2025 16:33:49 | 10/09/2025 16:42:33 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001037 | PCM-20251009-00001597 | TT-20251009-01677 | Telecom | Region_4 | TAF2405 | TAF2405 | Equipment | BSS_HW_fault | Replace Antenna | Ahmad Kamal Abdelmawla | 10/09/2025 16:28:25 | 10/22/2025 17:38:44 | 10/10/2025 04:28:25 | BASE STATION INFORMATION (No module fan detected) at TAF2405-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/09/2025 16:20:26 | Minor | 7115 | BASE STATION INFORMATION | 10/09/2025 16:20:16 | P2 | 2G | taif | Sceco | 2G NSA | TAF2405 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/09/2025 16:28:25 | 10/09/2025 16:30:01 | 10/22/2025 17:38:31 |  |  | 10/22/2025 17:38:44 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001088 | PCM-20251009-00001672 | TT-20251009-01746 | EM | Region_4 | HHR0507 | HHR0507 |  |  |  | Aly Ahmed Aly Sawy | 10/09/2025 16:54:46 | 10/09/2025 17:54:40 | 10/09/2025 22:54:46 | Generator Low Fuel at HHR0507-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/09/2025 16:46:51 | Major | 7103 | Generator Low Fuel | 10/09/2025 16:46:41 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0507 | FLM_EM | [5 empty] | Generator Low Fuel |  |  | API | 10/09/2025 16:54:46 | 10/09/2025 17:54:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251009001091 | PCM-20251009-00001676 | TT-20251008-02068 | MW_HC | Region_6 | WDS0500 | WDS0500 |  |  |  | Ahmed Mamdouh Helal Helal | 10/09/2025 16:56:44 | 10/11/2025 12:46:37 | 10/10/2025 04:56:44 | Nokia MW HC_P0 Observing Performance Issue at WDS0500 _01-WDS0501-2 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | wadi dawasar | Sceco | TX NSA | WDS0500 _01-WDS0501-2 | FLM_TE |  |  | PCM-20251009-00001590 | Link currently clear | Link currently clear |  |  |  | API | 10/09/2025 16:56:44 | 10/11/2025 12:46:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001123 | PCM-20251009-00001756 | TT-20251009-01803 | MW_HC | Region_3 | MDTB0348 | MDTB0348 |  |  |  | Tahir Abbas Fateh Khan | 10/09/2025 17:22:09 | 10/09/2025 17:54:54 | 10/10/2025 05:22:09 | (As per BO request) NEC HC for performance issue at link MDTB0348-MDTB0343(10.154.66.107) | 10/09/2025 17:21:33 | Minor | 1-631 | MW_LOF | 10/09/2025 17:21:33 | P1 | SRAN | tabouk | Sceco_STB | TX NSA | MDTB0348-MDTB0343(10.154.66.107) | FLM_TE | [5 empty] | (As per BO request) NEC HC for performance issue at link MDTB0348-MDTB0343(10.154.66.107) |  |  | API | 10/09/2025 17:22:09 | 10/09/2025 17:54:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001167 | PCM-20251009-00001835 | TT-20251009-01859 | EM | Region_4 | BHMF2137 | BHMF2137 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/09/2025 18:05:43 | 10/14/2025 14:25:58 | 10/10/2025 00:05:43 | 1(2G/LTE) sites down under BHMF2137-P3/BHMF2137-P3 @ Generator_SG | 10/09/2025 17:57:19 | Major | 7706 | BTS O&M LINK FAILURE | 10/09/2025 17:57:16 | P3 | 2G | jeddah | Generator_SG | 2G SA | BHMF2137-P3 | FLM_TE | BHMF2137 | Results: DOWN SITE HUB BHMF2137-P3 BHMF2137 Summary: Hub: BHMF2137, Down Count: 1, Down Sites: BHMF2137-P3 Alarm Summary: BHMF2137 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/09/2025 18:05:43 | 10/10/2025 14:19:19 | 10/10/2025 15:05:43 | 10/10/2025 15:05:47 |  | 10/14/2025 14:25:58 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001200 | PCM-20251009-00001885 | TT-20251009-01915 | Telecom | Region_1 | HMBY2429 | HMBY2429 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Imran Ali Yousaf | 10/09/2025 18:43:06 | 10/11/2025 21:36:05 | 10/10/2025 06:43:06 | NEC MW Observing Visibility Issue on 1 NE under HMBY2429 10.74.84.137 Cluster QRH2433 | 10/09/2025 18:42:26 | Minor | 2 | NE_NOT_LOGIN | 10/09/2025 18:42:26 | VIP | SRAN | dammam | Generator_SG | TX NSA | HMBY2429 10.74.84.137 | FLM_TE | [5 empty] | NEC MW Observing Visibility Issue on 1 NE under HMBY2429 10.74.84.137 Cluster QRH2433 |  |  | API | 10/09/2025 18:43:06 | 10/09/2025 20:07:11 | 10/11/2025 16:58:26 | 10/11/2025 16:58:29 | 10/11/2025 16:58:31 | 10/11/2025 21:36:05 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001290 | PCM-20251009-00002046 | TT-20251009-02078 | Reference_telecom | Region_6 | ABBS0162 | ABBS0162 | Equipment | CB_BTS | Switch on CB on Rectifier | Fawad Khan | 10/09/2025 20:35:22 | 10/20/2025 00:49:47 | 10/10/2025 02:35:22 | CELL SERVICE PROBLEM (Phase error exceeds the interference limit) at ABBS0162-G9-L8-L18-NL21-NNR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/09/2025 19:35:06 | Major | 7114 | CELL SERVICE PROBLEM | 10/09/2025 19:35:01 | P3 | 2G | namas | Sceco | 5G_Cell SA | ABBS0162 | FLM_TE | [5 empty] | Phase error exceeds the interference limit |  |  | API | 10/09/2025 20:35:22 | 10/10/2025 00:29:47 | 10/20/2025 00:49:03 |  |  | 10/20/2025 00:49:47 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001312 | PCM-20251009-00002078 | TT-20251009-02100 | Telecom | Region_4 | JED1M7376 | JED0376 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Bilal hassan shaukat ali | 10/09/2025 21:02:03 | 10/21/2025 17:12:36 | 10/10/2025 03:02:03 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7376-CA-L900-L800-SBTS-P3 @ Generator_SG | 10/09/2025 20:55:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 20:55:44 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7376 | FLM_TE |  |  | PCM-20251009-00002076 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/09/2025 21:02:03 | 10/14/2025 02:09:26 | 10/14/2025 02:10:56 | 10/14/2025 02:10:58 | 10/14/2025 02:11:00 | 10/14/2025 06:08:24 |  | Bilal hassan shaukat ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001313 | PCM-20251009-00002079 | TT-20251009-02102 | Telecom | Region_1 | HFB0031 | HFB0031 |  |  |  | Mohamed Magdy Fouad Zayed | 10/09/2025 21:03:02 | 10/22/2025 11:33:38 | 10/10/2025 09:03:02 | (As per BO Request) NEC MW HC Observing PM error and RSL degradation at MW link HFB0031 DIR HFB0032 | 10/09/2025 21:00:16 | Minor | 1-631 | MW_LOF | 10/09/2025 21:00:16 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFB0031 HFB0032 | FLM_TE | [5 empty] | (As per BO Request) NEC MW HC Observing PM error and RSL degradation at MW link HFB0031 DIR HFB0032 |  |  | API | 10/09/2025 21:03:02 | 10/09/2025 22:08:45 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001350 | PCM-20251009-00002148 | TT-20251009-02136 | Telecom | Region_4 | RAB0366 | RAB0366 |  |  |  | Khizer Hayat | 10/09/2025 21:36:16 | 10/10/2025 11:51:26 | 10/10/2025 09:36:16 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3 @ Sceco | 10/09/2025 21:26:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 21:25:57 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0366 | FLM_TE |  |  | PCM-20251009-00002143 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/09/2025 21:36:16 | 10/10/2025 11:51:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001352 | PCM-20251009-00002156 | TT-20251009-01997 | Reference_telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/09/2025 21:40:34 | 10/10/2025 10:17:27 | 10/10/2025 09:40:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/09/2025 17:30:20 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/09/2025 17:30:09 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0296 | FLM_TE |  |  | PCM-20251009-00002133 | Thanks to check & rectify related link JED0947-JED0759 | Thanks to check & rectify related link JED0947-JED0759 |  |  |  | API | 10/09/2025 21:40:34 | 10/10/2025 10:17:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001354 | PCM-20251009-00002166 | TT-20251009-02150 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/09/2025 21:45:05 | 10/20/2025 12:32:48 | 10/10/2025 01:45:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/09/2025 21:44:01 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 21:43:53 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 21:45:05 | 10/10/2025 10:17:41 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001363 | PCM-20251009-00002183 | TT-20251008-02117 | MW_HC | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/09/2025 21:55:04 | 10/11/2025 13:45:00 | 10/10/2025 09:55:04 | Nokia MW HC_P2 Observing Modem Down at JED0252_01-JED0325_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED0252_01-JED0325_02 | FLM_TE |  |  | PCM-20251009-00002092 | Still XPD out of accepted range for H part | Still XPD out of accepted range for H part |  |  |  | API | 10/09/2025 21:55:04 | 10/11/2025 13:45:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001372 | PCM-20251009-00002203 | TT-20251009-02157 | Reference_telecom | Region_6 | WRJL0002 | WRJL0002 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/09/2025 22:04:30 | 10/19/2025 14:22:18 | 10/10/2025 10:04:30 | WRJL0002 Complete Down | 10/09/2025 21:37:46 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/09/2025 21:37:46 | P3 | WIFI | mohail | Sceco | Wifi SA | WRJL0002 | FLM_TE |  |  | PCM-20251009-00002179 | WRJL0002 | WRJL0002 |  |  |  | API | 10/09/2025 22:04:30 | 10/10/2025 11:50:21 | 10/11/2025 14:52:58 | 10/11/2025 14:53:23 | 10/11/2025 15:38:28 | 10/19/2025 14:22:18 |  | Muhammad Jamal Khan Abbas Ali | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001375 | PCM-20251009-00002210 | TT-20251009-02152 | Telecom | Region_4 | JDJZ1M7870 | JDJZ0870 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/09/2025 22:13:29 | 10/19/2025 17:44:17 | 10/10/2025 04:13:29 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDJZ1M7870-G9-NL8-L18-SBTS-P3 @ Sceco | 10/09/2025 21:43:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 21:43:28 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JDJZ1M7870 | FLM_TE |  |  | PCM-20251009-00002171 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/09/2025 22:13:29 | 10/10/2025 13:43:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001377 | PCM-20251009-00002213 | TT-20251009-02167 | Telecom | Region_4 | NSH0138 | NSH0138 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/09/2025 22:13:59 | 10/14/2025 19:40:41 | 10/10/2025 04:13:59 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at NSH0138-GSM-UMTS-P3 @ Generator_DG | 10/09/2025 21:54:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 21:54:28 | P3 | 2G | adam | Generator_DG | 5G_Cell SA | NSH0138 | FLM_TE |  |  | PCM-20251009-00002191 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/09/2025 22:13:59 | 10/10/2025 11:32:30 | 10/14/2025 19:40:33 |  |  | 10/14/2025 19:40:41 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251009001380 | PCM-20251009-00002219 | TT-20251009-02177 | Telecom | Region_4 | JED0109 | JED0109 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/09/2025 22:17:06 | 10/21/2025 17:12:32 | 10/10/2025 04:17:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/09/2025 22:16:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 22:16:12 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/09/2025 22:17:06 | 10/09/2025 22:35:13 | 10/12/2025 13:14:48 |  |  | 10/12/2025 13:15:06 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001381 | PCM-20251009-00002220 | TT-20251009-02160 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/09/2025 22:17:22 | 10/10/2025 10:17:42 | 10/10/2025 10:17:22 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/09/2025 21:50:42 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/09/2025 21:50:35 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251009-00002185 | Please check the HW issue at site | Please check the HW issue at site |  |  |  | API | 10/09/2025 22:17:22 | 10/10/2025 10:17:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001395 | PCM-20251009-00002238 | TT-20251009-01862 | Reference_telecom | Region_1 | DMJR0129 | DMJR0129 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/09/2025 22:36:41 | 10/10/2025 00:11:45 | 10/10/2025 10:36:41 | External Clock Reference Problem at DMJR0129-P3_SRAN @ Sceco | 10/09/2025 15:07:46 | Minor | 26262 | External Clock Reference Problem | 10/09/2025 15:01:41 | P3 | SRAN | quriyat | Sceco | 2G NSA | DMJR0129 | FLM_TE |  |  | PCM-20251009-00002208 | Kindly check the below links locally as visibility issue QRY0608-DMJ0132-DMJR0129 | Kindly check the below links locally as visibility issue QRY0608-DMJ0132-DMJR0129 |  |  |  | API | 10/09/2025 22:36:41 | 10/10/2025 00:11:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251009001403 | PCM-20251009-00002250 | TT-20251009-02202 | Telecom | [7 empty] | 10/09/2025 22:45:46 | 10/09/2025 22:45:46 | 10/10/2025 04:45:46 | BASE STATION ANTENNA LINE PROBLEM at MAK1U6745-G18-L18-L21-SBTS-P1-HRM @ Sceco | 10/09/2025 22:33:34 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/09/2025 22:33:27 | P1 | 4G |  | Sceco | LTE NSA | MAK1U6745 | FLM_TE |  |  | PCM-20251009-00002246 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/09/2025 22:45:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001417 | PCM-20251009-00002280 | TT-20251009-02237 | Reference_telecom | Region_4 | TFBH9061 | TFBH9061 |  |  |  | Ahmad Kamal Abdelmawla | 10/09/2025 23:21:42 | 10/14/2025 20:35:21 | 10/10/2025 11:21:42 | ReplaceableUnitMissing observed in TFBH9061_01 towards 10.3.236.114 @ Generator_SG | 10/09/2025 11:23:50 | Minor |  | ReplaceableUnitMissing | 10/09/2025 11:21:35 | P3 | Repeater | taif | Generator_SG | TX NSA | TFBH9061 | FLM_TE | [8 empty] | API | 10/09/2025 23:21:42 | 10/14/2025 20:35:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251009001418 | PCM-20251009-00002282 | TT-20251009-02028 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/09/2025 23:21:49 | 10/09/2025 23:21:49 | 10/10/2025 05:21:49 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/09/2025 19:43:01 | Major | 7114 | CELL SERVICE PROBLEM | 10/09/2025 19:42:56 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251009-00001995 | Site is clear pls close | Site is clear pls close |  |  |  | API | 10/09/2025 23:21:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251009001420 | PCM-20251009-00002285 | TT-20251009-02211 | Reference_telecom | Region_4 | JED2886 | JED2886 |  |  |  | BARKAT ALI MAIN HILAL | 10/09/2025 23:24:16 | 10/10/2025 10:17:27 | 10/10/2025 11:24:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2886-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Generator_SG | 10/09/2025 20:51:46 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/09/2025 20:51:36 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2886 | FLM_TE |  |  | PCM-20251009-00002255 | Please check the site down | Please check the site down |  |  |  | API | 10/09/2025 23:24:16 | 10/10/2025 10:17:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000011 | PCM-20251010-00000016 | TT-20251009-01517 | Reference_telecom | Region_4 | JED0930 | JED0930 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/10/2025 00:21:32 | 10/11/2025 10:47:13 | 10/10/2025 06:21:32 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED0930-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/09/2025 14:48:16 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/09/2025 14:48:05 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0930 | FLM_TE |  |  | PCM-20251009-00001431 | GPS issue is clear , please check both AEHC are faulty | GPS issue is clear , please check both AEHC are faulty |  |  |  | API | 10/10/2025 00:21:32 | 10/11/2025 10:45:35 | 10/11/2025 10:47:08 |  |  | 10/11/2025 10:47:13 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000033 | PCM-20251010-00000066 | TT-20251010-00066 | EM | Region_5 | JDMK1M8406 | JDMK2406 |  |  |  | Atif Javed Javed Hussain | 10/10/2025 01:09:11 | 10/16/2025 11:25:51 | 10/10/2025 13:09:11 | SHELTER DOOR OPEN;Default System Time at JDMK1M8406-CA-P3 @ Generator_SG | 10/10/2025 01:08:45 | Minor | 7103 | SHELTER DOOR OPEN;Default System Time | 10/09/2025 03:01:33 | P3 | 4G | makkah | Generator_SG | LTE NSA | JDMK1M8406 | FLM_EM | [5 empty] | SHELTER DOOR OPEN;Default System Time |  |  | API | 10/10/2025 01:09:11 | 10/16/2025 11:25:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000054 | PCM-20251010-00000120 | TT-20251009-02226 | Telecom | Region_4 | JED0347 | JED0347 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/10/2025 01:58:28 | 10/15/2025 11:46:55 | 10/10/2025 07:58:28 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED0347-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/09/2025 23:03:06 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/09/2025 23:02:57 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0347 | FLM_TE |  |  | PCM-20251009-00002269 | Support to restore JED1MN0035 site. | Support to restore JED1MN0035 site. |  |  |  | API | 10/10/2025 01:58:28 | 10/15/2025 11:46:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000064 | PCM-20251010-00000138 | TT-20251010-00139 | Telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/10/2025 02:16:19 | 10/19/2025 13:20:38 | 10/10/2025 14:16:19 | RF Unit Maintenance Link Failure at RYQ0972-P3_SRAN @ Sceco | 10/10/2025 02:14:24 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/10/2025 01:47:54 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0972 | FLM_TE | [8 empty] | API | 10/10/2025 02:16:19 | 10/10/2025 09:21:10 | [6 empty] | ZAIN O-M |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000073 | PCM-20251010-00000152 | TT-20251010-00167 | EM | Region_5 | MAK6028 | MAK6028 |  |  |  | Atif Javed Javed Hussain | 10/10/2025 02:47:50 | 10/16/2025 11:25:51 | 10/10/2025 14:47:50 | AIRCON 1 FAILURE at MAK6028-GSM-P3 @ Sceco | 10/10/2025 02:39:28 | Minor | 7103 | AIRCON 1 FAILURE | 10/10/2025 02:39:23 | P3 | 2G | makkah | Sceco | 2G NSA | MAK6028 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/10/2025 02:47:50 | 10/16/2025 11:25:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000115 | PCM-20251010-00000242 | TT-20251010-00282 | EM | Region_1 | DAM0471 | DAM0471 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/10/2025 04:34:46 | 10/10/2025 08:14:35 | 10/10/2025 16:34:46 | NETECO: All Li Batt Communication Failure at DAM0471 @ Sceco | 10/10/2025 04:28:17 | Minor | 13800 | All Li Batt Communication Failure | 10/10/2025 04:28:17 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0471 | FLM_EM | [8 empty] | API | 10/10/2025 04:34:46 | 10/10/2025 08:14:35 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000118 | PCM-20251010-00000245 | TT-20251010-00287 | Telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/10/2025 04:37:22 | 10/20/2025 12:32:48 | 10/10/2025 16:37:22 | BASE STATION INFORMATION (No module fan detected) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/10/2025 04:29:23 | Minor | 7115 | BASE STATION INFORMATION | 10/10/2025 04:29:17 | VIP | 5G | jeddah | Generator_DG | 5G NSA | JED1MN0180 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/10/2025 04:37:22 | 10/10/2025 10:17:43 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000140 | PCM-20251010-00000282 | TT-20251010-00038 | Telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/10/2025 06:03:44 | 10/10/2025 09:21:11 | 10/10/2025 12:03:44 | 1(LTE) sites down under RYQ0972-P3_SRAN @ Sceco | 10/10/2025 00:38:57 | Major | 301 | NE Is Disconnected | 10/10/2025 00:38:49 | P3 | SRAN | majma | Sceco | LTE SA | RYQ0972-P3_SRAN | FLM_TE | RYQ0972 | Results: DOWN SITE HUB RYQ0972-P3_SRAN RYQ0972 Summary: Hub: RYQ0972, Down Count: 1, Down Sites: RYQ0972-P3_SRAN Alarm Summary: RYQ0972 No Active Alarm on HUB | PCM-20251010-00000065 | Dear FLM, kindly check site up now | Dear FLM, kindly check site up now |  | sites down |  | API | 10/10/2025 06:03:44 | 10/10/2025 09:21:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000142 | PCM-20251010-00000285 | TT-20251010-00343 | EM | Region_6 | MKW1M8121 | MKW2121 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/10/2025 06:09:21 | 10/11/2025 08:24:31 | 10/10/2025 18:09:21 | RECTIFIER MODULE FAILURE at MKW1M8121-L8-L18-SBTS-P3 @ Generator_SG | 10/10/2025 06:01:13 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/10/2025 06:01:07 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8121 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/10/2025 06:09:21 | 10/11/2025 08:24:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251010000158 | PCM-20251010-00000308 | TT-20251010-00373 | Telecom | Region_6 | BHAB2442 | BHAB2442 |  |  |  | Muhammad Tayyab | 10/10/2025 06:39:31 | 10/16/2025 18:32:52 | 10/10/2025 12:39:31 | 1(2G) sites down under BHAB2442-P3-WBB-G3/BHAB2442-P3-WBB-G3 @ Generator_SG | 10/10/2025 06:31:24 | Major | 7706 | BTS O&M LINK FAILURE | 10/10/2025 06:31:20 | P3 | 2G | Albaha | Generator_SG | 2G SA | BHAB2442-P3-WBB-G3 | FLM_TE | BHAB2442 | Results: DOWN SITE HUB BHAB2442-P3-WBB-G3 BHAB2442 Summary: Hub: BHAB2442, Down Count: 1, Down Sites: BHAB2442-P3-WBB-G3 Alarm Summary: BHAB2442 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/10/2025 06:39:31 | 10/14/2025 15:14:33 | 10/16/2025 18:32:52 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000190 | PCM-20251010-00000360 | TT-20251010-00430 | Reference_telecom | Region_1 | DMJR0138 | DMJR0138 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/10/2025 07:34:03 | 10/10/2025 12:00:04 | 10/10/2025 19:34:03 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR0138-P1-DIA_SRAN @ Sceco_STB | 10/10/2025 04:33:52 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/10/2025 04:33:49 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | DMJR0138 | FLM_TE | [8 empty] | API | 10/10/2025 07:34:03 | 10/10/2025 12:00:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000201 | PCM-20251010-00000377 | TT-20251010-00450 | Telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/10/2025 07:59:22 | 10/10/2025 12:56:49 | 10/10/2025 19:59:22 | DCU Optical Module Transmit/Receive Fault at RIYA6056-DCU3 @ Sceco | 10/10/2025 07:48:16 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/10/2025 07:52:24 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/10/2025 07:59:22 | 10/10/2025 12:56:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251010000212 | PCM-20251010-00000393 | TT-20251008-02099 | MW_HC | Region_5 | MAK0179 | MAK0179 |  |  |  | Amr Abdulla Ali Othman | 10/10/2025 08:12:46 | 10/10/2025 08:12:46 | 10/10/2025 20:12:46 | Nokia MW HC_P0 Observing Performance Issue at MAK0179-MAK0102-6 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0179-MAK0102-6 | FLM_TE |  |  | PCM-20251010-00000385 | Please share the RCA plus start & end time of action as currently link is cleared | Please share the RCA plus start & end time of action as currently link is cleared |  |  |  | API | 10/10/2025 08:12:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000229 | PCM-20251010-00000417 | TT-20251010-00478 | EM | Region_6 | QLW2370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/10/2025 08:27:46 | 10/21/2025 22:25:53 | 10/10/2025 14:27:46 | 1(2G/LTE) sites down under QLW2370-P3/QLW2370-P3 @ Generator_SG | 10/10/2025 08:19:34 | Major | 7706 | BTS O&M LINK FAILURE | 10/10/2025 08:19:32 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | QLW2370-P3 | FLM_EM | QLW2370 | Results: DOWN SITE HUB QLW2370-P3 QLW2370 Summary: Hub: QLW2370, Down Count: 1, Down Sites: QLW2370-P3 Alarm Summary: QLW2370 Alarm Active on HUB |  |  |  |  | sites down |  | Manual | 10/10/2025 08:27:46 | 10/21/2025 22:25:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251010000231 | PCM-20251010-00000419 | TT-20251009-00066 | Telecom | Region_2 | R2_RY3_HWBSC01 | RY3 |  |  |  | Saddam hussain muhammad khan | 10/10/2025 08:31:45 | 10/16/2025 12:51:12 | 10/10/2025 14:31:45 | Ethernet Link Fault at R2_RY3_HWBSC01 | 10/09/2025 00:29:09 | Major | 25880 | Ethernet Link Fault | 10/09/2025 00:29:09 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY3_HWBSC01 | FLM_TE |  | Dear IPRAN ,IPBB and DWDM Team Kindly check from your end as alarm stamped on time as below Name Alarm Source Last Occurred (NT) Location Information Ethernet Link Fault R2_RY3_HWBSC01 2025-10-09 00:49:33 Subrack No.=1, Slot No.=20, Subsystem No.=0, Ethernet Port No.=3, Alarm Cause=Link Broken Ethernet Link Fault R2_RY3_HWBSC01 2025-10-09 00:49:33 Subrack No.=1, Slot No.=20, Subsystem No.=0, Ethernet Port No.=2, Alarm Cause=Link Broken Ethernet Link Fault R2_RY3_HWBSC01 2025-10-09 00:49:32 Subrack No.=1, Slot No.=20, Subsystem No.=0, Ethernet Port No.=1, Alarm Cause=Link Broken Ethernet Link Fault R2_RY3_HWBSC01 2025-10-09 00:49:32 Subrack No.=1, Slot No.=20, Subsystem No.=0, Ethernet Port No.=0, Alarm Cause=Link Broken Ethernet Link Fault R2_RY3_HWBSC01 2025-10-09 00:29:09 Subrack No.=2, Slot No.=20, Subsystem No.=0, Ethernet Port No.=0, Alarm Cause=Link Broken | PCM-20251009-00002283 | dear FLM, Kindly close TT as alarm now cleared after change board form IPRAN side | dear FLM, Kindly close TT as alarm now cleared after change board form IPRAN side |  |  |  | API | 10/10/2025 08:31:45 | [7 empty] | Huawei_care_Spares |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000245 | PCM-20251010-00000437 | TT-20251010-00510 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/10/2025 08:42:15 | 10/10/2025 12:16:46 | 10/10/2025 20:42:15 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/10/2025 08:36:04 | Minor | 1589 | AC Overfrequency | 10/10/2025 08:36:04 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/10/2025 08:42:15 | 10/10/2025 11:25:01 | 10/10/2025 12:16:34 |  |  | 10/10/2025 12:16:46 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000255 | PCM-20251010-00000452 | TT-20251010-00522 | Reference_telecom | Region_5 | MAK0259 | MAK0259 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Husain Hassan Ishag Omer | 10/10/2025 08:51:02 | 10/12/2025 18:03:32 | 10/10/2025 20:51:02 | LossOfSignal observed in MAK0259 _02 towards 10.10.143.211 @ Sceco | 10/09/2025 20:51:00 | Minor |  | LossOfSignal | 10/09/2025 20:50:55 | P3 | 2G | makkah | Sceco | TX NSA | MAK0259 | FLM_TE | [8 empty] | API | 10/10/2025 08:51:02 | 10/12/2025 15:58:35 | 10/12/2025 16:03:27 | 10/12/2025 16:03:34 | 10/12/2025 16:22:04 | 10/12/2025 18:03:32 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000281 | PCM-20251010-00000492 | TT-20251010-00564 | Reference_telecom | Region_6 | TNM0723 | TNM0723 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/10/2025 09:24:35 | 10/10/2025 11:50:22 | 10/10/2025 21:24:35 | ReplaceableUnitMissing observed in TNM0723_01 towards 10.74.121.100 @ Generator_SG | 10/09/2025 21:25:34 | Minor |  | ReplaceableUnitMissing | 10/09/2025 21:24:29 | P3 | 2G | mohail | Generator_SG | TX NSA | TNM0723 | FLM_TE | [8 empty] | API | 10/10/2025 09:24:35 | 10/10/2025 11:50:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000285 | PCM-20251010-00000497 | TT-20251010-00568 | Reference_telecom | Region_6 | RJL0126 | RJL0126 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/10/2025 09:26:39 | 10/10/2025 11:50:23 | 10/10/2025 21:26:39 | DemFail observed in RJL0126 towards 10.3.86.36 @ Sceco | 10/09/2025 21:26:12 | Minor |  | DemFail | 10/09/2025 21:26:08 | P3 | 2G | mohail | Sceco | TX NSA | RJL0126 | FLM_TE | [8 empty] | API | 10/10/2025 09:26:39 | 10/10/2025 11:50:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000299 | PCM-20251010-00000516 | TT-20251010-00591 | Reference_telecom | Region_4 | HAW1M4360 | HAW2360 |  |  |  | Rashid Shafique | 10/10/2025 09:51:59 | 10/11/2025 14:08:47 | 10/10/2025 21:51:59 | BASE STATION NOTIFICATION (Fan failure) at HAW1M4360-P2 @ Sceco | 10/10/2025 09:21:57 | Minor | 7652 | BASE STATION NOTIFICATION | 10/10/2025 09:21:40 | P2 | 3G | taif | Sceco | 3G NSA | HAW1M4360 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/10/2025 09:51:59 | 10/11/2025 14:08:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000304 | PCM-20251010-00000521 | TT-20251010-00596 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/10/2025 09:59:13 | 10/19/2025 17:44:10 | 10/10/2025 15:59:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/10/2025 09:58:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 09:58:13 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/10/2025 09:59:13 | 10/11/2025 10:23:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251010000367 | PCM-20251010-00000621 | TT-20251010-00102 | Telecom | Region_4 | JED1M8619 | JED2619 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/10/2025 11:16:35 | 10/10/2025 11:16:35 | 10/10/2025 17:16:35 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M8619-P3-CA-L800 @ Sceco | 10/10/2025 01:25:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 01:26:39 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8619 | FLM_TE |  |  | PCM-20251010-00000105 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/10/2025 11:16:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251010000369 | PCM-20251010-00000625 | TT-20251010-00385 | Reference_telecom | Region_4 | JED1MN0625 | JED0625 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/10/2025 11:18:19 | 10/10/2025 11:18:19 | 10/10/2025 23:18:19 | Fronthaul loop back connectivity check failure at JED1MN0625-NR2.6-P2 @ Sceco | 10/10/2025 06:18:05 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/10/2025 06:17:57 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0625 | FLM_TE |  |  | PCM-20251010-00000315 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/10/2025 11:18:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000383 | PCM-20251010-00000643 | TT-20251010-00697 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/10/2025 11:27:04 | 10/10/2025 12:33:02 | 10/10/2025 23:27:04 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/10/2025 11:20:05 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/10/2025 11:20:01 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/10/2025 11:27:04 | 10/10/2025 12:33:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000401 | PCM-20251010-00000668 | TT-20251010-00716 | EM | Region_4 | HHR4-SEC0036 | SEC0036 | Enviroment | SCECO_Failure | SCECO auto restored | Aly Ahmed Aly Sawy | 10/10/2025 11:49:04 | 10/10/2025 13:50:23 | 10/10/2025 17:49:04 | MAIN AC POWER FAILURE ALARM AT HHR4-SEC0036 | 10/10/2025 11:44:34 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/10/2025 11:44:34 | P1 | DWDM | jeddah | Sceco | DWDM NSA | HHR4-SEC0036 | FLM_EM | [8 empty] | API | 10/10/2025 11:49:04 | 10/10/2025 13:09:55 | 10/10/2025 13:10:16 | 10/10/2025 13:10:21 | 10/10/2025 13:28:23 | 10/10/2025 13:50:23 |  | Aly Ahmed Aly Sawy |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000406 | PCM-20251010-00000675 | TT-20251010-00723 | EM | Region_4 | JED1U6729 | JED6029 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/10/2025 11:57:31 | 10/11/2025 13:29:29 | 10/10/2025 23:57:31 | Rectifier Low battery voltage at JED1U6729-G9-L18-L21-SBTS-P3 @ Sceco | 10/10/2025 11:49:02 | Minor | 7103 | Rectifier Low battery voltage | 10/10/2025 11:48:56 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6729 | FLM_EM | [5 empty] | Rectifier Low battery voltage |  |  | API | 10/10/2025 11:57:31 | 10/11/2025 13:29:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000461 | PCM-20251010-00000772 | TT-20251010-00841 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/10/2025 13:31:31 | 10/11/2025 13:29:29 | 10/11/2025 01:31:31 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/10/2025 13:23:34 | Minor | 7103 | AIRCON 1 FAILURE | 10/10/2025 13:23:25 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/10/2025 13:31:31 | 10/11/2025 13:29:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000466 | PCM-20251010-00000780 | TT-20251010-00857 | Telecom | Region_1 | DAM2330 | DAM2330 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/10/2025 13:42:54 | 10/10/2025 17:20:06 | 10/11/2025 01:42:54 | RF Unit Temperature Unacceptable at DAM2330-FWA-P1-VIP_SRAN @ Sceco | 10/10/2025 13:35:44 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/10/2025 13:35:39 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2330 | FLM_TE | [8 empty] | API | 10/10/2025 13:42:54 | 10/10/2025 17:20:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000475 | PCM-20251010-00000789 | TT-20251010-00870 | Telecom | Region_4 | THO0371 | THO0371 |  |  |  | Khizer Hayat | 10/10/2025 13:51:10 | 10/19/2025 17:44:09 | 10/10/2025 19:51:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/10/2025 13:50:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 13:50:24 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | THO0371 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/10/2025 13:51:10 | 10/10/2025 22:37:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251010000484 | PCM-20251010-00000798 | TT-20251010-00877 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/10/2025 13:54:15 | 10/10/2025 13:54:15 | 10/10/2025 19:54:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/10/2025 13:53:09 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 13:52:59 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/10/2025 13:54:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000502 | PCM-20251010-00000834 | TT-20251010-00900 | Telecom | Region_4 | JED0972 | JED0972 | Enviroment | Air Condition | Change Fan | Mohammed Ramadan A Abu Abid | 10/10/2025 14:25:29 | 10/12/2025 09:02:41 | 10/10/2025 20:25:29 | 2(2G) 2(LTE) 2(5G) sites down under JED0972-P3,JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/10/2025 14:13:38 | Major | 7706 | BTS O&M LINK FAILURE | 10/10/2025 14:13:34 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED6020-GSM-P3 2G_LTE,JED0972-P3 2G | FLM_TE | JED0972 | DOWN SITE HUB TX FB JED0972 JED0972 LOS to Air Scale JED6020 JED6020 Link flapping at HUB | PCM-20251010-00000827 | DOWN SITE HUB TX FB JED0972 JED0972 LOS to Air Scale JED6020 JED6020 Link flapping at HUB | DOWN SITE HUB TX FB JED0972 JED0972 LOS to Air Scale JED6020 JED6020 Link flapping at HUB |  | sites down |  | API | 10/10/2025 14:25:29 | 10/10/2025 19:35:20 | 10/11/2025 14:27:11 | 10/11/2025 14:27:16 | 10/11/2025 14:32:26 | 10/12/2025 09:02:41 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000560 | PCM-20251010-00000932 | TT-20251010-00275 | Telecom | Region_4 | TFBH9443-LL-CSG-01 | TFBH9443 |  |  |  | Ahmad Kamal Abdelmawla | 10/10/2025 15:49:37 | 10/14/2025 20:35:22 | 10/10/2025 21:49:37 | P0_MW_Router_Protection_To_LTH0330-SF-CSG-01_GigabitEthernet0/1/3_TFBH9443-LTH0330 | 10/10/2025 04:29:00 | Major | 15269 | LOS | 10/10/2025 04:29:00 | P1 | IPRAN | taif | Generator_DG | IPRAN_NSA | P0_MW_Router_Protection_To_LTH0330-SF-CSG-01_GigabitEthernet0/1/3_TFBH9443-LTH0330 | FLM_TE |  |  | PCM-20251010-00000586 | Dear FLM , Thanks to check | Dear FLM , Thanks to check |  |  |  | API | 10/10/2025 15:49:37 | 10/14/2025 20:35:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000572 | PCM-20251010-00000955 | TT-20251010-01039 | EM | Region_6 | BHAB1M8442 | BHAB2442 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/10/2025 16:02:53 | 10/10/2025 21:36:29 | 10/11/2025 04:02:53 | High temp at BHAB1M8442-G9-L8-SBTS-P3-WBB-G3 @ Generator_SG | 10/10/2025 15:54:59 | Minor | 7103 | High temp | 10/10/2025 15:54:49 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8442 | FLM_EM | [5 empty] | High temp |  |  | API | 10/10/2025 16:02:53 | 10/10/2025 21:36:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000577 | PCM-20251010-00000976 | TT-20251010-01057 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/10/2025 16:10:40 | 10/21/2025 22:25:55 | 10/11/2025 04:10:40 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/10/2025 16:08:36 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/10/2025 13:01:42 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | Manual | 10/10/2025 16:10:40 | 10/21/2025 22:25:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251010000654 | PCM-20251010-00001109 | TT-20251010-00833 | Reference_telecom | Region_4 | JED1MN0180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/10/2025 17:47:53 | 10/20/2025 12:32:50 | 10/10/2025 21:47:53 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0180-NR2.6-P1-VIP @ Generator_DG | 10/10/2025 09:24:02 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 09:23:54 | VIP | 5G | jeddah | Generator_DG | 5G_Cell SA | JED1MN0180 | FLM_TE |  |  | PCM-20251010-00000765 | Kindly perform HC | Kindly perform HC |  |  |  | API | 10/10/2025 17:47:53 | 10/12/2025 09:54:29 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000657 | PCM-20251010-00001112 | TT-20251010-01227 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/10/2025 17:52:56 | 10/10/2025 22:37:57 | 10/10/2025 23:52:56 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/10/2025 17:45:52 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/10/2025 17:45:43 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/10/2025 17:52:56 | 10/10/2025 22:37:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000667 | PCM-20251010-00001136 | TT-20251010-01257 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/10/2025 18:16:11 | 10/12/2025 09:54:29 | 10/10/2025 22:16:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/10/2025 18:15:32 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 18:15:24 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/10/2025 18:16:11 | 10/12/2025 09:54:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251010000695 | PCM-20251010-00001180 | TT-20251010-00846 | Telecom | Region_4 | JED0791 | JED0791 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/10/2025 19:09:44 | 10/10/2025 19:09:44 | 10/11/2025 07:09:44 | BASE STATION ANTENNA LINE PROBLEM at JED0791-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/10/2025 13:26:10 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/10/2025 13:25:59 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0791 | FLM_TE |  |  | PCM-20251010-00000774 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/10/2025 19:09:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000698 | PCM-20251010-00001183 | TT-20251010-01019 | Telecom | Region_4 | JED1M7552 | JED0552 | Equipment | BSS_HW_Stuck | Reset System Module | Abdullah Ahmad Mohammad Abdelsheekh | 10/10/2025 19:11:41 | 10/18/2025 10:52:06 | 10/11/2025 01:11:41 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/10/2025 15:43:52 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/10/2025 15:43:47 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251010-00000934 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/10/2025 19:11:41 | 10/18/2025 09:33:31 | 10/18/2025 09:35:59 | 10/18/2025 09:36:01 | 10/18/2025 09:36:03 | 10/18/2025 10:52:06 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000722 | PCM-20251010-00001212 | TT-20251010-01355 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/10/2025 19:40:24 | 10/12/2025 09:06:00 | 10/11/2025 01:40:24 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/10/2025 16:40:18 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/10/2025 16:40:04 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/10/2025 19:40:24 | 10/12/2025 09:06:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251010000723 | PCM-20251010-00001213 | TT-20251010-01357 | Telecom | [7 empty] | 10/10/2025 19:40:38 | 10/10/2025 19:40:38 | 10/11/2025 01:40:38 | BEFFEC_EXC ALARM AT RY4-ALRAJHI | 10/10/2025 12:08:45 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/10/2025 12:08:45 | P1 | DWDM |  | Sceco_STB | DWDM NSA | RY4-ALRAJHI | FLM_TE | [8 empty] | API | 10/10/2025 19:40:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000733 | PCM-20251010-00001228 | TT-20251010-01371 | Telecom | Region_4 | JED0557 | JED0557 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Mostafa Hamouda Ibrahem | 10/10/2025 19:53:19 | 10/19/2025 17:44:08 | 10/11/2025 01:53:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0557-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/10/2025 19:52:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 19:52:31 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0557 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/10/2025 19:53:19 | 10/17/2025 15:06:53 | 10/17/2025 15:19:26 | 10/17/2025 15:19:29 | 10/17/2025 15:19:31 | 10/17/2025 16:07:29 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000756 | PCM-20251010-00001257 | TT-20251010-01397 | Telecom | Region_4 | JED1M8127 | JED2127 | Equipment | SFP_BTS | Re-Plug SFP | Mohammed Ramadan A Abu Abid | 10/10/2025 20:13:59 | 10/12/2025 09:03:23 | 10/11/2025 02:13:59 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M8127-CA-L800-P3 @ Sceco | 10/10/2025 20:09:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 20:09:00 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M8127 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/10/2025 20:13:59 | 10/11/2025 10:15:50 | 10/11/2025 10:16:11 | 10/11/2025 10:16:13 | 10/11/2025 10:34:32 | 10/12/2025 09:03:23 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251010000764 | PCM-20251010-00001274 | TT-20251008-02049 | MW_HC | Region_4 | TURY0684 | TURY0684 |  |  |  | Rashid Shafique | 10/10/2025 20:35:04 | 10/22/2025 13:21:50 | 10/11/2025 08:35:04 | Nokia MW HC_P0 Observing Performance Issue at TURY0684_1-TURY0685_2 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | taif | Sceco | TX NSA | TURY0684_1-TURY0685_2 | FLM_TE |  |  | PCM-20251009-00002279 | XPD still 43 | XPD still 43 |  |  |  | API | 10/10/2025 20:35:04 | 10/11/2025 14:08:49 | 10/22/2025 13:02:46 | 10/22/2025 13:21:48 | 10/22/2025 13:21:50 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000776 | PCM-20251010-00001295 | TT-20251010-01434 | Reference_telecom | Region_4 | JED6008 | JED6008 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/10/2025 20:49:37 | 10/17/2025 17:37:54 | 10/11/2025 08:49:37 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6008-DCU-P3 @ Sceco | 10/10/2025 17:49:12 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/10/2025 17:49:08 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/10/2025 20:49:37 | 10/12/2025 13:42:36 | 10/17/2025 17:37:46 |  |  | 10/17/2025 17:37:54 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000780 | PCM-20251010-00001302 | TT-20251008-02008 | MW_HC | Region_4 | JED2266 | JED2266 |  |  |  | MALIK ATIF ZAMAN | 10/10/2025 21:00:00 | 10/12/2025 09:54:30 | 10/11/2025 09:00:00 | Nokia MW HC_P0 Observing RSL Issue at JED2266-JED0373 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2266-JED0373 | FLM_TE |  |  | PCM-20251009-00002266 | Degrade on RadioLAG#1 - TO JED0373 , alarm log not clear last 24h | Degrade on RadioLAG#1 - TO JED0373 , alarm log not clear last 24h |  |  |  | API | 10/10/2025 21:00:00 | 10/12/2025 09:54:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000791 | PCM-20251010-00001325 | TT-20251010-01467 | EM | Region_4 | JZMA1M8413 | JZMA2413 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/10/2025 21:21:40 | 10/11/2025 10:49:24 | 10/11/2025 09:21:40 | RECTIFIER MAJOR ALARM at JZMA1M8413-G9-L8-L18-SBTS-P3-CAP @ Generator_SG | 10/10/2025 21:13:41 | Minor | 7103 | RECTIFIER MAJOR ALARM | 10/10/2025 21:13:34 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8413 | FLM_EM | [5 empty] | RECTIFIER MAJOR ALARM |  |  | API | 10/10/2025 21:21:40 | 10/11/2025 10:49:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000797 | PCM-20251010-00001346 | TT-20251010-01493 | Telecom | Region_4 | JED0339 | JED0339 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/10/2025 21:46:59 | 10/11/2025 10:46:10 | 10/11/2025 09:46:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0339-G9-L18-L21-NR2.6-SBTS-P2-USF @ Generator_SG | 10/10/2025 21:45:58 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 21:45:53 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0339 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/10/2025 21:46:59 | 10/11/2025 10:45:37 | 10/11/2025 10:46:04 |  |  | 10/11/2025 10:46:10 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000807 | PCM-20251010-00001360 | TT-20251010-01503 | Reference_telecom | Region_1 | DMJR2266 | DMJR2266 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/10/2025 21:53:11 | 10/10/2025 22:13:51 | 10/11/2025 09:53:11 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR2266-P3-USF_SRAN @ Sceco | 10/10/2025 18:52:44 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/10/2025 18:52:39 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR2266 | FLM_TE | [8 empty] | API | 10/10/2025 21:53:11 | 10/10/2025 22:13:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000818 | PCM-20251010-00001386 | TT-20251010-00810 | Telecom | Region_4 | RNRY0667 | RNRY0667 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Ahmad Kamal Abdelmawla | 10/10/2025 22:01:47 | 10/14/2025 20:54:24 | 10/11/2025 04:01:47 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at RNRY0667-P3 @ Sceco | 10/10/2025 13:03:49 | Major | 7607 | TRX OPERATION DEGRADED | 10/10/2025 13:03:46 | P3 | 2G | taif | Sceco | 2G_TRX NSA | RNRY0667 | FLM_TE |  |  | PCM-20251010-00000750 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/10/2025 22:01:47 | 10/14/2025 20:35:23 | 10/14/2025 20:54:07 |  |  | 10/14/2025 20:54:24 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000828 | PCM-20251010-00001418 | TT-20251010-01528 | Telecom | Region_4 | JDJZ1M7870 | JDJZ0870 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/10/2025 22:22:52 | 10/19/2025 17:44:17 | 10/11/2025 04:22:52 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDJZ1M7870-G9-NL8-L18-SBTS-P3 @ Sceco | 10/10/2025 22:13:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 22:13:25 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JDJZ1M7870 | FLM_TE |  |  | PCM-20251010-00001411 | RSSI TS Steps: • Clean or Remake Jumper connectors • Check any bending in the Jumper cable. • Confirm MHA HW is OK and Configuration is as per physical connectivity.(If available at site). • RET HW and Values as per design (If available at site). • Hard reset to equipment if values are stuck and not changing at all with above actions. • Sector Swap to check if value swapping to other sector or port. • External interference test as per Care recommendation. • Finally HW replacement. | RSSI TS Steps: • Clean or Remake Jumper connectors • Check any bending in the Jumper cable. • Confirm MHA HW is OK and Configuration is as per physical connectivity.(If available at site). • RET HW and Values as per design (If available at site). • Hard reset to equipment if values are stuck and not changing at all with above actions. • Sector Swap to check if value swapping to other sector or port. • External interference test as per Care recommendation. • Finally HW replacement. |  |  |  | API | 10/10/2025 22:22:52 | 10/11/2025 10:48:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000829 | PCM-20251010-00001419 | TT-20251010-01524 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/10/2025 22:23:10 | 10/12/2025 09:54:31 | 10/11/2025 10:23:10 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/10/2025 22:12:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 22:11:58 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251010-00001405 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/10/2025 22:23:10 | 10/12/2025 09:54:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000831 | PCM-20251010-00001424 | TT-20251010-00777 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/10/2025 22:25:37 | 10/21/2025 18:13:48 | 10/11/2025 04:25:37 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/10/2025 12:41:36 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/10/2025 12:41:25 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251010-00000719 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/10/2025 22:25:37 | 10/20/2025 14:29:28 | 10/21/2025 18:13:43 |  |  | 10/21/2025 18:13:48 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000873 | PCM-20251010-00001497 | TT-20251010-01056 | Telecom | Region_6 | SRA1M8355 | SRA2355 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/10/2025 23:14:42 | 10/23/2025 16:24:31 | 10/11/2025 11:14:42 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/10/2025 16:08:36 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/10/2025 00:06:28 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_TE |  |  | PCM-20251010-00001376 | pls close TT as site was down | pls close TT as site was down |  |  |  | Manual | 10/10/2025 23:14:42 | 10/23/2025 13:11:44 | 10/23/2025 16:24:22 |  |  | 10/23/2025 16:24:31 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251010000877 | PCM-20251010-00001501 | TT-20251010-01593 | EM | Region_6 | BHAB1M8055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/10/2025 23:16:52 | 10/11/2025 11:48:00 | 10/11/2025 11:16:52 | RECTIFIER MAINS POWER FAILURE at BHAB1M8055-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/10/2025 23:08:56 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/10/2025 23:08:46 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAB1M8055 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/10/2025 23:16:52 | 10/11/2025 11:48:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251010000882 | PCM-20251010-00001508 | TT-20251010-01583 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/10/2025 23:21:52 | 10/10/2025 23:21:52 | 10/11/2025 05:21:52 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/10/2025 22:59:29 | Major | 7114 | CELL SERVICE PROBLEM | 10/10/2025 22:59:23 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251010-00001482 | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site |  |  |  | API | 10/10/2025 23:21:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000896 | PCM-20251010-00001530 | TT-20251010-01568 | Telecom | Region_4 | JED0109 | JED0109 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/10/2025 23:42:57 | 10/21/2025 17:12:32 | 10/11/2025 05:42:57 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/10/2025 22:48:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 22:47:52 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE |  |  | PCM-20251010-00001527 | TE issue | TE issue |  |  |  | API | 10/10/2025 23:42:57 | 10/11/2025 09:16:36 | 10/12/2025 10:05:47 |  |  | 10/12/2025 10:06:28 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251010000901 | PCM-20251010-00001537 | TT-20251010-01624 | Reference_telecom | Region_4 | MLJI1M7186 | MLJI0186 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/10/2025 23:53:39 | 10/11/2025 10:27:45 | 10/11/2025 05:53:39 | BASE STATION SERVICE PROBLEM(TX out of order) at MLJI1M7186-G9-NL8-L18-NL21-SBTS-P2 (Ref:TT-20251010-01550) | 10/10/2025 23:14:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 23:14:57 | P2 | 4G | alaith | Generator_DG | LTE SA | MLJI1M7186-G9-NL8-L18-NL21-SBTS-P2 | FLM_TE | [8 empty] | API | 10/10/2025 23:53:39 | 10/11/2025 10:24:05 | 10/11/2025 10:27:36 |  |  | 10/11/2025 10:27:45 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000026 | PCM-20251011-00000049 | TT-20251011-00047 | Telecom | Region_2 | MJM0495 | MJM0495 | Transsmission | DWDM_SW | Alarm at DWDM End Flapped and Cleared | Muhammad Tahir Abdulrazzaq | 10/11/2025 00:57:37 | 10/12/2025 10:19:05 | 10/11/2025 06:57:37 | SPAN_LOSS_EXCEED_EOL at MJM0495_OCS @ Sceco_STB | 10/11/2025 00:53:16 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/11/2025 00:53:07 | P1 | SRAN | majma | Sceco_STB | DWDM NSA | MJM0495 | FLM_TE | [5 empty] | 1-TO ZLF0510(1-B)-12-G6WDAPXF-11(LINEIN/LINEOUT(TO ZLF0510_OCS-G6WDAPXF(1-A02)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/11/2025 00:57:37 | 10/12/2025 09:56:43 | 10/12/2025 10:05:50 |  |  | 10/12/2025 10:19:05 |  | Muhammad Tahir Abdulrazzaq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000028 | PCM-20251011-00000051 | TT-20251011-00048 | EM | Region_6 | BHAB2055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/11/2025 01:03:33 | 10/11/2025 11:48:01 | 10/11/2025 07:03:33 | 1(2G/LTE) sites down under BHAB2055-P3-WBB-G3/BHAB2055-P3-WBB-G3 @ Sceco | 10/11/2025 00:55:15 | Major | 7706 | BTS O&M LINK FAILURE | 10/11/2025 00:55:11 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | BHAB2055-P3-WBB-G3 | FLM_EM | BHAB2055 | Results: DOWN SITE HUB BHAB2055-P3-WBB-G3 BHAB2055 Summary: Hub: BHAB2055, Down Count: 1, Down Sites: BHAB2055-P3-WBB-G3 Alarm Summary: BHAB2055 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/11/2025 01:03:33 | 10/11/2025 11:48:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000037 | PCM-20251011-00000071 | TT-20251011-00049 | Reference_telecom | Region_4 | JED1M7839 | JED0839 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/11/2025 01:17:06 | 10/11/2025 10:45:55 | 10/11/2025 05:17:06 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1M7839-CA-L900-P1-VIP @ Sceco | 10/11/2025 00:54:16 | Critical | 7654 | CELL OPERATION DEGRADED | 10/11/2025 00:54:08 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7839 | FLM_TE |  |  | PCM-20251011-00000050 | Please check the VSWR issue | Please check the VSWR issue |  |  |  | API | 10/11/2025 01:17:06 | 10/11/2025 10:45:39 | 10/11/2025 10:45:50 |  |  | 10/11/2025 10:45:55 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000053 | PCM-20251011-00000099 | TT-20251011-00097 | Reference_telecom | Region_6 | JDJ2040 | JDJ2040 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/11/2025 01:38:55 | 10/11/2025 10:20:17 | 10/11/2025 13:38:55 | DemFail observed in JDJ2040 towards 10.89.249.2 @ Sceco | 10/10/2025 13:38:37 | Minor |  | DemFail | 10/10/2025 13:38:32 | P3 | 2G | baish | Sceco | TX NSA | JDJ2040 | FLM_TE | [8 empty] | API | 10/11/2025 01:38:55 | 10/11/2025 10:20:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000063 | PCM-20251011-00000114 | TT-20251011-00105 | EM | Region_4 | JZMA2413 | JZMA2413 |  |  |  | Khizer Hayat | 10/11/2025 02:00:03 | 10/11/2025 03:57:00 | 10/11/2025 08:00:03 | 1(2G/LTE) sites down under JZMA2413-P3-CAP/JZMA2413-P3-CAP @ Generator_SG | 10/11/2025 01:51:35 | Major | 7706 | BTS O&M LINK FAILURE | 10/11/2025 01:51:28 | P3 | 2G | jeddah | Generator_SG | 2G SA | JZMA2413-P3-CAP | FLM_TE | JZMA2413 | Results: DOWN SITE HUB JZMA2413-P3-CAP JZMA2413 Summary: Hub: JZMA2413, Down Count: 1, Down Sites: JZMA2413-P3-CAP Alarm Summary: JZMA2413 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/11/2025 02:00:03 | 10/11/2025 03:57:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000070 | PCM-20251011-00000136 | TT-20251011-00035 | Telecom | Region_4 | RAB0366 | RAB0366 |  |  |  | Khizer Hayat | 10/11/2025 02:12:10 | 10/11/2025 03:57:00 | 10/11/2025 14:12:10 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3 @ Sceco | 10/11/2025 00:41:48 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 00:41:37 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0366 | FLM_TE |  |  | PCM-20251011-00000038 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/11/2025 02:12:10 | 10/11/2025 03:57:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000097 | PCM-20251011-00000191 | TT-20251011-00180 | Telecom | Region_4 | JDJZ1M8167 | JDJZ2167 | Equipment | BSS_HW_fault | Replace Interface Card | TOSIF AHMED - MUHAMMAD SHARIF | 10/11/2025 02:43:22 | 10/21/2025 17:12:35 | 10/11/2025 08:43:22 | BASE STATION SERVICE PROBLEM (Antenna link is down) at JDJZ1M8167-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/11/2025 02:27:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 02:27:48 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JDJZ1M8167 | FLM_TE |  |  | PCM-20251011-00000173 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/11/2025 02:43:22 | 10/20/2025 18:27:58 | 10/20/2025 18:36:57 | 10/20/2025 18:37:01 | 10/20/2025 18:40:38 | 10/20/2025 19:11:53 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000109 | PCM-20251011-00000217 | TT-20251011-00210 | Telecom | Region_4 | TAF1M7167 | TAF0167 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Ahmad Kamal Abdelmawla | 10/11/2025 03:03:45 | 10/14/2025 20:59:07 | 10/11/2025 09:03:45 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TAF1M7167-CA-L800-P2 @ Sceco | 10/11/2025 02:50:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 02:50:38 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7167 | FLM_TE |  |  | PCM-20251011-00000206 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/11/2025 03:03:45 | 10/14/2025 20:35:26 | 10/14/2025 20:58:58 |  |  | 10/14/2025 20:59:07 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251011000137 | PCM-20251011-00000267 | TT-20251011-00179 | Reference_telecom | Region_4 | BHR0318 | BHR0318 |  |  |  | Ali Mohamed | 10/11/2025 03:26:24 | 10/21/2025 11:39:03 | 10/11/2025 09:26:24 | MW Link down at JED0008-ZJe04-CSG-06 to BHR0318 // TT-20250922-01119 | 10/11/2025 02:31:40 | Major | 15269 | LOS | 10/11/2025 02:31:43 | P1 | 2G | jeddah | Sceco | IPRAN_NSA | MW Link down at JED0008-ZJe04-CSG-06 to BHR0318 // TT-20250922-01119 | FLM_TE | BHR0318 | Hub: BHR0318 We are observing visibility down from our end kindly send team to check locally | PCM-20251011-00000172 | Hub: BHR0318 We are observing visibility down from our end kindly send team to check locally | Hub: BHR0318 We are observing visibility down from our end kindly send team to check locally |  |  |  | API | 10/11/2025 03:26:24 | [7 empty] | STC |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000152 | PCM-20251011-00000301 | TT-20251011-00271 | Telecom | Region_4 | BHR0328 | BHR0328 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/11/2025 03:43:27 | 10/21/2025 13:17:55 | 10/11/2025 07:43:27 | 4(2G) 2(LTE) 4(5G) sites down under BHR2112-P3 @ Sceco | 10/11/2025 03:26:00 | Critical | 7706 | BTS O&M LINK FAILURE | 10/11/2025 03:25:32 | P2 | 2G | jeddah | Generator_SG | 2G_LTE_5G SA | JED0125-CA-L900-L800-SBTS LTE,BHR0328-G9-L8-L18-L21-NR2.6-SBTS-P3 5G,BHR2112-P3 2G_LTE_5G,JED2984-L8-L18-L21-NR2.6-P3-SBTS 5G,JED2019-P3 2G_5G,JED0816-P3 2G,JED0674-P2 2G | FLM_TE | BHR0328 | Site HUB TRM FB JED0125-CA-L900-L800-SBTS LTE JED0125 observing no alarm flapped BHR0328-G9-L8-L18-L21-NR2.6-SBTS-P3 5G BHR0328 observing LOS TO AIRSCALE BHR2112-P3 2G_LTE_5G BHR2112 observing LOS TO AIRSCALE JED2984-L8-L18-L21-NR2.6-P3-SBTS 5G JED2984 observing LOS TO AIRSCALE JED2019-P3 2G_5G JED2019 observing LOS TO AIRSCALE JED0816-P3 2G JED0816 observing LOS TO AIRSCALE JED0674-P2 2G JED0674 observing LOS TO AIRSCALE | PCM-20251011-00000282 | Site HUB TRM FB JED0125-CA-L900-L800-SBTS LTE JED0125 observing no alarm flapped BHR0328-G9-L8-L18-L21-NR2.6-SBTS-P3 5G BHR0328 observing LOS TO AIRSCALE BHR2112-P3 2G_LTE_5G BHR2112 observing LOS TO AIRSCALE JED2984-L8-L18-L21-NR2.6-P3-SBTS 5G JED2984 observing LOS TO AIRSCALE JED2019-P3 2G_5G JED2019 observing LOS TO AIRSCALE JED0816-P3 2G JED0816 observing LOS TO AIRSCALE JED0674-P2 2G JED0674 observing LOS TO AIRSCALE | Site HUB TRM FB JED0125-CA-L900-L800-SBTS LTE JED0125 observing no alarm flapped BHR0328-G9-L8-L18-L21-NR2.6-SBTS-P3 5G BHR0328 observing LOS TO AIRSCALE BHR2112-P3 2G_LTE_5G BHR2112 observing LOS TO AIRSCALE JED2984-L8-L18-L21-NR2.6-P3-SBTS 5G JED2984 observing LOS TO AIRSCALE JED2019-P3 2G_5G JED2019 observing LOS TO AIRSCALE JED0816-P3 2G JED0816 observing LOS TO AIRSCALE JED0674-P2 2G JED0674 observing LOS TO AIRSCALE |  | sites down |  | Manual | 10/11/2025 03:43:27 | 10/21/2025 13:17:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251011000215 | PCM-20251011-00000419 | TT-20251011-00431 | Reference_telecom | Region_4 | JED0063 | JED0063 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/11/2025 05:48:57 | 10/19/2025 14:09:29 | 10/11/2025 17:48:57 | DemFail observed in JED0063_CMOE4005 towards 10.221.226.138 @ Sceco | 10/10/2025 17:48:38 | Minor |  | DemFail | 10/10/2025 17:48:23 | P2 | 2G | jeddah | Sceco | TX NSA | JED0063 | FLM_TE | [8 empty] | API | 10/11/2025 05:48:57 | 10/19/2025 14:04:53 | 10/19/2025 14:08:02 | 10/19/2025 14:09:23 | 10/19/2025 14:09:29 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000261 | PCM-20251011-00000502 | TT-20251011-00524 | Telecom | Region_4 | RYMK0665 | RYMK0665 |  |  |  | Ehab Ali Mohamed Abdou | 10/11/2025 07:31:11 | 10/11/2025 21:15:01 | 10/11/2025 19:31:11 | WRYMK0001 Complete Down | 10/11/2025 07:20:27 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/11/2025 07:20:27 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251011-00000498 | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/11/2025 07:31:11 | 10/11/2025 21:15:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000286 | PCM-20251011-00000537 | TT-20251011-00558 | EM | Region_4 | QIA1M7361 | QIA0361 |  |  |  | Walid Magdy Tawfik Elbana | 10/11/2025 07:54:31 | 10/13/2025 23:46:28 | 10/11/2025 19:54:31 | RECTIFIER MAINS POWER FAILURE at QIA1M7361-L900-L800-P3 @ Sceco | 10/11/2025 07:46:10 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/11/2025 07:46:02 | P3 | 4G | taif | Sceco | LTE NSA | QIA1M7361 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/11/2025 07:54:31 | 10/13/2025 23:46:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000288 | PCM-20251011-00000541 | TT-20251010-00955 | Telecom | Region_4 | RYMK0671-LL-CSG-01 | RYMK0671 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/11/2025 07:56:43 | 10/11/2025 11:23:15 | 10/11/2025 13:56:43 | P0_MW_Router_Protection_To_MW Link_to peer_RYMK0671-LL-CSG-01_GigabitEthernet0/3/8 | 10/10/2025 14:48:44 | Major | 15269 | LOS | 10/10/2025 14:48:42 | P2 | IPRAN | taif | Sceco_STB | IPRAN NSA | RYMK0671-LL-CSG-01 | FLM_TE |  |  | PCM-20251011-00000098 | Thanks to check & rectify related link RNRY0660-RNRY0659 | Thanks to check & rectify related link RNRY0660-RNRY0659 |  |  |  | API | 10/11/2025 07:56:43 | 10/11/2025 11:23:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000308 | PCM-20251011-00000565 | TT-20251011-00155 | Telecom | Region_4 | MLJI0204 | MLJI0204 | Enviroment | SCECO_Failure | SCECO auto restored | TOSIF AHMED - MUHAMMAD SHARIF | 10/11/2025 08:06:40 | 10/14/2025 19:40:21 | 10/11/2025 14:06:40 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MLJI0204-P3 @ Generator_SG | 10/11/2025 02:16:38 | Major | 7607 | TRX OPERATION DEGRADED | 10/11/2025 02:16:36 | P3 | 2G | alaith | Generator_SG | 2G_TRX NSA | MLJI0204 | FLM_TE |  |  | PCM-20251011-00000155 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/11/2025 08:06:40 | 10/11/2025 10:24:09 | 10/14/2025 19:40:11 |  |  | 10/14/2025 19:40:21 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251011000313 | PCM-20251011-00000570 | TT-20251011-00443 | Telecom | Region_4 | JED1M8619 | JED2619 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/11/2025 08:08:16 | 10/11/2025 08:08:16 | 10/11/2025 14:08:16 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M8619-P3-CA-L800 @ Sceco | 10/11/2025 06:03:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 06:04:40 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8619 | FLM_TE |  |  | PCM-20251011-00000428 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/11/2025 08:08:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000316 | PCM-20251011-00000574 | TT-20251011-00308 | Telecom | Region_4 | RAB1M3475 | RAB0475 |  |  |  | Khizer Hayat | 10/11/2025 08:08:58 | 10/11/2025 10:08:34 | 10/11/2025 14:08:58 | CELL FAULTY (Failure in optical RP3 interface) at RAB1M3475-P2 @ Sceco | 10/11/2025 03:53:48 | Major | 7653 | CELL FAULTY | 10/11/2025 03:53:30 | P2 | 3G | jeddah | Sceco | LTE_Cell SA | RAB1M3475 | FLM_TE |  |  | PCM-20251011-00000325 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/11/2025 08:08:58 | 10/11/2025 10:08:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000332 | PCM-20251011-00000609 | TT-20251011-00106 | Reference_telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/11/2025 08:26:35 | 10/12/2025 11:00:13 | 10/11/2025 20:26:35 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/10/2025 23:55:01 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/10/2025 23:54:55 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0296 | FLM_TE |  |  | PCM-20251011-00000307 | Please close the site is clear | Please close the site is clear |  |  |  | API | 10/11/2025 08:26:35 | 10/12/2025 11:00:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000342 | PCM-20251011-00000620 | TT-20251011-00611 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/11/2025 08:28:58 | 10/20/2025 12:32:49 | 10/11/2025 14:28:58 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MKYL0914-GSM-UMTS-P3 @ Sceco | 10/11/2025 08:14:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 08:13:54 | P3 | 2G | alaith | Sceco | 5G_Cell SA | MKYL0914 | FLM_TE |  |  | PCM-20251011-00000588 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/11/2025 08:28:58 | 10/11/2025 10:23:27 | [6 empty] | Force_Majeure |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000344 | PCM-20251011-00000623 | TT-20251011-00413 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/11/2025 08:30:05 | 10/20/2025 12:32:51 | 10/11/2025 14:30:05 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/11/2025 05:22:38 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/11/2025 05:22:33 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251011-00000409 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/11/2025 08:30:05 | 10/12/2025 09:54:35 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000347 | PCM-20251011-00000626 | TT-20251011-00283 | Telecom | Region_4 | YLM1M3757 | YLM0757 |  |  |  | Riasat Ali Allah Baksh | 10/11/2025 08:30:35 | 10/11/2025 10:23:28 | 10/11/2025 14:30:35 | BASE STATION CONFIGURATION PROBLEM at YLM1M3757-P3 @ Generator_SG | 10/11/2025 03:29:35 | Major | 7112 | BASE STATION CONFIGURATION PROBLEM | 10/11/2025 03:29:22 | P3 | 3G | alaith | Generator_SG | 3G NSA | YLM1M3757 | FLM_TE |  |  | PCM-20251011-00000284 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/11/2025 08:30:35 | 10/11/2025 10:23:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000352 | PCM-20251011-00000631 | TT-20251011-00634 | Reference_telecom | Region_6 | BLJ2274 | BLJ2274 |  |  |  | Manzoor Ahmed | 10/11/2025 08:33:15 | 10/11/2025 09:13:31 | 10/11/2025 20:33:15 | ReplaceableUnitMissing observed in BLJ2274_01 towards 10.221.244.3 @ Generator_SG | 10/10/2025 20:33:14 | Minor |  | ReplaceableUnitMissing | 10/10/2025 20:33:06 | P3 | 2G | Albaha | Generator_SG | TX NSA | BLJ2274 | FLM_TE | [8 empty] | API | 10/11/2025 08:33:15 | 10/11/2025 09:13:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000356 | PCM-20251011-00000635 | TT-20251011-00282 | Reference_telecom | Region_4 | RAB1M3475 | RAB0475 | Equipment | SFP_BTS | Clean SFP | Khizer Hayat | 10/11/2025 08:34:48 | 10/14/2025 15:40:12 | 10/11/2025 14:34:48 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at RAB1M3475-P2 @ Sceco | 10/11/2025 03:06:04 | Major | 7771 | WCDMA CELL OUT OF USE | 10/11/2025 03:03:55 | P2 | 3G | jeddah | Sceco | 3G SA | RAB1M3475 | FLM_TE |  |  | PCM-20251011-00000283 | Please check the RFM issue | Please check the RFM issue |  |  |  | API | 10/11/2025 08:34:48 | 10/11/2025 10:08:34 | 10/12/2025 07:09:42 | 10/12/2025 07:09:52 | 10/12/2025 07:09:58 | 10/14/2025 15:40:12 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000448 | PCM-20251011-00000789 | TT-20251011-00787 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/11/2025 10:05:13 | 10/21/2025 22:26:01 | 10/11/2025 22:05:13 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/11/2025 09:57:10 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/11/2025 09:56:59 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | Manual | 10/11/2025 10:05:13 | 10/21/2025 22:26:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251011000456 | PCM-20251011-00000803 | TT-20251011-00798 | Telecom | Region_4 | JED0253 | JED0253 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/11/2025 10:14:00 | 10/19/2025 17:44:10 | 10/11/2025 16:14:00 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connector) at JED0253-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/11/2025 10:09:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 10:09:06 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0253 | FLM_TE | [5 empty] | Increased BER detected on the optical connector |  |  | API | 10/11/2025 10:14:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000471 | PCM-20251011-00000834 | TT-20251011-00816 | Telecom | Region_1 | DRN2328 | DRN2328 | Enviroment | SCECO_Failure | SCECO auto restored | Imran Ali Yousaf | 10/11/2025 10:36:21 | 10/19/2025 17:31:21 | 10/11/2025 14:36:21 | 2(2G) 1(3G) 2(LTE) sites down under DRN0110-P1-HUB,ARM0732-P3/DM1MBSCH01 @ Sceco | 10/11/2025 10:24:43 | Critical | 21825 | CSL Fault | 10/11/2025 10:24:41 | P3 | SRAN | dammam | Sceco | 2G_3G_LTE SA | ARM0732-P3 2G_3G_LTE,DRN0110-P1-HUB 2G_LTE | FLM_TE | DRN2328 | Dear FLM, Hub is DRN2328 We are observing HARD_BAD alarm active at EX1 & BUS_ERR alarm flapping at CSHUF ,Kindly check and support to resolve the issue. | PCM-20251011-00000830 | Dear FLM, Hub is DRN2328 We are observing HARD_BAD alarm active at EX1 & BUS_ERR alarm flapping at CSHUF ,Kindly check and support to resolve the issue. | Dear FLM, Hub is DRN2328 We are observing HARD_BAD alarm active at EX1 & BUS_ERR alarm flapping at CSHUF ,Kindly check and support to resolve the issue. |  | sites down |  | API | 10/11/2025 10:36:21 | 10/11/2025 13:13:03 | 10/19/2025 17:30:47 |  |  | 10/19/2025 17:31:21 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000490 | PCM-20251011-00000861 | TT-20251011-00852 | Reference_EM | Region_2 | QSDH2M5722 | QSDH0722 |  |  |  | Moustafa Elzaafarany Abdellah | 10/11/2025 10:55:50 | 10/11/2025 14:20:33 | 10/11/2025 22:55:50 | Low fuel alarm at QSDH2M5722-P3 @ Generator_SG | 10/11/2025 10:45:41 | Minor | 65115 | Low fuel alarm | 10/11/2025 10:45:37 | P3 | 2G | dawadmi | Generator_SG | 2G NSA | QSDH2M5722 | FLM_EM | [8 empty] | API | 10/11/2025 10:55:50 | 10/11/2025 14:20:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000491 | PCM-20251011-00000862 | TT-20251011-00853 | Telecom | Region_4 | JED1MN0957 | JED0957 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/11/2025 10:56:22 | 10/11/2025 13:45:14 | 10/11/2025 22:56:22 | BASE STATION INFORMATION (No module fan detected) at JED1MN0957-NR2.6-P3 @ Sceco | 10/11/2025 10:48:04 | Minor | 7115 | BASE STATION INFORMATION | 10/11/2025 10:48:00 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN0957 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/11/2025 10:56:22 | 10/11/2025 13:45:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000571 | PCM-20251011-00000990 | TT-20251011-00970 | Reference_telecom | Region_1 | SMN0837 | SMN0837 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/11/2025 12:00:26 | 10/21/2025 11:37:50 | 10/12/2025 00:00:26 | RF Unit RX Channel RTWP/RSSI Unbalanced at SMN0837-P2-USF_SRAN @ Sceco | 10/11/2025 09:00:16 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/11/2025 09:00:13 | P2 | SRAN | hafr | Sceco | 2G NSA | SMN0837 | FLM_TE | [8 empty] | API | 10/11/2025 12:00:26 | 10/11/2025 12:19:58 | [6 empty] | CITC |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000609 | PCM-20251011-00001058 | TT-20251011-01012 | Reference_telecom | Region_4 | JED0299 | JED0299 | Equipment | BSS_HW_Stuck | Reset Controller Card | Abdullah Ahmad Mohammad Abdelsheekh | 10/11/2025 12:37:20 | 10/11/2025 13:32:26 | 10/11/2025 18:37:20 | 4(2G) 1(LTE) 4(5G) sites down under JED2635-P3,JED0299-P2,JED0005-P2,JED0855-P2 (Ref::TT-20251011-00548) | 10/11/2025 11:00:18 | Major | 7706 | BTS O&M LINK FAILURE | 10/11/2025 11:00:18 | P2 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED2635-P3 JED0299-P2 JED0005-P2 JED0855-P2 | FLM_TE | JED2635 | Results: DOWN SITE HUB JED2635-P3 JED2635 JED0299-P2 JED0299 JED0005-P2 JED0005 JED0855-P2 JED0299 Summary: Hub: JED2635, Down Count: 1, Down Sites: JED2635-P3 Hub: JED0299, Down Count: 2, Down Sites: JED0299-P2, JED0855-P2 Hub: JED0005, Down Count: 1, Down Sites: JED0005-P2 Alarm Summary: JED2635 No Active Alarm on HUB JED0299 No Active Alarm on HUB JED0005 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/11/2025 12:37:20 | 10/11/2025 12:43:49 | 10/11/2025 13:29:09 | 10/11/2025 13:29:11 | 10/11/2025 13:29:13 | 10/11/2025 13:32:26 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251011000618 | PCM-20251011-00001074 | TT-20251011-01034 | Telecom | Region_4 | JED0151(JD1) | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/11/2025 12:47:02 | 10/11/2025 12:47:02 | 10/11/2025 18:47:02 | LOCAL_FAULT & REM_SEF ALARMs at PEACE CLS and JED0151(JD1) | 10/11/2025 12:41:58 | Major | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/11/2025 12:41:58 | P1 | DWDM | jeddah | Sceco_STB_Rental | DWDM NSA | JED0151(JD1) | FLM_TE | [8 empty] | API | 10/11/2025 12:47:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000623 | PCM-20251011-00001087 | TT-20251008-02659 | Telecom | Region_6 | RYAB0644 | RYAB0644 |  |  |  | Umair Abbas Muhammad Abbas | 10/11/2025 12:52:02 | 10/11/2025 19:20:25 | 10/12/2025 00:52:02 | As per BO request NEC MW link RYAB0644-RYAB9006 | 10/08/2025 19:06:54 | Minor | 113388 | LOF | 10/08/2025 19:06:56 | P2 | 2G | turaib | Sceco | TX NSA | RYAB0644-RYAB9006 | FLM_TE |  |  | PCM-20251011-00000892 | Dear FLM team as per process link should be stable and clear at least 1H and share snap evidence with PCM | Dear FLM team as per process link should be stable and clear at least 1H and share snap evidence with PCM |  |  |  | API | 10/11/2025 12:52:02 | 10/11/2025 19:20:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000631 | PCM-20251011-00001101 | TT-20251011-01058 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/11/2025 12:59:51 | 10/11/2025 13:29:33 | 10/12/2025 00:59:51 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/11/2025 12:51:45 | Minor | 7103 | AIRCON 1 FAILURE | 10/11/2025 12:51:38 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/11/2025 12:59:51 | 10/11/2025 13:29:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000733 | PCM-20251011-00001266 | TT-20251011-01217 | Telecom | Region_4 | JED0759 | JED0759 |  |  |  | BARKAT ALI MAIN HILAL | 10/11/2025 14:23:34 | 10/12/2025 11:00:15 | 10/12/2025 02:23:34 | PT::FLM need to perform HC at JED0759 (BO request) | 10/11/2025 14:23:26 | Minor | 676767671 | Health Check-WO to TE FME | 10/11/2025 14:23:26 | P2 | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G NSA | JED0759 | FLM_TE | [8 empty] | API | 10/11/2025 14:23:34 | 10/12/2025 11:00:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000750 | PCM-20251011-00001288 | TT-20251011-01238 | EM | Region_1 | RSK2624 | RSK2624 |  |  |  | Dileesh Muringothil Devarajan | 10/11/2025 14:37:29 | 10/11/2025 14:47:47 | 10/12/2025 02:37:29 | Door opening alarm at RSK2624-P3_SRAN-PC @ Sceco | 10/11/2025 14:37:03 | Minor | 65101 | Door opening alarm | 10/11/2025 13:57:34 | P3 | SRAN | jubail | Sceco | 2G NSA | RSK2624 | FLM_EM | [8 empty] | API | 10/11/2025 14:37:29 | 10/11/2025 14:47:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000752 | PCM-20251011-00001290 | TT-20251011-01241 | EM | Region_1 | RSK2624 | RSK2624 |  |  |  | Dileesh Muringothil Devarajan | 10/11/2025 14:39:02 | 10/11/2025 14:47:47 | 10/12/2025 02:39:02 | Mains Failure at RSK2624-P3_SRAN-PC @ Sceco | 10/11/2025 14:37:03 | Minor | 65109 | Mains Failure | 10/11/2025 13:57:34 | P3 | SRAN | jubail | Sceco | 2G NSA | RSK2624 | FLM_EM | [8 empty] | API | 10/11/2025 14:39:02 | 10/11/2025 14:47:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251011000787 | PCM-20251011-00001355 | TT-20251011-01305 | Telecom | Region_4 | JED2350 | JED2350 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/11/2025 15:01:45 | 10/19/2025 17:44:11 | 10/11/2025 21:01:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2350-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-FON @ Sceco | 10/11/2025 15:00:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 15:00:51 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED2350 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/11/2025 15:01:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000812 | PCM-20251011-00001386 | TT-20251011-01347 | Reference_telecom | Region_4 | USMD0696 | USMD0696 | Transsmission | SFP_Transmission | Replace SFP | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/11/2025 15:19:20 | 10/22/2025 17:17:10 | 10/12/2025 03:19:20 | BASE STATION INFORMATION (Unit temperature is high) at USMD0696-GSM-P1-HUB @ Sceco | 10/11/2025 14:39:00 | Minor | 7115 | BASE STATION INFORMATION | 10/11/2025 14:38:49 | P1 | 2G | taif | Sceco | 2G NSA | USMD0696 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/11/2025 15:19:20 | 10/12/2025 18:15:01 | 10/22/2025 14:06:16 | 10/22/2025 14:06:19 | 10/22/2025 14:06:21 | 10/22/2025 17:17:10 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000816 | PCM-20251011-00001391 | TT-20251011-01349 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/11/2025 15:21:55 | 10/19/2025 17:44:10 | 10/11/2025 21:21:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/11/2025 15:21:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 15:21:09 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/11/2025 15:21:55 | 10/12/2025 13:33:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000842 | PCM-20251011-00001424 | TT-20251011-01382 | EM | Region_6 | BHAB1M7883 | BHAB0883 |  |  |  | Zia Ur Rahamn | 10/11/2025 15:39:28 | 10/11/2025 16:14:56 | 10/12/2025 03:39:28 | AIRCON 2 FAILURE at BHAB1M7883-G9-L8-SBTS-P3 @ Sceco | 10/11/2025 15:31:09 | Minor | 7103 | AIRCON 2 FAILURE | 10/11/2025 15:30:57 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7883 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/11/2025 15:39:28 | 10/11/2025 16:14:56 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251011000866 | PCM-20251011-00001464 | TT-20251011-01405 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/11/2025 16:03:13 | 10/11/2025 16:03:13 | 10/11/2025 22:03:13 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/11/2025 15:49:11 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/11/2025 15:49:04 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251011-00001452 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/11/2025 16:03:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000879 | PCM-20251011-00001489 | TT-20251011-01439 | EM | Region_6 | BHAB1M8055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/11/2025 16:19:46 | 10/11/2025 17:52:06 | 10/12/2025 04:19:46 | RECTIFIER MAINS POWER FAILURE at BHAB1M8055-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/11/2025 16:11:42 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/11/2025 16:11:36 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAB1M8055 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/11/2025 16:19:46 | 10/11/2025 17:52:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000888 | PCM-20251011-00001505 | TT-20251008-02022 | MW_HC | Region_5 | MAK0626 | MAK0626 |  |  |  | Mosab Nasr eldeen Mohamed | 10/11/2025 16:35:10 | 10/14/2025 01:45:18 | 10/12/2025 04:35:10 | Nokia MW HC_P2 Observing Modem Down at MAK0626-MAK0575_02 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0626-MAK0575_02 | FLM_TE |  |  | PCM-20251011-00001485 | approved | approved |  |  |  | API | 10/11/2025 16:35:10 | 10/14/2025 01:45:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000890 | PCM-20251011-00001506 | TT-20251011-01460 | Telecom | Region_6 | RTH9007-LL-CSG-01 | RTH9007 | Transsmission | SFP_Transmission | Reset SFP | Muhammad Ali | 10/11/2025 16:35:38 | 10/12/2025 09:56:57 | 10/12/2025 04:35:38 | Optical Invalid at RTH9007-LL-CSG-01 @ Sceco_STB | 10/11/2025 14:57:25 | Minor | 101-2505224 | Optical Invalid | 10/11/2025 14:57:06 | P1 | IPRAN | raith | Sceco_STB | IPRAN NSA | RTH9007-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/11/2025 16:35:38 | 10/11/2025 17:05:29 | 10/12/2025 08:19:40 |  |  | 10/12/2025 09:56:57 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011000941 | PCM-20251011-00001578 | TT-20251011-01527 | Reference_telecom | Region_2 | RIYB6038 | RIYB6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/11/2025 17:13:27 | 10/12/2025 09:06:03 | 10/11/2025 23:13:27 | RF Unit VSWR Threshold Crossed at RIYB6038-P3_SRAN @ Sceco | 10/11/2025 14:13:35 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/11/2025 14:13:21 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6038 | FLM_TE | [8 empty] | API | 10/11/2025 17:13:27 | 10/12/2025 09:06:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251011000946 | PCM-20251011-00001584 | TT-20251011-01523 | EM | [7 empty] | 10/11/2025 17:15:13 | 10/11/2025 17:15:13 | 10/11/2025 23:15:13 | 1(2G/LTE) sites down under MUMA2070-P3-P3/MUMA2070-P3-P3 @ Sceco | 10/11/2025 17:06:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/11/2025 17:06:51 | P3 | 2G |  | Sceco | 2G_LTE SA | MUMA2070-P3-P3 | FLM_EM | MUMA2070 | Results: DOWN SITE HUB MUMA2070-P3-P3 MUMA2070 Summary: Hub: MUMA2070, Down Count: 1, Down Sites: MUMA2070-P3-P3 Alarm Summary: MUMA2070 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/11/2025 17:15:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011000958 | PCM-20251011-00001601 | TT-20251011-01543 | Telecom | Region_4 | MUMA1M8409 | MUMA2409 |  |  |  | Khizer Hayat | 10/11/2025 17:24:31 | 10/12/2025 06:30:50 | 10/11/2025 23:24:31 | 1(LTE) sites down under MUMA2409-G9-L8-L18-SBTS-P3 @ Sceco | 10/11/2025 17:16:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/11/2025 17:16:09 | P3 | 4G | jeddah | Sceco | LTE SA | MUMA2409-G9-L8-L18-SBTS-P3 | FLM_TE |  | Results: DOWN SITE HUB MUMA2409-G9-L8-L18-SBTS-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  | Timeout connecting to [/10.169.93.54:8080] [URL:http://10.169.93.54:8080/NE3S/1.0/] | sites down |  | API | 10/11/2025 17:24:31 | 10/12/2025 06:30:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011000969 | PCM-20251011-00001616 | TT-20251011-01471 | Reference_telecom | Region_4 | JED2886 | JED2886 | Transsmission | MW_HW_stuck | Reset IDU | Khaled Mohammad Abdallah | 10/11/2025 17:32:38 | 10/18/2025 23:07:28 | 10/12/2025 05:32:38 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2886-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Generator_SG | 10/11/2025 14:41:31 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/11/2025 14:41:20 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2886 | FLM_TE |  |  | PCM-20251011-00001518 | Please check the site down | Please check the site down |  |  |  | API | 10/11/2025 17:32:38 | 10/16/2025 08:41:32 | 10/18/2025 23:07:05 |  |  | 10/18/2025 23:07:28 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001023 | PCM-20251011-00001787 | TT-20251011-01719 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/11/2025 18:25:46 | 10/12/2025 09:54:38 | 10/11/2025 22:25:46 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/11/2025 18:25:01 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 18:24:50 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/11/2025 18:25:46 | 10/12/2025 09:54:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001037 | PCM-20251011-00001812 | TT-20251011-01748 | Reference_telecom | Region_5 | MKYL0912 | MKYL0912 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/11/2025 18:43:44 | 10/11/2025 19:41:50 | 10/12/2025 06:43:44 | NEC MW Observing FAN FAIL at MKYL0912(10.154.140.108) (Ref::TT-20250821-02316) | 08/15/2025 03:07:58 | Minor | FAN FAIL | FAN FAIL | 08/15/2025 03:07:58 | P2 | 2G | makkah | Generator_SG | TX NSA | MKYL0912 | FLM_TE | [5 empty] | NEC MW Observing FAN FAIL at MKYL0912(10.154.140.108) |  |  | API | 10/11/2025 18:43:44 | 10/11/2025 19:41:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001074 | PCM-20251011-00001869 | TT-20251011-01809 | Reference_telecom | Region_5 | MKYL0912 | MKYL0912 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/11/2025 19:15:26 | 10/11/2025 19:41:51 | 10/12/2025 07:15:26 | FAN FAIL at MKYL0912 on 10.154.140.108 @ Generator_SG Ref::(TT-20251003-00805) | 10/03/2025 12:10:07 | Minor | FAN FAIL | FAN FAIL | 10/03/2025 12:10:07 | P2 | 2G | makkah | Generator_SG | TX NSA | MKYL0912 | FLM_TE | [5 empty] | FAN FAIL at MKYL0912 on 10.154.140.108 @ Generator_SG Ref::(TT-20251003-00805) |  |  | API | 10/11/2025 19:15:26 | 10/11/2025 19:41:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011001080 | PCM-20251011-00001877 | TT-20251011-01815 | EM | Region_6 | BHAB1M7821 | BHAB0821 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 10/11/2025 19:19:29 | 10/18/2025 13:10:56 | 10/12/2025 07:19:29 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at BHAB1M7821-G9-L18-SBTS-P2 @ Sceco | 10/11/2025 19:11:31 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/11/2025 19:11:20 | P2 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7821 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/11/2025 19:19:29 | 10/12/2025 06:20:10 | 10/18/2025 13:10:45 |  |  | 10/18/2025 13:10:56 |  | Arif Ullah Shah | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251011001085 | PCM-20251011-00001882 | TT-20251011-01820 | Telecom | Region_4 | JED1M8596 | JED2596 | Equipment | BSS_HW_fault | Replace ALD | MALIK ATIF ZAMAN | 10/11/2025 19:22:36 | 10/19/2025 13:21:34 | 10/11/2025 23:22:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8596-P1-CA-L800 @ Sceco | 10/11/2025 19:21:54 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 19:21:45 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8596 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/11/2025 19:22:36 | 10/12/2025 09:54:39 | 10/17/2025 11:01:14 | 10/17/2025 11:01:20 | 10/17/2025 11:23:14 | 10/19/2025 13:21:34 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251011001103 | PCM-20251011-00001918 | TT-20251011-01853 | EM | [7 empty] | 10/11/2025 19:47:54 | 10/11/2025 19:47:54 | 10/12/2025 07:47:54 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at MUMA1M8070-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/11/2025 19:39:54 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/11/2025 19:39:49 | P3 | 4G |  | Sceco | LTE NSA | MUMA1M8070 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/11/2025 19:47:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251011001145 | PCM-20251011-00001988 | TT-20251011-01931 | Telecom | Region_4 | JED0229 | JED0229 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/11/2025 21:08:58 | 10/19/2025 17:44:12 | 10/12/2025 03:08:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/11/2025 21:08:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 21:08:11 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0229 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/11/2025 21:08:58 | 10/12/2025 11:27:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001161 | PCM-20251011-00002021 | TT-20251011-01968 | Telecom | Region_4 | JED1MN0416 | JED0416 |  |  |  | BARKAT ALI MAIN HILAL | 10/11/2025 21:36:22 | 10/12/2025 11:00:19 | 10/12/2025 09:36:22 | BASE STATION INFORMATION (No module fan detected) at JED1MN0416-NR2.6-P2 @ Sceco | 10/11/2025 21:28:08 | Minor | 7115 | BASE STATION INFORMATION | 10/11/2025 21:27:59 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN0416 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/11/2025 21:36:22 | 10/12/2025 11:00:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251011001167 | PCM-20251011-00002033 | TT-20251011-01978 | Telecom | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/11/2025 21:48:45 | 10/12/2025 13:13:53 | 10/12/2025 03:48:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0110-G9-L8-L18-L21-NR2.6-NNR600-SBTS-P1-VIP @ Sceco | 10/11/2025 21:48:05 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 21:47:54 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0110 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/11/2025 21:48:45 | 10/11/2025 23:33:03 | 10/12/2025 13:13:53 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251011001169 | PCM-20251011-00002037 | TT-20251011-01983 | Telecom | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/11/2025 21:54:27 | 10/12/2025 13:13:48 | 10/12/2025 09:54:27 | BASE STATION INFORMATION (No module fan detected) at JED0110-G9-L8-L18-L21-NR2.6-NNR600-SBTS-P1-VIP @ Sceco | 10/11/2025 21:46:14 | Minor | 7115 | BASE STATION INFORMATION | 10/11/2025 21:46:06 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0110 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/11/2025 21:54:27 | 10/11/2025 23:33:03 | 10/12/2025 13:13:48 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001207 | PCM-20251011-00002099 | TT-20251011-02035 | Reference_telecom | Region_1 | DMJR2266 | DMJR2266 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/11/2025 22:37:20 | 10/12/2025 00:27:36 | 10/12/2025 10:37:20 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR2266-P3-USF_SRAN @ Sceco | 10/11/2025 19:37:05 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/11/2025 19:37:01 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR2266 | FLM_TE | [8 empty] | API | 10/11/2025 22:37:20 | 10/12/2025 00:27:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011001211 | PCM-20251011-00002108 | TT-20251011-01985 | Telecom | Region_6 | KMBS0666 | KMBS0666 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/11/2025 22:42:57 | 10/12/2025 18:21:25 | 10/12/2025 04:42:57 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at KMBS0666-GSM-UMTS-P2-USF @ Sceco | 10/11/2025 21:49:50 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 21:49:38 | P2 | 2G | bisha | Sceco | 5G_Cell SA | KMBS0666 | FLM_TE |  |  | PCM-20251011-00002039 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/11/2025 22:42:57 | 10/11/2025 23:56:31 | 10/12/2025 11:36:39 |  |  | 10/12/2025 18:21:25 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251011001219 | PCM-20251011-00002141 | TT-20251011-02041 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/11/2025 23:00:29 | 10/17/2025 17:36:14 | 10/12/2025 03:00:29 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/11/2025 22:40:32 | Critical | 7654 | CELL OPERATION DEGRADED | 10/11/2025 22:40:25 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251011-00002115 | FLM need to check connecting ports and verify the antenna line FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check connecting ports and verify the antenna line FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/11/2025 23:00:29 | 10/12/2025 13:42:47 | 10/17/2025 17:36:06 |  |  | 10/17/2025 17:36:14 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001221 | PCM-20251011-00002143 | TT-20251011-02044 | Telecom | Region_4 | JED1MN0416 | JED0416 |  |  |  | BARKAT ALI MAIN HILAL | 10/11/2025 23:01:04 | 10/12/2025 11:00:20 | 10/12/2025 05:01:04 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at JED1MN0416-NR2.6-P2 @ Sceco | 10/11/2025 22:48:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 22:47:54 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0416 | FLM_TE |  |  | PCM-20251011-00002116 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/11/2025 23:01:04 | 10/12/2025 11:00:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001238 | PCM-20251011-00002170 | TT-20251011-02091 | Telecom | Region_6 | NAMARA-SEC0016 | SEC0016 |  |  |  | Sohail Nasir Mir Afzal | 10/11/2025 23:18:18 | 10/12/2025 23:42:50 | 10/12/2025 05:18:18 | SPAN_LOSS_UPPER_GAIN at NAMARA-SEC0016_OCS @ Sceco | 10/11/2025 23:12:34 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/11/2025 23:12:34 | P1 | DWDM | abha | Sceco | DWDM NSA | NAMARA-SEC0016 | FLM_TE | [8 empty] | API | 10/11/2025 23:18:18 | 10/12/2025 23:42:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001242 | PCM-20251011-00002178 | TT-20251011-02097 | Telecom | Region_1 | SAK0586 | SAK0586 |  |  |  | Syed Fawad Ali | 10/11/2025 23:26:24 | 10/19/2025 12:35:24 | 10/12/2025 05:26:24 | BBU CPRI Interface Error at SAK0586-P1-SHOP_SRAN @ Sceco | 10/11/2025 13:12:04 | Major | 26234 | BBU CPRI Interface Error | 10/11/2025 13:09:32 | P1 | SRAN | sakaka | Sceco | 2G NSA | SAK0586 | FLM_TE | [8 empty] | API | 10/11/2025 23:26:24 | 10/12/2025 04:29:58 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251011001250 | PCM-20251011-00002198 | TT-20251011-02111 | Telecom | Region_4 | JED1M7637 | JED0637 |  |  |  | MALIK ATIF ZAMAN | 10/11/2025 23:41:59 | 10/12/2025 09:54:40 | 10/12/2025 05:41:59 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M7637-P1-VIP-HUB-CA-L900-L800-SBTS @ Sceco | 10/11/2025 23:28:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 23:28:38 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7637 | FLM_TE |  |  | PCM-20251011-00002192 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/11/2025 23:41:59 | 10/12/2025 09:54:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251011001259 | PCM-20251011-00002230 | TT-20251011-02145 | Telecom | Region_5 | MK2 | MAK2 |  |  |  | Muhammad Zubair | 10/11/2025 23:59:26 | 10/12/2025 00:17:06 | 10/12/2025 03:59:26 | SCECO :: LINK DOWN B/W HAJ0102(HA1)--MAK2 | 10/11/2025 23:58:57 | Critical | 1-12843 | OSC_LOS | 10/11/2025 23:58:47 | P1 | BSC | makkah | Sceco_STB | DWDM NSA | MK2 | FLM_TE | [5 empty] | 0-TO HAJ0102(HA1)(1-A)-7-G2AST4-2(RM2/TM2(TO HAJ0102(HA1)_OCS,TNG6WDAPXF(1-A03)-RM1/TM1))-OSC:1 |  |  | API | 10/11/2025 23:59:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000003 | PCM-20251012-00000004 | TT-20251012-00006 | Telecom | Region_4 | TF1-ASG-02 | TF1 |  |  |  | Rashid Shafique | 10/12/2025 00:04:13 | 10/14/2025 10:12:12 | 10/12/2025 06:04:13 | DWDM_LINK DOWN AT TF1-ASG-02 | 10/11/2025 23:58:47 | Major | 15269 | LOS | 10/11/2025 23:58:47 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | TF1-ASG-02 | FLM_TE | [8 empty] | API | 10/12/2025 00:04:13 | 10/14/2025 10:12:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000009 | PCM-20251012-00000016 | TT-20251012-00016 | EM | Region_1 | AR1 | AR1 |  |  |  | Moustafa Mohamed Saleh Saif | 10/12/2025 00:13:54 | 10/12/2025 09:20:39 | 10/12/2025 04:13:54 | Door opening alarm BSC New shelter at AR1-Shelter 4-WDM-Core-P1 @ Sceco_STB | 10/12/2025 00:13:26 | Critical | 65134 | Door opening alarm BSC New shelter | 10/12/2025 00:13:21 | P1 | DWDM | arar | Sceco_STB | 2G NSA | AR1 | FLM_EM | [8 empty] | API | 10/12/2025 00:13:54 | 10/12/2025 09:20:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000063 | PCM-20251012-00000116 | TT-20251012-00147 | Reference_telecom | Region_4 | JED0803 | JED0803 |  |  |  | MALIK ATIF ZAMAN | 10/12/2025 01:38:36 | 10/12/2025 09:54:40 | 10/12/2025 13:38:36 | Degrade observed in JED0803_2 towards 10.10.150.115 @ Generator_SG | 10/11/2025 13:40:19 | Minor |  | Degrade | 10/11/2025 13:38:10 | VIP | 2G | jeddah | Generator_SG | TX NSA | JED0803 | FLM_TE | [8 empty] | API | 10/12/2025 01:38:36 | 10/12/2025 09:54:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000086 | PCM-20251012-00000147 | TT-20251012-00187 | Reference_telecom | Region_6 | AQQ0716 | AQQ0716 |  |  |  | Manzoor Ahmed | 10/12/2025 02:17:20 | 10/12/2025 04:54:36 | 10/12/2025 14:17:20 | ReplaceableUnitMissing observed in AQQ0716_01 towards 10.221.242.142 @ Sceco | 10/11/2025 14:17:05 | Minor |  | ReplaceableUnitMissing | 10/11/2025 14:16:50 | P3 | 2G | Albaha | Sceco | TX NSA | AQQ0716 | FLM_TE | [8 empty] | API | 10/12/2025 02:17:20 | 10/12/2025 04:54:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000109 | PCM-20251012-00000184 | TT-20251012-00221 | EM | Region_6 | NJR2173 | NJR2173 |  |  |  | Muhammad Shafeeq Muhammad Rafeeq | 10/12/2025 02:24:04 | 10/14/2025 11:16:40 | 10/12/2025 14:24:04 | AIRCON 1 FAILURE at NJR2173-GSM-P3 @ Sceco | 10/12/2025 02:15:59 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 02:15:54 | P3 | 2G | najran | Sceco | 2G NSA | NJR2173 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 02:24:04 | 10/12/2025 09:43:39 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000110 | PCM-20251012-00000186 | TT-20251012-00224 | EM | Region_6 | KMBS1M8312 | KMBS2312 |  |  |  | Asad Saddiq | 10/12/2025 02:25:06 | 10/13/2025 09:26:34 | 10/12/2025 14:25:06 | GEN SET RUNNING at KMBS1M8312-G9-L8-SBTS-P3 @ Sceco | 10/12/2025 02:18:04 | Minor | 7103 | GEN SET RUNNING | 10/12/2025 02:16:53 | P3 | 4G | bisha | Sceco | LTE NSA | KMBS1M8312 | FLM_EM | [5 empty] | GEN SET RUNNING |  |  | API | 10/12/2025 02:25:06 | 10/13/2025 09:26:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000111 | PCM-20251012-00000187 | TT-20251012-00225 | EM | Region_6 | BHAB1M8006 | BHAB2006 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/12/2025 02:25:06 | 10/12/2025 05:37:40 | 10/12/2025 14:25:06 | RECTIFIER MAINS POWER FAILURE at BHAB1M8006-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/12/2025 02:17:27 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/12/2025 02:16:52 | P3 | 4G | mohail | Generator_SG | LTE NSA | BHAB1M8006 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/12/2025 02:25:06 | 10/12/2025 05:37:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000112 | PCM-20251012-00000188 | TT-20251012-00226 | EM | Region_6 | BCH1M8321 | BCH2321 |  |  |  | Fathy Mohamed | 10/12/2025 02:25:06 | 10/12/2025 10:26:55 | 10/12/2025 14:25:06 | RECTIFIER MODULE FAILURE at BCH1M8321-G9-L8-SBTS-P3 @ Generator_SG | 10/12/2025 02:17:15 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/12/2025 02:16:41 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8321 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/12/2025 02:25:06 | 10/12/2025 10:26:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000113 | PCM-20251012-00000189 | TT-20251012-00227 | EM | Region_6 | TBL1M8324 | TBL2324 |  |  |  | Abdul Rauf Muhammad Aslam | 10/12/2025 02:25:06 | 10/13/2025 10:39:23 | 10/12/2025 14:25:06 | GEN SET RUNNING at TBL1M8324-G9-L8-SBTS-P3 @ Generator_DG | 10/12/2025 02:18:02 | Minor | 7103 | GEN SET RUNNING | 10/12/2025 02:16:44 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8324 | FLM_EM | [5 empty] | GEN SET RUNNING |  |  | API | 10/12/2025 02:25:06 | 10/13/2025 10:39:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Departed | CM20251012000136 | PCM-20251012-00000218 | TT-20251012-00257 | Telecom | Region_6 | SABH0098 | SABH0098 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/12/2025 02:43:43 | 10/13/2025 11:32:48 | 10/12/2025 14:43:43 | NSP MW observing visibility down at 1 NE at SABH0098 due to power issue | 10/12/2025 02:42:01 | Minor | 113388 | LOF | 10/12/2025 02:42:03 | P3 | SRAN | abha | Sceco | TX NSA | SABH0098 (10.10.155.90) | FLM_TE | [8 empty] | API | 10/12/2025 02:43:43 | 10/12/2025 08:49:19 | 10/13/2025 11:32:43 | 10/13/2025 11:32:48 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000145 | PCM-20251012-00000234 | TT-20251012-00276 | EM | Region_6 | FIF1M7150 | FIF0150 | Enviroment | Fire Alarm | Reset Fire Pannel | Muhammad Tayyab | 10/12/2025 02:55:03 | 10/18/2025 08:48:26 | 10/12/2025 14:55:03 | AIRCON 1 FAILURE at FIF1M7150-P2-L2100-L800 @ Sceco | 10/12/2025 02:46:47 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 02:46:35 | P2 | 4G | dair | Sceco | LTE NSA | FIF1M7150 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 02:55:03 | 10/12/2025 03:09:29 | 10/18/2025 08:48:00 |  |  | 10/18/2025 08:48:26 |  | Muhammad Tayyab | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000150 | PCM-20251012-00000244 | TT-20251012-00286 | EM | Region_6 | JIZ0170 | JIZ0170 | Enviroment | Air Condition | Change Fan | Adnan Nadeem Abdul Ghaffar | 10/12/2025 03:00:13 | 10/15/2025 01:28:55 | 10/12/2025 15:00:13 | AIRCON 1 FAILURE at JIZ0170-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/12/2025 02:52:05 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 02:51:41 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0170 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 03:00:13 | 10/14/2025 12:35:39 | 10/15/2025 01:28:26 | 10/15/2025 01:28:31 |  | 10/15/2025 01:28:55 |  | Adnan Nadeem Abdul Ghaffar | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000156 | PCM-20251012-00000254 | TT-20251012-00100 | Telecom | Region_5 | MAK1U6934 | MAK6034 |  |  |  | Atif Javed Javed Hussain | 10/12/2025 03:06:24 | 10/16/2025 11:25:54 | 10/12/2025 09:06:24 | CELL OPERATION DEGRADED (VSWR minor alarm) at MAK1U6934-P3-CA @ Sceco | 10/12/2025 00:50:45 | Major | 7654 | CELL OPERATION DEGRADED | 10/12/2025 00:50:35 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6934 | FLM_TE |  |  | PCM-20251012-00000070 | FLM need to check VSWR issue at site and close with RCA. | FLM need to check VSWR issue at site and close with RCA. |  |  |  | API | 10/12/2025 03:06:24 | 10/16/2025 11:25:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000164 | PCM-20251012-00000264 | TT-20251012-00042 | Telecom | Region_4 | JED0391 | JED0391 |  |  |  | BARKAT ALI MAIN HILAL | 10/12/2025 03:08:49 | 10/19/2025 17:44:17 | 10/12/2025 09:08:49 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED0391-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/12/2025 00:25:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 00:24:58 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0391 | FLM_TE |  |  | PCM-20251012-00000034 | FLM need to check SFP, Fiber and HW at site. | FLM need to check SFP, Fiber and HW at site. |  |  |  | API | 10/12/2025 03:08:49 | 10/12/2025 11:00:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000166 | PCM-20251012-00000267 | TT-20251012-00123 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/12/2025 03:09:56 | 10/17/2025 17:36:01 | 10/12/2025 09:09:56 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/12/2025 01:14:23 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/12/2025 01:14:13 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251012-00000086 | FLM need to check ALD and VSWR at site. | FLM need to check ALD and VSWR at site. |  |  |  | API | 10/12/2025 03:09:56 | 10/12/2025 13:43:06 | 10/17/2025 17:35:52 |  |  | 10/17/2025 17:36:01 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000170 | PCM-20251012-00000273 | TT-20251012-00037 | Telecom | Region_4 | JED1M8028 | JED2028 | Equipment | BSS_HW_fault | Replace RF Module | Ahmad Mostafa Hamouda Ibrahem | 10/12/2025 03:16:26 | 10/14/2025 11:57:29 | 10/12/2025 09:16:26 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M8028-CA-L800-SBTS @ Sceco | 10/12/2025 00:20:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 00:20:25 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8028 | FLM_TE |  |  | PCM-20251012-00000028 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/12/2025 03:16:26 | 10/14/2025 10:31:41 | 10/14/2025 11:08:06 | 10/14/2025 11:14:58 | 10/14/2025 11:15:00 | 10/14/2025 11:57:29 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000171 | PCM-20251012-00000274 | TT-20251012-00232 | Telecom | Region_4 | JED1M7178 | JED0178 | Equipment | BSS_HW_fault | Replace RRU | MALIK ATIF ZAMAN | 10/12/2025 03:17:58 | 10/21/2025 09:09:11 | 10/12/2025 09:17:58 | BASE STATION HARDWARE PROBLEM (Low noise amplifier failure) at JED1M7178-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/12/2025 02:20:43 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/12/2025 02:20:32 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7178 | FLM_TE |  |  | PCM-20251012-00000193 | FLM need to check HW and perform HC at site, | FLM need to check HW and perform HC at site, |  |  |  | API | 10/12/2025 03:17:58 | 10/12/2025 09:54:41 | 10/17/2025 16:49:32 | 10/17/2025 16:49:34 | 10/17/2025 17:25:49 | 10/21/2025 09:09:11 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000173 | PCM-20251012-00000279 | TT-20251012-00288 | Reference_telecom | Region_1 | HFF2U6708 | HFF6008 |  |  |  | Mohamed Magdy Fouad Zayed | 10/12/2025 03:20:14 | 10/12/2025 18:41:37 | 10/12/2025 15:20:14 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6708-P1-SHOP @ Sceco | 10/11/2025 23:59:50 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/11/2025 23:59:47 | P1 | 4G | hafouf | Sceco | 2G NSA | HFF2U6708 | FLM_TE |  |  | PCM-20251012-00000246 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/12/2025 03:20:14 | 10/12/2025 18:41:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000174 | PCM-20251012-00000281 | TT-20251012-00324 | EM | Region_6 | BSA2045 | BSA2045 |  |  |  | Asad Saddiq | 10/12/2025 03:20:54 | 10/14/2025 11:16:46 | 10/12/2025 15:20:54 | AIRCON 1 FAILURE at BSA2045-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/12/2025 03:12:55 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 03:12:31 | P3 | 2G | bisha | Sceco | 2G NSA | BSA2045 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 03:20:54 | 10/13/2025 09:26:36 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000178 | PCM-20251012-00000293 | TT-20251011-02136 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/12/2025 03:26:08 | 10/12/2025 09:54:41 | 10/12/2025 15:26:08 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/11/2025 23:46:52 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 23:46:47 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251011-00002221 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/12/2025 03:26:08 | 10/12/2025 09:54:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000194 | PCM-20251012-00000325 | TT-20251012-00368 | EM | Region_6 | BSH1M7034 | BSH0034 |  |  |  | Fizan Ahmed | 10/12/2025 03:47:44 | 10/14/2025 11:16:43 | 10/12/2025 15:47:44 | AIRCON 1 FAILURE at BSH1M7034-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/12/2025 03:39:27 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 03:39:22 | P3 | 4G | baish | Sceco | LTE NSA | BSH1M7034 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 03:47:44 | 10/12/2025 20:08:06 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000212 | PCM-20251012-00000361 | TT-20251012-00410 | Reference_telecom | Region_6 | QIS0267 | QIS0267 | Transsmission | MW_HW_fault | Replace ODU | Muhammad Ali | 10/12/2025 04:36:17 | 10/23/2025 18:04:50 | 10/12/2025 16:36:17 | DemFail observed in QIS0267 towards 10.74.121.179 @ Sceco | 10/11/2025 16:36:07 | Minor |  | DemFail | 10/11/2025 16:35:57 | P3 | 2G | jizan | Sceco | TX NSA | QIS0267 | FLM_TE | [8 empty] | API | 10/12/2025 04:36:17 | 10/12/2025 07:50:38 | 10/23/2025 17:26:06 | 10/23/2025 17:26:08 | 10/23/2025 17:26:10 | 10/23/2025 18:04:50 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000218 | PCM-20251012-00000371 | TT-20251012-00416 | Reference_telecom | Region_4 | JED1MN0416 | JED0416 | Equipment | FAN Cleaning | Clean FAN | BARKAT ALI MAIN HILAL | 10/12/2025 04:56:34 | 10/17/2025 13:20:29 | 10/12/2025 10:56:34 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN0416-NR2.6-P2 @ Sceco | 10/12/2025 00:49:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 00:49:06 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0416 | FLM_TE |  |  | PCM-20251012-00000368 | FLM need to check RF power and perform HC at site. | FLM need to check RF power and perform HC at site. |  |  |  | API | 10/12/2025 04:56:34 | 10/12/2025 11:00:23 | 10/16/2025 17:20:55 | 10/16/2025 17:21:03 | 10/16/2025 17:42:00 | 10/17/2025 13:20:29 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000226 | PCM-20251012-00000383 | TT-20251012-00430 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/12/2025 05:08:51 | 10/12/2025 09:06:07 | 10/12/2025 11:08:51 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/12/2025 02:07:10 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/12/2025 02:08:21 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/12/2025 05:08:51 | 10/12/2025 09:06:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000268 | PCM-20251012-00000432 | TT-20251012-00434 | Telecom | Region_4 | JED1U6049 | JED6149 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/12/2025 05:37:05 | 10/17/2025 17:35:45 | 10/12/2025 11:37:05 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at JED1U6049-P3-CA @ Sceco | 10/12/2025 05:05:28 | Major | 7654 | CELL OPERATION DEGRADED | 10/12/2025 05:05:17 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6049 | FLM_TE |  |  | PCM-20251012-00000386 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 05:37:05 | 10/12/2025 13:43:07 | 10/17/2025 17:35:36 |  |  | 10/17/2025 17:35:45 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000272 | PCM-20251012-00000446 | TT-20251012-00394 | Reference_telecom | Region_2 | QRN0556 | QRN0556 |  |  |  | Zakir Muhammad Yar Muhammad | 10/12/2025 05:47:04 | 10/16/2025 12:51:15 | 10/12/2025 17:47:04 | IP Clock Link Failure at QRN0556-P1-DIA_SRAN @ Sceco | 10/12/2025 01:18:54 | Minor | 26263 | IP Clock Link Failure | 10/12/2025 01:17:41 | P1 | SRAN | dawadmi | Sceco | 2G NSA | QRN0556 | FLM_TE |  |  | PCM-20251012-00000414 | kindly need Health check for MW link NIF0583-NIF0584 , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance | kindly need Health check for MW link NIF0583-NIF0584 , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance |  |  |  | API | 10/12/2025 05:47:04 | 10/14/2025 08:09:39 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000278 | PCM-20251012-00000457 | TT-20251012-00475 | Telecom | Region_4 | JED1U6831 | JED6131 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/12/2025 05:52:40 | 10/17/2025 17:35:30 | 10/12/2025 11:52:40 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/12/2025 05:39:15 | Major | 7654 | CELL OPERATION DEGRADED | 10/12/2025 05:39:06 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251012-00000447 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 05:52:40 | 10/12/2025 13:43:08 | 10/17/2025 17:35:16 |  |  | 10/17/2025 17:35:30 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000280 | PCM-20251012-00000462 | TT-20251011-00788 | Telecom | Region_4 | JED6021 | JED6021 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/12/2025 05:53:15 | 10/14/2025 16:38:29 | 10/12/2025 17:53:15 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6021-G9-L1800-L2100-SBTS-P3 @ Generator_SG | 10/11/2025 10:01:17 | Minor | 7114 | CELL SERVICE PROBLEM | 10/11/2025 10:01:08 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED6021 | FLM_TE |  |  | PCM-20251011-00000790 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 05:53:15 | 10/12/2025 13:43:09 | 10/14/2025 15:21:58 | 10/14/2025 15:23:32 | 10/14/2025 15:27:10 | 10/14/2025 16:38:29 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000281 | PCM-20251012-00000463 | TT-20251011-00067 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | BTS_Cable | Re-Tightened Indoor Feeder cable Connector | Mohamed Farag Abdelbary | 10/12/2025 05:53:22 | 10/21/2025 17:12:34 | 10/12/2025 11:53:22 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/11/2025 01:08:54 | Major | 7114 | CELL SERVICE PROBLEM | 10/11/2025 01:08:42 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251011-00000067 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 05:53:22 | 10/12/2025 13:43:10 | 10/14/2025 11:24:46 | 10/14/2025 11:25:17 | 10/14/2025 11:25:27 | 10/14/2025 12:02:59 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000283 | PCM-20251012-00000465 | TT-20251011-00506 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/12/2025 05:53:28 | 10/17/2025 17:35:11 | 10/12/2025 11:53:28 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/11/2025 07:02:19 | Major | 7654 | CELL OPERATION DEGRADED | 10/11/2025 07:02:13 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251011-00000480 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 05:53:28 | 10/12/2025 13:43:10 | 10/17/2025 17:35:04 |  |  | 10/17/2025 17:35:11 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000302 | PCM-20251012-00000511 | TT-20251012-00538 | Reference_telecom | Region_6 | BAH0225 | BAH0225 |  |  |  | Manzoor Ahmed | 10/12/2025 06:31:59 | 10/12/2025 07:08:16 | 10/12/2025 18:31:59 | LagPortDown observed in BAH0225 towards 10.221.240.110 @ Generator_SG | 10/11/2025 18:33:30 | Minor |  | LagPortDown | 10/11/2025 18:31:51 | P2 | 2G | Baha | Generator_SG | TX NSA | BAH0225 | FLM_TE | [8 empty] | API | 10/12/2025 06:31:59 | 10/12/2025 07:08:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000320 | PCM-20251012-00000542 | TT-20251012-00553 | Telecom | Region_1 | DRN2328 | DRN2328 | Enviroment | SCECO_Failure | SCECO auto restored | Imran Ali Yousaf | 10/12/2025 06:56:59 | 10/19/2025 17:30:38 | 10/12/2025 10:56:59 | 2(2G) 1(LTE) sites down under DRN0110-P1-HUB,ARM0732-P3/DM1MBSCH01 @ Sceco | 10/12/2025 06:31:25 | Critical | 21825 | CSL Fault | 10/12/2025 06:31:22 | P3 | SRAN | dammam | Sceco | 2G_LTE SA | DRN0110-P1-HUB 2G_LTE,ARM0732-P3 2G | FLM_TE | DRN2328 | Dear FLM Team, Hub : DRN2328 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the issue | PCM-20251012-00000522 | Dear FLM Team, Hub : DRN2328 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the issue | Dear FLM Team, Hub : DRN2328 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the issue |  | sites down |  | API | 10/12/2025 06:56:59 | 10/12/2025 10:30:02 | 10/19/2025 17:30:21 |  |  | 10/19/2025 17:30:38 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000325 | PCM-20251012-00000552 | TT-20251012-00604 | Reference_telecom | Region_2 | BUR6002 | BUR6002 |  |  |  | Raise Ahmed Nisar Ahmed | 10/12/2025 07:11:13 | 10/12/2025 22:49:29 | 10/12/2025 13:11:13 | RFC Port Underpower at BUR6002-DCU1 @ Sceco | 10/11/2025 23:42:18 | Major | 29803 | RFC Port Underpower | 10/11/2025 23:42:09 | VIP | SRAN | buraidah | Sceco | 2G NSA | BUR6002 | FLM_TE | [8 empty] | API | 10/12/2025 07:11:13 | 10/12/2025 22:49:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251012000340 | PCM-20251012-00000571 | TT-20251012-00612 | Telecom | Region_4 | JED1M8619 | JED2619 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/12/2025 07:25:22 | 10/12/2025 07:25:22 | 10/12/2025 13:25:22 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M8619-P3-CA-L800 @ Sceco | 10/12/2025 07:09:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 07:10:36 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8619 | FLM_TE |  |  | PCM-20251012-00000557 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 07:25:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000344 | PCM-20251012-00000583 | TT-20251012-00439 | Reference_telecom | Region_4 | JED1M7899 | JED0899 |  |  |  | BARKAT ALI MAIN HILAL | 10/12/2025 07:31:44 | 10/12/2025 11:00:24 | 10/12/2025 13:31:44 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at JED1M7899-CA-L800-SBTS @ Generator_SG | 10/12/2025 03:37:14 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/12/2025 03:16:06 | P2 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7899 | FLM_TE |  |  | PCM-20251012-00000437 | Dear FLM, Thanks to check | Dear FLM, Thanks to check |  |  |  | API | 10/12/2025 07:31:44 | 10/12/2025 11:00:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000357 | PCM-20251012-00000598 | TT-20251012-00590 | Reference_telecom | Region_4 | JDJZ1M7870 | JDJZ0870 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/12/2025 07:35:32 | 10/16/2025 11:24:10 | 10/12/2025 19:35:32 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JDJZ1M7870-G9-NL8-L18-SBTS-P3 @ Sceco | 10/12/2025 05:01:17 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/12/2025 05:01:11 | P3 | 4G | qunfuddah | Sceco | LTE NSA | JDJZ1M7870 | FLM_TE |  |  | PCM-20251012-00000573 | Thanks to check | Thanks to check |  |  |  | API | 10/12/2025 07:35:32 | 10/12/2025 07:52:54 | 10/16/2025 11:24:04 |  |  | 10/16/2025 11:24:10 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000360 | PCM-20251012-00000601 | TT-20251012-00479 | Telecom | Region_4 | TFBH0894 | TFBH0894 | Equipment | SFP_BTS | Clean SFP | Ahmad Kamal Abdelmawla | 10/12/2025 07:35:47 | 10/14/2025 21:00:48 | 10/12/2025 13:35:47 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TFBH0894-P3 @ Sceco | 10/12/2025 05:44:46 | Major | 7607 | TRX OPERATION DEGRADED | 10/12/2025 05:44:44 | P3 | 2G | taif | Sceco | 2G_TRX NSA | TFBH0894 | FLM_TE |  |  | PCM-20251012-00000450 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 07:35:47 | 10/14/2025 20:35:31 | 10/14/2025 21:00:41 |  |  | 10/14/2025 21:00:48 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000361 | PCM-20251012-00000602 | TT-20251012-00478 | Telecom | Region_4 | TFBH0763 | TFBH0763 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 10/12/2025 07:36:02 | 10/14/2025 21:01:13 | 10/12/2025 13:36:02 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TFBH0763-P3 @ Sceco | 10/12/2025 05:44:30 | Major | 7607 | TRX OPERATION DEGRADED | 10/12/2025 05:44:13 | P3 | 2G | taif | Sceco | 2G_TRX NSA | TFBH0763 | FLM_TE |  |  | PCM-20251012-00000449 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 07:36:02 | 10/14/2025 20:35:31 | 10/14/2025 21:01:06 |  |  | 10/14/2025 21:01:13 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000389 | PCM-20251012-00000643 | TT-20251012-00689 | Telecom | Region_5 | HAJ0116 | HAJ0116 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/12/2025 08:07:36 | 10/24/2025 01:40:10 | 10/12/2025 12:07:36 | LINK B/W HAJ0158-HAJ9902 & HAJ0219-HAJ0116 NCE flapped and auto restored | 10/12/2025 08:07:05 | Critical | 1-14579 | POWER_JITTER | 10/12/2025 08:06:55 | P3 | SRAN | makkah | Sceco | DWDM NSA | HAJ0116 | FLM_TE | [5 empty] | 0-TO HAJ0219(2-A)-2-G6WDAPXF-11(LINEIN/LINEOUT(TO HAJ0219_HYB-TNG6WDAPXF(1-A02)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/12/2025 08:07:36 | 10/24/2025 01:40:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000411 | PCM-20251012-00000688 | TT-20251012-00739 | Telecom | Region_5 | HAJ0116 | HAJ0116 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/12/2025 08:34:27 | 10/24/2025 01:40:10 | 10/12/2025 14:34:27 | SPAN_LOSS_EXCEED_EOL at HAJ0116_HYB @ Sceco | 10/12/2025 08:30:31 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/12/2025 08:30:22 | P3 | SRAN | makkah | Sceco | DWDM NSA | HAJ0116 | FLM_TE | [5 empty] | 0-TO HAJ0219(2-A)-2-G6WDAPXF-11(LINEIN/LINEOUT(TO HAJ0219_HYB-TNG6WDAPXF(1-A02)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/12/2025 08:34:27 | 10/24/2025 01:40:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000412 | PCM-20251012-00000689 | TT-20251012-00738 | Telecom | Region_5 | HAJ0219 | HAJ0219 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/12/2025 08:34:27 | 10/24/2025 01:40:11 | 10/12/2025 14:34:27 | SPAN_LOSS_EXCEED_EOL at HAJ0219_HYB @ Sceco | 10/12/2025 08:30:21 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/12/2025 08:30:12 | P3 | SRAN | makkah | Sceco | DWDM NSA | HAJ0219 | FLM_TE | [5 empty] | 0-TO HAJ0116(1-A)-2-G6WDAPXF-11(LINEIN/LINEOUTLINEIN/LINEOUT(TO HAJ0116_HYB-TNG6WDAPXF(1-A02)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/12/2025 08:34:27 | 10/24/2025 01:40:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251012000426 | PCM-20251012-00000727 | TT-20251012-00786 | EM | [7 empty] | 10/12/2025 09:04:54 | 10/12/2025 09:04:54 | 10/12/2025 21:04:54 | RECTIFIER MAJOR ALARM at MUMA1M8070-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/12/2025 09:03:15 | Minor | 7103 | RECTIFIER MAJOR ALARM | 10/12/2025 08:14:12 | P3 | 4G |  | Sceco | LTE NSA | MUMA1M8070 | FLM_EM | [5 empty] | RECTIFIER MAJOR ALARM |  |  | API | 10/12/2025 09:04:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000456 | PCM-20251012-00000779 | TT-20251012-00844 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/12/2025 09:33:20 | 10/12/2025 09:36:54 | 10/12/2025 21:33:20 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/12/2025 09:25:20 | Minor | 7103 | HIGH TEMP | 10/12/2025 09:25:14 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/12/2025 09:33:20 | 10/12/2025 09:36:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251012000483 | PCM-20251012-00000819 | TT-20251010-01299 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/12/2025 10:01:20 | 10/12/2025 10:01:20 | 10/12/2025 16:01:20 | Observing Bad Package Error Rising flapping on RYD-SR-01 connected to 100GE4/0/3 IfIndex=511 If Alias=<< To ¦ Akamai Switch ¦ 1 | 10/10/2025 18:55:33 | Major | 1103100 | Crc error alarm notification | 10/10/2025 18:55:33 | P1 | BSC | riyadh | Sceco_STB | TTImpacISPNSA | RY1 | FLM_TE |  |  | PCM-20251012-00000808 | The physical action needs to be done by FLM not BO this TT should be under FLM | The physical action needs to be done by FLM not BO this TT should be under FLM |  |  |  | API | 10/12/2025 10:01:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251012000487 | PCM-20251012-00000827 | TT-20251012-00884 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/12/2025 10:07:26 | 10/19/2025 17:44:12 | 10/12/2025 16:07:26 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connector) at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/12/2025 10:02:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 10:02:47 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0539 | FLM_TE | [5 empty] | Increased BER detected on the optical connector |  |  | API | 10/12/2025 10:07:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251012000509 | PCM-20251012-00000883 | TT-20251003-01260 | Reference_telecom | Region_4 | JED0284 | JED0284 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/12/2025 10:35:40 | 10/19/2025 10:49:44 | 10/12/2025 22:35:40 | FanFailure observed in JED0284 towards 10.10.138.226 @ Sceco | 10/03/2025 05:02:20 | Minor |  | FanFailure | 10/03/2025 05:01:33 | P2 | 2G | jeddah | Sceco | TX NSA | JED0284 | FLM_TE |  |  | PCM-20251012-00000659 | Dear FLM team, approved | Dear FLM team, approved |  |  |  | API | 10/12/2025 10:35:40 | 10/19/2025 10:30:50 | 10/19/2025 10:49:39 | 10/19/2025 10:49:41 | 10/19/2025 10:49:44 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000510 | PCM-20251012-00000885 | TT-20251012-00552 | Telecom | Region_4 | KHU0652-LL-CSG-01 | KHU0652 |  |  |  | Ahmad Kamal Abdelmawla | 10/12/2025 10:35:47 | 10/14/2025 20:35:34 | 10/12/2025 16:35:47 | P0_MW_LINK DOWN AT KHU0652-LL-CSG-01 to RYMK0671-LL-CSG-01 | 10/12/2025 06:10:08 | Major | 15269 | LOS | 10/12/2025 06:10:08 | P1 | IPRAN | taif | Sceco_STB | IPRAN NSA | KHU0652-LL-CSG-01 | FLM_TE |  |  | PCM-20251012-00000630 | Kindly check as router flapped power | Kindly check as router flapped power |  |  |  | API | 10/12/2025 10:35:47 | 10/14/2025 20:35:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000525 | PCM-20251012-00000904 | TT-20251012-00962 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/12/2025 10:44:39 | 10/12/2025 13:11:21 | 10/12/2025 22:44:39 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/12/2025 07:44:22 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/12/2025 07:44:17 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/12/2025 10:44:39 | 10/12/2025 13:11:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251012000556 | PCM-20251012-00000960 | TT-20251012-01001 | EM | [7 empty] | 10/12/2025 11:10:02 | 10/13/2025 00:14:36 | 10/12/2025 17:10:02 | 1(2G/3G/LTE) sites down under MLJI0098-P3 @ Sceco | 10/12/2025 11:01:42 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/12/2025 11:01:39 | P3 | 4G |  | Sceco | LTE SA | MLJI0098-G9-U9-ML8-SBTS-P3 | FLM_TE | MLJI0098 | Results: DOWN SITE HUB MLJI0098-G9-U9-ML8-SBTS-P3 MLJI0098 Summary: Hub: MLJI0098, Down Count: 1, Down Sites: MLJI0098-G9-U9-ML8-SBTS-P3 Alarm Summary: MLJI0098 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.88.31.212:8080] [URL:http://10.88.31.212:8080/NE3S/1.0/] | sites down |  | API | 10/12/2025 11:10:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000579 | PCM-20251012-00001012 | TT-20251012-00800 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/12/2025 11:37:43 | 10/21/2025 18:14:22 | 10/12/2025 17:37:43 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/12/2025 09:09:07 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/12/2025 09:08:58 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251012-00000826 | Dear FLM team, kindly check XPD NOK for MW JED6020-JED0146 | Dear FLM team, kindly check XPD NOK for MW JED6020-JED0146 |  |  |  | API | 10/12/2025 11:37:43 | 10/20/2025 14:29:27 | 10/21/2025 18:14:16 |  |  | 10/21/2025 18:14:22 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251012000604 | PCM-20251012-00001068 | TT-20251012-01133 | Reference_telecom | Region_4 | JED2352 | JED2352 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 10/12/2025 12:20:43 | 10/14/2025 16:29:30 | 10/13/2025 00:20:43 | ReplaceableUnitProblem observed in JED2352 towards 10.1.231.99 @ Sceco | 10/12/2025 00:22:32 | Minor |  | ReplaceableUnitProblem | 10/12/2025 00:20:32 | P2 | 2G | jeddah | Sceco | TX NSA | JED2352 | FLM_TE | [8 empty] | API | 10/12/2025 12:20:43 | 10/14/2025 16:25:57 | 10/14/2025 16:29:24 | 10/14/2025 16:29:26 | 10/14/2025 16:29:30 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000607 | PCM-20251012-00001076 | TT-20251012-01140 | EM | Region_4 | JZMA1M8413 | JZMA2413 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/12/2025 12:24:53 | 10/13/2025 09:22:39 | 10/13/2025 00:24:53 | RECTIFIER MAJOR ALARM at JZMA1M8413-G9-L8-L18-SBTS-P3-CAP @ Generator_SG | 10/12/2025 12:16:29 | Minor | 7103 | RECTIFIER MAJOR ALARM | 10/12/2025 12:16:18 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8413 | FLM_EM | [5 empty] | RECTIFIER MAJOR ALARM |  |  | API | 10/12/2025 12:24:53 | 10/13/2025 09:22:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000617 | PCM-20251012-00001096 | TT-20251002-01762 | MW_HC | Region_5 | MAK0615 | MAK0615 |  |  |  | Amjad Ali Muhammad Parves | 10/12/2025 12:37:09 | 10/12/2025 21:10:22 | 10/13/2025 00:37:09 | As per BO request NOKIA MW Link MAK0615-HHR0872 need to check B2B connection for HHR0872 (10.21.73.22 & 10.21.73.18 | 10/02/2025 14:54:46 | Minor | 113388 | LOF | 10/02/2025 14:54:48 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK0615-HHR0872 | FLM_TE |  |  | PCM-20251012-00000878 | Dear FLM team, kindly check V Ubt ACM degraded on V E.band | Dear FLM team, kindly check V Ubt ACM degraded on V E.band |  |  |  | API | 10/12/2025 12:37:09 | 10/12/2025 21:10:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000618 | PCM-20251012-00001097 | TT-20251008-02124 | MW_HC | Region_4 | JED0553 | JED0553 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Abd Elrahman Suliman Mohmed Suliman | 10/12/2025 12:37:42 | 10/16/2025 10:56:16 | 10/13/2025 00:37:42 | Nokia MW HC_P0 Observing Performance Issue at JED0553-JED0685_02 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | 2G | jeddah | Sceco | TX NSA | JED0553-JED0685_02 | FLM_TE |  | Approved | PCM-20251012-00001078 | Approved | Approved |  |  |  | API | 10/12/2025 12:37:42 | 10/16/2025 10:56:16 | [5 empty] | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000638 | PCM-20251012-00001145 | TT-20251012-01220 | Reference_EM | Region_2 | RIY2442 | RIY2442 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/12/2025 13:12:54 | 10/12/2025 13:53:47 | 10/13/2025 01:12:54 | Air condition 1 failure alarm at RIY2442-P3_SRAN @ Sceco | 10/12/2025 13:02:51 | Minor | 65104 | Air condition 1 failure alarm | 10/12/2025 13:02:47 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2442 | FLM_EM | [8 empty] | API | 10/12/2025 13:12:54 | 10/12/2025 13:53:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000650 | PCM-20251012-00001181 | TT-20251012-01252 | Reference_telecom | Region_6 | BAH0022 | BAH0022 |  |  |  | SHAH KHALID | 10/12/2025 13:26:50 | 10/12/2025 16:21:44 | 10/13/2025 01:26:50 | Degrade observed in BAH0022_02 towards 10.221.240.109 @ Sceco | 10/12/2025 01:27:44 | Minor |  | Degrade | 10/12/2025 01:26:40 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0022 | FLM_TE | [8 empty] | API | 10/12/2025 13:26:50 | 10/12/2025 16:21:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000655 | PCM-20251012-00001192 | TT-20251012-01262 | Telecom | Region_4 | MKJD1M9570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/12/2025 13:31:31 | 10/12/2025 21:10:23 | 10/13/2025 01:31:31 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MKJD1M9570-P3-L800-SBTS @ Generator_DG | 10/12/2025 13:23:13 | Minor | 7115 | BASE STATION INFORMATION | 10/12/2025 13:23:08 | P2 | 4G | jeddah | Generator_DG | LTE NSA | MKJD1M9570 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/12/2025 13:31:31 | 10/12/2025 21:10:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251012000699 | PCM-20251012-00001281 | TT-20251012-01356 | EM | Region_1 | RSK2624 | RSK2624 |  |  |  | Dileesh Muringothil Devarajan | 10/12/2025 14:11:17 | 10/14/2025 16:38:11 | 10/13/2025 02:11:17 | Mains Failure at RSK2624-P3_SRAN-PC @ Sceco | 10/12/2025 14:08:00 | Minor | 65109 | Mains Failure | 10/12/2025 14:01:25 | P3 | SRAN | jubail | Sceco | 2G NSA | RSK2624 | FLM_EM | [8 empty] | API | 10/12/2025 14:11:17 | 10/12/2025 16:03:08 | 10/14/2025 16:38:02 | 10/14/2025 16:38:08 | 10/14/2025 16:38:11 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012000701 | PCM-20251012-00001290 | TT-20251012-01372 | Reference_telecom | Region_6 | BHMF0856 | BHMF0856 |  |  |  | SHAH KHALID | 10/12/2025 14:14:07 | 10/12/2025 16:21:45 | 10/13/2025 02:14:07 | Nokia Eband Observing Degrade-LAG 1 at BHMF0856-10.221.244.85 | 09/02/2025 18:23:22 | Minor |  | LOF | 09/02/2025 18:23:22 | P3 | 2G | makhwa | Sceco | TX NSA | BHMF0856-10.221.244.85 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:07 | 10/12/2025 16:21:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000702 | PCM-20251012-00001291 | TT-20251012-01373 | Reference_telecom | Region_5 | HAJ0133 | HAJ0133 |  |  |  | Muhammad Saleem Iqbal | 10/12/2025 14:14:08 | 10/12/2025 22:33:47 | 10/13/2025 02:14:08 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 2 at HAJ0133-SH3-10.10.150.229 | 09/04/2025 08:49:14 | Minor |  | LOF | 09/04/2025 08:49:14 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0133-SH3-10.10.150.229 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:08 | 10/12/2025 22:33:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000704 | PCM-20251012-00001293 | TT-20251012-01375 | Reference_telecom | Region_4 | JED0102 | JED0102 |  |  |  | BARKAT ALI MAIN HILAL | 10/12/2025 14:14:10 | 10/12/2025 14:17:18 | 10/13/2025 02:14:10 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 2,DemFail-Port 3/ at JED0102-7-10.21.75.81 | 10/07/2025 18:53:35 | Minor |  | LOF | 10/07/2025 18:53:35 | P1 | 2G | jeddah | Sceco | TX NSA | JED0102-7-10.21.75.81 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:10 | 10/12/2025 14:17:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251012000706 | PCM-20251012-00001295 | TT-20251012-01377 | Reference_telecom | Region_4 | JED0299 | JED0299 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/12/2025 14:14:13 | 10/12/2025 14:14:13 | 10/13/2025 02:14:13 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at JED0299-01-10.3.233.163 | 10/11/2025 15:48:14 | Minor |  | LOF | 10/11/2025 15:48:14 | P2 | 2G | jeddah | Sceco | TX NSA | JED0299-01-10.3.233.163 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000710 | PCM-20251012-00001299 | TT-20251012-01381 | Reference_telecom | Region_4 | MKMD0560 | MKMD0560 |  |  |  | Khizer Hayat | 10/12/2025 14:14:17 | 10/12/2025 18:03:24 | 10/13/2025 02:14:17 | Nokia Eband Observing Degrade-LAG 1,LagPortDown-Port 3/4,LagPortDown-Por at MKMD0560_02-10.10.178.73 | 09/17/2025 16:39:14 | Minor |  | LOF | 09/17/2025 16:39:14 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0560_02-10.10.178.73 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:17 | 10/12/2025 18:03:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000711 | PCM-20251012-00001300 | TT-20251012-01382 | Reference_telecom | Region_4 | JED2189 | JED2189 |  |  |  | BARKAT ALI MAIN HILAL | 10/12/2025 14:14:19 | 10/12/2025 14:17:18 | 10/13/2025 02:14:19 | Nokia Eband Observing LagPortDown-Port 4/1,Degrade-LAG 1 at JED2189_01-10.21.74.148 | 10/08/2025 01:33:55 | Minor |  | LOF | 10/08/2025 01:33:55 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2189_01-10.21.74.148 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:19 | 10/12/2025 14:17:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000712 | PCM-20251012-00001301 | TT-20251012-01383 | Reference_telecom | Region_6 | MKW2128 | MKW2128 |  |  |  | Manzoor Ahmed | 10/12/2025 14:14:20 | 10/12/2025 18:16:49 | 10/13/2025 02:14:20 | Nokia Eband Observing LagPortDown-Port 7/3,Degrade-LAG 2,DemFail-Channel at MKW2128_01-10.221.246.56 | 09/28/2025 19:23:55 | Minor |  | LOF | 09/28/2025 19:23:55 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2128_01-10.221.246.56 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:20 | 10/12/2025 18:16:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000714 | PCM-20251012-00001303 | TT-20251012-01385 | Reference_telecom | Region_4 | JED2569 | JED2569 |  |  |  | MALIK ATIF ZAMAN | 10/12/2025 14:14:21 | 10/12/2025 15:40:46 | 10/13/2025 02:14:21 | Nokia Eband Observing DemFail-Port 3/5,Degrade-LAG 1,DemXpicLOS-Port 4/5 at JED2569-10.21.75.82 | 09/17/2025 07:03:36 | Minor |  | LOF | 09/17/2025 07:03:36 | P3 | 2G | jeddah | Sceco | TX NSA | JED2569-10.21.75.82 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:21 | 10/12/2025 15:40:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000720 | PCM-20251012-00001310 | TT-20251012-01393 | Reference_telecom | Region_4 | JED0540 | JED0540 |  |  |  | Nazeer Mohammed | 10/12/2025 14:14:28 | 10/12/2025 16:09:05 | 10/13/2025 02:14:28 | Nokia Eband Observing ReplaceableUnitProblem-Card - 6,Degrade-LAG 3 at JED0540_01-10.10.179.145 | 09/16/2025 13:36:20 | Minor |  | LOF | 09/16/2025 13:36:20 | P1 | 2G | jeddah | Sceco | TX NSA | JED0540_01-10.10.179.145 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:28 | 10/12/2025 16:09:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000722 | PCM-20251012-00001312 | TT-20251012-01395 | Reference_telecom | Region_5 | MAK0211 | MAK0211 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Husain Hassan Ishag Omer | 10/12/2025 14:14:31 | 10/20/2025 14:54:45 | 10/13/2025 02:14:31 | Nokia Eband Observing ReplaceableUnitProblem-Card - 6 at MAK0211 - 07-10.21.67.194 | 10/03/2025 19:59:50 | Minor |  | LOF | 10/03/2025 19:59:50 | P1 | 2G | makkah | Sceco | TX NSA | MAK0211 - 07-10.21.67.194 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:31 | 10/20/2025 11:16:55 | 10/20/2025 11:36:11 | 10/20/2025 11:36:29 | 10/20/2025 11:36:32 | 10/20/2025 14:54:45 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000723 | PCM-20251012-00001313 | TT-20251012-01396 | Reference_telecom | Region_4 | JED2005 | JED2005 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/12/2025 14:14:32 | 10/12/2025 15:43:40 | 10/13/2025 02:14:32 | Nokia Eband Observing DemXpicLOS-Port 4/5,LossOfSignal-Port 4/5,Internal at JED2005-10.10.150.12 | 09/26/2025 16:10:15 | Minor |  | LOF | 09/26/2025 16:10:15 | P3 | 2G | jeddah | Sceco | TX NSA | JED2005-10.10.150.12 | FLM_TE | [8 empty] | API | 10/12/2025 14:14:32 | 10/12/2025 15:43:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000731 | PCM-20251012-00001327 | TT-20251012-01410 | EM | Region_6 | RTH1M7650 | RTH0650 |  |  |  | Muhammad Usman Aslam | 10/12/2025 14:22:08 | 10/14/2025 11:16:42 | 10/13/2025 02:22:08 | AIRCON 1 FAILURE at RTH1M7650-G9-U9-L8-SBTS-P2 @ Sceco | 10/12/2025 14:16:26 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 14:14:02 | P2 | 4G | raith | Sceco | LTE NSA | RTH1M7650 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 14:22:08 | 10/12/2025 16:06:36 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000751 | PCM-20251012-00001378 | TT-20251012-01467 | Telecom | Region_6 | AB1 | AB1 | Transsmission | DWDM_SW | Alarm at DWDM End Flapped and Cleared | Muhammad Mohsin Ali Ghazanfar Ali | 10/12/2025 14:40:07 | 10/13/2025 18:46:08 | 10/12/2025 20:40:07 | Observing ALU CIDs Down Flapped b/w ABHA, JIZ | 10/12/2025 14:35:45 | Major | 5000003 | Link Down | 10/12/2025 14:35:45 | P1 | BSC | abha | Sceco_STB | IPBB NSA | Observing ALU CIDs Down Flapped b/w ABHA, JIZ | FLM_TE | [5 empty] | Observing ALU CIDs Down Flapped b/w ABHA, JIZ |  |  | API | 10/12/2025 14:40:07 | 10/13/2025 01:11:03 | 10/13/2025 01:16:50 |  |  | 10/13/2025 18:46:08 |  | Muhammad Mohsin Ali Ghazanfar Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000752 | PCM-20251012-00001379 | TT-20251012-01468 | Telecom | Region_6 | JZ1-ASG-02 | JZ1 | Transsmission | MW_bad_Weather | Heavy Rain | Mohammed Sideag Mohammed Ali | 10/12/2025 14:41:25 | 10/12/2025 19:29:39 | 10/13/2025 02:41:25 | DWDM Link Down at JZ1-ASG-02 | 10/12/2025 14:35:45 | Minor | 15269 | LOS | 10/12/2025 14:35:45 | P1 | IPRAN | jizan | Sceco_STB | IPRAN NSA | JZ1-ASG-02 | FLM_TE | [8 empty] | API | 10/12/2025 14:41:25 | 10/12/2025 18:22:18 | 10/12/2025 19:29:21 |  |  | 10/12/2025 19:29:39 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000776 | PCM-20251012-00001431 | TT-20251012-01528 | MW_HC | Region_4 | JDJZ0769 | JDJZ0769 |  |  |  | Riasat Ali Allah Baksh | 10/12/2025 15:01:58 | 10/13/2025 11:53:59 | 10/13/2025 03:01:58 | As BO Requested MW Nokia Observing XPD for V2 NOK For MW Link JDJZ0769-LTH0330 | 10/12/2025 14:58:08 | Minor | 113388 | LOF | 10/12/2025 14:58:10 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0769-LTH0330 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing XPD for V2 NOK For MW Link JDJZ0769-LTH0330 |  |  | API | 10/12/2025 15:01:58 | 10/13/2025 11:53:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000788 | PCM-20251012-00001454 | TT-20251012-01560 | EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/12/2025 15:11:12 | 10/21/2025 23:22:27 | 10/12/2025 21:11:12 | Door opening alarm at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/12/2025 15:10:54 | Major | 65101 | Door opening alarm | 10/12/2025 15:07:07 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/12/2025 15:11:12 | 10/21/2025 23:22:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251012000789 | PCM-20251012-00001456 | TT-20251012-01480 | Telecom | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/12/2025 15:11:14 | 10/12/2025 15:11:14 | 10/12/2025 21:11:14 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/12/2025 14:39:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 14:39:28 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7558 | FLM_TE |  |  | PCM-20251012-00001389 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/12/2025 15:11:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000796 | PCM-20251012-00001469 | TT-20251012-01570 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/12/2025 15:16:28 | 10/14/2025 12:03:25 | 10/12/2025 21:16:28 | PT:: FLM Need to perform HC at JED6135 under R4 (BO Request) | 10/12/2025 15:16:08 | Major | 676767671 | Health Check-WO to TE FME | 10/12/2025 15:16:08 | P3 | SRAN | jeddah | Sceco | 2G_3G_LTE_5G SA | JED6135 | FLM_TE | [8 empty] | API | 10/12/2025 15:16:28 | 10/13/2025 09:43:46 | 10/14/2025 11:08:33 | 10/14/2025 11:10:26 | 10/14/2025 11:10:31 | 10/14/2025 12:03:25 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000824 | PCM-20251012-00001530 | TT-20251012-01627 | Reference_telecom | Region_1 | DMJR0138 | DMJR0138 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/12/2025 15:46:50 | 10/12/2025 18:24:32 | 10/13/2025 03:46:50 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR0138-P1-DIA_SRAN @ Sceco_STB | 10/12/2025 12:46:20 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/12/2025 12:46:17 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | DMJR0138 | FLM_TE | [8 empty] | API | 10/12/2025 15:46:50 | 10/12/2025 18:24:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251012000857 | PCM-20251012-00001595 | TT-20251012-01688 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/12/2025 16:30:19 | 10/12/2025 16:30:19 | 10/12/2025 22:30:19 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/12/2025 16:21:23 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/12/2025 16:21:19 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251012-00001593 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/12/2025 16:30:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000863 | PCM-20251012-00001602 | TT-20251012-01690 | EM | Region_4 | JZMA2413 | JZMA2413 |  |  |  | Khizer Hayat | 10/12/2025 16:34:06 | 10/12/2025 18:03:24 | 10/12/2025 22:34:06 | 1(2G/LTE) sites down under JZMA2413-P3-CAP/JZMA2413-P3-CAP @ Generator_SG | 10/12/2025 16:26:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/12/2025 16:25:57 | P3 | 2G | jeddah | Generator_SG | 2G SA | JZMA2413-P3-CAP | FLM_TE | JZMA2413 | Results: DOWN SITE HUB JZMA2413-P3-CAP JZMA2413 Summary: Hub: JZMA2413, Down Count: 1, Down Sites: JZMA2413-P3-CAP Alarm Summary: JZMA2413 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/12/2025 16:34:06 | 10/12/2025 18:03:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000894 | PCM-20251012-00001674 | TT-20251012-01756 | Telecom | Region_5 | MAK0093 | MAK0093 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | IJAZ ALI | 10/12/2025 17:13:34 | 10/23/2025 12:41:12 | 10/12/2025 23:13:34 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MAK0093-P2 @ Sceco | 10/12/2025 16:58:19 | Major | 7607 | TRX OPERATION DEGRADED | 10/12/2025 16:58:16 | P2 | 2G | makkah | Sceco | 2G_TRX NSA | MAK0093 | FLM_TE |  |  | PCM-20251012-00001655 | RSSI alarm active at site, kindly check and clear | RSSI alarm active at site, kindly check and clear |  |  |  | API | 10/12/2025 17:13:34 | 10/23/2025 12:40:44 | 10/23/2025 12:40:57 |  |  | 10/23/2025 12:41:12 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000933 | PCM-20251012-00001757 | TT-20251012-01849 | Telecom | Region_1 | DAM2M4403 | DAM2403 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/12/2025 17:42:35 | 10/12/2025 18:04:13 | 10/13/2025 05:42:35 | Monitoring Device Maintenance Link Failure at DAM2M4403-P2 @ Sceco | 10/12/2025 14:15:50 | Minor | 25600 | Monitoring Device Maintenance Link Failure | 10/12/2025 14:15:00 | P2 | 3G | dammam | Sceco | 3G NSA | DAM2M4403 | FLM_TE | [8 empty] | API | 10/12/2025 17:42:35 | 10/12/2025 18:04:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000943 | PCM-20251012-00001789 | TT-20251012-01883 | Reference_telecom | Region_6 | ABBS0158 | ABBS0158 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Fawad Khan | 10/12/2025 17:58:49 | 10/21/2025 20:25:03 | 10/13/2025 05:58:49 | NEC MW Observing LOF,RX Level,Frame ID at ABBS0158-BLH0118(10.154.163.162) | 10/10/2025 11:21:45 | Minor |  | LOF | 10/10/2025 11:21:45 | P1 | 2G | namas | Sceco_STB | TX NSA | ABBS0158-BLH0118(10.154.163.162) | FLM_TE | [8 empty] | API | 10/12/2025 17:58:49 | 10/12/2025 18:21:06 | 10/21/2025 20:24:12 |  |  | 10/21/2025 20:25:03 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000945 | PCM-20251012-00001791 | TT-20251012-01885 | Reference_telecom | Region_6 | AFJ0198 | AFJ0198 |  |  |  | Saif Muhammad | 10/12/2025 17:58:51 | 10/12/2025 20:33:08 | 10/13/2025 05:58:51 | NEC MW Observing Low BER at AFJ0198(10.89.221.218) | 10/10/2025 10:56:24 | Minor |  | LOF | 10/10/2025 10:56:24 | P2 | 2G | sulail | Generator_DG | TX NSA | AFJ0198(10.89.221.218) | FLM_TE | [8 empty] | API | 10/12/2025 17:58:51 | 10/12/2025 20:33:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000948 | PCM-20251012-00001794 | TT-20251012-01888 | Reference_telecom | Region_6 | BAH0002 | BAH0002 |  |  |  | SHAH KHALID | 10/12/2025 17:58:55 | 10/12/2025 18:00:02 | 10/13/2025 05:58:55 | NEC MW Observing MODEM Power Supply Alarm,XIF,MODEM Power Supply Alarm,MODEM Power Supply Alarm at BAH0002(10.1.174.33) | 09/03/2025 06:50:16 | Minor |  | LOF | 09/03/2025 06:50:16 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0002(10.1.174.33) | FLM_TE | [8 empty] | API | 10/12/2025 17:58:55 | 10/12/2025 18:00:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000952 | PCM-20251012-00001798 | TT-20251012-01892 | Reference_telecom | Region_1 | DAM0353 | DAM0353 |  |  |  | Tahir Mahmood Hafiz Yar | 10/12/2025 17:58:59 | 10/12/2025 18:38:03 | 10/13/2025 05:58:59 | NEC MW Observing ODU CPU / Cable Open,LOF,LOF,LOF,RX Level,RX Level,LOF,RX Level,Radio Traffic Aggregation Link,Radio Traffic Aggregation Link at DAM0353-2(10.154.5.17) | 10/09/2025 03:14:41 | Minor |  | LOF | 10/09/2025 03:14:41 | P1 | SRAN | jubail | Sceco | TX NSA | DAM0353-2(10.154.5.17) | FLM_TE | [8 empty] | API | 10/12/2025 17:58:59 | 10/12/2025 18:38:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000961 | PCM-20251012-00001807 | TT-20251012-01901 | Reference_telecom | Region_1 | JBL0465 | JBL0465 |  |  |  | Tahir Mahmood Hafiz Yar | 10/12/2025 17:59:09 | 10/12/2025 18:38:03 | 10/13/2025 05:59:09 | NEC MW Observing RX Level,LOF,Radio Traffic Aggregation Link,LOF,RX Level,LOF,XIF,RX Level,RX Level,RX Level,LOF,RX Level,LOF,RX Level,LOF,LOF,LOF,RX Level,XIF at JBL0465(10.154.14.1) | 10/19/2023 18:23:54 | Minor |  | LOF | 10/19/2023 18:23:54 | P1 | SRAN | jubail | Sceco_STB | TX NSA | JBL0465(10.154.14.1) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:09 | 10/12/2025 18:38:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000965 | PCM-20251012-00001811 | TT-20251012-01906 | Reference_telecom | Region_4 | JDJZ0776 | JDJZ0776 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/12/2025 17:59:13 | 10/13/2025 19:47:05 | 10/13/2025 05:59:13 | NEC MW Observing MODEM Power Supply Alarm,XIF at JDJZ0776-IPS-2(10.157.105.241) | 10/11/2025 12:02:41 | Minor |  | LOF | 10/11/2025 12:02:41 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0776-IPS-2(10.157.105.241) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:13 | 10/13/2025 19:47:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000966 | PCM-20251012-00001812 | TT-20251012-01907 | Reference_telecom | Region_4 | JDRS0621 | JDRS0621 |  |  |  | Khizer Hayat | 10/12/2025 17:59:15 | 10/12/2025 18:03:25 | 10/13/2025 05:59:15 | NEC MW Observing Power Supply at JDRS0621(10.154.114.13) | 10/10/2025 07:28:04 | Minor |  | LOF | 10/10/2025 07:28:04 | P2 | 2G | jeddah | Sceco | TX NSA | JDRS0621(10.154.114.13) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:15 | 10/12/2025 18:03:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000967 | PCM-20251012-00001813 | TT-20251012-01908 | Reference_telecom | Region_4 | JDRS0757 | JDRS0757 |  |  |  | Khizer Hayat | 10/12/2025 17:59:16 | 10/12/2025 18:03:25 | 10/13/2025 05:59:16 | NEC MW Observing Communication FAIL at JDRS0757(10.154.113.82) | 10/11/2025 17:51:52 | Minor |  | LOF | 10/11/2025 17:51:52 | P3 | 2G | jeddah | Generator_DG | TX NSA | JDRS0757(10.154.113.82) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:16 | 10/12/2025 18:03:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000968 | PCM-20251012-00001814 | TT-20251012-01909 | Reference_telecom | Region_6 | JEC0286 | JEC0286 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/12/2025 17:59:18 | 10/12/2025 18:59:03 | 10/13/2025 05:59:18 | NEC MW Observing Radio Traffic Aggregation Link at JEC0286(10.199.24.85) | 10/10/2025 11:11:04 | Minor |  | LOF | 10/10/2025 11:11:04 | P2 | 2G | baish | Generator_SG | TX NSA | JEC0286(10.199.24.85) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:18 | 10/12/2025 18:59:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000969 | PCM-20251012-00001815 | TT-20251012-01910 | Reference_telecom | Region_6 | JEC0287 | JEC0287 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/12/2025 17:59:18 | 10/12/2025 18:59:04 | 10/13/2025 05:59:18 | NEC MW Observing LOF,XIF,MODEM Power Supply Alarm,RX Level at JEC0287(10.199.24.89) | 10/10/2025 00:48:37 | Minor |  | LOF | 10/10/2025 00:48:37 | VIP | 2G | baish | Generator_SG | TX NSA | JEC0287(10.199.24.89) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:18 | 10/12/2025 18:59:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000971 | PCM-20251012-00001817 | TT-20251012-01912 | Reference_telecom | Region_4 | JED0848 | JED0848 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/12/2025 17:59:21 | 10/12/2025 19:41:42 | 10/13/2025 05:59:21 | NEC MW Observing LOF,RX Level,RX Level,LOF at JED0848-2(10.154.96.177) | 10/11/2025 11:49:45 | Minor |  | LOF | 10/11/2025 11:49:45 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0848-2(10.154.96.177) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:21 | 10/12/2025 19:41:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000974 | PCM-20251012-00001820 | TT-20251012-01915 | Reference_telecom | Region_4 | KMMD0637 | KMMD0637 |  |  |  | Nazeer Mohammed | 10/12/2025 17:59:24 | 10/13/2025 12:38:11 | 10/13/2025 05:59:24 | NEC MW Observing RX Level,LOF at KMMD0637(10.154.115.89) | 10/10/2025 12:25:07 | Minor |  | LOF | 10/10/2025 12:25:07 | P3 | 2G | jeddah | Sceco | TX NSA | KMMD0637(10.154.115.89) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:24 | 10/13/2025 12:38:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000975 | PCM-20251012-00001821 | TT-20251012-01916 | Reference_telecom | Region_4 | KMMD9063 | KMMD9063 |  |  |  | Nazeer Mohammed | 10/12/2025 17:59:25 | 10/13/2025 12:38:11 | 10/13/2025 05:59:25 | NEC MW Observing FAN FAIL at KMMD9063(10.154.115.73) | 10/10/2025 12:25:06 | Minor |  | LOF | 10/10/2025 12:25:06 | P3 | Repeater | jeddah | Sceco_STB | TX NSA | KMMD9063(10.154.115.73) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:25 | 10/13/2025 12:38:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000977 | PCM-20251012-00001823 | TT-20251012-01918 | Reference_telecom | Region_5 | MAK0011 | MAK0011 |  |  |  | Atif Javed Javed Hussain | 10/12/2025 17:59:27 | 10/16/2025 11:25:57 | 10/13/2025 05:59:27 | NEC MW Observing RX Level,LOF at MAK0011-1(10.99.249.121) | 10/11/2025 18:14:06 | Minor |  | LOF | 10/11/2025 18:14:06 | VIP | 2G | makkah | Sceco | TX NSA | MAK0011-1(10.99.249.121) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:27 | 10/16/2025 11:25:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000982 | PCM-20251012-00001828 | TT-20251012-01923 | Reference_telecom | Region_4 | MLJI9434 | MLJI9434 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/12/2025 17:59:33 | 10/13/2025 14:58:59 | 10/13/2025 05:59:33 | NEC MW Observing High BER at MLJI9434 to NNL9427 PLL1(10.88.224.40) | 10/11/2025 18:06:50 | Minor |  | LOF | 10/11/2025 18:06:50 | P1 | Repeater | alaith | Generator_DG | TX NSA | MLJI9434 to NNL9427 PLL1(10.88.224.40) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:33 | 10/13/2025 14:58:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012000983 | PCM-20251012-00001829 | TT-20251012-01924 | Reference_telecom | Region_4 | NSH0128 | NSH0128 | Transsmission | SFP_Transmission | Replace SFP | Mudassar Bashir Bashir Ahmad | 10/12/2025 17:59:34 | 10/18/2025 13:58:13 | 10/13/2025 05:59:34 | NEC MW Observing SFP Type Mismatch at NSH0128-2(10.88.222.70) | 10/11/2025 11:54:22 | Minor |  | LOF | 10/11/2025 11:54:22 | P2 | 2G | adam | Generator_DG | TX NSA | NSH0128-2(10.88.222.70) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:34 | 10/13/2025 19:47:06 | 10/18/2025 13:57:33 |  |  | 10/18/2025 13:58:13 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000984 | PCM-20251012-00001830 | TT-20251012-01925 | Reference_telecom | Region_4 | QUN0334 | QUN0334 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/12/2025 17:59:35 | 10/13/2025 19:47:06 | 10/13/2025 05:59:35 | NEC MW Observing ODU CPU / Cable Open,ODU Power Supply at QUN0334(10.157.105.243) | 10/11/2025 12:05:02 | Minor |  | LOF | 10/11/2025 12:05:02 | P2 | 2G | qunfuddah | Sceco | TX NSA | QUN0334(10.157.105.243) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:35 | 10/13/2025 19:47:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000986 | PCM-20251012-00001831 | TT-20251012-01927 | Reference_telecom | Region_1 | RSK2932 | RSK2932 |  |  |  | Mohamed Abdelaziz | 10/12/2025 17:59:37 | 10/12/2025 20:25:56 | 10/13/2025 05:59:37 | NEC MW Observing LOF,RX Level,Radio Traffic Aggregation Link,RX Level,LOF,LOF,LOF,RX Level,RX Level at RSK2932(10.159.106.235) | 10/09/2025 02:19:23 | Minor |  | LOF | 10/09/2025 02:19:23 | P3 | SRAN | jubail | Generator_DG | TX NSA | RSK2932(10.159.106.235) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:37 | 10/12/2025 20:25:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251008001340 | PCM-20251008-00002199 | TT-20251008-02259 | EM | Region_4 | SQR0184 | SQR0184 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/08/2025 16:39:25 | 10/09/2025 10:45:42 | 10/09/2025 04:39:25 | RECTIFIER MAINS POWER FAILURE at SQR0184-GSM-UMTS-P2-USF @ Generator_DG | 10/08/2025 16:31:00 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/08/2025 16:30:55 | P2 | 2G | alaith | Generator_DG | 2G NSA | SQR0184 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/08/2025 16:39:25 | 10/09/2025 10:45:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251008001444 | PCM-20251008-00002385 | TT-20251008-02403 | EM | Region_1 | KFKM0783 | KFKM0783 | Enviroment | Air Condition | Change Fan | Abu Sufyan Mehfooz Ali | 10/08/2025 17:53:05 | 10/22/2025 10:50:42 | 10/08/2025 21:53:05 | AMBIENT_TEMP_FLUCT at KFKM0783_OCS @ Generator_SG | 10/08/2025 17:52:05 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/08/2025 15:28:53 | P3 | SRAN | khafji | Generator_SG | DWDM NSA | KFKM0783 | FLM_EM | [5 empty] | 0-TO JBKH0113&SMN0839(2-C) |  |  | API | 10/08/2025 17:53:05 | 10/09/2025 08:09:33 | 10/22/2025 10:50:29 |  |  | 10/22/2025 10:50:42 |  | Abu Sufyan Mehfooz Ali |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251008001629 | PCM-20251008-00002595 | TT-20251008-02622 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/08/2025 18:47:45 | 10/09/2025 13:15:59 | 10/09/2025 06:47:45 | RF Unit External Power Supply Insufficient at KBR2223-P3_SRAN @ Sceco | 10/08/2025 07:04:04 | Minor | 26546 | RF Unit External Power Supply Insufficient | 10/08/2025 07:03:32 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/08/2025 18:47:45 | 10/09/2025 13:15:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008001672 | PCM-20251008-00002665 | TT-20251008-02701 | EM | Region_4 | JED0674 | JED0674 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/08/2025 19:34:20 | 10/08/2025 20:21:04 | 10/09/2025 07:34:20 | AIRCON 1 at JED0674-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/08/2025 19:26:01 | Minor | 7103 | AIRCON 1 | 10/08/2025 19:25:54 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0674 | FLM_EM | [5 empty] | AIRCON 1 |  |  | API | 10/08/2025 19:34:20 | 10/08/2025 20:21:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251008001854 | PCM-20251008-00002964 | TT-20251008-02959 | EM | Region_4 | JED0327 | JED0327 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/08/2025 23:32:30 | 10/10/2025 10:47:57 | 10/09/2025 11:32:30 | RECTIFIER MODULE FAILURE at JED0327-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/08/2025 23:24:12 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/08/2025 23:24:01 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0327 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/08/2025 23:32:30 | 10/10/2025 10:47:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000008 | PCM-20251009-00000009 | TT-20251009-00015 | EM | Region_2 | RIY2903 | RIY2903 |  |  |  | Pawan Virdi Santokh Singh | 10/09/2025 00:06:42 | 10/20/2025 12:31:55 | 10/09/2025 06:06:42 | Door opening alarm at RIY2903-P1-VIP_SRAN @ Sceco | 10/09/2025 00:06:05 | Major | 65101 | Door opening alarm | 05/14/2025 23:38:54 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2903 | FLM_EM | [8 empty] | API | 10/09/2025 00:06:42 | 10/10/2025 00:55:41 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000011 | PCM-20251009-00000015 | TT-20251009-00019 | EM | Region_2 | RIY2903 | RIY2903 |  |  |  | Pawan Virdi Santokh Singh | 10/09/2025 00:08:07 | 10/20/2025 12:31:56 | 10/09/2025 06:08:07 | Low battery voltage at RIY2903-P1-VIP_SRAN @ Sceco | 10/09/2025 00:06:05 | Major | 65110 | Low battery voltage | 05/14/2025 23:43:14 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2903 | FLM_EM | [8 empty] | API | 10/09/2025 00:08:07 | 10/10/2025 00:55:43 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000012 | PCM-20251009-00000016 | TT-20251009-00020 | EM | Region_2 | RIY0274 | RIY0274 |  |  |  | RANJEET KUMAR YADAV | 10/09/2025 00:08:09 | 10/20/2025 12:31:54 | 10/09/2025 06:08:09 | Mains Failure at RIY0274-P1-VIP_SRAN @ Generator_SG | 10/09/2025 00:05:53 | Major | 65109 | Mains Failure | 06/16/2025 20:54:48 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY0274 | FLM_EM | [8 empty] | API | 10/09/2025 00:08:09 | 10/09/2025 18:21:16 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000018 | PCM-20251009-00000025 | TT-20251009-00021 | Telecom | Region_2 | RIY2903 | RIY2903 |  |  |  | Pawan Virdi Santokh Singh | 10/09/2025 00:15:21 | 10/20/2025 12:31:57 | 10/09/2025 12:15:21 | BBU DC Output Out of Range at RIY2903-P1-VIP_SRAN @ Sceco | 10/09/2025 00:06:05 | Minor | 26112 | BBU DC Output Out of Range | 05/14/2025 23:42:25 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2903 | FLM_EM |  |  | PCM-20251009-00000014 | power issue at site | power issue at site |  |  |  | API | 10/09/2025 00:15:21 | 10/10/2025 00:55:45 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000019 | PCM-20251009-00000026 | TT-20251009-00018 | Telecom | Region_2 | RIY2903 | RIY2903 |  |  |  | Pawan Virdi Santokh Singh | 10/09/2025 00:15:46 | 10/20/2025 12:31:58 | 10/09/2025 12:15:46 | NR DU Cell TRP Unavailable at RIY2903-P1-VIP_SRAN @ Sceco | 10/09/2025 00:06:05 | Minor | 29870 | NR DU Cell TRP Unavailable | 05/14/2025 23:42:30 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2903 | FLM_EM |  |  | PCM-20251009-00000013 | power issue at site | power issue at site |  |  |  | API | 10/09/2025 00:15:46 | 10/10/2025 00:55:47 | [6 empty] | Building Authority |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000077 | PCM-20251009-00000112 | TT-20251009-00122 | EM | Region_4 | JED2042 | JED2042 |  |  |  | Abdelhalim Hafez Fahmi Abdelaziz | 10/09/2025 01:18:21 | 10/09/2025 01:57:28 | 10/09/2025 07:18:21 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8042-P1-VIP-CA-L900-L800-SBTS @ Generator_SG | 10/09/2025 01:09:56 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/09/2025 01:09:44 | VIP | 4G | jeddah | Generator_SG | LTE NSA | JED1M8042 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/09/2025 01:18:21 | 10/09/2025 01:57:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000153 | PCM-20251009-00000251 | TT-20251009-00290 | Reference_EM | Region_1 | ARM0885 | ARM0885 |  |  |  | Dileesh Muringothil Devarajan | 10/09/2025 03:23:56 | 10/09/2025 07:27:31 | 10/09/2025 15:23:56 | Air condition 1 failure alarm at ARM0885-P3_SRAN @ Sceco | 10/09/2025 03:13:25 | Minor | 65104 | Air condition 1 failure alarm | 10/09/2025 03:13:21 | P3 | SRAN | khafji | Sceco | 2G NSA | ARM0885 | FLM_EM | [8 empty] | API | 10/09/2025 03:23:56 | 10/09/2025 07:27:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000184 | PCM-20251009-00000315 | TT-20251009-00382 | EM | Region_4 | SHB0670 | SHB0670 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/09/2025 04:46:01 | 10/09/2025 06:33:19 | 10/09/2025 16:46:01 | RECTIFIER MAINS POWER FAILURE at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/09/2025 04:37:40 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/09/2025 04:37:22 | P3 | 4G | qunfuddah | Sceco | LTE NSA | SHB1M7670 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/09/2025 04:46:01 | 10/09/2025 06:33:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000203 | PCM-20251009-00000340 | TT-20251009-00411 | EM | Region_4 | FYD0320 | FYD0320 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/09/2025 05:34:41 | 10/15/2025 07:06:13 | 10/09/2025 17:34:41 | AIRCON 1 FAILURE at FYD0320-GSM-P3 @ Sceco | 10/09/2025 05:26:24 | Minor | 7103 | AIRCON 1 FAILURE | 10/09/2025 05:26:17 | P3 | 2G | jeddah | Sceco | 2G NSA | FYD0320 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/09/2025 05:34:41 | 10/15/2025 07:06:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000255 | PCM-20251009-00000419 | TT-20251009-00495 | EM | Region_4 | JED0090 | JED0090 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/09/2025 06:50:36 | 10/10/2025 10:47:57 | 10/09/2025 12:50:36 | AIRCON 2 FAILURE at JED1M7090-P1-VIP-SHOP-CA-L900-L800-SBTS @ Sceco | 10/09/2025 06:41:59 | Major | 7103 | AIRCON 2 FAILURE | 10/09/2025 06:41:53 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M7090 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/09/2025 06:50:36 | 10/10/2025 10:47:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009000266 | PCM-20251009-00000437 | TT-20251009-00516 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/09/2025 07:15:55 | 10/09/2025 12:22:11 | 10/09/2025 19:15:55 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/09/2025 07:09:14 | Minor | 40564 | Genset Fault | 10/09/2025 07:09:14 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/09/2025 07:15:55 | 10/09/2025 11:42:24 | 10/09/2025 12:22:00 |  |  | 10/09/2025 12:22:11 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251009000305 | PCM-20251009-00000503 | TT-20251009-00611 | EM | Region_1 | SMN0806 | SMN0806 |  |  |  | Rahman Ullah Said Halim | 10/09/2025 08:03:55 | 10/09/2025 11:03:09 | 10/09/2025 20:03:55 | Genset not in auto mode at SMN0806-P2_SRAN @ Generator_DG | 10/09/2025 08:01:51 | Minor | 65113 | Genset not in auto mode | 10/09/2025 07:42:30 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/09/2025 08:03:55 | 10/09/2025 11:03:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251009000313 | PCM-20251009-00000514 | TT-20251009-00625 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/09/2025 08:12:45 | 10/11/2025 12:17:53 | 10/09/2025 20:12:45 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/09/2025 08:04:13 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/09/2025 08:04:10 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/09/2025 08:12:45 | 10/11/2025 12:17:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000322 | PCM-20251009-00000535 | TT-20251009-00648 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/09/2025 08:24:05 | 10/09/2025 09:30:38 | 10/09/2025 14:24:05 | high temprature 32 at DAM2066-P1-HUB_SRAN @ Sceco | 10/09/2025 08:09:21 | Major | 65102 | high temprature 32 | 10/09/2025 08:13:37 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/09/2025 08:24:05 | 10/09/2025 09:30:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000324 | PCM-20251009-00000539 | TT-20251009-00652 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/09/2025 08:25:05 | 10/09/2025 11:35:33 | 10/09/2025 20:25:05 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/09/2025 08:14:36 | Minor | 65102 | high temprature 32 | 10/09/2025 08:14:33 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/09/2025 08:25:05 | 10/09/2025 11:35:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251009000407 | PCM-20251009-00000653 | TT-20251009-00725 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/09/2025 09:05:26 | 10/11/2025 11:01:33 | 10/09/2025 21:05:26 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/09/2025 08:58:54 | Minor | 40564 | Genset Fault | 10/09/2025 08:58:54 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/09/2025 09:05:26 | 10/10/2025 03:46:18 | 10/11/2025 11:01:27 |  |  | 10/11/2025 11:01:33 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009000517 | PCM-20251009-00000815 | TT-20251009-00879 | EM | Region_1 | HFR2491 | HFR2491 | Enviroment | SCECO_Failure | SCECO auto restored | Reda Mohammed Mohamed Hassanein | 10/09/2025 10:29:35 | 10/17/2025 13:59:29 | 10/09/2025 22:29:35 | Air condition 2 failure alarm at HFR2491-P2_SRAN @ Sceco | 10/09/2025 10:27:30 | Minor | 65105 | Air condition 2 failure alarm | 10/09/2025 10:07:46 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR2491 | FLM_EM | [8 empty] | API | 10/09/2025 10:29:35 | 10/15/2025 13:15:09 | 10/17/2025 13:59:21 |  |  | 10/17/2025 13:59:29 |  | Reda Mohammed Mohamed Hassanein | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009000521 | PCM-20251009-00000820 | TT-20251009-00888 | EM | Region_4 | YLM0789 | YLM0789 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Karim Hamdy Mohamed Elashry | 10/09/2025 10:33:45 | 10/09/2025 15:25:58 | 10/09/2025 22:33:45 | GENERATOR LOW FUEL at YLM0789-GSM-UMTS-P3 @ Generator_SG | 10/09/2025 10:25:19 | Minor | 7103 | GENERATOR LOW FUEL | 10/09/2025 10:25:13 | P3 | 2G | alaith | Generator_SG | 2G NSA | YLM0789 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/09/2025 10:33:45 | 10/09/2025 15:25:33 | 10/09/2025 15:25:47 |  |  | 10/09/2025 15:25:58 |  | Karim Hamdy Mohamed Elashry |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000635 | PCM-20251009-00000973 | TT-20251009-01038 | EM | Region_1 | DAM0550 | DAM0550 |  |  |  | Ansar Abbas Muhammad Iqbal | 10/09/2025 11:44:31 | 10/10/2025 19:25:17 | 10/09/2025 23:44:31 | Door opening alarm at DAM0550-P2_SRAN @ Generator_SG | 10/09/2025 11:44:03 | Minor | 65101 | Door opening alarm | 10/09/2025 11:43:59 | P2 | SRAN | dammam | Generator_SG | 2G NSA | DAM0550 | FLM_EM | [8 empty] | API | 10/09/2025 11:44:31 | 10/10/2025 19:25:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000644 | PCM-20251009-00000987 | TT-20251009-01058 | EM | Region_4 | JED0707 | JED0707 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/09/2025 11:54:21 | 10/09/2025 18:05:44 | 10/09/2025 23:54:21 | RECTIFIER MODULE FAILURE at JED0707-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/09/2025 11:47:49 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/09/2025 11:45:50 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0707 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/09/2025 11:54:21 | 10/09/2025 18:05:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000697 | PCM-20251009-00001069 | TT-20251009-01139 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/09/2025 12:29:55 | 10/09/2025 13:18:28 | 10/10/2025 00:29:55 | high temprature 40 at KBR0166-P3_SRAN @ Sceco | 10/09/2025 12:19:23 | Minor | 65103 | high temprature 40 | 10/09/2025 12:19:19 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/09/2025 12:29:55 | 10/09/2025 13:18:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009000703 | PCM-20251009-00001082 | TT-20251009-01151 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/09/2025 12:36:40 | 10/09/2025 13:07:05 | 10/10/2025 00:36:40 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/09/2025 12:26:04 | Minor | 65102 | High temperature 32C alarm | 10/09/2025 12:26:00 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/09/2025 12:36:40 | 10/09/2025 13:07:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251009000712 | PCM-20251009-00001098 | TT-20251009-00878 | Reference_telecom | Region_6 | MHL0138 | MHL0138 |  |  |  | Zia Ur Rahamn | 10/09/2025 12:41:51 | 10/19/2025 10:01:56 | 10/09/2025 18:41:51 | 1 (3G) site down at MHL1M4138-P3 Under MHL1M4138-P3(REF::TT-20250927-01025) @ Sceco | 09/27/2025 23:42:14 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 09/27/2025 23:41:35 | P3 | 3G | mohail | Sceco | 3G SA | MHL1M4138 | FLM_EM |  | Results: DOWN SITE HUB MHL1M4138 MHL1M4138 Summary: Hub: MHL1M4138, Down Count: 1, Down Sites: MHL1M4138 Alarm Summary: MHL1M4138 No Active Alarm on HUB | PCM-20251009-00000819 | power issue at site | power issue at site |  | site down |  | API | 10/09/2025 12:41:51 | 10/09/2025 17:08:57 | 10/19/2025 10:01:48 | 10/19/2025 10:01:52 | 10/19/2025 10:01:56 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009000847 | PCM-20251009-00001300 | TT-20251009-01369 | EM | Region_6 | KHS0949 | KHS0949 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ezat Mohammed | 10/09/2025 14:14:50 | 10/12/2025 18:27:16 | 10/10/2025 02:14:50 | LOW FUEL at KHS1M7949-G9-L9-SBTS-P2 @ Generator_SG | 10/09/2025 14:06:12 | Minor | 7103 | LOW FUEL | 10/09/2025 14:06:01 | P2 | 4G | khamis mushyet | Generator_SG | LTE NSA | KHS1M7949 | FLM_EM | [5 empty] | LOW FUEL |  |  | API | 10/09/2025 14:14:50 | 10/11/2025 15:56:06 | 10/12/2025 18:27:07 |  |  | 10/12/2025 18:27:16 |  | Ezat Mohammed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009000854 | PCM-20251009-00001310 | TT-20251009-01383 | Reference_EM | Region_1 | ARR0919 | ARR0919 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Ismail Salah Ismail Elbery | 10/09/2025 14:19:02 | 10/11/2025 11:01:53 | 10/09/2025 20:19:02 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/09/2025 14:08:28 | Major | 65110 | Low battery voltage | 10/09/2025 14:08:23 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/09/2025 14:19:02 | 10/10/2025 03:46:19 | 10/11/2025 11:01:47 |  |  | 10/11/2025 11:01:53 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251009000944 | PCM-20251009-00001439 | TT-20251009-01525 | EM | Region_6 | MHL0133 | MHL0133 |  |  |  | Zia Ur Rahamn | 10/09/2025 15:22:01 | 10/09/2025 17:09:00 | 10/10/2025 03:22:01 | AIRCON 2 FAILURE at MHL0133-GSM-P3 @ Sceco | 10/09/2025 15:13:41 | Minor | 7103 | AIRCON 2 FAILURE | 10/09/2025 15:13:30 | P3 | 2G | mohail | Sceco | 2G NSA | MHL0133 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/09/2025 15:22:01 | 10/09/2025 17:09:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009001001 | PCM-20251009-00001530 | TT-20251009-01606 | EM | Region_4 | NNL0176 | NNL0176 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/09/2025 15:57:40 | 10/11/2025 12:17:53 | 10/10/2025 03:57:40 | RECTIFIER MODULE FAILURE at NNL0176-GSM-UMTS-P3 @ Generator_SG | 10/09/2025 15:49:20 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/09/2025 15:49:10 | P3 | 2G | qunfuddah | Generator_SG | 2G NSA | NNL0176 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/09/2025 15:57:40 | 10/11/2025 12:17:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251009001081 | PCM-20251009-00001663 | TT-20251009-01741 | EM | Region_4 | JED2680 | JED2680 |  |  |  | Sajid Nazir Muhammad Nazir | 10/09/2025 16:53:26 | 10/09/2025 18:22:34 | 10/10/2025 04:53:26 | AIRCON 1 FAILURE at JED1M8680-CA-L800-P3 @ Sceco | 10/09/2025 16:45:11 | Minor | 7103 | AIRCON 1 FAILURE | 10/09/2025 16:45:06 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8680 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/09/2025 16:53:26 | 10/09/2025 18:22:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251009001257 | PCM-20251009-00001984 | TT-20251009-02019 | EM | Region_4 | JED0647 | JED0647 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/09/2025 19:44:25 | 10/09/2025 19:44:25 | 10/10/2025 07:44:25 | COMMERCIAL POWER FAILURE at JED0647-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/09/2025 19:35:49 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/09/2025 19:35:41 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0647 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/09/2025 19:44:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009001267 | PCM-20251009-00002010 | TT-20251009-02043 | EM | Region_1 | SAK2903 | SAK2903 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mohammed Kholi | 10/09/2025 20:01:30 | 10/10/2025 05:42:11 | 10/10/2025 08:01:30 | NETECO: Default Differentiated Setting Restored at SAK2903 @ Generator_SG | 10/09/2025 17:41:47 | Minor | 63000 | Default Differentiated Setting Restored | 10/09/2025 17:41:47 | P3 | SRAN | sakaka | Generator_SG | 2G NSA | SAK2903 | FLM_EM | [8 empty] | API | 10/09/2025 20:01:30 | 10/10/2025 05:41:19 | 10/10/2025 05:42:03 |  |  | 10/10/2025 05:42:11 |  | Mohammed Kholi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251009001384 | PCM-20251009-00002223 | TT-20251009-01870 | Reference_telecom | Region_2 | RYQ0965 | RYQ0965 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/09/2025 22:19:56 | 10/19/2025 07:44:12 | 10/10/2025 10:19:56 | External Clock Reference Problem at RYQ0988-P2_SRAN @ Sceco | 10/09/2025 15:07:49 | Minor | 26262 | External Clock Reference Problem | 10/09/2025 15:04:25 | P2 | SRAN | majma | Generator_SG | 2G NSA | RYQ0988 | FLM_EM |  | Dear Team, Hub:- RYQ0965 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | PCM-20251009-00002214 | Dear Team, Hub:- RYQ0965 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM | Dear Team, Hub:- RYQ0965 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. Kindly update TT under EM FLM |  |  |  | API | 10/09/2025 22:19:56 | 10/10/2025 09:13:04 | 10/19/2025 07:44:05 |  |  | 10/19/2025 07:44:12 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251010000019 | PCM-20251010-00000034 | TT-20251010-00036 | EM | Region_1 | DMH0096 | DMH0096 |  |  |  | Dileesh Muringothil Devarajan | 10/10/2025 00:36:50 | 10/18/2025 15:03:06 | 10/10/2025 06:36:50 | Door opening alarm at DMH0096-P1-HUB_SRAN @ Sceco_STB | 10/10/2025 00:36:17 | Major | 65101 | Door opening alarm | 10/10/2025 00:36:13 | P1 | SRAN | jubail | Sceco_STB | 2G NSA | DMH0096 | FLM_EM | [8 empty] | API | 10/10/2025 00:36:50 | 10/18/2025 14:51:44 | 10/18/2025 15:03:01 | 10/18/2025 15:03:04 | 10/18/2025 15:03:06 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251010000111 | PCM-20251010-00000238 | TT-20251010-00276 | EM | Region_1 | SAK2908 | SAK2908 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mohammed Kholi | 10/10/2025 04:32:26 | 10/10/2025 06:58:31 | 10/10/2025 16:32:26 | Door opening alarm at SAK2908-P3-USF_SRAN @ Generator_SG | 10/10/2025 04:31:45 | Minor | 65101 | Door opening alarm | 10/10/2025 04:31:41 | P3 | SRAN | sakaka | Generator_SG | 2G NSA | SAK2908 | FLM_EM | [8 empty] | API | 10/10/2025 04:32:26 | 10/10/2025 05:41:19 | 10/10/2025 06:53:46 | 10/10/2025 06:54:05 | 10/10/2025 06:54:08 | 10/10/2025 06:58:31 |  | Mohammed Kholi |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251010000173 | PCM-20251010-00000336 | TT-20251010-00407 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/10/2025 07:03:45 | 10/11/2025 12:17:54 | 10/10/2025 19:03:45 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/10/2025 06:55:13 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/10/2025 06:55:09 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/10/2025 07:03:45 | 10/11/2025 12:17:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000185 | PCM-20251010-00000350 | TT-20251010-00414 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/10/2025 07:21:56 | 10/10/2025 08:14:36 | 10/10/2025 19:21:56 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/10/2025 07:11:07 | Minor | 65102 | high temprature 32 | 10/10/2025 07:11:05 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/10/2025 07:21:56 | 10/10/2025 08:14:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000227 | PCM-20251010-00000412 | TT-20251010-00485 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/10/2025 08:27:00 | 10/11/2025 19:16:12 | 10/10/2025 20:27:00 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/10/2025 08:16:21 | Minor | 65102 | high temprature 32 | 10/10/2025 08:16:17 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/10/2025 08:27:00 | 10/11/2025 19:16:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251010000235 | PCM-20251010-00000424 | TT-20251010-00500 | EM | Region_4 | TUR0693 | TUR0693 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Afzal Hussain Anwar Ul Haq | 10/10/2025 08:34:45 | 10/24/2025 02:57:38 | 10/10/2025 20:34:45 | RECTIFIER MAINS POWER FAILURE at TUR0693-GSM-P2 @ Sceco | 10/10/2025 08:26:13 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/10/2025 08:26:00 | P2 | 2G | taif | Sceco | 2G NSA | TUR0693 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/10/2025 08:34:45 | 10/14/2025 09:01:52 | 10/24/2025 02:57:26 |  |  | 10/24/2025 02:57:38 |  | Afzal Hussain Anwar Ul Haq |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000288 | PCM-20251010-00000500 | TT-20251010-00574 | EM | Region_6 | WDS9507 | WDS9507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Aslam Abdul Salam | 10/10/2025 09:31:35 | 10/15/2025 14:16:42 | 10/10/2025 13:31:35 | NEC Eband observing Rectifier Fault alarm at site WDS9507 | 10/10/2025 09:23:50 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 10/10/2025 09:23:50 | P1 | Repeater | wadi dawasar | Generator_SG | TX NSA | UKZ9444 | FLM_EM | [5 empty] | NEC Eband observing Rectifier Fault alarm at site WDS9507 |  |  | API | 10/10/2025 09:31:35 | 10/15/2025 14:16:42 | [5 empty] | Muhammad Aslam Abdul Salam | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251010000326 | PCM-20251010-00000553 | TT-20251010-00628 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/10/2025 10:28:55 | 10/10/2025 13:22:49 | 10/10/2025 16:28:55 | high temprature 40 at DAM2066-P1-HUB_SRAN @ Sceco | 10/10/2025 10:18:37 | Major | 65103 | high temprature 40 | 10/10/2025 10:18:31 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/10/2025 10:28:55 | 10/10/2025 13:22:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000418 | PCM-20251010-00000703 | TT-20251010-00754 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/10/2025 12:28:15 | 10/11/2025 02:42:09 | 10/11/2025 00:28:15 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/10/2025 12:19:44 | Minor | 7103 | AIRCON 1 FAILURE | 10/10/2025 12:19:36 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/10/2025 12:28:15 | 10/11/2025 02:42:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000439 | PCM-20251010-00000738 | TT-20251010-00794 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/10/2025 12:57:40 | 10/11/2025 13:50:27 | 10/11/2025 00:57:40 | high temprature 40 at KBR0166-P3_SRAN @ Sceco | 10/10/2025 12:47:02 | Minor | 65103 | high temprature 40 | 10/10/2025 12:46:57 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/10/2025 12:57:40 | 10/11/2025 13:50:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000451 | PCM-20251010-00000755 | TT-20251010-00817 | EM | Region_1 | KBR0608 | KBR0608 |  |  |  | Abdul Malik Shaik | 10/10/2025 13:16:16 | 10/11/2025 13:50:28 | 10/11/2025 01:16:16 | NETECO: DIN4 Alarm at KBR0608 @ Sceco | 10/10/2025 13:09:48 | Minor | 21942 | DIN4 Alarm | 10/10/2025 13:09:48 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0608 | FLM_EM | [8 empty] | API | 10/10/2025 13:16:16 | 10/11/2025 13:50:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000478 | PCM-20251010-00000791 | TT-20251010-00871 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/10/2025 13:52:25 | 10/10/2025 17:38:51 | 10/11/2025 01:52:25 | High temperature 40C alarm at ARM2M1871-P3 @ Sceco | 10/10/2025 13:42:01 | Minor | 65103 | High temperature 40C alarm | 10/10/2025 13:41:57 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/10/2025 13:52:25 | 10/10/2025 17:38:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251010000536 | PCM-20251010-00000898 | TT-20251010-00983 | Reference_EM | Region_1 | ARR0919 | ARR0919 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/10/2025 15:18:40 | 10/11/2025 11:02:02 | 10/10/2025 21:18:40 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/10/2025 15:08:03 | Major | 65110 | Low battery voltage | 10/10/2025 15:07:59 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/10/2025 15:18:40 | 10/11/2025 11:00:35 | 10/11/2025 11:01:57 |  |  | 10/11/2025 11:02:02 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251010000553 | PCM-20251010-00000920 | TT-20251010-01010 | EM | Region_4 | JED2352 | JED2352 |  |  |  | Amer Attallah Awadallah | 10/10/2025 15:40:56 | 10/10/2025 21:53:41 | 10/11/2025 03:40:56 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8352-CA-L900-L800-SBTS @ Sceco | 10/10/2025 15:32:25 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/10/2025 15:32:15 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M8352 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/10/2025 15:40:56 | 10/10/2025 21:53:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000556 | PCM-20251010-00000924 | TT-20251008-02035 | MW_HC | Region_6 | ABH0049 | ABH0049 |  |  |  | Khalid Frahan Almesetef | 10/10/2025 15:46:41 | 10/11/2025 20:13:21 | 10/11/2025 03:46:41 | Nokia MW HC_P0 Observing Performance Issue at ABH0049_01-ABH0161_10 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | abha | Sceco | TX NSA | ABH0049_01-ABH0161_10 | FLM_EM |  |  | PCM-20251010-00000807 | Dear FLM , Thanks to share below points in order to close ant TT , PCM 1- HC Duration : Record start & end time of HC 2- Clearance evidence duration : Record start & end time of clearance verification 3- Clearance snapshot : Provide 1h snapshot of stable link performance 4- Submit summary of corrective actions & RCA | Dear FLM , Thanks to share below points in order to close ant TT , PCM 1- HC Duration : Record start & end time of HC 2- Clearance evidence duration : Record start & end time of clearance verification 3- Clearance snapshot : Provide 1h snapshot of stable link performance 4- Submit summary of corrective actions & RCA |  |  |  | API | 10/10/2025 15:46:41 | 10/11/2025 20:13:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251010000587 | PCM-20251010-00000991 | TT-20251010-01071 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/10/2025 16:20:41 | 10/11/2025 14:38:43 | 10/11/2025 04:20:41 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/10/2025 16:14:12 | Minor | 40564 | Genset Fault | 10/10/2025 16:14:12 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/10/2025 16:20:41 | 10/11/2025 00:34:49 | 10/11/2025 14:38:29 |  |  | 10/11/2025 14:38:43 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251010000625 | PCM-20251010-00001062 | TT-20251010-01157 | EM | Region_4 | YLM0789 | YLM0789 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Karim Hamdy Mohamed Elashry | 10/10/2025 17:12:21 | 10/12/2025 12:21:43 | 10/11/2025 05:12:21 | GENERATOR LOW FUEL at YLM0789-GSM-UMTS-P3 @ Generator_SG | 10/10/2025 17:03:40 | Minor | 7103 | GENERATOR LOW FUEL | 10/10/2025 17:03:32 | P3 | 2G | alaith | Generator_SG | 2G NSA | YLM0789 | FLM_EM | [5 empty] | GENERATOR LOW FUEL |  |  | API | 10/10/2025 17:12:21 | 10/12/2025 12:20:27 | 10/12/2025 12:21:28 |  |  | 10/12/2025 12:21:43 |  | Karim Hamdy Mohamed Elashry |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251010000628 | PCM-20251010-00001065 | TT-20251010-01163 | EM | Region_4 | JED0647 | JED0647 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/10/2025 17:14:25 | 10/10/2025 17:14:25 | 10/11/2025 05:14:25 | COMMERCIAL POWER FAILURE at JED0647-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/10/2025 17:05:50 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/10/2025 17:05:43 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0647 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/10/2025 17:14:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251010000664 | PCM-20251010-00001130 | TT-20251010-01246 | EM | Region_4 | HHR0842 | HHR0842 |  |  |  | Aly Ahmed Aly Sawy | 10/10/2025 18:11:16 | 10/13/2025 00:22:01 | 10/11/2025 00:11:16 | GENERATOR1 + GENERATOR2 2 FAILURE at HHR0842-GSM-UMTS-P1-VIP-HHR @ Generator_DG | 10/10/2025 18:03:02 | Major | 7103 | GENERATOR1 + GENERATOR2 2 FAILURE | 10/10/2025 18:02:52 | VIP | 2G | jeddah | Generator_DG | 2G NSA | HHR0842 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 FAILURE |  |  | API | 10/10/2025 18:11:16 | 10/13/2025 00:22:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251010000680 | PCM-20251010-00001157 | TT-20251010-01286 | EM | Region_6 | ABH0233 | ABH0233 |  |  |  | Khalid Frahan Almesetef | 10/10/2025 18:41:11 | 10/11/2025 20:13:23 | 10/11/2025 06:41:11 | SHELTER DOOR OPEN at ABH0233-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/10/2025 18:40:22 | Minor | 7103 | SHELTER DOOR OPEN | 10/10/2025 18:40:16 | P3 | 2G | abha | Sceco | 2G NSA | ABH0233 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/10/2025 18:41:11 | 10/11/2025 20:13:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251010000898 | PCM-20251010-00001534 | TT-20251010-01622 | EM | Region_6 | BAH0018 | BAH0018 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 10/10/2025 23:51:40 | 10/11/2025 10:00:58 | 10/11/2025 11:51:40 | AIRCON 1 FAILURE at BAH1M7018-G9-L18-L21-SBTS-P3 @ Sceco | 10/10/2025 23:43:17 | Minor | 7103 | AIRCON 1 FAILURE | 10/10/2025 23:43:07 | P3 | 4G | Albaha | Sceco | LTE NSA | BAH1M7018 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/10/2025 23:51:40 | 10/11/2025 06:26:30 | 10/11/2025 10:00:48 |  |  | 10/11/2025 10:00:58 |  | Arif Ullah Shah |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011000066 | PCM-20251011-00000118 | TT-20251011-00119 | EM | Region_4 | JED0001 | JED0001 | Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator | Hamza Ahmed Aly Sawy | 10/11/2025 02:06:06 | 10/11/2025 03:45:43 | 10/11/2025 06:06:06 | NE_NOT_LOGIN at JED0001-OCS1 @ Sceco | 10/11/2025 02:03:50 | Critical | 0-2 | NE_NOT_LOGIN | 10/11/2025 02:03:48 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0001 | FLM_EM | [5 empty] | NE JED0001-OCS1 not login |  |  | API | 10/11/2025 02:06:06 | 10/11/2025 02:52:06 | 10/11/2025 02:52:11 | 10/11/2025 02:52:14 | 10/11/2025 03:09:21 | 10/11/2025 03:45:43 |  | Hamza Ahmed Aly Sawy |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251011000104 | PCM-20251011-00000210 | TT-20251011-00215 | EM | Region_4 | YLM2369 | YLM2369 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Karim Hamdy Mohamed Elashry | 10/11/2025 02:57:41 | 10/12/2025 12:21:13 | 10/11/2025 08:57:41 | RECTIFIER MODULE FAILURE at YLM1M8369-L800-P1-SBTS @ Sceco | 10/11/2025 02:49:29 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/11/2025 02:49:19 | P1 | 4G | alaith | Sceco | LTE NSA | YLM1M8369 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/11/2025 02:57:41 | 10/12/2025 12:20:28 | 10/12/2025 12:21:03 |  |  | 10/12/2025 12:21:13 |  | Karim Hamdy Mohamed Elashry |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000140 | PCM-20251011-00000272 | TT-20251011-00274 | EM | Region_4 | JED0674 | JED0674 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/11/2025 03:29:41 | 10/11/2025 13:29:30 | 10/11/2025 15:29:41 | SHELTER DOOR OPEN at JED0674-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/11/2025 03:29:20 | Minor | 7103 | SHELTER DOOR OPEN | 10/11/2025 03:28:40 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0674 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/11/2025 03:29:41 | 10/11/2025 13:29:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011000145 | PCM-20251011-00000286 | TT-20251011-00285 | EM | Region_1 | ARR9807 | ARR9807 | Equipment | FAN Cleaning | Clean FAN | Ismail Salah Ismail Elbery | 10/11/2025 03:35:21 | 10/11/2025 11:02:12 | 10/11/2025 15:35:21 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/11/2025 03:28:57 | Minor | 40564 | Genset Fault | 10/11/2025 03:28:57 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/11/2025 03:35:21 | 10/11/2025 11:00:35 | 10/11/2025 11:02:06 |  |  | 10/11/2025 11:02:12 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000149 | PCM-20251011-00000292 | TT-20251011-00288 | EM | Region_4 | JED0674 | JED0674 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/11/2025 03:37:26 | 10/11/2025 13:29:30 | 10/11/2025 15:37:26 | AIRCON 2 at JED0674-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/11/2025 03:29:20 | Minor | 7103 | AIRCON 2 | 10/11/2025 03:28:40 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0674 | FLM_EM | [5 empty] | AIRCON 2 |  |  | API | 10/11/2025 03:37:26 | 10/11/2025 13:29:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011000162 | PCM-20251011-00000322 | TT-20251011-00306 | Reference_EM | Region_1 | YBR0603 | YBR0603 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Montasir Awadalla Abdalla Bala | 10/11/2025 03:55:31 | 10/11/2025 06:00:19 | 10/11/2025 15:55:31 | Generator failure at YBR0603-P3-USF_SRAN-PC @ Power Cube | 10/11/2025 03:44:55 | Minor | 65114 | Generator failure | 10/11/2025 03:44:52 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0603 | FLM_EM | [8 empty] | API | 10/11/2025 03:55:31 | 10/11/2025 05:26:31 | 10/11/2025 05:26:44 | 10/11/2025 05:26:47 | 10/11/2025 05:26:50 | 10/11/2025 06:00:19 |  | Montasir Awadalla Abdalla Bala |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011000203 | PCM-20251011-00000400 | TT-20251011-00405 | EM | Region_4 | USMD0697 | USMD0697 | Enviroment | SCECO_Failure | SCECO auto restored | Waheed Ullah Said Haleem | 10/11/2025 05:20:46 | 10/22/2025 11:05:21 | 10/11/2025 17:20:46 | Aircraft Warning Tower Light Failure at USMD0697-GSM-P3 @ Generator_SG | 10/11/2025 05:12:26 | Minor | 7103 | Aircraft Warning Tower Light Failure | 10/11/2025 05:12:19 | P3 | 2G | taif | Generator_SG | 2G NSA | USMD0697 | FLM_EM | [5 empty] | Aircraft Warning Tower Light Failure |  |  | API | 10/11/2025 05:20:46 | 10/11/2025 23:11:29 | 10/22/2025 11:05:10 |  |  | 10/22/2025 11:05:21 |  | Waheed Ullah Said Haleem |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251011000213 | PCM-20251011-00000417 | TT-20251011-00429 | EM | Region_4 | SIR0158 | SIR0158 |  |  |  | Ibrahim Fawzy Mohamed Elbers | 10/11/2025 05:47:11 | 10/12/2025 06:15:18 | 10/11/2025 17:47:11 | GENERATOR1 + GENERATOR2 2 FAILURE at SIR0158-GSM-P2-USF @ Generator_SG | 10/11/2025 05:38:59 | Minor | 7103 | GENERATOR1 + GENERATOR2 2 FAILURE | 10/11/2025 05:38:49 | P2 | 2G | adam | Generator_SG | 2G NSA | SIR0158 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 FAILURE |  |  | API | 10/11/2025 05:47:11 | 10/12/2025 06:15:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000318 | PCM-20251011-00000576 | TT-20251011-00589 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/11/2025 08:09:45 | 10/11/2025 12:17:55 | 10/11/2025 20:09:45 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/11/2025 08:01:08 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/11/2025 08:01:05 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/11/2025 08:09:45 | 10/11/2025 12:17:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011000319 | PCM-20251011-00000577 | TT-20251011-00591 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/11/2025 08:12:20 | 10/11/2025 20:38:39 | 10/11/2025 20:12:20 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/11/2025 08:04:11 | Minor | 7103 | AIRCON 1 FAILURE | 10/11/2025 08:04:00 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/11/2025 08:12:20 | 10/11/2025 09:55:55 | 10/11/2025 20:38:27 |  |  | 10/11/2025 20:38:39 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000381 | PCM-20251011-00000674 | TT-20251011-00672 | EM | Region_4 | JED0355 | JED0355 |  |  |  | Ahmed Gamal Mohamed Farag | 10/11/2025 08:50:00 | 10/11/2025 20:48:11 | 10/11/2025 20:50:00 | AIRCON 1 FAILURE at JED1M7355-CA-L900-L800-SBTS @ Sceco | 10/11/2025 08:41:37 | Minor | 7103 | AIRCON 1 FAILURE | 10/11/2025 08:41:34 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7355 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/11/2025 08:50:00 | 10/11/2025 20:48:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251011000392 | PCM-20251011-00000691 | TT-20251011-00684 | EM | Region_4 | SQR0200 | SQR0200 |  |  |  | Faiz Muhammad Ghulam Sarwar | 10/11/2025 09:01:25 | 10/11/2025 09:01:25 | 10/11/2025 21:01:25 | RECTIFIER MAINS POWER FAILURE at SQR0200-GSM-UMTS-P2-USF @ Generator_SG | 10/11/2025 08:53:09 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/11/2025 08:53:00 | P2 | 2G | adam | Generator_SG | 2G NSA | SQR0200 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/11/2025 09:01:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000397 | PCM-20251011-00000702 | TT-20251011-00693 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/11/2025 09:05:03 | 10/11/2025 19:16:16 | 10/11/2025 21:05:03 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/11/2025 08:54:39 | Minor | 65102 | high temprature 32 | 10/11/2025 08:54:34 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/11/2025 09:05:03 | 10/11/2025 19:16:16 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251011000515 | PCM-20251011-00000904 | TT-20251011-00897 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/11/2025 11:14:40 | 10/11/2025 14:58:43 | 10/11/2025 17:14:40 | high temprature 32 at DAM2066-P1-HUB_SRAN @ Sceco | 10/11/2025 11:04:06 | Major | 65102 | high temprature 32 | 10/11/2025 11:04:02 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/11/2025 11:14:40 | 10/11/2025 14:58:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000720 | PCM-20251011-00001226 | TT-20251011-01179 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/11/2025 14:13:56 | 10/11/2025 14:58:45 | 10/12/2025 02:13:56 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/11/2025 14:03:19 | Minor | 65102 | High temperature 32C alarm | 10/11/2025 14:03:16 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/11/2025 14:13:56 | 10/11/2025 14:58:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011000734 | PCM-20251011-00001267 | TT-20251011-01218 | EM | Region_4 | TAF0320 | TAF0320 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 10/11/2025 14:24:16 | 10/17/2025 01:29:24 | 10/12/2025 02:24:16 | RECTIFIER MAINS POWER FAILURE at TAF1M7320-G9-L18-L21-SBTS-P3 @ Sceco | 10/11/2025 14:15:49 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/11/2025 14:15:42 | P3 | 4G | taif | Sceco | LTE NSA | TAF1M7320 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/11/2025 14:24:16 | 10/11/2025 17:30:27 | 10/17/2025 01:29:15 |  |  | 10/17/2025 01:29:24 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251011000953 | PCM-20251011-00001592 | TT-20251011-01541 | EM | Region_4 | KMMD9073 | KMMD9073 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/11/2025 17:19:20 | 10/15/2025 07:06:17 | 10/11/2025 21:19:20 | Main power failure at KMMD9073 on 10.154.115.83 @ Sceco | 10/11/2025 17:17:11 | Critical | Main power failure | Main power failure | 10/11/2025 17:06:47 | P1 | Repeater | jeddah | Sceco | TX NSA | KMMD9073 | FLM_EM | [8 empty] | API | 10/11/2025 17:19:20 | 10/15/2025 07:06:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Departed | CM20251011000965 | PCM-20251011-00001609 | TT-20251011-01559 | EM | Region_6 | JIZ0151 | JIZ0151 |  |  |  | Adnan Nadeem Abdul Ghaffar | 10/11/2025 17:30:19 | 10/17/2025 19:30:33 | 10/12/2025 05:30:19 | AIRCON 1 FAILURE at JIZ0151-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/11/2025 17:21:35 | Minor | 7103 | AIRCON 1 FAILURE | 10/11/2025 17:21:27 | P2 | 2G | jizan | Sceco | 2G NSA | JIZ0151 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/11/2025 17:30:19 | 10/11/2025 18:39:40 | 10/13/2025 04:18:55 | 10/17/2025 19:30:33 |  |  |  |  | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251011001059 | PCM-20251011-00001845 | TT-20251011-01784 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/11/2025 19:05:45 | 10/13/2025 14:48:57 | 10/12/2025 07:05:45 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/11/2025 18:59:00 | Minor | 40564 | Genset Fault | 10/11/2025 18:59:00 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/11/2025 19:05:45 | 10/12/2025 10:51:06 | 10/13/2025 14:48:47 |  |  | 10/13/2025 14:48:57 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251011001120 | PCM-20251011-00001946 | TT-20251011-01884 | EM | Region_6 | BSA0409 | BSA0409 |  |  |  | Asad Saddiq | 10/11/2025 20:31:01 | 10/13/2025 09:26:32 | 10/12/2025 08:31:01 | RECTIFIER MODULE FAILURE at BSA0409-CA-L800-NR2.6-P3-SBTS @ Generator_SG | 10/11/2025 20:22:32 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/11/2025 20:22:24 | P3 | 2G | bisha | Generator_SG | 2G NSA | BSA0409 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/11/2025 20:31:01 | 10/13/2025 09:26:32 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000068 | PCM-20251012-00000122 | TT-20251012-00152 | EM | Region_6 | JEC0287 | JEC0287 |  |  |  | Fizan Ahmed | 10/12/2025 01:48:11 | 10/12/2025 20:08:05 | 10/12/2025 07:48:11 | SHELTER DOOR OPEN at JEC1M7287-G9-L18-L21-SBTS-P1-VIP @ Generator_SG | 10/12/2025 01:47:41 | Major | 7103 | SHELTER DOOR OPEN | 10/12/2025 01:47:34 | VIP | 4G | baish | Generator_SG | LTE NSA | JEC1M7287 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/12/2025 01:48:11 | 10/12/2025 20:08:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000120 | PCM-20251012-00000198 | TT-20251012-00235 | EM | Region_6 | BSA0239 | BSA0239 |  |  |  | Asad Saddiq | 10/12/2025 02:31:00 | 10/13/2025 09:26:35 | 10/12/2025 14:31:00 | AIRCON 1 FAILURE at BSA1M7239-G9-CA-L800-NNR2.6-SBTS-P3 @ Sceco | 10/12/2025 02:22:58 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 02:22:23 | P3 | 4G | bisha | Sceco | LTE NSA | BSA1M7239 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 02:31:00 | 10/13/2025 09:26:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251012000143 | PCM-20251012-00000232 | TT-20251012-00274 | EM | Region_6 | BSA0465 | BSA0465 |  |  |  | Asad Saddiq | 10/12/2025 02:54:46 | 10/13/2025 09:26:35 | 10/12/2025 14:54:46 | AIRCON 1 FAILURE at BSA1M7465-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/12/2025 02:46:29 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 02:46:12 | P3 | 4G | bisha | Sceco | LTE NSA | BSA1M7465 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 02:54:46 | 10/13/2025 09:26:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000162 | PCM-20251012-00000260 | TT-20251012-00047 | Telecom | Region_4 | JED0667 | JED0667 |  |  |  | Amer Attallah Awadallah | 10/12/2025 03:08:02 | 10/12/2025 11:34:30 | 10/12/2025 15:08:02 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED1M7667-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/12/2025 00:28:13 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 00:28:08 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7667 | FLM_EM |  |  | PCM-20251012-00000035 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/12/2025 03:08:02 | 10/12/2025 11:34:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000172 | PCM-20251012-00000277 | TT-20251012-00320 | EM | Region_6 | BSH0070 | BSH0070 |  |  |  | Fizan Ahmed | 10/12/2025 03:19:36 | 10/14/2025 11:16:35 | 10/12/2025 15:19:36 | AIRCON 1 FAILURE at BSH0070-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/12/2025 03:11:35 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 03:11:05 | P2 | 2G | baish | Sceco | 2G NSA | BSH0070 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 03:19:36 | 10/12/2025 20:08:06 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251012000190 | PCM-20251012-00000321 | TT-20251012-00364 | EM | Region_6 | ARQ0019 | ARQ0019 |  |  |  | Khurram Nawaz Muhammad Akram | 10/12/2025 03:45:56 | 10/12/2025 07:11:33 | 10/12/2025 15:45:56 | AIRCON 2 FAILURE at ARQ1M7019-G9-L18-SBTS-P2 @ Sceco | 10/12/2025 03:37:24 | Minor | 7103 | AIRCON 2 FAILURE | 10/12/2025 03:37:11 | P2 | 4G | jizan | Sceco | LTE NSA | ARQ1M7019 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/12/2025 03:45:56 | 10/12/2025 07:11:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251012000191 | PCM-20251012-00000322 | TT-20251012-00365 | EM | Region_6 | DAR0023 | DAR0023 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Muhammad Tayyab | 10/12/2025 03:46:26 | 10/18/2025 08:49:39 | 10/12/2025 09:46:26 | AIRCON 1 FAILURE at DAR1M7023-G9-L8-L18-L21-SBTS-P1-DIA @ Generator_SG | 10/12/2025 03:39:44 | Major | 7103 | AIRCON 1 FAILURE | 10/12/2025 03:38:06 | P1 | 4G | dair | Generator_SG | LTE NSA | DAR1M7023 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 03:46:26 | 10/14/2025 12:40:56 | 10/18/2025 08:49:00 |  |  | 10/18/2025 08:49:39 |  | Muhammad Tayyab | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251012000201 | PCM-20251012-00000340 | TT-20251012-00386 | EM | Region_4 | TFBH0892 | TFBH0892 | Enviroment | SCECO_Failure | SCECO auto restored | Taher Abdulgawwad Hussain | 10/12/2025 04:13:16 | 10/12/2025 14:16:14 | 10/12/2025 08:13:16 | NE_COMMU_BREAK at TFBH0892_OSC1 @ Sceco_STB | 10/12/2025 04:11:27 | Critical | 0-1 | NE_COMMU_BREAK | 10/12/2025 04:11:25 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_EM | [5 empty] | Communication with common NE TFBH0892_OSC1 is interrupted |  |  | API | 10/12/2025 04:13:16 | 10/12/2025 07:22:02 | 10/12/2025 14:16:03 |  |  | 10/12/2025 14:16:14 |  | Taher Abdulgawwad Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251012000202 | PCM-20251012-00000342 | TT-20251012-00387 | EM | Region_4 | TFBH0892 | TFBH0892 | Enviroment | SCECO_Failure | SCECO auto restored | Taher Abdulgawwad Hussain | 10/12/2025 04:13:21 | 10/12/2025 14:17:23 | 10/12/2025 08:13:21 | NE_NOT_LOGIN at TFBH0892_ELC @ Sceco_STB | 10/12/2025 04:11:19 | Critical | 0-2 | NE_NOT_LOGIN | 10/12/2025 04:11:17 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_EM | [5 empty] | NE TFBH0892_ELC not login |  |  | API | 10/12/2025 04:13:21 | 10/12/2025 07:22:02 | 10/12/2025 14:17:15 |  |  | 10/12/2025 14:17:23 |  | Taher Abdulgawwad Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251012000203 | PCM-20251012-00000343 | TT-20251012-00390 | EM | Region_4 | TFBH0892 | TFBH0892 | Enviroment | SCECO_Failure | SCECO auto restored | Taher Abdulgawwad Hussain | 10/12/2025 04:13:46 | 10/12/2025 14:17:48 | 10/12/2025 08:13:46 | NE_NOT_LOGIN at TFBH0892_OSC2 @ Sceco_STB | 10/12/2025 04:11:35 | Critical | 0-2 | NE_NOT_LOGIN | 10/12/2025 04:11:31 | P1 | 2G | taif | Sceco_STB | DWDM NSA | TFBH0892 | FLM_EM | [5 empty] | NE TFBH0892_OSC2 not login |  |  | API | 10/12/2025 04:13:46 | 10/12/2025 07:22:03 | 10/12/2025 14:17:40 |  |  | 10/12/2025 14:17:48 |  | Taher Abdulgawwad Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251012000258 | PCM-20251012-00000421 | TT-20251012-00450 | Reference_EM | Region_1 | YBR0613 | YBR0613 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Montasir Awadalla Abdalla Bala | 10/12/2025 05:30:20 | 10/13/2025 12:20:52 | 10/12/2025 17:30:20 | Air condition 1 failure alarm at YBR0613-P2-USF_SRAN-PC @ Power Cube | 10/12/2025 05:19:39 | Minor | 65104 | Air condition 1 failure alarm | 10/12/2025 05:19:35 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0613 | FLM_EM | [8 empty] | API | 10/12/2025 05:30:20 | 10/12/2025 16:08:55 | 10/13/2025 11:52:48 | 10/13/2025 11:52:56 | 10/13/2025 11:53:24 | 10/13/2025 12:20:52 |  | Montasir Awadalla Abdalla Bala |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251012000356 | PCM-20251012-00000594 | TT-20251012-00648 | Reference_EM | Region_1 | ARR0903 | ARR0903 | Transsmission | IPRAN_Fluctuation | Change Port | Hassan rabie | 10/12/2025 07:34:45 | 10/15/2025 16:44:38 | 10/12/2025 19:34:45 | Minor Rec alarm at ARR0903-P2-USF_SRAN @ Generator_DG | 10/12/2025 07:24:09 | Minor | 65108 | Minor Rec alarm | 10/12/2025 07:24:05 | P2 | SRAN | arar | Generator_DG | 2G NSA | ARR0903 | FLM_EM | [8 empty] | API | 10/12/2025 07:34:45 | 10/15/2025 16:44:38 | [5 empty] | Hassan rabie | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000393 | PCM-20251012-00000663 | TT-20251012-00709 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/12/2025 08:20:45 | 10/14/2025 06:55:59 | 10/12/2025 20:20:45 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/12/2025 08:12:14 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/12/2025 08:12:11 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/12/2025 08:20:45 | 10/14/2025 06:55:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000409 | PCM-20251012-00000685 | TT-20251012-00725 | EM | Region_6 | BSA0447 | BSA0447 |  |  |  | Asad Saddiq | 10/12/2025 08:32:35 | 10/13/2025 09:26:36 | 10/12/2025 20:32:35 | AIRCON 1 FAILURE at BSA0447-GSM-P3 @ Generator_SG | 10/12/2025 08:23:57 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 08:23:51 | P3 | 2G | bisha | Generator_SG | 2G NSA | BSA0447 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 08:32:35 | 10/13/2025 09:26:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000416 | PCM-20251012-00000695 | TT-20251012-00743 | Reference_EM | Region_2 | KHJ0469 | KHJ0469 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/12/2025 08:40:20 | 10/20/2025 14:40:43 | 10/12/2025 20:40:20 | High temperature 32C alarm at KHJ2M1469-P3 @ Sceco | 10/12/2025 08:29:56 | Minor | 65102 | High temperature 32C alarm | 10/12/2025 08:29:52 | P3 | 2G | al kharj | Sceco | 2G NSA | KHJ2M1469 | FLM_EM | [8 empty] | API | 10/12/2025 08:40:20 | 10/20/2025 14:40:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000453 | PCM-20251012-00000769 | TT-20251012-00829 | EM | Region_1 | KBR0156 | KBR0156 |  |  |  | Abdul Malik Shaik | 10/12/2025 09:30:25 | 10/12/2025 13:33:50 | 10/12/2025 15:30:25 | high temprature 40 at KBR0156-P1-SHOP_SRAN @ Sceco | 10/12/2025 09:23:48 | Major | 65103 | high temprature 40 | 10/12/2025 09:19:51 | P1 | SRAN | dammam | Sceco | 2G NSA | KBR0156 | FLM_EM | [8 empty] | API | 10/12/2025 09:30:25 | 10/12/2025 13:33:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000501 | PCM-20251012-00000865 | TT-20251012-00922 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/12/2025 10:25:19 | 10/12/2025 13:33:50 | 10/12/2025 22:25:19 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/12/2025 10:14:55 | Minor | 65102 | high temprature 32 | 10/12/2025 10:14:50 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/12/2025 10:25:19 | 10/12/2025 13:33:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012000987 | PCM-20251012-00001833 | TT-20251012-01928 | Reference_telecom | Region_6 | RYAB0627 | RYAB0627 |  |  |  | Ahmed Mamdouh Helal Helal | 10/12/2025 17:59:37 | 10/13/2025 20:17:32 | 10/13/2025 05:59:37 | NEC MW Observing High BER at RYAB0627-2(10.157.250.61) | 10/11/2025 21:53:00 | Minor |  | LOF | 10/11/2025 21:53:00 | P1 | 2G | wadi dawasar | Sceco_STB | TX NSA | RYAB0627-2(10.157.250.61) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:37 | 10/13/2025 20:17:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012000991 | PCM-20251012-00001837 | TT-20251012-01932 | Reference_telecom | Region_1 | SAR0076 | SAR0076 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/12/2025 17:59:43 | 10/22/2025 11:33:40 | 10/13/2025 05:59:43 | NEC MW Observing ODU CPU / Cable Open,LOF,Frame ID at SAR0076-1(10.154.19.161) | 10/09/2025 14:04:01 | Minor |  | LOF | 10/09/2025 14:04:01 | P1 | SRAN | quriyat | Generator_DG | TX NSA | SAR0076-1(10.154.19.161) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:43 | 10/12/2025 18:02:25 | [6 empty] | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001000 | PCM-20251012-00001846 | TT-20251012-01941 | Reference_telecom | Region_3 | YNB0670 | YNB0670 |  |  |  | Muhammad Sajjad R3 | 10/12/2025 17:59:52 | 10/13/2025 03:09:56 | 10/13/2025 05:59:52 | NEC MW Observing LOF,RX Level,RX Level,LOF,LOF,RX Level,RX Level,LOF,LOF,RX Level,LOF,RX Level,Radio Traffic Aggregation Link,RX Level,LOF,RX Level,LOF at YNB0670-MDYB0313_2(10.248.39.7) | 09/18/2025 16:56:32 | Minor |  | LOF | 09/18/2025 16:56:32 | P1 | SRAN | yanbu | Sceco | TX NSA | YNB0670-MDYB0313_2(10.248.39.7) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:52 | 10/13/2025 03:09:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251012001002 | PCM-20251012-00001848 | TT-20251012-01943 | MW_HC | Region_4 | JED0125 | JED0125 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/12/2025 17:59:54 | 10/14/2025 11:46:25 | 10/13/2025 05:59:54 | NEC MW HC_P2 Observing Modem Down at JED0125(10.154.142.201)--JED0644(10.154.142.202) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED0125(10.154.142.201)--JED0644(10.154.142.202) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:54 | 10/14/2025 11:38:14 | 10/14/2025 11:39:37 | 10/14/2025 11:39:39 | 10/14/2025 11:46:25 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001003 | PCM-20251012-00001849 | TT-20251012-01944 | MW_HC | Region_4 | JDJZ0767 | JDJZ0767 |  |  |  | Riasat Ali Allah Baksh | 10/12/2025 17:59:55 | 10/13/2025 11:54:05 | 10/13/2025 05:59:55 | NEC MW HC_P0 Observing Performance Issue at JDJZ0767(10.154.140.100)--MKYL0915(10.154.140.109) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0767(10.154.140.100)--MKYL0915(10.154.140.109) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:55 | 10/13/2025 11:54:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001004 | PCM-20251012-00001850 | TT-20251012-01945 | MW_HC | Region_4 | TFBH9401 | TFBH9401 |  |  |  | Ahmad Kamal Abdelmawla | 10/12/2025 17:59:57 | 10/14/2025 20:35:37 | 10/13/2025 05:59:57 | NEC MW HC_P0 Observing Modem Down at TFBH9401(10.88.221.178)--TFBH9443(10.88.221.215) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9401(10.88.221.178)--TFBH9443(10.88.221.215) | FLM_TE | [8 empty] | API | 10/12/2025 17:59:57 | 10/14/2025 20:35:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001009 | PCM-20251012-00001855 | TT-20251012-01950 | MW_HC | Region_6 | KHS0563 | KHS0563 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/12/2025 18:00:03 | 10/12/2025 18:19:27 | 10/13/2025 06:00:03 | NEC MW HC_P0 Observing Performance Issue at KHS0563(10.89.220.84)--KMBS0663(10.89.220.87) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KHS0563(10.89.220.84)--KMBS0663(10.89.220.87) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:03 | 10/12/2025 18:19:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001010 | PCM-20251012-00001856 | TT-20251012-01951 | MW_HC | Region_6 | JEC0331 | JEC0331 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/12/2025 18:00:06 | 10/12/2025 18:59:05 | 10/13/2025 06:00:06 | NEC MW HC_P0 VIP Observing Performance Issue at JEC0331(10.154.126.6)--JEC0377(10.154.126.8) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | 2G | baish | Generator_SG | TX NSA | JEC0331(10.154.126.6)--JEC0377(10.154.126.8) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:06 | 10/12/2025 18:59:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001012 | PCM-20251012-00001859 | TT-20251012-01954 | MW_HC | Region_6 | ABDB9020 | ABDB9020 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/12/2025 18:00:09 | 10/12/2025 18:19:04 | 10/13/2025 06:00:09 | NEC MW HC_P0 Observing Modem Down at ABDB9020(10.1.170.225)--RJL0129(10.1.170.227) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | Repeater | mohail | Sceco | TX NSA | ABDB9020(10.1.170.225)--RJL0129(10.1.170.227) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:09 | 10/12/2025 18:19:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001013 | PCM-20251012-00001860 | TT-20251012-01955 | MW_HC | Region_6 | ABDB9020 | ABDB9020 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/12/2025 18:00:11 | 10/12/2025 18:19:04 | 10/13/2025 06:00:11 | NEC MW HC_P0 Observing Modem Down at ABDB9020(10.1.170.225)--RJL0127(10.1.170.226) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | Repeater | mohail | Sceco | TX NSA | ABDB9020(10.1.170.225)--RJL0127(10.1.170.226) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:11 | 10/12/2025 18:19:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001014 | PCM-20251012-00001861 | TT-20251012-01956 | MW_HC | Region_5 | MAK0603 | MAK0603 | Transsmission | MW_Connectors | Remade Indoor MW Connector | IJAZ ALI | 10/12/2025 18:00:12 | 10/13/2025 12:45:10 | 10/13/2025 06:00:12 | NEC MW HC_P0 VIP Observing Performance Issue at MAK0603(10.1.163.25)--MAK6140(10.1.163.26) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | VIP | 2G | makkah | Sceco | TX NSA | MAK0603(10.1.163.25)--MAK6140(10.1.163.26) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:12 | 10/13/2025 11:00:31 | 10/13/2025 11:01:10 | 10/13/2025 11:01:13 | 10/13/2025 11:17:33 | 10/13/2025 12:45:10 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001017 | PCM-20251012-00001864 | TT-20251012-01959 | MW_HC | Region_1 | HFBD0009 | HFBD0009 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/12/2025 18:00:15 | 10/13/2025 08:24:20 | 10/13/2025 06:00:15 | NEC MW HC_P0 Observing Modem Down at HFBD0009(10.159.106.132)--HFBD0660(10.159.106.133) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFBD0009(10.159.106.132)--HFBD0660(10.159.106.133) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:15 | 10/13/2025 08:24:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001018 | PCM-20251012-00001865 | TT-20251012-01960 | MW_HC | Region_1 | HFB0027 | HFB0027 |  |  |  | Mohamed Magdy Fouad Zayed | 10/12/2025 18:00:17 | 10/22/2025 11:33:41 | 10/13/2025 06:00:17 | NEC MW HC_P0 Observing Performance Issue at HFB0027(10.74.86.98)--HFB0028(10.74.86.101) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | hafouf | Generator_SG | TX NSA | HFB0027(10.74.86.98)--HFB0028(10.74.86.101) | FLM_TE | [8 empty] | API | 10/12/2025 18:00:17 | 10/12/2025 18:41:39 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001022 | PCM-20251012-00001869 | TT-20251012-01964 | MW_HC | Region_2 | ZRN0245 | ZRN0245 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Tahir Abdulrazzaq | 10/12/2025 18:00:21 | 10/16/2025 11:36:32 | 10/13/2025 06:00:21 | Huawei MW HC_P2 Observing Errors at ZRN0245-ZRN0237 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | rumah | Sceco | TX NSA | ZRN0245-ZRN0237 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:21 | 10/13/2025 12:37:08 | 10/16/2025 11:36:06 |  |  | 10/16/2025 11:36:32 |  | Muhammad Tahir Abdulrazzaq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001023 | PCM-20251012-00001870 | TT-20251012-01965 | MW_HC | Region_1 | YBR0669 | YBR0669 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/12/2025 18:00:22 | 10/13/2025 08:24:21 | 10/13/2025 06:00:22 | Huawei MW HC_P2 Observing Errors at YBR0669-YBR0603 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | hafouf | Power Cube | TX NSA | YBR0669-YBR0603 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:22 | 10/13/2025 08:24:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001030 | PCM-20251012-00001877 | TT-20251012-01973 | MW_HC | Region_2 | RYAB0603 | RYAB0603 | Transsmission | MW_RSL_fading | Fading issue | Hakim Ullah Raif Ullah Jan | 10/12/2025 18:00:31 | 10/15/2025 07:13:05 | 10/13/2025 06:00:31 | Huawei MW HC_P2 Observing Errors at RYAB0603-RYAB0604 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | al kharj | Sceco_STB | TX NSA | RYAB0603-RYAB0604 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:31 | 10/13/2025 21:37:44 | 10/15/2025 07:11:39 |  |  | 10/15/2025 07:13:05 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001031 | PCM-20251012-00001878 | TT-20251012-01974 | MW_HC | Region_2 | RIY0959 | RIY0959 |  |  |  | Farmanullah Akbar Jan | 10/12/2025 18:00:32 | 10/12/2025 21:56:49 | 10/13/2025 06:00:32 | Huawei MW HC_P2 Observing Errors at RIY0959-RIY0416 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0959-RIY0416 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:32 | 10/12/2025 21:56:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001032 | PCM-20251012-00001879 | TT-20251012-01975 | MW_HC | Region_2 | RIY0371 | RIY0371 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Waseem Shahzad Ghulam Rasool | 10/12/2025 18:00:34 | 10/13/2025 13:57:57 | 10/13/2025 06:00:34 | Huawei MW HC_P2 Observing Errors at RIY0371-RIY0773 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | VIP | SRAN | riyadh | Sceco_STB | TX NSA | RIY0371-RIY0773 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:34 | 10/13/2025 12:18:20 | 10/13/2025 13:57:31 |  |  | 10/13/2025 13:57:57 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251012001033 | PCM-20251012-00001880 | TT-20251012-01976 | MW_HC | Region_2 | RIY2976 | RIY2976 |  |  |  | Asad Ali Nadiq Khan | 10/12/2025 18:00:34 | 10/23/2025 16:31:29 | 10/13/2025 06:00:34 | Huawei MW HC_P2 Observing Errors at RIY2976-RIY2919 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | riyadh | Sceco | TX NSA | RIY2976-RIY2919 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:34 | 10/13/2025 13:00:09 | 10/23/2025 16:31:29 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001036 | PCM-20251012-00001883 | TT-20251012-01978 | MW_HC | Region_2 | RIY0283 | RIY0283 |  |  |  | Farmanullah Akbar Jan | 10/12/2025 18:00:37 | 10/12/2025 21:56:51 | 10/13/2025 06:00:37 | Huawei MW HC_P2 Observing Errors at RIY0283-RIY0075 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0283-RIY0075 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:37 | 10/12/2025 21:56:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001039 | PCM-20251012-00001886 | TT-20251012-01981 | MW_HC | Region_2 | QSDH0716 | QSDH0716 |  |  |  | Zakir Muhammad Yar Muhammad | 10/12/2025 18:00:40 | 10/14/2025 08:09:39 | 10/13/2025 06:00:40 | Huawei MW HC_P2 Observing Errors at QSDH0716-QSDH0715 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | dawadmi | Sceco | TX NSA | QSDH0716-QSDH0715 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:40 | 10/14/2025 08:09:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001043 | PCM-20251012-00001890 | TT-20251012-01985 | MW_HC | Region_2 | RIY0130 | RIY0130 |  |  |  | Farmanullah Akbar Jan | 10/12/2025 18:00:45 | 10/12/2025 21:56:51 | 10/13/2025 06:00:45 | Huawei MW HC_P2 Observing Errors at RIY0130-RIY0338 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0130-RIY0338 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:45 | 10/12/2025 21:56:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001044 | PCM-20251012-00001891 | TT-20251012-01986 | MW_HC | Region_1 | JDNR9012 | JDNR9012 |  |  |  | Tahir Mahmood Hafiz Yar | 10/12/2025 18:00:46 | 10/12/2025 18:38:05 | 10/13/2025 06:00:46 | Huawei MW HC_P2 Observing Errors at JDNR9012-JBL0549 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | Repeater | jubail | Power Cube | TX NSA | JDNR9012-JBL0549 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:46 | 10/12/2025 18:38:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001045 | PCM-20251012-00001892 | TT-20251012-01987 | MW_HC | Region_1 | JBL0531 | JBL0531 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Tahir Mahmood Hafiz Yar | 10/12/2025 18:00:48 | 10/20/2025 16:41:02 | 10/13/2025 06:00:48 | Huawei MW HC_P2 Observing Errors at JBL0531-JBL0558 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | jubail | Power Cube | TX NSA | JBL0531-JBL0558 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:48 | 10/12/2025 18:38:05 | 10/20/2025 14:41:24 | 10/20/2025 14:41:27 | 10/20/2025 15:39:57 | 10/20/2025 16:41:02 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001049 | PCM-20251012-00001896 | TT-20251012-01991 | MW_HC | Region_1 | HFF2733 | HFF2733 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/12/2025 18:00:52 | 10/13/2025 08:24:21 | 10/13/2025 06:00:52 | Huawei MW HC_P2 Observing Errors at HFF2733-DMV0095 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF2733-DMV0095 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:52 | 10/13/2025 08:24:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001050 | PCM-20251012-00001897 | TT-20251012-01992 | MW_HC | Region_1 | HFF2365 | HFF2365 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/12/2025 18:00:53 | 10/13/2025 08:24:22 | 10/13/2025 06:00:53 | Huawei MW HC_P2 Observing Errors at HFF2365-HFF2357 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF2365-HFF2357 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:53 | 10/13/2025 08:24:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001054 | PCM-20251012-00001901 | TT-20251012-01996 | MW_HC | Region_2 | RIY0065 | RIY0065 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/12/2025 18:00:58 | 10/13/2025 13:58:15 | 10/13/2025 06:00:58 | Huawei MW HC_P2 Observing Errors at FC372-RIY0065 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | SRAN | riyadh | Sceco | TX NSA | FC372-RIY0065 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:58 | 10/13/2025 12:18:21 | 10/13/2025 13:58:05 |  |  | 10/13/2025 13:58:15 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001055 | PCM-20251012-00001902 | TT-20251012-01997 | MW_HC | Region_1 | DMHF0823 | DMHF0823 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/12/2025 18:00:59 | 10/13/2025 08:24:23 | 10/13/2025 06:00:59 | Huawei MW HC_P2 Observing Errors at DMHF0823-HFF0179 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | hafouf | Power Cube | TX NSA | DMHF0823-HFF0179 | FLM_TE | [8 empty] | API | 10/12/2025 18:00:59 | 10/13/2025 08:24:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001063 | PCM-20251012-00001910 | TT-20251012-02004 | Reference_telecom | Region_2 | RIY0792 | RIY0792 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/12/2025 18:01:08 | 10/16/2025 20:16:39 | 10/13/2025 06:01:08 | MW RTN Observing MW_LOF,PLA_MEMBER_DOWN_EXT,PLA_DOWN,MW_LOF,PLA_MEM at RIY0792_NE_24_SDB | 08/28/2024 02:55:00 | Minor |  | LOF | 08/28/2024 02:55:00 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0792_NE_24_SDB | FLM_TE | [8 empty] | API | 10/12/2025 18:01:08 | 10/12/2025 18:30:32 | 10/16/2025 20:16:31 |  |  | 10/16/2025 20:16:39 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001072 | PCM-20251012-00001919 | TT-20251012-02014 | Reference_telecom | Region_2 | RIY0328 | RIY0328 |  |  |  | Muhammad Naseer Muhammad Nazir | 10/12/2025 18:01:18 | 10/13/2025 00:05:31 | 10/13/2025 06:01:18 | MW RTN Observing PLA_MEMBER_DOWN_EXT at RIY0328_NE_13_SDB | 10/10/2025 03:58:00 | Minor |  | LOF | 10/10/2025 03:58:00 | P2 | SRAN | riyadh | Generator_SG | TX NSA | RIY0328_NE_13_SDB | FLM_TE | [8 empty] | API | 10/12/2025 18:01:18 | 10/13/2025 00:05:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001165 | PCM-20251012-00002041 | TT-20251012-02128 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/12/2025 18:28:03 | 10/12/2025 18:53:33 | 10/12/2025 22:28:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/12/2025 18:27:25 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 18:27:18 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/12/2025 18:28:03 | 10/12/2025 18:53:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001167 | PCM-20251012-00002051 | TT-20251012-02140 | Reference_telecom | Region_6 | WJZ0065 | WJZ0065 |  |  |  | Muhammad Ali | 10/12/2025 18:28:32 | 10/12/2025 18:50:38 | 10/13/2025 06:28:32 | ReplaceableUnitProblem observed in WJZ0065_01 towards 10.74.121.180 @ Sceco | 10/12/2025 06:28:33 | Minor |  | ReplaceableUnitProblem | 10/12/2025 06:28:01 | P3 | 2G | jizan | Sceco | TX NSA | WJZ0065 | FLM_TE | [8 empty] | API | 10/12/2025 18:28:32 | 10/12/2025 18:50:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001243 | PCM-20251012-00002140 | TT-20251012-02236 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/12/2025 19:12:28 | 10/13/2025 13:10:41 | 10/13/2025 01:12:28 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/12/2025 16:12:21 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/12/2025 16:12:06 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/12/2025 19:12:28 | 10/13/2025 13:10:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001308 | PCM-20251012-00002170 | TT-20251012-02249 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/12/2025 19:25:31 | 10/13/2025 11:36:47 | 10/13/2025 01:25:31 | 1(2G/LTE/5G) sites down under JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/12/2025 19:17:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/12/2025 19:16:59 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED6020-GSM-P3 | FLM_EM | JED6020 | Results: DOWN SITE HUB JED6020-GSM-P3 JED6020 Summary: Hub: JED6020, Down Count: 1, Down Sites: JED6020-GSM-P3 Alarm Summary: JED6020 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/12/2025 19:25:31 | 10/13/2025 11:36:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012001323 | PCM-20251012-00002173 | TT-20251012-02263 | EM | Region_6 | ALA1M8197 | ALA2197 |  |  |  | Asad Saddiq | 10/12/2025 19:26:56 | 10/13/2025 09:26:40 | 10/13/2025 07:26:56 | RECTIFIER MAINS POWER FAILURE at ALA1M8197-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/12/2025 19:24:55 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/12/2025 18:32:03 | P3 | 4G | bisha | Generator_SG | LTE NSA | ALA1M8197 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/12/2025 19:26:56 | 10/13/2025 09:26:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251012001428 | PCM-20251012-00002248 | TT-20251012-02334 | Telecom | Region_1 | QRY2U6708 | QRY6008 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/12/2025 20:20:40 | 10/21/2025 11:37:52 | 10/13/2025 02:20:40 | RF Out of Service at QRY2U6708-P3 @ Sceco | 10/12/2025 20:16:07 | Major | 29248 | RF Out of Service | 10/12/2025 20:14:34 | P3 | 4G | quriyat | Sceco | 2G SA | QRY2U6708 | FLM_TE | [8 empty] | API | 10/12/2025 20:20:40 | 10/13/2025 01:21:06 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001449 | PCM-20251012-00002297 | TT-20251012-02327 | Telecom | Region_1 | QRY6008 | QRY6008 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/12/2025 20:43:00 | 10/13/2025 01:21:07 | 10/13/2025 02:43:00 | Local Cell Capability Decline at QRY6008-P3_SRAN @ Sceco | 10/12/2025 20:14:55 | Major | 28206 | Local Cell Capability Decline | 10/12/2025 20:13:19 | P3 | SRAN | quriyat | Sceco | 2G NSA | QRY6008 | FLM_TE |  |  | PCM-20251012-00002244 | pease do HC as site suffer from HW alarms | pease do HC as site suffer from HW alarms |  |  |  | API | 10/12/2025 20:43:00 | 10/13/2025 01:21:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001459 | PCM-20251012-00002312 | TT-20251012-02395 | Telecom | Region_4 | JED0109 | JED0109 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/12/2025 21:01:59 | 10/21/2025 17:12:34 | 10/13/2025 03:01:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/12/2025 21:01:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 21:01:08 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/12/2025 21:01:59 | 10/13/2025 04:18:41 | 10/15/2025 09:06:50 |  |  | 10/15/2025 09:07:03 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001461 | PCM-20251012-00002318 | TT-20251012-01585 | Telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/12/2025 21:05:06 | 10/19/2025 13:20:39 | 10/13/2025 09:05:06 | Configured Capacity Limit Exceeding Licensed Limit at RYQ0972-P3_SRAN @ Sceco | 10/12/2025 15:23:59 | Minor | 26811 | Configured Capacity Limit Exceeding Licensed Limit | 10/12/2025 15:11:14 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0972 | FLM_TE |  |  | PCM-20251012-00001492 | Dear FLM, Need to change UBBPg3 to old log UBBPd6 | Dear FLM, Need to change UBBPg3 to old log UBBPd6 |  |  |  | API | 10/12/2025 21:05:06 | 10/13/2025 07:33:23 | [6 empty] | ZAIN O-M |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001497 | PCM-20251012-00002360 | TT-20251012-02300 | Telecom | Region_6 | SDA1M9319 | SDA0319 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/12/2025 21:24:29 | 10/12/2025 21:35:42 | 10/13/2025 03:24:29 | BASE STATION OPERATION DEGRADED (Inter-Site CA link establishment failure) at SDA1M9319-L800 @ Sceco | 10/12/2025 19:46:20 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/12/2025 19:46:10 | P3 | 4G | abha | Sceco | LTE NSA | SDA1M9319 | FLM_TE |  |  | PCM-20251012-00002223 | Kindly check the anchor Site SDA1MT0139 having HW errors active | Kindly check the anchor Site SDA1MT0139 having HW errors active |  |  |  | API | 10/12/2025 21:24:29 | 10/12/2025 21:33:28 | 10/12/2025 21:35:33 |  |  | 10/12/2025 21:35:42 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001506 | PCM-20251012-00002376 | TT-20251012-02439 | Telecom | Region_4 | JED1M8108 | JED2108 |  |  |  | BARKAT ALI MAIN HILAL | 10/12/2025 21:36:21 | 10/12/2025 22:03:18 | 10/13/2025 03:36:21 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M8108-P3-L800-CA @ Sceco | 10/12/2025 21:24:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 21:24:18 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8108 | FLM_TE |  |  | PCM-20251012-00002367 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/12/2025 21:36:21 | 10/12/2025 22:03:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001518 | PCM-20251012-00002388 | TT-20251012-02461 | EM | Region_2 | RIY2110 | RIY2110 |  |  |  | Kadri Jalal Mohammed Asmail | 10/12/2025 21:46:25 | 10/13/2025 09:14:37 | 10/13/2025 03:46:25 | Door opening alarm at RIY2110-P1-VIP_SRAN @ Sceco | 10/12/2025 21:46:11 | Major | 65101 | Door opening alarm | 10/12/2025 21:46:06 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2110 | FLM_EM | [8 empty] | API | 10/12/2025 21:46:25 | 10/13/2025 09:14:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251012001548 | PCM-20251012-00002430 | TT-20251012-02506 | Reference_telecom | Region_4 | JED1MN0924 | JED0924 | Equipment | BSS_HW_fault | Replace Controller Card | Ali Mohamed | 10/12/2025 22:36:16 | 10/21/2025 11:42:04 | 10/13/2025 02:36:16 | 1(5G) site down under JED1MN0924-NR2.6-P2 (Ref::TT-20251012-02036) | 10/12/2025 18:18:24 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/12/2025 18:18:24 | VIP | 5G | jeddah | Sceco | 5G SA | JED1MN0924-NR2.6-P2 | FLM_TE | JED1MN0924 | Results: DOWN SITE HUB JED1MN0924-NR2.6-P2 JED1MN0924 Summary: Hub: JED1MN0924, Down Count: 1, Down Sites: JED1MN0924-NR2.6-P2 Alarm Summary: JED1MN0924 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/12/2025 22:36:16 | [6 empty] | Bilal hassan shaukat ali | NSN_Care |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251012001553 | PCM-20251012-00002442 | TT-20251012-01145 | Telecom | Region_4 | JED1MN0752 | JED0752 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/12/2025 22:46:02 | 10/12/2025 22:46:02 | 10/13/2025 04:46:02 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED1MN0752-NR2.6-P3 @ Sceco | 10/12/2025 12:22:07 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/12/2025 12:22:02 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0752 | FLM_TE |  |  | PCM-20251012-00001085 | Kindly check the anchoring site, its down | Kindly check the anchoring site, its down |  |  |  | API | 10/12/2025 22:46:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251012001554 | PCM-20251012-00002444 | TT-20251012-02526 | Reference_telecom | Region_6 | SAB0055 | SAB0055 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/12/2025 22:46:50 | 10/19/2025 18:49:03 | 10/13/2025 10:46:50 | DemFail observed in SAB0055 towards 10.3.86.154 @ Sceco | 10/12/2025 10:46:30 | Minor |  | DemFail | 10/12/2025 10:46:27 | P2 | 2G | baish | Sceco | TX NSA | SAB0055 | FLM_TE | [8 empty] | API | 10/12/2025 22:46:50 | 10/13/2025 01:31:50 | 10/19/2025 18:12:43 | 10/19/2025 18:12:46 | 10/19/2025 18:49:03 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001557 | PCM-20251012-00002448 | TT-20251012-02531 | Reference_telecom | Region_6 | SAB0055 | SAB0055 | Transsmission | MW_HW_fault | Replace Control Card | Ansir Iqbal Muhammad Iqbal | 10/12/2025 22:48:22 | 10/19/2025 22:06:21 | 10/13/2025 10:48:22 | ReplaceableUnitMissing observed in SAB0055 NE4 towards 10.10.155.134 @ Sceco | 10/12/2025 10:49:32 | Minor |  | ReplaceableUnitMissing | 10/12/2025 10:47:52 | P2 | 2G | baish | Sceco | TX NSA | SAB0055 | FLM_TE | [8 empty] | API | 10/12/2025 22:48:22 | 10/13/2025 01:31:50 | 10/19/2025 18:12:34 | 10/19/2025 18:12:38 | 10/19/2025 18:49:50 | 10/19/2025 22:06:21 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001582 | PCM-20251012-00002477 | TT-20251012-02549 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/12/2025 23:00:21 | 10/19/2025 17:44:13 | 10/13/2025 05:00:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/12/2025 22:59:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 22:59:27 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/12/2025 23:00:21 | 10/13/2025 09:32:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001586 | PCM-20251012-00002488 | TT-20251012-02535 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/12/2025 23:27:33 | 10/17/2025 17:34:25 | 10/13/2025 03:27:33 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/12/2025 22:41:37 | Critical | 7654 | CELL OPERATION DEGRADED | 10/12/2025 22:41:32 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251012-00002453 | Please check ALD HW & all the connectivity from ALD To RMOD_r3_ANt1&2 port. | Please check ALD HW & all the connectivity from ALD To RMOD_r3_ANt1&2 port. |  |  |  | API | 10/12/2025 23:27:33 | 10/13/2025 09:43:48 | 10/17/2025 17:34:16 |  |  | 10/17/2025 17:34:25 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251012001590 | PCM-20251012-00002494 | TT-20251012-02574 | Reference_telecom | Region_6 | FIF0045 | FIF0045 |  |  |  | Muhammad Ali | 10/12/2025 23:36:57 | 10/12/2025 23:42:49 | 10/13/2025 11:36:57 | DemFail observed in FIF0045 towards 10.74.121.188 @ Sceco | 10/12/2025 11:36:44 | Minor |  | DemFail | 10/12/2025 11:36:40 | P2 | 2G | dair | Sceco | TX NSA | FIF0045 | FLM_TE | [8 empty] | API | 10/12/2025 23:36:57 | 10/12/2025 23:42:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001597 | PCM-20251012-00002511 | TT-20251012-02592 | Telecom | Region_4 | JED1M7498 | JED0498 | Equipment | BTS_Cable | Replace Fiber Cable | Khaled Mohammad Abdallah | 10/12/2025 23:51:56 | 10/13/2025 08:28:24 | 10/13/2025 03:51:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7498-CA-L800-L900-P1-HUB-WDM @ Sceco | 10/12/2025 23:51:22 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 23:51:16 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7498 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/12/2025 23:51:56 |  | 10/13/2025 04:57:21 | 10/13/2025 04:57:23 | 10/13/2025 04:57:25 | 10/13/2025 08:28:24 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251013000039 | PCM-20251013-00000072 | TT-20251013-00073 | EM | [7 empty] | 10/13/2025 00:55:03 | 10/13/2025 00:55:03 | 10/13/2025 04:55:03 | NE_COMMU_GNE_SWITCH at USH-SEC0030_HYB @ Sceco_STB_Rental | 10/13/2025 00:53:06 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/13/2025 00:53:03 | P1 | DWDM |  | Sceco_STB_Rental | DWDM NSA | USH | FLM_EM | [5 empty] | NE USH-SEC0030_HYB's current GNE has been switched to standby GNE |  |  | API | 10/13/2025 00:55:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000051 | PCM-20251013-00000085 | TT-20251012-00716 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/13/2025 01:03:10 | 10/17/2025 17:34:12 | 10/13/2025 07:03:10 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/12/2025 08:15:21 | Major | 7654 | CELL OPERATION DEGRADED | 10/12/2025 08:15:09 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251012-00000673 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/13/2025 01:03:10 | 10/13/2025 09:43:48 | 10/17/2025 17:34:06 |  |  | 10/17/2025 17:34:12 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000056 | PCM-20251013-00000094 | TT-20251013-00084 | Reference_telecom | Region_4 | JED1M7839 | JED0839 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/13/2025 01:16:17 | 10/13/2025 14:28:09 | 10/13/2025 05:16:17 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1M7839-CA-L900-P1-VIP @ Sceco | 10/13/2025 00:53:54 | Critical | 7654 | CELL OPERATION DEGRADED | 10/13/2025 00:53:43 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7839 | FLM_TE |  |  | PCM-20251013-00000084 | FLM need to check VSWR at site. | FLM need to check VSWR at site. |  |  |  | API | 10/13/2025 01:16:17 | 10/13/2025 12:38:14 | 10/13/2025 14:28:03 |  |  | 10/13/2025 14:28:09 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000063 | PCM-20251013-00000102 | TT-20251013-00106 | Reference_telecom | Region_1 | QRY2605 | QRY2605 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/13/2025 01:22:20 | 10/13/2025 01:22:22 | 10/13/2025 13:22:20 | RF Unit RX Channel RTWP/RSSI Unbalanced at QRY2605-P3-USF_SRAN @ Sceco | 10/12/2025 22:22:08 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/12/2025 22:22:05 | P3 | SRAN | quriyat | Sceco | 2G NSA | QRY2605 | FLM_TE | [8 empty] | API | 10/13/2025 01:22:20 | 10/13/2025 01:22:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000104 | PCM-20251013-00000282 | TT-20251013-00287 | EM | Region_2 | RIY2334 | RIY2334 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/13/2025 02:13:49 | 10/22/2025 17:49:37 | 10/13/2025 14:13:49 | high temprature 32 at RIY2334-P2_SRAN-PC @ Sceco | 10/13/2025 02:09:36 | Minor | 65102 | high temprature 32 | 10/13/2025 02:02:57 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2334 | FLM_EM | [8 empty] | API | 10/13/2025 02:13:49 | 10/22/2025 17:49:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000108 | PCM-20251013-00000288 | TT-20251013-00293 | EM | Region_2 | RIY2442 | RIY2442 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/13/2025 02:14:02 | 10/13/2025 03:11:42 | 10/13/2025 14:14:02 | Door opening alarm at RIY2442-P3_SRAN @ Sceco | 10/13/2025 02:13:36 | Minor | 65101 | Door opening alarm | 10/13/2025 02:03:16 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2442 | FLM_EM | [8 empty] | API | 10/13/2025 02:14:02 | 10/13/2025 03:11:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000138 | PCM-20251013-00000430 | TT-20251013-00434 | EM | Region_2 | RIY2913 | RIY2913 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Moin Uddin | 10/13/2025 02:20:42 | 10/16/2025 12:37:41 | 10/13/2025 14:20:42 | Mains Failure at RIY2913-P3_SRAN-PC @ Sceco | 10/13/2025 02:19:05 | Minor | 65109 | Mains Failure | 10/13/2025 02:08:26 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2913 | FLM_EM | [8 empty] | API | 10/13/2025 02:20:42 | 10/13/2025 11:23:18 | 10/13/2025 18:11:04 | 10/13/2025 18:11:08 | 10/13/2025 18:11:11 | 10/16/2025 12:37:41 |  | Moin Uddin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000160 | PCM-20251013-00000476 | TT-20251013-00497 | EM | Region_6 | BHAB2334 | BHAB2334 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 02:34:40 | 10/13/2025 08:18:26 | 10/13/2025 14:34:40 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at BHAB2334-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/13/2025 02:27:43 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/13/2025 02:26:34 | P3 | 2G | Albaha | Generator_SG | 2G NSA | BHAB2334 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/13/2025 02:34:40 | 10/13/2025 08:18:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000166 | PCM-20251013-00000485 | TT-20251013-00506 | EM | Region_6 | BHAB1M8011 | BHAB2011 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 02:39:50 | 10/13/2025 08:18:27 | 10/13/2025 14:39:50 | RECTIFIER MODULE FAILURE at BHAB1M8011-CA-L800-SBTS-P3 @ Generator_SG | 10/13/2025 02:31:43 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/13/2025 02:31:32 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8011 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/13/2025 02:39:50 | 10/13/2025 08:18:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000173 | PCM-20251013-00000495 | TT-20251013-00489 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 02:48:41 | 10/13/2025 09:32:48 | 10/13/2025 08:48:41 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/13/2025 02:24:39 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/13/2025 02:24:31 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251013-00000472 | FLM need to check ALD and VSWR at site. | FLM need to check ALD and VSWR at site. |  |  |  | API | 10/13/2025 02:48:41 | 10/13/2025 09:32:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000174 | PCM-20251013-00000496 | TT-20251013-00503 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/13/2025 02:49:06 | 10/17/2025 17:34:01 | 10/13/2025 08:49:06 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/13/2025 02:31:42 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/13/2025 02:31:34 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251013-00000482 | FLM need to check ALD and VSWR at site. | FLM need to check ALD and VSWR at site. |  |  |  | API | 10/13/2025 02:49:06 | 10/13/2025 09:43:49 | 10/17/2025 17:33:55 |  |  | 10/17/2025 17:34:01 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000176 | PCM-20251013-00000499 | TT-20251013-00520 | EM | Region_6 | BHAB1M8442 | BHAB2442 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 02:51:12 | 10/13/2025 08:18:27 | 10/13/2025 14:51:12 | AIRCON 1 FAILURE at BHAB1M8442-G9-L8-SBTS-P3-WBB-G3 @ Generator_SG | 10/13/2025 02:44:06 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 02:42:52 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8442 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 02:51:12 | 10/13/2025 08:18:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000177 | PCM-20251013-00000498 | TT-20251013-00521 | EM | Region_6 | ABBS2064 | ABBS2064 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/13/2025 02:51:12 | 10/13/2025 19:12:15 | 10/13/2025 14:51:12 | SMOKE ALARM at ABBS2064-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/13/2025 02:43:21 | Minor | 7103 | SMOKE ALARM | 10/13/2025 02:43:05 | P3 | 2G | Baha | Generator_SG | 2G NSA | ABBS2064 | FLM_EM | [5 empty] | SMOKE ALARM |  |  | API | 10/13/2025 02:51:12 | 10/13/2025 19:12:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000178 | PCM-20251013-00000500 | TT-20251013-00522 | EM | Region_6 | MRD2071 | MRD2071 |  |  |  | Zia Ur Rahamn | 10/13/2025 02:51:42 | 10/13/2025 16:29:11 | 10/13/2025 14:51:42 | TAWER LIGHT at MRD2071-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/13/2025 02:44:38 | Minor | 7103 | TAWER LIGHT | 10/13/2025 02:43:25 | P3 | 2G | mohail | Generator_SG | 2G NSA | MRD2071 | FLM_EM | [5 empty] | TAWER LIGHT |  |  | API | 10/13/2025 02:51:42 | 10/13/2025 16:29:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251013000179 | PCM-20251013-00000501 | TT-20251013-00523 | EM | Region_6 | MRD1M8077 | MRD2077 |  |  |  | Muhammad Tayyab | 10/13/2025 02:51:43 | 10/16/2025 23:12:46 | 10/13/2025 14:51:43 | Tower light Alarm at MRD1M8077-G900-L800-L1800-P3-SBTS-WBB-G3 @ Generator_DG | 10/13/2025 02:44:34 | Minor | 7103 | Tower light Alarm | 10/13/2025 02:43:21 | P3 | 4G | namas | Generator_DG | LTE NSA | MRD1M8077 | FLM_EM | [5 empty] | Tower light Alarm |  |  | API | 10/13/2025 02:51:43 | 10/13/2025 10:11:35 | 10/16/2025 23:12:46 | [8 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000197 | PCM-20251013-00000534 | TT-20251013-00562 | EM | Region_6 | ABH0084 | ABH0084 |  |  |  | Khalid Frahan Almesetef | 10/13/2025 03:19:37 | 10/15/2025 11:52:54 | 10/13/2025 15:19:37 | AIRCON 1 FAILURE at ABH0084-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/13/2025 03:11:20 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 03:11:07 | P3 | 2G | abha | Sceco | 2G NSA | ABH0084 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 03:19:37 | 10/13/2025 16:03:26 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000198 | PCM-20251013-00000536 | TT-20251013-00563 | EM | Region_6 | ABH0023 | ABH0023 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/13/2025 03:20:08 | 10/13/2025 10:09:58 | 10/13/2025 15:20:08 | AIRCON 1 FAILURE at ABH0023-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/13/2025 03:11:46 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 03:11:46 | P2 | 2G | abha | Sceco | 2G NSA | ABH0023 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 03:20:08 | 10/13/2025 10:09:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Departed | CM20251013000200 | PCM-20251013-00000569 | TT-20251013-00595 | Telecom | Region_2 | RIY0445 | RIY0445 |  |  |  | Asad Ali Nadiq Khan | 10/13/2025 03:23:05 | 10/23/2025 17:35:49 | 10/13/2025 09:23:05 | NR Cell Unavailable at RIY0445-P1_SRAN @ Sceco | 10/13/2025 02:22:21 | Major | 29841 | NR Cell Unavailable | 10/13/2025 02:08:38 | P1 | SRAN | riyadh | Sceco | 5G SA | RIY0445 | FLM_TE | [8 empty] | API | 10/13/2025 03:23:05 | 10/13/2025 13:00:10 | 10/23/2025 16:31:23 | 10/23/2025 17:35:49 |  |  |  |  | ZAIN O-M |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000216 | PCM-20251013-00000603 | TT-20251013-00633 | EM | Region_6 | ABH0173 | ABH0173 |  |  |  | Khalid Frahan Almesetef | 10/13/2025 03:45:58 | 10/15/2025 11:52:54 | 10/13/2025 15:45:58 | AIRCON 1 FAILURE at ABH0173-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/13/2025 03:37:51 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 03:37:28 | P3 | 2G | abha | Sceco | 2G NSA | ABH0173 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 03:45:58 | 10/13/2025 16:03:27 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000217 | PCM-20251013-00000604 | TT-20251013-00634 | EM | Region_6 | ABH0174 | ABH0174 |  |  |  | Khalid Frahan Almesetef | 10/13/2025 03:45:59 | 10/15/2025 11:52:55 | 10/13/2025 15:45:59 | AIRCON 1 FAILURE at ABH0174-G9-L18-L21-NR2.6-P3 @ Generator_SG | 10/13/2025 03:38:00 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 03:37:37 | P3 | 2G | abha | Generator_SG | 2G NSA | ABH0174 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 03:45:59 | 10/13/2025 16:03:27 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000226 | PCM-20251013-00000618 | TT-20251013-00603 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/13/2025 04:00:11 | 10/21/2025 17:12:35 | 10/13/2025 10:00:11 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/13/2025 03:23:51 | Major | 7114 | CELL SERVICE PROBLEM | 10/13/2025 03:23:41 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251013-00000580 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/13/2025 04:00:11 | 10/13/2025 09:43:49 | 10/14/2025 11:20:51 | 10/14/2025 11:21:07 | 10/14/2025 11:24:06 | 10/14/2025 12:02:46 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000231 | PCM-20251013-00000627 | TT-20251012-01673 | Telecom | Region_6 | JEC1M7318 | JEC0318 | Equipment | BSS_HW_fault | Replace ALD | Ansir Iqbal Muhammad Iqbal | 10/13/2025 04:05:33 | 10/21/2025 23:37:29 | 10/13/2025 10:05:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at JEC1M7318-VIP-CA-L800 @ Generator_SG | 10/12/2025 16:18:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/12/2025 16:18:33 | VIP | 4G | baish | Generator_SG | 5G_Cell SA | JEC1M7318 | FLM_TE |  |  | PCM-20251013-00000595 | For HW approval kindly share over mail | For HW approval kindly share over mail |  |  |  | API | 10/13/2025 04:05:33 | 10/13/2025 05:39:43 | 10/14/2025 00:56:08 | 10/18/2025 01:45:30 | 10/21/2025 17:26:43 | 10/21/2025 23:37:29 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000262 | PCM-20251013-00000677 | TT-20251013-00716 | Reference_telecom | Region_1 | SMN0837 | SMN0837 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/13/2025 04:46:56 | 10/21/2025 11:37:53 | 10/13/2025 16:46:56 | RF Unit RX Channel RTWP/RSSI Unbalanced at SMN0837-P2-USF_SRAN @ Sceco | 10/13/2025 01:46:48 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/13/2025 01:46:43 | P2 | SRAN | hafr | Sceco | 2G NSA | SMN0837 | FLM_TE | [8 empty] | API | 10/13/2025 04:46:56 | 10/13/2025 07:24:35 | [6 empty] | CITC |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000312 | PCM-20251013-00000769 | TT-20251013-00801 | Telecom | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 06:01:51 | 10/19/2025 17:44:12 | 10/13/2025 12:01:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/13/2025 06:01:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 06:01:07 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2259 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 06:01:51 | 10/13/2025 19:51:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000329 | PCM-20251013-00000789 | TT-20251013-00823 | Reference_telecom | Region_6 | JIZ0412 | JIZ0412 |  |  |  | Mohammed Sideag Mohammed Ali | 10/13/2025 06:26:38 | 10/13/2025 12:10:03 | 10/13/2025 18:26:38 | DemFail observed in JIZ0412 towards 10.10.157.70 @ Sceco | 10/12/2025 18:27:30 | Minor |  | DemFail | 10/12/2025 18:26:17 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0412 | FLM_TE | [8 empty] | API | 10/13/2025 06:26:38 | 10/13/2025 12:10:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000330 | PCM-20251013-00000792 | TT-20251013-00826 | Reference_telecom | Region_4 | JED2899 | JED2899 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 06:29:37 | 10/19/2025 12:56:50 | 10/13/2025 18:29:37 | BASE STATION INFORMATION (No module fan detected) at JED2899-G9-L8-L18-L21-NR2.6-SBTS -P3 @ Sceco | 10/13/2025 04:27:20 | Minor | 7115 | BASE STATION INFORMATION | 10/13/2025 04:27:17 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2899 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/13/2025 06:29:37 | 10/13/2025 19:51:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000333 | PCM-20251013-00000795 | TT-20251013-00830 | Reference_telecom | Region_2 | BUR6002 | BUR6002 |  |  |  | Raise Ahmed Nisar Ahmed | 10/13/2025 06:32:13 | 10/13/2025 22:53:30 | 10/13/2025 12:32:13 | RFC Port Underpower at BUR6002-DCU1 @ Sceco | 10/12/2025 23:42:14 | Major | 29803 | RFC Port Underpower | 10/12/2025 23:42:09 | VIP | SRAN | buraidah | Sceco | 2G NSA | BUR6002 | FLM_TE | [8 empty] | API | 10/13/2025 06:32:13 | 10/13/2025 22:53:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000341 | PCM-20251013-00000807 | TT-20251013-00844 | Reference_telecom | Region_4 | TAF0287 | TAF0287 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 10/13/2025 06:43:42 | 10/14/2025 21:04:45 | 10/13/2025 18:43:42 | BASE STATION INFORMATION (Unit temperature is high) at TAF0287-GSM-P3 @ Sceco | 10/13/2025 06:03:23 | Minor | 7115 | BASE STATION INFORMATION | 10/13/2025 06:03:12 | P3 | 2G | taif | Sceco | 2G NSA | TAF0287 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/13/2025 06:43:42 | 10/14/2025 20:35:41 | 10/14/2025 21:04:38 |  |  | 10/14/2025 21:04:45 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000344 | PCM-20251013-00000811 | TT-20251013-00847 | Reference_telecom | Region_6 | WDS0503 | WDS0503 |  |  |  | Ahmed Mamdouh Helal Helal | 10/13/2025 06:45:45 | 10/13/2025 20:17:38 | 10/13/2025 18:45:45 | ReplaceableUnitMissing observed in WDS0503_01 towards 10.10.159.212 @ Sceco | 10/12/2025 18:47:32 | Minor |  | ReplaceableUnitMissing | 10/12/2025 18:45:16 | P3 | 2G | wadi dawasar | Sceco | TX NSA | WDS0503 | FLM_TE | [8 empty] | API | 10/13/2025 06:45:45 | 10/13/2025 20:17:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000350 | PCM-20251013-00000822 | TT-20251013-00857 | EM | Region_4 | JDMK1M8401 | JDMK2401 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/13/2025 06:54:33 | 10/23/2025 12:57:11 | 10/13/2025 18:54:33 | GENERATOR at JDMK1M8401-G9-L8-L18-L21-P3 @ Generator_SG | 10/13/2025 06:47:56 | Minor | 7103 | GENERATOR | 10/13/2025 06:46:04 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JDMK1M8401 | FLM_EM | [5 empty] | GENERATOR |  |  | API | 10/13/2025 06:54:33 | 10/23/2025 12:57:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000361 | PCM-20251013-00000841 | TT-20251013-00871 | Telecom | Region_2 | RIYB6029-CSG-01 | RIYB6029 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 07:03:52 | 10/13/2025 08:27:13 | 10/13/2025 11:03:52 | The Device is offline at RIYB6029-CSG-01 @ Sceco | 10/13/2025 07:03:19 | Critical | 101-7 | The Device is offline | 10/13/2025 07:03:17 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6029-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:03:52 | 10/13/2025 08:27:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000364 | PCM-20251013-00000844 | TT-20251013-00875 | Telecom | Region_2 | RIYA6114-CSG-01 | RIYB6114 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 07:05:25 | 10/13/2025 08:27:14 | 10/13/2025 11:05:25 | The Device is offline at RIYA6114-CSG-01 @ Sceco_STB | 10/13/2025 07:05:04 | Critical | 101-7 | The Device is offline | 10/13/2025 07:05:02 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN SA | RIYA6114-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:05:25 | 10/13/2025 08:27:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000365 | PCM-20251013-00000846 | TT-20251013-00876 | Telecom | Region_2 | RIYD6022-CSG-01 | RIYD6022 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/13/2025 07:05:25 | 10/13/2025 13:10:44 | 10/13/2025 11:05:25 | The Device is offline at RIYD6022-CSG-01 @ Sceco_STB | 10/13/2025 07:05:01 | Critical | 101-7 | The Device is offline | 10/13/2025 07:05:00 | P3 | IPRAN | riyadh | Sceco_STB | IPRAN SA | RIYD6022-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:05:25 | 10/13/2025 13:10:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000366 | PCM-20251013-00000845 | TT-20251013-00873 | Telecom | Region_2 | RIYA6111-CSG-01 | RIYA6111 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 07:05:25 | 10/13/2025 08:27:14 | 10/13/2025 11:05:25 | The Device is offline at RIYA6111-CSG-01 @ Sceco_STB | 10/13/2025 07:05:04 | Critical | 101-7 | The Device is offline | 10/13/2025 07:05:02 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN SA | RIYA6111-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:05:25 | 10/13/2025 08:27:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000367 | PCM-20251013-00000847 | TT-20251013-00874 | Telecom | Region_2 | RIYD6030-CSG-01 | RIYB6030 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 07:05:25 | 10/13/2025 08:27:14 | 10/13/2025 11:05:25 | The Device is offline at RIYD6030-CSG-01 @ Sceco_STB | 10/13/2025 07:05:01 | Critical | 101-7 | The Device is offline | 10/13/2025 07:05:00 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN SA | RIYD6030-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:05:25 | 10/13/2025 08:27:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251013000368 | PCM-20251013-00000850 | TT-20251013-00880 | EM | [7 empty] | 10/13/2025 07:07:58 | 10/13/2025 07:42:38 | 10/13/2025 11:07:58 | link down between FRIY0001-2 to FRIY0005 & FRIY0005 NCE NODE ISOLATED | 10/13/2025 07:06:22 | Critical | 0-1 | NE_COMMU_BREAK | 10/13/2025 07:06:19 | P3 | DWDM |  | Sceco | DWDM NSA | FRIY0005 | FLM_EM | [5 empty] | Communication with common NE FRIY0005 is interrupted |  |  | API | 10/13/2025 07:07:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000371 | PCM-20251013-00000855 | TT-20251013-00119 | Reference_telecom | Region_4 | TAF1M3159 | TAF0159 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/13/2025 07:10:07 | 10/14/2025 09:50:27 | 10/13/2025 13:10:07 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TAF1M3159-P2 @ Sceco | 10/13/2025 01:02:30 | Major | 7771 | WCDMA CELL OUT OF USE | 10/13/2025 01:00:20 | P2 | 3G | taif | Sceco | 3G SA | TAF1M3159 | FLM_TE |  |  | PCM-20251013-00000117 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/13/2025 07:10:07 | 10/14/2025 09:50:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000373 | PCM-20251013-00000857 | TT-20251013-00681 | Telecom | Region_4 | JED1MN2910 | JED2910 | Equipment | SW | Issue was solved after softaware configuration | Abdullah Ahmad Mohammad Abdelsheekh | 10/13/2025 07:10:21 | 10/23/2025 16:08:29 | 10/13/2025 13:10:21 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/13/2025 04:15:52 | Major | 7114 | CELL SERVICE PROBLEM | 10/13/2025 04:15:45 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE |  |  | PCM-20251013-00000652 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/13/2025 07:10:21 | 10/20/2025 11:59:51 | 10/23/2025 13:31:56 | 10/23/2025 13:31:59 | 10/23/2025 13:32:03 | 10/23/2025 16:08:29 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000383 | PCM-20251013-00000871 | TT-20251013-00889 | Telecom | Region_4 | JED0229 | JED0229 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 07:13:40 | 10/19/2025 17:44:14 | 10/13/2025 13:13:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/13/2025 07:13:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 07:12:50 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0229 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 07:13:40 | 10/13/2025 09:36:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000388 | PCM-20251013-00000880 | TT-20251013-00825 | Telecom | Region_4 | JED1U6049 | JED6149 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/13/2025 07:14:50 | 10/17/2025 17:33:49 | 10/13/2025 13:14:50 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at JED1U6049-P3-CA @ Sceco | 10/13/2025 06:20:24 | Major | 7654 | CELL OPERATION DEGRADED | 10/13/2025 06:20:17 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6049 | FLM_TE |  |  | PCM-20251013-00000791 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/13/2025 07:14:50 | 10/13/2025 09:43:50 | 10/17/2025 17:33:42 |  |  | 10/17/2025 17:33:49 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000395 | PCM-20251013-00000883 | TT-20251013-00898 | Telecom | Region_2 | RIYD6030-CSG-01 | RIYB6030 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 07:16:15 | 10/13/2025 08:27:15 | 10/13/2025 19:16:15 | Chassis Fail at RIYD6030-CSG-01 @ Sceco_STB | 10/13/2025 07:16:01 | Minor | 101-2505202 | Chassis Fail | 10/13/2025 07:09:30 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | RIYD6030-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:16:15 | 10/13/2025 08:27:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000396 | PCM-20251013-00000887 | TT-20251013-00890 | EM | Region_2 | SHIR2S5217 | SHIR0217 | Enviroment | Bill | SCECO was restored after Bill was paid by the owner | Mubashar Farooq Abdul Majeed | 10/13/2025 07:19:02 | 10/13/2025 10:30:16 | 10/13/2025 13:19:02 | 1(3G/LTE) sites down under SHIR0217-P3/RY1RNCH05 @ Sceco | 10/13/2025 07:10:44 | Major | 22214 | NodeB Unavailable | 10/13/2025 07:10:41 | P3 | 3G | riyadh | Sceco | 3G_LTE SA | SHIR0217-P3 | FLM_EM | SHIR0217 | Results: DOWN SITE HUB SHIR0217-P3 SHIR0217 Summary: Hub: SHIR0217, Down Count: 1, Down Sites: SHIR0217-P3 Alarm Summary: SHIR0217 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/13/2025 07:19:02 | 10/13/2025 08:52:32 | 10/13/2025 08:57:24 | 10/13/2025 10:16:26 | 10/13/2025 10:16:29 | 10/13/2025 10:30:16 |  | Mubashar Farooq Abdul Majeed |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251013000402 | PCM-20251013-00000894 | TT-20251013-00900 | Telecom | Region_4 | SJED1S7341 | SJED0341 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 07:23:32 | 10/13/2025 08:05:51 | 10/13/2025 13:23:32 | 1(LTE) sites down under SJED0341-CA @ Sceco | 10/13/2025 07:15:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/13/2025 07:15:09 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0341-CA | FLM_TE | SJED0341 | Results: DOWN SITE HUB SJED0341-CA SJED0341 Summary: Hub: SJED0341, Down Count: 1, Down Sites: SJED0341-CA Alarm Summary: SJED0341 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.8.236:8080] [URL:http://10.96.8.236:8080/NE3S/1.0/] | sites down |  | API | 10/13/2025 07:23:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000404 | PCM-20251013-00000896 | TT-20251013-00916 | EM | Region_2 | RIYA6199 | RIYA6199 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/13/2025 07:25:33 | 10/13/2025 11:44:41 | 10/13/2025 19:25:33 | Mains Failure at RIYA6199-P3_SRAN @ Sceco | 10/13/2025 07:21:16 | Minor | 65109 | Mains Failure | 10/13/2025 07:15:20 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6199 | FLM_EM | [8 empty] | API | 10/13/2025 07:25:33 | 10/13/2025 11:44:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251013000416 | PCM-20251013-00000920 | TT-20251013-00923 | Telecom | Region_4 | SJED0340 | SJED0340 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 07:38:27 | 10/13/2025 07:43:02 | 10/13/2025 11:38:27 | 3(2G) 2(LTE) 3(5G) sites down under SJED1S7342-CA @ Sceco | 10/13/2025 07:24:41 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/13/2025 07:24:39 | P3 | SRAN | jeddah | Sceco | 2G_LTE SA | SJED0342-CA LTE,SJED0340-CA LTE,JED2313-P3 2G,JED2177-P3 2G,JED2030-FWA-P1-VIP 2G | FLM_EM | SJED0340 | Dear team , Hub: SJED0340 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251013-00000906 | Dear team , Hub: SJED0340 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: SJED0340 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/13/2025 07:38:27 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000417 | PCM-20251013-00000923 | TT-20251013-00946 | EM | Region_1 | SAK2953 | SAK2953 | Enviroment | Rectifier Module | Change rectifer module | Mohamed Amjad Muhammad | 10/13/2025 07:38:58 | 10/17/2025 14:01:42 | 10/13/2025 19:38:58 | Minor Rec alarm at SAK2953-P3-USF_SRAN @ Sceco | 10/13/2025 07:31:00 | Minor | 65108 | Minor Rec alarm | 10/13/2025 07:28:43 | P3 | SRAN | sakaka | Sceco | 2G NSA | SAK2953 | FLM_EM | [8 empty] | API | 10/13/2025 07:38:58 | 10/13/2025 11:44:05 | 10/17/2025 14:01:11 |  |  | 10/17/2025 14:01:42 |  | Mohamed Amjad Muhammad | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251013000423 | PCM-20251013-00000934 | TT-20251013-00948 | Reference_telecom | Region_4 | SJED0340 | SJED0340 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 07:42:39 | 10/13/2025 19:51:57 | 10/13/2025 19:42:39 | SJED1W0340, SJED1W0341, SJED1W0342 complete down | 10/13/2025 07:28:22 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/13/2025 07:28:22 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0340, SJED1W0341, SJED1W0342 | FLM_EM | SJED0340 | Dear team , Hub: SJED0340 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251013-00000927 | Dear team , Hub: SJED0340 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: SJED0340 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/13/2025 07:42:39 | 10/13/2025 19:51:43 | 10/13/2025 19:51:50 | 10/13/2025 19:51:54 | 10/13/2025 19:51:57 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000434 | PCM-20251013-00000952 | TT-20251013-00970 | Reference_telecom | Region_4 | RAB0473-SF-CSG-01 | RAB0473 |  |  |  | Khizer Hayat | 10/13/2025 07:54:58 | 10/13/2025 11:15:00 | 10/13/2025 19:54:58 | Optical Invalid at RAB0473-SF-CSG-01 TT-20251003-01382 @ Sceco | 10/13/2025 04:09:15 | Minor | 101-2505224 | Optical Invalid | 10/13/2025 04:08:56 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | RAB0473-SF-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 07:54:58 | 10/13/2025 11:15:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000440 | PCM-20251013-00000962 | TT-20251013-00981 | Reference_telecom | Region_4 | JED0399-ZJe01-CSG-01 | JED0399 |  |  |  | Mohammed Ramadan A Abu Abid | 10/13/2025 08:02:20 | 10/13/2025 08:04:28 | 10/13/2025 20:02:20 | Optical Invalid at JED0399-ZJe01-CSG-01 TT-20241226-00968 @ Sceco | 10/13/2025 00:50:07 | Minor | 101-2505224 | Optical Invalid | 10/13/2025 00:49:45 | P1 | IPRAN | jeddah | Sceco | IPRAN NSA | JED0399-ZJe01-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 08:02:20 | 10/13/2025 08:04:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000454 | PCM-20251013-00000976 | TT-20251013-00990 | Telecom | Region_5 | MAK1U6934 | MAK6034 |  |  |  | Atif Javed Javed Hussain | 10/13/2025 08:08:24 | 10/16/2025 11:25:57 | 10/13/2025 14:08:24 | CELL FAULTY (VSWR major alarm) at MAK1U6934-P3-CA @ Sceco | 10/13/2025 08:03:59 | Major | 7653 | CELL FAULTY | 10/13/2025 08:03:49 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6934 | FLM_TE | [5 empty] | VSWR major alarm |  |  | API | 10/13/2025 08:08:24 | 10/16/2025 11:25:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000478 | PCM-20251013-00001013 | TT-20251013-01032 | Reference_EM | Region_2 | RIY2804 | RIY2804 | Enviroment | Genset failure_Pump | Change Fuel Pump | Amr Abbas Zaghloul Abbas | 10/13/2025 08:38:54 | 10/15/2025 23:44:53 | 10/13/2025 14:38:54 | Mains Failure at RIY2804-P1-VIP_SRAN-PC @ Generator_SG | 10/13/2025 08:28:50 | Major | 65109 | Mains Failure | 10/13/2025 08:28:45 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2804 | FLM_EM | [8 empty] | API | 10/13/2025 08:38:54 | 10/13/2025 09:16:51 | 10/15/2025 23:44:31 |  |  | 10/15/2025 23:44:53 |  | Amr Abbas Zaghloul Abbas |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000480 | PCM-20251013-00001014 | TT-20250907-01722 | Reference_telecom | Region_6 | BHAB9035 | BHAB9035 |  |  |  | Fawad Khan | 10/13/2025 08:39:52 | 10/13/2025 09:57:50 | 10/13/2025 20:39:52 | NEC MW Observing Power Supply at BHAB9035-1(10.154.171.195) | 08/10/2025 09:16:40 | Minor |  | LOF | 08/10/2025 09:16:40 | P1 | Repeater | namas | Sceco_STB | TX NSA | BHAB9035-1(10.154.171.195) | FLM_TE |  |  | PCM-20251013-00000050 | Dear FLM, Thanks to share all TS steps done from your side | Dear FLM, Thanks to share all TS steps done from your side |  |  |  | API | 10/13/2025 08:39:52 | 10/13/2025 09:57:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000483 | PCM-20251013-00001018 | TT-20251013-01036 | EM | Region_6 | BHAB1M8041 | BHAB2041 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 08:45:36 | 10/13/2025 09:29:32 | 10/13/2025 20:45:36 | COMMERCIAL POWER FAILURE at BHAB1M8041-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/13/2025 08:37:23 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/13/2025 08:37:12 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8041 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/13/2025 08:45:36 | 10/13/2025 09:29:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000498 | PCM-20251013-00001038 | TT-20251013-01056 | Telecom | Region_4 | JDAP1M7940 | JDAP0940 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/13/2025 08:59:33 | 10/21/2025 18:14:38 | 10/13/2025 14:59:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/13/2025 08:58:50 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 08:58:40 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JDAP1M7940 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 08:59:33 | 10/20/2025 14:29:27 | 10/21/2025 18:14:32 |  |  | 10/21/2025 18:14:38 |  | Mohamed Farag Abdelbary | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000507 | PCM-20251013-00001061 | TT-20251013-01057 | Reference_telecom | Region_1 | HFF2U6708 | HFF6008 |  |  |  | Mohamed Magdy Fouad Zayed | 10/13/2025 09:07:40 | 10/13/2025 11:18:19 | 10/13/2025 21:07:40 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6708-P1-SHOP @ Sceco | 10/13/2025 05:59:51 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/13/2025 05:59:47 | P1 | 4G | hafouf | Sceco | 2G NSA | HFF2U6708 | FLM_TE |  |  | PCM-20251013-00001039 | Dear FLM, For Cell Rx Channel interference noise power unbalance, please need physical HC to verify below. 1-Jumpers. 2-Connectors. 3-Antenna & RRU ports for damage. 4-Change antenna port if any free port available. 5-Remake connectors. | Display Board Manufacturing Information --------------------------------------- Type = WD5MJRUBC30 Serial Number = 2102310SSQ4MF1007431 |  |  |  | API | 10/13/2025 09:07:40 | 10/13/2025 11:18:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013000517 | PCM-20251013-00001081 | TT-20251013-01098 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 09:14:32 | 10/13/2025 09:14:32 | 10/13/2025 15:14:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/13/2025 09:13:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 09:13:21 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 09:14:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000520 | PCM-20251013-00001089 | TT-20251013-01104 | Telecom | Region_6 | JIZ0018 | JIZ0018 | Equipment | FAN Cleaning | Clean FAN | Osama Hadi | 10/13/2025 09:17:08 | 10/14/2025 10:44:30 | 10/13/2025 21:17:08 | BASE STATION INFORMATION (Fan vendor not detected) at JIZ0018-G9-L8-L18-L21-NR2.6-NR3.5-SBTS -P2 @ Sceco | 10/13/2025 09:11:07 | Minor | 7115 | BASE STATION INFORMATION | 10/13/2025 09:08:35 | P2 | 2G | jizan | Sceco | 2G NSA | JIZ0018 | FLM_TE | [5 empty] | Fan vendor not detected |  |  | API | 10/13/2025 09:17:08 | 10/13/2025 14:40:33 | 10/14/2025 10:43:59 |  |  | 10/14/2025 10:44:30 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000526 | PCM-20251013-00001102 | TT-20251013-01118 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/13/2025 09:23:19 | 10/21/2025 23:22:28 | 10/13/2025 15:23:19 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/13/2025 09:12:56 | Major | 65102 | high temprature 32 | 10/13/2025 09:12:52 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/13/2025 09:23:19 | 10/21/2025 23:22:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000531 | PCM-20251013-00001111 | TT-20251013-01125 | Telecom | Region_4 | JDJZ0772 | JDJZ0772 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/13/2025 09:28:59 | 10/13/2025 19:47:07 | 10/13/2025 21:28:59 | ODU CPU / Cable Open at JDJZ0772_2 on 10.154.113.12 @ Generator_DG | 10/13/2025 09:27:56 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/13/2025 09:24:43 | P3 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0772 | FLM_TE | [8 empty] | API | 10/13/2025 09:28:59 | 10/13/2025 19:47:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000557 | PCM-20251013-00001155 | TT-20251012-02270 | Reference_telecom | Region_6 | WDS0277-SF-CSG-01 | WDS0277 |  |  |  | Ahmed Mamdouh Helal Helal | 10/13/2025 09:53:20 | 10/13/2025 20:17:40 | 10/13/2025 15:53:20 | MW Link Down at WDS0277-SF-CSG-01 ¦¦ ref TT-20250817-00807 @ Sceco_STB | 10/12/2025 10:28:10 | Major | 101-1102218 | Alarm of failed LAG negotiation | 10/12/2025 10:28:03 | P1 | IPRAN | wadi dawasar | Sceco_STB | IPRAN NSA | WDS0277-SF-CSG-01 | FLM_TE |  | Thanks to keep till reroute done WDS0503-WDS0499 and configure protection | PCM-20251013-00001052 | Thanks to keep till reroute done WDS0503-WDS0499 and configure protection | Thanks to keep till reroute done WDS0503-WDS0499 and configure protection |  |  |  | API | 10/13/2025 09:53:20 | 10/13/2025 20:17:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000558 | PCM-20251013-00001156 | TT-20251013-01119 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/13/2025 09:53:50 | 10/21/2025 18:14:50 | 10/13/2025 15:53:50 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/13/2025 09:16:54 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/13/2025 09:16:43 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251013-00001103 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/13/2025 09:53:50 | 10/20/2025 14:29:26 | 10/21/2025 18:14:44 |  |  | 10/21/2025 18:14:50 |  | Mohamed Farag Abdelbary | Zain Site Management |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000575 | PCM-20251013-00001201 | TT-20251013-01222 | EM | Region_4 | NNL0139 | NNL0139 | Equipment | FAN Cleaning | Reset FAN | Basyouni Kotb Basyouni Eldabsha | 10/13/2025 10:16:04 | 10/15/2025 17:55:48 | 10/13/2025 16:16:04 | 1(2G/3G) sites down under NNL0139-P3/NNL0139-P3 @ Generator_SG | 10/13/2025 10:08:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/13/2025 10:08:04 | P3 | 2G | qunfuddah | Generator_SG | 2G_3G SA | NNL0139-P3 | FLM_EM | NNL0139 | Results: DOWN SITE HUB NNL0139-P3 NNL0139 Summary: Hub: NNL0139, Down Count: 1, Down Sites: NNL0139-P3 Alarm Summary: NNL0139 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/13/2025 10:16:04 | 10/13/2025 11:32:27 | 10/15/2025 17:55:42 |  |  | 10/15/2025 17:55:48 |  | Basyouni Kotb Basyouni Eldabsha |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000589 | PCM-20251013-00001237 | TT-20251012-01505 | MW_HC | Region_4 | FW317 | FW317 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 10:30:15 | 10/13/2025 19:51:37 | 10/13/2025 22:30:15 | As BO Requested MW Nokia Observing Performance issue For MW Link FW317-JED2568 | 10/12/2025 14:52:40 | Minor | 113388 | LOF | 10/12/2025 14:52:42 | P3 | Shop | jeddah | Sceco | TX NSA | FW317-JED2568 | FLM_TE |  |  | PCM-20251013-00001072 | Thanks to share complete data and HC time - RCA - Action details | Thanks to share complete data and HC time - RCA - Action details |  |  |  | API | 10/13/2025 10:30:15 | 10/13/2025 19:51:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000595 | PCM-20251013-00001248 | TT-20251013-01273 | EM | Region_2 | RIY2M2804 | RIY2804 | Enviroment | Genset failure_Pump | Change Fuel Pump | Amr Abbas Zaghloul Abbas | 10/13/2025 10:36:33 | 10/15/2025 23:44:25 | 10/13/2025 14:36:33 | 1(2G/LTE) sites down under RIY2804-P1-VIP/R2_RY1_HWBSC01 @ Generator_SG | 10/13/2025 10:28:13 | Critical | 21825 | CSL Fault | 10/13/2025 10:28:08 | VIP | 2G | riyadh | Generator_SG | 2G_LTE SA | RIY2804-P1-VIP | FLM_EM | RIY2804 | Results: DOWN SITE HUB RIY2804-P1-VIP RIY2804 Summary: Hub: RIY2804, Down Count: 1, Down Sites: RIY2804-P1-VIP Alarm Summary: RIY2804 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/13/2025 10:36:33 | 10/13/2025 11:34:38 | 10/15/2025 23:44:03 |  |  | 10/15/2025 23:44:25 |  | Amr Abbas Zaghloul Abbas |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000617 | PCM-20251013-00001302 | TT-20251013-01323 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/13/2025 11:03:33 | 10/13/2025 11:13:51 | 10/13/2025 23:03:33 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/13/2025 08:03:03 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/13/2025 08:03:00 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/13/2025 11:03:33 | 10/13/2025 11:13:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000621 | PCM-20251013-00001308 | TT-20251013-01330 | EM | Region_6 | BHAB1M7883 | BHAB0883 |  |  |  | Zia Ur Rahamn | 10/13/2025 11:05:06 | 10/13/2025 16:29:12 | 10/13/2025 23:05:06 | SHELTER DOOR OPEN at BHAB1M7883-G9-L8-SBTS-P3 @ Sceco | 10/13/2025 11:04:49 | Minor | 7103 | SHELTER DOOR OPEN | 10/13/2025 11:04:44 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7883 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/13/2025 11:05:06 | 10/13/2025 16:29:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000622 | PCM-20251013-00001309 | TT-20251013-01331 | Telecom | Region_6 | JIZ0186 | JIZ0186 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Mohammed Sideag Mohammed Ali | 10/13/2025 11:05:10 | 10/13/2025 19:33:37 | 10/13/2025 17:05:10 | PT::: As Per BO request need FLM to do HC in JIZ0186/R6 | 10/13/2025 11:04:43 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/13/2025 11:04:43 | P2 | 2G | jizan | Sceco | 2G_3G_LTE_5G NSA | JIZ0186 | FLM_TE | [8 empty] | API | 10/13/2025 11:05:10 | 10/13/2025 12:10:05 | 10/13/2025 14:23:37 | 10/13/2025 14:23:40 | 10/13/2025 14:23:42 | 10/13/2025 19:33:37 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000628 | PCM-20251013-00001319 | TT-20251013-01329 | Telecom | Region_4 | KMMD0761 | KMMD0761 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/13/2025 11:07:30 | 10/15/2025 11:27:04 | 10/13/2025 17:07:30 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at KMMD0761-GSM-P3 @ Sceco | 10/13/2025 10:59:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 10:59:31 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | KMMD0761 | FLM_TE |  |  | PCM-20251013-00001307 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/13/2025 11:07:30 | 10/13/2025 12:38:15 | 10/15/2025 11:26:58 |  |  | 10/15/2025 11:27:04 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000631 | PCM-20251013-00001324 | TT-20251013-01304 | Reference_telecom | Region_2 | RIYC2U6725 | RIYC6025 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 11:11:20 | 10/13/2025 18:00:05 | 10/13/2025 23:11:20 | Cell RX Channel Interference Noise Power Unbalanced at RIYC2U6725-L800-CA-P3 @ Sceco | 10/13/2025 07:50:16 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/13/2025 07:50:14 | P2 | 4G | riyadh | Sceco | 2G NSA | RIYC2U6725 | FLM_TE |  | Dears Kindly check HW | PCM-20251013-00001273 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/13/2025 11:11:20 | 10/13/2025 18:00:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000642 | PCM-20251013-00001344 | TT-20251013-01386 | Reference_EM | Region_4 | JED2979 | JED2979 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/13/2025 11:21:43 | 10/13/2025 12:21:24 | 10/13/2025 15:21:43 | 1(2G/LTE/5G) sites down under JED2979-P1-VIP (REF_TT-20251013-01274) | 10/13/2025 10:33:36 | Critical | 7706 | BTS O&M LINK FAILURE | 10/13/2025 10:33:36 | VIP | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G SA | JED2979-P1-VIP | FLM_EM | JED2979 | Results: DOWN SITE HUB JED2979-P1-VIP JED2979 Summary: Hub: JED2979, Down Count: 1, Down Sites: JED2979-P1-VIP Alarm Summary: JED2979 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/13/2025 11:21:43 | 10/13/2025 11:30:09 | 10/13/2025 12:21:04 | 10/13/2025 12:21:08 | 10/13/2025 12:21:10 | 10/13/2025 12:21:24 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251013000660 | PCM-20251013-00001371 | TT-20251001-01893 | Reference_telecom | Region_4 | JED0215 | JED0215 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/13/2025 11:38:02 | 10/13/2025 18:11:04 | 10/13/2025 23:38:02 | LagPortDown observed in JED0215 towards 10.10.149.4 @ Sceco | 10/01/2025 07:19:36 | Minor |  | LagPortDown | 10/01/2025 07:16:32 | P2 | 2G | jeddah | Sceco | TX NSA | JED0215 | FLM_TE |  |  | PCM-20251013-00001314 | follow Planning request and update Dear Hani, Please try below options. JED0572 JED0883 JED0113 | follow Planning request and update Dear Hani, Please try below options. JED0572 JED0883 JED0113 |  |  |  | API | 10/13/2025 11:38:02 | 10/13/2025 14:37:17 | 10/13/2025 18:10:59 | 10/13/2025 18:11:01 | 10/13/2025 18:11:04 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000673 | PCM-20251013-00001387 | TT-20251013-01443 | Telecom | Region_2 | RIYB6031-CSG-01 | RIYB6031 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/13/2025 11:51:33 | 10/13/2025 13:10:45 | 10/13/2025 15:51:33 | The Device is offline at RIYB6031-CSG-01 @ Sceco | 10/13/2025 11:51:19 | Critical | 101-7 | The Device is offline | 10/13/2025 11:51:17 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6031-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 11:51:33 | 10/13/2025 13:10:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000674 | PCM-20251013-00001388 | TT-20251013-01444 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/13/2025 11:51:34 | 10/13/2025 13:10:45 | 10/13/2025 15:51:34 | The Device is offline at RIYB6066-CSG-01 @ Sceco | 10/13/2025 11:51:19 | Critical | 101-7 | The Device is offline | 10/13/2025 11:51:17 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/13/2025 11:51:34 | 10/13/2025 13:10:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000692 | PCM-20251013-00001416 | TT-20251013-01224 | Reference_telecom | Region_2 | RIY0316 | RIY0316 | Enviroment | Fire Alarm | Reset Fire Pannel | Tanveer Ahmad Fateh Muhammad | 10/13/2025 12:02:21 | 10/19/2025 12:42:24 | 10/14/2025 00:02:21 | External Clock Reference Problem at RIY0316-P3_SRAN @ Sceco | 10/13/2025 07:15:04 | Minor | 26262 | External Clock Reference Problem | 10/13/2025 07:11:39 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY0316 | FLM_EM | RIY0316 | Hub:- RIY0316 we were suspecting power issue at hub site, kindly send FLM_EM team to check and resolve issue at site. | PCM-20251013-00001298 | Hub:- RIY0316 we were suspecting power issue at hub site, kindly send FLM_EM team to check and resolve issue at site. | Hub:- RIY0316 we were suspecting power issue at hub site, kindly send FLM_EM team to check and resolve issue at site. |  |  |  | API | 10/13/2025 12:02:21 | 10/14/2025 13:46:09 | 10/19/2025 12:38:11 | 10/19/2025 12:38:17 | 10/19/2025 12:38:22 | 10/19/2025 12:42:24 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000699 | PCM-20251013-00001424 | TT-20251013-01226 | Reference_telecom | Region_2 | RIY2796 | RIY2796 |  |  |  | Kadri Jalal Mohammed Asmail | 10/13/2025 12:05:40 | 10/13/2025 13:10:19 | 10/14/2025 00:05:40 | External Clock Reference Problem at RIY2796-P2_SRAN-PC @ Sceco | 10/13/2025 07:16:41 | Minor | 26262 | External Clock Reference Problem | 10/13/2025 07:13:20 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2796 | FLM_EM | RIY2796 |  | PCM-20251013-00001310 | Hub:- RIY2796 we were suspecting power issue at hub site, kindly send FLM_EM team to check and resolve issue at site. | Hub:- RIY2796 we were suspecting power issue at hub site, kindly send FLM_EM team to check and resolve issue at site. |  |  |  | API | 10/13/2025 12:05:40 | 10/13/2025 13:10:19 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000712 | PCM-20251013-00001441 | TT-20251013-01502 | Reference_EM | Region_2 | RIYB2U6173a | RIYB6073 |  |  |  | Kadri Jalal Mohammed Asmail | 10/13/2025 12:19:28 | 10/13/2025 13:10:20 | 10/13/2025 18:19:28 | Major Rec. alarm at RIYB2U6173A-P1-DIA-SHOP @ Sceco | 10/13/2025 12:09:12 | Major | 65107 | Major Rec. alarm | 10/13/2025 12:09:10 | P1 | 2G | riyadh | Sceco | 2G NSA | RIYB2U6173A | FLM_EM | [8 empty] | API | 10/13/2025 12:19:28 | 10/13/2025 13:10:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251013000717 | PCM-20251013-00001449 | TT-20251013-01510 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/13/2025 12:23:03 | 10/13/2025 12:23:03 | 10/13/2025 18:23:03 | Physically identify the Meqyas White Box | 10/13/2025 12:22:51 | Major | 4205 | The interface traffic exceeds the threshold | 10/13/2025 12:22:51 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | Physically identify the Meqyas White Box | FLM_TE | [5 empty] | Physically identify the Meqyas White Box |  |  | API | 10/13/2025 12:23:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251013000725 | PCM-20251013-00001465 | TT-20251013-01528 | Telecom | Region_4 | JED0008 | JED0008 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/13/2025 12:36:56 | 10/15/2025 11:30:22 | 10/14/2025 00:36:56 | p0_MW Link Down at JED0008 to JED0211 ¦¦ ref TT-20250922-01119 | 10/13/2025 12:34:53 | Minor | 15269 | LOS | 10/13/2025 12:34:56 | VIP | 2G | jeddah | Sceco | IPRAN NSA | JED0008 | FLM_TE | [8 empty] | API | 10/13/2025 12:36:56 | 10/15/2025 11:13:33 | 10/15/2025 11:30:18 | 10/15/2025 11:30:19 | 10/15/2025 11:30:22 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000735 | PCM-20251013-00001479 | TT-20251013-01543 | Telecom | Region_6 | ARS0017 | ARS0017 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/13/2025 12:41:32 | 10/16/2025 01:48:15 | 10/14/2025 00:41:32 | p0_MW_Link Down at ARS0017 to JIZ0245 ¦¦ ref TT-20250916-02400 | 10/13/2025 12:40:25 | Minor | 15269 | LOS | 10/13/2025 12:40:27 | P1 | 2G | jizan | Sceco | IPRAN NSA | ARS0017 | FLM_TE | [8 empty] | API | 10/13/2025 12:41:32 | 10/13/2025 16:02:04 | 10/15/2025 20:16:26 | 10/15/2025 20:16:38 | 10/15/2025 20:16:51 | 10/16/2025 01:48:15 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000743 | PCM-20251013-00001493 | TT-20251013-01549 | Telecom | Region_6 | JDJZ0788 | JDJZ0788 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/13/2025 12:48:10 | 10/13/2025 20:12:10 | 10/14/2025 00:48:10 | p0_MW_Link Down at JDJZ0788 to SAB0057 ¦¦ ref TT-20250908-00130 | 10/13/2025 12:47:51 | Minor | 15269 | LOS | 10/13/2025 12:47:51 | P1 | 2G | baish | Sceco_STB | IPRAN NSA | JDJZ0788 | FLM_TE | [8 empty] | API | 10/13/2025 12:48:10 | 10/13/2025 14:29:40 | 10/13/2025 19:30:33 |  |  | 10/13/2025 20:12:10 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000745 | PCM-20251013-00001498 | TT-20251013-01520 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/13/2025 12:50:26 | 10/13/2025 13:10:45 | 10/14/2025 00:50:26 | Chassis Fail at RIYB6066-CSG-01 @ Sceco | 10/13/2025 12:30:11 | Minor | 101-2505202 | Chassis Fail | 10/13/2025 12:23:47 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6066-CSG-01 | FLM_TE |  |  | PCM-20251013-00001462 | kindly check RIYB6066-CSG-01,suspected power issue | kindly check RIYB6066-CSG-01,suspected power issue |  |  |  | API | 10/13/2025 12:50:26 | 10/13/2025 13:10:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000746 | PCM-20251013-00001500 | TT-20251013-01476 | Telecom | Region_2 | RIYB6031-CSG-01 | RIYB6031 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/13/2025 12:50:56 | 10/13/2025 13:10:46 | 10/14/2025 00:50:56 | Chassis Fail at RIYB6031-CSG-01 @ Sceco | 10/13/2025 12:03:37 | Minor | 101-2505202 | Chassis Fail | 10/13/2025 11:58:21 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6031-CSG-01 | FLM_TE |  |  | PCM-20251013-00001463 | kindly check RIYB6031-CSG-01,flapped power | kindly check RIYB6031-CSG-01,flapped power |  |  |  | API | 10/13/2025 12:50:56 | 10/13/2025 13:10:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000749 | PCM-20251013-00001504 | TT-20251013-01477 | Telecom | Region_2 | RIYB6029-CSG-01 | RIYB6029 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/13/2025 12:51:49 | 10/13/2025 18:00:06 | 10/14/2025 00:51:49 | Chassis Fail at RIYB6029-CSG-01 @ Sceco | 10/13/2025 12:04:05 | Minor | 101-2505202 | Chassis Fail | 10/13/2025 11:58:18 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6029-CSG-01 | FLM_TE |  |  | PCM-20251013-00001480 | Kindly check RIYB6029-CSG-01 as flapped power | Kindly check RIYB6029-CSG-01 as flapped power |  |  |  | API | 10/13/2025 12:51:49 | 10/13/2025 18:00:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000752 | PCM-20251013-00001510 | TT-20250929-02106 | MW_HC | Region_3 | SHR0009 | SHR0009 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Hossam Ali Ahmed Ali | 10/13/2025 12:54:57 | 10/14/2025 12:26:34 | 10/14/2025 00:54:57 | Huawei MW HC_P2 Observing Errors at SHR0009-TBK9042 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | VIP | SRAN | tabouk | Sceco | TX NSA | SHR0009-TBK9042 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00001496 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 12:54:57 | 10/13/2025 12:58:00 | 10/14/2025 12:26:26 |  |  | 10/14/2025 12:26:34 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251013000756 | PCM-20251013-00001514 | TT-20251008-02974 | MW_HC | Region_4 | JED0947 | JED0947 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 12:57:12 | 10/17/2025 11:02:59 | 10/14/2025 00:57:12 | As per bo request Nokia MW HC JED0947-JED0759 | 10/08/2025 23:41:55 | Minor | 113388 | LOF | 10/08/2025 23:42:00 | P2 | 2G | jeddah | Sceco | TX NSA | JED0947-JED0759 | FLM_TE | JED0947 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00001243 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 12:57:12 | 10/13/2025 19:51:37 | 10/17/2025 10:35:14 | 10/17/2025 10:35:20 | 10/17/2025 11:02:59 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000768 | PCM-20251013-00001532 | TT-20251013-01578 | Telecom | Region_6 | TNM0140 | TNM0140 | Transsmission | SFP_Transmission | Replace SFP | Fawad Khan | 10/13/2025 13:06:13 | 10/21/2025 18:39:58 | 10/14/2025 01:06:13 | p0_MW Link Down at MHL0123 to TNM0140 ¦¦ ref TT-20250810-00530 | 10/13/2025 13:05:43 | Minor | 15269 | LOS | 10/13/2025 13:05:43 | P1 | 2G | namas | Sceco_STB | IPRAN NSA | TNM0140 | FLM_TE | [8 empty] | API | 10/13/2025 13:06:13 | 10/13/2025 13:16:30 | 10/21/2025 18:38:34 |  |  | 10/21/2025 18:39:58 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013000769 | PCM-20251013-00001538 | TT-20251013-01584 | MW_HC | Region_5 | USMD0710 | USMD0710 |  |  |  | Amr Abdulla Ali Othman | 10/13/2025 13:07:43 | 10/13/2025 13:07:43 | 10/14/2025 01:07:43 | As BO Requested MW Nokia Observing modem 12 counting PM errors USMD0710-MKMD0551 | 10/13/2025 13:07:09 | Minor | 113388 | LOF | 10/13/2025 13:07:11 | P1 | 2G | makkah | Sceco_STB | TX NSA | USMD0710-MKMD0551 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing modem 12 counting PM errors USMD0710-MKMD0551 |  |  | API | 10/13/2025 13:07:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000775 | PCM-20251013-00001542 | TT-20251013-01589 | Telecom | Region_6 | NMR0133 | NMR0133 | Transsmission | MW_RSL_fading | Fading issue | Manzoor Ahmed | 10/13/2025 13:09:22 | 10/23/2025 12:44:17 | 10/14/2025 01:09:22 | P0_MW_LINK DOWN AT NMR0133-CSG-01 TO BHAB9036-LL-CSG-01 ¦¦ ref TT-20251010-00709 | 10/13/2025 13:08:52 | Minor | 15269 | LOS | 10/13/2025 13:08:52 | P2 | 2G | makhwa | Sceco | IPRAN NSA | NMR0133 | FLM_TE | [8 empty] | API | 10/13/2025 13:09:22 | 10/13/2025 14:52:58 | 10/23/2025 12:11:16 | 10/23/2025 12:11:30 | 10/23/2025 12:11:34 | 10/23/2025 12:44:17 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000781 | PCM-20251013-00001555 | TT-20251013-01605 | EM | Region_6 | RYAB0634 | RYAB0634 |  |  |  | Faisal Javed Javed Akhtar | 10/13/2025 13:14:45 | 10/13/2025 16:50:07 | 10/14/2025 01:14:45 | Generator Running Alarm at RYAB0634-GSM-UMTS-P3 @ Generator_DG | 10/13/2025 13:06:20 | Minor | 7103 | Generator Running Alarm | 10/13/2025 13:06:14 | P3 | 2G | tathleeth | Generator_DG | 2G NSA | RYAB0634 | FLM_EM | [5 empty] | Generator Running Alarm |  |  | API | 10/13/2025 13:14:45 | 10/13/2025 16:50:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013000788 | PCM-20251013-00001562 | TT-20251013-01614 | Telecom | Region_4 | TAF0324 | TAF0324 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/13/2025 13:17:38 | 10/14/2025 09:50:29 | 10/14/2025 01:17:38 | p0_MW Link Down at TAF0324 to TAF0170 ¦¦ ref TT-20240904-00920 | 10/13/2025 13:17:15 | Minor | 15269 | LOS | 10/13/2025 13:17:15 | P1 | 2G | taif | Sceco_STB | IPRAN NSA | TAF0324 | FLM_TE | [8 empty] | API | 10/13/2025 13:17:38 | 10/14/2025 09:50:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000797 | PCM-20251013-00001578 | TT-20251013-01628 | Reference_telecom | Region_1 | DMJR2266 | DMJR2266 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/13/2025 13:25:05 | 10/13/2025 13:47:12 | 10/14/2025 01:25:05 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR2266-P3-USF_SRAN @ Sceco | 10/13/2025 10:24:54 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/13/2025 10:24:50 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR2266 | FLM_TE | [8 empty] | API | 10/13/2025 13:25:05 | 10/13/2025 13:47:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000801 | PCM-20251013-00001583 | TT-20251013-01633 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/13/2025 13:26:07 | 10/13/2025 14:42:23 | 10/14/2025 01:26:07 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/13/2025 13:17:42 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 13:17:37 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 13:26:07 | 10/13/2025 14:42:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000856 | PCM-20251013-00001681 | TT-20251013-01780 | Reference_telecom | Region_6 | ABBS0162 | ABBS0162 | Equipment | CB_BTS | Switch on CB on Rectifier | Fawad Khan | 10/13/2025 14:10:33 | 10/20/2025 00:47:17 | 10/13/2025 20:10:33 | CELL SERVICE PROBLEM (Phase error exceeds the interference limit) at ABBS0162-G9-L8-L18-NL21-NNR2.6-SBTS-P3-WBB-G3 @ Sceco | 10/13/2025 13:10:19 | Major | 7114 | CELL SERVICE PROBLEM | 10/13/2025 13:10:14 | P3 | 2G | namas | Sceco | 5G_Cell SA | ABBS0162 | FLM_TE | [5 empty] | Phase error exceeds the interference limit |  |  | API | 10/13/2025 14:10:33 | 10/13/2025 14:13:39 | 10/20/2025 00:46:36 |  |  | 10/20/2025 00:47:17 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251013000864 | PCM-20251013-00001693 | TT-20251013-01805 | EM | [7 empty] | 10/13/2025 14:15:49 | 10/13/2025 14:15:49 | 10/13/2025 18:15:49 | DOOR ALARM at SHEDGUN-SEC0034_OCS @ Sceco_STB | 10/13/2025 14:15:12 | Critical | 1-12307 | DOOR ALARM | 10/13/2025 14:15:03 | P1 | DWDM |  | Sceco_STB | DWDM NSA | SHEDGUN | FLM_EM | [5 empty] | 0-TO GHUNAN-SEC0021&RWPS5-SEC0032(1-A)-72-E1EFI-[DOOR ALARM]:1 |  |  | API | 10/13/2025 14:15:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251013000870 | PCM-20251013-00001700 | TT-20251013-01812 | Telecom | Region_4 | JED2619 | JED2619 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/13/2025 14:19:46 | 10/13/2025 18:11:36 | 10/13/2025 20:19:46 | PT:: FLM Need to perform HC at JED2619 under R4 (BO Request) | 10/13/2025 14:19:37 | Major | 676767671 | Health Check-WO to TE FME | 10/13/2025 14:19:37 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED2619 | FLM_TE | [8 empty] | API | 10/13/2025 14:19:46 | 10/13/2025 17:34:44 | 10/13/2025 18:11:25 | 10/13/2025 18:11:31 | 10/13/2025 18:11:36 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013000875 | PCM-20251013-00001708 | TT-20251013-01821 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/13/2025 14:23:29 | 10/13/2025 14:23:29 | 10/13/2025 20:23:29 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/13/2025 14:19:38 | Major | 1-12545 | LOCAL_FAULT | 10/13/2025 14:19:25 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE | [5 empty] | 1-ELC(1-E)-2-G1M520S-9(RX7/TX7)-CLIENT:1 |  |  | API | 10/13/2025 14:23:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000883 | PCM-20251013-00001718 | TT-20251013-01832 | Telecom | Region_4 | JED0103 | JED0103 | Equipment | BTS_Cable | Replace Fiber Cable | Khaled Mohammad Abdallah | 10/13/2025 14:29:03 | 10/24/2025 06:48:27 | 10/13/2025 20:29:03 | PT:: FLM Need to perform HC at JED0103 under R4 (BO Request) | 10/13/2025 14:28:46 | Major | 676767671 | Health Check-WO to TE FME | 10/13/2025 14:28:46 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0103 | FLM_TE | [8 empty] | API | 10/13/2025 14:29:03 | 10/22/2025 22:32:12 | 10/22/2025 22:32:18 | 10/22/2025 22:32:19 | 10/22/2025 22:32:22 | 10/24/2025 06:48:27 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000885 | PCM-20251013-00001721 | TT-20251013-01839 | EM | Region_4 | HHR0818 | HHR0818 |  |  |  | Aly Ahmed Aly Sawy | 10/13/2025 14:31:12 | 10/14/2025 13:57:59 | 10/13/2025 20:31:12 | SHELTER DOOR OPEN at HHR0818-GSM-UMTS-P1-VIP-HHR @ Generator_DG | 10/13/2025 14:30:39 | Major | 7103 | SHELTER DOOR OPEN | 10/13/2025 14:30:26 | VIP | 2G | jeddah | Generator_DG | 2G NSA | HHR0818 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/13/2025 14:31:12 | 10/14/2025 13:57:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013000886 | PCM-20251013-00001722 | TT-20251013-01841 | Telecom | Region_4 | JED0984 | JED0984 | Equipment | BSS_HW_fault | Replace FAN | Mohammed Ramadan A Abu Abid | 10/13/2025 14:32:15 | 10/16/2025 16:15:42 | 10/14/2025 02:32:15 | BASE STATION INFORMATION (No module fan detected) at JED0984-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/13/2025 14:24:13 | Minor | 7115 | BASE STATION INFORMATION | 10/13/2025 14:24:04 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0984 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/13/2025 14:32:15 | 10/13/2025 14:38:54 | 10/16/2025 16:15:30 |  |  | 10/16/2025 16:15:42 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013000888 | PCM-20251013-00001725 | TT-20251013-01852 | Telecom | Region_6 | DRB1M8004 | DRB2004 |  |  |  | AKHTAR ALI MASIN ZADA | 10/13/2025 14:33:18 | 10/13/2025 14:33:18 | 10/14/2025 02:33:18 | BASE STATION INFORMATION (No module fan detected) at DRB1M8004-P3-CA-L800 @ Sceco | 10/13/2025 14:25:03 | Minor | 7115 | BASE STATION INFORMATION | 10/13/2025 14:24:54 | P3 | 4G | derb | Sceco | LTE NSA | DRB1M8004 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/13/2025 14:33:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000896 | PCM-20251013-00001735 | TT-20251013-01861 | EM | Region_3 | MKMD2563 | MKMD2563 |  |  |  | Walid Mohamad Fazil | 10/13/2025 14:36:23 | 10/15/2025 10:37:10 | 10/14/2025 02:36:23 | NETECO: Communication Failure at MKMD2563 @ Sceco | 10/13/2025 14:30:05 | Minor | 17451 | Communication Failure | 10/13/2025 14:30:05 | P3 | 2G | madinah | Sceco | 2G NSA | MKMD2563 | FLM_EM | [8 empty] | API | 10/13/2025 14:36:23 | 10/15/2025 10:37:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251013000905 | PCM-20251013-00001755 | TT-20251013-01887 | Telecom | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/13/2025 14:47:46 | 10/16/2025 16:15:51 | 10/13/2025 20:47:46 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0110-G9-L8-L18-L21-NR2.6-NNR600-SBTS-P1-VIP @ Sceco | 10/13/2025 14:46:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 14:46:50 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0110 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 14:47:46 | 10/13/2025 15:06:18 | 10/16/2025 16:15:51 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000909 | PCM-20251013-00001761 | TT-20251013-01891 | Reference_telecom | Region_2 | RIY2208 | RIY2208 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/13/2025 14:50:21 | 10/19/2025 13:20:42 | 10/14/2025 02:50:21 | RF Unit RX Channel RTWP/RSSI Unbalanced at RIY2208-P1-VIP-SRAN @ Generator_SG | 10/13/2025 11:49:57 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/13/2025 11:49:52 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2208 | FLM_TE | [8 empty] | API | 10/13/2025 14:50:21 | 10/13/2025 14:58:51 | [6 empty] | Vandalism |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251013000913 | PCM-20251013-00001777 | TT-20251013-01902 | Telecom | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/13/2025 14:54:27 | 10/16/2025 16:16:13 | 10/14/2025 02:54:27 | BASE STATION INFORMATION (No module fan detected) at JED0110-G9-L8-L18-L21-NR2.6-NNR600-SBTS-P1-VIP @ Sceco | 10/13/2025 14:45:45 | Minor | 7115 | BASE STATION INFORMATION | 10/13/2025 14:45:56 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0110 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/13/2025 14:54:27 | 10/13/2025 15:06:18 | 10/16/2025 16:16:13 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000929 | PCM-20251013-00001801 | TT-20251013-01910 | EM | Region_4 | BHMF2137 | BHMF2137 |  |  |  | Khizer Hayat | 10/13/2025 15:04:01 | 10/13/2025 18:43:41 | 10/13/2025 21:04:01 | 1(2G/LTE) sites down under BHMF2137-P3/BHMF2137-P3 @ Generator_SG | 10/13/2025 14:55:59 | Major | 7706 | BTS O&M LINK FAILURE | 10/13/2025 14:55:54 | P3 | 2G | jeddah | Generator_SG | 2G SA | BHMF2137-P3 | FLM_TE | BHMF2137 | Results: DOWN SITE HUB BHMF2137-P3 BHMF2137 Summary: Hub: BHMF2137, Down Count: 1, Down Sites: BHMF2137-P3 Alarm Summary: BHMF2137 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/13/2025 15:04:01 | 10/13/2025 18:43:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000943 | PCM-20251013-00001826 | TT-20251006-02086 | MW_HC | Region_5 | MAK0636 | MAK0636 |  |  |  | Muhammad Shabbir Muhammad | 10/13/2025 15:11:22 | 10/19/2025 10:12:09 | 10/14/2025 03:11:22 | As per bo request Nokia MW HC Check MAK0636-MAK0144 need HC | 10/06/2025 19:30:01 | Minor | 321339 | Demodulator Fail | 10/06/2025 19:29:58 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK0636-MAK0144 | FLM_TE | MAK0636 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00001632 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 15:11:22 | 10/19/2025 10:12:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251013000945 | PCM-20251013-00001829 | TT-20251013-01946 | Reference_telecom | [7 empty] | 10/13/2025 15:12:03 | 10/14/2025 14:40:45 | 10/13/2025 19:12:03 | SCECO : LINK DOWN B/W SHEDGUM-SEC0034-GHUNAN-SEC0021 NCE , Under SCECO planned activity. | 10/13/2025 15:11:30 | Critical | 1-14579 | POWER_JITTER | 10/13/2025 15:11:19 | P1 | DWDM |  | Sceco_STB | DWDM NSA | SHEDGUN | FLM_TE | [5 empty] | 0-TO GHUNAN-SEC0021&RWPS5-SEC0032(1-A)-9-G6WDAPXF-11(LINEIN/LINEOUT(TO GHUNAN-SEC0021_OCS-TNG6WDAPXF(1-B09)-LINEIN))-OTS:1 |  |  | API | 10/13/2025 15:12:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000969 | PCM-20251013-00001859 | TT-20251006-02080 | MW_HC | Region_5 | MAK1M9681 | MAK0681 |  |  |  | Husain Hassan Ishag Omer | 10/13/2025 15:28:45 | 10/13/2025 15:46:58 | 10/14/2025 03:28:45 | As per bo request Nokia MW HC Check SFP port 1.6 to BTS MAK1M9681 | 10/06/2025 19:28:38 | Minor | 321339 | Demodulator Fail | 10/06/2025 19:28:35 | P2 | 4G | makkah | Sceco | TX NSA | MAK1M9681 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00001631 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 15:28:45 | 10/13/2025 15:46:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000970 | PCM-20251013-00001861 | TT-20251006-02078 | MW_HC | Region_5 | MAK2090 | MAK2090 |  |  |  | Husain Hassan Ishag Omer | 10/13/2025 15:29:37 | 10/13/2025 15:46:59 | 10/14/2025 03:29:37 | As per bo request Nokia MW HC FLM to check MAK2090-MAK2077 | 10/06/2025 19:26:51 | Minor | 321339 | Demodulator Fail | 10/06/2025 19:26:48 | P2 | 2G | makkah | Sceco | TX NSA | MAK2090-MAK2077 | FLM_TE | MAK2090 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00001629 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 15:29:37 | 10/13/2025 15:46:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013000984 | PCM-20251013-00001877 | TT-20251013-02005 | Reference_telecom | Region_5 | MAK1M8310 | MAK2310 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/13/2025 15:37:04 | 10/13/2025 15:37:04 | 10/13/2025 21:37:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M8310-CA-L800-SBTS-P3 (Ref:TT-20251013-01265) | 10/13/2025 13:35:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 13:35:13 | P3 | 4G | makkah | Sceco | LTE SA | MAK1M8310-CA-L800-SBTS-P3 | FLM_TE | [8 empty] | API | 10/13/2025 15:37:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000989 | PCM-20251013-00001884 | TT-20251013-02015 | MW_HC | Region_6 | WABH0017 | ABH0017 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/13/2025 15:40:12 | 10/13/2025 16:11:34 | 10/14/2025 03:40:12 | Nokia MW HC_P2 Observing Modem Down at WABH0017-ABH0015 | 10/13/2025 15:39:35 | Minor |  | LOF | 10/13/2025 15:39:35 | P2 | WIFI | abha | Sceco | TX NSA | WABH0017-ABH0015 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:12 | 10/13/2025 16:11:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000990 | PCM-20251013-00001885 | TT-20251013-02016 | MW_HC | Region_4 | JED0824 | JED0824 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 15:40:14 | 10/13/2025 19:51:39 | 10/14/2025 03:40:14 | Nokia MW HC_P0 Observing Performance Issue at JED0824-JDJZ0761_15 | 10/13/2025 15:39:35 | Minor |  | LOF | 10/13/2025 15:39:35 | P2 | 2G | jeddah | Sceco | TX NSA | JED0824-JDJZ0761_15 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:14 | 10/13/2025 19:51:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000991 | PCM-20251013-00001886 | TT-20251013-02017 | MW_HC | Region_4 | JED2641 | JED2641 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 15:40:15 | 10/13/2025 19:51:39 | 10/14/2025 03:40:15 | Nokia MW HC_P2 Observing Modem Down at JED2641-JED0804_2 | 10/13/2025 15:39:35 | Minor |  | LOF | 10/13/2025 15:39:35 | P3 | 2G | jeddah | Sceco | TX NSA | JED2641-JED0804_2 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:15 | 10/13/2025 19:51:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000995 | PCM-20251013-00001890 | TT-20251013-02021 | MW_HC | Region_6 | MKW2140 | MKW2140 |  |  |  | Manzoor Ahmed | 10/13/2025 15:40:19 | 10/13/2025 17:28:48 | 10/14/2025 03:40:19 | Nokia MW HC_P2 Observing Modem Down at MKW2140_01-MKW2128_01 | 10/13/2025 15:39:35 | Minor |  | LOF | 10/13/2025 15:39:35 | P3 | 2G | Baha | Sceco | TX NSA | MKW2140_01-MKW2128_01 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:19 | 10/13/2025 17:28:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013000998 | PCM-20251013-00001893 | TT-20251013-02024 | MW_HC | Region_6 | NMS0098 | NMS0098 |  |  |  | Fawad Khan | 10/13/2025 15:40:22 | 10/13/2025 19:51:59 | 10/14/2025 03:40:22 | Nokia MW HC_P1 Observing Performance Issue at NMS0098_01-NMS0094_03 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | namas | Sceco | TX NSA | NMS0098_01-NMS0094_03 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:22 | 10/13/2025 19:51:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001000 | PCM-20251013-00001895 | TT-20251013-02026 | MW_HC | Region_6 | MKW2358 | MKW2358 |  |  |  | SHAH KHALID | 10/13/2025 15:40:25 | 10/13/2025 15:54:28 | 10/14/2025 03:40:25 | Nokia MW HC_P0 Observing Performance Issue at MKW2358_01-MKW0035_01 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | Baha | Generator_SG | TX NSA | MKW2358_01-MKW0035_01 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:25 | 10/13/2025 15:54:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001001 | PCM-20251013-00001897 | TT-20251013-02028 | MW_HC | Region_6 | NMR2024 | NMR2024 |  |  |  | SHAH KHALID | 10/13/2025 15:40:26 | 10/13/2025 15:54:29 | 10/14/2025 03:40:26 | Nokia MW HC_P2 Observing Performance Issue at NMR2024_02-NMR0133_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | Albaha | Generator_SG | TX NSA | NMR2024_02-NMR0133_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:26 | 10/13/2025 15:54:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001002 | PCM-20251013-00001898 | TT-20251013-02029 | MW_HC | Region_6 | ABBS2107 | ABBS2107 |  |  |  | Fawad Khan | 10/13/2025 15:40:28 | 10/13/2025 19:52:00 | 10/14/2025 03:40:28 | Nokia MW HC_P1 Observing Performance Issue at ABBS2107_01-MRD2104_01 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | namas | Sceco | TX NSA | ABBS2107_01-MRD2104_01 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:28 | 10/13/2025 19:52:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001004 | PCM-20251013-00001900 | TT-20251013-02031 | MW_HC | Region_4 | JZMA2413 | JZMA2413 |  |  |  | Khizer Hayat | 10/13/2025 15:40:30 | 10/13/2025 18:43:42 | 10/14/2025 03:40:30 | Nokia MW HC_P2 Observing Modem Down at JZMA2413_01-JZMA2414_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Generator_SG | TX NSA | JZMA2413_01-JZMA2414_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:30 | 10/13/2025 18:43:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251013001005 | PCM-20251013-00001901 | TT-20251013-02032 | MW_HC | Region_6 | KMS0510 | KMS0510 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/13/2025 15:40:31 | 10/16/2025 21:07:26 | 10/14/2025 03:40:31 | Nokia MW HC_P1 Observing Performance Issue at KMS0510_01-KMS0436_05 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0510_01-KMS0436_05 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:31 | 10/13/2025 16:13:59 | 10/16/2025 21:07:20 | 10/16/2025 21:07:26 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001006 | PCM-20251013-00001902 | TT-20251013-02033 | MW_HC | Region_6 | ABH2005 | ABH2005 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Jamshaid Muhammad Ashraf | 10/13/2025 15:40:32 | 10/13/2025 17:54:06 | 10/14/2025 03:40:32 | Nokia MW HC_P0 Observing Performance Issue at ABH2005-MHA0433 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | abha | Generator_SG | TX NSA | ABH2005-MHA0433 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:32 | 10/13/2025 16:11:35 | 10/13/2025 17:53:53 |  |  | 10/13/2025 17:54:06 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001007 | PCM-20251013-00001903 | TT-20251013-02034 | MW_HC | Region_4 | JED0793 | JED0793 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 15:40:34 | 10/13/2025 15:40:34 | 10/14/2025 03:40:34 | Nokia MW HC_P0 Observing Performance Issue at JED0793-3-JED2074 FTK | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED0793-3-JED2074 FTK | FLM_TE | [8 empty] | API | 10/13/2025 15:40:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001008 | PCM-20251013-00001904 | TT-20251013-02035 | MW_HC | Region_4 | JED2146 | JED2146 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/13/2025 15:40:35 | 10/13/2025 15:40:35 | 10/14/2025 03:40:35 | Nokia MW HC_P1 Observing Performance Issue at JED2146-JED0115 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2146-JED0115 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001009 | PCM-20251013-00001905 | TT-20251013-02036 | MW_HC | Region_4 | JED0945 | JED0945 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 15:40:36 | 10/13/2025 22:00:56 | 10/14/2025 03:40:36 | Nokia MW HC_P0 Observing Performance Issue at JED0945-JED0131_04 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0945-JED0131_04 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:36 | 10/13/2025 22:00:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001010 | PCM-20251013-00001906 | TT-20251013-02037 | MW_HC | Region_6 | WDS0679 | WDS0679 |  |  |  | Ahmed Mamdouh Helal Helal | 10/13/2025 15:40:37 | 10/13/2025 20:17:43 | 10/14/2025 03:40:37 | Nokia MW HC_P1 Observing Performance Issue at WDS0679-WDS0094 _04 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | Wadi Dawasir | Generator_SG | TX NSA | WDS0679-WDS0094 _04 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:37 | 10/13/2025 20:17:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001011 | PCM-20251013-00001907 | TT-20251013-02038 | MW_HC | Region_6 | KMS0513 | KMS0513 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/13/2025 15:40:38 | 10/13/2025 17:52:59 | 10/14/2025 03:40:38 | Nokia MW HC_P1 Observing Performance Issue at KMS0513_01-KMS0039 NE_3 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0513_01-KMS0039 NE_3 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:38 | 10/13/2025 17:52:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251013001012 | PCM-20251013-00001908 | TT-20251013-02039 | MW_HC | Region_6 | KMS0254 | KMS0254 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/13/2025 15:40:39 | 10/16/2025 21:07:36 | 10/14/2025 03:40:39 | Nokia MW HC_P0 Observing Performance Issue at KMS0254-KMS0436_01 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | KMS0254-KMS0436_01 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:39 | 10/13/2025 16:14:00 | 10/16/2025 21:07:31 | 10/16/2025 21:07:36 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251013001014 | PCM-20251013-00001910 | TT-20251013-02041 | MW_HC | Region_6 | KMS0589 | KMS0589 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/13/2025 15:40:41 | 10/16/2025 21:08:00 | 10/14/2025 03:40:41 | Nokia MW HC_P0 Observing Performance Issue at KMS0589-KMS0314_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0589-KMS0314_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:41 | 10/13/2025 16:14:00 | 10/16/2025 21:07:57 | 10/16/2025 21:08:00 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001017 | PCM-20251013-00001913 | TT-20251013-02044 | MW_HC | Region_4 | JED2899 | JED2899 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 15:40:45 | 10/13/2025 19:51:39 | 10/14/2025 03:40:45 | Nokia MW HC_P0 Observing Performance Issue at JED2899_01-JED0759_03 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2899_01-JED0759_03 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:45 | 10/13/2025 19:51:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001018 | PCM-20251013-00001914 | TT-20251013-02045 | MW_HC | Region_6 | ABH0086 | ABH0086 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Jamshaid Muhammad Ashraf | 10/13/2025 15:40:46 | 10/13/2025 17:54:34 | 10/14/2025 03:40:46 | Nokia MW HC_P0 Observing Performance Issue at ABH0086_1-ABH0280-4 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | abha | Sceco | TX NSA | ABH0086_1-ABH0280-4 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:46 | 10/13/2025 16:11:35 | 10/13/2025 17:54:20 |  |  | 10/13/2025 17:54:34 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001019 | PCM-20251013-00001915 | TT-20251013-02046 | MW_HC | Region_5 | MK2 | MAK2 |  |  |  | Muhammad Zubair | 10/13/2025 15:40:48 | 10/13/2025 15:40:48 | 10/14/2025 03:40:48 | Nokia MW HC_P1 Observing Performance Issue at MK2-30-MAK0066 -16 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | BSC | makkah | Sceco_STB | TX NSA | MK2-30-MAK0066 -16 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001020 | PCM-20251013-00001916 | TT-20251013-02047 | MW_HC | Region_4 | JDMK2403 | JDMK2403 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 15:40:49 | 10/13/2025 15:40:49 | 10/14/2025 03:40:49 | Nokia MW HC_P1 Observing Performance Issue at JDMK2403-JED0890 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Generator_SG | TX NSA | JDMK2403-JED0890 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001021 | PCM-20251013-00001917 | TT-20251013-02048 | MW_HC | Region_4 | JED6040 | JED6040 |  |  |  | Mohamed Farag Abdelbary | 10/13/2025 15:40:50 | 10/14/2025 20:54:33 | 10/14/2025 03:40:50 | Nokia MW HC_P0 Observing Performance Issue at JED6040-JED0365_08 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED6040-JED0365_08 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:50 | 10/14/2025 20:54:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001023 | PCM-20251013-00001919 | TT-20251013-02050 | MW_HC | Region_4 | JED2295 | JED2295 |  |  |  | Nazeer Mohammed | 10/13/2025 15:40:52 | 10/13/2025 18:13:12 | 10/14/2025 03:40:52 | Nokia MW HC_P0 Observing Performance Issue at JED2295_01-JED0723_13 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2295_01-JED0723_13 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:52 | 10/13/2025 18:13:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001024 | PCM-20251013-00001920 | TT-20251013-02051 | MW_HC | Region_4 | RAB0366 | RAB0366 |  |  |  | Khizer Hayat | 10/13/2025 15:40:53 | 10/13/2025 18:43:42 | 10/14/2025 03:40:53 | Nokia MW HC_P1 Observing Performance Issue at RAB0366_01-RAB0473 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | RAB0366_01-RAB0473 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:53 | 10/13/2025 18:43:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251013001025 | PCM-20251013-00001921 | TT-20251013-02052 | MW_HC | Region_4 | JED0185 | JED0185 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/13/2025 15:40:54 | 10/20/2025 12:29:48 | 10/14/2025 03:40:54 | Nokia MW HC_P0 Observing Performance Issue at JED0185_01-JED0600 -9 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0185_01-JED0600 -9 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:54 | 10/20/2025 12:03:01 | 10/20/2025 12:29:28 | 10/20/2025 12:29:41 | 10/20/2025 12:29:48 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001028 | PCM-20251013-00001924 | TT-20251013-02055 | MW_HC | Region_5 | MAK0634 | MAK0634 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/13/2025 15:40:58 | 10/15/2025 19:13:55 | 10/14/2025 03:40:58 | Nokia MW HC_P1 Observing Performance Issue at MAK0634_03-MAK2185 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0634_03-MAK2185 | FLM_TE | [8 empty] | API | 10/13/2025 15:40:58 | 10/15/2025 19:13:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001031 | PCM-20251013-00001927 | TT-20251013-02058 | MW_HC | Region_4 | DAF0476 | DAF0476 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | Nazeer Mohammed | 10/13/2025 15:41:00 | 10/13/2025 18:13:41 | 10/14/2025 03:41:00 | Nokia MW HC_P2 Observing Performance Issue at DAF0476-DAF0470_01 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | DAF0476-DAF0470_01 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:00 | 10/13/2025 18:13:12 | 10/13/2025 18:13:28 |  |  | 10/13/2025 18:13:41 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001032 | PCM-20251013-00001928 | TT-20251013-02059 | MW_HC | Region_6 | JIZ0011 | JIZ0011 |  |  |  | Mohammed Sideag Mohammed Ali | 10/13/2025 15:41:02 | 10/13/2025 20:20:23 | 10/14/2025 03:41:02 | Nokia MW HC_P1 Observing Performance Issue at JIZ0011-Single Box-JIZ0245_04 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | jizan | Sceco | TX NSA | JIZ0011-Single Box-JIZ0245_04 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:02 | 10/13/2025 20:20:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001033 | PCM-20251013-00001929 | TT-20251013-02060 | MW_HC | Region_4 | JED2025 | JED2025 |  |  |  | Nazeer Mohammed | 10/13/2025 15:41:03 | 10/13/2025 18:13:13 | 10/14/2025 03:41:03 | Nokia MW HC_P1 Observing Performance Issue at JED2025-JED0497_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2025-JED0497_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:03 | 10/13/2025 18:13:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001034 | PCM-20251013-00001930 | TT-20251013-02061 | MW_HC | Region_6 | KMS0464 | KMS0464 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/13/2025 15:41:04 | 10/13/2025 17:52:59 | 10/14/2025 03:41:04 | Nokia MW HC_P1 Observing Performance Issue at KMS0464_1_SB-KMS0465_07 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0464_1_SB-KMS0465_07 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:04 | 10/13/2025 17:52:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251013001035 | PCM-20251013-00001931 | TT-20251013-02062 | MW_HC | Region_6 | KMS0461 | KMS0461 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/13/2025 15:41:05 | 10/16/2025 21:04:42 | 10/14/2025 03:41:05 | Nokia MW HC_P0 Observing Performance Issue at KMS0461_01-KMS0063_10 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0461_01-KMS0063_10 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:05 | 10/13/2025 16:14:02 | 10/16/2025 21:04:37 | 10/16/2025 21:04:42 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001038 | PCM-20251013-00001934 | TT-20251013-02065 | MW_HC | Region_4 | JED2382 | JED2382 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 15:41:08 | 10/13/2025 19:51:40 | 10/14/2025 03:41:08 | Nokia MW HC_P0 Observing Performance Issue at JED2382-JED2022 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2382-JED2022 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:08 | 10/13/2025 19:51:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001039 | PCM-20251013-00001935 | TT-20251013-02066 | MW_HC | Region_4 | JED2627 | JED2627 |  |  |  | Nazeer Mohammed | 10/13/2025 15:41:09 | 10/13/2025 18:13:13 | 10/14/2025 03:41:09 | Nokia MW HC_P2 Observing Performance Issue at JED2627-JED0919-07 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2627-JED0919-07 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:09 | 10/13/2025 18:13:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001040 | PCM-20251013-00001936 | TT-20251013-02067 | MW_HC | Region_4 | JED2816 | JED2816 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 15:41:10 | 10/13/2025 19:51:40 | 10/14/2025 03:41:10 | Nokia MW HC_P0 Observing Performance Issue at JED2816-JED2045_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2816-JED2045_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:10 | 10/13/2025 19:51:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001041 | PCM-20251013-00001937 | TT-20251013-02068 | MW_HC | Region_4 | ASQ0342 | ASQ0342 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/13/2025 15:41:12 | 10/13/2025 19:47:07 | 10/14/2025 03:41:12 | Nokia MW HC_P0 Observing Performance Issue at ASQ0342_01-JDJZ0771_04 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | adam | Sceco_STB | TX NSA | ASQ0342_01-JDJZ0771_04 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:12 | 10/13/2025 19:47:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001042 | PCM-20251013-00001938 | TT-20251013-02069 | MW_HC | Region_4 | JED2640 | JED2640 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 15:41:13 | 10/13/2025 15:41:13 | 10/14/2025 03:41:13 | Nokia MW HC_P2 Observing Performance Issue at JED2640-JED0095-14 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2640-JED0095-14 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001043 | PCM-20251013-00001939 | TT-20251013-02070 | MW_HC | Region_5 | MAK0640 | MAK0640 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/13/2025 15:41:14 | 10/21/2025 19:56:56 | 10/14/2025 03:41:14 | Nokia MW HC_P1 Observing Performance Issue at MAK0640_01-MAK0533_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0640_01-MAK0533_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:14 | 10/21/2025 19:56:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001044 | PCM-20251013-00001940 | TT-20251013-02071 | MW_HC | Region_5 | MKMD0552 | MKMD0552 |  |  |  | Amr Abdulla Ali Othman | 10/13/2025 15:41:15 | 10/13/2025 15:41:15 | 10/14/2025 03:41:15 | Nokia MW HC_P0 Observing Performance Issue at MKMD0552_01-MKMD0551_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | makkah | Generator_SG | TX NSA | MKMD0552_01-MKMD0551_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001047 | PCM-20251013-00001943 | TT-20251013-02074 | MW_HC | Region_4 | JED2596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 15:41:19 | 10/13/2025 22:00:57 | 10/14/2025 03:41:19 | Nokia MW HC_P2 Observing Performance Issue at JED2596-JED2069 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | jeddah | Sceco | TX NSA | JED2596-JED2069 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:19 | 10/13/2025 22:00:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_BO_with_Closed | CM20251013001048 | PCM-20251013-00001944 | TT-20251013-02075 | MW_HC | Region_4 | JED0225 | JED0225 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/13/2025 15:41:20 | 10/14/2025 10:04:22 | 10/14/2025 03:41:20 | Nokia MW HC_P2 Observing Modem Down at JED0225-JED0342-4 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED0225-JED0342-4 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:20 | 10/13/2025 17:11:53 | 10/13/2025 17:12:13 | 10/13/2025 17:12:18 | 10/13/2025 17:12:22 | 10/14/2025 10:04:22 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001051 | PCM-20251013-00001947 | TT-20251013-02078 | MW_HC | Region_6 | AHM0019 | AHM0019 | Transsmission | SFP_Transmission | Reset SFP | Zeshan Ali Adnan | 10/13/2025 15:41:24 | 10/16/2025 14:15:16 | 10/14/2025 03:41:24 | Nokia MW HC_P1 Observing Performance Issue at AHM0019_01-JDSM0793_12 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | jizan | Sceco | TX NSA | AHM0019_01-JDSM0793_12 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:24 | 10/13/2025 16:02:04 | 10/16/2025 14:14:43 |  |  | 10/16/2025 14:15:16 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001052 | PCM-20251013-00001948 | TT-20251013-02079 | MW_HC | Region_4 | JED0959 | JED0959 |  |  |  | Nazeer Mohammed | 10/13/2025 15:41:25 | 10/13/2025 18:13:14 | 10/14/2025 03:41:25 | Nokia MW HC_P1 Observing Performance Issue at JED0959-01-JED0919-03 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0959-01-JED0919-03 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:25 | 10/13/2025 18:13:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251013001057 | PCM-20251013-00001954 | TT-20251013-02085 | MW_HC | Region_6 | ARF0068 | ARF0068 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/13/2025 15:41:29 | 10/19/2025 16:00:47 | 10/14/2025 03:41:29 | Nokia MW HC_P0 Observing Performance Issue at ARF0068-ARF0066_05 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | al harja | Sceco | TX NSA | ARF0068-ARF0066_05 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:29 | 10/13/2025 16:14:02 | 10/16/2025 21:04:21 | 10/16/2025 21:04:30 | 10/19/2025 16:00:47 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001059 | PCM-20251013-00001956 | TT-20251013-02087 | MW_HC | Region_4 | TAF2400 | TAF2400 |  |  |  | Ahmad Kamal Abdelmawla | 10/13/2025 15:41:31 | 10/14/2025 20:35:42 | 10/14/2025 03:41:31 | Nokia MW HC_P1 Observing Performance Issue at TAF2400_01-SHF0329 _02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | taif | Sceco | TX NSA | TAF2400_01-SHF0329 _02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:31 | 10/14/2025 20:35:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001060 | PCM-20251013-00001957 | TT-20251013-02088 | MW_HC | Region_4 | JED2623 | JED2623 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 15:41:32 | 10/13/2025 22:00:57 | 10/14/2025 03:41:32 | Nokia MW HC_P1 Observing Performance Issue at JED2623_01-JED0637_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2623_01-JED0637_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:32 | 10/13/2025 22:00:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001061 | PCM-20251013-00001958 | TT-20251013-02089 | MW_HC | Region_4 | TAF0327 | TAF0327 |  |  |  | Ahmad Kamal Abdelmawla | 10/13/2025 15:41:33 | 10/14/2025 20:35:42 | 10/14/2025 03:41:33 | Nokia MW HC_P2 Observing Performance Issue at TAF0327-TAF0151 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | taif | Sceco | TX NSA | TAF0327-TAF0151 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:33 | 10/14/2025 20:35:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001062 | PCM-20251013-00001959 | TT-20251013-02090 | MW_HC | Region_4 | TAF0151 | TAF0151 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/13/2025 15:41:35 | 10/14/2025 09:50:29 | 10/14/2025 03:41:35 | Nokia MW HC_P1 Observing Performance Issue at TAF0151-TAF0283-6 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | taif | Sceco | TX NSA | TAF0151-TAF0283-6 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:35 | 10/14/2025 09:50:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001063 | PCM-20251013-00001961 | TT-20251013-02091 | MW_HC | Region_4 | TAF0134 | TAF0134 |  |  |  | Ahmad Kamal Abdelmawla | 10/13/2025 15:41:36 | 10/14/2025 20:35:43 | 10/14/2025 03:41:36 | Nokia MW HC_P0 Observing Performance Issue at TAF0134-TAF0283-9 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | taif | Sceco | TX NSA | TAF0134-TAF0283-9 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:36 | 10/14/2025 20:35:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001066 | PCM-20251013-00001964 | TT-20251013-02094 | MW_HC | Region_6 | SAB0053 | SAB0053 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/13/2025 15:41:40 | 10/13/2025 20:21:23 | 10/14/2025 03:41:40 | Nokia MW HC_P1 Observing Performance Issue at SAB0053_01-SAB0057_07 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | baish | Sceco | TX NSA | SAB0053_01-SAB0057_07 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:40 | 10/13/2025 20:21:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001067 | PCM-20251013-00001965 | TT-20251013-02095 | MW_HC | Region_6 | QIS0102 | QIS0102 |  |  |  | Muhammad Ali | 10/13/2025 15:41:41 | 10/13/2025 15:48:32 | 10/14/2025 03:41:41 | Nokia MW HC_P1 Observing Performance Issue at QIS0102-QIS0031 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jizan | Sceco | TX NSA | QIS0102-QIS0031 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:41 | 10/13/2025 15:48:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001068 | PCM-20251013-00001966 | TT-20251013-02096 | MW_HC | Region_5 | MAK2080 | MAK2080 |  |  |  | Mosab Nasr eldeen Mohamed | 10/13/2025 15:41:42 | 10/14/2025 01:45:20 | 10/14/2025 03:41:42 | Nokia MW HC_P1 Observing Performance Issue at MAK2080-MAK0190 SH03 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | makkah | Sceco | TX NSA | MAK2080-MAK0190 SH03 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:42 | 10/14/2025 01:45:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001069 | PCM-20251013-00001967 | TT-20251013-02097 | MW_HC | Region_5 | MAK0599 | MAK0599 |  |  |  | Atif Javed Javed Hussain | 10/13/2025 15:41:43 | 10/16/2025 11:25:58 | 10/14/2025 03:41:43 | Nokia MW HC_P0 Observing Performance Issue at MAK0599-MAK0602 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | makkah | Sceco | TX NSA | MAK0599-MAK0602 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:43 | 10/16/2025 11:25:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001070 | PCM-20251013-00001968 | TT-20251013-02098 | MW_HC | Region_5 | MAK0539 | MAK0539 |  |  |  | Husain Hassan Ishag Omer | 10/13/2025 15:41:44 | 10/13/2025 15:46:59 | 10/14/2025 03:41:44 | Nokia MW HC_P0 Observing Performance Issue at MAK0539-MAK0016-3 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0539-MAK0016-3 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:44 | 10/13/2025 15:46:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001071 | PCM-20251013-00001969 | TT-20251013-02099 | MW_HC | Region_5 | MAK0520 | MAK0520 |  |  |  | Husain Hassan Ishag Omer | 10/13/2025 15:41:45 | 10/13/2025 15:47:00 | 10/14/2025 03:41:45 | Nokia MW HC_P2 Observing Performance Issue at MAK0520-MAK0053 -11 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0520-MAK0053 -11 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:45 | 10/13/2025 15:47:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001072 | PCM-20251013-00001970 | TT-20251013-02100 | MW_HC | Region_5 | MAK0264 | MAK0264 |  |  |  | Husain Hassan Ishag Omer | 10/13/2025 15:41:46 | 10/13/2025 15:47:01 | 10/14/2025 03:41:46 | Nokia MW HC_P1 Observing Performance Issue at MAK0264-MAK0714 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | makkah | Sceco | TX NSA | MAK0264-MAK0714 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:46 | 10/13/2025 15:47:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001074 | PCM-20251013-00001972 | TT-20251013-02102 | MW_HC | Region_5 | MAK0212 | MAK0212 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/13/2025 15:41:49 | 10/15/2025 19:13:55 | 10/14/2025 03:41:49 | Nokia MW HC_P1 Observing Performance Issue at MAK0212-MK2-20 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0212-MK2-20 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:49 | 10/15/2025 19:13:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001075 | PCM-20251013-00001973 | TT-20251013-02103 | MW_HC | Region_5 | MAK0209 | MAK0209 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/13/2025 15:41:50 | 10/21/2025 19:56:57 | 10/14/2025 03:41:50 | Nokia MW HC_P0 Observing Performance Issue at MAK0209_01-MAK0014-13 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0209_01-MAK0014-13 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:50 | 10/21/2025 19:56:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001076 | PCM-20251013-00001974 | TT-20251013-02104 | MW_HC | Region_5 | MAK0206 | MAK0206 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Husain Hassan Ishag Omer | 10/13/2025 15:41:51 | 10/14/2025 12:22:28 | 10/14/2025 03:41:51 | Nokia MW HC_P2 Observing Modem Down at MAK0206 -1-MAK0030-5 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | makkah | Sceco | TX NSA | MAK0206 -1-MAK0030-5 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:51 | 10/13/2025 15:47:02 | 10/14/2025 11:01:28 | 10/14/2025 11:01:33 | 10/14/2025 11:01:35 | 10/14/2025 12:22:28 |  | Husain Hassan Ishag Omer |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001077 | PCM-20251013-00001975 | TT-20251013-02105 | MW_HC | Region_5 | MAK0067 | MAK0067 |  |  |  | Atif Javed Javed Hussain | 10/13/2025 15:41:52 | 10/16/2025 11:25:59 | 10/14/2025 03:41:52 | Nokia MW HC_P1 Observing Performance Issue at MAK0067-MAK0308 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | VIP | 2G | makkah | Sceco | TX NSA | MAK0067-MAK0308 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:52 | 10/16/2025 11:25:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001079 | PCM-20251013-00001977 | TT-20251013-02107 | MW_HC | Region_4 | LTH2122 | LTH2122 |  |  |  | Riasat Ali Allah Baksh | 10/13/2025 15:41:55 | 10/14/2025 10:14:13 | 10/14/2025 03:41:55 | Nokia MW HC_P2 Observing Performance Issue at LTH2122-LTH0329 _02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | LTH2122-LTH0329 _02 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:55 | 10/14/2025 10:14:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251013001084 | PCM-20251013-00001982 | TT-20251013-02112 | MW_HC | Region_6 | KMS0033 | KMS0033 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/13/2025 15:41:59 | 10/16/2025 21:04:09 | 10/14/2025 03:41:59 | Nokia MW HC_P1 Observing Performance Issue at KMS0033_NE1-KMS0039 NE_8 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0033_NE1-KMS0039 NE_8 | FLM_TE | [8 empty] | API | 10/13/2025 15:41:59 | 10/13/2025 16:14:03 | 10/16/2025 21:03:58 | 10/16/2025 21:04:09 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001085 | PCM-20251013-00001983 | TT-20251013-02113 | MW_HC | Region_4 | JED2131 | JED2131 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 15:42:00 | 10/13/2025 15:42:00 | 10/14/2025 03:42:00 | Nokia MW HC_P0 Observing Performance Issue at JED2131-JED0197 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED2131-JED0197 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001086 | PCM-20251013-00001984 | TT-20251013-02114 | MW_HC | Region_4 | JED2050 | JED2050 | Transsmission | MW_HW_stuck | Reset Control Card | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 15:42:02 | 10/19/2025 14:01:39 | 10/14/2025 03:42:02 | Nokia MW HC_P0 Observing Performance Issue at JED2050-JED0024 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED2050-JED0024 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:02 | 10/18/2025 14:16:31 | 10/18/2025 14:31:38 | 10/18/2025 14:31:40 | 10/18/2025 14:37:41 | 10/19/2025 14:01:39 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001087 | PCM-20251013-00001985 | TT-20251013-02115 | MW_HC | Region_4 | JED0990 | JED0990 |  |  |  | Mohammed Ramadan A Abu Abid | 10/13/2025 15:42:03 | 10/13/2025 16:02:43 | 10/14/2025 03:42:03 | Nokia MW HC_P0 Observing Performance Issue at JED0990-JED0403- 5 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0990-JED0403- 5 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:03 | 10/13/2025 16:02:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001088 | PCM-20251013-00001986 | TT-20251013-02116 | MW_HC | Region_4 | JED0011 | JED0011 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 15:42:04 | 10/13/2025 16:43:16 | 10/14/2025 03:42:04 | Nokia MW HC_P2 Observing Modem Down at JED0011-JED0893_2 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | DWDM | jeddah | Sceco | TX NSA | JED0011-JED0893_2 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:04 | 10/13/2025 16:43:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001089 | PCM-20251013-00001987 | TT-20251013-02117 | MW_HC | Region_4 | JED0869 | JED0869 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 15:42:05 | 10/13/2025 22:00:57 | 10/14/2025 03:42:05 | Nokia MW HC_P2 Observing Modem Down at JED0869_1-JED0676 -8 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED0869_1-JED0676 -8 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:05 | 10/13/2025 22:00:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001091 | PCM-20251013-00001989 | TT-20251013-02119 | MW_HC | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 15:42:08 | 10/13/2025 19:51:41 | 10/14/2025 03:42:08 | Nokia MW HC_P1 Observing Performance Issue at JED0296-JED0947_2 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED0296-JED0947_2 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:08 | 10/13/2025 19:51:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001092 | PCM-20251013-00001990 | TT-20251013-02120 | MW_HC | Region_4 | JED0235 | JED0235 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 15:42:09 | 10/13/2025 16:43:16 | 10/14/2025 03:42:09 | Nokia MW HC_P2 Observing Modem Down at JED0235-JED0789 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0235-JED0789 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:09 | 10/13/2025 16:43:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001093 | PCM-20251013-00001991 | TT-20251013-02121 | MW_HC | Region_5 | HHR0873 | HHR0873 |  |  |  | Amjad Ali Muhammad Parves | 10/13/2025 15:42:10 | 10/14/2025 03:38:05 | 10/14/2025 03:42:10 | Nokia MW HC_P0 Observing Performance Issue at HHR0873_2-MAK0679 _03 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | VIP | 2G | makkah | Generator_SG | TX NSA | HHR0873_2-MAK0679 _03 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:10 | 10/14/2025 03:38:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001094 | PCM-20251013-00001992 | TT-20251013-02122 | MW_HC | Region_4 | JED0536 | JED0536 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 15:42:11 | 10/13/2025 22:00:58 | 10/14/2025 03:42:11 | Nokia MW HC_P0 Observing Performance Issue at JED0536 - 02-JED0938-2 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0536 - 02-JED0938-2 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:11 | 10/13/2025 22:00:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001095 | PCM-20251013-00001993 | TT-20251013-02123 | MW_HC | Region_4 | JED0487 | JED0487 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 15:42:12 | 10/13/2025 16:43:17 | 10/14/2025 03:42:12 | Nokia MW HC_P1 Observing Performance Issue at JED0487 _01-JED0008-14 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED0487 _01-JED0008-14 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:12 | 10/13/2025 16:43:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001096 | PCM-20251013-00001994 | TT-20251013-02124 | MW_HC | Region_4 | JED0717 | JED0717 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 15:42:14 | 10/13/2025 22:00:58 | 10/14/2025 03:42:14 | Nokia MW HC_P2 Observing Modem Down at JED0717-JED0025-4 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | VIP | 2G | jeddah | Sceco_STB | TX NSA | JED0717-JED0025-4 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:14 | 10/13/2025 22:00:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001097 | PCM-20251013-00001995 | TT-20251013-02125 | MW_HC | Region_4 | JED0766 | JED0766 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/13/2025 15:42:14 | 10/14/2025 17:55:02 | 10/14/2025 03:42:14 | Nokia MW HC_P2 Observing Modem Down at JED0766-JED0264 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | VIP | 2G | jeddah | Sceco | TX NSA | JED0766-JED0264 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:14 | 10/14/2025 17:55:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001099 | PCM-20251013-00001997 | TT-20251013-02127 | MW_HC | Region_4 | HAW0307 | HAW0307 |  |  |  | Rashid Shafique | 10/13/2025 15:42:17 | 10/13/2025 15:43:25 | 10/14/2025 03:42:17 | Nokia MW HC_P2 Observing Performance Issue at HAW0307_01-HAW0297 _02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | taif | Sceco | TX NSA | HAW0307_01-HAW0297 _02 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:17 | 10/13/2025 15:43:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001100 | PCM-20251013-00001998 | TT-20251013-02128 | MW_HC | Region_4 | JED0383 | JED0383 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 15:42:18 | 10/22/2025 15:00:02 | 10/14/2025 03:42:18 | Nokia MW HC_P0 Observing Performance Issue at JED0383-JED0125-12 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0383-JED0125-12 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:18 | 10/13/2025 16:43:17 | 10/21/2025 17:29:58 | 10/21/2025 17:36:25 |  | 10/22/2025 15:00:02 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001101 | PCM-20251013-00001999 | TT-20251013-02129 | MW_HC | Region_4 | JED0408 | JED0408 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/13/2025 15:42:19 | 10/13/2025 15:42:19 | 10/14/2025 03:42:19 | Nokia MW HC_P2 Observing Performance Issue at JED0408_14-JD1_35 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | DWDM | jeddah | Sceco | TX NSA | JED0408_14-JD1_35 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001102 | PCM-20251013-00002000 | TT-20251013-02130 | MW_HC | Region_6 | ABH0281 | ABH0281 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Jamshaid Muhammad Ashraf | 10/13/2025 15:42:20 | 10/13/2025 17:55:14 | 10/14/2025 03:42:20 | Nokia MW HC_P1 Observing Performance Issue at ABH0281_01-ABH0087_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P2 | 2G | abha | Sceco | TX NSA | ABH0281_01-ABH0087_02 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:20 | 10/13/2025 16:11:36 | 10/13/2025 17:55:02 |  |  | 10/13/2025 17:55:14 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001103 | PCM-20251013-00002001 | TT-20251013-02131 | MW_HC | Region_4 | JED0572 | JED0572 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/13/2025 15:42:21 | 10/13/2025 15:42:21 | 10/14/2025 03:42:21 | Nokia MW HC_P2 Observing Modem Down at JED0572-JED0341 - 13 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P1 | 2G | jeddah | Sceco | TX NSA | JED0572-JED0341 - 13 | FLM_TE | [8 empty] | API | 10/13/2025 15:42:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251013001137 | PCM-20251013-00002059 | TT-20251013-02176 | EM | [7 empty] | 10/13/2025 16:07:17 | 10/13/2025 16:07:17 | 10/13/2025 20:07:17 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/13/2025 16:05:21 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/13/2025 16:05:13 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/13/2025 16:07:17 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251013001145 | PCM-20251013-00002075 | TT-20251013-02180 | EM | Region_6 | BHAB2041 | BHAB2041 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 16:13:03 | 10/14/2025 09:58:38 | 10/13/2025 22:13:03 | 1(2G/LTE) sites down under BHAB2041-P3/BHAB2041-P3 @ Generator_SG | 10/13/2025 16:05:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/13/2025 16:05:06 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2041-P3 | FLM_EM | BHAB2041 | Results: DOWN SITE HUB BHAB2041-P3 BHAB2041 Summary: Hub: BHAB2041, Down Count: 1, Down Sites: BHAB2041-P3 Alarm Summary: BHAB2041 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/13/2025 16:13:03 | 10/14/2025 09:58:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001167 | PCM-20251013-00002109 | TT-20251013-02225 | Telecom | Region_2 | RIY0639 | RIY0639 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/13/2025 16:26:08 | 10/16/2025 20:16:16 | 10/14/2025 04:26:08 | p0_MW Link Down at RIY0639 to RIY0792 ¦¦ ref TT-20250713-01634 | 10/13/2025 16:25:45 | Minor | 15269 | LOS | 10/13/2025 16:25:45 | P2 | DWDM | riyadh | Sceco | IPRAN NSA | RIY0639 | FLM_TE | [8 empty] | API | 10/13/2025 16:26:08 | 10/13/2025 16:27:13 | 10/16/2025 20:16:08 |  |  | 10/16/2025 20:16:16 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001189 | PCM-20251013-00002141 | TT-20251012-01958 | MW_HC | Region_1 | HFF2354 | HFF2354 |  |  |  | Mohamed Magdy Fouad Zayed | 10/13/2025 16:36:08 | 10/13/2025 18:30:29 | 10/14/2025 04:36:08 | NEC MW HC_P0 Observing Performance Issue at HFF2354(10.248.39.82)--HFSW0017(10.248.39.83) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | SRAN | hafouf | Sceco | TX NSA | HFF2354(10.248.39.82)--HFSW0017(10.248.39.83) | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00002117 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 16:36:08 | 10/13/2025 18:30:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001195 | PCM-20251013-00002156 | TT-20251013-02256 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/13/2025 16:48:38 | 10/14/2025 11:02:35 | 10/13/2025 22:48:38 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/13/2025 13:46:57 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/13/2025 13:48:08 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/13/2025 16:48:38 | 10/14/2025 11:02:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001217 | PCM-20251013-00002191 | TT-20251013-02271 | EM | Region_6 | SRA2355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 16:58:40 | 10/21/2025 22:26:06 | 10/13/2025 22:58:40 | 1(2G/LTE) sites down under SRA2355-P3/SRA2355-P3 @ Generator_SG | 10/13/2025 16:50:10 | Major | 7706 | BTS O&M LINK FAILURE | 10/13/2025 16:50:04 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2355-P3 | FLM_EM | SRA2355 | Results: DOWN SITE HUB SRA2355-P3 SRA2355 Summary: Hub: SRA2355, Down Count: 1, Down Sites: SRA2355-P3 Alarm Summary: SRA2355 Alarm Active on HUB |  |  |  |  | sites down |  | Manual | 10/13/2025 16:58:40 | 10/21/2025 22:26:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251013001246 | PCM-20251013-00002238 | TT-20251013-02334 | Telecom | Region_4 | JED2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 17:20:10 | 10/13/2025 17:20:10 | 10/13/2025 23:20:10 | PT:: FLM Need to perform HC at JED2979 under R4 (BO Request) | 10/13/2025 17:19:52 | Major | 676767671 | Health Check-WO to TE FME | 10/13/2025 17:19:52 | VIP | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G SA | JED2979 | FLM_TE | [8 empty] | API | 10/13/2025 17:20:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001263 | PCM-20251013-00002259 | TT-20251013-02360 | OSS_HC | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/13/2025 17:35:12 | 10/13/2025 17:35:12 | 10/13/2025 23:35:12 | AC failure at MAK6018 | 10/13/2025 17:33:00 | Major | 676767672 | Health Check-WO to TE FME | 10/13/2025 17:33:00 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/13/2025 17:35:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001269 | PCM-20251013-00002271 | TT-20251013-02362 | Telecom | Region_4 | JED0391 | JED0391 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 17:39:24 | 10/19/2025 17:44:17 | 10/13/2025 23:39:24 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED0391-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/13/2025 17:31:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 17:31:28 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0391 | FLM_TE |  |  | PCM-20251013-00002262 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/13/2025 17:39:24 | 10/13/2025 19:51:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001270 | PCM-20251013-00002272 | TT-20251013-02276 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 17:39:53 | 10/13/2025 17:39:53 | 10/13/2025 23:39:53 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/13/2025 16:49:23 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/13/2025 16:49:18 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251013-00002179 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/13/2025 17:39:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001275 | PCM-20251013-00002278 | TT-20251013-02374 | Reference_telecom | Region_4 | JED0965 | JED0965 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 17:42:20 | 10/13/2025 21:23:31 | 10/14/2025 05:42:20 | DemFail observed in JED0965 towards 10.10.147.38 @ Sceco | 10/13/2025 05:41:58 | Minor |  | DemFail | 10/13/2025 05:41:52 | P1 | DWDM | jeddah | Sceco | TX NSA | JED0965 | FLM_TE | [8 empty] | API | 10/13/2025 17:42:20 | 10/13/2025 21:23:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001277 | PCM-20251013-00002280 | TT-20251013-02376 | Reference_telecom | Region_4 | JED0550 | JED0550 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/13/2025 17:43:22 | 10/13/2025 21:23:32 | 10/14/2025 05:43:22 | DemXpicLOS observed in JED0550_03 towards 10.10.147.37 @ Sceco | 10/13/2025 05:45:16 | Minor |  | DemXpicLOS | 10/13/2025 05:43:11 | P2 | 2G | jeddah | Sceco | TX NSA | JED0550 | FLM_TE | [8 empty] | API | 10/13/2025 17:43:22 | 10/13/2025 21:23:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001278 | PCM-20251013-00002281 | TT-20251013-02378 | Telecom | Region_4 | HHR1MN0465 | HHR0465 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 17:44:03 | 10/13/2025 22:00:59 | 10/13/2025 23:44:03 | PT:: FLM Need to check CELL SERVICE PROBLEM (Phase error exceeds the interference limit) at at HHR1MN0465-NR2.6-P2 under R4. | 10/13/2025 17:43:48 | Major | 676767671 | Health Check-WO to TE FME | 10/13/2025 17:43:48 | P1 | 5G | jeddah | Sceco | 2G_3G_LTE_5G SA | HHR1MN0465 | FLM_TE | [8 empty] | API | 10/13/2025 17:44:03 | 10/13/2025 22:00:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001284 | PCM-20251013-00002287 | TT-20251013-02385 | Telecom | Region_4 | JED1M8146 | JED2146 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/13/2025 17:46:29 | 10/13/2025 17:46:29 | 10/13/2025 23:46:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8146-P3-CA-L800 @ Sceco | 10/13/2025 17:45:31 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 17:45:25 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8146 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 17:46:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001296 | PCM-20251013-00002308 | TT-20251013-02403 | Telecom | Region_2 | RY1 | RY1 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Junaid Riaz Arbab Khan | 10/13/2025 17:58:28 | 10/14/2025 06:00:09 | 10/13/2025 23:58:28 | Observing Link Down at RYD1_vMSE_RN06_NEW_EOR Connected to 10GE2/3/0/20 If Alias=to New FTTH-MOI Server 02 & 10GE2/3/0/21 If Alias=to New FTTH-MOI Server 02 | 10/13/2025 17:55:40 | Major | 5000003 | Link Down | 10/13/2025 17:55:40 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | Observing Link Down at RYD1_vMSE_RN06_NEW_EOR Connected to 10GE2/3/0/20 If Alias=to New FTTH-MOI Server 02 & 10GE2/3/0/21 If Alias=to New FTTH-MOI Server 02 | FLM_TE | [5 empty] | Observing Link Down at RYD1_vMSE_RN06_NEW_EOR Connected to 10GE2/3/0/20 If Alias=to New FTTH-MOI Server 02 & 10GE2/3/0/21 If Alias=to New FTTH-MOI Server 02 |  |  | API | 10/13/2025 17:58:28 | 10/14/2025 05:52:17 | 10/14/2025 05:58:23 | 10/14/2025 05:58:41 |  | 10/14/2025 06:00:09 |  | Junaid Riaz Arbab Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001302 | PCM-20251013-00002314 | TT-20251013-02407 | Reference_telecom | Region_4 | JED0807 | JED0807 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 18:00:24 | 10/13/2025 18:00:24 | 10/14/2025 06:00:24 | FanFailure observed in JED0807 towards 10.10.150.51 @ Sceco | 10/13/2025 06:00:56 | Minor |  | FanFailure | 10/13/2025 05:59:58 | P2 | 2G | jeddah | Sceco | TX NSA | JED0807 | FLM_TE | [8 empty] | API | 10/13/2025 18:00:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001318 | PCM-20251013-00002339 | TT-20251013-02428 | Telecom | Region_5 | USMD0704 | USMD0704 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Amjad Ali Muhammad Parves | 10/13/2025 18:15:55 | 10/16/2025 18:20:32 | 10/14/2025 06:15:55 | ODU CPU / Cable Open at USMD0704 on 10.154.140.169 @ Sceco | 10/13/2025 18:14:54 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/13/2025 18:07:07 | P2 | 2G | makkah | Sceco | TX NSA | USMD0704 | FLM_TE | [8 empty] | API | 10/13/2025 18:15:55 | 10/16/2025 10:49:27 | 10/16/2025 11:07:29 | 10/16/2025 11:07:31 | 10/16/2025 13:37:24 | 10/16/2025 18:20:32 |  | Amjad Ali Muhammad Parves |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001331 | PCM-20251013-00002359 | TT-20251013-02448 | Telecom | Region_4 | JD1 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/13/2025 18:31:22 | 10/14/2025 23:37:51 | 10/14/2025 00:31:22 | Observing ALU CIDs Down b/w JED, KMS, RIY | 10/13/2025 18:26:27 | Major | 5000003 | Link Down | 10/13/2025 18:26:27 | P1 | DWDM | jeddah | Sceco_STB | IPBB NSA | Observing ALU CIDs Down b/w JED, KMS, RIY | FLM_TE | [5 empty] | Observing ALU CIDs Down b/w JED, KMS, RIY |  |  | API | 10/13/2025 18:31:22 | 10/14/2025 23:37:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001334 | PCM-20251013-00002363 | TT-20251013-02454 | Telecom | Region_2 | RIYB2U6754 | RIYB6054 |  |  |  | Farmanullah Akbar Jan | 10/13/2025 18:33:28 | 10/13/2025 18:38:05 | 10/14/2025 06:33:28 | GNSS Antenna Fault at RIYB2U6754-P3 @ Sceco | 10/13/2025 15:55:04 | Minor | 26125 | GNSS Antenna Fault | 10/13/2025 15:53:32 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6754 | FLM_TE | [8 empty] | API | 10/13/2025 18:33:28 | 10/13/2025 18:38:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001336 | PCM-20251013-00002367 | TT-20251013-02463 | Telecom | Region_1 | DAM6001 | DAM6001 |  |  |  | Meraj Husain Idd Baksh | 10/13/2025 18:34:02 | 10/21/2025 11:37:54 | 10/14/2025 00:34:02 | RFC Port Underpower at DAM6001-DCU1 @ Sceco | 10/13/2025 12:25:36 | Major | 29803 | RFC Port Underpower | 10/13/2025 12:26:09 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6001 | FLM_TE | [8 empty] | API | 10/13/2025 18:34:02 | 10/14/2025 01:04:08 | [6 empty] | Mobily |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001341 | PCM-20251013-00002373 | TT-20251013-02465 | Reference_telecom | Region_6 | ABBS2245 | ABBS2245 |  |  |  | Manzoor Ahmed | 10/13/2025 18:37:04 | 10/13/2025 20:27:00 | 10/14/2025 06:37:04 | ReplaceableUnitProblem observed in ABBS2245 towards 10.74.122.244 @ Sceco | 10/13/2025 06:37:05 | Minor |  | ReplaceableUnitProblem | 10/13/2025 06:36:37 | P3 | 2G | Albaha | Sceco | TX NSA | ABBS2245 | FLM_TE | [8 empty] | API | 10/13/2025 18:37:04 | 10/13/2025 20:27:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001358 | PCM-20251013-00002406 | TT-20251013-02499 | Telecom | Region_2 | RIY0351 | RIY0351 | Transsmission | DWDM_HW | Alarm Cleared | DILSHAD ALI ABDUL HAMEED | 10/13/2025 18:56:54 | 10/22/2025 03:51:16 | 10/14/2025 00:56:54 | IN_PWR_LOW alarm at RIY0351 and RY3 NCE | 10/13/2025 18:52:48 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/13/2025 18:52:48 | P1 | DWDM | riyadh | Sceco | DWDM NSA | RIY0351 - RY3 | FLM_TE | [8 empty] | API | 10/13/2025 18:56:54 | 10/22/2025 00:59:32 | 10/22/2025 01:01:39 | 10/22/2025 01:01:43 | 10/22/2025 02:26:19 | 10/22/2025 03:51:16 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251013001379 | PCM-20251013-00002435 | TT-20251013-02495 | Telecom | Region_6 | DAR0901 | DAR0901 |  |  |  | Muhammad Ali | 10/13/2025 19:18:02 | 10/17/2025 02:09:38 | 10/14/2025 07:18:02 | p0_MW Link Down at RTH9007 to DAR0901 | 10/13/2025 18:52:53 | Minor | 15269 | LOS | 10/13/2025 18:52:53 | P1 | 2G | raith | Generator_DG | IPRAN NSA | DAR0901 | FLM_TE |  |  | PCM-20251013-00002399 | share all require data | share all require data |  |  |  | API | 10/13/2025 19:18:02 | 10/13/2025 19:52:09 | 10/17/2025 02:08:13 | 10/17/2025 02:09:36 | 10/17/2025 02:09:38 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001391 | PCM-20251013-00002452 | TT-20251008-01739 | MW_HC | Region_1 | SLW0913 | SLW0913 |  |  |  | Mohamed Magdy Fouad Zayed | 10/13/2025 19:28:02 | 10/14/2025 13:24:11 | 10/14/2025 07:28:02 | Huawei MW HC_P2 Observing Errors at SLW0913-SLW0911 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | hafouf | Power Cube | TX NSA | SLW0913-SLW0911 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00002439 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 19:28:02 | 10/14/2025 13:24:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001392 | PCM-20251013-00002454 | TT-20251008-01972 | MW_HC | Region_1 | RYHF2042 | RYHF2042 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/13/2025 19:28:57 | 10/14/2025 01:15:06 | 10/14/2025 07:28:57 | NEC MW HC_P0 Observing Performance Issue at RYHF0041(10.248.32.99)--RYHF2042(10.248.32.100) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | SRAN | hafouf | Generator_SG | TX NSA | RYHF0041(10.248.32.99)--RYHF2042(10.248.32.100) | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251013-00002441 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/13/2025 19:28:57 | 10/14/2025 01:15:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001398 | PCM-20251013-00002463 | TT-20251013-02543 | Telecom | Region_4 | JED0361 | JED0361 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 19:37:32 | 10/13/2025 19:37:32 | 10/14/2025 01:37:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0361-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Sceco | 10/13/2025 19:36:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 19:36:28 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0361 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 19:37:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001403 | PCM-20251013-00002471 | TT-20251013-02542 | Reference_telecom | Region_1 | DAM2M7644 | DAM0644 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/13/2025 19:42:02 | 10/13/2025 19:42:26 | 10/14/2025 07:42:02 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M7644-CA-L800-P2 @ Sceco | 10/13/2025 16:36:33 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/13/2025 16:36:28 | P2 | 4G | dammam | Sceco | 2G NSA | DAM2M7644 | FLM_TE |  |  | PCM-20251013-00002462 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/13/2025 19:42:02 | 10/13/2025 19:42:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001408 | PCM-20251013-00002480 | TT-20251013-01319 | Telecom | Region_4 | JED1MN0351 | JED0351 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/13/2025 19:45:07 | 10/13/2025 19:45:07 | 10/14/2025 01:45:07 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED1MN0351-NR2.6-P2 @ Sceco | 10/13/2025 10:53:26 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/13/2025 10:53:19 | P1 | 5G | jeddah | Sceco | 5G NSA | JED1MN0351 | FLM_TE |  |  | PCM-20251013-00001292 | Kindly check Not able to sync baseband bus alarm is active at site, support to perform HC at site | Kindly check Not able to sync baseband bus alarm is active at site, support to perform HC at site |  |  |  | API | 10/13/2025 19:45:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251013001409 | PCM-20251013-00002481 | TT-20251013-01321 | Telecom | Region_4 | JED0347 | JED0347 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/13/2025 19:45:54 | 10/15/2025 11:42:05 | 10/14/2025 01:45:54 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED0347-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/13/2025 10:53:32 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/13/2025 10:53:26 | P1 | DWDM | jeddah | Sceco | 2G NSA | JED0347 | FLM_TE |  |  | PCM-20251013-00001296 | Kindly check as anchor site JED1MN0035-NR2.6-P2 is down, | Kindly check as anchor site JED1MN0035-NR2.6-P2 is down, |  |  |  | API | 10/13/2025 19:45:54 | 10/15/2025 11:41:43 | 10/15/2025 11:42:00 | 10/15/2025 11:42:03 | 10/15/2025 11:42:05 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001414 | PCM-20251013-00002495 | TT-20251013-02565 | Telecom | Region_4 | JDJZ1MN0761 | JDJZ0761 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 19:52:13 | 10/15/2025 10:55:19 | 10/14/2025 01:52:13 | PT:: FLM Need to perform HC at JDJZ1MN0761 & JED1MN2024 under R4 (BO Request) | 10/13/2025 19:52:02 | Major | 676767671 | Health Check-WO to TE FME | 10/13/2025 19:52:02 | P1 | 5G | jeddah | Sceco_STB | 2G_3G_LTE_5G SA | JDJZ1MN0761 & JED1MN2024 | FLM_TE | [8 empty] | API | 10/13/2025 19:52:13 | 10/15/2025 10:55:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001417 | PCM-20251013-00002500 | TT-20251013-02571 | Reference_telecom | Region_4 | JDRS0759 | JDRS0759 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Khizer Hayat | 10/13/2025 19:57:40 | 10/21/2025 21:34:56 | 10/14/2025 07:57:40 | Degrade observed in JDRS0759_04 towards 10.21.75.149 @ Generator_DG | 10/13/2025 07:58:58 | Minor |  | Degrade | 10/13/2025 07:57:36 | P3 | 2G | jeddah | Generator_DG | TX NSA | JDRS0759 | FLM_TE | [8 empty] | API | 10/13/2025 19:57:40 | 10/14/2025 14:38:08 | 10/21/2025 17:20:11 | 10/21/2025 17:20:14 | 10/21/2025 17:20:22 | 10/21/2025 21:34:56 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001418 | PCM-20251013-00002501 | TT-20251013-02573 | Telecom | Region_4 | JED1MN0901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 19:59:43 | 10/13/2025 22:01:00 | 10/13/2025 23:59:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0901-NR2.6-P1-VIP @ Sceco | 10/13/2025 19:59:01 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 19:58:50 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0901 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 19:59:43 | 10/13/2025 22:01:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251013001421 | PCM-20251013-00002505 | TT-20251013-02574 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/13/2025 20:03:53 | 10/21/2025 17:12:34 | 10/14/2025 02:03:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/13/2025 20:03:05 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 20:02:57 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0500 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 20:03:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001428 | PCM-20251013-00002514 | TT-20251013-02557 | Telecom | Region_4 | JED1M7553 | JED0553 | Equipment | SFP_BTS | Clean SFP | MALIK ATIF ZAMAN | 10/13/2025 20:18:00 | 10/23/2025 15:11:09 | 10/14/2025 02:18:00 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7553-CA-L900-L800-SBTS @ Sceco | 10/13/2025 19:42:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 19:42:48 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7553 | FLM_TE |  |  | PCM-20251013-00002482 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/13/2025 20:18:00 | 10/13/2025 22:01:01 | 10/23/2025 09:40:01 | 10/23/2025 09:40:26 | 10/23/2025 10:18:10 | 10/23/2025 15:11:09 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001431 | PCM-20251013-00002517 | TT-20251013-02586 | Telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/13/2025 20:18:51 | 10/13/2025 22:01:01 | 10/14/2025 02:18:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8061-CA-L800-SBTS @ Sceco | 10/13/2025 20:18:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 20:17:56 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8061 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 20:18:51 | 10/13/2025 22:01:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001437 | PCM-20251013-00002527 | TT-20251013-02594 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/13/2025 20:34:08 | 10/14/2025 09:58:39 | 10/14/2025 02:34:08 | 2(2G) 2(LTE) sites down under BHAB2103-P3,BHAB2091-P3/BHAB2091-P3 @ Generator_SG | 10/13/2025 20:25:00 | Major | 7706 | BTS O&M LINK FAILURE | 10/13/2025 20:24:57 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2091-P3 2G_LTE,BHAB2103-P3 2G_LTE | FLM_EM | BHAB2091 | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251013-00002526 | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/13/2025 20:34:08 | 10/14/2025 09:58:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251013001468 | PCM-20251013-00002582 | TT-20251013-02652 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/13/2025 21:18:15 | 10/19/2025 17:44:16 | 10/14/2025 03:18:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/13/2025 21:17:09 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 21:17:01 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/13/2025 21:18:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251013001503 | PCM-20251013-00002645 | TT-20251013-02711 | Telecom | Region_6 | BAH0005 | BAH0005 |  |  |  | Farhan Ali Khan | 10/13/2025 22:28:28 | 10/14/2025 15:30:48 | 10/14/2025 04:28:28 | LAN_LOC at BAH0005_OCS1 @ Sceco_STB | 10/13/2025 13:39:15 | Major | 1-12926 | LAN_LOC | 10/13/2025 13:39:06 | P1 | DWDM | Albaha | Sceco_STB | DWDM NSA | BAH0005 | FLM_TE | [5 empty] | 0-TO TFBH0887(3-B)-7-T1SCC-5(ETH2&EXT1/ETH2&EXT1)-COM:1 |  |  | API | 10/13/2025 22:28:28 | 10/14/2025 14:36:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001522 | PCM-20251013-00002674 | TT-20251013-02751 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 23:07:44 | 10/19/2025 17:44:19 | 10/14/2025 05:07:44 | BASE STATION SERVICE PROBLEM (No feedback signal) at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/13/2025 23:03:09 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 23:03:04 | P3 | 2G | jeddah | Sceco | LTE_Cell SA | JED2279 | FLM_TE | [5 empty] | No feedback signal |  |  | API | 10/13/2025 23:07:44 | 10/15/2025 10:55:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251013001529 | PCM-20251013-00002688 | TT-20251013-02757 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/13/2025 23:28:11 | 10/17/2025 17:32:24 | 10/14/2025 03:28:11 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/13/2025 23:05:14 | Critical | 7654 | CELL OPERATION DEGRADED | 10/13/2025 23:05:09 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251013-00002677 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/13/2025 23:28:11 | 10/14/2025 20:54:34 | 10/17/2025 17:32:15 |  |  | 10/17/2025 17:32:24 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001531 | PCM-20251013-00002691 | TT-20251013-02733 | Reference_telecom | Region_4 | JED1MN2382 | JED2382 |  |  |  | BARKAT ALI MAIN HILAL | 10/13/2025 23:28:37 | 10/15/2025 10:55:20 | 10/14/2025 05:28:37 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1MN2382-NR2.6-P3 @ Sceco | 10/13/2025 18:45:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/13/2025 18:45:00 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2382 | FLM_TE |  |  | PCM-20251013-00002661 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/13/2025 23:28:37 | 10/15/2025 10:55:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251013001537 | PCM-20251013-00002698 | TT-20251013-02764 | Reference_telecom | Region_2 | RIYB6004 | RIYB6004 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/13/2025 23:30:47 | 10/22/2025 17:49:39 | 10/14/2025 01:30:47 | 11(2G) 10(LTE) sites down under R2_RY4_HWBSC01 @ Sceco(REF:TT-20251013-01455) | 10/13/2025 11:52:51 | Emergency | 21825 | CSL Fault | 10/13/2025 11:52:51 | P3 | SRAN | riyadh | Sceco | 2G_LTE SA | RIYB6004-P3 2G RIYB6031-P3 2G_LTE RIYB6033-P1-VIP 2G_LTE RYAP2832-P1 2G_LTE RYAP2833-P1 2G_LTE RIYB6055-P3 2G_LTE RIYB6066-P3 2G_LTE RIYB6067-P3 2G_LTE RIYB6073-P1-DIA-SHOP 2G_LTE RIYB6108-P3 2G_LTE RIYC6023-P3 2G_LTE | FLM_TE | RIYB6004 | Results: DOWN SITE HUB RIYB6004-P3 RIYB6004 RIYB6031-P3 RIYB6031 RIYB6033-P1-VIP RIYB6033 RYAP2832-P1 RYAP2832 RYAP2833-P1 RYAP2833 RIYB6055-P3 RIYB6055 RIYB6066-P3 RIYB6066 RIYB6067-P3 RIYB6067 RIYB6073-P1-DIA-SHOP RIYB6073 RIYB6108-P3 RIYB6108 RIYC6023-P3 RIYC6023 Summary: Hub: RIYB6004, Down Count: 1, Down Sites: RIYB6004-P3 Hub: RIYB6031, Down Count: 1, Down Sites: RIYB6031-P3 Hub: RIYB6033, Down Count: 1, Down Sites: RIYB6033-P1-VIP Hub: RYAP2832, Down Count: 1, Down Sites: RYAP2832-P1 Hub: RYAP2833, Down Count: 1, Down Sites: RYAP2833-P1 Hub: RIYB6055, Down Count: 1, Down Sites: RIYB6055-P3 Hub: RIYB6066, Down Count: 1, Down Sites: RIYB6066-P3 Hub: RIYB6067, Down Count: 1, Down Sites: RIYB6067-P3 Hub: RIYB6073, Down Count: 1, Down Sites: RIYB6073-P1-DIA-SHOP Hub: RIYB6108, Down Count: 1, Down Sites: RIYB6108-P3 Hub: RIYC6023, Down Count: 1, Down Sites: RIYC6023-P3 Alarm Summary: RIYB6004 No Active Alarm on HUB RIYB6031 No Active Alarm on HUB RIYB6033 No Active Alarm on HUB RYAP2832 No Active Alarm on HUB RYAP2833 No Active Alarm on HUB RIYB6055 No Active Alarm on HUB RIYB6066 No Active Alarm on HUB RIYB6067 No Active Alarm on HUB RIYB6073 No Active Alarm on HUB RIYB6108 No Active Alarm on HUB RIYC6023 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/13/2025 23:30:47 | 10/22/2025 17:49:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014000001 | PCM-20251014-00000001 | TT-20251014-00002 | EM | [7 empty] | 10/14/2025 00:01:28 | 10/14/2025 00:01:28 | 10/14/2025 04:01:28 | DOOR OPEN at MUHAYIL-SEC0048_OCS @ Sceco | 10/14/2025 00:01:05 | Critical | 1-12307 | DOOR OPEN | 10/14/2025 00:00:54 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/14/2025 00:01:28 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000005 | PCM-20251014-00000006 | TT-20251013-02220 | Telecom | Region_6 | WDS0499 | WDS0499 |  |  |  | Ahmed Mamdouh Helal Helal | 10/14/2025 00:04:23 | 10/14/2025 12:06:49 | 10/14/2025 12:04:23 | p0_MW Link Down at WDS0499 to WDS0277 ¦¦ ref TT-20250817-00807 | 10/13/2025 16:22:45 | Minor | 15269 | LOS | 10/13/2025 16:22:45 | P1 | 2G | wadi dawasar | Sceco | IPRAN NSA | WDS0499 | FLM_TE |  |  | PCM-20251013-00002683 | Dear FLM team, kindly share Mail for HW approval | Dear FLM team, kindly share Mail for HW approval |  |  |  | API | 10/14/2025 00:04:23 | 10/14/2025 12:06:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000007 | PCM-20251014-00000011 | TT-20251013-02742 | Reference_telecom | Region_5 | MAK1U6453 | MAK6153 |  |  |  | Atif Javed Javed Hussain | 10/14/2025 00:07:50 | 10/16/2025 11:26:00 | 10/14/2025 06:07:50 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at MAK1U6453-P1-VIP-HAJJ-HRM @ Sceco | 10/13/2025 22:29:14 | Major | 7771 | WCDMA CELL OUT OF USE | 10/13/2025 22:27:06 | VIP | 3G | makkah | Sceco | 3G SA | MAK1U6453 | FLM_TE |  |  | PCM-20251014-00000004 | Kindly check the site locally as cells are down due to degraded connectivity | Kindly check the site locally as cells are down due to degraded connectivity |  |  |  | API | 10/14/2025 00:07:50 | 10/16/2025 11:26:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000021 | PCM-20251014-00000041 | TT-20251014-00044 | Reference_telecom | Region_4 | JED0532 | JED0532 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 00:31:56 | 10/14/2025 10:07:02 | 10/14/2025 12:31:56 | Degrade observed in JED0532 towards 10.10.184.194 @ Sceco | 10/13/2025 12:31:48 | Minor |  | Degrade | 10/13/2025 12:31:43 | P2 | 2G | jeddah | Sceco | TX NSA | JED0532 | FLM_TE | [8 empty] | API | 10/14/2025 00:31:56 | 10/14/2025 10:07:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000022 | PCM-20251014-00000042 | TT-20251014-00045 | Reference_telecom | Region_4 | JED2574 | JED2574 | Transsmission | SFP_Transmission | Replace SFP | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 00:31:57 | 10/15/2025 12:17:59 | 10/14/2025 12:31:57 | Degrade observed in JED2574 towards 10.10.184.195 @ Sceco | 10/13/2025 12:31:49 | Minor |  | Degrade | 10/13/2025 12:31:45 | P1 | 2G | jeddah | Sceco | TX NSA | JED2574 | FLM_TE | [8 empty] | API | 10/14/2025 00:31:57 | 10/14/2025 10:07:02 | 10/14/2025 19:58:53 | 10/14/2025 19:58:56 | 10/14/2025 20:08:08 | 10/15/2025 12:17:59 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000024 | PCM-20251014-00000044 | TT-20251013-02307 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/14/2025 00:37:01 | 10/17/2025 17:31:56 | 10/14/2025 06:37:01 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/13/2025 17:02:23 | Major | 7654 | CELL OPERATION DEGRADED | 10/13/2025 17:02:14 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251013-00002219 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 00:37:01 | 10/14/2025 20:54:36 | 10/17/2025 17:31:50 |  |  | 10/17/2025 17:31:56 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000033 | PCM-20251014-00000061 | TT-20251014-00082 | Telecom | Region_2 | RYD-SR-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/14/2025 00:56:44 | 10/14/2025 00:56:44 | 10/14/2025 12:56:44 | Bad Package Error Rising at RYD-SR-01 @ Sceco_STB | 10/14/2025 00:56:07 | Minor | 101-2501403 | Bad Package Error Rising | 10/14/2025 00:55:59 | P1 | IPBB | riyadh | Sceco_STB | IPRAN NSA | RYD-SR-01 | FLM_TE | [8 empty] | API | 10/14/2025 00:56:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000038 | PCM-20251014-00000066 | TT-20251014-00088 | Reference_telecom | Region_1 | RSK2M8301 | RSK2301 |  |  |  | Mohamed Abdelaziz | 10/14/2025 01:00:54 | 10/14/2025 01:26:55 | 10/14/2025 07:00:54 | RF Unit VSWR Threshold Crossed at RSK2M8301-P2 @ Sceco | 10/13/2025 22:00:56 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/13/2025 22:00:44 | P2 | 4G | jubail | Sceco | LTE NSA | RSK2M8301 | FLM_TE | [8 empty] | API | 10/14/2025 01:00:54 | 10/14/2025 01:26:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000042 | PCM-20251014-00000072 | TT-20251014-00096 | Telecom | Region_1 | SAK-PE-01 | SK1 |  |  |  | Syed Fawad Ali | 10/14/2025 01:08:38 | 10/14/2025 01:15:38 | 10/14/2025 05:08:38 | The Device is offline at SAK-PE-01 @ Sceco_STB | 10/14/2025 01:08:18 | Critical | 101-7 | The Device is offline | 10/14/2025 01:08:16 | P1 | IPBB | sakaka | Sceco_STB | IPRAN SA | SAK-PE-01 | FLM_TE | [8 empty] | API | 10/14/2025 01:08:38 | 10/14/2025 01:15:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000044 | PCM-20251014-00000074 | TT-20251014-00098 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/14/2025 01:09:40 | 10/14/2025 01:32:00 | 10/14/2025 05:09:40 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/14/2025 01:09:27 | Critical | 65334 | Door open Alarm Equipment room | 10/14/2025 01:09:22 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/14/2025 01:09:40 | 10/14/2025 01:32:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000051 | PCM-20251014-00000085 | TT-20251014-00109 | Telecom | Region_5 | HAJ0325 | HAJ0325 |  |  |  | Muhammad Saleem Iqbal | 10/14/2025 01:17:25 | 10/14/2025 22:24:53 | 10/14/2025 13:17:25 | ODC_FAN_FAILED at HAJ0325_NE_1 @ Sceco | 10/14/2025 01:17:15 | Minor | 1-13161 | ODC_FAN_FAILED | 10/12/2025 20:52:02 | P3 | SRAN | makkah | Sceco | TX NSA | HAJ0325 | FLM_TE | [8 empty] | API | 10/14/2025 01:17:25 | 10/14/2025 22:24:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014000054 | PCM-20251014-00000089 | TT-20251014-00114 | Telecom | [7 empty] | 10/14/2025 01:20:31 | 10/14/2025 01:20:31 | 10/14/2025 05:20:31 | The Device is offline at SAK-PE-02 @ Sceco_STB | 10/14/2025 01:20:00 | Critical | 101-7 | The Device is offline | 10/14/2025 01:19:58 | P1 | IPBB |  | Sceco_STB | IPRAN SA | SAK-PE-02 | FLM_TE | [8 empty] | API | 10/14/2025 01:20:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000057 | PCM-20251014-00000101 | TT-20251014-00132 | Telecom | Region_4 | JED1M8178 | JED2178 | Equipment | SFP_BTS | Clean SFP | Khaled Mohammad Abdallah | 10/14/2025 01:24:38 | 10/21/2025 23:25:44 | 10/14/2025 07:24:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8178-P3-CA-L800 @ Sceco | 10/14/2025 01:23:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 01:23:43 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8178 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 01:24:38 | 10/20/2025 07:29:25 | 10/20/2025 07:29:31 | 10/20/2025 07:29:37 | 10/20/2025 07:29:46 | 10/21/2025 23:25:44 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000076 | PCM-20251014-00000143 | TT-20251014-00177 | Telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/14/2025 01:50:58 | 10/14/2025 01:50:58 | 10/14/2025 13:50:58 | RF Out of Service at MAK6018-DCU-P3 @ Sceco | 10/14/2025 01:46:13 | Minor | 28753 | RF Out of Service | 10/14/2025 01:44:40 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/14/2025 01:50:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000079 | PCM-20251014-00000150 | TT-20251013-02027 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/14/2025 01:53:32 | 10/14/2025 09:50:32 | 10/14/2025 07:53:32 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TURY0826-P2 @ Sceco | 10/13/2025 15:35:50 | Major | 7607 | TRX OPERATION DEGRADED | 10/13/2025 15:35:45 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TURY0826 | FLM_TE |  |  | PCM-20251013-00001896 | Please perform HC on SFP, Cable connectivity & HW. SA alarm active on FXDB RMOD-1 | Please perform HC on SFP, Cable connectivity & HW. SA alarm active on FXDB RMOD-1 |  |  |  | API | 10/14/2025 01:53:32 | 10/14/2025 09:50:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000080 | PCM-20251014-00000152 | TT-20251014-00183 | EM | Region_1 | ARR0518 | ARR0518 |  |  |  | Moustafa Mohamed Saleh Saif | 10/14/2025 01:54:36 | 10/15/2025 09:45:45 | 10/14/2025 05:54:36 | Door opening alarm at ARR0518-P1-Core-HUB-WDM_SRAN-FON @ Generator_SG | 10/14/2025 01:54:01 | Critical | 65101 | Door opening alarm | 10/14/2025 01:53:56 | P1 | DWDM | arar | Generator_SG | 2G NSA | ARR0518 | FLM_EM | [8 empty] | API | 10/14/2025 01:54:36 | 10/15/2025 09:45:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251014000082 | PCM-20251014-00000155 | TT-20251014-00184 | Telecom | Region_1 | DMM1_vMSE_RN03_NEW_EOR | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/14/2025 01:57:42 | 10/14/2025 01:57:42 | 10/14/2025 05:57:42 | Board Invalid at DMM1_vMSE_RN03_NEW_EOR @ Sceco_STB | 10/14/2025 01:56:29 | Critical | 101-2505210 | Board Invalid | 10/14/2025 01:56:26 | P1 | IPBB | dammam | Sceco_STB | IPRAN SA | DMM1_vMSE_RN03_NEW_EOR | FLM_TE | [8 empty] | API | 10/14/2025 01:57:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000148 | PCM-20251014-00000294 | TT-20251008-02038 | MW_HC | Region_6 | JIZ0186 | JIZ0186 |  |  |  | Mohammed Sideag Mohammed Ali | 10/14/2025 03:37:15 | 10/14/2025 08:34:23 | 10/14/2025 15:37:15 | Nokia MW HC_P0 Observing Performance Issue at JIZ0186-JIZ0245_01 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | jizan | Sceco | TX NSA | JIZ0186-JIZ0245_01 | FLM_TE |  |  | PCM-20251014-00000131 | Dear FLM team, MW performance Enhancement ,Kindly enhance XPD value also | Dear FLM team, MW performance Enhancement ,Kindly enhance XPD value also |  |  |  | API | 10/14/2025 03:37:15 | 10/14/2025 08:34:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014000154 | PCM-20251014-00000301 | TT-20251014-00337 | Telecom | [7 empty] | 10/14/2025 03:41:02 | 10/14/2025 03:41:02 | 10/14/2025 07:41:02 | 1(2G) sites down under ABH0167-P1-HUB/ABH2167-P1-HUB @ Sceco | 10/14/2025 03:32:52 | Critical | 7706 | BTS O&M LINK FAILURE | 10/14/2025 03:32:49 | P1 | 2G |  | Sceco | 2G SA | ABH0167-P1-HUB | FLM_TE | ABH0167 | Results: DOWN SITE HUB ABH0167-P1-HUB ABH0167 Summary: Hub: ABH0167, Down Count: 1, Down Sites: ABH0167-P1-HUB Alarm Summary: ABH0167 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/14/2025 03:41:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000168 | PCM-20251014-00000331 | TT-20251014-00372 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/14/2025 04:10:29 | 10/16/2025 11:26:02 | 10/14/2025 16:10:29 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/14/2025 04:02:07 | Minor | 7115 | BASE STATION INFORMATION | 10/14/2025 04:01:58 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/14/2025 04:10:29 | 10/16/2025 11:26:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000173 | PCM-20251014-00000350 | TT-20251014-00407 | Telecom | Region_3 | DBQL0258 | DBQL0258 |  |  |  | Waqas Shah | 10/14/2025 04:30:39 | 10/15/2025 11:29:31 | 10/14/2025 08:30:39 | SALAM :: DBQL0258_LH -- TBK9053-LH Link flapped and restored | 10/14/2025 04:30:20 | Critical | 1-14579 | POWER_JITTER | 10/14/2025 04:30:07 | P2 | DWDM | tabouk | Sceco_STB | DWDM NSA | DBQL0258 | FLM_TE | [5 empty] | 0-TO TBK9053(2-A)-2-G6WDAPXF-11(LINEIN/LINEOUT)-OTS:1 |  |  | API | 10/14/2025 04:30:39 | 10/15/2025 00:26:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000186 | PCM-20251014-00000380 | TT-20251014-00442 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/14/2025 05:03:12 | 10/15/2025 17:40:50 | 10/14/2025 09:03:12 | OSC_LOS at YBDB2655_OCS1 @ Sceco_STB | 10/14/2025 05:02:49 | Critical | 1-12843 | OSC_LOS | 10/14/2025 05:02:39 | P1 | DWDM | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE | [5 empty] | 0-TO YBDB0290(1-A)-1-B1SAFS-6(RX1/TX1(TO YBDB0290_OCS,B1SAFS(1-A01(TRM1))-OSC:1 |  |  | API | 10/14/2025 05:03:12 | 10/15/2025 17:40:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000187 | PCM-20251014-00000381 | TT-20251014-00394 | Reference_telecom | Region_4 | JED1MN0743 | JED0743 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 05:04:05 | 10/14/2025 05:04:05 | 10/14/2025 17:04:05 | Fronthaul loop back connectivity check failure at JED1MN0743-NR2.6-P3 @ Sceco | 10/14/2025 03:51:00 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/14/2025 03:50:54 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0743 | FLM_TE |  |  | PCM-20251014-00000337 | FLM need to check RFM and Fronthaul connectivity. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/14/2025 05:04:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000189 | PCM-20251014-00000384 | TT-20251014-00445 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/14/2025 05:06:18 | 10/15/2025 17:40:51 | 10/14/2025 11:06:18 | LOCAL_FAULT at YBDB2655_ELC @ Sceco_STB | 10/14/2025 05:02:49 | Major | 1-12545 | LOCAL_FAULT | 10/14/2025 05:02:39 | P1 | DWDM | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE | [5 empty] | 0-ELC(1-C)-4-G1M520S-4(RX2/TX2)-CLIENT:1 |  |  | API | 10/14/2025 05:06:18 | 10/15/2025 17:40:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000204 | PCM-20251014-00000428 | TT-20251014-00493 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/14/2025 05:38:51 | 10/16/2025 11:26:02 | 10/14/2025 09:38:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/14/2025 05:38:06 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 05:37:59 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 05:38:51 | 10/16/2025 11:26:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000210 | PCM-20251014-00000439 | TT-20251014-00503 | Telecom | Region_4 | JED0981 | JED0981 | Equipment | BSS_HW_Stuck | Reset RRU | MALIK ATIF ZAMAN | 10/14/2025 05:55:54 | 10/15/2025 11:15:51 | 10/14/2025 11:55:54 | BASE STATION SERVICE PROBLEM (TX out of order) at JED0981-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/14/2025 05:51:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 05:51:04 | P3 | 2G | jeddah | Sceco | LTE_Cell SA | JED0981 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/14/2025 05:55:54 | 10/15/2025 10:29:16 | 10/15/2025 10:31:50 | 10/15/2025 10:31:53 | 10/15/2025 10:49:44 | 10/15/2025 11:15:51 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000211 | PCM-20251014-00000457 | TT-20251014-00523 | Reference_EM | Region_2 | RIYB6081 | RIYB6081 |  |  |  | Pawan Virdi Santokh Singh | 10/14/2025 06:00:33 | 10/14/2025 16:42:05 | 10/14/2025 12:00:33 | high temprature 40 at RIYB6081-P1-VIP-ARP_SRAN @ Sceco | 10/14/2025 01:34:53 | Major | 65103 | high temprature 40 | 10/14/2025 01:34:19 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYB6081 | FLM_EM | [8 empty] | API | 10/14/2025 06:00:33 | 10/14/2025 16:42:05 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000219 | PCM-20251014-00000471 | TT-20251014-00534 | Reference_telecom | Region_4 | HHR0459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/14/2025 06:12:21 | 10/14/2025 10:25:53 | 10/14/2025 10:12:21 | 1(2G) site down Under HHR0459-P1-VIP (Ref::TT-20250929-01003) @ Sceco | 09/29/2025 07:33:45 | Critical | 7706 | BTS O&M LINK FAILURE | 09/29/2025 07:33:43 | VIP | 2G | jeddah | Sceco | 2G SA | HHR0459 | FLM_TE | HHR0459 | Results: DOWN SITE HUB HHR0459 HHR0459 Summary: Hub: HHR0459, Down Count: 1, Down Sites: HHR0459 Alarm Summary: HHR0459 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/14/2025 06:12:21 | 10/14/2025 10:25:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000230 | PCM-20251014-00000484 | TT-20251014-00553 | Reference_telecom | Region_6 | BRQ0414 | BRQ0414 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/14/2025 06:27:24 | 10/14/2025 11:27:34 | 10/14/2025 18:27:24 | ReplaceableUnitMissing observed in BRQ0414_01 towards 10.3.224.210 @ Sceco | 10/13/2025 18:26:53 | Minor |  | ReplaceableUnitMissing | 10/13/2025 18:26:49 | P2 | 2G | mohail | Sceco | TX NSA | BRQ0414 | FLM_TE | [8 empty] | API | 10/14/2025 06:27:24 | 10/14/2025 11:27:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000234 | PCM-20251014-00000490 | TT-20251014-00559 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/14/2025 06:30:05 | 10/17/2025 17:31:45 | 10/14/2025 18:30:05 | External Clock Reference Not Configured at JED6008-DCU-P3 @ Sceco | 10/14/2025 05:03:03 | Minor | 26261 | External Clock Reference Not Configured | 10/14/2025 05:01:31 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/14/2025 06:30:05 | 10/14/2025 20:54:37 | 10/17/2025 17:31:38 |  |  | 10/17/2025 17:31:45 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000256 | PCM-20251014-00000529 | TT-20251014-00443 | Telecom | Region_4 | MKYL0918 | MKYL0918 |  |  |  | Riasat Ali Allah Baksh | 10/14/2025 07:00:49 | 10/14/2025 10:14:16 | 10/14/2025 13:00:49 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MKYL0918-P2 @ Generator_SG | 10/14/2025 05:00:16 | Major | 7607 | TRX OPERATION DEGRADED | 10/14/2025 05:00:13 | P2 | 2G | jeddah | Generator_SG | 2G_TRX NSA | MKYL0918 | FLM_TE |  |  | PCM-20251014-00000383 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 07:00:49 | 10/14/2025 10:14:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014000264 | PCM-20251014-00000542 | TT-20251014-00607 | EM | [7 empty] | 10/14/2025 07:04:36 | 10/14/2025 07:04:36 | 10/14/2025 11:04:36 | high temprature 40 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/14/2025 07:02:29 | Critical | 65103 | high temprature 40 | 10/14/2025 07:02:25 | P1 | DWDM |  | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/14/2025 07:04:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000266 | PCM-20251014-00000548 | TT-20251014-00600 | Reference_telecom | Region_4 | JED1M8435 | JED2435 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 07:07:38 | 10/16/2025 11:35:56 | 10/14/2025 13:07:38 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M8435-FWA-P1-VIP-CA-L800 (Ref:TT-20251011-00132) @ Sceco | 10/14/2025 03:51:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 03:51:21 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8435 | FLM_TE |  |  | PCM-20251014-00000533 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 07:07:38 | 10/14/2025 10:07:03 | 10/15/2025 12:17:34 | 10/15/2025 12:17:36 |  | 10/16/2025 11:35:56 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000268 | PCM-20251014-00000551 | TT-20251014-00598 | Reference_telecom | Region_4 | JED1M7449 | JED0449 | Equipment | BSS_HW_Stuck | Reset ALD | MALIK ATIF ZAMAN | 10/14/2025 07:08:29 | 10/19/2025 18:26:58 | 10/14/2025 19:08:29 | BASE STATION ANTENNA LINE PROBLEM (RET Antenna control failure) at JED1M7449-CA-L800-P3-SBTS @ Generator_SG | 10/14/2025 02:03:00 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/14/2025 02:02:48 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7449 | FLM_TE |  |  | PCM-20251014-00000527 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 07:08:29 | 10/14/2025 10:25:53 | 10/19/2025 17:47:48 | 10/19/2025 17:47:50 | 10/19/2025 18:07:37 | 10/19/2025 18:26:58 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000278 | PCM-20251014-00000565 | TT-20251014-00608 | Reference_telecom | Region_4 | HHR1M7447 | HHR0447 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 07:14:59 | 10/19/2025 12:56:50 | 10/14/2025 11:14:59 | BASE STATION HARDWARE PROBLEM (Connection Unstable At 6Gbps) at HHR1M7447-P1-VIP-HHR-L800-CA@ Generator_SG | 10/14/2025 03:58:04 | Critical | 7100 | BASE STATION HARDWARE PROBLEM | 10/14/2025 03:57:55 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7447 | FLM_TE |  |  | PCM-20251014-00000545 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 07:14:59 | 10/14/2025 10:07:03 | 10/14/2025 13:34:10 | 10/14/2025 13:34:12 | 10/14/2025 13:34:14 | 10/15/2025 12:19:04 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000280 | PCM-20251014-00000568 | TT-20251014-00121 | Telecom | Region_4 | HAW2119 | HAW2119 |  |  |  | Rashid Shafique | 10/14/2025 07:16:15 | 10/14/2025 18:55:36 | 10/14/2025 13:16:15 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at HAW2119 @ Sceco | 10/14/2025 01:17:45 | Major | 7607 | TRX OPERATION DEGRADED | 10/14/2025 01:17:42 | P3 | 2G | taif | Sceco | 2G_TRX NSA | HAW2119 | FLM_TE |  |  | PCM-20251014-00000093 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 07:16:15 | 10/14/2025 18:55:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014000287 | PCM-20251014-00000576 | TT-20251014-00630 | EM | [7 empty] | 10/14/2025 07:24:44 | 10/14/2025 07:24:44 | 10/14/2025 11:24:44 | MAJOR + MINOR RECTIFIER ALARM at NAMARA-SEC0016_OCS @ Sceco | 10/14/2025 07:22:53 | Critical | 1-12307 | MAJOR + MINOR RECTIFIER ALARM | 10/14/2025 07:22:43 | P1 | DWDM |  | Sceco | DWDM NSA | NAMARA | FLM_EM | [5 empty] | 0-TO SWAMLA-SEC0023(1-A)-71-E1EFI-[MAJOR + MINOR RECTIFIER ALARM]:2 |  |  | API | 10/14/2025 07:24:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000297 | PCM-20251014-00000601 | TT-20251014-00647 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/14/2025 07:43:00 | 10/17/2025 17:31:33 | 10/14/2025 13:43:00 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/14/2025 07:33:59 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/14/2025 07:33:52 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251014-00000599 | FLM need to check ALD and VSWR at site | FLM need to check ALD and VSWR at site |  |  |  | API | 10/14/2025 07:43:00 | 10/14/2025 20:54:37 | 10/17/2025 17:31:26 |  |  | 10/17/2025 17:31:33 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000299 | PCM-20251014-00000604 | TT-20251014-00652 | Telecom | Region_4 | TAF0151 | TAF0151 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/14/2025 07:45:56 | 10/19/2025 17:44:16 | 10/14/2025 13:45:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF0151-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/14/2025 07:44:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 07:44:52 | P2 | 2G | taif | Sceco | 5G_Cell SA | TAF0151 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 07:45:56 | 10/14/2025 09:50:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000301 | PCM-20251014-00000610 | TT-20251014-00658 | Telecom | Region_4 | JED2056 | JED2056 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 07:47:59 | 10/14/2025 07:47:59 | 10/14/2025 19:47:59 | BCF NOTIFICATION (01 00 00 69 00 00) at JED2056-P3 @ Sceco | 10/14/2025 07:41:01 | Minor | 7602 | BCF NOTIFICATION | 10/14/2025 07:40:47 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2056 | FLM_TE | [5 empty] | 01 00 00 69 00 00 |  |  | API | 10/14/2025 07:47:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000305 | PCM-20251014-00000615 | TT-20251014-00655 | Telecom | Region_4 | JED0229 | JED0229 | Equipment | SFP_BTS | Replace SFP | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 07:52:52 | 10/15/2025 12:18:55 | 10/14/2025 13:52:52 | Fronthaul loop back connectivity check failure at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/14/2025 07:37:33 | Major | 61009 | Fronthaul loop back connectivity check failure | 10/14/2025 07:37:22 | P2 | 2G | jeddah | Sceco | 2G SA | JED0229 | FLM_TE |  |  | PCM-20251014-00000607 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 07:52:52 | 10/14/2025 10:07:04 | 10/14/2025 10:07:17 | 10/14/2025 10:07:22 | 10/14/2025 10:20:55 | 10/15/2025 12:18:55 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000308 | PCM-20251014-00000618 | TT-20251014-00640 | Telecom | Region_4 | SJED0664 | SJED0664 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 07:53:32 | 10/14/2025 07:53:32 | 10/14/2025 13:53:32 | 3(LTE) sites down under SJED0666-CA-P3,SJED0665-CA-P3,SJED0664-CA-P3 @ Sceco | 10/14/2025 07:33:26 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/14/2025 07:33:24 | P3 | SRAN | jeddah | Sceco | LTE SA | SJED0664-CA-P3 LTE,SJED0666-CA-P3 LTE,SJED0665-CA-P3 LTE | FLM_EM | SJED0664 | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251014-00000600 | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/14/2025 07:53:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251014000309 | PCM-20251014-00000619 | TT-20251014-00661 | Telecom | Region_4 | SJED0664 | SJED0664 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 07:54:35 | 10/14/2025 07:54:35 | 10/14/2025 19:54:35 | SJED1W0665, SJED1W0666 complete down | 10/14/2025 07:44:16 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/14/2025 07:44:16 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0665, SJED1W0666 | FLM_EM | SJED0664 | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251014-00000612 | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: SJED0664 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/14/2025 07:54:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251014000322 | PCM-20251014-00000651 | TT-20251014-00684 | EM | [7 empty] | 10/14/2025 08:07:06 | 10/14/2025 08:07:06 | 10/14/2025 12:07:06 | DOOR OPEN at NAMARA-SEC0016_OCS @ Sceco | 10/14/2025 08:06:43 | Critical | 1-12307 | DOOR OPEN | 10/14/2025 08:06:33 | P1 | DWDM |  | Sceco | DWDM NSA | NAMARA | FLM_EM | [5 empty] | 0-TO SWAMLA-SEC0023(1-A)-71-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/14/2025 08:07:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251014000324 | PCM-20251014-00000653 | TT-20251014-00685 | Telecom | Region_1 | DMM1_vMSE_RN03_NEW_EOR | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/14/2025 08:07:37 | 10/14/2025 08:07:37 | 10/14/2025 20:07:37 | Crc error alarm notification at DMM1_vMSE_RN03_NEW_EOR @ Sceco_STB | 10/14/2025 08:07:03 | Minor | 101-1103100 | Crc error alarm notification | 10/14/2025 08:06:49 | P1 | IPBB | dammam | Sceco_STB | IPRAN NSA | DMM1_vMSE_RN03_NEW_EOR | FLM_TE | [8 empty] | API | 10/14/2025 08:07:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000329 | PCM-20251014-00000660 | TT-20251010-00503 | Reference_telecom | Region_4 | JED2038 | JED2038 |  |  |  | BARKAT ALI MAIN HILAL | 10/14/2025 08:10:40 | 10/15/2025 10:55:21 | 10/14/2025 20:10:40 | BatteryFail observed in JED2038_04 towards 10.3.227.88 @ Sceco | 10/09/2025 20:35:46 | Minor |  | BatteryFail | 10/09/2025 20:35:41 | P3 | 2G | jeddah | Sceco | TX NSA | JED2038 | FLM_TE |  |  | PCM-20251014-00000633 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/14/2025 08:10:40 | 10/15/2025 10:55:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000336 | PCM-20251014-00000670 | TT-20251014-00694 | Telecom | Region_1 | DM1 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/14/2025 08:13:55 | 10/14/2025 08:13:55 | 10/14/2025 14:13:55 | Observing link down on DMM1_vMSE_RN03_NEW_EOR connected to 40GE2/2/0/14 If Alias=Stack&DAD port | 10/14/2025 08:06:49 | Major | 5000003 | Link Down | 10/14/2025 08:06:49 | P1 | DWDM | dammam | Sceco_STB | IPBB NSA | DM1 | FLM_TE | [5 empty] | Observing link down on DMM1_vMSE_RN03_NEW_EOR connected to 40GE2/2/0/14 If Alias=Stack&DAD port |  |  | API | 10/14/2025 08:13:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000337 | PCM-20251014-00000671 | TT-20251011-00626 | Reference_telecom | Region_4 | JED2067 | JED2067 | Transsmission | SFP_Transmission | Replace SFP | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 08:14:10 | 10/16/2025 14:39:06 | 10/14/2025 20:14:10 | LossOfSignal observed in JED2067 _02 FTK towards 10.10.148.1 @ Sceco | 10/10/2025 20:27:55 | Minor |  | LossOfSignal | 10/10/2025 20:27:05 | P3 | 2G | jeddah | Sceco | TX NSA | JED2067 | FLM_TE |  |  | PCM-20251014-00000636 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/14/2025 08:14:10 | 10/14/2025 10:07:05 | 10/16/2025 14:38:44 |  |  | 10/16/2025 14:39:06 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000345 | PCM-20251014-00000680 | TT-20251014-00701 | Telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 10/14/2025 08:17:27 | 10/17/2025 17:31:19 | 10/14/2025 20:17:27 | JED1W6081 is partial down | 10/14/2025 08:09:35 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/14/2025 08:09:35 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_2-3F-AP06 | FLM_TE | [8 empty] | API | 10/14/2025 08:17:27 | 10/14/2025 20:54:38 | 10/17/2025 17:31:11 |  |  | 10/17/2025 17:31:19 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000348 | PCM-20251014-00000684 | TT-20251014-00675 | Telecom | Region_6 | ABH1M7522 | ABH0522 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/14/2025 08:19:59 | 10/14/2025 16:05:31 | 10/14/2025 20:19:59 | BASE STATION ANTENNA LINE PROBLEM at ABH1M7522-SBTS-P3-CA-L800 @ Sceco | 10/14/2025 07:52:44 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/14/2025 07:52:35 | P2 | 4G | abha | Sceco | LTE NSA | ABH1M7522 | FLM_TE |  |  | PCM-20251014-00000628 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/14/2025 08:19:59 | 10/14/2025 16:04:55 | 10/14/2025 16:05:23 |  |  | 10/14/2025 16:05:31 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000354 | PCM-20251014-00000701 | TT-20251014-00721 | Telecom | Region_4 | TAF2987 | TAF2987 | Equipment | BSS_HW_fault | Replace RF Module | Ahmad Kamal Abdelmawla | 10/14/2025 08:30:52 | 10/21/2025 10:12:24 | 10/14/2025 20:30:52 | BASE STATION INFORMATION (No module fan detected) at TAF2987-G9-L8-L18-L21-NR2.6-SBTS @ Sceco | 10/14/2025 08:23:05 | Minor | 7115 | BASE STATION INFORMATION | 10/14/2025 08:22:35 | P3 | 2G | jeddah | Sceco | 2G NSA | TAF2987 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/14/2025 08:30:52 | 10/14/2025 20:35:45 | 10/21/2025 10:12:11 |  |  | 10/21/2025 10:12:24 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000408 | PCM-20251014-00000792 | TT-20251014-00799 | Telecom | Region_4 | JED0647 | JED0647 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 09:32:15 | 10/19/2025 17:44:17 | 10/14/2025 15:32:15 | BASE STATION SERVICE PROBLEM (Baseband card crash has been detected) at JED0647-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/14/2025 09:18:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 09:18:05 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0647 | FLM_TE |  |  | PCM-20251014-00000776 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/14/2025 09:32:15 | 10/14/2025 10:07:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000409 | PCM-20251014-00000794 | TT-20251014-00812 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/14/2025 09:33:14 | 10/17/2025 17:31:04 | 10/14/2025 15:33:14 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/14/2025 09:24:56 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/14/2025 09:24:46 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251014-00000793 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/14/2025 09:33:14 | 10/14/2025 20:54:39 | 10/17/2025 17:30:58 |  |  | 10/17/2025 17:31:04 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000425 | PCM-20251014-00000815 | TT-20251014-00842 | EM | Region_3 | DBTB9037 | DBTB9037 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Ahmed Abdel Moaty Sayed Abd Alla | 10/14/2025 09:50:40 | 10/14/2025 11:02:36 | 10/14/2025 13:50:40 | RELAY_ALARM_MAJOR AT DBTB9037_NE_1 | 10/05/2025 09:41:52 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/14/2025 09:47:41 | P3 | Repeater | tabouk | Generator_DG | TX NSA | DBTB9037_NE_1 | FLM_EM | [5 empty] | RELAY_ALARM_MAJOR AT DBTB9037_NE_1 |  |  | API | 10/14/2025 09:50:40 | 10/14/2025 11:02:22 | 10/14/2025 11:02:28 |  |  | 10/14/2025 11:02:36 |  | Ahmed Abdel Moaty Sayed Abd Alla |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000428 | PCM-20251014-00000821 | TT-20251014-00846 | Reference_EM | Region_2 | RIYA2U6199A | RIYA6099 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/14/2025 09:57:09 | 10/14/2025 13:46:12 | 10/14/2025 15:57:09 | Air-condition #2 failure alarm at RIYA2U6199A-P1-VIP-SHOP @ Sceco | 10/14/2025 09:46:56 | Major | 65105 | Air-condition #2 failure alarm | 10/14/2025 09:46:51 | VIP | 2G | riyadh | Sceco | 2G NSA | RIYA2U6199A | FLM_EM | [8 empty] | API | 10/14/2025 09:57:09 | 10/14/2025 13:46:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000430 | PCM-20251014-00000822 | TT-20251014-00847 | Reference_EM | Region_2 | RIYA2U6195 | RIYA6095 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/14/2025 09:57:39 | 10/15/2025 11:53:00 | 10/14/2025 15:57:39 | High temperature 32C alarm at RIYA2U6195-P1-VIP @ Sceco | 10/14/2025 09:47:37 | Major | 65102 | High temperature 32C alarm | 10/14/2025 09:47:14 | VIP | 2G | riyadh | Sceco | 2G NSA | RIYA2U6195 | FLM_EM | [8 empty] | API | 10/14/2025 09:57:39 | 10/14/2025 18:37:17 | [6 empty] | EM phased out spare |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000432 | PCM-20251014-00000827 | TT-20251014-00639 | Reference_telecom | Region_4 | QUN0341 | QUN0341 | Equipment | SFP_BTS | Replace SFP | Mudassar Bashir Bashir Ahmad | 10/14/2025 10:02:09 | 10/16/2025 11:25:59 | 10/14/2025 16:02:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QUN0341-G9-L8-L18-L21-SBTS-P1-VIP @ Sceco | 10/14/2025 05:44:35 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/14/2025 05:33:32 | VIP | 2G | qunfuddah | Sceco | 2G NSA | QUN0341 | FLM_TE |  |  | PCM-20251014-00000640 | Please close alarm during site down | Please close alarm during site down |  |  |  | API | 10/14/2025 10:02:09 | 10/14/2025 13:54:58 | 10/16/2025 11:25:41 |  |  | 10/16/2025 11:25:59 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000433 | PCM-20251014-00000830 | TT-20251014-00852 | Telecom | Region_1 | DAM6001 | DAM6001 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Meraj Husain Idd Baksh | 10/14/2025 10:03:35 | 10/14/2025 15:13:52 | 10/14/2025 16:03:35 | RFC Port Underpower at DAM6001-DCU1 @ Sceco | 10/13/2025 12:25:36 | Major | 29803 | RFC Port Underpower | 10/13/2025 12:26:09 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6001 | FLM_TE | [8 empty] | API | 10/14/2025 10:03:35 | 10/14/2025 11:39:27 | 10/14/2025 12:27:41 | 10/14/2025 12:28:10 | 10/14/2025 12:28:25 | 10/14/2025 15:13:52 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000435 | PCM-20251014-00000834 | TT-20251014-00857 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/14/2025 10:04:53 | 10/14/2025 14:38:10 | 10/14/2025 16:04:53 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/14/2025 09:57:41 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/14/2025 09:57:29 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/14/2025 10:04:53 | 10/14/2025 14:38:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000443 | PCM-20251014-00000847 | TT-20251014-00501 | Reference_telecom | Region_3 | MDYB0313 | MDYB0313 |  |  |  | Muhammad Sajjad R3 | 10/14/2025 10:10:30 | 10/15/2025 17:40:53 | 10/14/2025 22:10:30 | External Clock Reference Problem at MDYB2M1313-P1-HUB @ Generator_DG | 10/14/2025 02:16:53 | Minor | 26262 | External Clock Reference Problem | 10/14/2025 02:13:31 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB2M1313 | FLM_TE | MDYB0313 | dear team , we observing MW_BER_SD Alarm at YNB0659 DIR TO YNB0292 , KIndly visit the site and check this issue | PCM-20251014-00000838 | dear team , we observing MW_BER_SD Alarm at YNB0659 DIR TO YNB0292 , KIndly visit the site and check this issue | dear team , we observing MW_BER_SD Alarm at YNB0659 DIR TO YNB0292 , KIndly visit the site and check this issue |  |  |  | API | 10/14/2025 10:10:30 | 10/15/2025 17:40:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000445 | PCM-20251014-00000851 | TT-20251014-00872 | Reference_telecom | Region_4 | SHB1M3671 | SHB0671 |  |  |  | Riasat Ali Allah Baksh | 10/14/2025 10:13:00 | 10/14/2025 10:14:17 | 10/14/2025 16:13:00 | CELL FAULTY (Failure in optical RP3 interface) at SHB1M3671-P2 @ Sceco | 10/14/2025 09:59:54 | Major | 7653 | CELL FAULTY | 10/14/2025 10:10:15 | P2 | 3G | qunfuddah | Sceco | LTE_Cell SA | SHB1M3671 | FLM_TE |  |  | PCM-20251014-00000848 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/14/2025 10:13:00 | 10/14/2025 10:14:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000458 | PCM-20251014-00000878 | TT-20251014-00893 | Telecom | Region_2 | RIY0647 | RIY0647 |  |  |  | Farmanullah Akbar Jan | 10/14/2025 10:26:36 | 10/14/2025 18:38:29 | 10/14/2025 14:26:36 | STC : LINK DOWN B/W RIY0443-RIY0647 | 10/14/2025 10:26:03 | Critical | 1-12843 | OSC_LOS | 10/14/2025 10:25:52 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0647 | FLM_TE | [5 empty] | 0-1-C-9-F1AST4-1(RM1/TM1(FROM RIY0443))-OSC:1 |  |  | API | 10/14/2025 10:26:36 | 10/14/2025 10:36:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000469 | PCM-20251014-00000893 | TT-20251008-01769 | MW_HC | Region_1 | HFF0838 | HFF0838 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/14/2025 10:30:55 | 10/14/2025 14:09:07 | 10/14/2025 22:30:55 | Huawei MW HC_P2 Observing Errors at HFF0838-HFF0839 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | hafouf | Power Cube | TX NSA | HFF0838-HFF0839 | FLM_TE | HFF0838 | dear team , link is flapping , kindly check locally | PCM-20251014-00000874 | dear team , link is flapping , kindly check locally | dear team , link is flapping , kindly check locally |  |  |  | API | 10/14/2025 10:30:55 | 10/14/2025 14:09:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000472 | PCM-20251014-00000903 | TT-20251014-00918 | Telecom | Region_2 | RY3-ASG-02 | RY3 | Transsmission | Fiber CUT | STC LL cut | DILSHAD ALI ABDUL HAMEED | 10/14/2025 10:35:36 | 10/15/2025 07:13:21 | 10/14/2025 16:35:36 | DWDM_Link down at RY3-ASG-02 @ Sceco_STB | 10/14/2025 10:26:00 | Major | 102-2601239 | Local Fault Alarm | 10/14/2025 10:29:18 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN SA | RY3-ASG-02 | FLM_TE | [8 empty] | API | 10/14/2025 10:35:36 | 10/15/2025 07:08:31 | 10/15/2025 07:09:58 |  |  | 10/15/2025 07:13:21 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000479 | PCM-20251014-00000911 | TT-20251014-00912 | Reference_telecom | Region_4 | SHB1M3671 | SHB0671 |  |  |  | Riasat Ali Allah Baksh | 10/14/2025 10:41:01 | 10/14/2025 11:25:47 | 10/14/2025 16:41:01 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at SHB1M3671-P2 @ Sceco | 10/14/2025 10:04:42 | Major | 7771 | WCDMA CELL OUT OF USE | 10/14/2025 10:02:35 | P2 | 3G | qunfuddah | Sceco | 3G SA | SHB1M3671 | FLM_TE |  |  | PCM-20251014-00000898 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/14/2025 10:41:01 | 10/14/2025 11:25:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000496 | PCM-20251014-00000946 | TT-20251014-00948 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Riasat Ali Allah Baksh | 10/14/2025 10:57:32 | 10/14/2025 13:08:31 | 10/14/2025 16:57:32 | 1(2G/3G/LTE) sites down under SHB0671-P2/SHB0671-P2 @ Sceco | 10/14/2025 10:49:04 | Major | 7706 | BTS O&M LINK FAILURE | 10/14/2025 10:49:01 | P2 | 2G | qunfuddah | Sceco | 2G SA | SHB0671-P2 | FLM_TE | SHB0671 | Results: DOWN SITE HUB SHB0671-P2 SHB0671 Summary: Hub: SHB0671, Down Count: 1, Down Sites: SHB0671-P2 Alarm Summary: SHB0671 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/14/2025 10:57:32 | 10/14/2025 11:25:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000506 | PCM-20251014-00000966 | TT-20251014-00890 | Reference_telecom | Region_4 | JED0647 | JED0647 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 11:09:11 | 10/15/2025 12:24:08 | 10/14/2025 23:09:11 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED0647-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/14/2025 09:52:15 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/14/2025 09:52:10 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0647 | FLM_TE |  |  | PCM-20251014-00000871 | Please check the ABIO is down DH241610227 | Please check the ABIO is down DH241610227 |  |  |  | API | 10/14/2025 11:09:11 | 10/14/2025 12:23:26 | 10/14/2025 13:11:14 | 10/14/2025 13:11:16 | 10/14/2025 13:11:18 | 10/15/2025 12:24:08 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000544 | PCM-20251014-00001022 | TT-20251014-01029 | Telecom | Region_4 | JED1M8574 | JED2574 | Equipment | BTS_Cable | Replace Fiber Cable | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 11:36:17 | 10/15/2025 12:24:25 | 10/14/2025 17:36:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8574-CA-L900-P1-L800-SBTS @ Sceco | 10/14/2025 11:35:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 11:35:24 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8574 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 11:36:17 | 10/14/2025 12:23:27 | 10/14/2025 15:52:33 | 10/14/2025 15:52:35 | 10/14/2025 15:52:37 | 10/15/2025 12:24:25 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000582 | PCM-20251014-00001087 | TT-20251014-01111 | Reference_telecom | Region_1 | HFF6036 | HFF6036 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/14/2025 12:10:02 | 10/14/2025 14:09:08 | 10/15/2025 00:10:02 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFF6036-DCU2 @ Sceco | 10/14/2025 09:09:26 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/14/2025 09:09:24 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6036 | FLM_TE | [8 empty] | API | 10/14/2025 12:10:02 | 10/14/2025 14:09:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000586 | PCM-20251014-00001092 | TT-20251014-01115 | Telecom | Region_4 | JED0582 | JED0582 |  |  |  | MALIK ATIF ZAMAN | 10/14/2025 12:11:46 | 10/14/2025 14:21:53 | 10/15/2025 00:11:46 | As per BO request NEC MW link JED0582-JED0221 | 10/14/2025 12:10:31 | Minor | 113388 | LOF | 10/14/2025 12:10:37 | VIP | 2G | jeddah | Sceco | TX NSA | JED0582-JED0221 | FLM_TE | [8 empty] | API | 10/14/2025 12:11:46 | 10/14/2025 14:21:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000588 | PCM-20251014-00001096 | TT-20251014-01120 | Telecom | Region_4 | JED0215 | JED0215 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/14/2025 12:16:17 | 10/14/2025 12:16:17 | 10/15/2025 00:16:17 | As per BO request NSP MW link JED0215-JED0193 observing Low RSL | 10/14/2025 12:13:46 | Minor | 113388 | LOF | 10/14/2025 12:13:49 | P2 | 2G | jeddah | Sceco | TX NSA | JED0215-JED0193 | FLM_TE | [8 empty] | API | 10/14/2025 12:16:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000590 | PCM-20251014-00001102 | TT-20251014-01131 | Telecom | Region_5 | MAK1MN2523 | MAK2523 |  |  |  | Zakir Hossan | 10/14/2025 12:18:45 | 10/14/2025 18:32:41 | 10/15/2025 00:18:45 | PT:: FLM need to perform HC at MAK1MN2523 /R5 (BO request) | 10/14/2025 12:18:30 | Minor | 7115 | BASE STATION INFORMATION | 10/14/2025 12:18:30 | P3 | 5G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK1MN2523 | FLM_TE | [8 empty] | API | 10/14/2025 12:18:45 | 10/14/2025 18:32:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000643 | PCM-20251014-00001183 | TT-20251014-01066 | Reference_telecom | Region_2 | RIYD6030-CSG-01 | RIYB6030 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/14/2025 13:07:29 | 10/14/2025 17:11:29 | 10/15/2025 01:07:29 | Optical Invalid at RIYD6030-CSG-01 ¦¦ ref TT-20250825-02385 @ Sceco_STB | 10/13/2025 07:16:14 | Minor | 101-2505224 | Optical Invalid | 10/13/2025 07:14:48 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | RIYD6030-CSG-01 | FLM_TE |  |  | PCM-20251014-00001060 | received low power in below ports in P2 RIYD6030-CSG-01 , please change the SFP and fiber cable BOM mentioned for each port as below 0-5-3 34060686 0-6-2 34060689 0-4-3 34060687 Below sites will be impacted RIYD6031 RIYD6030 RIYD6032 | received low power in below ports in P2 RIYD6030-CSG-01 , please change the SFP and fiber cable BOM mentioned for each port as below 0-5-3 34060686 0-6-2 34060689 0-4-3 34060687 Below sites will be impacted RIYD6031 RIYD6030 RIYD6032 |  |  |  | API | 10/14/2025 13:07:29 | 10/14/2025 17:11:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000656 | PCM-20251014-00001212 | TT-20251014-01194 | Telecom | Region_6 | HJR0027 | HJR0027 | Equipment | SFP_BTS | Re-Plug SFP | SHAH KHALID | 10/14/2025 13:20:00 | 10/14/2025 14:02:57 | 10/15/2025 01:20:00 | WHJR0001 is complete down | 10/14/2025 12:42:35 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/14/2025 12:42:35 | P3 | 2G | makhwa | Sceco | Wifi SA | WHJR0001 | FLM_TE | HJR0027 | Hub: HJR0027 We are observing no alarm flapped from our end at the outage time kindly send the FLM, EM to check the site | PCM-20251014-00001166 | Hub: HJR0027 We are observing no alarm flapped from our end at the outage time kindly send the FLM, EM to check the site | Hub: HJR0027 We are observing no alarm flapped from our end at the outage time kindly send the FLM, EM to check the site |  |  |  | API | 10/14/2025 13:20:00 | 10/14/2025 13:26:23 | 10/14/2025 14:01:22 | 10/14/2025 14:01:45 |  | 10/14/2025 14:02:57 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000665 | PCM-20251014-00001233 | TT-20251014-01040 | Reference_telecom | Region_2 | RIY0906-ZRi04-3-CSG-03 | RIY0906 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/14/2025 13:25:49 | 10/14/2025 18:09:56 | 10/15/2025 01:25:49 | Optical Invalid at RIY0906-ZRi04-3-CSG-03 ¦¦ ref TT-20250906-01155 @ Sceco | 10/13/2025 12:02:25 | Minor | 101-2505224 | Optical Invalid | 10/13/2025 12:02:08 | VIP | IPRAN | riyadh | Sceco | IPRAN NSA | RIY0906-ZRi04-3-CSG-03 | FLM_TE |  |  | PCM-20251014-00001066 | change the SFP and Fiber in RIY0906-ZRi04-3-CSG-03 port 0-9-2 34060742 | change the SFP and Fiber in RIY0906-ZRi04-3-CSG-03 port 0-9-2 34060742 |  |  |  | API | 10/14/2025 13:25:49 | 10/14/2025 18:09:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000670 | PCM-20251014-00001240 | TT-20251014-01222 | Reference_telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/14/2025 13:29:00 | 10/16/2025 11:26:03 | 10/14/2025 17:29:00 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/14/2025 09:08:06 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 09:08:00 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE |  |  | PCM-20251014-00001184 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/14/2025 13:29:00 | 10/16/2025 11:26:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000676 | PCM-20251014-00001249 | TT-20251014-01224 | Reference_telecom | Region_4 | JED1M7839 | JED0839 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/14/2025 13:32:34 | 10/15/2025 11:26:16 | 10/14/2025 17:32:34 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1M7839-CA-L900-P1-VIP @ Sceco | 10/14/2025 13:00:50 | Critical | 7654 | CELL OPERATION DEGRADED | 10/14/2025 13:00:43 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7839 | FLM_TE |  |  | PCM-20251014-00001186 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/14/2025 13:32:34 | 10/15/2025 11:24:17 | 10/15/2025 11:26:10 |  |  | 10/15/2025 11:26:16 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014000698 | PCM-20251014-00001282 | TT-20251014-01318 | EM | [7 empty] | 10/14/2025 13:54:43 | 10/14/2025 13:54:43 | 10/14/2025 17:54:43 | BATTERY FAILURE ALARM at REPEATER-SEC0047_OCS @ Sceco | 10/14/2025 13:53:14 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/14/2025 13:53:04 | P1 | DWDM |  | Sceco | DWDM NSA | REPEATER | FLM_EM | [5 empty] | 0-TO AL-LITH-SEC0046(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/14/2025 13:54:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000699 | PCM-20251014-00001287 | TT-20251014-01321 | Telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/14/2025 13:57:48 | 10/15/2025 10:55:22 | 10/15/2025 01:57:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/14/2025 13:57:02 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 13:56:51 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0296 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 13:57:48 | 10/15/2025 10:55:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000714 | PCM-20251014-00001306 | TT-20251014-01345 | Telecom | Region_4 | JED0028 | JED0028 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 14:06:35 | 10/14/2025 14:06:35 | 10/14/2025 20:06:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0028-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/14/2025 14:05:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 14:05:53 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0028 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 14:06:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000730 | PCM-20251014-00001338 | TT-20251014-01376 | Telecom | Region_4 | JDAP1M7940 | JDAP0940 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/14/2025 14:23:33 | 10/17/2025 17:30:53 | 10/14/2025 20:23:33 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/14/2025 14:13:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 14:13:27 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JDAP1M7940 | FLM_TE |  |  | PCM-20251014-00001329 | Please check RSSI locally | Please check RSSI locally |  |  |  | API | 10/14/2025 14:23:33 | 10/16/2025 14:11:50 | 10/17/2025 17:30:46 |  |  | 10/17/2025 17:30:53 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000735 | PCM-20251014-00001346 | TT-20251014-01259 | Telecom | Region_1 | QRY2U6108 | QRY6008 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/14/2025 14:27:06 | 10/21/2025 11:37:55 | 10/15/2025 02:27:06 | Radio Link Failure at QRY2U6108-P3 @ Sceco | 10/14/2025 13:16:22 | Minor | 28008 | Radio Link Failure | 10/14/2025 13:14:49 | P3 | 2G | quriyat | Sceco | 2G NSA | QRY2U6108 | FLM_TE |  | Dears Kindly check HW | PCM-20251014-00001227 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/14/2025 14:27:06 | 10/14/2025 15:37:51 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251014000747 | PCM-20251014-00001373 | TT-20251014-01424 | EM | Region_6 | JIZ0120 | JIZ0120 |  |  |  | Adnan Nadeem Abdul Ghaffar | 10/14/2025 14:40:09 | 10/15/2025 01:30:17 | 10/15/2025 02:40:09 | RECTIFIER MAINS POWER FAILURE at JIZ0120-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/14/2025 14:32:13 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/14/2025 14:31:52 | P2 | 2G | jizan | Sceco | 2G NSA | JIZ0120 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/14/2025 14:40:09 | 10/14/2025 16:38:09 | 10/15/2025 01:30:17 | [8 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000751 | PCM-20251014-00001378 | TT-20251014-01425 | EM | Region_4 | JDJZ1M8418 | JDJZ2418 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/14/2025 14:42:13 | 10/14/2025 17:08:40 | 10/15/2025 02:42:13 | TOWER LIGHT at JDJZ1M8418-G9-L8-L18-SBTS-CAP @ Generator_SG | 10/14/2025 14:34:05 | Minor | 7103 | TOWER LIGHT | 10/14/2025 14:33:58 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JDJZ1M8418 | FLM_EM | [5 empty] | TOWER LIGHT |  |  | API | 10/14/2025 14:42:13 | 10/14/2025 17:08:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000752 | PCM-20251014-00001381 | TT-20251014-01430 | Reference_telecom | Region_4 | BHR1M7332 | BHR0332 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 14:43:15 | 10/14/2025 14:56:43 | 10/15/2025 02:43:15 | BASE STATION INFORMATION (Unit temperature is high) at BHR1M7332-P3-L800-CA @ Sceco | 10/14/2025 14:03:04 | Minor | 7115 | BASE STATION INFORMATION | 10/14/2025 14:02:53 | P3 | 4G | jeddah | Sceco | LTE NSA | BHR1M7332 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/14/2025 14:43:15 | 10/14/2025 14:56:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000775 | PCM-20251014-00001410 | TT-20251014-01462 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/14/2025 14:57:15 | 10/15/2025 17:08:51 | 10/15/2025 02:57:15 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/14/2025 14:49:10 | Minor | 7103 | AIRCON 2 FAILURE | 10/14/2025 14:49:00 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/14/2025 14:57:15 | 10/15/2025 17:08:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000797 | PCM-20251014-00001447 | TT-20251014-01504 | EM | Region_4 | KHY1M8251 | KHY2251 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/14/2025 15:15:47 | 10/14/2025 18:54:07 | 10/15/2025 03:15:47 | GENERATOR RUNING ALARM at KHY1M8251-G9-L8-SBTS-P3 @ Generator_SG | 10/14/2025 15:07:38 | Minor | 7103 | GENERATOR RUNING ALARM | 10/14/2025 15:07:30 | P3 | 4G | jeddah | Generator_SG | LTE NSA | KHY1M8251 | FLM_EM | [5 empty] | GENERATOR RUNING ALARM |  |  | API | 10/14/2025 15:15:47 | 10/14/2025 18:54:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000808 | PCM-20251014-00001472 | TT-20251014-01523 | EM | Region_2 | ZRN0245 | ZRN0245 | Enviroment | Air Condition | Change compressor | Mohamed Moustafa Aboelmagd Hefny | 10/14/2025 15:25:06 | 10/19/2025 10:29:05 | 10/15/2025 03:25:06 | Door opening alarm at ZRN0245-P2_SRAN @ Sceco | 10/14/2025 15:24:48 | Minor | 65101 | Door opening alarm | 10/14/2025 15:17:00 | P2 | SRAN | rumah | Sceco | 2G NSA | ZRN0245 | FLM_EM | [8 empty] | API | 10/14/2025 15:25:06 | 10/14/2025 17:26:25 | 10/19/2025 07:34:52 | 10/19/2025 07:34:56 | 10/19/2025 07:34:58 | 10/19/2025 10:29:05 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000813 | PCM-20251014-00001479 | TT-20251014-01528 | EM | Region_2 | ZRN0245 | ZRN0245 | Enviroment | Air Condition | Change compressor | Mohamed Moustafa Aboelmagd Hefny | 10/14/2025 15:27:10 | 10/19/2025 10:29:22 | 10/15/2025 03:27:10 | Air condition 1 failure alarm at ZRN0245-P2_SRAN @ Sceco | 10/14/2025 15:24:48 | Minor | 65104 | Air condition 1 failure alarm | 10/14/2025 15:17:00 | P2 | SRAN | rumah | Sceco | 2G NSA | ZRN0245 | FLM_EM | [8 empty] | API | 10/14/2025 15:27:10 | 10/14/2025 17:26:26 | 10/19/2025 07:34:26 | 10/19/2025 07:34:29 | 10/19/2025 07:34:34 | 10/19/2025 10:29:22 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251014000823 | PCM-20251014-00001491 | TT-20251014-01529 | Telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/14/2025 15:32:31 | 10/15/2025 10:55:24 | 10/14/2025 21:32:31 | 1(5G) sites down under JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/14/2025 15:24:25 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/14/2025 15:24:23 | P2 | 2G | jeddah | Sceco | 5G SA | JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF | FLM_TE | JED0296 | Results: DOWN SITE HUB JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF JED0296 Summary: Hub: JED0296, Down Count: 1, Down Sites: JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF Alarm Summary: JED0296 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.232.108:8080] [URL:http://10.97.232.108:8080/NE3S/1.0/] | sites down |  | API | 10/14/2025 15:32:31 | 10/15/2025 10:55:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000833 | PCM-20251014-00001506 | TT-20251014-01559 | Telecom | Region_4 | JED1M8066 | JED2066 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/14/2025 15:40:35 | 10/19/2025 17:44:19 | 10/14/2025 21:40:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8066-CA-L800-SBTS-P3 @ Generator_SG | 10/14/2025 15:39:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 15:39:33 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 15:40:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000843 | PCM-20251014-00001529 | TT-20251014-01245 | Reference_telecom | Region_5 | MAK1MN2022 | MAK2022 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/14/2025 15:53:40 | 10/14/2025 15:53:40 | 10/14/2025 21:53:40 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at MAK1MN2022-NR2.6-P3 @ Sceco | 10/14/2025 12:46:34 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/14/2025 12:46:27 | P3 | 5G | makkah | Sceco | 5G NSA | MAK1MN2022 | FLM_TE |  |  | PCM-20251014-00001210 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/14/2025 15:53:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000846 | PCM-20251014-00001533 | TT-20251008-01917 | MW_HC | Region_5 | MKTF9070 | MKTF9070 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/14/2025 15:57:03 | 10/14/2025 16:29:57 | 10/15/2025 03:57:03 | NEC MW HC_P0 Observing Modem Down at MKTF0635(10.154.125.241)--MKTF9070(10.154.125.242) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | Repeater | makkah | Generator_SG | TX NSA | MKTF0635(10.154.125.241)--MKTF9070(10.154.125.242) | FLM_TE |  |  | PCM-20251014-00001498 | Please share the RCA plus start & end time of action | Please share the RCA plus start & end time of action |  |  |  | API | 10/14/2025 15:57:03 | 10/14/2025 16:29:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000847 | PCM-20251014-00001535 | TT-20251014-01332 | Reference_telecom | Region_4 | JED0695 | JED0695 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/14/2025 15:57:13 | 10/14/2025 15:57:13 | 10/14/2025 19:57:13 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0695-P1-HUB @ Sceco | 10/14/2025 13:52:40 | Critical | 7602 | BCF NOTIFICATION | 10/14/2025 13:52:25 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0695 | FLM_TE |  |  | PCM-20251014-00001297 | Please check SM locally | Please check SM locally |  |  |  | API | 10/14/2025 15:57:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000865 | PCM-20251014-00001567 | TT-20251014-01624 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/14/2025 16:15:41 | 10/14/2025 16:15:41 | 10/14/2025 22:15:41 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/14/2025 16:12:06 | Major | 1-12545 | LOCAL_FAULT | 10/14/2025 16:11:54 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE | [5 empty] | 1-ELC(1-E)-2-G1M520S-9(RX7/TX7)-CLIENT:1 |  |  | API | 10/14/2025 16:15:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000873 | PCM-20251014-00001583 | TT-20251014-01636 | Telecom | Region_4 | JED1U6831 | JED6131 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/14/2025 16:25:01 | 10/17/2025 17:30:29 | 10/14/2025 22:25:01 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/14/2025 16:14:24 | Major | 7654 | CELL OPERATION DEGRADED | 10/14/2025 16:14:15 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251014-00001578 | Please check the VSWR issue | Please check the VSWR issue |  |  |  | API | 10/14/2025 16:25:01 | 10/16/2025 14:11:51 | 10/17/2025 17:30:22 |  |  | 10/17/2025 17:30:29 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000905 | PCM-20251014-00001632 | TT-20251014-01689 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 16:48:41 | 10/14/2025 16:48:41 | 10/14/2025 22:48:41 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/14/2025 16:38:57 | Major | 7114 | CELL SERVICE PROBLEM | 10/14/2025 16:38:46 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251014-00001619 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/14/2025 16:48:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000914 | PCM-20251014-00001644 | TT-20251014-01700 | Reference_telecom | Region_5 | MAK0995 | MAK0995 |  |  |  | Atif Javed Javed Hussain | 10/14/2025 16:53:34 | 10/16/2025 11:26:05 | 10/14/2025 20:53:34 | 2(2G) 2(LTE) 2(5G) Site down under MAK0995-P1-VIP-HRM,MAK0753-P1-VIP-HRM (Ref: TT-20251014-01477 ) | 10/14/2025 15:00:18 | Critical | 7706 | BTS O&M LINK FAILURE | 10/14/2025 15:00:18 | VIP | 2G | makkah | Sceco | 2G_LTE_5G SA | MAK0995-P1-VIP-HRM,MAK0753-P1-VIP-HRM | FLM_TE | MAK0995 | Results: DOWN SITE HUB MAK0995-P1-VIP-HRM MAK0995 MAK0753-P1-VIP-HRM MAK0753 Summary: Hub: MAK0995, Down Count: 1, Down Sites: MAK0995-P1-VIP-HRM Hub: MAK0753, Down Count: 1, Down Sites: MAK0753-P1-VIP-HRM Alarm Summary: MAK0995 No Active Alarm on HUB MAK0753 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/14/2025 16:53:34 | 10/16/2025 11:26:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000918 | PCM-20251014-00001650 | TT-20251014-01644 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/14/2025 16:57:42 | 10/14/2025 19:49:47 | 10/14/2025 22:57:42 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TURY0826-P2 @ Sceco | 10/14/2025 16:23:11 | Major | 7607 | TRX OPERATION DEGRADED | 10/14/2025 16:23:08 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TURY0826 | FLM_TE |  |  | PCM-20251014-00001589 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/14/2025 16:57:42 | 10/14/2025 19:49:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000937 | PCM-20251014-00001683 | TT-20251014-01743 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/14/2025 17:16:39 | 10/15/2025 10:12:21 | 10/14/2025 23:16:39 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/14/2025 14:16:21 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/14/2025 14:16:08 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/14/2025 17:16:39 | 10/15/2025 10:12:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000952 | PCM-20251014-00001703 | TT-20251014-01770 | Reference_telecom | Region_6 | ARS0315 | ARS0315 | Transsmission | IPBB Fluctuation | Reset SFP | Zeshan Ali Adnan | 10/14/2025 17:27:42 | 10/16/2025 14:17:27 | 10/15/2025 05:27:42 | NEC MW Observing Module at ARS0315(10.1.174.51) | 10/09/2025 23:18:15 | Minor |  | LOF | 10/09/2025 23:18:15 | P2 | 2G | jizan | Sceco | TX NSA | ARS0315(10.1.174.51) | FLM_TE | [8 empty] | API | 10/14/2025 17:27:42 | 10/14/2025 19:20:15 | 10/16/2025 14:16:45 |  |  | 10/16/2025 14:17:27 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000956 | PCM-20251014-00001708 | TT-20251014-01774 | Reference_telecom | Region_1 | DMH0107 | DMH0107 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/14/2025 17:27:46 | 10/22/2025 11:33:42 | 10/15/2025 05:27:46 | NEC MW Observing LOF,Frame ID,LOF,Frame ID at DMH0107-2(10.159.105.165) | 10/09/2025 21:35:18 | Minor |  | LOF | 10/09/2025 21:35:18 | P1 | SRAN | hafr | Generator_DG | TX NSA | DMH0107-2(10.159.105.165) | FLM_TE | [8 empty] | API | 10/14/2025 17:27:46 | 10/14/2025 18:57:39 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014000959 | PCM-20251014-00001711 | TT-20251014-01777 | Reference_telecom | Region_6 | DRB0163 | DRB0163 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Muhammad Usman Muhammad Zia ul haq | 10/14/2025 17:27:50 | 10/21/2025 23:25:02 | 10/15/2025 05:27:50 | NEC MW Observing High BER at DRB0163(10.154.171.29) | 10/10/2025 17:40:14 | Minor |  | LOF | 10/10/2025 17:40:14 | P2 | 2G | derb | Sceco | TX NSA | DRB0163(10.154.171.29) | FLM_TE | [8 empty] | API | 10/14/2025 17:27:50 | 10/14/2025 18:23:51 | 10/21/2025 23:24:54 |  |  | 10/21/2025 23:25:02 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000960 | PCM-20251014-00001712 | TT-20251014-01778 | Reference_telecom | Region_4 | HAW0300 | HAW0300 |  |  |  | Rashid Shafique | 10/14/2025 17:27:50 | 10/14/2025 18:55:37 | 10/15/2025 05:27:50 | NEC MW Observing ODU CPU / Cable Open,FAN FAIL,ODU Power Supply at HAW0300-DIR CHAW0004(10.154.118.200) | 10/12/2025 02:14:25 | Minor |  | LOF | 10/12/2025 02:14:25 | P2 | 2G | taif | Generator_SG | TX NSA | HAW0300-DIR CHAW0004(10.154.118.200) | FLM_TE | [8 empty] | API | 10/14/2025 17:27:50 | 10/14/2025 18:55:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000963 | PCM-20251014-00001715 | TT-20251014-01781 | Reference_telecom | Region_4 | JDJZ0762 | JDJZ0762 |  |  |  | Riasat Ali Allah Baksh | 10/14/2025 17:27:54 | 10/16/2025 08:05:12 | 10/15/2025 05:27:54 | NEC MW Observing Low BER,High BER,LOF,Frame ID,LOF,Frame ID,LOF,Frame ID,LOF,Frame ID,High BER,Low BER,High BER,High BER at JDJZ0762(10.154.140.73) | 10/12/2025 04:20:48 | Minor |  | LOF | 10/12/2025 04:20:48 | P1 | 2G | jeddah | Sceco | TX NSA | JDJZ0762(10.154.140.73) | FLM_TE | [8 empty] | API | 10/14/2025 17:27:54 | 10/16/2025 08:05:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000968 | PCM-20251014-00001720 | TT-20251014-01786 | Reference_telecom | Region_4 | JDRS0756 | JDRS0756 |  |  |  | Khizer Hayat | 10/14/2025 17:27:59 | 10/15/2025 13:39:38 | 10/15/2025 05:27:59 | NEC MW Observing LOF,Frame ID,LOF,Frame ID,High BER at JDRS0756(10.154.113.83) | 10/11/2025 02:48:55 | Minor |  | LOF | 10/11/2025 02:48:55 | P1 | 2G | jeddah | Generator_SG | TX NSA | JDRS0756(10.154.113.83) | FLM_TE | [8 empty] | API | 10/14/2025 17:27:59 | 10/15/2025 13:39:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000969 | PCM-20251014-00001721 | TT-20251014-01787 | Reference_telecom | Region_6 | KHS0339 | KHS0339 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/14/2025 17:28:01 | 10/14/2025 19:23:01 | 10/15/2025 05:28:01 | NEC MW Observing ODU CPU / Cable Open,LOF at KHS0339-1(10.89.220.39) | 10/04/2025 06:43:30 | Minor |  | LOF | 10/04/2025 06:43:30 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KHS0339-1(10.89.220.39) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:01 | 10/14/2025 19:23:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000971 | PCM-20251014-00001723 | TT-20251014-01790 | Reference_telecom | Region_4 | MKJD0573 | MKJD0573 |  |  |  | Amjad Ali Muhammad Parves | 10/14/2025 17:28:03 | 10/15/2025 09:37:06 | 10/15/2025 05:28:03 | NEC MW Observing ODU Alarm,TX Power at MKJD0573(10.154.128.249) | 10/13/2025 13:21:12 | Minor |  | LOF | 10/13/2025 13:21:12 | P3 | 2G | jeddah | Generator_SG | TX NSA | MKJD0573(10.154.128.249) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:03 | 10/15/2025 09:37:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000972 | PCM-20251014-00001724 | TT-20251014-01791 | Reference_telecom | Region_4 | MKMD0560 | MKMD0560 |  |  |  | Khizer Hayat | 10/14/2025 17:28:04 | 10/15/2025 13:39:39 | 10/15/2025 05:28:04 | NEC MW Observing High BER at MKMD0560 -1(10.154.119.222) | 10/11/2025 02:51:42 | Minor |  | LOF | 10/11/2025 02:51:42 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0560 -1(10.154.119.222) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:04 | 10/15/2025 13:39:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000980 | PCM-20251014-00001732 | TT-20251014-01799 | Reference_telecom | Region_6 | WDS0457 | WDS0457 |  |  |  | Ahmed Mamdouh Helal Helal | 10/14/2025 17:28:14 | 10/16/2025 00:48:43 | 10/15/2025 05:28:14 | NEC MW Observing SFP Type Mismatch at WDS0457(10.1.171.245) | 10/13/2025 17:26:33 | Minor |  | LOF | 10/13/2025 17:26:33 | P2 | 2G | wadi dawasar | Sceco | TX NSA | WDS0457(10.1.171.245) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:14 | 10/16/2025 00:48:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000983 | PCM-20251014-00001735 | TT-20251014-01802 | Reference_telecom | Region_4 | TAF0170 | TAF0170 |  |  |  | Ahmad Kamal Abdelmawla | 10/14/2025 17:28:17 | 10/14/2025 20:35:46 | 10/15/2025 05:28:17 | NEC MW Observing High BER at TAF0170-RYMK0540(NEW)(10.154.118.65) | 10/12/2025 04:09:42 | Minor |  | LOF | 10/12/2025 04:09:42 | P1 | 2G | taif | Sceco_STB | TX NSA | TAF0170-RYMK0540(NEW)(10.154.118.65) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:17 | 10/14/2025 20:35:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000985 | PCM-20251014-00001737 | TT-20251014-01804 | Reference_telecom | Region_1 | TBJ0955 | TBJ0955 |  |  |  | SARFARAZ MUHAMMAD HUSSAIN | 10/14/2025 17:28:19 | 10/14/2025 18:37:13 | 10/15/2025 05:28:19 | NEC MW Observing LOF,LOF,RX Level,RX Level at TBJ0955-3(10.147.9.193) | 10/09/2025 17:10:54 | Minor |  | LOF | 10/09/2025 17:10:54 | P1 | SRAN | quriyat | Sceco | TX NSA | TBJ0955-3(10.147.9.193) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:19 | 10/14/2025 18:37:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014000989 | PCM-20251014-00001741 | TT-20251014-01808 | Reference_telecom | Region_3 | YNB0308 | YNB0308 |  |  |  | Muhammad Sajjad R3 | 10/14/2025 17:28:24 | 10/15/2025 17:40:55 | 10/15/2025 05:28:24 | NEC MW Observing Low BER at YNB0308(10.101.186.156) | 09/30/2025 15:27:16 | Minor |  | LOF | 09/30/2025 15:27:16 | P3 | SRAN | yanbu | Sceco | TX NSA | YNB0308(10.101.186.156) | FLM_TE | [8 empty] | API | 10/14/2025 17:28:24 | 10/15/2025 17:40:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014000998 | PCM-20251014-00001753 | TT-20251014-01752 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 17:40:16 | 10/14/2025 17:40:16 | 10/14/2025 23:40:16 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/14/2025 17:10:53 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/14/2025 17:10:48 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251014-00001686 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/14/2025 17:40:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014001041 | PCM-20251014-00001821 | TT-20251014-01907 | Telecom | Region_4 | JD1 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/14/2025 18:29:49 | 10/14/2025 23:37:51 | 10/15/2025 00:29:49 | BGP Status Changed On JED1-PE-01 | 10/14/2025 18:22:35 | Major | 1100476 | BGP Status Changed | 10/14/2025 18:22:35 | P1 | DWDM | jeddah | Sceco_STB | IPBB NSA | BGP Status Changed On JED1-PE-01 | FLM_TE | [5 empty] | BGP Status Changed On JED1-PE-01 |  |  | API | 10/14/2025 18:29:49 | 10/14/2025 23:37:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014001062 | PCM-20251014-00001857 | TT-20251014-01937 | Reference_telecom | Region_4 | HAW1M3328 | HAW0328 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Rashid Shafique | 10/14/2025 18:50:40 | 10/18/2025 19:32:40 | 10/15/2025 06:50:40 | BASE STATION NOTIFICATION (Fan failure) at HAW1M3328-P1-DIA @ Sceco | 10/14/2025 18:20:46 | Minor | 7652 | BASE STATION NOTIFICATION | 10/14/2025 18:20:28 | P1 | 3G | taif | Sceco | 3G NSA | HAW1M3328 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/14/2025 18:50:40 | 10/14/2025 18:55:38 | 10/18/2025 12:00:56 | 10/18/2025 12:00:59 | 10/18/2025 12:01:01 | 10/18/2025 19:32:40 |  | Rashid Shafique |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014001067 | PCM-20251014-00001867 | TT-20251014-01936 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/14/2025 18:55:01 | 10/15/2025 17:08:52 | 10/15/2025 00:55:01 | 1(2G/LTE/5G) sites down under JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/14/2025 18:46:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/14/2025 18:46:28 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED6020-GSM-P3 | FLM_EM | JED6020 | Results: DOWN SITE HUB JED6020-GSM-P3 JED6020 Summary: Hub: JED6020, Down Count: 1, Down Sites: JED6020-GSM-P3 Alarm Summary: JED6020 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/14/2025 18:55:01 | 10/15/2025 17:08:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014001077 | PCM-20251014-00001882 | TT-20251014-01958 | Telecom | Region_1 | DRN2M4073 | DRN2073 |  |  |  | AbdalHafiz Sirageldin Mohamed Yasin | 10/14/2025 19:09:32 | 10/21/2025 11:37:55 | 10/15/2025 01:09:32 | Outage-20251014-0057 : 1(LTE) sites down under DRN2073-P3 @ Sceco | 10/14/2025 19:04:29 | Major | 301 | NE Is Disconnected | 10/14/2025 14:14:12 | P3 | 3G | dammam | Sceco | LTE SA | DRN2073-P3 | FLM_TE | DRN2073 | Results: DOWN SITE HUB DRN2073-P3 DRN2073 Summary: Hub: DRN2073, Down Count: 1, Down Sites: DRN2073-P3 Alarm Summary: DRN2073 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/14/2025 19:09:32 | 10/14/2025 22:14:05 | [6 empty] | Huawei_RO |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014001087 | PCM-20251014-00001898 | TT-20251014-01962 | Telecom | Region_4 | JED1M7637 | JED0637 |  |  |  | MALIK ATIF ZAMAN | 10/14/2025 19:22:07 | 10/15/2025 10:10:46 | 10/15/2025 01:22:07 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED1M7637-P1-VIP-HUB-CA-L900-L800-SBTS @ Sceco | 10/14/2025 19:02:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 19:02:47 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7637 | FLM_TE |  |  | PCM-20251014-00001880 | Kindly check the fiber and SFP at site | Kindly check the fiber and SFP at site |  |  |  | API | 10/14/2025 19:22:07 | 10/15/2025 10:10:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014001094 | PCM-20251014-00001907 | TT-20251014-01993 | Reference_telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/14/2025 19:27:21 | 10/14/2025 19:27:21 | 10/15/2025 07:27:21 | RF Unit RX Channel RTWP/RSSI Unbalanced at MAK6018-DCU-P3 @ Sceco | 10/14/2025 16:27:20 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/14/2025 16:27:16 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/14/2025 19:27:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014001116 | PCM-20251014-00001944 | TT-20251014-02041 | Telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/14/2025 20:20:34 | 10/15/2025 10:10:47 | 10/15/2025 02:20:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8061-CA-L800-SBTS @ Sceco | 10/14/2025 20:19:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 20:19:36 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8061 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 20:20:34 | 10/15/2025 10:10:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014001125 | PCM-20251014-00001967 | TT-20251014-02066 | Telecom | Region_6 | WBSH0001 | WBSH0001 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Ansir Iqbal Muhammad Iqbal | 10/14/2025 20:40:22 | 10/19/2025 16:01:36 | 10/15/2025 08:40:22 | WBSH0001 Partial Down | 10/14/2025 20:33:21 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/14/2025 20:33:21 | P2 | WIFI | bisha | Sceco | Wifi SA | WBSH0001_1-1F-AP18 | FLM_TE | [8 empty] | API | 10/14/2025 20:40:22 | 10/14/2025 20:41:22 | 10/15/2025 02:21:26 | 10/15/2025 11:05:31 |  | 10/19/2025 16:01:36 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014001129 | PCM-20251014-00001976 | TT-20251014-02081 | Telecom | Region_4 | JED1M8146 | JED2146 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/14/2025 20:54:39 | 10/14/2025 20:54:39 | 10/15/2025 02:54:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8146-P3-CA-L800 @ Sceco | 10/14/2025 20:54:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 20:53:59 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8146 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 20:54:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014001136 | PCM-20251014-00001985 | TT-20251014-02088 | EM | [7 empty] | 10/14/2025 21:02:24 | 10/14/2025 21:02:24 | 10/15/2025 01:02:24 | LOW BATTERY VOLTAGE + BATTERY FAILURE ALARM at FARAS-SEC0001_OCS @ Sceco | 10/14/2025 21:00:28 | Critical | 1-12307 | LOW BATTERY VOLTAGE + BATTERY FAILURE ALARM | 10/14/2025 21:00:19 | P1 | DWDM |  | Sceco | DWDM NSA | FARAS | FLM_EM | [5 empty] | 0-TO HFF0018 (HF1)&SC2-SEC0002(1-A)-71-E1EFI-[LOW BATTERY VOLTAGE + BATTERY FAILURE ALARM]:3 |  |  | API | 10/14/2025 21:02:24 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014001150 | PCM-20251014-00002003 | TT-20251014-02075 | Telecom | Region_4 | JED0391 | JED0391 |  |  |  | BARKAT ALI MAIN HILAL | 10/14/2025 21:19:53 | 10/19/2025 17:44:48 | 10/15/2025 03:19:53 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED0391-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/14/2025 20:43:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 20:43:35 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0391 | FLM_TE |  |  | PCM-20251014-00001973 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/14/2025 21:19:53 | 10/15/2025 10:55:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251014001162 | PCM-20251014-00002030 | TT-20251014-02129 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 21:39:05 | 10/19/2025 17:44:19 | 10/15/2025 03:39:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/14/2025 21:38:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 21:38:17 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 21:39:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014001163 | PCM-20251014-00002031 | TT-20251014-02123 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/14/2025 21:39:34 | 10/15/2025 07:55:13 | 10/15/2025 03:39:34 | 2(2G) 2(LTE) sites down under BHAB2091-P3,BHAB2103-P3/BHAB2103-P3 @ Generator_DG | 10/14/2025 21:29:10 | Major | 7706 | BTS O&M LINK FAILURE | 10/14/2025 21:29:06 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2103-P3 2G_LTE,BHAB2091-P3 2G_LTE | FLM_EM | BHAB2091 | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251014-00002026 | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: BHAB2091 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/14/2025 21:39:34 | 10/15/2025 07:55:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251014001172 | PCM-20251014-00002043 | TT-20251014-02143 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/14/2025 21:48:23 | 10/14/2025 21:48:23 | 10/15/2025 03:48:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/14/2025 21:47:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 21:47:35 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/14/2025 21:48:23 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251014001201 | PCM-20251014-00002093 | TT-20251014-02181 | EM | [7 empty] | 10/14/2025 22:20:04 | 10/14/2025 22:20:04 | 10/15/2025 04:20:04 | 1(2G/LTE) sites down under AQQ2426-P3/AQQ2426-P3 @ Generator_SG | 10/14/2025 22:11:45 | Major | 7706 | BTS O&M LINK FAILURE | 10/14/2025 22:11:41 | P3 | 2G |  | Generator_SG | 2G_LTE SA | AQQ2426-P3 | FLM_EM | AQQ2426 | Results: DOWN SITE HUB AQQ2426-P3 AQQ2426 Summary: Hub: AQQ2426, Down Count: 1, Down Sites: AQQ2426-P3 Alarm Summary: AQQ2426 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/14/2025 22:20:04 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014001206 | PCM-20251014-00002102 | TT-20251014-02201 | Telecom | Region_4 | JED0260 | JED0260 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/14/2025 22:33:32 | 10/15/2025 10:24:07 | 10/15/2025 04:33:32 | PT:: FLM Need to perform HC at JED0260-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 under R4. | 10/14/2025 22:33:04 | Major | 676767671 | Health Check-WO to TE FME | 10/14/2025 22:33:04 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0260-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | [8 empty] | API | 10/14/2025 22:33:32 | 10/15/2025 10:24:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251014001227 | PCM-20251014-00002140 | TT-20251014-02244 | EM | Region_6 | SRA1M8353 | SRA2353 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/14/2025 23:17:45 | 10/15/2025 07:52:34 | 10/15/2025 11:17:45 | RECTIFIER MODULE FAILURE at SRA1M8353-G9-L800-P3-SBTS @ Generator_SG | 10/14/2025 23:09:45 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/14/2025 23:09:34 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8353 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/14/2025 23:17:45 | 10/15/2025 07:52:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014001234 | PCM-20251014-00002154 | TT-20251014-02264 | EM | Region_6 | BHAB1M8011 | BHAB2011 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/14/2025 23:34:16 | 10/15/2025 07:55:13 | 10/15/2025 11:34:16 | RECTIFIER MODULE FAILURE at BHAB1M8011-CA-L800-SBTS-P3 @ Generator_SG | 10/14/2025 23:26:11 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/14/2025 23:26:00 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8011 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/14/2025 23:34:16 | 10/15/2025 07:55:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251014001235 | PCM-20251014-00002155 | TT-20251014-02238 | Reference_telecom | Region_1 | DAM2M8802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/14/2025 23:35:08 | 10/15/2025 00:54:53 | 10/15/2025 11:35:08 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M8802-CA-L800-FWA-P1-VIP @ Sceco | 10/14/2025 20:12:34 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/14/2025 20:12:32 | P3 | 4G | dammam | Sceco | 2G NSA | DAM2M8802 | FLM_TE |  |  | PCM-20251014-00002137 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/14/2025 23:35:08 | 10/15/2025 00:54:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251014001249 | PCM-20251014-00002176 | TT-20251014-02245 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/14/2025 23:59:44 | 10/17/2025 17:30:18 | 10/15/2025 03:59:44 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/14/2025 23:11:14 | Critical | 7654 | CELL OPERATION DEGRADED | 10/14/2025 23:11:07 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251014-00002142 | Check the VSWR issue active at site | Check the VSWR issue active at site |  |  |  | API | 10/14/2025 23:59:44 | 10/16/2025 14:11:51 | 10/17/2025 17:30:09 |  |  | 10/17/2025 17:30:18 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000001 | PCM-20251015-00000001 | TT-20251014-02248 | Telecom | Region_4 | USMD0699 | USMD0699 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/15/2025 00:00:05 | 10/15/2025 23:51:10 | 10/15/2025 06:00:05 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at USMD0699-GSM-P3 @ Sceco | 10/14/2025 23:18:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 23:18:11 | P3 | 2G | taif | Sceco | 5G_Cell SA | USMD0699 | FLM_TE |  |  | PCM-20251014-00002143 | Check the RSSI alarm active at site. | Check the RSSI alarm active at site. |  |  |  | API | 10/15/2025 00:00:05 | 10/15/2025 23:51:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000002 | PCM-20251015-00000002 | TT-20251015-00001 | EM | Region_1 | RYHR0632 | RYHR0632 | Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator | Essam Salah Marsa Hassan | 10/15/2025 00:00:06 | 10/23/2025 20:01:03 | 10/15/2025 12:00:06 | Air condition 2 failure alarm at RYHR0632-P3_SRAN @ Generator_SG | 10/14/2025 23:58:02 | Minor | 65105 | Air condition 2 failure alarm | 10/14/2025 22:44:24 | P3 | SRAN | hafr | Generator_SG | 2G NSA | RYHR0632 | FLM_EM | [8 empty] | API | 10/15/2025 00:00:06 | 10/15/2025 00:23:23 | 10/23/2025 20:00:54 |  |  | 10/23/2025 20:01:03 |  | Essam Salah Marsa Hassan | Vandalism |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000006 | PCM-20251015-00000007 | TT-20251015-00005 | Telecom | Region_4 | JED0361 | JED0361 | Equipment | SFP_BTS | Replace SFP | Khaled Mohammad Abdallah | 10/15/2025 00:03:11 | 10/16/2025 00:21:37 | 10/15/2025 06:03:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0361-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Sceco | 10/15/2025 00:02:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 00:02:14 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0361 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 00:03:11 |  | 10/15/2025 06:00:05 | 10/15/2025 06:00:08 | 10/15/2025 06:00:10 | 10/16/2025 00:21:37 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000008 | PCM-20251015-00000009 | TT-20251015-00010 | EM | Region_1 | KB2 | KB2 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/15/2025 00:06:18 | 10/15/2025 10:09:16 | 10/15/2025 06:06:18 | Door opening alarm at KB2-Main Shelter-Core-P1 @ Sceco_STB | 10/15/2025 00:05:59 | Major | 65101 | Door opening alarm | 10/15/2025 00:05:56 | P1 | DWDM | dammam | Sceco_STB | 2G NSA | KB2 | FLM_EM | [8 empty] | API | 10/15/2025 00:06:18 | 10/15/2025 10:09:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000010 | PCM-20251015-00000012 | TT-20251014-02171 | Telecom | Region_4 | JED1M7667 | JED0667 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 00:07:27 | 10/15/2025 10:10:48 | 10/15/2025 12:07:27 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED1M7667-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/14/2025 22:06:21 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 22:06:13 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7667 | FLM_TE |  |  | PCM-20251014-00002076 | Kindly check the over heating issue at site | Kindly check the over heating issue at site |  |  |  | API | 10/15/2025 00:07:27 | 10/15/2025 10:10:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000020 | PCM-20251015-00000028 | TT-20251015-00035 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/15/2025 00:23:21 | 10/15/2025 10:09:18 | 10/15/2025 04:23:21 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/15/2025 00:23:01 | Critical | 65334 | Door open Alarm Equipment room | 10/15/2025 00:22:57 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/15/2025 00:23:21 | 10/15/2025 10:09:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000035 | PCM-20251015-00000054 | TT-20251014-02100 | Telecom | Region_6 | MRD1M7092 | MRD0092 | Equipment | BSS_HW_fault | Replace RF Module | Fawad Khan | 10/15/2025 00:55:07 | 10/15/2025 02:22:13 | 10/15/2025 12:55:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at MRD1M7092-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/14/2025 21:10:51 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 21:10:39 | P3 | 4G | mohail | Sceco | 5G_Cell SA | MRD1M7092 | FLM_TE |  |  | PCM-20251015-00000039 | FLM need to check HW, SFP and fiber at site. | FLM need to check HW, SFP and fiber at site. |  |  |  | API | 10/15/2025 00:55:07 | 10/15/2025 02:19:03 | 10/15/2025 02:21:24 |  |  | 10/15/2025 02:22:13 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000048 | PCM-20251015-00000081 | TT-20251015-00102 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/15/2025 01:12:56 | 10/15/2025 10:12:22 | 10/15/2025 05:12:56 | The Device is offline at RIYB6066-CSG-01 @ Sceco | 10/15/2025 01:12:19 | Critical | 101-7 | The Device is offline | 10/15/2025 01:12:17 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/15/2025 01:12:56 | 10/15/2025 10:12:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000049 | PCM-20251015-00000083 | TT-20251015-00106 | Telecom | Region_2 | RIY0322(RY1) | RY2 |  |  |  | Saddam hussain muhammad khan | 10/15/2025 01:14:18 | 10/15/2025 01:14:18 | 10/15/2025 07:14:18 | REMOTE_FAULT alarm at RIY0322 (RY1) NCE | 10/15/2025 01:07:56 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/15/2025 01:07:56 | P1 | DWDM | riyadh | Sceco_STB_Rental | DWDM NSA | RIY0322 (RY1) | FLM_TE | [8 empty] | API | 10/15/2025 01:14:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000056 | PCM-20251015-00000107 | TT-20251015-00132 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/15/2025 01:25:21 | 10/15/2025 10:12:22 | 10/15/2025 13:25:21 | Chassis Fail at RIYB6066-CSG-01 @ Sceco | 10/15/2025 01:25:07 | Minor | 101-2505202 | Chassis Fail | 10/15/2025 01:18:35 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/15/2025 01:25:21 | 10/15/2025 10:12:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000062 | PCM-20251015-00000115 | TT-20251015-00146 | Reference_telecom | Region_1 | RSK2M8301 | RSK2301 | Equipment | BSS_HW_fault | Replace RRU | Mohamed Abdelaziz | 10/15/2025 01:34:08 | 10/15/2025 17:00:54 | 10/15/2025 07:34:08 | RF Unit VSWR Threshold Crossed at RSK2M8301-P2 @ Sceco | 10/14/2025 22:34:02 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/14/2025 22:33:49 | P2 | 4G | jubail | Sceco | LTE NSA | RSK2M8301 | FLM_TE | [8 empty] | API | 10/15/2025 01:34:08 | 10/15/2025 11:19:54 | 10/15/2025 16:20:03 | 10/15/2025 16:20:08 | 10/15/2025 16:20:43 | 10/15/2025 17:00:54 |  | Mohamed Abdelaziz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000083 | PCM-20251015-00000159 | TT-20251015-00204 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/15/2025 02:24:15 | 10/15/2025 10:09:23 | 10/15/2025 06:24:15 | Intruder Alarm - DC Floor2 at DM1MBSCH01 @ Generator_DG | 10/15/2025 02:23:39 | Critical | 65365 | Intruder Alarm - DC Floor2 | 10/15/2025 02:23:34 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/15/2025 02:24:15 | 10/15/2025 10:09:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000085 | PCM-20251015-00000161 | TT-20251015-00153 | Reference_telecom | Region_4 | JED2820 | JED2820 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 02:25:57 | 10/15/2025 10:10:49 | 10/15/2025 14:25:57 | Fronthaul loop back connectivity check failure at JED2820-G900-CA-NR2.6-SBTS-P3 @ Generator_SG | 10/15/2025 01:12:57 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/15/2025 01:12:47 | P4 | 2G | jeddah | Generator_SG | 2G NSA | JED2820 | FLM_TE |  |  | PCM-20251015-00000119 | FLM need to check RFM and fronthaul cabling at site. | FLM need to check RFM and fronthaul cabling at site. |  |  |  | API | 10/15/2025 02:25:57 | 10/15/2025 10:10:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000100 | PCM-20251015-00000183 | TT-20251015-00227 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 02:50:24 | 10/15/2025 10:10:50 | 10/15/2025 08:50:24 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/15/2025 02:36:23 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/15/2025 02:36:15 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251015-00000176 | FLM need to check ALD and VSWR at site. | FLM need to check ALD and VSWR at site. |  |  |  | API | 10/15/2025 02:50:24 | 10/15/2025 10:10:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000102 | PCM-20251015-00000184 | TT-20251015-00232 | Telecom | Region_1 | UQL-0282-NE40E-X2-PE01 | UQL0282 |  |  |  | Almmoez Almmoez | 10/15/2025 02:50:36 | 10/15/2025 10:41:11 | 10/15/2025 06:50:36 | The Device is offline at UQL-0282-NE40E-X2-PE01 @ Sceco | 10/15/2025 02:50:00 | Critical | 101-7 | The Device is offline | 10/15/2025 02:49:58 | P2 | IPRAN | rafha | Sceco | IPRAN SA | UQL-0282-NE40E-X2-PE01 | FLM_TE | [8 empty] | API | 10/15/2025 02:50:36 | 10/15/2025 10:41:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000103 | PCM-20251015-00000186 | TT-20251015-00234 | Telecom | Region_4 | JD1 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/15/2025 02:50:56 | 10/18/2025 22:41:31 | 10/15/2025 08:50:56 | Observing Optical Module Is Not Authorized at JED-SR-01 (100GE4/0/2) | 10/15/2025 02:41:52 | Major | 3065541 | The optical module is removed | 10/15/2025 02:41:52 | P1 | DWDM | jeddah | Sceco_STB | TTImpacISPNSA | Observing Optical Module Is Not Authorized at JED-SR-01 (100GE4/0/2) | FLM_TE | [5 empty] | Observing Optical Module Is Not Authorized at JED-SR-01 (100GE4/0/2) |  |  | API | 10/15/2025 02:50:56 | 10/18/2025 22:41:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000120 | PCM-20251015-00000214 | TT-20251015-00262 | Telecom | Region_1 | DMM1_vMSE_RN03_NEW_EOR | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/15/2025 03:13:21 | 10/15/2025 03:13:21 | 10/15/2025 07:13:21 | Board Invalid at DMM1_vMSE_RN03_NEW_EOR @ Sceco_STB | 10/15/2025 03:11:56 | Critical | 101-2505210 | Board Invalid | 10/15/2025 03:11:51 | P1 | IPBB | dammam | Sceco_STB | IPRAN SA | DMM1_vMSE_RN03_NEW_EOR | FLM_TE | [8 empty] | API | 10/15/2025 03:13:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000143 | PCM-20251015-00000255 | TT-20251015-00294 | Reference_telecom | Region_4 | HHR0459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 03:37:21 | 10/15/2025 10:10:50 | 10/15/2025 07:37:21 | 1(2G) site down under HHR0459-P1-VIP @ Sceco (REF_TT-20250929-01003) | 09/29/2025 07:33:43 | Critical | 7706 | BTS O&M LINK FAILURE | 09/29/2025 07:33:43 | VIP | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | HHR0459 | FLM_TE | HHR0459 | Results: DOWN SITE HUB HHR0459 HHR0459 Summary: Hub: HHR0459, Down Count: 1, Down Sites: HHR0459 Alarm Summary: HHR0459 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/15/2025 03:37:21 | 10/15/2025 10:10:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000147 | PCM-20251015-00000265 | TT-20251015-00325 | Reference_telecom | Region_1 | ABQ0509 | ABQ0509 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/15/2025 03:53:37 | 10/15/2025 08:20:22 | 10/15/2025 15:53:37 | RF Unit RX Channel RTWP/RSSI Unbalanced at ABQ0509-P3-USF_SRAN-PC @ Power Cube | 10/15/2025 00:53:19 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/15/2025 00:53:15 | P3 | SRAN | hafouf | Power Cube | 2G NSA | ABQ0509 | FLM_TE | [8 empty] | API | 10/15/2025 03:53:37 | 10/15/2025 08:20:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000160 | PCM-20251015-00000285 | TT-20251015-00345 | Reference_telecom | Region_4 | JED0411 | JED0411 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 04:16:19 | 10/15/2025 10:55:27 | 10/15/2025 16:16:19 | LagPortDown observed in JED0411 _6 towards 10.1.237.33 @ Sceco | 10/14/2025 16:16:42 | Minor |  | LagPortDown | 10/14/2025 16:16:11 | P1 | 2G | jeddah | Sceco | TX NSA | JED0411 | FLM_TE | [8 empty] | API | 10/15/2025 04:16:19 | 10/15/2025 10:55:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000161 | PCM-20251015-00000286 | TT-20251015-00346 | Reference_telecom | Region_4 | JED2985 | JED2985 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 04:16:50 | 10/15/2025 10:55:27 | 10/15/2025 16:16:50 | LossOfSignal observed in JED2985 towards 10.1.237.34 @ Sceco | 10/14/2025 16:16:44 | Minor |  | LossOfSignal | 10/14/2025 16:16:17 | P3 | 2G | jeddah | Sceco | TX NSA | JED2985 | FLM_TE | [8 empty] | API | 10/15/2025 04:16:50 | 10/15/2025 10:55:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000166 | PCM-20251015-00000293 | TT-20251015-00357 | Reference_telecom | Region_4 | BHR2323 | BHR2323 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/15/2025 04:23:33 | 10/15/2025 10:24:08 | 10/15/2025 16:23:33 | ReplaceableUnitMissing observed in BHR2323 towards 10.3.234.69 @ Sceco | 10/14/2025 16:23:18 | Minor |  | ReplaceableUnitMissing | 10/14/2025 16:23:14 | P3 | 2G | jeddah | Sceco | TX NSA | BHR2323 | FLM_TE | [8 empty] | API | 10/15/2025 04:23:33 | 10/15/2025 10:24:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000176 | PCM-20251015-00000311 | TT-20251015-00386 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/15/2025 04:52:02 | 10/15/2025 04:52:02 | 10/15/2025 10:52:02 | Observing Multiple Links Down at RYD-SR-01/02 Connected to Qwilt | 10/15/2025 04:42:51 | Major | 5000003 | Link Down | 10/15/2025 04:42:51 | P1 | BSC | riyadh | Sceco_STB | TTImpacISPNSA | Observing Multiple Links Down at RYD-SR-01/02 Connected to Qwilt | FLM_TE | [5 empty] | Observing Multiple Links Down at RYD-SR-01/02 Connected to Qwilt |  |  | API | 10/15/2025 04:52:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000196 | PCM-20251015-00000343 | TT-20251015-00421 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/15/2025 05:28:39 | 10/16/2025 11:26:07 | 10/15/2025 17:28:39 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/15/2025 05:20:15 | Minor | 7115 | BASE STATION INFORMATION | 10/15/2025 05:20:05 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/15/2025 05:28:39 | 10/16/2025 11:26:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000197 | PCM-20251015-00000346 | TT-20251015-00426 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 05:33:19 | 10/19/2025 17:44:21 | 10/15/2025 11:33:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/15/2025 05:32:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 05:32:31 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 05:33:19 | 10/15/2025 10:10:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000207 | PCM-20251015-00000360 | TT-20251015-00447 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/15/2025 05:57:04 | 10/16/2025 11:26:08 | 10/15/2025 09:57:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/15/2025 05:56:06 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 05:55:59 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 05:57:04 | 10/16/2025 11:26:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000210 | PCM-20251015-00000364 | TT-20251015-00451 | Reference_telecom | Region_5 | MKMD0551 | MKMD0551 |  |  |  | Amr Abdulla Ali Othman | 10/15/2025 06:00:40 | 10/15/2025 06:00:40 | 10/15/2025 18:00:40 | ReplaceableUnitMissing observed in MKMD0551_02 towards 10.21.70.165 @ Generator_DG | 10/15/2025 04:58:11 | Minor |  | ReplaceableUnitMissing | 10/15/2025 04:57:58 | P1 | 2G | makkah | Generator_DG | TX NSA | MKMD0551 | FLM_TE | [8 empty] | API | 10/15/2025 06:00:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000211 | PCM-20251015-00000365 | TT-20251015-00452 | Reference_telecom | Region_5 | MKMD0549 | MKMD0549 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/15/2025 06:00:40 | 10/18/2025 14:02:51 | 10/15/2025 18:00:40 | ReplaceableUnitMissing observed in MKMD0549_07 towards 10.21.70.161 @ Generator_DG | 10/15/2025 01:16:03 | Minor |  | ReplaceableUnitMissing | 10/15/2025 01:15:07 | P1 | 2G | makkah | Generator_DG | TX NSA | MKMD0549 | FLM_TE | [8 empty] | API | 10/15/2025 06:00:40 | 10/18/2025 14:02:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000212 | PCM-20251015-00000366 | TT-20251015-00454 | Reference_telecom | Region_5 | MKMD0549 | MKMD0549 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/15/2025 06:00:40 | 10/18/2025 14:02:52 | 10/15/2025 18:00:40 | ReplaceableUnitMissing observed in MKMD0549_03 towards 10.74.121.49 @ Generator_DG | 10/15/2025 04:17:49 | Minor |  | ReplaceableUnitMissing | 10/15/2025 04:17:45 | P1 | 2G | makkah | Generator_DG | TX NSA | MKMD0549 | FLM_TE | [8 empty] | API | 10/15/2025 06:00:40 | 10/18/2025 14:02:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000223 | PCM-20251015-00000389 | TT-20251015-00481 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/15/2025 06:20:48 | 10/15/2025 19:34:58 | 10/15/2025 18:20:48 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/15/2025 06:14:44 | Minor | 1589 | AC Overfrequency | 10/15/2025 06:14:44 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/15/2025 06:20:48 | 10/15/2025 09:17:23 | 10/15/2025 19:34:34 |  |  | 10/15/2025 19:34:58 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Stuck | CM20251015000226 | PCM-20251015-00000397 | TT-20251015-00415 | Telecom | [7 empty] | 10/15/2025 06:23:43 | 10/15/2025 06:23:43 | 10/15/2025 12:23:43 | BASE STATION ANTENNA LINE PROBLEM at MAK1U6745-G18-L18-L21-SBTS-P1-HRM @ Sceco | 10/15/2025 05:10:25 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/15/2025 05:10:14 | P1 | 4G |  | Sceco | LTE NSA | MAK1U6745 | FLM_TE |  |  | PCM-20251015-00000335 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/15/2025 06:23:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000234 | PCM-20251015-00000405 | TT-20251015-00479 | Reference_telecom | Region_5 | MAK0718 | MAK0718 |  |  |  | Amr Abdulla Ali Othman | 10/15/2025 06:27:39 | 10/15/2025 06:27:39 | 10/15/2025 12:27:39 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at MAK0718-G9-L8-L18-L21-NNR2.6-SBTS-P1-HUB-USF @ Sceco | 10/15/2025 05:49:29 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/15/2025 05:49:25 | P1 | 2G | makkah | Sceco | 2G NSA | MAK0718 | FLM_TE |  |  | PCM-20251015-00000386 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:27:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000239 | PCM-20251015-00000416 | TT-20251015-00056 | Telecom | Region_4 | JED1M7901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 06:28:47 | 10/15/2025 10:10:51 | 10/15/2025 12:28:47 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1M7901-CA-L800-P1-VIP-SBTS @ Sceco | 10/15/2025 00:30:31 | Major | 7114 | CELL SERVICE PROBLEM | 10/15/2025 00:30:22 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7901 | FLM_TE |  |  | PCM-20251015-00000041 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:28:47 | 10/15/2025 10:10:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000241 | PCM-20251015-00000417 | TT-20251014-02241 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 06:28:56 | 10/19/2025 17:44:48 | 10/15/2025 12:28:56 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/14/2025 23:10:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/14/2025 23:10:16 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2279 | FLM_TE |  |  | PCM-20251014-00002138 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:28:56 | 10/15/2025 10:55:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000242 | PCM-20251015-00000418 | TT-20251014-02233 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/15/2025 06:29:04 | 10/17/2025 17:29:59 | 10/15/2025 12:29:04 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/14/2025 23:00:15 | Major | 7654 | CELL OPERATION DEGRADED | 10/14/2025 23:00:09 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251014-00002134 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:29:04 | 10/16/2025 14:11:53 | 10/17/2025 17:29:54 |  |  | 10/17/2025 17:29:59 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000248 | PCM-20251015-00000425 | TT-20251015-00497 | Telecom | Region_4 | JED1U6049 | JED6149 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/15/2025 06:30:41 | 10/17/2025 17:29:49 | 10/15/2025 12:30:41 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at JED1U6049-P3-CA @ Sceco | 10/15/2025 06:20:25 | Major | 7654 | CELL OPERATION DEGRADED | 10/15/2025 06:20:18 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6049 | FLM_TE |  |  | PCM-20251015-00000413 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:30:41 | 10/16/2025 14:11:53 | 10/17/2025 17:29:40 |  |  | 10/17/2025 17:29:49 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000250 | PCM-20251015-00000426 | TT-20251015-00261 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/15/2025 06:30:49 | 10/21/2025 17:12:37 | 10/15/2025 12:30:49 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/15/2025 03:08:56 | Major | 7114 | CELL SERVICE PROBLEM | 10/15/2025 03:08:42 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251015-00000213 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:30:49 | 10/16/2025 14:11:54 | 10/17/2025 17:29:28 |  |  | 10/17/2025 17:29:35 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000252 | PCM-20251015-00000428 | TT-20251015-00503 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/15/2025 06:30:58 | 10/17/2025 17:29:20 | 10/15/2025 18:30:58 | RFC RF Port Input Power Out of Range at JED6008-DCU-P3 @ Sceco | 10/14/2025 20:09:47 | Minor | 28754 | RFC RF Port Input Power Out of Range | 10/14/2025 20:09:13 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/15/2025 06:30:58 | 10/16/2025 14:11:54 | 10/17/2025 17:29:14 |  |  | 10/17/2025 17:29:20 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000253 | PCM-20251015-00000429 | TT-20251015-00198 | Telecom | Region_4 | JED6021 | JED6021 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/15/2025 06:31:02 | 10/17/2025 17:28:49 | 10/15/2025 18:31:02 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6021-G9-L1800-L2100-SBTS-P3 @ Generator_SG | 10/15/2025 02:16:26 | Minor | 7114 | CELL SERVICE PROBLEM | 10/15/2025 02:16:19 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED6021 | FLM_TE |  |  | PCM-20251015-00000151 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/15/2025 06:31:02 | 10/16/2025 14:11:54 | 10/17/2025 17:28:42 |  |  | 10/17/2025 17:28:49 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000256 | PCM-20251015-00000435 | TT-20251015-00256 | Telecom | Region_2 | RIY0175 | RIY0175 | Equipment | SFP_BTS | Clean SFP | Ejaz Hussain Muhammad Sharif | 10/15/2025 06:32:36 | 10/15/2025 17:15:21 | 10/15/2025 10:32:36 | 2(2G) 2(LTE) sites down under RIYA6014-P3,RIY0175-P1-VIP/R2_RY1_HWBSC01 @ Sceco | 10/15/2025 03:05:32 | Critical | 21825 | CSL Fault | 10/15/2025 03:05:27 | VIP | SRAN | riyadh | Sceco | 2G_LTE SA | RIYA6014-P3 2G_LTE,RIY0175-P1-VIP 2G_LTE | FLM_TE | RIY0175 | Hub:- RIY0175 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251015-00000225 | EM team visited site and found no power issue | EM team visited site and found no power issue |  | sites down |  | API | 10/15/2025 06:32:36 | 10/15/2025 11:27:01 | 10/15/2025 11:28:05 | 10/15/2025 11:28:09 | 10/15/2025 12:29:21 | 10/15/2025 17:15:21 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000269 | PCM-20251015-00000456 | TT-20251015-00529 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/15/2025 06:43:55 | 10/15/2025 06:43:55 | 10/15/2025 12:43:55 | Observing ALU CIDs Down b/w RY, JED | 10/15/2025 06:34:00 | Major | 5000003 | Link Down | 10/15/2025 06:34:00 | P1 | BSC | riyadh | Sceco_STB | TTImpacISPNSA | Observing ALU CIDs Down b/w RY, JED | FLM_TE | [5 empty] | Observing ALU CIDs Down b/w RY, JED |  |  | API | 10/15/2025 06:43:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251012001207 | PCM-20251012-00001658 | TT-20251012-01760 | Reference_EM | Region_1 | ARR0919 | ARR0919 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/12/2025 18:53:53 | 10/14/2025 17:17:41 | 10/13/2025 00:53:53 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/12/2025 16:55:55 | Major | 65110 | Low battery voltage | 10/12/2025 16:55:51 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/12/2025 18:53:53 | 10/13/2025 14:13:21 | 10/14/2025 17:17:34 |  |  | 10/14/2025 17:17:41 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251012001214 | PCM-20251012-00001716 | TT-20251012-01773 | Telecom | Region_2 | RIY2219 | RIY2219 | Enviroment | SCECO_Failure | SCECO auto restored | Adel Abdelaziz Mohamed Ayedi | 10/12/2025 18:55:19 | 10/14/2025 14:39:42 | 10/13/2025 00:55:19 | BBU CPRI Interface Error at RIY2219-P2_SRAN @ Sceco | 10/12/2025 17:09:27 | Major | 26234 | BBU CPRI Interface Error | 10/12/2025 17:04:46 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2219 | FLM_EM |  |  | PCM-20251012-00001669 | power issue at site | power issue at site |  |  |  | API | 10/12/2025 18:55:19 | 10/12/2025 21:35:24 | 10/14/2025 13:33:40 | 10/14/2025 13:33:42 | 10/14/2025 13:33:44 | 10/14/2025 14:39:42 |  | Adel Abdelaziz Mohamed Ayedi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001230 | PCM-20251012-00001971 | TT-20251012-01792 | Telecom | Region_6 | QIS0031 | QIS0031 |  |  |  | Khurram Nawaz Muhammad Akram | 10/12/2025 19:04:59 | 10/18/2025 10:32:43 | 10/13/2025 01:04:59 | BASE STATION ANTENNA LINE PROBLEM at QIS1MT0031-P1 @ Sceco_STB | 10/12/2025 17:11:37 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/12/2025 17:11:27 | P1 | 4G | jizan | Sceco_STB | LTE NSA | QIS1MT0031 | FLM_EM |  |  | PCM-20251012-00001689 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/12/2025 19:04:59 | 10/12/2025 20:31:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251012001232 | PCM-20251012-00001975 | TT-20251012-02063 | EM | Region_6 | ARQ0019 | ARQ0019 |  |  |  | Khurram Nawaz Muhammad Akram | 10/12/2025 19:05:17 | 10/12/2025 20:31:54 | 10/13/2025 07:05:17 | HIGH TEMPERATURE 32 DEGREE C at ARQ1M7019-G9-L18-SBTS-P2 @ Sceco | 10/12/2025 18:09:58 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/12/2025 18:09:46 | P2 | 4G | jizan | Sceco | LTE NSA | ARQ1M7019 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/12/2025 19:05:17 | 10/12/2025 20:31:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001264 | PCM-20251012-00001610 | TT-20251012-01705 | Reference_EM | Region_2 | HIR0943 | HIR0943 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/12/2025 19:22:21 | 10/22/2025 17:49:37 | 10/13/2025 01:22:21 | Air condition 2 failure alarm at HIR0943-FWA-P1-VIP_SRAN @ Sceco | 10/12/2025 16:29:01 | Major | 65105 | Air condition 2 failure alarm | 10/12/2025 16:28:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | HIR0943 | FLM_EM | [8 empty] | API | 10/12/2025 19:22:21 | 10/22/2025 17:49:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Reject_FME | CM20251012001281 | PCM-20251012-00001093 | TT-20251012-01153 | EM | Region_4 | JED0961 | JED0961 |  |  |  | Hussein Sayed Salama Hussein | 10/12/2025 19:23:44 | 10/13/2025 14:05:00 | 10/13/2025 07:23:44 | RECTIFIER MODULE FAILURE at JED0961-G9-L18-L21-NR2.6-SBTS-P2-USF @ Generator_SG | 10/12/2025 12:27:40 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/12/2025 12:27:27 | P2 | 2G | jeddah | Generator_SG | 2G NSA | JED0961 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/12/2025 19:23:44 | 10/13/2025 13:47:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001295 | PCM-20251012-00001053 | TT-20251012-01114 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/12/2025 19:24:37 | 10/13/2025 15:02:10 | 10/13/2025 07:24:37 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/12/2025 12:05:14 | Minor | 7103 | AIRCON 1 FAILURE | 10/12/2025 12:05:05 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/12/2025 19:24:37 | 10/13/2025 15:02:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251012001310 | PCM-20251012-00001013 | TT-20251012-01069 | Reference_EM | Region_2 | RIY2586 | RIY2586 | Enviroment | Rectifier Module | Change rectifer module | Ajmal Hafeez Hafeez Ahmed Awan | 10/12/2025 19:25:37 | 10/14/2025 17:37:06 | 10/13/2025 07:25:37 | Minor Rec alarm at RIY2586-P3_SRAN-PC @ Sceco | 10/12/2025 11:27:47 | Minor | 65108 | Minor Rec alarm | 10/12/2025 11:27:42 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2586 | FLM_EM | [8 empty] | API | 10/12/2025 19:25:37 | 10/14/2025 15:56:18 | 10/14/2025 15:59:53 | 10/14/2025 15:59:56 | 10/14/2025 15:59:58 | 10/14/2025 17:37:06 |  | Ajmal Hafeez Hafeez Ahmed Awan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001315 | PCM-20251012-00000988 | TT-20251012-01046 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/12/2025 19:25:51 | 10/13/2025 00:40:58 | 10/13/2025 01:25:51 | high temprature 40 at DAM2066-P1-HUB_SRAN @ Sceco | 10/12/2025 11:15:01 | Major | 65103 | high temprature 40 | 10/12/2025 11:14:59 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/12/2025 19:25:51 | 10/13/2025 00:40:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001333 | PCM-20251012-00001174 | TT-20251012-01247 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/12/2025 19:28:36 | 10/13/2025 10:14:47 | 10/13/2025 07:28:36 | high temprature 40 at RYHF2036-P2_SRAN @ Generator_SG | 10/12/2025 13:13:54 | Minor | 65103 | high temprature 40 | 10/12/2025 13:13:50 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/12/2025 19:28:36 | 10/13/2025 10:14:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251012001382 | PCM-20251012-00001265 | TT-20251012-01335 | EM | Region_4 | GMK2154 | GMK2154 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Muhammad Rizwan Basharat Hussain | 10/12/2025 19:34:33 | 10/16/2025 23:50:32 | 10/13/2025 07:34:33 | Fire Alarm at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/12/2025 13:57:45 | Minor | 7103 | Fire Alarm | 10/12/2025 13:57:34 | P3 | 2G | jeddah | Generator_SG | 2G NSA | GMK2154 | FLM_EM | [5 empty] | Fire Alarm |  |  | API | 10/12/2025 19:34:33 | 10/12/2025 20:07:54 | 10/16/2025 23:50:22 |  |  | 10/16/2025 23:50:32 |  | Muhammad Rizwan Basharat Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001386 | PCM-20251012-00001235 | TT-20251012-01306 | Reference_EM | Region_1 | JBL0142 | JBL0142 |  |  |  | Mohamed Samir Farahat Allam | 10/12/2025 19:34:54 | 10/15/2025 22:25:04 | 10/13/2025 01:34:54 | Low battery voltage at JBL2M3142-P1 @ Sceco | 10/12/2025 13:37:34 | Major | 65110 | Low battery voltage | 10/12/2025 13:37:29 | P1 | 3G | jubail | Sceco | 3G NSA | JBL2M3142 | FLM_EM | [8 empty] | API | 10/12/2025 19:34:54 | 10/15/2025 22:25:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001390 | PCM-20251012-00002188 | TT-20251012-02268 | Reference_telecom | Region_2 | RYQ0955 | RYQ0955 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/12/2025 19:35:26 | 10/12/2025 22:07:28 | 10/13/2025 07:35:26 | IP Link Performance Measurement Fault at RYQ0955-P2_SRAN @ Generator_DG | 10/12/2025 15:18:22 | Minor | 25904 | IP Link Performance Measurement Fault | 10/12/2025 15:13:43 | P2 | SRAN | majma | Generator_DG | 2G NSA | RYQ0955 | FLM_EM |  |  | PCM-20251012-00002181 | RYQ0972 need to be restored | RYQ0972 need to be restored |  |  |  | API | 10/12/2025 19:35:26 | 10/12/2025 22:07:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251012001559 | PCM-20251012-00002449 | TT-20251012-02532 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/12/2025 22:48:35 | 10/14/2025 17:17:29 | 10/13/2025 10:48:35 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/12/2025 22:41:55 | Minor | 40564 | Genset Fault | 10/12/2025 22:41:55 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/12/2025 22:48:35 | 10/13/2025 14:13:23 | 10/14/2025 17:17:16 |  |  | 10/14/2025 17:17:29 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Accept | CM20251012001569 | PCM-20251012-00002462 | TT-20251012-02396 | Reference_telecom | Region_6 | BLG0211 | BLG0211 |  |  |  | Muhammad Tayyab | 10/12/2025 22:54:21 | 10/16/2025 18:35:53 | 10/13/2025 10:54:21 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BLG0211-G9-L8-L18-L21-P3-SBTS @ Generator_SG | 10/12/2025 19:23:48 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/12/2025 19:01:44 | P3 | 2G | jizan | Generator_SG | 2G NSA | BLG0211 | FLM_EM |  |  | PCM-20251012-00002332 | alarm appeared due to power issue | alarm appeared due to power issue |  |  |  | API | 10/12/2025 22:54:21 | 10/13/2025 09:18:33 | 10/16/2025 18:35:53 | [8 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001585 | PCM-20251012-00002486 | TT-20251012-02566 | EM | Region_6 | BCH0080 | BCH0080 |  |  |  | Sohail Nasir Mir Afzal | 10/12/2025 23:22:11 | 10/12/2025 23:42:53 | 10/13/2025 11:22:11 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at BCH0080-G9-NL8-L9-NL18-NR2.6-SBTS-P3 @ Sceco | 10/12/2025 23:13:55 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/12/2025 23:13:26 | P3 | 2G | Albaha | Sceco | 2G NSA | BCH0080 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/12/2025 23:22:11 | 10/12/2025 23:42:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251012001591 | PCM-20251012-00002495 | TT-20251012-02577 | EM | Region_6 | WDS0501 | WDS0501 |  |  |  | Ijaz Ahmad Ali Muhammad | 10/12/2025 23:38:45 | 10/13/2025 09:42:27 | 10/13/2025 11:38:45 | RECTIFIER MODULE FAILURE at WDS0501-G9-L8-L18-L21-NR2.6-P2-USF @ Sceco | 10/12/2025 23:30:34 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/12/2025 23:30:24 | P2 | 2G | wadi dawasar | Sceco | 2G NSA | WDS0501 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/12/2025 23:38:45 | 10/13/2025 09:42:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000007 | PCM-20251013-00000016 | TT-20251013-00018 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/13/2025 00:18:00 | 10/14/2025 08:54:42 | 10/13/2025 12:18:00 | SHELTER DOOR OPEN at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/13/2025 00:17:22 | Minor | 7103 | SHELTER DOOR OPEN | 10/13/2025 00:15:26 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/13/2025 00:18:00 | 10/14/2025 08:54:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000011 | PCM-20251013-00000021 | TT-20251013-00025 | EM | Region_4 | MLJI0098 | MLJI0098 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/13/2025 00:24:11 | 10/14/2025 08:54:42 | 10/13/2025 12:24:11 | RECTIFIER MODULE FAILURE at MLJI1M7098-G9-U9-ML8-SBTS-P3 @ Sceco | 10/13/2025 00:17:22 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/13/2025 00:15:26 | P3 | 4G | alaith | Sceco | LTE NSA | MLJI1M7098 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/13/2025 00:24:11 | 10/14/2025 08:54:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000041 | PCM-20251013-00000070 | TT-20251013-00071 | EM | Region_4 | RYMK0671 | RYMK0671 |  |  |  | Mohamed Elsaid Abdou Younes | 10/13/2025 00:55:20 | 10/14/2025 22:31:49 | 10/13/2025 04:55:20 | NE_COMMU_GNE_SWITCH at RYMK0671_OCS @ Sceco_STB | 10/13/2025 00:53:06 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/13/2025 00:53:03 | P1 | 2G | taif | Sceco_STB | DWDM NSA | RYMK0671 | FLM_EM | [5 empty] | NE RYMK0671_OCS's current GNE has been switched to standby GNE |  |  | API | 10/13/2025 00:55:20 | 10/14/2025 22:31:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251013000044 | PCM-20251013-00000069 | TT-20251013-00070 | EM | Region_4 | RYMK0671 | RYMK0671 |  |  |  | Mohamed Elsaid Abdou Younes | 10/13/2025 00:55:21 | 10/14/2025 22:31:49 | 10/13/2025 04:55:21 | NE_COMMU_GNE_SWITCH at RYMK0671_ELC @ Sceco_STB | 10/13/2025 00:53:06 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/13/2025 00:53:03 | P1 | 2G | taif | Sceco_STB | DWDM NSA | RYMK0671 | FLM_EM | [5 empty] | NE RYMK0671_ELC's current GNE has been switched to standby GNE |  |  | API | 10/13/2025 00:55:21 | 10/14/2025 22:31:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251013000099 | PCM-20251013-00000200 | TT-20251013-00204 | EM | Region_2 | RIY2221 | RIY2221 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 02:12:15 | 10/13/2025 07:23:41 | 10/13/2025 14:12:15 | Door opening alarm at RIY2221-P2_SRAN @ Sceco | 10/13/2025 02:11:32 | Minor | 65101 | Door opening alarm | 10/13/2025 02:04:02 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2221 | FLM_EM | [8 empty] | API | 10/13/2025 02:12:15 | 10/13/2025 07:23:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000100 | PCM-20251013-00000205 | TT-20251013-00209 | EM | Region_2 | RIY2287 | RIY2287 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/13/2025 02:12:20 | 10/22/2025 17:49:37 | 10/13/2025 08:12:20 | Door opening alarm at RIY2287-P1-DIA_SRAN @ Sceco | 10/13/2025 02:11:40 | Major | 65101 | Door opening alarm | 10/13/2025 02:03:09 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2287 | FLM_EM | [8 empty] | API | 10/13/2025 02:12:20 | 10/22/2025 17:49:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000102 | PCM-20251013-00000257 | TT-20251013-00262 | EM | Region_2 | RIY0414 | RIY0414 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/13/2025 02:13:45 | 10/13/2025 05:30:43 | 10/13/2025 08:13:45 | Air condition 2 failure alarm at RIY0414-P1-DIA-HUB_SRAN @ Sceco | 10/13/2025 02:06:05 | Major | 65105 | Air condition 2 failure alarm | 10/13/2025 02:03:15 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0414 | FLM_EM | [8 empty] | API | 10/13/2025 02:13:45 | 10/13/2025 05:30:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000103 | PCM-20251013-00000259 | TT-20251013-00264 | EM | Region_2 | RIY2287 | RIY2287 | Enviroment | Rectifier Module | Adding module due to load issue | Adham Adham Hassan Farghal | 10/13/2025 02:13:47 | 10/13/2025 16:56:16 | 10/13/2025 08:13:47 | Minor Rec alarm at RIY2287-P1-DIA_SRAN @ Sceco | 10/13/2025 02:11:40 | Major | 65108 | Minor Rec alarm | 10/13/2025 02:03:09 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2287 | FLM_EM | [8 empty] | API | 10/13/2025 02:13:47 | 10/13/2025 16:16:30 | 10/13/2025 16:18:48 | 10/13/2025 16:18:50 | 10/13/2025 16:19:05 | 10/13/2025 16:56:16 |  | Adham Adham Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000105 | PCM-20251013-00000267 | TT-20251013-00272 | EM | Region_2 | RIY2268 | RIY2268 | Enviroment | Air Condition | Change Fan | Vignesh Sivakumar Sivakumar | 10/13/2025 02:13:50 | 10/13/2025 15:54:55 | 10/13/2025 14:13:50 | Fire Fighting system alarm at RIY2268-P3_SRAN-PC @ Sceco | 10/13/2025 02:03:54 | Minor | 65111 | Fire Fighting system alarm | 10/13/2025 02:03:13 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2268 | FLM_EM | [8 empty] | API | 10/13/2025 02:13:50 | 10/13/2025 10:38:08 | 10/13/2025 15:29:03 | 10/13/2025 15:29:06 | 10/13/2025 15:29:08 | 10/13/2025 15:54:55 |  | Vignesh Sivakumar Sivakumar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000106 | PCM-20251013-00000270 | TT-20251013-00275 | EM | Region_2 | RIY0346 | RIY0346 |  |  |  | Adham Adham Hassan Farghal | 10/13/2025 02:13:51 | 10/15/2025 11:52:25 | 10/13/2025 14:13:51 | Minor Rec alarm at RIY0346-P2_SRAN @ Sceco | 10/13/2025 02:08:50 | Minor | 65108 | Minor Rec alarm | 10/13/2025 02:03:01 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0346 | FLM_EM | [8 empty] | API | 10/13/2025 02:13:51 | 10/13/2025 14:30:18 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000109 | PCM-20251013-00000285 | TT-20251013-00290 | EM | Region_2 | RIY0347 | RIY0347 |  |  |  | Adham Adham Hassan Farghal | 10/13/2025 02:14:16 | 10/15/2025 11:52:26 | 10/13/2025 14:14:16 | Air condition 1 failure alarm at RIY0347-P2_SRAN @ Sceco | 10/13/2025 02:11:59 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 02:03:32 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0347 | FLM_EM | [8 empty] | API | 10/13/2025 02:14:16 | 10/13/2025 14:30:18 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000110 | PCM-20251013-00000290 | TT-20251013-00295 | EM | Region_2 | RIY0590 | RIY0590 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/13/2025 02:14:21 | 10/15/2025 11:52:22 | 10/13/2025 08:14:21 | Air condition 1 failure alarm at RIY0590-P1-VVIP_SRAN @ Sceco | 10/13/2025 02:04:33 | Major | 65104 | Air condition 1 failure alarm | 10/13/2025 02:03:40 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0590 | FLM_EM | [8 empty] | API | 10/13/2025 02:14:21 | 10/13/2025 11:44:36 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013000111 | PCM-20251013-00000306 | TT-20251013-00310 | EM | Region_2 | RIY0389 | RIY0389 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 02:14:46 | 10/15/2025 11:52:15 | 10/13/2025 14:14:46 | Air condition 1 failure alarm at RIY0389-P2_SRAN-FON @ Sceco | 10/13/2025 02:11:44 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 02:03:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0389 | FLM_EM | [8 empty] | API | 10/13/2025 02:14:46 | 10/13/2025 07:23:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251013000113 | PCM-20251013-00000318 | TT-20251013-00323 | EM | Region_2 | RIY2221 | RIY2221 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 02:14:55 | 10/13/2025 07:23:42 | 10/13/2025 14:14:55 | high temprature 32 at RIY2221-P2_SRAN @ Sceco | 10/13/2025 02:11:32 | Minor | 65102 | high temprature 32 | 10/13/2025 02:04:02 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2221 | FLM_EM | [8 empty] | API | 10/13/2025 02:14:55 | 10/13/2025 07:23:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000114 | PCM-20251013-00000317 | TT-20251013-00322 | EM | Region_2 | RIY0615 | RIY0615 |  |  |  | Kadri Jalal Mohammed Asmail | 10/13/2025 02:14:58 | 10/15/2025 11:52:18 | 10/13/2025 14:14:58 | Air condition 2 failure alarm at RIY0615-P2_SRAN @ Sceco | 10/13/2025 02:11:37 | Minor | 65105 | Air condition 2 failure alarm | 10/13/2025 02:04:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0615 | FLM_EM | [8 empty] | API | 10/13/2025 02:14:58 | 10/13/2025 09:14:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000115 | PCM-20251013-00000326 | TT-20251013-00331 | EM | Region_2 | RIY0594 | RIY0594 |  |  |  | Kadri Jalal Mohammed Asmail | 10/13/2025 02:15:01 | 10/15/2025 11:52:18 | 10/13/2025 14:15:01 | Air condition 2 failure alarm at RIY0594-P2_SRAN @ Sceco | 10/13/2025 02:12:50 | Minor | 65105 | Air condition 2 failure alarm | 10/13/2025 02:03:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0594 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:01 | 10/13/2025 09:14:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000116 | PCM-20251013-00000325 | TT-20251013-00330 | EM | Region_2 | RIY0032 | RIY0032 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 02:15:02 | 10/15/2025 11:52:16 | 10/13/2025 08:15:02 | Air condition 1 failure alarm at RIY0032-P1-DIA_SRAN-FON @ Sceco | 10/13/2025 02:12:03 | Major | 65104 | Air condition 1 failure alarm | 10/13/2025 02:04:10 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0032 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:02 | 10/13/2025 07:23:43 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251013000117 | PCM-20251013-00000324 | TT-20251013-00329 | EM | Region_2 | RIY0416 | RIY0416 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 02:15:04 | 10/13/2025 07:23:43 | 10/13/2025 14:15:04 | Air condition 2 failure alarm at RIY0416-P2_SRAN @ Sceco | 10/13/2025 02:12:51 | Minor | 65105 | Air condition 2 failure alarm | 10/13/2025 02:04:16 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0416 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:04 | 10/13/2025 07:23:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013000118 | PCM-20251013-00000327 | TT-20251013-00332 | EM | Region_2 | RIY0789 | RIY0789 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/13/2025 02:15:05 | 10/22/2025 17:49:38 | 10/13/2025 08:15:05 | Air condition 1 failure alarm at RIY0789-P1-HUB_SRAN-FON @ Sceco | 10/13/2025 02:12:10 | Major | 65104 | Air condition 1 failure alarm | 10/13/2025 02:04:13 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0789 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:05 | 10/22/2025 17:49:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251013000119 | PCM-20251013-00000337 | TT-20251013-00340 | EM | Region_2 | RIY0345 | RIY0345 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 10/13/2025 02:15:21 | 10/15/2025 11:52:08 | 10/13/2025 08:15:21 | Door opening alarm at RIY0345-P1-VIP_SRAN @ Generator_SG | 10/13/2025 02:14:34 | Major | 65101 | Door opening alarm | 10/13/2025 02:03:47 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY0345 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:21 | 10/13/2025 02:31:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000120 | PCM-20251013-00000334 | TT-20251013-00337 | EM | Region_2 | RIY0368 | RIY0368 |  |  |  | Adham Adham Hassan Farghal | 10/13/2025 02:15:21 | 10/13/2025 14:30:19 | 10/13/2025 14:15:21 | Air condition 1 failure alarm at RIY0368-P2_SRAN @ Sceco | 10/13/2025 02:13:14 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 02:04:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0368 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:21 | 10/13/2025 14:30:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000121 | PCM-20251013-00000346 | TT-20251013-00349 | EM | Region_2 | RIY0437 | RIY0437 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/13/2025 02:15:51 | 10/15/2025 11:52:23 | 10/13/2025 14:15:51 | Fire Alarm at RIY0437-P2_SRAN @ Sceco | 10/13/2025 02:13:42 | Minor | 65119 | Fire Alarm | 10/13/2025 02:04:05 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0437 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:51 | 10/13/2025 11:44:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000122 | PCM-20251013-00000345 | TT-20251013-00347 | EM | Region_2 | RIY0400 | RIY0400 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/13/2025 02:15:51 | 10/15/2025 11:52:10 | 10/13/2025 14:15:51 | Air condition 2 failure alarm at RIY0400-P2_SRAN @ Sceco | 10/13/2025 02:13:41 | Minor | 65105 | Air condition 2 failure alarm | 10/13/2025 02:04:25 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0400 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:51 | 10/13/2025 03:11:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000123 | PCM-20251013-00000349 | TT-20251013-00352 | EM | Region_2 | RIY2410 | RIY2410 |  |  |  | Kadri Jalal Mohammed Asmail | 10/13/2025 02:15:55 | 10/15/2025 11:52:19 | 10/13/2025 14:15:55 | Air condition 2 failure alarm at RIY2410-P2_SRAN @ Sceco | 10/13/2025 02:13:34 | Minor | 65105 | Air condition 2 failure alarm | 10/13/2025 02:04:03 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2410 | FLM_EM | [8 empty] | API | 10/13/2025 02:15:55 | 10/13/2025 09:14:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013000125 | PCM-20251013-00000357 | TT-20251013-00361 | EM | Region_2 | RIY0662 | RIY0662 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/13/2025 02:16:21 | 10/21/2025 23:22:28 | 10/13/2025 14:16:21 | Generator failure at RIY0662-P2_SRAN @ Generator_SG | 10/13/2025 02:12:15 | Minor | 65114 | Generator failure | 10/13/2025 02:05:37 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0662 | FLM_EM | [8 empty] | API | 10/13/2025 02:16:21 | 10/21/2025 23:22:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251013000127 | PCM-20251013-00000378 | TT-20251013-00379 | EM | Region_2 | RIY2264 | RIY2264 | Enviroment | Rectifier Module | Adding module due to load issue | Adham Adham Hassan Farghal | 10/13/2025 02:16:50 | 10/13/2025 16:18:26 | 10/13/2025 08:16:50 | Major Rec alarm at RIY2264-P1-VIP_SRAN @ Sceco | 10/13/2025 02:14:50 | Major | 65107 | Major Rec alarm | 10/13/2025 02:02:57 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2264 | FLM_EM | [8 empty] | API | 10/13/2025 02:16:50 | 10/13/2025 14:30:18 | 10/13/2025 14:30:31 | 10/13/2025 14:30:33 | 10/13/2025 14:30:36 | 10/13/2025 16:18:26 |  | Adham Adham Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000128 | PCM-20251013-00000374 | TT-20251013-00377 | EM | Region_2 | RIY0345 | RIY0345 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 10/13/2025 02:16:51 | 10/15/2025 11:52:09 | 10/13/2025 08:16:51 | Air condition 1 failure alarm at RIY0345-P1-VIP_SRAN @ Generator_SG | 10/13/2025 02:14:34 | Major | 65104 | Air condition 1 failure alarm | 10/13/2025 02:03:47 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY0345 | FLM_EM | [8 empty] | API | 10/13/2025 02:16:51 | 10/13/2025 02:31:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000131 | PCM-20251013-00000393 | TT-20251013-00397 | EM | Region_2 | RIY2985 | RIY2985 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 02:17:30 | 10/13/2025 07:23:43 | 10/13/2025 14:17:30 | Low battery voltage at RIY2985-P3_SRAN @ Generator_DG | 10/13/2025 02:13:44 | Minor | 65110 | Low battery voltage | 10/13/2025 02:06:51 | P3 | SRAN | riyadh | Generator_DG | 2G NSA | RIY2985 | FLM_EM | [8 empty] | API | 10/13/2025 02:17:30 | 10/13/2025 07:23:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000133 | PCM-20251013-00000409 | TT-20251013-00410 | EM | Region_2 | RIY0404 | RIY0404 |  |  |  | Moin Uddin | 10/13/2025 02:18:22 | 10/13/2025 11:23:17 | 10/13/2025 14:18:22 | Low battery voltage at RIY0404-P2_SRAN @ Sceco | 10/13/2025 02:16:06 | Minor | 65110 | Low battery voltage | 10/13/2025 02:04:11 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0404 | FLM_EM | [8 empty] | API | 10/13/2025 02:18:22 | 10/13/2025 11:23:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000136 | PCM-20251013-00000416 | TT-20251013-00420 | EM | Region_2 | RIY2439 | RIY2439 |  |  |  | Vignesh Sivakumar Sivakumar | 10/13/2025 02:18:57 | 10/13/2025 10:38:08 | 10/13/2025 08:18:57 | Burglar Alarm at RIY2439-FWA-P1-VIP-SHOP-VIP_SRAN @ Sceco | 10/13/2025 02:18:22 | Major | 25672 | Burglar Alarm | 10/13/2025 02:04:48 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2439 | FLM_EM | [8 empty] | API | 10/13/2025 02:18:57 | 10/13/2025 10:38:08 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000139 | PCM-20251013-00000433 | TT-20251013-00437 | EM | Region_2 | RIY2374 | RIY2374 | Enviroment | Fire Alarm | Reset Fire Pannel | Tanveer Ahmad Fateh Muhammad | 10/13/2025 02:20:55 | 10/14/2025 13:55:29 | 10/13/2025 14:20:55 | Mains Failure at RIY2374-P3_SRAN-PC @ Sceco | 10/13/2025 02:18:42 | Minor | 65109 | Mains Failure | 10/13/2025 02:08:06 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2374 | FLM_EM | [8 empty] | API | 10/13/2025 02:20:55 | 10/13/2025 11:44:39 | 10/14/2025 13:46:33 | 10/14/2025 13:46:35 | 10/14/2025 13:46:37 | 10/14/2025 13:55:29 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000144 | PCM-20251013-00000438 | TT-20251013-00442 | EM | Region_2 | RIY0383 | RIY0383 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/13/2025 02:21:31 | 10/15/2025 11:52:11 | 10/13/2025 14:21:31 | Air condition 1 failure alarm at RIY0383-P3_SRAN-FON @ Sceco | 10/13/2025 02:19:20 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 02:07:58 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY0383 | FLM_EM | [8 empty] | API | 10/13/2025 02:21:31 | 10/13/2025 03:11:43 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251013000146 | PCM-20251013-00000445 | TT-20251013-00449 | EM | Region_2 | RIY0405 | RIY0405 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/13/2025 02:22:30 | 10/15/2025 11:52:14 | 10/13/2025 14:22:30 | Air condition 1 failure alarm at RIY0405-P2_SRAN @ Sceco | 10/13/2025 02:20:27 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 02:03:58 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0405 | FLM_EM | [8 empty] | API | 10/13/2025 02:22:30 | 10/13/2025 05:30:44 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000152 | PCM-20251013-00000460 | TT-20251013-00466 | EM | Region_2 | RIY0039 | RIY0039 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/13/2025 02:23:31 | 10/15/2025 11:52:12 | 10/13/2025 08:23:31 | high temprature 40 at RIY0039-P1-DIA-SHOP_SRAN @ Sceco | 10/13/2025 02:21:19 | Major | 65103 | high temprature 40 | 10/13/2025 02:08:30 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0039 | FLM_EM | [8 empty] | API | 10/13/2025 02:23:31 | 10/13/2025 03:11:44 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000155 | PCM-20251013-00000466 | TT-20251013-00474 | EM | Region_2 | RIY2274 | RIY2274 | Enviroment | SCECO_Failure | SCECO auto restored | Moin Uddin | 10/13/2025 02:24:00 | 10/13/2025 16:43:23 | 10/13/2025 14:24:00 | Mains Failure at RIY2274-P3_SRAN-PC @ Sceco | 10/13/2025 02:21:46 | Minor | 65109 | Mains Failure | 10/13/2025 02:07:42 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2274 | FLM_EM | [8 empty] | API | 10/13/2025 02:24:00 | 10/13/2025 11:23:19 | 10/13/2025 16:24:35 | 10/13/2025 16:24:38 | 10/13/2025 16:24:51 | 10/13/2025 16:43:23 |  | Moin Uddin |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000193 | PCM-20251013-00000530 | TT-20251013-00559 | EM | Region_6 | ABH0010 | ABH0010 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/13/2025 03:18:53 | 10/13/2025 10:09:57 | 10/13/2025 15:18:53 | AIRCON 1 FAILURE at ABH0010-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/13/2025 03:10:31 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 03:10:25 | P2 | 2G | abha | Sceco | 2G NSA | ABH0010 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 03:18:53 | 10/13/2025 10:09:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000196 | PCM-20251013-00000532 | TT-20251013-00560 | EM | Region_6 | ABH0031 | ABH0031 |  |  |  | Khalid Frahan Almesetef | 10/13/2025 03:19:22 | 10/13/2025 16:03:25 | 10/13/2025 15:19:22 | AIRCON 2 FAILURE at ABH0031-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/13/2025 03:10:55 | Minor | 7103 | AIRCON 2 FAILURE | 10/13/2025 03:10:39 | P3 | 2G | abha | Sceco | 2G NSA | ABH0031 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/13/2025 03:19:22 | 10/13/2025 16:03:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000218 | PCM-20251013-00000602 | TT-20251013-00632 | EM | Region_6 | ABH0157 | ABH0157 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/13/2025 03:46:11 | 10/13/2025 10:09:59 | 10/13/2025 09:46:11 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at ABH0157-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP @ Sceco | 10/13/2025 03:37:51 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/13/2025 03:37:45 | VIP | 2G | abha | Sceco | 2G NSA | ABH0157 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/13/2025 03:46:11 | 10/13/2025 10:09:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000244 | PCM-20251013-00000647 | TT-20251013-00677 | EM | Region_1 | RYHR0117 | RYHR0117 | Enviroment | Genset failure_High Temperature | Change Radiator fan | Essam Salah Marsa Hassan | 10/13/2025 04:18:46 | 10/13/2025 08:55:18 | 10/13/2025 16:18:46 | Door opening alarm at RYHR0117-P3_SRAN @ Generator_SG | 10/13/2025 04:18:03 | Minor | 65101 | Door opening alarm | 10/13/2025 04:18:00 | P3 | SRAN | hafr | Generator_SG | 2G NSA | RYHR0117 | FLM_EM | [8 empty] | API | 10/13/2025 04:18:46 | 10/13/2025 04:32:44 | 10/13/2025 04:32:50 | 10/13/2025 04:32:55 | 10/13/2025 05:44:50 | 10/13/2025 08:55:18 |  | Essam Salah Marsa Hassan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251013000261 | PCM-20251013-00000676 | TT-20251013-00715 | EM | Region_1 | RYHR0117 | RYHR0117 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Essam Salah Marsa Hassan | 10/13/2025 04:46:06 | 10/15/2025 17:28:58 | 10/13/2025 16:46:06 | Air condition 1 failure alarm at RYHR0117-P3_SRAN @ Generator_SG | 10/13/2025 04:39:31 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 04:35:35 | P3 | SRAN | hafr | Generator_SG | 2G NSA | RYHR0117 | FLM_EM | [8 empty] | API | 10/13/2025 04:46:06 | 10/13/2025 13:12:10 | 10/15/2025 17:28:48 |  |  | 10/15/2025 17:28:58 |  | Essam Salah Marsa Hassan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251013000274 | PCM-20251013-00000693 | TT-20251013-00729 | EM | Region_2 | SAM0576 | SAM0576 |  |  |  | Ahmed Mahmoud Mohamed Mahmoud | 10/13/2025 04:59:36 | 10/15/2025 11:52:14 | 10/13/2025 16:59:36 | Low battery voltage at SAM0576-P2_SRAN @ Sceco | 10/13/2025 04:51:55 | Minor | 65110 | Low battery voltage | 10/13/2025 04:48:50 | P2 | SRAN | buraidah | Sceco | 2G NSA | SAM0576 | FLM_EM | [8 empty] | API | 10/13/2025 04:59:36 | [7 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000305 | PCM-20251013-00000759 | TT-20251013-00792 | Reference_EM | Region_1 | YBR0613 | YBR0613 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Montasir Awadalla Abdalla Bala | 10/13/2025 05:53:51 | 10/16/2025 14:39:57 | 10/13/2025 17:53:51 | Air condition 1 failure alarm at YBR0613-P2-USF_SRAN-PC @ Power Cube | 10/13/2025 05:43:24 | Minor | 65104 | Air condition 1 failure alarm | 10/13/2025 05:43:19 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0613 | FLM_EM | [8 empty] | API | 10/13/2025 05:53:51 | 10/13/2025 12:21:06 | 10/16/2025 11:32:20 | 10/16/2025 11:33:18 | 10/16/2025 11:33:30 | 10/16/2025 14:39:57 |  | Montasir Awadalla Abdalla Bala |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251013000327 | PCM-20251013-00000787 | TT-20251013-00822 | EM | Region_6 | MKW9706 | MKW9706 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 10/13/2025 06:26:21 | 10/14/2025 02:20:26 | 10/13/2025 10:26:21 | Main Power at MKW9706_1 on 10.154.162.17 @ Sceco | 10/13/2025 06:24:18 | Critical | Main Power | Main Power | 10/13/2025 06:18:32 | P3 | Repeater | makhwa | Sceco | TX NSA | MKW9706 | FLM_EM | [8 empty] | API | 10/13/2025 06:26:21 | 10/13/2025 08:40:15 | 10/14/2025 02:20:14 |  |  | 10/14/2025 02:20:26 |  | Arif Ullah Shah |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251013000385 | PCM-20251013-00000872 | TT-20251013-00891 | EM | Region_2 | RIY2688 | RIY2688 | Enviroment | SCECO_Failure | SCECO auto restored | Adel Abdelaziz Mohamed Ayedi | 10/13/2025 07:14:26 | 10/14/2025 10:23:09 | 10/13/2025 19:14:26 | Low battery voltage at RIY2688-P2_SRAN @ Sceco | 10/13/2025 07:07:05 | Minor | 65110 | Low battery voltage | 10/13/2025 07:04:06 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2688 | FLM_EM | [8 empty] | API | 10/13/2025 07:14:26 | 10/13/2025 07:28:14 | 10/14/2025 09:53:58 | 10/14/2025 09:54:01 | 10/14/2025 10:15:35 | 10/14/2025 10:23:09 |  | Adel Abdelaziz Mohamed Ayedi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000420 | PCM-20251013-00000930 | TT-20251013-00951 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/13/2025 07:41:16 | 10/13/2025 15:08:37 | 10/13/2025 19:41:16 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/13/2025 07:30:49 | Minor | 65102 | high temprature 32 | 10/13/2025 07:30:46 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/13/2025 07:41:16 | 10/13/2025 15:08:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000427 | PCM-20251013-00000943 | TT-20251013-00961 | EM | Region_4 | JED0056 | JED0056 |  |  |  | Sajid Nazir Muhammad Nazir | 10/13/2025 07:51:05 | 10/13/2025 11:43:25 | 10/13/2025 19:51:05 | AIRCON 1 FAILURE at JED1M7056-P3-CA-L800 @ Sceco | 10/13/2025 07:42:26 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 07:42:21 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7056 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 07:51:05 | 10/13/2025 11:43:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000433 | PCM-20251013-00000950 | TT-20251013-00968 | EM | Region_4 | TAF0268 | TAF0268 |  |  |  | Walid Magdy Tawfik Elbana | 10/13/2025 07:54:41 | 10/13/2025 23:46:33 | 10/13/2025 19:54:41 | AIRCON 1 FAILURE at TAF0268-GSM-P3 @ Sceco | 10/13/2025 07:46:27 | Minor | 7103 | AIRCON 1 FAILURE | 10/13/2025 07:46:15 | P3 | 2G | taif | Sceco | 2G NSA | TAF0268 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/13/2025 07:54:41 | 10/13/2025 23:46:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000450 | PCM-20251013-00000970 | TT-20251013-00987 | EM | Region_4 | SHB0671 | SHB0671 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/13/2025 08:07:05 | 10/14/2025 06:56:02 | 10/13/2025 20:07:05 | HIGH TEMPERATURE 32 DEGREE C at SHB0671-P2 @ Sceco | 10/13/2025 07:58:47 | Minor | 7407 | HIGH TEMPERATURE 32 DEGREE C | 10/13/2025 07:58:43 | P2 | 2G | qunfuddah | Sceco | 2G NSA | SHB0671 | FLM_EM | [8 empty] | API | 10/13/2025 08:07:05 | 10/14/2025 06:56:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000479 | PCM-20251013-00001012 | TT-20251013-01031 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/13/2025 08:39:05 | 10/13/2025 14:46:44 | 10/13/2025 20:39:05 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/13/2025 08:32:36 | Minor | 40564 | Genset Fault | 10/13/2025 08:32:36 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/13/2025 08:39:05 | 10/13/2025 09:15:49 | 10/13/2025 14:46:32 |  |  | 10/13/2025 14:46:44 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013000489 | PCM-20251013-00001025 | TT-20251013-01043 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/13/2025 08:52:35 | 10/22/2025 17:49:38 | 10/13/2025 20:52:35 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/13/2025 08:41:47 | Minor | 65107 | Major Rec alarm | 10/13/2025 08:41:44 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/13/2025 08:52:35 | 10/22/2025 17:49:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000508 | PCM-20251013-00001063 | TT-20251013-01080 | EM | Region_2 | RIY0289 | RIY0289 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/13/2025 09:08:35 | 10/14/2025 13:21:55 | 10/13/2025 21:08:35 | Air condition 2 failure alarm at RIY0289-P2_SRAN @ Sceco | 10/13/2025 09:02:35 | Minor | 65105 | Air condition 2 failure alarm | 10/13/2025 08:57:53 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0289 | FLM_EM | [8 empty] | API | 10/13/2025 09:08:35 | 10/14/2025 13:21:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000546 | PCM-20251013-00001137 | TT-20251013-01157 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/13/2025 09:42:41 | 10/14/2025 04:52:19 | 10/13/2025 21:42:41 | Genset not in auto mode at SMN0805-P3_SRAN @ Generator_DG | 10/13/2025 09:34:18 | Minor | 65113 | Genset not in auto mode | 10/13/2025 09:32:01 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/13/2025 09:42:41 | 10/14/2025 04:52:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000597 | PCM-20251013-00001250 | TT-20251013-01275 | EM | Region_1 | DAM0314 | DAM0314 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/13/2025 10:38:31 | 10/23/2025 11:12:39 | 10/13/2025 16:38:31 | 1(2G/3G/LTE) sites down under DAM0314-P2/R1_DM_HWBSC01 @ Sceco | 10/13/2025 10:29:59 | Major | 21825 | CSL Fault | 10/13/2025 10:29:55 | P2 | 2G | dammam | Sceco | 2G_3G_LTE SA | DAM0314-P2 | FLM_EM |  | Results: DOWN SITE HUB DAM0314-P2 DAM0314 Summary: Hub: DAM0314, Down Count: 1, Down Sites: DAM0314-P2 Alarm Summary: DAM0314 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/13/2025 10:38:31 | 10/13/2025 10:46:44 | 10/23/2025 11:09:02 |  |  | 10/23/2025 11:12:39 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251013000606 | PCM-20251013-00001269 | TT-20251013-01301 | EM | Region_4 | SQR0200 | SQR0200 |  |  |  | Faiz Muhammad Ghulam Sarwar | 10/13/2025 10:48:45 | 10/13/2025 10:48:45 | 10/13/2025 22:48:45 | RECTIFIER MODULE FAILURE at SQR0200-GSM-UMTS-P2-USF @ Generator_SG | 10/13/2025 10:40:12 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/13/2025 10:40:05 | P2 | 2G | adam | Generator_SG | 2G NSA | SQR0200 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/13/2025 10:48:45 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000641 | PCM-20251013-00001341 | TT-20251013-01390 | EM | Region_4 | SHB0670 | SHB0670 |  |  |  | Walid Fathi Abdelmottaleb Elbayoumi | 10/13/2025 11:21:21 | 10/14/2025 06:56:03 | 10/13/2025 23:21:21 | SHELTER DOOR OPEN at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/13/2025 11:20:53 | Minor | 7103 | SHELTER DOOR OPEN | 10/13/2025 11:20:44 | P3 | 4G | qunfuddah | Sceco | LTE NSA | SHB1M7670 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/13/2025 11:21:21 | 10/14/2025 06:56:03 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000656 | PCM-20251013-00001367 | TT-20251013-01422 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/13/2025 11:36:50 | 10/13/2025 13:58:39 | 10/13/2025 17:36:50 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/13/2025 11:26:07 | Major | 65110 | Low battery voltage | 10/13/2025 11:26:04 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/13/2025 11:36:50 | 10/13/2025 13:58:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000666 | PCM-20251013-00001379 | TT-20251013-01432 | EM | Region_2 | KHJ0001 | KHJ0001 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/13/2025 11:43:00 | 10/20/2025 14:40:44 | 10/13/2025 23:43:00 | Low battery voltage at KHJ0001-P2-USF_SRAN-PC @ Power Cube | 10/13/2025 11:36:41 | Minor | 65110 | Low battery voltage | 10/13/2025 11:32:27 | P2 | SRAN | al kharj | Power Cube | 2G NSA | KHJ0001 | FLM_EM | [8 empty] | API | 10/13/2025 11:43:00 | 10/20/2025 14:40:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000719 | PCM-20251013-00001454 | TT-20251013-01516 | EM | Region_4 | JED0296 | JED0296 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/13/2025 12:28:30 | 10/13/2025 18:42:52 | 10/14/2025 00:28:30 | HIGH TEMPERATURE 32 DEGREE C at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/13/2025 12:20:04 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/13/2025 12:19:55 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0296 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/13/2025 12:28:30 | 10/13/2025 18:42:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000779 | PCM-20251013-00001548 | TT-20251013-01593 | Reference_EM | Region_1 | QLB0006 | QLB0006 |  |  |  | Elsaid Adel Mohamed Abouhegara | 10/13/2025 13:10:50 | 10/14/2025 12:55:22 | 10/14/2025 01:10:50 | Generator Failure(SH1) at QLB2M7006-P3-PC @ Power Cube | 10/13/2025 13:00:27 | Minor | 65046 | Generator Failure(SH1) | 10/13/2025 13:00:25 | P3 | 4G | quriyat | Power Cube | 2G NSA | QLB2M7006 | FLM_EM | [8 empty] | API | 10/13/2025 13:10:50 | 10/14/2025 12:55:22 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000808 | PCM-20251013-00001596 | TT-20251013-01651 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/13/2025 13:35:06 | 10/13/2025 15:26:02 | 10/14/2025 01:35:06 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/13/2025 13:24:43 | Minor | 65102 | high temprature 32 | 10/13/2025 13:24:39 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/13/2025 13:35:06 | 10/13/2025 15:26:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000839 | PCM-20251013-00001658 | TT-20251013-01760 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/13/2025 13:59:56 | 10/13/2025 18:03:20 | 10/14/2025 01:59:56 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/13/2025 13:49:41 | Minor | 65102 | High temperature 32C alarm | 10/13/2025 13:49:37 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/13/2025 13:59:56 | 10/13/2025 18:03:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000900 | PCM-20251013-00001743 | TT-20251012-02009 | Reference_telecom | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/13/2025 14:41:16 | 10/13/2025 18:03:21 | 10/14/2025 02:41:16 | MW RTN Observing ETH_LOS,ETH_LOS,PLA_MEMBER_DOWN_EXT,PLA_MEMBER_DOW at DAM2066_NE_3_SDB | 10/02/2025 20:28:00 | Minor |  | LOF | 10/02/2025 20:28:00 | P1 | SRAN | dammam | Sceco | TX NSA | DAM2066_NE_3_SDB | FLM_EM |  |  | PCM-20251012-00001914 | escalate to LATIS due to access issue at DAM2066escalate to LATIS due to access issue at DAM2066 | escalate to LATIS due to access issue at DAM2066 |  |  |  | API | 10/13/2025 14:41:16 | 10/13/2025 18:03:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013000933 | PCM-20251013-00001815 | TT-20251012-02510 | Telecom | Region_4 | JED2382 | JED2382 |  |  |  | Muhammad Javed Muhammad Anwar | 10/13/2025 15:07:55 | 10/13/2025 15:09:36 | 10/14/2025 03:07:55 | BASE STATION INFORMATION (No module fan detected) at JED1MN2382-NR2.6-P3 @ Sceco | 10/12/2025 22:23:42 | Minor | 7115 | BASE STATION INFORMATION | 10/12/2025 22:23:52 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN2382 | FLM_EM |  |  | PCM-20251012-00002427 | as site imparting due to load issue. | as site imparting due to load issue. |  |  |  | API | 10/13/2025 15:07:55 | 10/13/2025 15:09:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013000936 | PCM-20251013-00001818 | TT-20251013-00915 | Reference_telecom | Region_1 | SLW2996 | SLW2996 | Enviroment | Genset failure_Pump | Change Fuel Pump | Ayman Ibrahim Mohamed Elayad | 10/13/2025 15:09:05 | 10/14/2025 08:31:54 | 10/14/2025 03:09:05 | MW_LOF at SLWB2048_NE_4_H @ Sceco_STB | 10/13/2025 03:25:39 | Minor | 1-631 | MW_LOF | 10/13/2025 03:25:27 | P3 | SRAN | hafouf | Generator_SG | TX NSA | SLWB2048 | FLM_EM |  | Hub:- SLW2996 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251013-00001798 | Hub:- SLW2996 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- SLW2996 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/13/2025 15:09:05 | 10/14/2025 08:21:47 | 10/14/2025 08:31:33 |  |  | 10/14/2025 08:31:54 |  | Ayman Ibrahim Mohamed Elayad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013001138 | PCM-20251013-00002062 | TT-20251013-02181 | EM | Region_6 | TLT0809 | TLT0809 | Enviroment | Weak Battery/Sceco and Standby Gen | Site has dead BB and site was down during switching from SCECO to Generator | Amir Arif Ali | 10/13/2025 16:09:05 | 10/21/2025 09:56:33 | 10/14/2025 04:09:05 | GENERATOR1 + GENERATOR2 2 RUNNING at TLT0809-GSM-UMTS-P3 @ Generator_DG | 10/13/2025 16:00:21 | Minor | 7103 | GENERATOR1 + GENERATOR2 2 RUNNING | 10/13/2025 16:00:16 | P3 | 2G | turaib | Generator_DG | 2G NSA | TLT0809 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 RUNNING |  |  | API | 10/13/2025 16:09:05 | 10/13/2025 18:16:56 | 10/21/2025 09:55:53 | 10/21/2025 09:55:59 |  | 10/21/2025 09:56:33 |  | Amir Arif Ali |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013001164 | PCM-20251013-00002106 | TT-20251012-01742 | MW_HC | Region_2 | RIY0671 | RIY0671 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/13/2025 16:25:35 | 10/13/2025 20:50:21 | 10/14/2025 04:25:35 | (As per BO Request) Huawei MW HC At link RIY0808- RIY0671 as PM errors &alarms observed and T-Band flapping down | 10/12/2025 16:53:45 | Minor | 1-631 | MW_LOF | 10/12/2025 16:53:45 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0808- RIY0671 | FLM_EM |  |  | PCM-20251012-00001638 | power issue at site | power issue at site |  |  |  | API | 10/13/2025 16:25:35 | 10/13/2025 20:50:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013001215 | PCM-20251013-00002187 | TT-20251013-01951 | Telecom | Region_6 | NJR2036 | NJR2036 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/13/2025 16:57:45 | 10/13/2025 19:55:17 | 10/14/2025 04:57:45 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at NJR1M8036-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/13/2025 15:11:31 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/13/2025 07:06:42 | P1 | 4G | najran | Sceco | LTE NSA | NJR1M8036 | FLM_EM |  |  | PCM-20251013-00002037 | power issue | power issue |  |  |  | API | 10/13/2025 16:57:45 | 10/13/2025 17:08:05 | 10/13/2025 19:55:06 |  |  | 10/13/2025 19:55:17 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251013001240 | PCM-20251013-00002223 | TT-20251013-02310 | Reference_EM | Region_1 | ARR0919 | ARR0919 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Ismail Salah Ismail Elbery | 10/13/2025 17:11:35 | 10/14/2025 17:17:09 | 10/13/2025 23:11:35 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/13/2025 17:01:12 | Major | 65110 | Low battery voltage | 10/13/2025 17:01:09 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/13/2025 17:11:35 | 10/14/2025 17:16:50 | 10/14/2025 17:17:03 |  |  | 10/14/2025 17:17:09 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013001251 | PCM-20251013-00002245 | TT-20251013-02342 | EM | Region_4 | KMMD0719 | KMMD0719 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/13/2025 17:25:30 | 10/15/2025 07:06:20 | 10/14/2025 05:25:30 | RECTIFIER MODULE FAILURE at KMMD0719-GSM-P3 @ Sceco | 10/13/2025 17:17:08 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/13/2025 17:16:56 | P3 | 2G | jeddah | Sceco | 2G NSA | KMMD0719 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/13/2025 17:25:30 | 10/15/2025 07:06:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251013001252 | PCM-20251013-00002246 | TT-20251013-02343 | EM | Region_4 | KMMD0751 | KMMD0751 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/13/2025 17:25:35 | 10/15/2025 07:06:20 | 10/14/2025 05:25:35 | AIRCON 2 FAILURE at KMMD0751-GSM-P3 @ Sceco | 10/13/2025 17:17:03 | Minor | 7103 | AIRCON 2 FAILURE | 10/13/2025 17:16:57 | P3 | 2G | jeddah | Sceco | 2G NSA | KMMD0751 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/13/2025 17:25:35 | 10/15/2025 07:06:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001301 | PCM-20251013-00002313 | TT-20251013-02406 | EM | Region_4 | AQA0241 | AQA0241 |  |  |  | Yassir Omer Ibrahim Mahmoud | 10/13/2025 18:00:06 | 10/13/2025 22:33:12 | 10/14/2025 06:00:06 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at AQA1M7241-G9-L9-L8-L18-SBTS-P3 @ Generator_SG | 10/13/2025 17:53:09 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/13/2025 17:51:27 | P2 | 4G | adam | Generator_SG | LTE NSA | AQA1M7241 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/13/2025 18:00:06 | 10/13/2025 22:33:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001303 | PCM-20251013-00002315 | TT-20251013-02408 | EM | Region_1 | JBL0296 | JBL0296 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/13/2025 18:00:40 | 10/14/2025 02:01:37 | 10/14/2025 06:00:40 | Low battery voltage at JBL0296-P3-USF_SRAN-PC @ Power Cube | 10/13/2025 17:50:23 | Minor | 65110 | Low battery voltage | 10/13/2025 17:50:20 | P3 | SRAN | jubail | Power Cube | 2G NSA | JBL0296 | FLM_EM | [8 empty] | API | 10/13/2025 18:00:40 | 10/14/2025 02:01:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001364 | PCM-20251013-00002417 | TT-20251013-02506 | Reference_EM | Region_2 | RIY0446 | RIY0446 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/13/2025 19:04:10 | 10/22/2025 17:49:39 | 10/14/2025 07:04:10 | Minor Rec alarm at RIY0446-P2_SRAN @ Sceco | 10/13/2025 18:53:29 | Minor | 65108 | Minor Rec alarm | 10/13/2025 18:53:24 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0446 | FLM_EM | [8 empty] | API | 10/13/2025 19:04:10 | 10/22/2025 17:49:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001405 | PCM-20251013-00002474 | TT-20251013-02550 | EM | Region_2 | QSHL0737 | QSHL0737 |  |  |  | Ibrahim Abdou Ibrahim Abdou | 10/13/2025 19:43:30 | 10/13/2025 23:42:25 | 10/13/2025 23:43:30 | AMBIENT_TEMP_FLUCT at QSHL0737-LH NCE | 10/13/2025 19:39:51 | Critical | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/13/2025 19:39:51 | P1 | DWDM | buraidah | Sceco_STB_Rental | DWDM NSA | QSHL0737-LH | FLM_EM | [8 empty] | API | 10/13/2025 19:43:30 | 10/13/2025 23:42:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Accept | CM20251013001419 | PCM-20251013-00002502 | TT-20251013-02367 | Reference_telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Mahmoud Hefny Ali Ahmed | 10/13/2025 20:01:35 | 10/24/2025 02:01:44 | 10/14/2025 08:01:35 | BFD Session Fault at RYQ0955-P2_SRAN @ Generator_DG | 10/12/2025 15:18:22 | Minor | 25899 | BFD Session Fault | 10/12/2025 15:10:19 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0955 | FLM_EM |  |  | PCM-20251013-00002487 | RYQ0972 down ,need to be restored | RYQ0972 down ,need to be restored |  |  |  | API | 10/13/2025 20:01:35 | 10/13/2025 22:46:51 | 10/24/2025 02:01:44 | [8 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001420 | PCM-20251013-00002503 | TT-20251013-02366 | Reference_telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Mahmoud Hefny Ali Ahmed | 10/13/2025 20:03:00 | 10/13/2025 22:46:52 | 10/14/2025 08:03:00 | BFD Session Fault at RYQ0969-P1-VIP_SRAN @ Sceco | 10/12/2025 15:19:20 | Minor | 25899 | BFD Session Fault | 10/12/2025 15:14:32 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0969 | FLM_EM |  |  | PCM-20251013-00002484 | RYQ0972 down ,need to be restored | RYQ0972 down ,need to be restored |  |  |  | API | 10/13/2025 20:03:00 | 10/13/2025 22:46:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001422 | PCM-20251013-00002506 | TT-20251013-02365 | Reference_telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Mahmoud Hefny Ali Ahmed | 10/13/2025 20:04:50 | 10/13/2025 22:46:52 | 10/14/2025 08:04:50 | BFD Session Fault at RYQ0981-P3_SRAN @ Generator_SG | 10/12/2025 15:19:24 | Minor | 25899 | BFD Session Fault | 10/12/2025 15:13:57 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0981 | FLM_EM |  | Dear TRM BO,IPRAN. Kindly check the transmission link for below sites , they are fluctuated IP PM Activation Failure ,BFD seesion fault, TWAMP alarms , SCTP link failure alarms at same time RYQ0981 RYQ0969 RYQ0955 | PCM-20251013-00002483 | RYQ0972 down ,need to be restored | RYQ0972 down ,need to be restored |  |  |  | API | 10/13/2025 20:04:50 | 10/13/2025 22:46:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251013001435 | PCM-20251013-00002522 | TT-20251013-02592 | EM | Region_4 | JED0090 | JED0090 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/13/2025 20:24:16 | 10/14/2025 14:33:06 | 10/14/2025 02:24:16 | AIRCON 2 FAILURE at JED1M7090-P1-VIP-SHOP-CA-L900-L800-SBTS @ Sceco | 10/13/2025 20:15:44 | Major | 7103 | AIRCON 2 FAILURE | 10/13/2025 20:15:35 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M7090 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/13/2025 20:24:16 | 10/14/2025 14:33:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000088 | PCM-20251014-00000176 | TT-20251014-00211 | EM | Region_6 | SHF0235 | SHF0235 |  |  |  | Khalid Frahan Almesetef | 10/14/2025 02:20:41 | 10/14/2025 03:48:10 | 10/14/2025 14:20:41 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at SHF1M7235-G9-L9-SBTS-P2-USF @ Generator_SG | 10/14/2025 02:12:59 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/14/2025 02:11:54 | P2 | 4G | al harja | Generator_SG | LTE NSA | SHF1M7235 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/14/2025 02:20:41 | 10/14/2025 03:48:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000089 | PCM-20251014-00000177 | TT-20251014-00212 | EM | Region_6 | SDA0425 | SDA0425 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/14/2025 02:21:11 | 10/14/2025 03:44:39 | 10/14/2025 14:21:11 | AIRCON 2 FAILURE at SDA1M9425-L800-P2 @ Sceco | 10/14/2025 02:12:29 | Minor | 7103 | AIRCON 2 FAILURE | 10/14/2025 02:12:25 | P3 | 4G | abha | Sceco | LTE NSA | SDA1M9425 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/14/2025 02:21:11 | 10/14/2025 03:44:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251014000090 | PCM-20251014-00000179 | TT-20251014-00214 | EM | Region_6 | ABH0341 | ABH0341 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/14/2025 02:23:16 | 10/14/2025 03:44:39 | 10/14/2025 14:23:16 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at ABH1M7341-P3-CA-L800 @ Sceco | 10/14/2025 02:16:03 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/14/2025 02:14:52 | P3 | 4G | abha | Sceco | LTE NSA | ABH1M7341 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/14/2025 02:23:16 | 10/14/2025 03:44:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000091 | PCM-20251014-00000184 | TT-20251014-00221 | EM | Region_6 | ABH2166 | ABH2166 |  |  |  | Khalid Frahan Almesetef | 10/14/2025 02:28:56 | 10/14/2025 03:48:10 | 10/14/2025 14:28:56 | AIRCON 2 FAILURE at ABH2166-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/14/2025 02:20:39 | Minor | 7103 | AIRCON 2 FAILURE | 10/14/2025 02:20:34 | P3 | 2G | abha | Sceco | 2G NSA | ABH2166 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/14/2025 02:28:56 | 10/14/2025 03:48:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251014000107 | PCM-20251014-00000208 | TT-20251014-00243 | EM | Region_4 | JED2279 | JED2279 | Enviroment | SCECO_Failure | SCECO auto restored | Amer Attallah Awadallah | 10/14/2025 02:43:26 | 10/14/2025 21:53:34 | 10/14/2025 14:43:26 | RECTIFIER MODULE FAILURE at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/14/2025 02:35:00 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/14/2025 02:34:50 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2279 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/14/2025 02:43:26 | 10/14/2025 21:31:52 | 10/14/2025 21:32:14 | 10/14/2025 21:32:34 |  | 10/14/2025 21:53:34 |  | Amer Attallah Awadallah |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000300 | PCM-20251014-00000608 | TT-20251014-00656 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/14/2025 07:47:40 | 10/14/2025 10:41:49 | 10/14/2025 19:47:40 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/14/2025 07:37:19 | Minor | 65102 | high temprature 32 | 10/14/2025 07:37:15 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/14/2025 07:47:40 | 10/14/2025 10:41:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251014000352 | PCM-20251014-00000695 | TT-20251014-00715 | Reference_EM | Region_1 | HFR2368 | HFR2368 | Enviroment | SCECO_Failure | SCECO auto restored | Reda Mohammed Mohamed Hassanein | 10/14/2025 08:29:00 | 10/17/2025 13:58:44 | 10/14/2025 20:29:00 | Air condition 1 failure alarm at HFR2368-P2_SRAN @ Sceco | 10/14/2025 08:18:26 | Minor | 65104 | Air condition 1 failure alarm | 10/14/2025 08:18:24 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR2368 | FLM_EM | [8 empty] | API | 10/14/2025 08:29:00 | 10/14/2025 12:44:18 | 10/17/2025 13:58:36 |  |  | 10/17/2025 13:58:44 |  | Reda Mohammed Mohamed Hassanein |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000353 | PCM-20251014-00000697 | TT-20251014-00717 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/14/2025 08:30:05 | 10/14/2025 12:38:50 | 10/14/2025 14:30:05 | high temprature 32 at RIY0232-P1_SRAN @ Sceco | 10/14/2025 08:19:42 | Major | 65102 | high temprature 32 | 10/14/2025 08:19:39 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/14/2025 08:30:05 | 10/14/2025 12:38:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000383 | PCM-20251014-00000753 | TT-20251014-00775 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/14/2025 09:07:45 | 10/14/2025 13:51:14 | 10/14/2025 21:07:45 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/14/2025 08:57:04 | Minor | 65102 | high temprature 32 | 10/14/2025 08:57:01 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/14/2025 09:07:45 | 10/14/2025 13:51:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251014000471 | PCM-20251014-00000899 | TT-20251014-00915 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/14/2025 10:34:00 | 10/14/2025 17:29:35 | 10/14/2025 22:34:00 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/14/2025 10:27:25 | Minor | 40564 | Genset Fault | 10/14/2025 10:27:25 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/14/2025 10:34:00 | 10/14/2025 14:31:59 | 10/14/2025 17:29:20 |  |  | 10/14/2025 17:29:35 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251014000511 | PCM-20251014-00000971 | TT-20251014-00979 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/14/2025 11:11:45 | 10/15/2025 14:17:40 | 10/14/2025 15:11:45 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/14/2025 11:09:45 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/14/2025 11:09:39 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 1-(1-B) |  |  | API | 10/14/2025 11:11:45 | 10/14/2025 12:00:49 | 10/15/2025 14:17:25 |  |  | 10/15/2025 14:17:40 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251014000517 | PCM-20251014-00000981 | TT-20251014-00989 | EM | Region_6 | ABBS0159 | ABBS0159 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/14/2025 11:15:50 | 10/18/2025 08:57:05 | 10/14/2025 23:15:50 | AIRCON 1 FAILURE at ABBS1M7159-L800-P3 @ Sceco | 10/14/2025 11:07:16 | Minor | 7103 | AIRCON 1 FAILURE | 10/14/2025 11:07:08 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M7159 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/14/2025 11:15:50 | 10/18/2025 08:57:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000547 | PCM-20251014-00001027 | TT-20251014-01036 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/14/2025 11:38:35 | 10/14/2025 12:57:55 | 10/14/2025 17:38:35 | high temprature 40 at DAM2066-P1-HUB_SRAN @ Sceco | 10/14/2025 11:28:14 | Major | 65103 | high temprature 40 | 10/14/2025 11:28:09 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/14/2025 11:38:35 | 10/14/2025 12:57:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000562 | PCM-20251014-00001057 | TT-20251014-01065 | Reference_telecom | Region_2 | RIY0933 | RIY0933 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/14/2025 11:53:55 | 10/15/2025 08:20:16 | 10/14/2025 17:53:55 | 2(2G) 2(LTE) sites down under RIY0933-P2,RIY2417-P3/R2_RY2_HWBSC01 (REF:TT-20251006-02255) | 10/07/2025 17:19:38 | Major | 21825 | CSL Fault | 10/07/2025 17:19:38 | P2 | SRAN | riyadh | Sceco | 2G_LTE SA | RIY0933,RIY2417 | FLM_EM |  | Results: DOWN SITE HUB RIY0933 RIY0933 RIY2417 RIY0933 Summary: Hub: RIY0933, Down Count: 2, Down Sites: RIY0933, RIY2417 Alarm Summary: RIY0933 No Active Alarm on HUB | PCM-20251014-00001055 | power issue at site | power issue at site |  | sites down |  | API | 10/14/2025 11:53:55 | 10/14/2025 13:21:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000577 | PCM-20251014-00001075 | TT-20251014-01097 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/14/2025 12:04:26 | 10/16/2025 18:58:23 | 10/15/2025 00:04:26 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/14/2025 11:56:11 | Minor | 7103 | AIRCON 1 FAILURE | 10/14/2025 11:56:01 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/14/2025 12:04:26 | 10/16/2025 18:58:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251014000576 | PCM-20251014-00001076 | TT-20251014-01099 | Reference_EM | Region_1 | RSK0990 | RSK0990 | Enviroment | Rectifier Module | Change rectifer module | Mohamed Ahmed Mohamed Ahmed | 10/14/2025 12:04:26 | 10/15/2025 06:04:10 | 10/15/2025 00:04:26 | Minor Rec. alarm at RSK2M1990-P3 @ Sceco | 10/14/2025 11:53:45 | Minor | 65108 | Minor Rec. alarm | 10/14/2025 11:53:40 | P3 | 2G | jubail | Sceco | 2G NSA | RSK2M1990 | FLM_EM | [8 empty] | API | 10/14/2025 12:04:26 | 10/15/2025 05:07:10 | 10/15/2025 05:33:49 | 10/15/2025 05:34:38 | 10/15/2025 05:35:40 | 10/15/2025 06:04:10 |  | Mohamed Ahmed Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251014000625 | PCM-20251014-00001151 | TT-20251014-01177 | EM | Region_4 | JED0125 | JED0125 | Enviroment | Air Condition | Change Fan | Hussein Sayed Salama Hussein | 10/14/2025 12:41:05 | 10/14/2025 13:36:07 | 10/14/2025 16:41:05 | AMBIENT_TEMP_FLUCT at JED0125_HYB @ Generator_SG | 10/14/2025 12:39:11 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/14/2025 12:39:04 | P1 | 2G | jeddah | Generator_SG | DWDM NSA | JED0125 | FLM_EM | [5 empty] | 4-LOCAL-2(2-A) |  |  | API | 10/14/2025 12:41:05 |  | 10/14/2025 13:30:32 | 10/14/2025 13:30:48 | 10/14/2025 13:31:38 | 10/14/2025 13:36:07 |  | Hussein Sayed Salama Hussein |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251014000627 | PCM-20251014-00001153 | TT-20251014-01182 | EM | Region_6 | KMS0303 | KMS0303 |  |  |  | Amir Abbas Arif Raza | 10/14/2025 12:44:10 | 10/14/2025 14:25:26 | 10/15/2025 00:44:10 | SHELTER DOOR OPEN at KMS0303-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/14/2025 12:43:42 | Minor | 7103 | SHELTER DOOR OPEN | 10/14/2025 12:41:52 | P2 | 2G | abha | Sceco | 2G NSA | KMS0303 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/14/2025 12:44:10 | 10/14/2025 14:25:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000631 | PCM-20251014-00001164 | TT-20251014-01192 | EM | Region_6 | KMS0303 | KMS0303 |  |  |  | Amir Abbas Arif Raza | 10/14/2025 12:50:20 | 10/14/2025 14:25:26 | 10/15/2025 00:50:20 | AIRCON 1 FAILURE at KMS0303-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/14/2025 12:43:43 | Minor | 7103 | AIRCON 1 FAILURE | 10/14/2025 12:41:52 | P2 | 2G | abha | Sceco | 2G NSA | KMS0303 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/14/2025 12:50:20 | 10/14/2025 14:25:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000765 | PCM-20251014-00001395 | TT-20251014-01449 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/14/2025 14:52:50 | 10/15/2025 15:27:17 | 10/15/2025 02:52:50 | high temprature 40 at KBR0166-P3_SRAN @ Sceco | 10/14/2025 14:42:28 | Minor | 65103 | high temprature 40 | 10/14/2025 14:42:25 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/14/2025 14:52:50 | 10/15/2025 15:27:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Reject_FME | CM20251014000777 | PCM-20251014-00001411 | TT-20251014-01465 | EM | Region_4 | JED0862 | JED0862 |  |  |  | Hussein Sayed Salama Hussein | 10/14/2025 14:57:55 | 10/15/2025 00:30:36 | 10/15/2025 02:57:55 | RECTIFIER MAINS POWER FAILURE at JED1M7862-CA-L900-L800-SBTS @ Generator_SG | 10/14/2025 14:49:24 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/14/2025 14:49:14 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7862 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/14/2025 14:57:55 | 10/15/2025 00:29:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014000781 | PCM-20251014-00001416 | TT-20251014-01471 | EM | Region_4 | JED2684 | JED2684 |  |  |  | Sajid Nazir Muhammad Nazir | 10/14/2025 15:01:00 | 10/14/2025 16:46:44 | 10/15/2025 03:01:00 | RECTIFIER MODULE FAILURE at JED1M8684-CA-L800-SBTS-P3 @ Sceco | 10/14/2025 14:52:19 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/14/2025 14:52:14 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8684 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/14/2025 15:01:00 | 10/14/2025 16:46:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251014000831 | PCM-20251014-00001502 | TT-20251014-01556 | EM | Region_6 | ZHR0495 | ZHR0495 | Enviroment | SCECO_Failure | SCECO auto restored | Irfan Yousaf | 10/14/2025 15:39:45 | 10/16/2025 19:21:29 | 10/15/2025 03:39:45 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at ZHR0495-GSM-UMTS-P2-USF @ Generator_SG | 10/14/2025 15:31:28 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/14/2025 15:31:22 | P2 | 2G | al harja | Generator_SG | 2G NSA | ZHR0495 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/14/2025 15:39:45 | 10/15/2025 07:55:20 | 10/16/2025 19:21:08 |  |  | 10/16/2025 19:21:29 |  | Irfan Yousaf |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251014001056 | PCM-20251014-00001844 | TT-20251014-01924 | EM | Region_6 | TLT0370 | TLT0370 |  |  |  | Muhammad Gomaa | 10/14/2025 18:43:40 | 10/14/2025 19:07:25 | 10/15/2025 06:43:40 | GENSIT 1 RUNNING at TLT0370-GSM-UMTS-P3-HUB @ Generator_DG | 10/14/2025 18:35:14 | Minor | 7103 | GENSIT 1 RUNNING | 10/14/2025 18:35:06 | P1 | 2G | tathleeth | Generator_DG | 2G NSA | TLT0370 | FLM_EM | [5 empty] | GENSIT 1 RUNNING |  |  | API | 10/14/2025 18:43:40 | 10/14/2025 19:07:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251014001149 | PCM-20251014-00002002 | TT-20251014-02107 | EM | Region_4 | HAW2301 | HAW2301 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 10/14/2025 21:17:35 | 10/17/2025 01:27:13 | 10/15/2025 09:17:35 | HIGH TEMP ALARM at HAW2301-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/14/2025 21:09:11 | Minor | 7103 | HIGH TEMP ALARM | 10/14/2025 21:09:06 | P3 | 2G | taif | Sceco | 2G NSA | HAW2301 | FLM_EM | [5 empty] | HIGH TEMP ALARM |  |  | API | 10/14/2025 21:17:35 | 10/14/2025 23:08:45 | 10/17/2025 01:27:05 |  |  | 10/17/2025 01:27:13 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251014001184 | PCM-20251014-00002064 | TT-20251014-02158 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/14/2025 22:04:35 | 10/22/2025 13:21:52 | 10/15/2025 10:04:35 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/14/2025 21:58:19 | Minor | 40564 | Genset Fault | 10/14/2025 21:58:19 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/14/2025 22:04:35 | 10/15/2025 11:11:56 | 10/22/2025 13:21:46 |  |  | 10/22/2025 13:21:52 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251015000038 | PCM-20251015-00000060 | TT-20251015-00080 | Reference_EM | Region_1 | HFS2026 | HFS2026 | Enviroment | Air Condition | Change Fan | Moustafa Mohamed Saleh Saif | 10/15/2025 01:02:50 | 10/20/2025 14:11:54 | 10/15/2025 13:02:50 | High temperature 32C alarm at HFS2M2026-P3 @ Generator_SG | 10/15/2025 00:52:17 | Minor | 65102 | High temperature 32C alarm | 10/15/2025 00:52:13 | P3 | 2G | hafouf | Generator_SG | 2G NSA | HFS2M2026 | FLM_EM | [8 empty] | API | 10/15/2025 01:02:50 | 10/20/2025 11:27:54 | 10/20/2025 11:36:59 | 10/20/2025 11:37:09 | 10/20/2025 11:37:13 | 10/20/2025 14:11:54 |  | Moustafa Mohamed Saleh Saif |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251015000054 | PCM-20251015-00000102 | TT-20251015-00107 | EM | Region_1 | URY9013 | URY9013 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/15/2025 01:21:45 | 10/17/2025 02:19:41 | 10/15/2025 13:21:45 | NETECO: Low Fuel Level at URY9013 @ Power Cube | 10/15/2025 01:10:23 | Minor | 301 | Low Fuel Level | 10/15/2025 01:10:23 | P3 | Repeater | jubail | Power Cube | 2G NSA | URY9013 | FLM_EM |  | Results: DOWN SITE HUB URY9013 URY9013 Summary: Hub: URY9013, Down Count: 1, Down Sites: URY9013 Alarm Summary: URY9013 No Active Alarm on HUB | [6 empty] | API | 10/15/2025 01:21:45 | 10/17/2025 02:19:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000060 | PCM-20251015-00000111 | TT-20251015-00137 | EM | Region_1 | URY9013 | URY9013 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/15/2025 01:28:40 | 10/17/2025 02:19:41 | 10/15/2025 05:28:40 | RELAY_ALARM_CRITICAL at URY9013_NE_2 @ Power Cube | 10/15/2025 01:27:46 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/15/2025 01:27:33 | P3 | Repeater | jubail | Power Cube | TX NSA | URY9013 | FLM_EM | [8 empty] | API | 10/15/2025 01:28:40 | 10/17/2025 02:19:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000077 | PCM-20251015-00000149 | TT-20251015-00196 | EM | Region_6 | BSA0430 | BSA0430 |  |  |  | Asad Saddiq | 10/15/2025 02:19:21 | 10/15/2025 11:23:15 | 10/15/2025 14:19:21 | AIRCON FAILURE at BSA0430-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/15/2025 02:10:54 | Minor | 7103 | AIRCON FAILURE | 10/15/2025 02:10:45 | P2 | 2G | bisha | Sceco | 2G NSA | BSA0430 | FLM_EM | [5 empty] | AIRCON FAILURE |  |  | API | 10/15/2025 02:19:21 | 10/15/2025 11:23:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251015000082 | PCM-20251015-00000156 | TT-20251015-00202 | EM | Region_6 | KMS2060 | KMS2060 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ezat Mohammed | 10/15/2025 02:23:26 | 10/17/2025 20:48:00 | 10/15/2025 14:23:26 | AIRCONE 2 FAILURE at KMS1M8060-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/15/2025 02:15:51 | Minor | 7103 | AIRCONE 2 FAILURE | 10/15/2025 02:14:54 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M8060 | FLM_EM | [5 empty] | AIRCONE 2 FAILURE |  |  | API | 10/15/2025 02:23:26 |  | 10/17/2025 20:47:51 |  |  | 10/17/2025 20:48:00 |  | Ezat Mohammed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000087 | PCM-20251015-00000163 | TT-20251015-00209 | EM | Region_6 | NJR0006 | NJR0006 |  |  |  | Muhammad Shafeeq Muhammad Rafeeq | 10/15/2025 02:29:41 | 10/15/2025 11:28:44 | 10/15/2025 14:29:41 | RECTIFIER MODULE FAILURE at NJR0006-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/15/2025 02:21:08 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/15/2025 02:20:53 | P2 | 2G | najran | Sceco | 2G NSA | NJR0006 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/15/2025 02:29:41 | 10/15/2025 11:28:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000112 | PCM-20251015-00000196 | TT-20251015-00246 | EM | Region_6 | KMS0046 | KMS0046 |  |  |  | Amir Abbas Arif Raza | 10/15/2025 02:58:06 | 10/15/2025 02:59:43 | 10/15/2025 14:58:06 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at KMS1M7046-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/15/2025 02:49:58 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/15/2025 02:49:17 | P2 | 4G | abha | Sceco | LTE NSA | KMS1M7046 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/15/2025 02:58:06 | 10/15/2025 02:59:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000113 | PCM-20251015-00000199 | TT-20251015-00247 | EM | Region_6 | KMS0043 | KMS0043 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/15/2025 02:59:36 | 10/15/2025 06:23:41 | 10/15/2025 14:59:36 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at KMS1M7043-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/15/2025 02:51:35 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/15/2025 02:50:54 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M7043 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/15/2025 02:59:36 | 10/15/2025 06:23:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000134 | PCM-20251015-00000238 | TT-20251015-00283 | EM | Region_2 | RYRN0767 | RYRN0767 |  |  |  | Saleem Khan Amir Dost | 10/15/2025 03:30:36 | 10/16/2025 12:51:10 | 10/15/2025 15:30:36 | Major Rec alarm at RYRN0767-P2_SRAN @ Sceco | 10/15/2025 03:28:21 | Minor | 65107 | Major Rec alarm | 10/15/2025 03:16:01 | P2 | SRAN | quweyah | Sceco | 2G NSA | RYRN0767 | FLM_EM | [8 empty] | API | 10/15/2025 03:30:36 | 10/15/2025 13:53:16 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000135 | PCM-20251015-00000239 | TT-20251015-00284 | EM | Region_6 | KMS0471 | KMS0471 |  |  |  | Amir Abbas Arif Raza | 10/15/2025 03:30:38 | 10/15/2025 10:28:17 | 10/15/2025 09:30:38 | RECTIFIER MAINS POWER FAILURE at KMS1M7471-CA-P1-VIP-SBTS @ Generator_SG | 10/15/2025 03:22:07 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/15/2025 03:21:54 | VIP | 4G | khamis mushyet | Generator_SG | LTE NSA | KMS1M7471 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/15/2025 03:30:38 | 10/15/2025 10:28:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000138 | PCM-20251015-00000247 | TT-20251015-00292 | EM | Region_6 | KMS0280 | KMS0280 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/15/2025 03:32:11 | 10/15/2025 06:23:42 | 10/15/2025 15:32:11 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at KMS1M7280-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/15/2025 03:26:50 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/15/2025 03:23:45 | P3 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M7280 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/15/2025 03:32:11 | 10/15/2025 06:23:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251015000142 | PCM-20251015-00000253 | TT-20251015-00308 | EM | Region_6 | KMS0473 | KMS0473 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ezat Mohammed | 10/15/2025 03:34:46 | 10/17/2025 20:47:47 | 10/15/2025 15:34:46 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at KMS0473-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/15/2025 03:27:05 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/15/2025 03:26:21 | P3 | 2G | khamis mushyet | Sceco | 2G NSA | KMS0473 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/15/2025 03:34:46 | 10/15/2025 21:20:17 | 10/17/2025 20:47:39 |  |  | 10/17/2025 20:47:47 |  | Ezat Mohammed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000153 | PCM-20251015-00000273 | TT-20251015-00326 | EM | Region_6 | KMS0064 | KMS0064 |  |  |  | Amir Abbas Arif Raza | 10/15/2025 03:57:56 | 10/15/2025 10:28:18 | 10/15/2025 15:57:56 | HiTEMPERATURE ALARM at KMS1M7064-CA-L800 @ Sceco | 10/15/2025 03:50:28 | Minor | 7103 | HiTEMPERATURE ALARM | 10/15/2025 03:49:25 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M7064 | FLM_EM | [5 empty] | HiTEMPERATURE ALARM |  |  | API | 10/15/2025 03:57:56 | 10/15/2025 10:28:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000190 | PCM-20251015-00000333 | TT-20251015-00413 | EM | Region_2 | RIY2447 | RIY2447 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/15/2025 05:17:30 | 10/16/2025 12:51:10 | 10/15/2025 17:17:30 | Air condition 1 failure alarm at RIY2447-P2_SRAN @ Sceco | 10/15/2025 05:13:39 | Minor | 65104 | Air condition 1 failure alarm | 10/15/2025 05:06:54 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2447 | FLM_EM | [8 empty] | API | 10/15/2025 05:17:30 | 10/15/2025 11:24:57 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000254 | PCM-20251015-00000430 | TT-20251015-00504 | EM | Region_2 | BUR0053 | BUR0053 |  |  |  | Farman Ullah Muhammad Nazir | 10/15/2025 06:31:45 | 10/16/2025 06:54:35 | 10/15/2025 18:31:45 | RF Unit External Power Supply Insufficient at BUR0053-P2_SRAN @ Sceco | 10/14/2025 21:40:51 | Minor | 26546 | RF Unit External Power Supply Insufficient | 10/14/2025 21:40:17 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0053 | FLM_EM | [8 empty] | API | 10/15/2025 06:31:45 | 10/16/2025 06:54:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251015000303 | PCM-20251015-00000499 | TT-20251015-00550 | Reference_telecom | Region_6 | JZ1-ASG-02 | JZ1 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/15/2025 07:01:58 | 10/15/2025 18:54:54 | 10/15/2025 19:01:58 | Optical Invalid at JZ1-ASG-02 ¦¦ ref TT-20250827-02034 @ Sceco_STB | 10/15/2025 02:26:19 | Minor | 101-2505224 | Optical Invalid | 10/15/2025 02:26:02 | P1 | IPRAN | jizan | Sceco_STB | IPRAN NSA | JZ1-ASG-02 | FLM_TE | [8 empty] | API | 10/15/2025 07:01:58 | 10/15/2025 10:21:54 | 10/15/2025 18:54:42 |  |  | 10/15/2025 18:54:54 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000319 | PCM-20251015-00000522 | TT-20251015-00572 | EM | Region_6 | RYAB0623 | RYAB0623 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Muhammad Bilal Niamat Ali | 10/15/2025 07:21:47 | 10/20/2025 20:11:27 | 10/15/2025 13:21:47 | SHELTER DOOR OPEN at RYAB0623-GSM-UMTS-P1-HUB-USF @ Sceco_STB | 10/15/2025 07:21:30 | Major | 7103 | SHELTER DOOR OPEN | 10/15/2025 07:19:32 | P1 | 2G | sulail | Sceco_STB | 2G NSA | RYAB0623 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/15/2025 07:21:47 | 10/15/2025 10:50:13 | 10/20/2025 20:11:05 |  |  | 10/20/2025 20:11:27 |  | Muhammad Bilal Niamat Ali |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000328 | PCM-20251015-00000558 | TT-20251015-00606 | Telecom | Region_5 | MAK1M9452 | MAK0452 | Equipment | BSS_HW_fault | Replace RRU | IJAZ ALI | 10/15/2025 07:31:36 | 10/16/2025 12:22:58 | 10/15/2025 19:31:36 | BASE STATION INFORMATION (No module fan detected) at MAK1M9452-G9-L8-L18-L21-SBTS-P1-HRM @ Generator_SG | 10/15/2025 07:23:32 | Minor | 7115 | BASE STATION INFORMATION | 10/15/2025 07:23:22 | P1 | 4G | makkah | Generator_SG | LTE NSA | MAK1M9452 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/15/2025 07:31:36 | 10/16/2025 09:39:22 | 10/16/2025 10:45:30 | 10/16/2025 10:45:32 | 10/16/2025 11:41:05 | 10/16/2025 12:22:58 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000344 | PCM-20251015-00000592 | TT-20251015-00618 | Telecom | Region_5 | MAK1M9254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/15/2025 07:59:08 | 10/15/2025 19:13:58 | 10/15/2025 13:59:08 | BASE STATION ANTENNA LINE PROBLEM at MAK1M9254-P1-SHOP-CA-L800-SBTS @ Sceco | 10/15/2025 07:30:14 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/15/2025 07:30:07 | P1 | 4G | makkah | Sceco | LTE NSA | MAK1M9254 | FLM_TE |  |  | PCM-20251015-00000567 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/15/2025 07:59:08 | 10/15/2025 19:13:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000351 | PCM-20251015-00000610 | TT-20251015-00657 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/15/2025 08:15:47 | 10/17/2025 17:26:23 | 10/15/2025 14:15:47 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/15/2025 08:01:35 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/15/2025 08:01:27 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251015-00000602 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/15/2025 08:15:47 | 10/16/2025 14:11:55 | 10/17/2025 17:26:16 |  |  | 10/17/2025 17:26:23 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251015000355 | PCM-20251015-00000616 | TT-20251015-00672 | Telecom | [7 empty] | 10/15/2025 08:17:02 | 10/15/2025 08:17:02 | 10/15/2025 14:17:02 | LAN_LOC at WD8782-SEC0044_OCS @ Sceco | 10/15/2025 08:16:09 | Major | 1-12926 | LAN_LOC | 10/15/2025 08:07:13 | P1 | DWDM |  | Sceco | DWDM NSA | WD8782 | FLM_TE | [5 empty] | 1-TO WADI9701-SEC0045(1-B)-74-TMF2AUX-7(GE2)-COM:1 |  |  | API | 10/15/2025 08:17:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000356 | PCM-20251015-00000617 | TT-20251015-00673 | Telecom | Region_1 | ARM2657 | ARM2657 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Mohamed Abdelaziz | 10/15/2025 08:17:51 | 10/21/2025 11:44:30 | 10/15/2025 14:17:51 | Local Cell Unusable at ARM2657-P3_SRAN @ Sceco | 10/15/2025 08:14:56 | Major | 28203 | Local Cell Unusable | 10/15/2025 08:14:07 | P3 | SRAN | khafji | Sceco | 3G SA | ARM2657 | FLM_TE | [8 empty] | API | 10/15/2025 08:17:51 | 10/21/2025 11:44:30 | [5 empty] | Mohamed Abdelaziz | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20251015000362 | PCM-20251015-00000626 | TT-20251015-00682 | EM | Region_3 | DBTB9039 | DBTB9039 |  |  |  | Walid Attia Shahata Alim | 10/15/2025 08:20:10 | 10/22/2025 11:55:07 | 10/15/2025 12:20:10 | NEC MW observing intruder(INPUT-1) At DBTB9039_EAS | 10/15/2025 08:18:32 | Critical | 383 | POWER_ALM | 10/15/2025 08:18:32 | P3 | Repeater | tabouk | Generator_DG | TX NSA | DBTB9039_EAS | FLM_EM | [5 empty] | NEC MW observing intruder(INPUT-1) At DBTB9039_EAS |  |  | API | 10/15/2025 08:20:10 | 10/16/2025 00:09:14 | 10/22/2025 11:55:03 | 10/22/2025 11:55:07 | [7 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000368 | PCM-20251015-00000651 | TT-20251015-00699 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/15/2025 08:37:11 | 10/19/2025 17:44:21 | 10/15/2025 14:37:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/15/2025 08:36:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 08:36:20 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 08:37:11 | 10/16/2025 08:05:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000382 | PCM-20251015-00000683 | TT-20251015-00727 | Reference_EM | Region_1 | RYHF2M2040 | RYHF2040 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/15/2025 08:56:49 | 10/16/2025 00:14:52 | 10/15/2025 20:56:49 | Air-condition #2 failure alarm at RYHF2M2040-P2 @ Generator_SG | 10/15/2025 08:46:47 | Minor | 65105 | Air-condition #2 failure alarm | 10/15/2025 08:46:43 | P2 | 2G | hafouf | Generator_SG | 2G NSA | RYHF2M2040 | FLM_EM | [8 empty] | API | 10/15/2025 08:56:49 | 10/16/2025 00:14:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000413 | PCM-20251015-00000734 | TT-20250929-02244 | MW_HC | Region_4 | JED0521 | JED0521 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 09:25:40 | 10/15/2025 10:55:29 | 10/15/2025 21:25:40 | Nokia MW HC_P2 Observing Modem Down at JED0521-JED0389_01 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P3 | 2G | jeddah | Sceco | TX NSA | JED0521-JED0389_01 | FLM_TE |  |  | PCM-20251015-00000675 | Dear FLM, Confirmed for replacement | Dear FLM, Confirmed for replacement |  |  |  | API | 10/15/2025 09:25:40 | 10/15/2025 10:55:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000424 | PCM-20251015-00000759 | TT-20251015-00805 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/15/2025 09:40:45 | 10/15/2025 11:34:49 | 10/15/2025 21:40:45 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/15/2025 09:32:25 | Minor | 7103 | HIGH TEMP | 10/15/2025 09:32:17 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/15/2025 09:40:45 | 10/15/2025 11:34:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000430 | PCM-20251015-00000766 | TT-20251015-00809 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/15/2025 09:42:49 | 10/21/2025 23:22:29 | 10/15/2025 15:42:49 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/15/2025 09:32:19 | Major | 65102 | high temprature 32 | 10/15/2025 09:32:15 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/15/2025 09:42:49 | 10/21/2025 23:22:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000447 | PCM-20251015-00000789 | TT-20251009-01558 | Reference_telecom | Region_4 | JED0085 | JED0085 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohammed Ramadan A Abu Abid | 10/15/2025 09:56:03 | 10/19/2025 09:30:09 | 10/15/2025 21:56:03 | LossOfSignal observed in JED0085 towards 10.10.181.35 @ Sceco | 10/09/2025 03:36:55 | Minor |  | LossOfSignal | 10/09/2025 03:36:34 | P2 | 2G | jeddah | Sceco | TX NSA | JED0085 | FLM_TE |  |  | PCM-20251015-00000681 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/15/2025 09:56:03 | 10/15/2025 10:10:46 | 10/19/2025 09:29:57 |  |  | 10/19/2025 09:30:09 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000456 | PCM-20251015-00000803 | TT-20251015-00839 | Reference_telecom | Region_4 | JED2191 | JED2191 |  |  |  | Nazeer Mohammed | 10/15/2025 10:05:00 | 10/15/2025 11:24:21 | 10/15/2025 22:05:00 | Degrade observed in JED2191_04 towards 10.10.188.150 @ Sceco | 10/14/2025 22:05:48 | Minor |  | Degrade | 10/14/2025 22:04:54 | VIP | 2G | jeddah | Sceco | TX NSA | JED2191 | FLM_TE | [8 empty] | API | 10/15/2025 10:05:00 | 10/15/2025 11:24:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000471 | PCM-20251015-00000834 | TT-20251015-00859 | EM | Region_1 | RYHF2M2040 | RYHF2040 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/15/2025 10:20:33 | 10/16/2025 00:14:53 | 10/15/2025 16:20:33 | 1(2G/3G/LTE) sites down under RYHF2040-P2/R1_HF_HWBSC01 @ Generator_SG | 10/15/2025 10:13:32 | Major | 21807 | OML Fault | 10/15/2025 10:13:24 | P2 | 2G | hafouf | Generator_SG | 2G_3G_LTE SA | RYHF2040-P2 | FLM_EM | RYHF2040 | Results: DOWN SITE HUB RYHF2040-P2 RYHF2040 Summary: Hub: RYHF2040, Down Count: 1, Down Sites: RYHF2040-P2 Alarm Summary: RYHF2040 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/15/2025 10:20:33 | 10/16/2025 00:14:53 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000475 | PCM-20251015-00000841 | TT-20251015-00878 | EM | Region_4 | JDAP1M7940 | JDAP0940 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/15/2025 10:24:08 | 10/15/2025 13:46:54 | 10/15/2025 16:24:08 | RECTIFIER MAINS POWER FAILURE at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/15/2025 10:18:45 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/15/2025 10:15:48 | VIP | 4G | jeddah | Sceco | LTE NSA | JDAP1M7940 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/15/2025 10:24:08 | 10/15/2025 13:46:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000484 | PCM-20251015-00000863 | TT-20251015-00897 | Reference_telecom | Region_4 | JED0854 | JED0854 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | Abdulraqib Abdo Saif Abdulaleem | 10/15/2025 10:34:58 | 10/20/2025 19:22:38 | 10/15/2025 22:34:58 | LagPortDown observed in JED0854 towards 10.10.150.148 @ Sceco | 10/14/2025 22:36:26 | Minor |  | LagPortDown | 10/14/2025 22:34:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0854 | FLM_TE | [8 empty] | API | 10/15/2025 10:34:58 | 10/20/2025 19:14:07 | 10/20/2025 19:14:41 | 10/20/2025 19:14:44 | 10/20/2025 19:14:46 | 10/20/2025 19:22:38 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251015000485 | PCM-20251015-00000862 | TT-20251015-00898 | Reference_telecom | Region_4 | JED0241 | JED0241 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/15/2025 10:34:58 | 10/21/2025 18:24:00 | 10/15/2025 22:34:58 | Degrade observed in JED0241 towards 10.10.150.149 @ Sceco | 10/14/2025 22:36:26 | Minor |  | Degrade | 10/14/2025 22:34:38 | P2 | 2G | jeddah | Sceco | TX NSA | JED0241 | FLM_TE | [8 empty] | API | 10/15/2025 10:34:58 | 10/21/2025 18:23:44 | 10/21/2025 18:23:56 | 10/21/2025 18:23:58 | 10/21/2025 18:24:00 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000492 | PCM-20251015-00000876 | TT-20250929-02196 | MW_HC | Region_4 | JED0084 | JED0084 |  |  |  | Mohammed Ramadan A Abu Abid | 10/15/2025 10:41:03 | 10/15/2025 11:20:10 | 10/15/2025 22:41:03 | Nokia MW HC_P2 Observing Modem Down at JED0084-JED0895_03 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0084-JED0895_03 | FLM_TE |  |  | PCM-20251015-00000678 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/15/2025 10:41:03 | 10/15/2025 11:20:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251015000500 | PCM-20251015-00000891 | TT-20251015-00201 | Telecom | Region_4 | JED2127 | JED2127 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/15/2025 10:48:10 | 10/19/2025 17:44:20 | 10/15/2025 16:48:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2127-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/15/2025 02:22:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 02:22:22 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2127 | FLM_TE |  |  | PCM-20251015-00000164 | Site was Access night issue, RT door closed and haris not available EM team confirmed no power issue | Site was Access night issue, RT door closed and haris not available EM team confirmed no power issue |  |  |  | API | 10/15/2025 10:48:10 | 10/15/2025 16:39:27 | 10/15/2025 16:57:25 | 10/15/2025 16:57:38 | 10/15/2025 16:58:11 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000506 | PCM-20251015-00000898 | TT-20251005-02283 | Telecom | Region_4 | TAF1M4383 | TAF2383 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/15/2025 10:54:07 | 10/16/2025 00:08:22 | 10/15/2025 16:54:07 | CELL OPERATION DEGRADED (Failure in optical RP3 interface) at TAF1M4383-P2 @ Sceco | 10/05/2025 15:48:25 | Major | 7654 | CELL OPERATION DEGRADED | 09/05/2025 14:28:21 | P2 | 3G | taif | Sceco | LTE_Cell SA | TAF1M4383 | FLM_TE |  |  | PCM-20251015-00000878 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/15/2025 10:54:07 | 10/15/2025 23:51:12 | 10/16/2025 00:08:15 |  |  | 10/16/2025 00:08:22 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000509 | PCM-20251015-00000902 | TT-20251015-00940 | Telecom | Region_4 | JED0981 | JED0981 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 10:56:10 | 10/15/2025 10:57:00 | 10/15/2025 16:56:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0981-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/15/2025 10:55:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 10:55:18 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0981 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 10:56:10 | 10/15/2025 10:57:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000551 | PCM-20251015-00000963 | TT-20251015-01002 | Reference_telecom | Region_4 | JED0070 | JED0070 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 11:23:32 | 10/15/2025 12:54:48 | 10/15/2025 23:23:32 | LagPortDown observed in JED0070 towards 10.10.177.146 @ Sceco | 10/14/2025 23:23:20 | Minor |  | LagPortDown | 10/14/2025 23:23:06 | P2 | 2G | jeddah | Sceco | TX NSA | JED0070 | FLM_TE | [8 empty] | API | 10/15/2025 11:23:32 | 10/15/2025 12:54:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000552 | PCM-20251015-00000964 | TT-20251015-01003 | Reference_telecom | Region_4 | JED0726 | JED0726 | Equipment | CB_BTS | Replace CB on Rectifier | Khaled Mohammad Abdallah | 10/15/2025 11:23:33 | 10/21/2025 23:25:26 | 10/15/2025 23:23:33 | Degrade observed in JED0726 _01 towards 10.10.177.147 @ Sceco | 10/14/2025 23:23:20 | Minor |  | Degrade | 10/14/2025 23:23:07 | P3 | 2G | jeddah | Sceco | TX NSA | JED0726 | FLM_TE | [8 empty] | API | 10/15/2025 11:23:33 |  | 10/20/2025 22:07:53 | 10/20/2025 22:08:09 | 10/20/2025 22:08:22 | 10/21/2025 23:25:26 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000565 | PCM-20251015-00000982 | TT-20251015-01026 | Reference_telecom | Region_4 | BHR2323 | BHR2323 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/15/2025 11:31:11 | 10/15/2025 12:16:43 | 10/15/2025 23:31:11 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at BHR2323-10.3.234.69 | 10/14/2025 16:23:14 | Minor |  | LOF | 10/14/2025 16:23:14 | P3 | 2G | jeddah | Sceco | TX NSA | BHR2323-10.3.234.69 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:11 | 10/15/2025 12:16:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000567 | PCM-20251015-00000984 | TT-20251015-01028 | Reference_telecom | Region_4 | JED0070 | JED0070 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 11:31:14 | 10/15/2025 12:54:49 | 10/15/2025 23:31:14 | Nokia Eband Observing DemFail-Port 6/5,Degrade-LAG 2,LagPortDown-Port 6/ at JED0070-10.10.177.146 | 10/14/2025 23:23:06 | Minor |  | LOF | 10/14/2025 23:23:06 | P2 | 2G | jeddah | Sceco | TX NSA | JED0070-10.10.177.146 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:14 | 10/15/2025 12:54:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000570 | PCM-20251015-00000988 | TT-20251015-01032 | Reference_telecom | Region_4 | JED0726 | JED0726 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 11:31:19 | 10/15/2025 12:54:50 | 10/15/2025 23:31:19 | Nokia Eband Observing ReplaceableUnitProblem-Port 4/5,LagPortDown-Port 4 at JED0726 _01-10.10.177.147 | 10/14/2025 23:23:07 | Minor |  | LOF | 10/14/2025 23:23:07 | P3 | 2G | jeddah | Sceco | TX NSA | JED0726 _01-10.10.177.147 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:19 | 10/15/2025 12:54:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000571 | PCM-20251015-00000989 | TT-20251015-01033 | Reference_telecom | Region_4 | JED2052 | JED2052 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/15/2025 11:31:21 | 10/15/2025 11:31:21 | 10/15/2025 23:31:21 | Nokia Eband Observing ReplaceableUnitMissing-Card - 7 at JED2052-2-10.10.145.102 | 10/14/2025 19:00:07 | Minor |  | LOF | 10/14/2025 19:00:07 | P2 | 2G | jeddah | Sceco | TX NSA | JED2052-2-10.10.145.102 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000574 | PCM-20251015-00000992 | TT-20251015-01036 | Reference_telecom | Region_4 | JED0241 | JED0241 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 11:31:25 | 10/15/2025 11:31:25 | 10/15/2025 23:31:25 | Nokia Eband Observing LagPortDown-Port 4/5,DemFail-Port 4/5,Degrade-LAG at JED0241-10.10.150.149 | 10/14/2025 22:34:38 | Minor |  | LOF | 10/14/2025 22:34:38 | P2 | 2G | jeddah | Sceco | TX NSA | JED0241-10.10.150.149 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251015000575 | PCM-20251015-00000993 | TT-20251015-01037 | Reference_telecom | Region_4 | JED2191 | JED2191 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/15/2025 11:31:27 | 10/17/2025 22:57:11 | 10/15/2025 23:31:27 | Nokia Eband Observing Degrade-LAG 2 at JED2191_04-10.10.188.150 | 10/14/2025 22:04:54 | Minor |  | LOF | 10/14/2025 22:04:54 | VIP | 2G | jeddah | Sceco | TX NSA | JED2191_04-10.10.188.150 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:27 | 10/17/2025 22:53:51 | 10/17/2025 22:56:50 | 10/17/2025 22:56:55 | 10/17/2025 22:57:11 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251015000578 | PCM-20251015-00000996 | TT-20251015-01040 | Reference_telecom | Region_5 | MAK0066 | MAK0066 |  |  |  | Atif Javed Javed Hussain | 10/15/2025 11:31:31 | 10/16/2025 11:26:25 | 10/15/2025 23:31:31 | Nokia Eband Observing Degrade-LAG 1 at MAK0066-10-10.10.142.241 | 10/14/2025 12:35:58 | Minor |  | LOF | 10/14/2025 12:35:58 | P1 | 2G | makkah | Sceco | TX NSA | MAK0066-10-10.10.142.241 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:31 | 10/16/2025 11:26:11 | 10/16/2025 11:26:22 | 10/16/2025 11:26:25 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000581 | PCM-20251015-00000999 | TT-20251015-01043 | Reference_telecom | Region_4 | JED0411 | JED0411 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 11:31:35 | 10/15/2025 12:54:50 | 10/15/2025 23:31:35 | Nokia Eband Observing Degrade-LAG 1,DemFail-Port 4/5,LagPortDown-Port 4/ at JED0411 _6-10.1.237.33 | 10/14/2025 16:16:11 | Minor |  | LOF | 10/14/2025 16:16:11 | P1 | 2G | jeddah | Sceco | TX NSA | JED0411 _6-10.1.237.33 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:35 | 10/15/2025 12:54:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000582 | PCM-20251015-00001000 | TT-20251015-01044 | Reference_telecom | Region_5 | MAK0010 | MAK0010 | Enviroment | SCECO_Failure | SCECO auto restored | KAMRAN AAMIR | 10/15/2025 11:31:36 | 10/23/2025 13:51:37 | 10/15/2025 23:31:36 | Nokia Eband Observing DemFail-Port 3/5,LagPortDown-Port 3/5,Degrade-LAG at MAK0010-3-10.10.149.68 | 10/11/2025 22:49:14 | Minor |  | LOF | 10/11/2025 22:49:14 | VIP | 2G | makkah | Sceco | TX NSA | MAK0010-3-10.10.149.68 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:36 |  | 10/23/2025 12:56:32 | 10/23/2025 12:56:54 | 10/23/2025 13:07:37 | 10/23/2025 13:51:37 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015000583 | PCM-20251015-00001001 | TT-20251015-01045 | Reference_telecom | Region_4 | JED0854 | JED0854 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 11:31:37 | 10/15/2025 11:31:37 | 10/15/2025 23:31:37 | Nokia Eband Observing Degrade-LAG 2,LagPortDown-Port 6/5 at JED0854-10.10.150.148 | 10/14/2025 22:34:37 | Minor |  | LOF | 10/14/2025 22:34:37 | P2 | 2G | jeddah | Sceco | TX NSA | JED0854-10.10.150.148 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000584 | PCM-20251015-00001002 | TT-20251015-01046 | Reference_telecom | Region_4 | JED2985 | JED2985 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 11:31:38 | 10/15/2025 12:54:50 | 10/15/2025 23:31:38 | Nokia Eband Observing InternalCommunicationProblem-Port 4/5,ReplaceableU at JED2985 -10.1.237.34 | 10/14/2025 16:16:17 | Minor |  | LOF | 10/14/2025 16:16:17 | P3 | 2G | jeddah | Sceco | TX NSA | JED2985 -10.1.237.34 | FLM_TE | [8 empty] | API | 10/15/2025 11:31:38 | 10/15/2025 12:54:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000594 | PCM-20251015-00001020 | TT-20251015-01062 | Reference_telecom | Region_6 | AQQ2425 | AQQ2425 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Manzoor Ahmed | 10/15/2025 11:37:29 | 10/23/2025 23:04:28 | 10/15/2025 23:37:29 | LossOfSignal observed in AQQ2425_01 towards 10.221.245.103 @ Generator_SG | 10/14/2025 23:38:20 | Minor |  | LossOfSignal | 10/14/2025 23:37:04 | P3 | 2G | Baha | Generator_SG | TX NSA | AQQ2425 | FLM_TE | [8 empty] | Manual | 10/15/2025 11:37:29 | 10/23/2025 13:11:45 | 10/23/2025 23:04:16 |  |  | 10/23/2025 23:04:28 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000598 | PCM-20251015-00001024 | TT-20251015-01065 | Telecom | Region_5 | MAK0106 | MAK0106 |  |  |  | Sher Ali Munir | 10/15/2025 11:39:40 | 10/20/2025 05:42:35 | 10/15/2025 17:39:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0106-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HAJJ-Core-HUB-WDM-HRM | 10/15/2025 11:30:16 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 11:30:16 | VIP | 2G | makkah | Sceco_STB | 5G SA | MAK0106-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HAJJ-Core-HUB-WDM-HRM | FLM_TE | [8 empty] | API | 10/15/2025 11:39:40 | 10/20/2025 05:42:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251015000604 | PCM-20251015-00001032 | TT-20251015-01075 | EM | [7 empty] | 10/15/2025 11:43:42 | 10/15/2025 11:43:42 | 10/15/2025 15:43:42 | HIGH TEMP 32 + HIGH TEMP 40 at 8809-SEC0004_OCS @ Sceco | 10/15/2025 11:41:57 | Critical | 1-12307 | HIGH TEMP 32 + HIGH TEMP 40 | 10/15/2025 11:41:48 | P1 | DWDM |  | Sceco | DWDM NSA | 8809 | FLM_EM | [5 empty] | 0-TO RAS0098&9006-SEC0005(1-A)-72-E1EFI-[HIGH TEMP 32 + HIGH TEMP 40]:1 |  |  | API | 10/15/2025 11:43:42 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000617 | PCM-20251015-00001052 | TT-20251015-01093 | Telecom | Region_4 | JED1M7344 | JED0344 | Equipment | SW | Issue was solved after softaware configuration | Khaled Mohammad Abdallah | 10/15/2025 11:55:05 | 10/18/2025 23:06:47 | 10/15/2025 17:55:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7344-CA-L900-L800-SBTS @ Sceco | 10/15/2025 11:54:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 11:54:03 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7344 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 11:55:05 | 10/16/2025 08:41:31 | 10/18/2025 23:06:36 |  |  | 10/18/2025 23:06:47 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000625 | PCM-20251015-00001080 | TT-20251015-01120 | Reference_telecom | Region_5 | MAK0528 | MAK0528 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/15/2025 12:02:52 | 10/15/2025 19:13:59 | 10/16/2025 00:02:52 | LagPortDown observed in MAK0528_02 towards 10.10.141.195 @ Sceco | 10/15/2025 00:03:55 | Minor |  | LagPortDown | 10/15/2025 00:02:28 | P2 | 2G | makkah | Sceco | TX NSA | MAK0528 | FLM_TE | [8 empty] | API | 10/15/2025 12:02:52 | 10/15/2025 19:13:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251015000643 | PCM-20251015-00001112 | TT-20251015-01173 | EM | [7 empty] | 10/15/2025 12:15:16 | 10/15/2025 12:15:16 | 10/16/2025 00:15:16 | COMMERCIAL POWER FAILURE at JDJZ1M8181-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/15/2025 12:07:07 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/15/2025 12:07:00 | P3 | 4G |  | Generator_SG | LTE NSA | JDJZ1M8181 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/15/2025 12:15:16 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000661 | PCM-20251015-00001133 | TT-20251015-01199 | Telecom | Region_4 | RYMK0671-LL-CSG-01 | RYMK0671 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/15/2025 12:26:34 | 10/15/2025 23:51:13 | 10/15/2025 16:26:34 | DWDM_Physical Port Down at RYMK0671-LL-CSG-01 @ Sceco_STB | 10/15/2025 12:24:57 | Critical | 101-2505274 | Physical Port Down | 10/15/2025 12:24:48 | P2 | IPRAN | taif | Sceco_STB | IPRAN SA | RYMK0671-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/15/2025 12:26:34 | 10/15/2025 23:51:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251015000666 | PCM-20251015-00001140 | TT-20251015-01205 | EM | [7 empty] | 10/15/2025 12:31:15 | 10/15/2025 12:31:15 | 10/15/2025 16:31:15 | NE_COMMU_GNE_SWITCH at 8076-SEC0024_OCS @ Sceco | 10/15/2025 12:29:30 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/15/2025 12:29:27 | P1 | DWDM |  | Sceco | DWDM NSA | 8076 | FLM_EM | [5 empty] | NE 8076-SEC0024_OCS's current GNE has been switched to standby GNE |  |  | API | 10/15/2025 12:31:15 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251015000667 | PCM-20251015-00001142 | TT-20251015-01207 | EM | [7 empty] | 10/15/2025 12:31:15 | 10/15/2025 12:31:15 | 10/15/2025 16:31:15 | NE_COMMU_GNE_SWITCH at 8077-SEC0025_OCS-1 @ Sceco | 10/15/2025 12:29:30 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/15/2025 12:29:27 | P1 | DWDM |  | Sceco | DWDM NSA | 8077 | FLM_EM | [5 empty] | NE 8077-SEC0025_OCS-1's current GNE has been switched to standby GNE |  |  | API | 10/15/2025 12:31:15 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251015000668 | PCM-20251015-00001141 | TT-20251015-01206 | EM | [7 empty] | 10/15/2025 12:31:15 | 10/15/2025 12:31:15 | 10/15/2025 16:31:15 | NE_COMMU_GNE_SWITCH at 8077-SEC0025_ELC @ Sceco | 10/15/2025 12:29:30 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/15/2025 12:29:27 | P1 | DWDM |  | Sceco | DWDM NSA | 8077 | FLM_EM | [5 empty] | NE 8077-SEC0025_ELC's current GNE has been switched to standby GNE |  |  | API | 10/15/2025 12:31:15 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000672 | PCM-20251015-00001145 | TT-20251015-01210 | EM | Region_2 | SEC0024 | SEC0024 |  |  |  | Saleem Khan Amir Dost | 10/15/2025 12:32:16 | 10/15/2025 13:53:17 | 10/15/2025 16:32:16 | NE_COMMU_GNE_SWITCH at SEC0024_ELC @ Sceco | 10/15/2025 12:30:41 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/15/2025 12:30:37 | P1 | DWDM | riyadh | Sceco | DWDM NSA | SEC0024 | FLM_EM | [5 empty] | NE SEC0024_ELC's current GNE has been switched to standby GNE |  |  | API | 10/15/2025 12:32:16 | 10/15/2025 13:53:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000674 | PCM-20251015-00001147 | TT-20251015-01215 | Telecom | Region_4 | JD1 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/15/2025 12:34:12 | 10/18/2025 22:41:32 | 10/15/2025 18:34:12 | Observing Link Down B/W JD & MAK | 10/15/2025 12:24:48 | Major | 5000003 | Link Down | 10/15/2025 12:24:48 | P1 | DWDM | jeddah | Sceco_STB | IPBB NSA | Observing Link Down B/W JD & MAK | FLM_TE | [5 empty] | Observing Link Down B/W JD & MAK |  |  | API | 10/15/2025 12:34:12 | 10/18/2025 22:41:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000686 | PCM-20251015-00001160 | TT-20251015-01229 | Reference_telecom | Region_1 | DMH0100 | DMH0100 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/15/2025 12:38:42 | 10/22/2025 11:33:43 | 10/16/2025 00:38:42 | MW RTN Observing PG_PRT_DEGRADED,PG_PRT_DEGRADED at DMH0100_NE_1_VRRP | 10/15/2025 08:08:15 | Minor |  | LOF | 10/15/2025 08:08:15 | P3 | SRAN | hafr | Generator_SG | TX NSA | DMH0100_NE_1_VRRP | FLM_TE | [8 empty] | API | 10/15/2025 12:38:42 | 10/15/2025 13:22:41 | [6 empty] | ZAIN Planning |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000687 | PCM-20251015-00001161 | TT-20251015-01230 | Reference_telecom | Region_1 | DMV0098 | DMV0098 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/15/2025 12:38:43 | 10/16/2025 16:01:56 | 10/16/2025 00:38:43 | MW RTN Observing MW_BER_SD,MW_BER_SD,PG_PRT_DEGRADED,PG_PRT_DEGRADE at DMV0098_NE_1 | 10/15/2025 06:49:48 | Minor |  | LOF | 10/15/2025 06:49:48 | P1 | SRAN | hafouf | Sceco_STB | TX NSA | DMV0098_NE_1 | FLM_TE | [8 empty] | API | 10/15/2025 12:38:43 | 10/16/2025 16:01:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000689 | PCM-20251015-00001163 | TT-20251015-01232 | Reference_telecom | Region_1 | DRN2387 | DRN2387 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Imran Ali Yousaf | 10/15/2025 12:38:46 | 10/16/2025 15:51:13 | 10/16/2025 00:38:46 | MW RTN Observing DROPRATIO_OVER at DRN2387_NE_4_V | 10/15/2025 09:39:46 | Minor |  | LOF | 10/15/2025 09:39:46 | P3 | SRAN | dammam | Sceco | TX NSA | DRN2387_NE_4_V | FLM_TE | [8 empty] | API | 10/15/2025 12:38:46 | 10/15/2025 13:40:16 | 10/16/2025 14:59:41 | 10/16/2025 14:59:44 | 10/16/2025 14:59:47 | 10/16/2025 15:51:13 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000690 | PCM-20251015-00001164 | TT-20251015-01233 | Reference_telecom | Region_1 | HFR0496 | HFR0496 | Transsmission | SFP_Transmission | Reset SFP | Muhammad Anwar Hussain Akhtar Hussain | 10/15/2025 12:38:47 | 10/16/2025 15:26:31 | 10/16/2025 00:38:47 | MW RTN Observing IN_PWR_LOW at HFR0496_NE_5_H | 10/15/2025 09:45:28 | Minor |  | LOF | 10/15/2025 09:45:28 | P2 | SRAN | hafr | Sceco | TX NSA | HFR0496_NE_5_H | FLM_TE | [8 empty] | API | 10/15/2025 12:38:47 | 10/15/2025 13:22:42 | 10/15/2025 16:52:53 | 10/15/2025 16:52:56 | 10/16/2025 14:15:12 | 10/16/2025 15:26:31 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000691 | PCM-20251015-00001165 | TT-20251015-01234 | Reference_telecom | Region_1 | HRD9017 | HRD9017 |  |  |  | Mohamed Magdy Fouad Zayed | 10/15/2025 12:38:48 | 10/15/2025 15:53:41 | 10/16/2025 00:38:48 | MW RTN Observing MW_BER_SD at HRD9017_NE_7 | 10/15/2025 09:45:44 | Minor |  | LOF | 10/15/2025 09:45:44 | P3 | Repeater | hafouf | Power Cube | TX NSA | HRD9017_NE_7 | FLM_TE | [8 empty] | API | 10/15/2025 12:38:48 | 10/15/2025 15:53:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000698 | PCM-20251015-00001172 | TT-20251015-01241 | Reference_telecom | Region_2 | QSMD0589 | QSMD0589 |  |  |  | Muhammad Naeem Muhammad Gulzar | 10/15/2025 12:38:56 | 10/15/2025 13:56:08 | 10/16/2025 00:38:56 | MW RTN Observing PG_PRT_DEGRADED at QSMD0589_NE_3 | 10/13/2025 02:27:45 | Minor |  | LOF | 10/13/2025 02:27:45 | P2 | SRAN | buraidah | Sceco_STB | TX NSA | QSMD0589_NE_3 | FLM_TE | [8 empty] | API | 10/15/2025 12:38:56 | 10/15/2025 13:56:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251015000701 | PCM-20251015-00001175 | TT-20251015-01245 | EM | [7 empty] | 10/15/2025 12:38:59 | 10/15/2025 12:38:59 | 10/16/2025 00:38:59 | SHELTER DOOR OPEN at JDJZ1M8181-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/15/2025 12:38:35 | Minor | 7103 | SHELTER DOOR OPEN | 10/15/2025 12:38:28 | P3 | 4G |  | Generator_SG | LTE NSA | JDJZ1M8181 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/15/2025 12:38:59 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000706 | PCM-20251015-00001180 | TT-20251015-01250 | Reference_telecom | Region_2 | RIY0322 | RIY0322 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/15/2025 12:39:06 | 10/15/2025 18:46:27 | 10/16/2025 00:39:06 | MW RTN Observing MW_LOF,RADIO_RSL_LOW at RIY0322_NE_6_H | 10/15/2025 08:49:16 | Minor |  | LOF | 10/15/2025 08:49:16 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY0322_NE_6_H | FLM_TE | [8 empty] | API | 10/15/2025 12:39:06 | 10/15/2025 14:45:11 | 10/15/2025 18:46:17 |  |  | 10/15/2025 18:46:27 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000710 | PCM-20251015-00001184 | TT-20251015-01254 | Reference_telecom | Region_2 | RIY2371 | RIY2371 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Farmanullah Akbar Jan | 10/15/2025 12:39:12 | 10/23/2025 16:02:22 | 10/16/2025 00:39:12 | MW RTN Observing MAC_EXT_EXC,MAC_FCS_EXC at RIY2371_NE_27_V | 10/15/2025 09:41:06 | Minor |  | LOF | 10/15/2025 09:41:06 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY2371_NE_27_V | FLM_TE | [8 empty] | API | 10/15/2025 12:39:12 | 10/23/2025 14:00:03 | 10/23/2025 14:34:46 | 10/23/2025 14:34:50 | 10/23/2025 15:03:26 | 10/23/2025 16:02:22 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000714 | PCM-20251015-00001188 | TT-20251015-01258 | Reference_telecom | Region_2 | RIY2571 | RIY2571 | Transsmission | MW_LOW_RSL | Link Alignment Issue | Khan zeb Shah nawaz | 10/15/2025 12:39:17 | 10/19/2025 17:04:16 | 10/16/2025 00:39:17 | MW RTN Observing RADIO_RSL_LOW,MW_FEC_EXC at RIY2571_NE_3_V | 10/15/2025 05:48:19 | Minor |  | LOF | 10/15/2025 05:48:19 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2571_NE_3_V | FLM_TE | [8 empty] | API | 10/15/2025 12:39:17 | 10/19/2025 13:40:28 | 10/19/2025 13:41:21 | 10/19/2025 13:41:24 | 10/19/2025 13:59:45 | 10/19/2025 17:04:16 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000724 | PCM-20251015-00001198 | TT-20251015-01268 | Reference_telecom | Region_3 | YBDB0290 | YBDB0290 |  |  |  | Muhammad Sajjad R3 | 10/15/2025 12:39:28 | 10/15/2025 17:40:57 | 10/16/2025 00:39:28 | MW RTN Observing MW_BER_SD,MW_BER_SD,MW_BER_SD at YBDB0290_NE_1_MMM | 10/14/2025 05:43:32 | Minor |  | LOF | 10/14/2025 05:43:32 | P1 | SRAN | yanbu | Generator_DG | TX NSA | YBDB0290_NE_1_MMM | FLM_TE | [8 empty] | API | 10/15/2025 12:39:28 | 10/15/2025 17:40:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251015000725 | PCM-20251015-00001199 | TT-20251015-01269 | Reference_telecom | Region_2 | RYD0941 | RYD0941 |  |  |  | Asad Ali Nadiq Khan | 10/15/2025 12:39:30 | 10/22/2025 11:16:15 | 10/16/2025 00:39:30 | MW RTN Observing MW_BER_SD,MW_BER_SD,PG_PRT_DEGRADED at RYD0941_NE_3 | 10/15/2025 09:31:31 | Minor |  | LOF | 10/15/2025 09:31:31 | VIP | SRAN | rumah | Generator_SG | TX NSA | RYD0941_NE_3 | FLM_TE | [8 empty] | API | 10/15/2025 12:39:30 | 10/22/2025 11:15:35 | 10/22/2025 11:16:02 | 10/22/2025 11:16:13 | 10/22/2025 11:16:15 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000744 | PCM-20251015-00001232 | TT-20251015-01306 | EM | Region_6 | QLW1M8370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/15/2025 12:59:40 | 10/21/2025 22:26:09 | 10/16/2025 00:59:40 | RECTIFIER MODULE FAILURE at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/15/2025 12:57:51 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/15/2025 09:55:39 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | Manual | 10/15/2025 12:59:40 | 10/21/2025 22:26:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000748 | PCM-20251015-00001237 | TT-20251015-01316 | Reference_telecom | Region_2 | RIYB2U6754 | RIYB6054 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/15/2025 13:04:12 | 10/18/2025 14:26:52 | 10/16/2025 01:04:12 | GNSS Antenna Fault at RIYB2U6754-P3(Ref::TT-20251014-02079) @ Sceco | 10/14/2025 18:26:06 | Minor | 26125 | GNSS Antenna Fault | 10/14/2025 18:24:32 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6754 | FLM_TE | [8 empty] | API | 10/15/2025 13:04:12 | 10/18/2025 14:26:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000768 | PCM-20251015-00001269 | TT-20251015-01277 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 13:17:32 | 10/15/2025 15:35:38 | 10/16/2025 01:17:32 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/15/2025 12:38:43 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 12:38:38 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251015-00001207 | Please close alarm is clear | Please close alarm is clear |  |  |  | API | 10/15/2025 13:17:32 | 10/15/2025 15:35:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000774 | PCM-20251015-00001276 | TT-20251015-01361 | Reference_telecom | Region_4 | JED0922 | JED0922 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohammed Ramadan A Abu Abid | 10/15/2025 13:24:26 | 10/19/2025 09:30:44 | 10/16/2025 01:24:26 | LossOfSignal observed in JED0922_01 towards 10.10.148.118 @ Generator_SG | 10/15/2025 01:26:03 | Minor |  | LossOfSignal | 10/15/2025 01:24:05 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0922 | FLM_TE | [8 empty] | API | 10/15/2025 13:24:26 | 10/15/2025 13:53:35 | 10/19/2025 09:30:20 |  |  | 10/19/2025 09:30:44 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000812 | PCM-20251015-00001327 | TT-20251015-01419 | Telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/15/2025 13:59:04 | 10/15/2025 14:41:21 | 10/16/2025 01:59:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/15/2025 13:58:05 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 13:57:53 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0296 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 13:59:04 | 10/15/2025 14:41:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000814 | PCM-20251015-00001329 | TT-20251015-01422 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/15/2025 14:00:37 | 10/15/2025 16:32:51 | 10/16/2025 02:00:37 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/15/2025 13:53:41 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/15/2025 13:53:38 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/15/2025 14:00:37 | 10/15/2025 16:32:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000817 | PCM-20251015-00001332 | TT-20251015-01395 | Reference_telecom | Region_4 | JED1M7839 | JED0839 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/15/2025 14:02:16 | 10/16/2025 12:36:13 | 10/15/2025 18:02:16 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1M7839-CA-L900-P1-VIP @ Sceco | 10/15/2025 13:34:36 | Critical | 7654 | CELL OPERATION DEGRADED | 10/15/2025 13:34:30 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7839 | FLM_TE |  |  | PCM-20251015-00001306 | Please check the VSWR issue | Please check the VSWR issue |  |  |  | API | 10/15/2025 14:02:16 | 10/15/2025 14:09:20 | 10/16/2025 12:36:07 |  |  | 10/16/2025 12:36:13 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000819 | PCM-20251015-00001335 | TT-20251015-01427 | Reference_telecom | Region_4 | THO0371 | THO0371 |  |  |  | Khizer Hayat | 10/15/2025 14:03:42 | 10/15/2025 18:12:32 | 10/16/2025 02:03:42 | ReplaceableUnitProblem observed in THO0371 _02 towards 10.10.148.147 @ Sceco | 10/15/2025 02:03:15 | Minor |  | ReplaceableUnitProblem | 10/15/2025 02:03:11 | P2 | 2G | jeddah | Sceco | TX NSA | THO0371 | FLM_TE | [8 empty] | API | 10/15/2025 14:03:42 | 10/15/2025 18:12:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000820 | PCM-20251015-00001338 | TT-20251015-01431 | EM | Region_1 | JBL0465 | JBL0465 | Enviroment | Air Condition | Change Outdoor motor | Islam Elsawi Mohamed Elsawi | 10/15/2025 14:04:14 | 10/17/2025 19:20:16 | 10/15/2025 20:04:14 | Door opening alarm at JBL0465-Core-P1_SRAN @ Sceco_STB | 10/15/2025 14:03:54 | Major | 65101 | Door opening alarm | 10/15/2025 14:03:49 | P1 | SRAN | jubail | Sceco_STB | 2G NSA | JBL0465 | FLM_EM | [8 empty] | API | 10/15/2025 14:04:14 | 10/17/2025 06:45:41 | 10/17/2025 19:20:03 |  |  | 10/17/2025 19:20:16 |  | Islam Elsawi Mohamed Elsawi |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000822 | PCM-20251015-00001339 | TT-20251015-01432 | EM | Region_1 | JB1 | JB1 |  |  |  | Mohamed Samir Farahat Allam | 10/15/2025 14:04:45 | 10/15/2025 22:25:05 | 10/15/2025 18:04:45 | Door opening alarm BSC New shelter at JB1-Shelter 6-WDM-Core-P1 @ Sceco_STB | 10/15/2025 14:04:32 | Critical | 65134 | Door opening alarm BSC New shelter | 10/15/2025 14:04:29 | P1 | BSC | jubail | Sceco_STB | 2G NSA | JB1 | FLM_EM | [8 empty] | API | 10/15/2025 14:04:45 | 10/15/2025 22:25:05 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000825 | PCM-20251015-00001343 | TT-20251015-01435 | EM | Region_1 | R1_JB_HWBSC01 | JB1 |  |  |  | Mohamed Samir Farahat Allam | 10/15/2025 14:06:18 | 10/15/2025 22:25:06 | 10/15/2025 18:06:18 | Intruder Alarm(SH1) at R1_JB_HWBSC01 @ Sceco_STB | 10/15/2025 14:06:02 | Critical | 65334 | Intruder Alarm(SH1) | 10/15/2025 14:05:58 | P1 | BSC | jubail | Sceco_STB | 2G NSA | R1_JB_HWBSC01 | FLM_EM | [8 empty] | API | 10/15/2025 14:06:18 | 10/15/2025 22:25:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000827 | PCM-20251015-00001347 | TT-20251015-01440 | EM | Region_1 | JBL0465 | JBL0465 | Enviroment | Air Condition | Change Fan | Islam Elsawi Mohamed Elsawi | 10/15/2025 14:07:20 | 10/17/2025 19:19:55 | 10/15/2025 18:07:20 | Door opening alarm at JBL0465-RPT2-P1-Core-DIA-WDM @ Sceco_STB | 10/15/2025 14:07:09 | Critical | 65101 | Door opening alarm | 10/15/2025 14:07:04 | P1 | SRAN | jubail | Sceco_STB | 3G NSA | JBL0465 | FLM_EM | [8 empty] | API | 10/15/2025 14:07:20 | 10/17/2025 06:45:42 | 10/17/2025 19:19:43 |  |  | 10/17/2025 19:19:55 |  | Islam Elsawi Mohamed Elsawi |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251015000841 | PCM-20251015-00001373 | TT-20251015-01496 | EM | Region_3 | MDYB2533 | MDYB2533 |  |  |  | Yasser Mohamed Mohamed Yousef | 10/15/2025 14:19:12 | 10/15/2025 14:19:12 | 10/16/2025 02:19:12 | NETECO: Communication Failure at MDYB2533 @ Generator_SG | 10/15/2025 14:13:04 | Minor | 1602 | Communication Failure | 10/15/2025 14:13:04 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDYB2533 | FLM_EM | [8 empty] | API | 10/15/2025 14:19:12 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251015000844 | PCM-20251015-00001378 | TT-20251015-01510 | Reference_EM | Region_3 | MDYB2533 | MDYB2533 |  |  |  | Yasser Mohamed Mohamed Yousef | 10/15/2025 14:23:21 | 10/15/2025 14:23:21 | 10/16/2025 02:23:21 | Minor Rec alarm at MDYB2533-P3-USF_SRAN @ Generator_SG | 10/15/2025 14:13:08 | Minor | 65108 | Minor Rec alarm | 10/15/2025 14:13:05 | P3 | SRAN | madinah | Generator_SG | 2G NSA | MDYB2533 | FLM_EM | [8 empty] | API | 10/15/2025 14:23:21 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251015000853 | PCM-20251015-00001391 | TT-20251015-01526 | EM | [7 empty] | 10/15/2025 14:26:58 | 10/15/2025 14:26:58 | 10/15/2025 18:26:58 | DOOR OPEN at NAMARA-SEC0016_OCS @ Sceco | 10/15/2025 14:26:23 | Critical | 1-12307 | DOOR OPEN | 10/15/2025 14:26:15 | P1 | DWDM |  | Sceco | DWDM NSA | NAMARA | FLM_EM | [5 empty] | 0-TO SWAMLA-SEC0023(1-A)-71-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/15/2025 14:26:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000865 | PCM-20251015-00001408 | TT-20251015-01542 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/15/2025 14:36:47 | 10/15/2025 17:08:54 | 10/16/2025 02:36:47 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/15/2025 14:28:35 | Minor | 7103 | AIRCON 1 FAILURE | 10/15/2025 14:28:27 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/15/2025 14:36:47 | 10/15/2025 17:08:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251015000889 | PCM-20251015-00001451 | TT-20251015-01576 | Telecom | [7 empty] | 10/15/2025 14:59:31 | 10/15/2025 14:59:31 | 10/16/2025 02:59:31 | Transmission Optical Interface Error at UQL2722-P3_SRAN @ Generator_SG | 10/15/2025 14:56:58 | Minor | 26222 | Transmission Optical Interface Error | 10/15/2025 14:55:25 | P3 | SRAN |  | Generator_SG | 2G NSA | UQL2722 | FLM_TE | [8 empty] | API | 10/15/2025 14:59:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000895 | PCM-20251015-00001458 | TT-20251015-01585 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/15/2025 15:07:46 | 10/21/2025 22:26:11 | 10/16/2025 03:07:46 | SHELTER DOOR OPEN at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/15/2025 15:07:12 | Minor | 7103 | SHELTER DOOR OPEN | 10/15/2025 15:05:51 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | Manual | 10/15/2025 15:07:46 | 10/21/2025 22:26:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015000903 | PCM-20251015-00001474 | TT-20251015-01600 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/15/2025 15:13:58 | 10/21/2025 22:26:13 | 10/16/2025 03:13:58 | AIRCON 1 FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/15/2025 15:07:11 | Minor | 7103 | AIRCON 1 FAILURE | 10/15/2025 15:05:51 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | Manual | 10/15/2025 15:13:58 | 10/21/2025 22:26:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000926 | PCM-20251015-00001512 | TT-20251008-02010 | MW_HC | Region_4 | JED6135 | JED6135 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohamed Farag Abdelbary | 10/15/2025 15:30:50 | 10/17/2025 17:25:55 | 10/16/2025 03:30:50 | Nokia MW HC_P0 Observing Performance Issue at JED6135-JED0155-7 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | SRAN | jeddah | Sceco | TX NSA | JED6135-JED0155-7 | FLM_TE | JED6135 | JED6135 | PCM-20251014-00001843 | Kindly close TT with RCA or share required data Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Kindly close TT with RCA or share required data Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/15/2025 15:30:50 | 10/16/2025 14:11:56 | 10/17/2025 17:25:45 |  |  | 10/17/2025 17:25:55 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000927 | PCM-20251015-00001514 | TT-20251015-01589 | Reference_telecom | Region_2 | UNZ2M7186 | UNZ0186 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/15/2025 15:31:10 | 10/15/2025 21:07:09 | 10/16/2025 03:31:10 | Cell RX Channel Interference Noise Power Unbalanced at UNZ2M7186-P3-L800 @ Sceco | 10/15/2025 12:08:52 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/15/2025 12:08:50 | P3 | 4G | buraidah | Sceco | 2G NSA | UNZ2M7186 | FLM_TE |  |  | PCM-20251015-00001463 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/15/2025 15:31:10 | 10/15/2025 21:07:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015000950 | PCM-20251015-00001553 | TT-20251015-01645 | Telecom | Region_2 | RIY0175 | RIY0175 | Equipment | SFP_BTS | Clean SFP | Ejaz Hussain Muhammad Sharif | 10/15/2025 15:45:29 | 10/15/2025 17:19:28 | 10/15/2025 19:45:29 | 2(2G) 1(LTE) sites down under RIYA6014-P3,RIY0175-P1-VIP/R2_RY1_HWBSC01 @ Sceco | 10/15/2025 15:27:06 | Critical | 21825 | CSL Fault | 10/15/2025 15:27:02 | VIP | SRAN | riyadh | Sceco | 2G_LTE SA | RIY0175-P1-VIP 2G_LTE,RIYA6014-P3 2G | FLM_TE | RIY0175 | Dear FLM EM Team, Hub : RIY0175 We are observing ETH_LOS alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. | PCM-20251015-00001539 | Dear FLM EM Team, Hub : RIY0175 We are observing ETH_LOS alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. | Dear FLM EM Team, Hub : RIY0175 We are observing ETH_LOS alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. |  | sites down |  | API | 10/15/2025 15:45:29 | 10/15/2025 17:18:21 | 10/15/2025 17:18:31 | 10/15/2025 17:18:34 | 10/15/2025 17:18:53 | 10/15/2025 17:19:28 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000954 | PCM-20251015-00001562 | TT-20250929-02144 | MW_HC | Region_1 | ARM0888 | ARM0888 |  |  |  | Mohamed Abdelaziz | 10/15/2025 15:50:23 | 10/15/2025 16:54:54 | 10/16/2025 03:50:23 | Huawei MW HC_P2 Observing Errors at ARM0888-ARM0884 | 09/29/2025 16:35:38 | Minor |  | LOF | 09/29/2025 16:35:38 | P2 | SRAN | khafji | Sceco | TX NSA | ARM0888-ARM0884 | FLM_TE | ARM0888 | dear team , link is flapping , kindly check locally | PCM-20251015-00001554 | dear team , link is flapping , kindly check locally | dear team , link is flapping , kindly check locally |  |  |  | API | 10/15/2025 15:50:23 | 10/15/2025 16:54:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000957 | PCM-20251015-00001565 | TT-20251015-01682 | Telecom | Region_4 | JED1M7435 | JED0435 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 15:52:29 | 10/16/2025 09:37:46 | 10/15/2025 21:52:29 | BASE STATION SERVICE PROBLEM (RF Module filter input power missing) at JED1M7435-P1-WDM-CA-L900-L800-SBTS @ Sceco | 10/15/2025 15:42:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 15:42:15 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7435 | FLM_TE |  |  | PCM-20251015-00001556 | 1. Check if the ambient temperature or environmental conditions are within the designed limits of the radio module. When the ambient temperature or environmental conditions are out of limits, the alarm is expected and no further actions are needed. 2. Check if the airflow is not blocked by some objects. Make sure that the minimum thermal clearances are followed. Remove any objects that might be blocking the airflow, and mount the module according to instructions and recommendations. 3. Check if excessive sunlight might be causing overheating. Install the sun shield and follow the mounting instructions and recommendations. | 1. Check if the ambient temperature or environmental conditions are within the designed limits of the radio module. When the ambient temperature or environmental conditions are out of limits, the alarm is expected and no further actions are needed. 2. Check if the airflow is not blocked by some objects. Make sure that the minimum thermal clearances are followed. Remove any objects that might be blocking the airflow, and mount the module according to instructions and recommendations. 3. Check if excessive sunlight might be causing overheating. Install the sun shield and follow the mounting instructions and recommendations. |  |  |  | API | 10/15/2025 15:52:29 | 10/16/2025 09:37:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251015001025 | PCM-20251015-00001671 | TT-20251015-01793 | EM | Region_6 | AQQ1M8425 | AQQ2425 |  |  |  | Muhammad Raees | 10/15/2025 16:50:36 | 10/21/2025 20:21:36 | 10/16/2025 04:50:36 | SHELTER DOOR OPEN at AQQ1M8425-G9-L8-SBTS-P3 @ Generator_SG | 10/15/2025 16:50:17 | Minor | 7103 | SHELTER DOOR OPEN | 10/15/2025 16:50:07 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8425 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | Manual | 10/15/2025 16:50:36 | 10/21/2025 20:21:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015001027 | PCM-20251015-00001675 | TT-20251015-01042 | Reference_telecom | Region_4 | JED0604 | JED0604 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 16:53:21 | 10/16/2025 09:37:47 | 10/16/2025 04:53:21 | Nokia Eband Observing Degrade-LAG 2,ReplaceableUnitProblem-Card - 6 at JED0604-8-10.10.178.193 | 10/12/2025 14:08:31 | Minor |  | LOF | 10/12/2025 14:08:31 | P1 | 2G | jeddah | Sceco | TX NSA | JED0604-8-10.10.178.193 | FLM_TE |  |  | PCM-20251015-00001644 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/15/2025 16:53:21 | 10/16/2025 09:37:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001053 | PCM-20251015-00001712 | TT-20251015-01824 | EM | Region_6 | QLW1M8364 | QLW2364 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/15/2025 17:10:44 | 10/15/2025 17:25:30 | 10/16/2025 05:10:44 | RECTIFIER MODULE FAILURE at QLW1M8364-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/15/2025 17:02:32 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/15/2025 17:02:26 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8364 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/15/2025 17:10:44 | 10/15/2025 17:25:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251015001056 | PCM-20251015-00001716 | TT-20251015-01223 | Reference_telecom | Region_3 | MDYB2M3503 | MDYB0503 |  |  |  | Muhammad Sajjad R3 | 10/15/2025 17:11:56 | 10/15/2025 17:40:58 | 10/16/2025 05:11:56 | External Clock Reference Problem at MDYB2M3503-P3 @ Sceco | 10/15/2025 09:38:19 | Minor | 26262 | External Clock Reference Problem | 10/15/2025 09:37:41 | P3 | 3G | yanbu | Sceco | 3G NSA | MDYB2M3503 | FLM_TE |  |  | PCM-20251015-00001613 | Need HC on below link as bad performance MDYB0313-YNB0670 | Need HC on below link as bad performance MDYB0313-YNB0670 |  |  |  | API | 10/15/2025 17:11:56 | 10/15/2025 17:40:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001058 | PCM-20251015-00001718 | TT-20251015-01828 | Telecom | Region_6 | BAH0017 | BAH0017 |  |  |  | SHAH KHALID | 10/15/2025 17:12:16 | 10/15/2025 19:54:42 | 10/16/2025 05:12:16 | ODU CPU / Cable Open at BAH0017-1 on 10.1.174.2 @ Sceco | 10/15/2025 17:11:12 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/15/2025 16:52:55 | P1 | 2G | Albaha | Sceco | TX NSA | BAH0017 | FLM_TE | [8 empty] | API | 10/15/2025 17:12:16 | 10/15/2025 19:54:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001077 | PCM-20251015-00001753 | TT-20251015-01875 | Telecom | Region_2 | RIY0647 | RIY0647 | Transsmission | Fiber CUT | STC LL cut | Mubashar Farooq Abdul Majeed | 10/15/2025 17:30:53 | 10/15/2025 19:55:41 | 10/15/2025 21:30:53 | STC : LINK DOWN B/W RIY0443-RIY0647 | 10/15/2025 17:30:24 | Critical | 1-12843 | OSC_LOS | 10/15/2025 17:30:15 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0647 | FLM_TE | [5 empty] | 0-1-C-9-F1AST4-1(RM1/TM1(FROM RIY0443))-OSC:1 |  |  | API | 10/15/2025 17:30:53 | 10/15/2025 18:45:56 | 10/15/2025 19:55:27 |  |  | 10/15/2025 19:55:41 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001086 | PCM-20251015-00001767 | TT-20251015-01888 | Telecom | Region_2 | RIY0443-ZRi02-2-CSG-03 | RIY0443 |  |  |  | Farmanullah Akbar Jan | 10/15/2025 17:37:04 | 10/16/2025 09:31:16 | 10/15/2025 23:37:04 | DWDM_Physical Port Down at RIY0443-ZRi02-2-CSG-03 @ Sceco | 10/15/2025 17:30:36 | Major | 101-2505274 | Physical Port Down | 10/15/2025 17:30:14 | P1 | IPRAN | riyadh | Sceco | IPRAN SA | RIY0443-ZRi02-2-CSG-03 | FLM_TE | [8 empty] | API | 10/15/2025 17:37:04 | 10/16/2025 09:31:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001089 | PCM-20251015-00001775 | TT-20251015-01894 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/15/2025 17:40:42 | 10/18/2025 14:26:52 | 10/15/2025 23:40:42 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/15/2025 14:40:21 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/15/2025 14:40:09 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/15/2025 17:40:42 | 10/18/2025 14:26:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001092 | PCM-20251015-00001778 | TT-20251015-01896 | Telecom | Region_4 | JED1MN0743 | JED0743 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 17:42:15 | 10/15/2025 17:42:15 | 10/15/2025 23:42:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0743-NR2.6-P3 @ Sceco | 10/15/2025 17:41:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 17:41:21 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0743 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 17:42:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001098 | PCM-20251015-00001792 | TT-20251015-01909 | Reference_telecom | Region_4 | JED0177 | JED0177 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | Abdulraqib Abdo Saif Abdulaleem | 10/15/2025 17:48:26 | 10/21/2025 13:24:41 | 10/16/2025 05:48:26 | Degrade observed in JED0177 towards 10.10.184.100 @ Sceco | 10/15/2025 05:48:48 | Minor |  | Degrade | 10/15/2025 05:48:05 | P2 | 2G | jeddah | Sceco | TX NSA | JED0177 | FLM_TE | [8 empty] | API | 10/15/2025 17:48:26 | 10/21/2025 11:17:26 | 10/21/2025 11:20:32 | 10/21/2025 11:20:35 | 10/21/2025 11:20:42 | 10/21/2025 13:24:41 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20251015001097 | PCM-20251015-00001791 | TT-20251015-01908 | Reference_telecom | Region_4 | JED0743 | JED0743 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/15/2025 17:48:26 | 10/23/2025 17:53:03 | 10/16/2025 05:48:26 | LagPortDown observed in JED0743 towards 10.10.184.99 @ Sceco | 10/15/2025 05:48:48 | Minor |  | LagPortDown | 10/15/2025 05:48:05 | P2 | 2G | jeddah | Sceco | TX NSA | JED0743 | FLM_TE | [8 empty] | API | 10/15/2025 17:48:26 |  | 10/23/2025 17:52:36 | 10/23/2025 17:53:03 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001107 | PCM-20251015-00001811 | TT-20251015-01927 | Reference_telecom | Region_4 | JDMD0860 | JDMD0860 |  |  |  | Khizer Hayat | 10/15/2025 18:00:17 | 10/15/2025 18:12:34 | 10/16/2025 06:00:17 | DemFail observed in JDMD0860_15 towards 10.3.235.1 @ Sceco_STB | 10/15/2025 08:08:07 | Minor |  | DemFail | 10/15/2025 08:08:03 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDMD0860 | FLM_TE | [8 empty] | API | 10/15/2025 18:00:17 | 10/15/2025 18:12:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001116 | PCM-20251015-00001824 | TT-20251015-01922 | Telecom | Region_4 | JED0922 | JED0922 | Transsmission | MW_HW_stuck | Reset IDU | Mohammed Ramadan A Abu Abid | 10/15/2025 18:04:41 | 10/16/2025 08:48:51 | 10/16/2025 00:04:41 | 2(2G) 2(5G) sites down under JED2929-P2-USF,JED0922-P3/JED0922-P3 @ Generator_SG | 10/15/2025 17:53:07 | Major | 7706 | BTS O&M LINK FAILURE | 10/15/2025 17:53:04 | P3 | 2G | jeddah | Generator_SG | 2G SA | JED0922-P3 2G,JED2929-P2-USF 2G | FLM_TE | JED0922 | Results: DOWN SITE HUB JED0922-P3 JED0922 JED2929-P2-USF JED0922 Summary: Hub: JED0922, Down Count: 2, Down Sites: JED0922-P3, JED2929-P2-USF Alarm Summary: JED0922 Alarm Active on HUB | PCM-20251015-00001817 | Thanks to check locally HUB site JED0922 | Thanks to check locally HUB site JED0922 |  | sites down |  | API | 10/15/2025 18:04:41 | 10/15/2025 18:31:56 | 10/15/2025 20:56:12 | 10/15/2025 20:56:19 | 10/15/2025 20:56:31 | 10/16/2025 08:48:51 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001131 | PCM-20251015-00001846 | TT-20251013-02040 | MW_HC | Region_6 | JIZ0550 | JIZ0550 | Transsmission | MW_HW_stuck | Reset ODU | Mohammed Sideag Mohammed Ali | 10/15/2025 18:19:29 | 10/15/2025 18:26:58 | 10/16/2025 06:19:29 | Nokia MW HC_P0 Observing Performance Issue at JIZ0550_01-JIZ0169_03 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jizan | Generator_DG | TX NSA | JIZ0550_01-JIZ0169_03 | FLM_TE |  |  | PCM-20251015-00001665 | Please share the RCA plus start & end time of action | Please share the RCA plus start & end time of action |  |  |  | API | 10/15/2025 18:19:29 | 10/15/2025 18:26:32 | 10/15/2025 18:26:38 |  |  | 10/15/2025 18:26:58 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251015001132 | PCM-20251015-00001847 | TT-20251015-01654 | Telecom | Region_4 | JED1MC2112 | JED2112 | Equipment | SFP_BTS | Clean SFP | Abdullah Ahmad Mohammad Abdelsheekh | 10/15/2025 18:20:23 | 10/16/2025 16:58:44 | 10/16/2025 00:20:23 | BASE STATION CONNECTIVITY PROBLEM (NG SCTP endpoint broken) at JED1MC2112-5G-NR3.5-P3 @ | 10/15/2025 15:31:51 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/15/2025 15:18:39 | VIP | 5G | jeddah |  | 5G NSA | JED1MC2112 | FLM_TE |  |  | PCM-20251015-00001522 | Please check the GPS is not available | Please check the GPS is not available |  |  |  | API | 10/15/2025 18:20:23 | 10/16/2025 16:58:36 | 10/16/2025 16:58:40 | 10/16/2025 16:58:42 | 10/16/2025 16:58:44 |  |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001142 | PCM-20251015-00001872 | TT-20251015-01996 | EM | Region_3 | TBQL2M5234 | TBQL0234 |  |  |  | Moustafa Samir Omar | 10/15/2025 18:38:31 | 10/22/2025 21:57:15 | 10/16/2025 00:38:31 | Mains Failure at TBQL2M5234-P1-HUB @ Sceco | 10/15/2025 18:28:42 | Major | 65109 | Mains Failure | 10/15/2025 18:28:39 | P1 | 2G | tabouk | Sceco | 2G NSA | TBQL2M5234 | FLM_EM | [8 empty] | API | 10/15/2025 18:38:31 | 10/22/2025 21:57:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001158 | PCM-20251015-00001904 | TT-20251015-01993 | Telecom | Region_4 | JED2979 | JED2979 | Transsmission | IPRAN_Fluctuation | Change Port | Abd EL Azeez EL Sayed Soliman | 10/15/2025 18:58:09 | 10/15/2025 19:55:09 | 10/15/2025 22:58:09 | 2(2G) 2(LTE) 2(5G) sites down under JED2979-P1-VIP,JED2903-P3/JED2903-P3 @ Sceco | 10/15/2025 18:31:59 | Critical | 7706 | BTS O&M LINK FAILURE | 10/15/2025 18:31:56 | VIP | 2G | jeddah | Generator_SG | 2G_LTE_5G SA | JED2903-P3 2G_LTE,JED2979-P1-VIP 2G_5G | FLM_EM | JED2979 | Scattered sites: JED2979,JED2903 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251015-00001874 | Scattered sites: JED2979,JED2903 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Scattered sites: JED2979,JED2903 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/15/2025 18:58:09 | 10/15/2025 19:08:19 | 10/15/2025 19:54:58 |  |  | 10/15/2025 19:55:09 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251015001166 | PCM-20251015-00001915 | TT-20251015-02030 | Reference_telecom | Region_5 | HAJ0181 | HAJ0181 |  |  |  | Muhammad Saleem Iqbal | 10/15/2025 19:07:25 | 10/15/2025 23:06:09 | 10/16/2025 07:07:25 | ETH_LOS at HAJ0181_NE_1 @ Sceco | 10/15/2025 15:07:22 | Minor | 1-235 | ETH_LOS | 10/15/2025 15:07:09 | VIP | SRAN | makkah | Sceco | TX NSA | HAJ0181 | FLM_TE | [8 empty] | API | 10/15/2025 19:07:25 | 10/15/2025 23:06:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001188 | PCM-20251015-00001954 | TT-20251015-02062 | Telecom | Region_4 | JED1M8066 | JED2066 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/15/2025 19:32:44 | 10/19/2025 17:44:22 | 10/16/2025 01:32:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8066-CA-L800-SBTS-P3 @ Generator_SG | 10/15/2025 19:31:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 19:31:45 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 19:32:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001198 | PCM-20251015-00001969 | TT-20251015-01959 | Reference_telecom | Region_1 | DAM2M7644 | DAM0644 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/15/2025 19:42:02 | 10/16/2025 01:16:25 | 10/16/2025 07:42:02 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M7644-CA-L800-P2 @ Sceco | 10/15/2025 15:16:31 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/15/2025 15:16:28 | P2 | 4G | dammam | Sceco | 2G NSA | DAM2M7644 | FLM_TE |  |  | PCM-20251015-00001838 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/15/2025 19:42:02 | 10/16/2025 01:16:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001206 | PCM-20251015-00001977 | TT-20251015-01943 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 19:47:37 | 10/15/2025 19:47:37 | 10/16/2025 01:47:37 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/15/2025 17:57:51 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/15/2025 17:57:40 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251015-00001825 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/15/2025 19:47:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001208 | PCM-20251015-00001979 | TT-20251014-01155 | Telecom | Region_4 | JED6031 | JED6031 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Mohamed Farag Abdelbary | 10/15/2025 19:49:03 | 10/17/2025 17:25:30 | 10/16/2025 07:49:03 | As per BO request NEC MW link JED6031-JED0139 | 10/14/2025 12:30:53 | Minor | 113388 | LOF | 10/14/2025 12:30:56 | P3 | 2G | jeddah | Sceco | TX NSA | JED6031-JED0139 | FLM_TE |  |  | PCM-20251015-00001573 | Please share the RCA plus start & end time of action | Please share the RCA plus start & end time of action |  |  |  | API | 10/15/2025 19:49:03 | 10/16/2025 14:11:56 | 10/17/2025 17:25:21 |  |  | 10/17/2025 17:25:30 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001212 | PCM-20251015-00001983 | TT-20251015-01804 | Reference_telecom | Region_4 | RYMK1M3536 | RYMK0536 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/15/2025 19:56:02 | 10/15/2025 23:51:13 | 10/16/2025 01:56:02 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at RYMK1M3536-P2 @ Generator_DG | 10/15/2025 16:31:52 | Major | 7771 | WCDMA CELL OUT OF USE | 10/15/2025 16:29:43 | P2 | 3G | taif | Generator_DG | 3G SA | RYMK1M3536 | FLM_TE |  |  | PCM-20251015-00001694 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/15/2025 19:56:02 | 10/15/2025 23:51:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001222 | PCM-20251015-00001994 | TT-20251015-02092 | Telecom | Region_4 | JED1M8602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 20:01:40 | 10/16/2025 09:37:48 | 10/16/2025 02:01:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8602-CA-L800-P3 @ Sceco | 10/15/2025 20:01:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 20:00:51 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8602 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 20:01:40 | 10/16/2025 09:37:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001229 | PCM-20251015-00002006 | TT-20251015-02097 | Reference_telecom | Region_2 | RIYD2U6721 | RIYD6021 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/15/2025 20:09:59 | 10/16/2025 08:35:24 | 10/16/2025 08:09:59 | Cell RX Channel Interference Noise Power Unbalanced at RIYD2U6721-L800-CA-P3 @ Sceco | 10/15/2025 17:03:14 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/15/2025 17:03:10 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYD2U6721 | FLM_TE |  |  | PCM-20251015-00001998 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/15/2025 20:09:59 | 10/16/2025 08:35:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001233 | PCM-20251015-00002012 | TT-20251015-02114 | Telecom | Region_4 | JED0271 | JED0271 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/15/2025 20:17:11 | 10/19/2025 17:44:22 | 10/16/2025 02:17:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/15/2025 20:16:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 20:16:27 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 20:17:11 | 10/16/2025 05:46:05 | 10/19/2025 09:31:42 |  |  | 10/19/2025 09:31:59 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001234 | PCM-20251015-00002013 | TT-20251015-02106 | Telecom | Region_4 | MLJI1M3187 | MLJI0187 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/15/2025 20:18:01 | 10/18/2025 11:08:43 | 10/16/2025 02:18:01 | 1(3G) sites down under MLJI0187-P2-USF/MLJI1M3187-P2-USF @ Sceco | 10/15/2025 20:10:21 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/15/2025 20:09:42 | P2 | 3G | alaith | Sceco | 3G SA | MLJI0187-P2-USF | FLM_TE | MLJI0187 | Results: DOWN SITE HUB MLJI0187-P2-USF MLJI0187 Summary: Hub: MLJI0187, Down Count: 1, Down Sites: MLJI0187-P2-USF Alarm Summary: MLJI0187 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/15/2025 20:18:01 | 10/16/2025 12:08:42 | 10/18/2025 11:08:28 |  |  | 10/18/2025 11:08:43 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001246 | PCM-20251015-00002027 | TT-20251015-01783 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 20:33:48 | 10/15/2025 20:33:48 | 10/16/2025 02:33:48 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/15/2025 16:41:19 | Major | 7114 | CELL SERVICE PROBLEM | 10/15/2025 16:41:10 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251015-00001662 | SoC autonomous reset as recovery action alarm observed on multiple times causing fluctuation , Please perform HC on SFP, Cable connectivity & HW. | SoC autonomous reset as recovery action alarm observed on multiple times causing fluctuation , Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/15/2025 20:33:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001251 | PCM-20251015-00002039 | TT-20251015-02135 | Reference_telecom | Region_6 | DAR0916 | DAR0916 |  |  |  | Muhammad Ali | 10/15/2025 20:47:07 | 10/15/2025 22:13:10 | 10/16/2025 08:47:07 | DemFail observed in DAR0916 towards 10.74.120.156 @ Sceco | 10/15/2025 08:48:19 | Minor |  | DemFail | 10/15/2025 08:46:51 | P2 | 2G | dair | Sceco | TX NSA | DAR0916 | FLM_TE | [8 empty] | API | 10/15/2025 20:47:07 | 10/15/2025 22:13:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001252 | PCM-20251015-00002040 | TT-20251015-02136 | Reference_telecom | Region_6 | DAR0913 | DAR0913 |  |  |  | Muhammad Ali | 10/15/2025 20:47:07 | 10/15/2025 22:13:10 | 10/16/2025 08:47:07 | LossOfSignal observed in DAR0913 towards 10.74.120.155 @ Generator_SG | 10/15/2025 08:48:19 | Minor |  | LossOfSignal | 10/15/2025 08:46:49 | P2 | 2G | dair | Generator_SG | TX NSA | DAR0913 | FLM_TE | [8 empty] | API | 10/15/2025 20:47:07 | 10/15/2025 22:13:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001256 | PCM-20251015-00002044 | TT-20251008-02030 | MW_HC | Region_5 | QUR0337 | QUR0337 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/15/2025 20:49:10 | 10/15/2025 20:49:10 | 10/16/2025 08:49:10 | Nokia MW HC_P0 Observing Performance Issue at QUR0337_01-MAK0188_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Sceco | TX NSA | QUR0337_01-MAK0188_01 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251015-00002033 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/15/2025 20:49:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001258 | PCM-20251015-00002047 | TT-20251015-02141 | Telecom | Region_4 | JED2623 | JED2623 | Equipment | SFP_BTS | Clean SFP | Khaled Mohammad Abdallah | 10/15/2025 20:50:04 | 10/16/2025 00:21:01 | 10/16/2025 02:50:04 | PT:: FLM Need to perform HC at JED2623 under R4 (BO Request) | 10/15/2025 20:49:40 | Major | 676767671 | Health Check-WO to TE FME | 10/15/2025 20:49:40 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED2623 | FLM_TE | [8 empty] | API | 10/15/2025 20:50:04 | 10/15/2025 23:32:47 | 10/15/2025 23:32:54 | 10/15/2025 23:32:56 | 10/15/2025 23:33:00 | 10/16/2025 00:21:01 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001262 | PCM-20251015-00002052 | TT-20251015-01926 | Reference_telecom | Region_4 | HHR0447 | HHR0447 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/15/2025 20:52:20 | 10/16/2025 10:13:00 | 10/16/2025 00:52:20 | BCF NOTIFICATION (FF FF FF FF FF FF) at HHR0447-P1-VIP-HHR @ Generator_SG | 10/15/2025 17:52:37 | Critical | 7602 | BCF NOTIFICATION | 10/15/2025 17:52:23 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0447 | FLM_TE |  |  | PCM-20251015-00001810 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/15/2025 20:52:20 | 10/16/2025 10:13:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001268 | PCM-20251015-00002061 | TT-20251015-02158 | Telecom | Region_4 | HAW1M8351 | HAW2351 |  |  |  | Rashid Shafique | 10/15/2025 21:07:18 | 10/15/2025 22:05:20 | 10/16/2025 03:07:18 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAW1M8351-P3-CA-L800 @ Sceco | 10/15/2025 21:06:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 21:06:06 | P2 | 4G | taif | Sceco | 5G_Cell SA | HAW1M8351 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 21:07:18 | 10/15/2025 22:05:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001269 | PCM-20251015-00002062 | TT-20251015-02159 | Telecom | Region_4 | JED1M8243 | JED2243 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 21:07:48 | 10/19/2025 17:44:22 | 10/16/2025 03:07:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8243-L800-CA-SBTS-P3 @ Sceco | 10/15/2025 21:06:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 21:06:35 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8243 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 21:07:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001277 | PCM-20251015-00002080 | TT-20251015-02180 | EM | Region_1 | JBL0465 | JBL0465 | Enviroment | Air Condition | Change Outdoor motor | Islam Elsawi Mohamed Elsawi | 10/15/2025 21:22:47 | 10/17/2025 19:20:51 | 10/16/2025 01:22:47 | Door opening alarm at JBL0465-RPT-P1-Core-DIA-WDM @ Sceco_STB | 10/15/2025 21:22:18 | Critical | 65101 | Door opening alarm | 10/15/2025 21:22:15 | P1 | SRAN | jubail | Sceco_STB | 3G NSA | JBL0465 | FLM_EM | [8 empty] | API | 10/15/2025 21:22:47 | 10/17/2025 06:45:42 | 10/17/2025 19:20:35 |  |  | 10/17/2025 19:20:51 |  | Islam Elsawi Mohamed Elsawi |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251015001279 | PCM-20251015-00002082 | TT-20251015-02182 | EM | Region_1 | JB1 | JB1 |  |  |  | Mohamed Samir Farahat Allam | 10/15/2025 21:23:18 | 10/15/2025 22:25:06 | 10/16/2025 01:23:18 | Door opening alarm BSC New shelter at JB1-Shelter 6-WDM-Core-P1 @ Sceco_STB | 10/15/2025 21:23:04 | Critical | 65134 | Door opening alarm BSC New shelter | 10/15/2025 21:23:01 | P1 | BSC | jubail | Sceco_STB | 2G NSA | JB1 | FLM_EM | [8 empty] | API | 10/15/2025 21:23:18 | 10/15/2025 22:25:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251015001304 | PCM-20251015-00002126 | TT-20251015-02236 | Telecom | Region_4 | JED2179 | JED2179 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/15/2025 22:07:13 | 10/19/2025 17:44:24 | 10/16/2025 04:07:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2179-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/15/2025 22:06:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 22:06:14 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2179 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/15/2025 22:07:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251015001325 | PCM-20251015-00002162 | TT-20251015-02277 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/15/2025 22:59:23 | 10/15/2025 22:59:23 | 10/16/2025 04:59:23 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/15/2025 22:55:54 | Major | 1-12545 | LOCAL_FAULT | 10/15/2025 22:55:41 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE | [5 empty] | 1-ELC(1-E)-2-G1M520S-9(RX7/TX7)-CLIENT:1 |  |  | API | 10/15/2025 22:59:23 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001326 | PCM-20251015-00002164 | TT-20251015-02264 | Reference_telecom | Region_1 | DMHF2M7081 | DMHF0081 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/15/2025 23:01:09 | 10/16/2025 08:21:38 | 10/16/2025 11:01:09 | Cell RX Channel Interference Noise Power Unbalanced at DMHF2M7081-P1-HUB-L800-CA @ Generator_SG | 10/15/2025 19:46:09 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/15/2025 19:46:06 | P1 | 4G | hafouf | Generator_SG | 2G NSA | DMHF2M7081 | FLM_TE |  | Dears Kindly check HW | PCM-20251015-00002149 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/15/2025 23:01:09 | 10/16/2025 08:21:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251015001329 | PCM-20251015-00002167 | TT-20251015-02279 | Telecom | Region_2 | SRIY0386 | SRIY0386 |  |  |  | Asad Ali Nadiq Khan | 10/15/2025 23:04:31 | 10/23/2025 16:30:44 | 10/16/2025 05:04:31 | 1(LTE) sites down under SRIY0386-P3_SRAN @ Sceco | 10/15/2025 22:56:25 | Major | 301 | NE Is Disconnected | 10/15/2025 22:56:22 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0386-P3_SRAN | FLM_TE | SRIY0386 | Results: DOWN SITE HUB SRIY0386-P3_SRAN SRIY0386 Summary: Hub: SRIY0386, Down Count: 1, Down Sites: SRIY0386-P3_SRAN Alarm Summary: SRIY0386 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/15/2025 23:04:31 | 10/16/2025 09:41:35 | 10/23/2025 16:30:44 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001330 | PCM-20251015-00002168 | TT-20251015-02284 | Reference_telecom | Region_4 | JED0126 | JED0126 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 23:05:02 | 10/16/2025 09:37:49 | 10/16/2025 11:05:02 | InternalCommunicationProblem observed in JED0126_02 towards 10.10.147.182 @ Sceco_STB | 10/15/2025 11:06:36 | Minor |  | InternalCommunicationProblem | 10/15/2025 11:04:30 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JED0126 | FLM_TE | [8 empty] | API | 10/15/2025 23:05:02 | 10/16/2025 09:37:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001339 | PCM-20251015-00002181 | TT-20251015-02296 | Reference_telecom | Region_4 | JED0676 | JED0676 |  |  |  | MALIK ATIF ZAMAN | 10/15/2025 23:18:27 | 10/16/2025 09:37:49 | 10/16/2025 11:18:27 | DemFail observed in JED0676_18 towards 10.10.147.183 @ Sceco | 10/15/2025 11:18:05 | Minor |  | DemFail | 10/15/2025 11:17:55 | VIP | 2G | jeddah | Sceco | TX NSA | JED0676 | FLM_TE | [8 empty] | API | 10/15/2025 23:18:27 | 10/16/2025 09:37:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001340 | PCM-20251015-00002182 | TT-20251015-02289 | Reference_telecom | Region_2 | RIYB2U6786 | RIYB6086 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/15/2025 23:19:32 | 10/16/2025 08:35:24 | 10/16/2025 11:19:32 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6786-L1800-CA-P3 @ Sceco | 10/15/2025 20:08:22 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/15/2025 20:08:19 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6786 | FLM_TE |  | Dears Kindly check HW | PCM-20251015-00002175 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/15/2025 23:19:32 | 10/16/2025 08:35:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001347 | PCM-20251015-00002192 | TT-20251015-02212 | Telecom | Region_4 | JED1M7244 | JED0244 | Equipment | BSS_HW_fault | Replace RRU | MALIK ATIF ZAMAN | 10/15/2025 23:25:09 | 10/21/2025 16:02:11 | 10/16/2025 05:25:09 | BASE STATION SERVICE PROBLEM (RF Module filter input power missing) at JED1M7244-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/15/2025 21:41:47 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/15/2025 21:41:37 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7244 | FLM_TE |  |  | PCM-20251015-00002108 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/15/2025 23:25:09 | 10/16/2025 09:37:50 | 10/21/2025 14:04:56 | 10/21/2025 14:04:58 | 10/21/2025 14:58:55 | 10/21/2025 16:02:11 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001350 | PCM-20251015-00002195 | TT-20251015-02305 | Reference_telecom | Region_4 | MKMD0561 | MKMD0561 |  |  |  | Khizer Hayat | 10/15/2025 23:26:12 | 10/15/2025 23:56:38 | 10/16/2025 11:26:12 | Degrade observed in MKMD0561_02 towards 10.10.178.74 @ Sceco | 10/15/2025 11:27:39 | Minor |  | Degrade | 10/15/2025 11:26:07 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0561 | FLM_TE | [8 empty] | API | 10/15/2025 23:26:12 | 10/15/2025 23:56:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251015001361 | PCM-20251015-00002213 | TT-20251015-02308 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/15/2025 23:39:19 | 10/17/2025 17:24:20 | 10/16/2025 03:39:19 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/15/2025 23:19:47 | Critical | 7654 | CELL OPERATION DEGRADED | 10/15/2025 23:19:36 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251015-00002199 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/15/2025 23:39:19 | 10/16/2025 14:11:56 | 10/17/2025 17:24:14 |  |  | 10/17/2025 17:24:20 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015001371 | PCM-20251015-00002229 | TT-20251015-02335 | Telecom | Region_2 | RIY2208 | RIY2208 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/15/2025 23:59:48 | 10/16/2025 08:46:22 | 10/16/2025 05:59:48 | BBU CPRI Interface Error at RIY2208-P1-VIP-SRAN @ Generator_SG | 10/15/2025 23:57:48 | Major | 26234 | BBU CPRI Interface Error | 10/15/2025 23:54:41 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2208 | FLM_TE | [8 empty] | API | 10/15/2025 23:59:48 | 10/16/2025 08:46:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251016000001 | PCM-20251016-00000002 | TT-20251002-02044 | Telecom | Region_2 | R1-RYMK-SEC0027 | SEC0027 |  |  |  | Asad Ali Nadiq Khan | 10/16/2025 00:00:05 | 10/23/2025 16:30:40 | 10/16/2025 04:00:05 | SCECO :: LINK DOWN B/W R1-RYMK-SEC0027--R2-RYMK-SEC0028 | 10/02/2025 16:47:11 | Critical | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/02/2025 16:47:11 | P1 | DWDM | quweyah | Sceco_STB | DWDM NSA | R1-RYMK-SEC0027 | FLM_TE |  |  | PCM-20251015-00002158 | dear teams , issue was fiber cut in SEC span , so please support to close PCM . | dear teams , issue was fiber cut in SEC span , so please support to close PCM . |  |  |  | API | 10/16/2025 00:00:05 | 10/16/2025 09:41:36 | 10/23/2025 16:30:40 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000007 | PCM-20251016-00000011 | TT-20251016-00010 | Telecom | Region_4 | JED0053 | JED0053 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 00:08:04 | 10/16/2025 10:48:46 | 10/16/2025 06:08:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0053-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-SHOP @ Sceco | 10/16/2025 00:07:16 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 00:07:05 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0053 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 00:08:04 | 10/16/2025 10:48:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000022 | PCM-20251016-00000052 | TT-20251016-00057 | Reference_telecom | Region_5 | MAK0784 | MAK0784 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/16/2025 00:42:05 | 10/18/2025 14:02:53 | 10/16/2025 12:42:05 | LossOfSignal observed in MAK0784_02_ towards 10.21.74.65 @ Generator_SG | 10/15/2025 12:44:15 | Minor |  | LossOfSignal | 10/15/2025 12:41:59 | P1 | 2G | makkah | Generator_SG | TX NSA | MAK0784 | FLM_TE | [8 empty] | API | 10/16/2025 00:42:05 | 10/18/2025 14:02:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000029 | PCM-20251016-00000066 | TT-20251016-00074 | Telecom | Region_3 | MDN0442 | MDN0442 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/16/2025 00:57:04 | 10/16/2025 15:04:36 | 10/16/2025 12:57:04 | RF Unit Maintenance Link Failure at MDN0442-P3_SRAN @ Sceco | 10/16/2025 00:53:13 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/16/2025 00:51:31 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN0442 | FLM_TE | [8 empty] | API | 10/16/2025 00:57:04 | 10/16/2025 15:04:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000038 | PCM-20251016-00000083 | TT-20251016-00044 | Telecom | Region_4 | MLJI1M3196 | MLJI0196 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/16/2025 01:12:34 | 10/18/2025 11:09:06 | 10/16/2025 07:12:34 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at MLJI1M3196-P3 @ Generator_SG | 10/16/2025 00:26:16 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/15/2025 22:31:30 | P3 | 3G | alaith | Generator_SG | 3G NSA | MLJI1M3196 | FLM_TE |  |  | PCM-20251016-00000040 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/16/2025 01:12:34 | 10/16/2025 12:08:42 | 10/18/2025 11:08:55 |  |  | 10/18/2025 11:09:06 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000040 | PCM-20251016-00000085 | TT-20251016-00034 | Telecom | Region_4 | MLJI1M3204 | MLJI0204 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/16/2025 01:12:46 | 10/18/2025 11:07:42 | 10/16/2025 07:12:46 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at MLJI1M3204-P3 @ Generator_SG | 10/16/2025 00:21:42 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/15/2025 22:31:33 | P3 | 3G | alaith | Generator_SG | 3G NSA | MLJI1M3204 | FLM_TE |  |  | PCM-20251016-00000034 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/16/2025 01:12:46 | 10/16/2025 12:08:43 | 10/18/2025 11:07:27 |  |  | 10/18/2025 11:07:42 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000041 | PCM-20251016-00000089 | TT-20251016-00097 | EM | [7 empty] | 10/16/2025 01:15:10 | 10/16/2025 01:15:10 | 10/16/2025 05:15:10 | LOW BATTERY VOLTAGE + BATTERY FAILURE ALARM at RWPS5-SEC0032_OCS @ Sceco_STB | 10/16/2025 01:13:20 | Critical | 1-12307 | LOW BATTERY VOLTAGE + BATTERY FAILURE ALARM | 10/16/2025 01:13:12 | P1 | DWDM |  | Sceco_STB | DWDM NSA | RWPS5 | FLM_EM | [5 empty] | 0-TO WASIA-SEC0031(2-D)-71-E1EFI-[LOW BATTERY VOLTAGE + BATTERY FAILURE ALARM]:3 |  |  | API | 10/16/2025 01:15:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000060 | PCM-20251016-00000119 | TT-20251016-00121 | Reference_telecom | Region_2 | KHJ2M8304 | KHJ2304 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hakim Ullah Raif Ullah Jan | 10/16/2025 01:48:58 | 10/16/2025 09:52:29 | 10/16/2025 13:48:58 | Cell RX Channel Interference Noise Power Unbalanced at KHJ2M8304-P3-CA-L800 @ Sceco | 10/15/2025 22:39:01 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/15/2025 22:38:57 | P3 | 4G | riyadh | Sceco | 2G NSA | KHJ2M8304 | FLM_TE |  | Dears Kindly check HW | PCM-20251016-00000106 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/16/2025 01:48:58 | 10/16/2025 09:51:07 | 10/16/2025 09:51:46 |  |  | 10/16/2025 09:52:29 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000061 | PCM-20251016-00000122 | TT-20251016-00138 | Reference_telecom | Region_4 | JED0980 | JED0980 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 01:50:16 | 10/16/2025 01:50:16 | 10/16/2025 13:50:16 | DemFail observed in JED0980 _01 towards 10.10.182.178 @ Sceco | 10/15/2025 13:51:30 | Minor |  | DemFail | 10/15/2025 13:50:03 | P3 | 2G | jeddah | Sceco | TX NSA | JED0980 | FLM_TE | [8 empty] | API | 10/16/2025 01:50:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000063 | PCM-20251016-00000125 | TT-20251016-00031 | Telecom | Region_4 | JED1U6831 | JED6131 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/16/2025 01:51:34 | 10/17/2025 17:23:51 | 10/16/2025 07:51:34 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/16/2025 00:12:24 | Major | 7654 | CELL OPERATION DEGRADED | 10/16/2025 00:12:17 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251016-00000031 | FLM need to check VSWR issue at site. | FLM need to check VSWR issue at site. |  |  |  | API | 10/16/2025 01:51:34 | 10/16/2025 14:12:08 | 10/17/2025 17:23:43 |  |  | 10/17/2025 17:23:51 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000066 | PCM-20251016-00000129 | TT-20251016-00149 | EM | [7 empty] | 10/16/2025 01:55:27 | 10/16/2025 01:55:27 | 10/16/2025 05:55:27 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/16/2025 01:53:46 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/16/2025 01:53:35 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/16/2025 01:55:27 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000113 | PCM-20251016-00000195 | TT-20251016-00229 | Telecom | Region_2 | RIYA2U6848 | RIYA6148 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 02:16:07 | 10/18/2025 14:26:55 | 10/16/2025 08:16:07 | RF Out of Service at RIYA2U6848-P3 @ Sceco | 10/16/2025 02:14:25 | Major | 29248 | RF Out of Service | 10/16/2025 02:05:25 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6848 | FLM_TE | [8 empty] | API | 10/16/2025 02:16:07 | 10/18/2025 14:26:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000118 | PCM-20251016-00000206 | TT-20251016-00242 | EM | Region_2 | RIY0971 | RIY0971 | Enviroment | SCECO_Failure | SCECO auto restored | Ahmed Mohamed Ibrahim Elnagar | 10/16/2025 02:17:40 | 10/17/2025 17:46:10 | 10/16/2025 08:17:40 | Fire Alarm at RIY0971-P1-PNU-VIP_SRAN @ Sceco | 10/16/2025 02:14:40 | Major | 65119 | Fire Alarm | 10/16/2025 02:07:11 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0971 | FLM_EM | [8 empty] | API | 10/16/2025 02:17:40 | 10/16/2025 13:09:12 | 10/17/2025 16:49:56 | 10/17/2025 16:50:04 | 10/17/2025 16:50:07 | 10/17/2025 17:46:10 |  | Ahmed Mohamed Ibrahim Elnagar |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000122 | PCM-20251016-00000208 | TT-20251016-00244 | Telecom | Region_2 | RIYA2U6760A | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/16/2025 02:18:11 | 10/16/2025 08:35:26 | 10/16/2025 08:18:11 | RF Out of Service at RIYA2U6760A-P3 @ Sceco | 10/16/2025 02:16:11 | Major | 29248 | RF Out of Service | 10/16/2025 02:11:12 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6760A | FLM_TE | [8 empty] | API | 10/16/2025 02:18:11 | 10/16/2025 08:35:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000132 | PCM-20251016-00000228 | TT-20251016-00281 | Telecom | Region_4 | JED1M7667 | JED0667 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 02:38:08 | 10/16/2025 09:37:51 | 10/16/2025 14:38:08 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED1M7667-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/16/2025 02:27:28 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 02:27:15 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7667 | FLM_TE |  |  | PCM-20251016-00000223 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/16/2025 02:38:08 | 10/16/2025 09:37:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000133 | PCM-20251016-00000230 | TT-20251016-00296 | Telecom | [7 empty] | 10/16/2025 02:39:22 | 10/16/2025 02:39:22 | 10/16/2025 08:39:22 | COMMUN_FAIL at WADI9701-SEC0045_OCS @ Sceco | 10/16/2025 02:35:41 | Major | 1-199 | COMMUN_FAIL | 10/16/2025 02:35:31 | P1 | DWDM |  | Sceco | DWDM NSA | WADI9701 | FLM_TE | [5 empty] | 2-LOCAL-1(2-A)-1-G2TMD20-OTHER |  |  | API | 10/16/2025 02:39:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000141 | PCM-20251016-00000243 | TT-20251016-00311 | EM | [7 empty] | 10/16/2025 02:51:14 | 10/16/2025 02:51:14 | 10/16/2025 06:51:14 | NE_COMMU_GNE_SWITCH at SALWA-SEC0017_OCS @ Sceco | 10/16/2025 02:49:33 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 02:49:28 | P1 | DWDM |  | Sceco | DWDM NSA | SALWA | FLM_EM | [5 empty] | NE SALWA-SEC0017_OCS's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 02:51:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000142 | PCM-20251016-00000248 | TT-20251016-00316 | Telecom | Region_2 | RIYA6042 | RIYA6042 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/16/2025 02:52:17 | 10/16/2025 08:35:26 | 10/16/2025 14:52:17 | RF Unit Maintenance Link Failure at RIYA6042-DCU-3 @ Sceco | 10/16/2025 02:44:10 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/16/2025 02:46:51 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6042 | FLM_TE | [8 empty] | API | 10/16/2025 02:52:17 | 10/16/2025 08:35:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000146 | PCM-20251016-00000257 | TT-20251015-02326 | Telecom | Region_4 | HAW2371 | HAW2371 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/16/2025 03:02:12 | 10/16/2025 12:13:38 | 10/16/2025 09:02:12 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at HAW2371-P3 @ Sceco | 10/15/2025 23:46:17 | Major | 7607 | TRX OPERATION DEGRADED | 10/15/2025 23:46:14 | P3 | 2G | taif | Sceco | 2G_TRX NSA | HAW2371 | FLM_TE |  |  | PCM-20251015-00002222 | RSSI | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 03:02:12 | 10/16/2025 12:13:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000149 | PCM-20251016-00000270 | TT-20251016-00339 | EM | [7 empty] | 10/16/2025 03:10:22 | 10/16/2025 03:10:22 | 10/16/2025 07:10:22 | NE_COMMU_GNE_SWITCH at NAMARA-SEC0016_OCS @ Sceco | 10/16/2025 03:08:44 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 03:08:41 | P1 | DWDM |  | Sceco | DWDM NSA | NAMARA | FLM_EM | [5 empty] | NE NAMARA-SEC0016_OCS's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 03:10:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251016000150 | PCM-20251016-00000273 | TT-20251016-00342 | EM | [7 empty] | 10/16/2025 03:10:53 | 10/16/2025 03:10:53 | 10/16/2025 07:10:53 | NE_COMMU_GNE_SWITCH at MISLIM-SEC0015_OCS @ Sceco | 10/16/2025 03:09:03 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 03:09:01 | P1 | DWDM |  | Sceco | DWDM NSA | MISLIM | FLM_EM | [5 empty] | NE MISLIM-SEC0015_OCS's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 03:10:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251016000151 | PCM-20251016-00000274 | TT-20251016-00343 | EM | [7 empty] | 10/16/2025 03:10:55 | 10/16/2025 03:10:55 | 10/16/2025 07:10:55 | NE_COMMU_GNE_SWITCH at NAMARA-SEC0016_ELC @ Sceco | 10/16/2025 03:08:55 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 03:08:51 | P1 | DWDM |  | Sceco | DWDM NSA | NAMARA | FLM_EM | [5 empty] | NE NAMARA-SEC0016_ELC's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 03:10:55 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251016000152 | PCM-20251016-00000275 | TT-20251016-00344 | EM | [7 empty] | 10/16/2025 03:10:56 | 10/16/2025 03:10:56 | 10/16/2025 07:10:56 | NE_COMMU_GNE_SWITCH at MISLIM-SEC0015_ELC @ Sceco | 10/16/2025 03:08:54 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 03:08:51 | P1 | DWDM |  | Sceco | DWDM NSA | MISLIM | FLM_EM | [5 empty] | NE MISLIM-SEC0015_ELC's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 03:10:56 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000159 | PCM-20251016-00000292 | TT-20251008-02052 | MW_HC | Region_6 | RYAB9006 | RYAB9006 |  |  |  | Muhammad Afzal Muhammad Aslam | 10/16/2025 03:26:08 | 10/16/2025 10:05:34 | 10/16/2025 15:26:08 | Nokia MW HC_P0 Observing Performance Issue at RYAB9006_01-RYAB0644_02 VRRP | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P1 | Repeater | tathleeth | Generator_SG | TX NSA | RYAB9006_01-RYAB0644_02 VRRP | FLM_TE |  | Kindly close with RCA | PCM-20251016-00000144 | Kindly close with RCA | Kindly close with RCA |  |  |  | API | 10/16/2025 03:26:08 | 10/16/2025 10:05:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000161 | PCM-20251016-00000312 | TT-20251008-02563 | Reference_telecom | Region_6 | TLT0890 | TLT0890 |  |  |  | Muhammad Afzal Muhammad Aslam | 10/16/2025 03:26:55 | 10/16/2025 10:05:35 | 10/16/2025 15:26:55 | NEC MW Observing ODU CPU / Cable Open,LOF at TLT0890(10.89.224.4) | 09/30/2025 13:35:12 | Minor |  | LOF | 09/30/2025 13:35:12 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0890(10.89.224.4) | FLM_TE |  | kindly close with RCA | PCM-20251016-00000138 | kindly close with RCA | kindly close with RCA |  |  |  | API | 10/16/2025 03:26:55 | 10/16/2025 10:05:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000162 | PCM-20251016-00000313 | TT-20251015-01673 | Telecom | Region_5 | BIK0788 | BIK0788 |  |  |  | Hazem Ali Moustafa Ali | 10/16/2025 03:27:55 | 10/18/2025 03:16:09 | 10/16/2025 09:27:55 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at BIK0788-P3 @ Generator_SG | 10/15/2025 15:38:19 | Major | 7607 | TRX OPERATION DEGRADED | 10/15/2025 15:38:16 | P3 | 2G | makkah | Generator_SG | 2G_TRX NSA | BIK0788 | FLM_TE |  |  | PCM-20251015-00001543 | RSSI | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 03:27:55 | 10/18/2025 03:16:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000163 | PCM-20251016-00000314 | TT-20251016-00386 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 03:27:56 | 10/18/2025 14:26:55 | 10/16/2025 07:27:56 | The Device is offline at RIYB6066-CSG-01 @ Sceco | 10/16/2025 03:27:19 | Critical | 101-7 | The Device is offline | 10/16/2025 03:27:17 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/16/2025 03:27:56 | 10/18/2025 14:26:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000165 | PCM-20251016-00000324 | TT-20251013-02023 | MW_HC | Region_6 | TLT0311 | TLT0311 |  |  |  | Muhammad Afzal Muhammad Aslam | 10/16/2025 03:29:43 | 10/16/2025 10:05:36 | 10/16/2025 15:29:43 | Nokia MW HC_P1 Observing Performance Issue at TLT0311_01-TLT0743-3 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0311_01-TLT0743-3 | FLM_TE |  | Kindly close with RCA | PCM-20251016-00000130 | Kindly close with RCA | Kindly close with RCA |  |  |  | API | 10/16/2025 03:29:43 | 10/16/2025 10:05:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000177 | PCM-20251016-00000370 | TT-20251016-00444 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 03:42:55 | 10/18/2025 14:26:56 | 10/16/2025 15:42:55 | Chassis Fail at RIYB6066-CSG-01 @ Sceco | 10/16/2025 03:42:22 | Minor | 101-2505202 | Chassis Fail | 10/16/2025 03:35:45 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/16/2025 03:42:55 | 10/18/2025 14:26:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000184 | PCM-20251016-00000383 | TT-20251016-00460 | EM | Region_1 | ARR0518 | ARR0518 |  |  |  | Moustafa Mohamed Saleh Saif | 10/16/2025 03:52:14 | 10/16/2025 11:14:24 | 10/16/2025 07:52:14 | Door opening alarm at ARR0518-P1-Core-HUB-WDM_SRAN-FON @ Sceco_STB | 10/16/2025 03:52:00 | Critical | 65101 | Door opening alarm | 10/16/2025 03:51:57 | P1 | SRAN | arar | Sceco_STB | 2G NSA | ARR0518 | FLM_EM | [8 empty] | API | 10/16/2025 03:52:14 | 10/16/2025 11:14:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000186 | PCM-20251016-00000386 | TT-20251016-00448 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 03:54:42 | 10/16/2025 09:37:51 | 10/16/2025 09:54:42 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/16/2025 03:38:48 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/16/2025 03:38:38 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251016-00000373 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/16/2025 03:54:42 | 10/16/2025 09:37:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000191 | PCM-20251016-00000392 | TT-20251016-00465 | Reference_telecom | Region_5 | MAK0599 | MAK0599 |  |  |  | Atif Javed Javed Hussain | 10/16/2025 03:58:24 | 10/16/2025 11:26:13 | 10/16/2025 15:58:24 | ReplaceableUnitProblem observed in MAK0599 towards 10.10.190.51 @ Sceco | 10/15/2025 15:59:32 | Minor |  | ReplaceableUnitProblem | 10/15/2025 15:57:56 | P1 | 2G | makkah | Sceco | TX NSA | MAK0599 | FLM_TE | [8 empty] | API | 10/16/2025 03:58:24 | 10/16/2025 11:26:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000197 | PCM-20251016-00000412 | TT-20251016-00487 | EM | [7 empty] | 10/16/2025 04:12:22 | 10/16/2025 04:12:22 | 10/16/2025 08:12:22 | NE_COMMU_GNE_SWITCH at WADI9701-SEC0045_ELC @ Sceco | 10/16/2025 04:10:48 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 04:10:45 | P1 | DWDM |  | Sceco | DWDM NSA | WADI9701 | FLM_EM | [5 empty] | NE WADI9701-SEC0045_ELC's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 04:12:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251016000198 | PCM-20251016-00000413 | TT-20251016-00491 | EM | [7 empty] | 10/16/2025 04:12:54 | 10/16/2025 04:12:54 | 10/16/2025 08:12:54 | NE_COMMU_GNE_SWITCH at WADI9701-SEC0045_OCS @ Sceco | 10/16/2025 04:10:58 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/16/2025 04:10:55 | P1 | DWDM |  | Sceco | DWDM NSA | WADI9701 | FLM_EM | [5 empty] | NE WADI9701-SEC0045_OCS's current GNE has been switched to standby GNE |  |  | API | 10/16/2025 04:12:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000210 | PCM-20251016-00000427 | TT-20251016-00480 | Telecom | Region_4 | JDAP1M7940 | JDAP0940 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/16/2025 04:15:51 | 10/17/2025 17:23:32 | 10/16/2025 10:15:51 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/16/2025 03:58:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 03:58:31 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JDAP1M7940 | FLM_TE |  |  | PCM-20251016-00000405 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 04:15:51 | 10/16/2025 14:12:08 | 10/17/2025 17:23:26 |  |  | 10/17/2025 17:23:32 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251016000220 | PCM-20251016-00000449 | TT-20251016-00304 | EM | Region_5 | MAK2967 | MAK2967 |  |  |  | Sher Ali Munir | 10/16/2025 04:36:35 | 10/16/2025 05:36:17 | 10/16/2025 10:36:35 | 1(2G/5G) sites down under MAK2967-P3/MAK2967-P3 @ Generator_SG | 10/16/2025 02:42:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 02:41:59 | P3 | 2G | makkah | Generator_SG | 2G SA | MAK2967-P3 | FLM_TE | MAK2967 | Results: DOWN SITE HUB MAK2967-P3 MAK2967 Summary: Hub: MAK2967, Down Count: 1, Down Sites: MAK2967-P3 Alarm Summary: MAK2967 Alarm Active on HUB | PCM-20251016-00000315 | No Power Issue | No Power Issue |  | sites down |  | API | 10/16/2025 04:36:35 |  | 10/16/2025 05:36:07 | 10/16/2025 05:36:14 | 10/16/2025 05:36:17 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000222 | PCM-20251016-00000451 | TT-20251016-00519 | Telecom | Region_4 | JED0056 | JED0056 | Equipment | BTS_Cable | Replace GPS Cable | BARKAT ALI MAIN HILAL | 10/16/2025 04:39:13 | 10/20/2025 11:02:02 | 10/16/2025 10:39:13 | PT:: FLM Need to perform HC at JED0056 under R4 (BO Request) | 10/16/2025 04:39:02 | Major | 676767671 | Health Check-WO to TE FME | 10/16/2025 04:39:02 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED0056 | FLM_TE | [8 empty] | API | 10/16/2025 04:39:13 | 10/16/2025 10:48:47 | 10/16/2025 15:00:17 | 10/16/2025 15:00:19 | 10/16/2025 15:02:48 | 10/20/2025 11:02:02 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000226 | PCM-20251016-00000459 | TT-20251016-00527 | Reference_telecom | Region_2 | RIYA6087 | RIYA6087 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/16/2025 04:50:37 | 10/16/2025 08:35:26 | 10/16/2025 10:50:37 | RF Unit VSWR Threshold Crossed at RIYA6087-P3_SRAN @ Sceco | 10/16/2025 01:50:37 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/16/2025 01:50:25 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6087 | FLM_TE | [8 empty] | API | 10/16/2025 04:50:37 | 10/16/2025 08:35:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000245 | PCM-20251016-00000521 | TT-20251016-00577 | Telecom | Region_4 | JED1M7344 | JED0344 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/16/2025 05:27:01 | 10/16/2025 05:27:01 | 10/16/2025 11:27:01 | 1(LTE) sites down under JED0344-CA-L900-L800-SBTS @ Sceco | 10/16/2025 05:18:41 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 05:18:38 | P2 | 4G | jeddah | Sceco | LTE SA | JED0344-CA-L900-L800-SBTS | FLM_TE | JED0344 | Results: DOWN SITE HUB JED0344-CA-L900-L800-SBTS JED0344 Summary: Hub: JED0344, Down Count: 1, Down Sites: JED0344-CA-L900-L800-SBTS Alarm Summary: JED0344 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.144.20:8080] [URL:http://10.97.144.20:8080/NE3S/1.0/] | sites down |  | API | 10/16/2025 05:27:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000249 | PCM-20251016-00000526 | TT-20251016-00592 | Telecom | [7 empty] | 10/16/2025 05:30:24 | 10/16/2025 05:30:24 | 10/16/2025 09:30:24 | OSC_LOS at SALWA-SEC0017_OCS @ Sceco | 10/16/2025 05:29:48 | Critical | 1-12843 | OSC_LOS | 10/16/2025 05:29:36 | P1 | DWDM |  | Sceco | DWDM NSA | SALWA | FLM_TE | [5 empty] | 0-TO DH-JANUB-SEC0013&NJR0025(1-A)-6-G2AST4-3(RM3/TM3(TO DH-JANUB-SEC0013_OCS,TNG6WDAPXF(1-A01)-RM2/TM2))-OSC:1 |  |  | API | 10/16/2025 05:30:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000253 | PCM-20251016-00000534 | TT-20251016-00531 | Telecom | Region_4 | JED0284 | JED0284 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/16/2025 05:35:41 | 10/19/2025 09:37:59 | 10/16/2025 17:35:41 | BASE STATION ANTENNA LINE PROBLEM at JED0284-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/16/2025 04:46:19 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/16/2025 04:46:13 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0284 | FLM_TE |  |  | PCM-20251016-00000465 | FLM need to check ALD and VSWR at site. | FLM need to check ALD and VSWR at site. |  |  |  | API | 10/16/2025 05:35:41 | 10/16/2025 05:46:07 | 10/19/2025 09:37:46 |  |  | 10/19/2025 09:37:59 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000254 | PCM-20251016-00000535 | TT-20251016-00593 | Telecom | Region_4 | JED0294 | JED0294 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/16/2025 05:36:32 | 10/16/2025 12:35:45 | 10/16/2025 11:36:32 | 1(5G) sites down under JED0294-GSM-P3 @ Generator_SG | 10/16/2025 05:28:02 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 05:28:00 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5304297 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/16/2025 05:36:32 | 10/16/2025 11:45:01 | 10/16/2025 12:35:39 |  |  | 10/16/2025 12:35:45 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000258 | PCM-20251016-00000544 | TT-20251016-00605 | Reference_telecom | Region_2 | RIY2M7185 | RIY0185 | Equipment | BSS_HW_Stuck | Reset RRU | DILSHAD ALI ABDUL HAMEED | 10/16/2025 05:42:58 | 10/19/2025 12:56:47 | 10/16/2025 11:42:58 | Cell Unavailable at RIY2M7185-P2-L900-L800 | 10/16/2025 02:12:28 | Major | 29240 | Cell Unavailable | 10/16/2025 02:12:28 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7185 | FLM_TE | [8 empty] | API | 10/16/2025 05:42:58 | 10/16/2025 05:53:27 | 10/16/2025 05:53:32 | 10/16/2025 05:53:35 | 10/16/2025 06:15:32 | 10/16/2025 07:02:18 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000263 | PCM-20251016-00000559 | TT-20251016-00618 | Reference_telecom | Region_2 | RIY2M8560 | RIY2560 | Equipment | SFP_BTS | Clean SFP | WAQAR AHMED BASHIR AHMED | 10/16/2025 05:53:39 | 10/19/2025 12:56:47 | 10/16/2025 11:53:39 | Cell Unavailable at RIY2M8560-P2-L900-L800 | 10/16/2025 02:07:16 | Major | 29240 | Cell Unavailable | 10/16/2025 02:07:16 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M8560 | FLM_TE | [8 empty] | API | 10/16/2025 05:53:39 | 10/16/2025 06:01:04 | 10/16/2025 07:23:14 | 10/16/2025 07:23:16 | 10/16/2025 07:23:19 | 10/16/2025 08:04:31 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000264 | PCM-20251016-00000560 | TT-20251016-00620 | Reference_telecom | Region_6 | MTB2377 | MTB2377 |  |  |  | Manzoor Ahmed | 10/16/2025 05:54:08 | 10/16/2025 10:20:53 | 10/16/2025 17:54:08 | LossOfSignal observed in MTB2377 towards 10.221.243.154 @ Sceco | 10/15/2025 17:53:45 | Minor |  | LossOfSignal | 10/15/2025 17:53:42 | P2 | 2G | Baha | Sceco | TX NSA | MTB2377 | FLM_TE | [8 empty] | API | 10/16/2025 05:54:08 | 10/16/2025 10:20:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000265 | PCM-20251016-00000566 | TT-20251016-00627 | Telecom | [7 empty] | 10/16/2025 05:57:15 | 10/16/2025 05:57:15 | 10/16/2025 11:57:15 | LAN_LOC at MISLIM-SEC0015_OCS @ Sceco | 10/16/2025 05:56:26 | Major | 1-12926 | LAN_LOC | 10/09/2025 02:49:52 | P1 | DWDM |  | Sceco | DWDM NSA | MISLIM | FLM_TE | [5 empty] | 1-TO AL-ALAYA-SEC0011(1-B)-74-TMF2AUX-6(GE1)-COM:1 |  |  | API | 10/16/2025 05:57:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000266 | PCM-20251016-00000571 | TT-20251016-00633 | Telecom | Region_2 | RIY2866 | RIY2866 |  |  |  | Khan zeb Shah nawaz | 10/16/2025 06:00:21 | 10/16/2025 16:11:56 | 10/16/2025 18:00:21 | BBU Fan Stalled at RIY2866-P3_SRAN-PC @ Sceco | 10/16/2025 02:46:40 | Minor | 26110 | BBU Fan Stalled | 10/16/2025 02:43:57 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_TE | [8 empty] | API | 10/16/2025 06:00:21 | 10/16/2025 16:11:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000277 | PCM-20251016-00000613 | TT-20251014-00743 | Telecom | Region_4 | MLJI0204 | MLJI0204 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/16/2025 06:13:45 | 10/17/2025 18:11:19 | 10/16/2025 12:13:45 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MLJI0204-P3 @ Generator_SG | 10/14/2025 08:42:48 | Major | 7607 | TRX OPERATION DEGRADED | 10/14/2025 08:42:45 | P3 | 2G | alaith | Generator_SG | 2G_TRX NSA | MLJI0204 | FLM_TE |  | Thanks to check | PCM-20251016-00000238 | Thanks to check | Thanks to check |  |  |  | API | 10/16/2025 06:13:45 | 10/16/2025 12:08:44 | 10/17/2025 18:11:07 |  |  | 10/17/2025 18:11:19 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000279 | PCM-20251016-00000617 | TT-20251016-00677 | Reference_telecom | Region_1 | HFS2M4025 | HFS2025 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/16/2025 06:14:56 | 10/16/2025 08:21:42 | 10/16/2025 18:14:56 | RF Unit RX Channel RTWP/RSSI Too Low at HFS2M4025-P3 @ Generator_SG | 10/16/2025 03:14:30 | Minor | 26521 | RF Unit RX Channel RTWP/RSSI Too Low | 10/16/2025 03:14:26 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M4025 | FLM_TE | [8 empty] | API | 10/16/2025 06:14:56 | 10/16/2025 08:21:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000299 | PCM-20251016-00000657 | TT-20251016-00715 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/16/2025 06:45:17 | 10/17/2025 19:03:56 | 10/16/2025 18:45:17 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/16/2025 06:39:04 | Minor | 1589 | AC Overfrequency | 10/16/2025 06:39:04 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/16/2025 06:45:17 | 10/16/2025 10:59:32 | 10/17/2025 19:03:46 |  |  | 10/17/2025 19:03:56 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000327 | PCM-20251016-00000713 | TT-20251016-00762 | Telecom | Region_2 | RIYA2U6248 | RIYA6148 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 07:10:34 | 10/18/2025 14:26:56 | 10/16/2025 19:10:34 | GSM Local Cell Capability Decline at RIYA2U6248-P3 @ Sceco | 10/16/2025 02:14:44 | Minor | 28017 | GSM Local Cell Capability Decline | 10/16/2025 02:06:55 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYA2U6248 | FLM_TE | [8 empty] | API | 10/16/2025 07:10:34 | 10/18/2025 14:26:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000329 | PCM-20251016-00000715 | TT-20251016-00764 | Telecom | Region_2 | RIYA6148 | RIYA6148 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 07:11:01 | 10/18/2025 14:26:56 | 10/16/2025 19:11:01 | RF Unit Maintenance Link Failure at RIYA6148-P3_SRAN @ Sceco | 10/16/2025 02:14:11 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/16/2025 02:03:53 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6148 | FLM_TE | [8 empty] | API | 10/16/2025 07:11:01 | 10/18/2025 14:26:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000335 | PCM-20251016-00000723 | TT-20251016-00739 | Telecom | Region_2 | SRIY0020 | SRIY0020 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/16/2025 07:17:24 | 10/16/2025 07:20:55 | 10/16/2025 13:17:24 | 2(LTE) sites down under SRIY0020-P3,SRIY0021-P3 @ Sceco | 10/16/2025 06:55:59 | Major | 301 | NE Is Disconnected | 10/16/2025 06:55:55 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0021-P3 LTE,SRIY0020-P3 LTE | FLM_TE | SRIY0020 | Sites collocated Hub:- SRIY0020 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the B2B cable connections at hub site. | PCM-20251016-00000699 | Sites collocated Hub:- SRIY0020 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the B2B cable connections at hub site. | Sites collocated Hub:- SRIY0020 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the B2B cable connections at hub site. |  | sites down |  | API | 10/16/2025 07:17:24 | 10/16/2025 07:20:25 | 10/16/2025 07:20:45 |  |  | 10/16/2025 07:20:55 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000337 | PCM-20251016-00000727 | TT-20251016-00771 | Telecom | Region_4 | JED2350 | JED2350 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 07:20:56 | 10/19/2025 17:44:24 | 10/16/2025 13:20:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2350-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-FON @ Sceco | 10/16/2025 07:20:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 07:20:08 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED2350 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 07:20:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000345 | PCM-20251016-00000739 | TT-20251016-00691 | Telecom | Region_4 | JED1U6049 | JED6149 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/16/2025 07:28:25 | 10/17/2025 17:23:20 | 10/16/2025 13:28:25 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at JED1U6049-P3-CA @ Sceco | 10/16/2025 06:20:26 | Major | 7654 | CELL OPERATION DEGRADED | 10/16/2025 06:20:18 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6049 | FLM_TE |  |  | PCM-20251016-00000634 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:28:25 | 10/16/2025 14:12:09 | 10/17/2025 17:23:13 |  |  | 10/17/2025 17:23:20 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251016000350 | PCM-20251016-00000748 | TT-20251016-00780 | EM | Region_6 | AQQ2425 | AQQ2425 |  |  |  | Muhammad Raees | 10/16/2025 07:31:28 | 10/21/2025 20:21:53 | 10/16/2025 13:31:28 | 1(2G/LTE) sites down under AQQ2425-P3/AQQ2425-P3 @ Generator_SG | 10/16/2025 07:22:43 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 07:22:37 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | AQQ2425-P3 | FLM_EM | AQQ2425 | Results: DOWN SITE HUB AQQ2425-P3 AQQ2425 Summary: Hub: AQQ2425, Down Count: 1, Down Sites: AQQ2425-P3 Alarm Summary: AQQ2425 Alarm Active on HUB |  |  |  |  | sites down |  | Manual | 10/16/2025 07:31:28 | 10/21/2025 20:21:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000355 | PCM-20251016-00000755 | TT-20251009-00312 | Reference_telecom | Region_4 | JED0899 | JED0899 | Equipment | BSS_HW_Stuck | Reset System Module | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 07:33:01 | 10/19/2025 14:01:04 | 10/16/2025 19:33:01 | DemXpicLOS observed in JED0899_02 towards 10.10.146.243 @ Generator_SG | 10/08/2025 15:38:20 | Minor |  | DemXpicLOS | 10/08/2025 15:38:15 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0899 | FLM_TE |  | Approved | PCM-20251016-00000725 | Approved | Approved |  |  |  | API | 10/16/2025 07:33:01 | 10/18/2025 09:58:35 | 10/18/2025 09:58:43 | 10/18/2025 09:58:49 | 10/18/2025 10:29:06 | 10/19/2025 14:01:04 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000356 | PCM-20251016-00000760 | TT-20251016-00795 | Telecom | Region_4 | JED6008 | JED6008 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/16/2025 07:35:09 | 10/17/2025 17:23:07 | 10/16/2025 19:35:09 | Cell Capability Degraded at JED6008-DCU-P3 @ Sceco | 10/15/2025 19:18:51 | Minor | 28751 | Cell Capability Degraded | 10/15/2025 19:17:18 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/16/2025 07:35:09 | 10/16/2025 14:12:09 | 10/17/2025 17:22:56 |  |  | 10/17/2025 17:23:07 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000357 | PCM-20251016-00000761 | TT-20251016-00776 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/16/2025 07:35:37 | 10/17/2025 17:22:45 | 10/16/2025 13:35:37 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/16/2025 07:17:19 | Major | 7654 | CELL OPERATION DEGRADED | 10/16/2025 07:17:14 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251016-00000731 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:35:37 | 10/16/2025 14:12:10 | 10/17/2025 17:22:39 |  |  | 10/17/2025 17:22:45 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000360 | PCM-20251016-00000764 | TT-20251016-00574 | Reference_telecom | Region_4 | TURY0826 | TURY0826 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/16/2025 07:36:40 | 10/16/2025 18:16:54 | 10/16/2025 13:36:40 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TURY0826-P2 @ Sceco | 10/16/2025 05:03:42 | Major | 7607 | TRX OPERATION DEGRADED | 10/16/2025 05:03:38 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TURY0826 | FLM_TE |  |  | PCM-20251016-00000512 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:36:40 | 10/16/2025 12:13:39 | 10/16/2025 14:10:30 | 10/16/2025 14:11:24 | 10/16/2025 14:16:41 | 10/16/2025 18:16:54 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000365 | PCM-20251016-00000772 | TT-20251016-00188 | Telecom | Region_4 | JED2627 | JED2627 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/16/2025 07:41:43 | 10/18/2025 10:17:33 | 10/16/2025 13:41:43 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED2627-P3 @ Sceco | 10/16/2025 02:01:25 | Major | 7602 | BCF NOTIFICATION | 10/16/2025 02:01:11 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2627 | FLM_TE |  |  | PCM-20251016-00000150 | FLM need to check and perform HC at site. | FLM need to check and perform HC at site. |  |  |  | API | 10/16/2025 07:41:43 | 10/16/2025 11:45:02 | 10/18/2025 10:17:27 |  |  | 10/18/2025 10:17:33 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000368 | PCM-20251016-00000775 | TT-20251016-00436 | Telecom | Region_6 | ABBS2107 | ABBS2107 | Equipment | BSS_HW_Stuck | Reset Air Scale | Fawad Khan | 10/16/2025 07:42:55 | 10/16/2025 08:57:32 | 10/16/2025 13:42:55 | BCF NOTIFICATION (FF FF FF FF FF FF) at ABBS2107-P3 @ Sceco | 10/16/2025 03:34:29 | Major | 7602 | BCF NOTIFICATION | 10/16/2025 03:29:53 | P3 | 2G | namas | Sceco | 2G NSA | ABBS2107 | FLM_TE |  |  | PCM-20251016-00000361 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/16/2025 07:42:55 | 10/16/2025 08:53:30 | 10/16/2025 08:56:43 |  |  | 10/16/2025 08:57:32 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000371 | PCM-20251016-00000779 | TT-20251016-00808 | Reference_telecom | Region_1 | HFF2M7226 | HFF0226 | Equipment | BSS_HW_fault | Replace RRU | Shakeel Ahmad Ghulam Murtaza | 10/16/2025 07:44:33 | 10/16/2025 13:30:05 | 10/16/2025 13:44:33 | Cell Unavailable at HFF2M7226-CA-L800-L1800-F (REF:TT-20251016-00608)WA-P1-VIP @ Generator_SG | 10/16/2025 05:41:35 | Major | 29240 | Cell Unavailable | 10/16/2025 05:40:02 | P3 | 4G | hafouf | Generator_SG | LTE SA | HFF2M7226 | FLM_TE | [8 empty] | API | 10/16/2025 07:44:33 | 10/16/2025 08:21:42 | 10/16/2025 09:24:52 | 10/16/2025 09:24:56 | 10/16/2025 09:25:00 | 10/16/2025 13:30:05 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000373 | PCM-20251016-00000781 | TT-20251016-00081 | Telecom | Region_4 | FRS2020 | FRS2020 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/16/2025 07:44:51 | 10/16/2025 11:14:05 | 10/16/2025 19:44:51 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at FRS2020-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/16/2025 01:00:23 | Minor | 7114 | CELL SERVICE PROBLEM | 10/16/2025 01:00:09 | P3 | 2G | qunfuddah | Sceco | 5G_Cell SA | FRS2020 | FLM_TE |  |  | PCM-20251016-00000072 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:44:51 | 10/16/2025 11:14:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000376 | PCM-20251016-00000785 | TT-20251016-00230 | Reference_telecom | Region_4 | UKHA1M3733 | UKHA0733 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/16/2025 07:45:29 | 10/16/2025 11:29:15 | 10/16/2025 11:45:29 | WCDMA CELL OUT OF USE at UKHA1M3733-P1-HUB-USF @ Sceco | 10/16/2025 02:11:41 | Critical | 7771 | WCDMA CELL OUT OF USE | 10/16/2025 02:09:30 | P1 | 3G | adam | Sceco | 3G SA | UKHA1M3733 | FLM_TE |  |  | PCM-20251016-00000196 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/16/2025 07:45:29 | 10/16/2025 11:14:06 | 10/16/2025 11:29:09 |  |  | 10/16/2025 11:29:15 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000380 | PCM-20251016-00000789 | TT-20251016-00300 | Reference_telecom | Region_4 | UKHA1M3733 | UKHA0733 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/16/2025 07:45:53 | 10/16/2025 11:14:07 | 10/16/2025 11:45:53 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at UKHA1M3733-P1-HUB-USF @ Sceco | 10/16/2025 02:14:36 | Critical | 7771 | WCDMA CELL OUT OF USE | 10/16/2025 02:12:27 | P1 | 3G | adam | Sceco | 3G SA | UKHA1M3733 | FLM_TE |  |  | PCM-20251016-00000234 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:45:53 | 10/16/2025 11:14:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000389 | PCM-20251016-00000805 | TT-20251016-00820 | Telecom | Region_4 | JED1M8595 | JED2595 | Equipment | SFP_BTS | Replace SFP | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 07:57:47 | 10/19/2025 14:01:23 | 10/16/2025 13:57:47 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at JED1M8595-P3-CA-L800 @ Sceco | 10/16/2025 07:50:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 07:50:45 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8595 | FLM_TE |  |  | PCM-20251016-00000801 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:57:47 | 10/18/2025 11:00:02 | 10/18/2025 11:07:55 | 10/18/2025 11:07:58 | 10/18/2025 12:06:02 | 10/19/2025 14:01:23 |  | Moustafa Mahmoud Ahmed Fathelbab |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000390 | PCM-20251016-00000806 | TT-20251016-00822 | Telecom | Region_4 | JED2820 | JED2820 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 07:58:02 | 10/16/2025 09:37:52 | 10/16/2025 19:58:02 | BASE STATION ANTENNA LINE PROBLEM at JED2820-G900-CA-NR2.6-SBTS-P3 @ Generator_SG | 10/16/2025 07:49:59 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/16/2025 07:49:49 | P4 | 2G | jeddah | Generator_SG | 2G NSA | JED2820 | FLM_TE |  |  | PCM-20251016-00000803 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 07:58:02 | 10/16/2025 09:37:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000413 | PCM-20251016-00000869 | TT-20251016-00884 | EM | Region_5 | MAK0764 | MAK0764 |  |  |  | Israr Ahmed Muhammad Ghauri | 10/16/2025 08:36:32 | 10/16/2025 09:04:22 | 10/16/2025 12:36:32 | 1(2G/5G) sites down under MAK0764-P1-HRM/MAK0764-P1-HRM @ Sceco | 10/16/2025 08:28:19 | Critical | 7706 | BTS O&M LINK FAILURE | 10/16/2025 08:28:15 | VIP | 2G | makkah | Sceco | 2G SA | MAK0764-P1-HRM | FLM_TE | MAK0764 | Results: DOWN SITE HUB MAK0764-P1-HRM MAK0764 Summary: Hub: MAK0764, Down Count: 1, Down Sites: MAK0764-P1-HRM Alarm Summary: MAK0764 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/16/2025 08:36:32 | 10/16/2025 09:04:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251016000418 | PCM-20251016-00000881 | TT-20251016-00897 | Telecom | Region_4 | JED0229 | JED0229 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 08:43:12 | 10/19/2025 17:52:06 | 10/16/2025 14:43:12 | Fronthaul loop back connectivity check failure at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/16/2025 08:29:33 | Major | 61009 | Fronthaul loop back connectivity check failure | 10/16/2025 08:29:23 | P2 | 2G | jeddah | Sceco | 2G SA | JED0229 | FLM_TE |  |  | PCM-20251016-00000873 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/16/2025 08:43:12 | 10/16/2025 10:13:01 | 10/19/2025 17:50:55 | 10/19/2025 17:51:28 | 10/19/2025 17:52:06 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000426 | PCM-20251016-00000914 | TT-20251016-00927 | Reference_telecom | Region_4 | JED0922 | JED0922 |  |  |  | Mohammed Ramadan A Abu Abid | 10/16/2025 08:50:17 | 10/16/2025 09:04:58 | 10/16/2025 20:50:17 | ReplaceableUnitMissing observed in JED0922_02 towards 10.10.148.119 @ Generator_SG | 10/15/2025 20:50:59 | Minor |  | ReplaceableUnitMissing | 10/15/2025 20:49:43 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0922 | FLM_TE | [8 empty] | API | 10/16/2025 08:50:17 | 10/16/2025 09:04:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000430 | PCM-20251016-00000919 | TT-20251016-00926 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/16/2025 08:52:09 | 10/17/2025 17:22:31 | 10/16/2025 14:52:09 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/16/2025 08:42:00 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/16/2025 08:41:52 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251016-00000911 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 08:52:09 | 10/16/2025 14:12:10 | 10/17/2025 17:22:25 |  |  | 10/17/2025 17:22:31 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000437 | PCM-20251016-00000940 | TT-20251016-00799 | Reference_telecom | Region_2 | RIYB6029-CSG-01 | RIYB6029 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/16/2025 09:02:22 | 10/16/2025 09:36:00 | 10/16/2025 21:02:22 | Optical Invalid at RIYB6029-CSG-01 ¦¦ ref TT-20250927-00105 @ Sceco | 10/14/2025 03:19:27 | Minor | 101-2505224 | Optical Invalid | 10/14/2025 03:17:52 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6029-CSG-01 | FLM_TE |  |  | PCM-20251016-00000813 | Dear FLM, low power received on both int g0-4-2 , 0-4-3 carrying Sites {RIYB6065 , RIYA6116} please do HC on both also find below POM under TT approval from zain and take confirmation from access as both sites will be down int g0-4-2 BarCode=Z18041EB0 Item=34060693 Description=10300Mbs-1611nm-LC-70km(0.009mm) int g0-4-3 BarCode=Z171407B4 Item=34060689 Description=10300Mbs-1531nm-LC-70km(0.009mm) | Dear FLM, low power received on both int g0-4-2 , 0-4-3 carrying Sites {RIYB6065 , RIYA6116} please do HC on both also find below POM under TT approval from zain and take confirmation from access as both sites will be down int g0-4-2 BarCode=Z18041EB0 Item=34060693 Description=10300Mbs-1611nm-LC-70km(0.009mm) int g0-4-3 BarCode=Z171407B4 Item=34060689 Description=10300Mbs-1531nm-LC-70km(0.009mm) |  |  |  | API | 10/16/2025 09:02:22 | 10/16/2025 09:36:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000464 | PCM-20251016-00000993 | TT-20251016-00967 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/16/2025 09:27:35 | 10/17/2025 17:22:17 | 10/16/2025 15:27:35 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/16/2025 09:02:59 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/16/2025 09:02:48 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251016-00000958 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/16/2025 09:27:35 | 10/16/2025 14:12:10 | 10/17/2025 17:22:10 |  |  | 10/17/2025 17:22:17 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000480 | PCM-20251016-00001016 | TT-20251016-01049 | Telecom | Region_4 | JED2056 | JED2056 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 09:44:32 | 10/16/2025 09:44:32 | 10/16/2025 21:44:32 | BCF NOTIFICATION (01 00 00 69 00 00) at JED2056-P3 @ Sceco | 10/16/2025 09:37:17 | Minor | 7602 | BCF NOTIFICATION | 10/16/2025 09:37:02 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2056 | FLM_TE | [5 empty] | 01 00 00 69 00 00 |  |  | API | 10/16/2025 09:44:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000509 | PCM-20251016-00001061 | TT-20251016-01097 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 10:07:44 | 10/16/2025 14:40:18 | 10/16/2025 22:07:44 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/16/2025 09:59:22 | Minor | 7103 | HIGH TEMP | 10/16/2025 09:59:14 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/16/2025 10:07:44 | 10/16/2025 14:40:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000515 | PCM-20251016-00001071 | TT-20251015-02307 | Telecom | Region_2 | RIY2M8039 | RIY2039 | Equipment | BSS_HW_fault | Replace RFU | Ejaz Hussain Muhammad Sharif | 10/16/2025 10:13:03 | 10/16/2025 10:40:17 | 10/16/2025 16:13:03 | Cell Unavailable at RIY2M8039-P2-L900-L800 @ Sceco | 10/15/2025 23:26:53 | Major | 29240 | Cell Unavailable | 10/15/2025 23:25:18 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M8039 | FLM_TE |  | Approved as per your TS | PCM-20251016-00000147 | TE issue | TE issue |  |  |  | API | 10/16/2025 10:13:03 | 10/16/2025 10:21:24 | 10/16/2025 10:39:38 | 10/16/2025 10:39:41 | 10/16/2025 10:39:47 | 10/16/2025 10:40:17 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000516 | PCM-20251016-00001072 | TT-20251015-02192 | Telecom | Region_2 | RIY2039 | RIY2039 | Equipment | BSS_HW_fault | Replace RFU | Ejaz Hussain Muhammad Sharif | 10/16/2025 10:13:22 | 10/16/2025 10:39:26 | 10/16/2025 22:13:22 | RF Unit Hardware Fault at RIY2039-P2_SRAN @ Sceco | 10/15/2025 21:26:57 | Minor | 26532 | RF Unit Hardware Fault | 10/15/2025 21:25:42 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2039 | FLM_TE |  |  | PCM-20251016-00000146 | TE issue | TE issue |  |  |  | API | 10/16/2025 10:13:22 | 10/16/2025 10:13:42 | 10/16/2025 10:17:23 | 10/16/2025 10:17:26 | 10/16/2025 10:17:30 | 10/16/2025 10:39:26 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000524 | PCM-20251016-00001086 | TT-20251016-01125 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/16/2025 10:21:45 | 10/16/2025 13:12:46 | 10/16/2025 22:21:45 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/16/2025 10:12:30 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/16/2025 10:12:18 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251016-00001083 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/16/2025 10:21:45 | 10/16/2025 13:12:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000529 | PCM-20251016-00001095 | TT-20251016-01134 | EM | Region_6 | QLW1M8354 | QLW2354 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/16/2025 10:26:52 | 10/19/2025 06:13:08 | 10/16/2025 22:26:52 | HIGH TEMP at QLW1M8354-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/16/2025 10:18:31 | Minor | 7103 | HIGH TEMP | 10/16/2025 10:18:19 | P3 | 4G | Albaha | Generator_SG | LTE NSA | QLW1M8354 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/16/2025 10:26:52 | 10/19/2025 06:13:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000534 | PCM-20251016-00001102 | TT-20251009-01430 | Telecom | Region_3 | MDN3W6068 | MDN3W6068 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/16/2025 10:32:21 | 10/16/2025 15:04:37 | 10/16/2025 22:32:21 | MDN3W6068 partial Down | 10/09/2025 14:38:46 | Minor | 676767675 | Health Check-WO to TE FME | 10/09/2025 14:38:46 | P3 | WIFI | madinah | Sceco | Wifi SA | MDN3W6068 | FLM_TE |  |  | PCM-20251009-00001351 | site JED3W6071 partial down as below details and assign to FLM to check JED3W6071_1-1F-AP-14 70:db:98:b6:9d:b8 JED3W6071_1-1F-AP-15 f8:0b:cb:a1:6b:7c | site JED3W6071 partial down as below details and assign to FLM to check JED3W6071_1-1F-AP-14 70:db:98:b6:9d:b8 JED3W6071_1-1F-AP-15 f8:0b:cb:a1:6b:7c |  |  |  | API | 10/16/2025 10:32:21 | 10/16/2025 15:04:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000545 | PCM-20251016-00001126 | TT-20251016-01140 | Telecom | Region_4 | JED2979 | JED2979 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/16/2025 10:43:57 | 10/17/2025 04:54:42 | 10/16/2025 14:43:57 | 1(2G) 6(LTE) 1(5G) sites down under JED2979-P1-VIP @ Generator_SG | 10/16/2025 10:27:58 | Critical | 7706 | BTS O&M LINK FAILURE | 10/16/2025 10:27:55 | VIP | 2G | jeddah | Generator_SG | 2G_LTE_5G SA | JED2979-P1-VIP 2G_5G,SJED0040-CA-P3 LTE,SJED0046-P3 LTE,SJED0043-P3 LTE,SJED0053-P3 LTE,SJED0052-P3 LTE | FLM_EM | JED2979 | Site HUB TRM FB JED2979-P1-VIP 2G_5G JED2979 Suspecting power issue SJED0040-CA-P3 LTE JED0063 Suspecting power issue SJED0046-P3 LTE JED0063 Suspecting power issue SJED0043-P3 LTE JED0063 Suspecting power issue SJED0053-P3 LTE JED0063 Suspecting power issue SJED0052-P3 LTE JED0063 Suspecting power issue | PCM-20251016-00001107 | Site HUB TRM FB JED2979-P1-VIP 2G_5G JED2979 Suspecting power issue SJED0040-CA-P3 LTE JED0063 Suspecting power issue SJED0046-P3 LTE JED0063 Suspecting power issue SJED0043-P3 LTE JED0063 Suspecting power issue SJED0053-P3 LTE JED0063 Suspecting power issue SJED0052-P3 LTE JED0063 Suspecting power issue | Site HUB TRM FB JED2979-P1-VIP 2G_5G JED2979 Suspecting power issue SJED0040-CA-P3 LTE JED0063 Suspecting power issue SJED0046-P3 LTE JED0063 Suspecting power issue SJED0043-P3 LTE JED0063 Suspecting power issue SJED0053-P3 LTE JED0063 Suspecting power issue SJED0052-P3 LTE JED0063 Suspecting power issue |  | sites down |  | API | 10/16/2025 10:43:57 | 10/16/2025 10:57:17 | 10/17/2025 04:54:31 |  |  | 10/17/2025 04:54:42 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251016000563 | PCM-20251016-00001154 | TT-20251016-01195 | Telecom | Region_4 | JED0519 | JED0519 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/16/2025 10:52:41 | 10/19/2025 17:44:25 | 10/16/2025 16:52:41 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0519-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/16/2025 10:52:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 10:51:52 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0519 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 10:52:41 | 10/17/2025 18:03:38 | 10/17/2025 18:19:24 | 10/17/2025 18:20:28 | 10/17/2025 18:20:49 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000566 | PCM-20251016-00001163 | TT-20251016-01197 | EM | Region_4 | JDJZ2167 | JDJZ2167 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/16/2025 10:58:11 | 10/23/2025 12:57:12 | 10/16/2025 16:58:11 | 1(2G/5G) sites down under JDJZ2167-P3/JDJZ2167-P3 @ Generator_SG | 10/16/2025 10:49:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 10:49:43 | P3 | 4G | jeddah | Generator_SG | 2G SA | JDJZ2167-P3 | FLM_EM | JDJZ2167 | Results: DOWN SITE HUB JDJZ2167-P3 JDJZ2167 Summary: Hub: JDJZ2167, Down Count: 1, Down Sites: JDJZ2167-P3 Alarm Summary: JDJZ2167 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/16/2025 10:58:11 | 10/23/2025 12:57:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000569 | PCM-20251016-00001169 | TT-20251016-01216 | Telecom | Region_4 | JED1MN0326 | JED0326 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 11:02:21 | 10/16/2025 11:35:02 | 10/16/2025 17:02:21 | PT::FLM need to check Phase error exceeds the interference limit at JED1MN0326-NR2.6-P2 | 10/16/2025 11:01:41 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/16/2025 11:01:41 | P2 | 5G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1MN0326 | FLM_TE | [8 empty] | API | 10/16/2025 11:02:21 | 10/16/2025 11:35:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000570 | PCM-20251016-00001171 | TT-20251016-01218 | Telecom | Region_6 | ABH1BSCN03 | AB1 | Enviroment | Rectifier Module | Change rectifer module | Muhammad Mohsin Ali Ghazanfar Ali | 10/16/2025 11:02:32 | 10/18/2025 13:56:23 | 10/16/2025 17:02:32 | PT::minor flapping 1(2G/3G/LTE) site down at BAH2158-P3-CAP FLM need to check | 10/16/2025 11:02:20 | Major | 7115 | BASE STATION INFORMATION | 10/16/2025 11:02:23 | P1 | BSC | abha | Sceco_STB | 2G_3G_LTE_5G SA | BAH2158 | FLM_TE | [6 empty] | site down |  | API | 10/16/2025 11:02:32 | 10/16/2025 15:59:36 | 10/18/2025 13:41:25 |  |  | 10/18/2025 13:56:23 |  | Muhammad Mohsin Ali Ghazanfar Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000577 | PCM-20251016-00001184 | TT-20251016-01194 | Telecom | Region_2 | RIY0319 | RIY0319 |  |  |  | Khan zeb Shah nawaz | 10/16/2025 11:06:58 | 10/16/2025 19:58:31 | 10/16/2025 15:06:58 | 3(2G) 3(LTE) sites down under RIYA6014-P3,RIY0754-P3,RIY0175-P1-VIP/R2_RY1_HWBSC01 @ Sceco | 10/16/2025 10:49:21 | Critical | 21825 | CSL Fault | 10/16/2025 10:49:17 | VIP | SRAN | riyadh | Sceco | 2G_LTE SA | RIY0754-P3 2G_LTE,RIYA6014-P3 2G_LTE,RIY0175-P1-VIP 2G_LTE | FLM_TE | RIY0319 | Dear team , Sites HUB FB RIY0754-P3 RIY0754 suspecting power issue at hub site RIYA6014-P3 RIY0319 observing visibility down at P2 Router RIY0175-P1-VIP RIY0319 observing visibility down at P2 Router | PCM-20251016-00001161 | Dear team , Sites HUB FB RIY0754-P3 RIY0754 suspecting power issue at hub site RIYA6014-P3 RIY0319 observing visibility down at P2 Router RIY0175-P1-VIP RIY0319 observing visibility down at P2 Router | Dear team , Sites HUB FB RIY0754-P3 RIY0754 suspecting power issue at hub site RIYA6014-P3 RIY0319 observing visibility down at P2 Router RIY0175-P1-VIP RIY0319 observing visibility down at P2 Router |  | sites down |  | API | 10/16/2025 11:06:58 | 10/16/2025 16:11:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251016000579 | PCM-20251016-00001186 | TT-20251016-01226 | Telecom | [7 empty] | 10/16/2025 11:07:25 | 10/16/2025 11:07:25 | 10/16/2025 17:07:25 | PT::FLM need to check Phase error exceeds the interference limit at JED1MNC2184-NR2.6-NR3.5-P3 | 10/16/2025 11:06:59 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/16/2025 11:06:59 | P3 | 5G |  | Sceco | 2G_3G_LTE_5G NSA | JED1MNC2184-NR2.6-NR3.5-P3 | FLM_TE | [8 empty] | API | 10/16/2025 11:07:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000580 | PCM-20251016-00001187 | TT-20251016-01227 | Reference_telecom | Region_6 | NJR0234 | NJR0234 |  |  |  | Shahid Ali Roshan Ali | 10/16/2025 11:07:39 | 10/16/2025 13:18:15 | 10/16/2025 23:07:39 | Degrade observed in NJR0234 towards 10.10.155.246 @ Sceco | 10/15/2025 23:07:34 | Minor |  | Degrade | 10/15/2025 23:07:28 | P3 | 2G | najran | Sceco | TX NSA | NJR0234 | FLM_TE | [8 empty] | API | 10/16/2025 11:07:39 | 10/16/2025 13:18:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251016000613 | PCM-20251016-00001239 | TT-20251016-01279 | Telecom | Region_4 | JED0947 | JED0947 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 11:33:16 | 10/17/2025 10:34:12 | 10/16/2025 17:33:16 | PT::FLM need to perform HC at JED0947 (Bo request) | 10/16/2025 11:32:47 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/16/2025 11:32:47 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0947 | FLM_TE | [8 empty] | API | 10/16/2025 11:33:16 | 10/16/2025 12:48:37 | 10/17/2025 10:34:12 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000616 | PCM-20251016-00001243 | TT-20251016-01284 | Telecom | Region_6 | ARS0161 | ARS0161 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/16/2025 11:35:06 | 10/16/2025 14:32:57 | 10/16/2025 17:35:06 | PT::: As Per BO request need FLM to do HC in site ARS0161 /R6 | 10/16/2025 11:34:48 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/16/2025 11:34:52 | P2 | 2G | jizan | Sceco | 2G_3G_LTE_5G NSA | ARS0161 | FLM_TE | [8 empty] | API | 10/16/2025 11:35:06 | 10/16/2025 13:05:56 | 10/16/2025 13:49:02 | 10/16/2025 13:49:39 |  | 10/16/2025 14:32:57 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000632 | PCM-20251016-00001265 | TT-20251016-01308 | Telecom | Region_4 | JED0578 | JED0578 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 11:47:27 | 10/16/2025 11:47:27 | 10/16/2025 17:47:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0578-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/16/2025 11:46:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 11:46:18 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0578 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 11:47:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000639 | PCM-20251016-00001275 | TT-20251016-01341 | Telecom | Region_4 | JED1MN0196 | JED0196 | Equipment | BSS_HW_Stuck | Reset System Module | Abdullah Ahmad Mohammad Abdelsheekh | 10/16/2025 11:51:05 | 10/18/2025 18:41:36 | 10/16/2025 17:51:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0196-NR2.6 @ Sceco | 10/16/2025 11:50:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 11:49:53 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0196 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 11:51:05 | 10/18/2025 18:12:17 | 10/18/2025 18:29:59 | 10/18/2025 18:30:05 | 10/18/2025 18:30:07 | 10/18/2025 18:41:36 |  | Abdullah Ahmad Mohammad Abdelsheekh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000642 | PCM-20251016-00001277 | TT-20251016-01275 | Reference_telecom | Region_5 | SMAK0901 | SMAK0901 | Enviroment | SCECO_Failure | SCECO auto restored | Inam ullah | 10/16/2025 11:52:15 | 10/16/2025 15:13:22 | 10/16/2025 17:52:15 | 1(LTE) Site down under SMAK1S7901-USF-P3(ref. TT-20251016-00971) | 10/16/2025 09:13:48 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 09:13:48 | P3 | SRAN | makkah | Sceco | LTE SA | SMAK1S7901 | FLM_TE | SMAK0901 | Hub:SMAK0901 We are observing visibility down from our end kindly send team to check locally | PCM-20251016-00001249 | Hub:SMAK0901 We are observing visibility down from our end kindly send team to check locally | Hub:SMAK0901 We are observing visibility down from our end kindly send team to check locally |  | site down |  | API | 10/16/2025 11:52:15 | 10/16/2025 12:56:57 | 10/16/2025 12:58:57 | 10/16/2025 12:59:00 | 10/16/2025 13:42:24 | 10/16/2025 15:13:22 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000690 | PCM-20251016-00001356 | TT-20251016-01447 | Telecom | Region_4 | TAF1M7279 | TAF0279 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/16/2025 12:29:18 | 10/21/2025 17:12:36 | 10/16/2025 18:29:18 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF1M7279-G9-L18-L21-SBTS-P2 @ Sceco | 10/16/2025 12:28:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 12:28:18 | P2 | 4G | taif | Sceco | 5G_Cell SA | TAF1M7279 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 12:29:18 | 10/16/2025 21:43:32 | 10/19/2025 08:47:27 |  |  | 10/19/2025 08:47:33 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000702 | PCM-20251016-00001371 | TT-20251016-01252 | Telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/16/2025 12:34:53 | 10/16/2025 18:43:37 | 10/17/2025 00:34:53 | Remote Maintenance Link Running Data and Configuration Mismatch at RYQ0972-P3_SRAN @ Sceco | 10/16/2025 11:11:21 | Minor | 25902 | Remote Maintenance Link Running Data and Configuration Mismatch | 10/16/2025 11:10:40 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0972 | FLM_TE |  |  | PCM-20251016-00001213 | Dear FLM , Kindly need support where site is down & need to check | Dear FLM , Kindly need support where site is down & need to check |  |  |  | API | 10/16/2025 12:34:53 | 10/16/2025 18:43:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000717 | PCM-20251016-00001395 | TT-20251016-01483 | Reference_telecom | Region_2 | RIY2208 | RIY2208 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/16/2025 12:43:46 | 10/16/2025 13:10:05 | 10/17/2025 00:43:46 | RF Unit RX Channel RTWP/RSSI Unbalanced at RIY2208-P1-VIP-SRAN @ Generator_SG | 10/16/2025 09:43:18 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/16/2025 09:43:13 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2208 | FLM_TE | [8 empty] | API | 10/16/2025 12:43:46 | 10/16/2025 13:10:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000721 | PCM-20251016-00001400 | TT-20251016-01387 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/16/2025 12:45:33 | 10/20/2025 21:24:13 | 10/16/2025 18:45:33 | BASE STATION SERVICE PROBLEM (Receiving failure in Optical Interface) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/16/2025 12:04:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 12:04:12 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE |  |  | PCM-20251016-00001310 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/16/2025 12:45:33 | 10/20/2025 21:24:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000734 | PCM-20251016-00001417 | TT-20251016-01499 | EM | Region_6 | BHAB1M8011 | BHAB2011 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/16/2025 12:53:36 | 10/16/2025 14:56:43 | 10/17/2025 00:53:36 | RECTIFIER MODULE FAILURE at BHAB1M8011-CA-L800-SBTS-P3 @ Generator_SG | 10/16/2025 12:45:17 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 12:45:05 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8011 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 12:53:36 | 10/16/2025 14:56:43 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000750 | PCM-20251016-00001440 | TT-20251016-01491 | Telecom | Region_4 | KUL1M7006 | KUL0006 | Equipment | SFP_BTS | Clean SFP | Khizer Hayat | 10/16/2025 13:03:30 | 10/17/2025 12:47:26 | 10/16/2025 19:03:30 | CELL OPERATION DEGRADED (Failure in optical interface) at KUL1M7006-USF-P3 @ Sceco | 10/16/2025 12:41:10 | Major | 7654 | CELL OPERATION DEGRADED | 10/16/2025 12:40:56 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | KUL1M7006 | FLM_TE |  |  | PCM-20251016-00001435 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/16/2025 13:03:30 | 10/16/2025 13:12:46 | 10/16/2025 19:26:32 | 10/16/2025 19:26:35 | 10/16/2025 19:26:37 | 10/17/2025 12:47:26 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000761 | PCM-20251016-00001461 | TT-20251016-01547 | EM | Region_6 | TLT0719 | TLT0719 | Enviroment | SCECO_Failure | SCECO auto restored | Amir Arif Ali | 10/16/2025 13:15:54 | 10/17/2025 22:13:24 | 10/17/2025 01:15:54 | LOW FUEL at TLT0719-GSM-UMTS-P3 @ Generator_SG | 10/16/2025 13:07:47 | Minor | 7103 | LOW FUEL | 10/16/2025 13:07:42 | P3 | 2G | turaib | Generator_SG | 2G NSA | TLT0719 | FLM_EM | [5 empty] | LOW FUEL |  |  | API | 10/16/2025 13:15:54 | 10/17/2025 04:21:04 | 10/17/2025 22:12:58 | 10/17/2025 22:13:02 |  | 10/17/2025 22:13:24 |  | Amir Arif Ali |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000767 | PCM-20251016-00001470 | TT-20251016-01560 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/16/2025 13:20:58 | 10/18/2025 08:40:54 | 10/16/2025 19:20:58 | high temprature 32 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/16/2025 13:10:26 | Major | 65102 | high temprature 32 | 10/16/2025 13:10:23 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/16/2025 13:20:58 | 10/18/2025 08:40:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000807 | PCM-20251016-00001562 | TT-20251016-01649 | EM | Region_6 | TLM1M8225 | TLM2225 |  |  |  | Zia Ur Rahamn | 10/16/2025 13:58:10 | 10/16/2025 14:29:18 | 10/17/2025 01:58:10 | SHELTER DOOR OPEN at TLM1M8225-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/16/2025 13:57:46 | Minor | 7103 | SHELTER DOOR OPEN | 10/16/2025 13:57:40 | P3 | 4G | mohail | Generator_SG | LTE NSA | TLM1M8225 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/16/2025 13:58:10 | 10/16/2025 14:29:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251016000808 | PCM-20251016-00001565 | TT-20251016-01651 | Telecom | [7 empty] | 10/16/2025 13:59:12 | 10/16/2025 13:59:12 | 10/17/2025 01:59:12 | RF Unit Maintenance Link Failure at UQL2722-P3_SRAN @ Generator_SG | 10/16/2025 13:55:29 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/16/2025 13:53:46 | P3 | SRAN |  | Generator_SG | 2G NSA | UQL2722 | FLM_TE | [8 empty] | API | 10/16/2025 13:59:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000826 | PCM-20251016-00001595 | TT-20251016-01685 | Telecom | Region_4 | JED2259 | JED2259 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 14:10:35 | 10/19/2025 17:44:27 | 10/16/2025 20:10:35 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2259-G9-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/16/2025 14:09:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 14:09:22 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2259 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 14:10:35 | 10/17/2025 10:34:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000833 | PCM-20251016-00001603 | TT-20251013-02080 | MW_HC | Region_4 | JED2573 | JED2573 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 14:13:57 | 10/16/2025 14:29:21 | 10/17/2025 02:13:57 | Nokia MW HC_P2 Observing Performance Issue at JED2573_01-JED0008 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED2573_01-JED0008 | FLM_TE |  | please share related mail | PCM-20251016-00001572 | please share related mail | please share related mail |  |  |  | API | 10/16/2025 14:13:57 | 10/16/2025 14:29:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000868 | PCM-20251016-00001653 | TT-20251016-01737 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/16/2025 14:36:24 | 10/16/2025 14:58:43 | 10/17/2025 02:36:24 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/16/2025 14:29:38 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/16/2025 14:29:35 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/16/2025 14:36:24 | 10/16/2025 14:58:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000873 | PCM-20251016-00001662 | TT-20251016-01744 | EM | Region_4 | JDAP1M7940 | JDAP0940 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/16/2025 14:40:02 | 10/16/2025 15:29:02 | 10/16/2025 20:40:02 | RECTIFIER MODULE FAILURE at JDAP1M7940-CA-L800-P1-VIP-ARP-SBTS @ Sceco | 10/16/2025 14:34:27 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 14:31:29 | VIP | 4G | jeddah | Sceco | LTE NSA | JDAP1M7940 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 14:40:02 | 10/16/2025 15:29:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000876 | PCM-20251016-00001665 | TT-20251016-01750 | Telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 14:42:36 | 10/17/2025 10:34:04 | 10/17/2025 02:42:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0296-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/16/2025 14:41:45 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 14:41:33 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0296 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 14:42:36 | 10/17/2025 10:34:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000877 | PCM-20251016-00001669 | TT-20251016-01756 | EM | Region_4 | BHMF1M8137 | BHMF2137 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 14:44:09 | 10/16/2025 17:54:11 | 10/17/2025 02:44:09 | COMMERCIAL POWER FAILURE at BHMF1M8137-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/16/2025 14:36:00 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/16/2025 14:35:53 | P3 | 4G | jeddah | Generator_SG | LTE NSA | BHMF1M8137 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/16/2025 14:44:09 | 10/16/2025 17:54:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000878 | PCM-20251016-00001672 | TT-20251016-01760 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/16/2025 14:44:40 | 10/16/2025 15:24:00 | 10/17/2025 02:44:40 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/16/2025 14:36:39 | Minor | 7103 | AIRCON 1 FAILURE | 10/16/2025 14:36:35 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/16/2025 14:44:40 | 10/16/2025 15:24:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000885 | PCM-20251016-00001689 | TT-20251016-01767 | EM | Region_4 | MUMA1M8204 | MUMA2204 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 14:49:20 | 10/16/2025 17:54:12 | 10/17/2025 02:49:20 | COMMERCIAL POWER FAILURE at MUMA1M8204-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/16/2025 14:41:17 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/16/2025 14:41:09 | P3 | 4G | jeddah | Generator_SG | LTE NSA | MUMA1M8204 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/16/2025 14:49:20 | 10/16/2025 17:54:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000890 | PCM-20251016-00001693 | TT-20251016-01771 | Telecom | Region_1 | DAM0371 | DAM0371 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/16/2025 14:51:23 | 10/16/2025 14:58:44 | 10/16/2025 20:51:23 | SPAN_LOSS_EXCEED_EOL at DAM0371-OCS1 @ Sceco | 10/16/2025 14:47:19 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/16/2025 14:47:10 | P1 | SRAN | dammam | Sceco | DWDM NSA | DAM0371 | FLM_TE | [5 empty] | 0-1-C-8-F1DSFIU-1(WLINE1/WLINE2(FROM DM1))-OTS:1 |  |  | API | 10/16/2025 14:51:23 | 10/16/2025 14:58:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000910 | PCM-20251016-00001721 | TT-20251016-01800 | EM | Region_6 | TBL1M8324 | TBL2324 |  |  |  | Abdul Rauf Muhammad Aslam | 10/16/2025 15:04:48 | 10/16/2025 16:50:07 | 10/17/2025 03:04:48 | GEN SET RUNNING at TBL1M8324-G9-L8-SBTS-P3 @ Generator_DG | 10/16/2025 14:56:25 | Minor | 7103 | GEN SET RUNNING | 10/16/2025 14:56:14 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8324 | FLM_EM | [5 empty] | GEN SET RUNNING |  |  | API | 10/16/2025 15:04:48 | 10/16/2025 16:50:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000911 | PCM-20251016-00001722 | TT-20251016-01801 | Telecom | Region_1 | SAK0562 | SAK0562 | Equipment | SFP_BTS | Replace SFP | Syed Fawad Ali | 10/16/2025 15:04:48 | 10/16/2025 16:59:36 | 10/16/2025 21:04:48 | NR Cell Unavailable at SAK0562-P1-HUB_SRAN @ Sceco | 10/16/2025 14:58:11 | Major | 29841 | NR Cell Unavailable | 10/16/2025 14:56:37 | P1 | SRAN | sakaka | Sceco | 5G SA | SAK0562 | FLM_TE | [8 empty] | API | 10/16/2025 15:04:48 | 10/16/2025 16:30:27 | 10/16/2025 16:30:48 | 10/16/2025 16:30:51 | 10/16/2025 16:35:28 | 10/16/2025 16:59:36 |  | Syed Fawad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000914 | PCM-20251016-00001730 | TT-20251016-01814 | Telecom | Region_4 | JED0557 | JED0557 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/16/2025 15:10:29 | 10/19/2025 17:44:26 | 10/16/2025 21:10:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0557-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/16/2025 15:09:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 15:09:29 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0557 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 15:10:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000915 | PCM-20251016-00001736 | TT-20251016-01820 | EM | Region_3 | MDHL9054 | MDHL9054 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Sami Mohammed Jad Shahatah | 10/16/2025 15:11:22 | 10/19/2025 16:25:52 | 10/16/2025 19:11:22 | NEC MW observing INTRUDER Alarm (Input-1) at MDHL9054-MDHL0384 | 10/16/2025 15:09:08 | Critical | 383 | POWER_ALM | 10/16/2025 15:09:08 | P3 | Repeater | hail | Generator_DG | TX NSA | MDHL9054-MDHL0384 | FLM_EM | [5 empty] | NEC MW observing INTRUDER Alarm (Input-1) at MDHL9054-MDHL0384 |  |  | API | 10/16/2025 15:11:22 | 10/19/2025 16:25:30 | 10/19/2025 16:25:40 |  |  | 10/19/2025 16:25:52 |  | Sami Mohammed Jad Shahatah |  |  |  | EM | Zain |  | Running |  | OWS
Stuck | CM20251016000920 | PCM-20251016-00001747 | TT-20251016-01833 | EM | [7 empty] | 10/16/2025 15:15:39 | 10/16/2025 15:15:39 | 10/16/2025 19:15:39 | MAIN AC POWER FAILURE at SHB-SEC0018_OCS @ Sceco | 10/16/2025 15:13:49 | Critical | 1-12307 | MAIN AC POWER FAILURE | 10/16/2025 15:13:39 | P1 | DWDM |  | Sceco | DWDM NSA | SHB | FLM_EM | [5 empty] | 0-TO SWAMLA-SEC0023(1-A)-71-E1EFI-[MAIN AC POWER FAILURE]:4 |  |  | API | 10/16/2025 15:15:39 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000922 | PCM-20251016-00001751 | TT-20251016-01839 | Telecom | Region_4 | JED2629 | JED2629 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/16/2025 15:17:12 | 10/19/2025 17:44:26 | 10/16/2025 21:17:12 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2629-G9-L8-L18-L21-NR2.6-P3-SBTS-CAP @ Sceco | 10/16/2025 15:16:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 15:16:22 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2629 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 15:17:12 | 10/16/2025 16:13:34 | 10/16/2025 16:13:41 |  |  | 10/16/2025 16:13:47 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000928 | PCM-20251016-00001758 | TT-20251016-01846 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 15:22:21 | 10/19/2025 17:44:26 | 10/16/2025 21:22:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/16/2025 15:21:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 15:21:38 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 15:22:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000929 | PCM-20251016-00001759 | TT-20251016-01840 | Reference_telecom | Region_1 | DAM2M8802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/16/2025 15:22:29 | 10/16/2025 15:28:33 | 10/17/2025 03:22:29 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M8802-CA-L800-FWA-P1-VIP @ Sceco | 10/16/2025 12:17:24 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/16/2025 12:17:21 | P3 | 4G | dammam | Sceco | 2G NSA | DAM2M8802 | FLM_TE |  |  | PCM-20251016-00001752 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. - | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. - |  |  |  | API | 10/16/2025 15:22:29 | 10/16/2025 15:28:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000931 | PCM-20251016-00001763 | TT-20251016-01849 | EM | Region_4 | JED6077 | JED6077 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/16/2025 15:25:59 | 10/16/2025 17:01:25 | 10/17/2025 03:25:59 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED6077-GSM-P3 @ Sceco | 10/16/2025 15:17:41 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/16/2025 15:17:33 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6077 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/16/2025 15:25:59 | 10/16/2025 17:01:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016000935 | PCM-20251016-00001768 | TT-20251016-01857 | Telecom | Region_4 | MKJD1M9570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/16/2025 15:30:07 | 10/16/2025 18:20:55 | 10/17/2025 03:30:07 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at MKJD1M9570-P3-L800-SBTS @ Generator_DG | 10/16/2025 15:21:39 | Minor | 7115 | BASE STATION INFORMATION | 10/16/2025 15:21:31 | P2 | 4G | jeddah | Generator_DG | LTE NSA | MKJD1M9570 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/16/2025 15:30:07 | 10/16/2025 18:20:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000937 | PCM-20251016-00001772 | TT-20251016-01821 | Telecom | Region_3 | WFR2275 | WFR2275 | Enviroment | SCECO_Failure | SCECO auto restored | TAUSEEF ILYAS | 10/16/2025 15:30:11 | 10/22/2025 07:03:58 | 10/16/2025 21:30:11 | 2(2G) 2(LTE) sites down under WFR2275-P3,WFR2277-P3/R3_MD_HWBSC01 @ Generator_DG | 10/16/2025 15:08:16 | Major | 21825 | CSL Fault | 10/16/2025 15:08:13 | P3 | SRAN | madinah | Generator_SG | 2G_LTE SA | WFR2277-P3 2G_LTE,WFR2275-P3 2G_LTE | FLM_TE | WFR2275 | We cannot found on mux plan | PCM-20251016-00001748 | We cannot found on mux plan | We cannot found on mux plan |  | sites down |  | Manual | 10/16/2025 15:30:11 | 10/21/2025 12:46:18 | 10/22/2025 07:03:47 |  |  | 10/22/2025 07:03:58 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251016000952 | PCM-20251016-00001794 | TT-20251016-00663 | Telecom | Region_6 | TNM2230 | TNM2230 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/16/2025 15:41:10 | 10/17/2025 12:57:53 | 10/16/2025 21:41:10 | BCF NOTIFICATION (FF FF FF FF FF FF) at TNM2230-P3-CAP @ Sceco | 10/16/2025 05:55:48 | Major | 7602 | BCF NOTIFICATION | 10/16/2025 05:55:34 | P3 | 2G | namas | Sceco | 2G NSA | TNM2230 | FLM_TE |  |  | PCM-20251016-00001340 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/16/2025 15:41:10 | 10/17/2025 12:55:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000968 | PCM-20251016-00001828 | TT-20251016-01804 | Telecom | Region_4 | GMK1M7349 | GMK0349 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/16/2025 15:54:02 | 10/17/2025 11:57:57 | 10/16/2025 21:54:02 | BASE STATION SERVICE PROBLEM (RF Module filter input power missing) at GMK1M7349-L800-CA-P3-USF @ Sceco | 10/16/2025 15:01:48 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 15:01:41 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | GMK1M7349 | FLM_TE |  |  | PCM-20251016-00001723 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/16/2025 15:54:02 | 10/17/2025 11:57:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000971 | PCM-20251016-00001831 | TT-20251012-01982 | MW_HC | Region_1 | QTF0534 | QTF0534 |  |  |  | Meraj Husain Idd Baksh | 10/16/2025 15:54:46 | 10/16/2025 17:37:25 | 10/17/2025 03:54:46 | Huawei MW HC_P1 Observing Errors at QTF0534-DMAP0084 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | dammam | Sceco | TX NSA | QTF0534-DMAP0084 | FLM_TE | QTF0534 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251016-00001556 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/16/2025 15:54:46 | 10/16/2025 17:37:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016000980 | PCM-20251016-00001841 | TT-20251008-01790 | MW_HC | Region_1 | DAM0247 | DAM0247 |  |  |  | Meraj Husain Idd Baksh | 10/16/2025 15:57:43 | 10/16/2025 17:37:26 | 10/17/2025 03:57:43 | Huawei MW HC_P2 Observing Errors at DAM0247-DAM0239 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0247-DAM0239 | FLM_TE | DAM0247 | Dear team , Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251016-00001560 | Dear team , Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Dear team , Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/16/2025 15:57:43 | 10/16/2025 17:37:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016000985 | PCM-20251016-00001847 | TT-20251016-01927 | Reference_telecom | Region_6 | WBSH0001 | WBSH0001 | Equipment | BTS_Cable | Replace Ethernet Cable | Ansir Iqbal Muhammad Iqbal | 10/16/2025 15:59:38 | 10/19/2025 11:31:21 | 10/17/2025 03:59:38 | WBSH0001 Partial Down | 10/16/2025 15:36:17 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/16/2025 15:36:17 | P2 | WIFI | bisha | Sceco | Wifi SA | WBSH0001_1-1F-AP18 | FLM_TE | [8 empty] | API | 10/16/2025 15:59:38 | 10/16/2025 18:52:54 | 10/19/2025 11:25:26 |  |  | 10/19/2025 11:31:21 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016000990 | PCM-20251016-00001851 | TT-20251016-01930 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 16:00:05 | 10/19/2025 17:44:29 | 10/16/2025 22:00:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/16/2025 15:59:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 15:59:16 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0539 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 16:00:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001000 | PCM-20251016-00001868 | TT-20251016-01505 | Telecom | Region_6 | SMT0064 | SMT0064 | Equipment | SFP_BTS | Clean SFP | Zeshan Ali Adnan | 10/16/2025 16:08:16 | 10/16/2025 19:13:54 | 10/17/2025 04:08:16 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at SMT0064-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/16/2025 12:53:46 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 03:01:56 | P2 | 2G | jizan | Sceco | 2G NSA | SMT0064 | FLM_TE |  |  | PCM-20251016-00001467 | Please check site was down | Please check site was down |  |  |  | API | 10/16/2025 16:08:16 | 10/16/2025 18:02:24 | 10/16/2025 18:48:14 |  |  | 10/16/2025 19:13:54 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001007 | PCM-20251016-00001876 | TT-20251016-01950 | Telecom | Region_6 | TBL1M7451 | TBL0451 |  |  |  | Asad Saddiq | 10/16/2025 16:12:16 | 10/16/2025 20:45:11 | 10/16/2025 22:12:16 | PT::: As Per BO request need FLM to do HC in site TBL1M7451 /R6 | 10/16/2025 16:12:02 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/16/2025 16:12:06 | P3 | 4G | bisha | Sceco | 2G_3G_LTE_5G NSA | TBL1M7451 | FLM_TE | [8 empty] | API | 10/16/2025 16:12:16 | 10/16/2025 20:45:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001013 | PCM-20251016-00001889 | TT-20251016-01964 | Telecom | Region_2 | RIY2M7221 | RIY0221 | Equipment | BSS_HW_fault | Replace RFU | Ejaz Hussain Muhammad Sharif | 10/16/2025 16:17:59 | 10/16/2025 18:22:39 | 10/16/2025 22:17:59 | Cell Unavailable at RIY2M7221-P2-L800-L900 @ Sceco | 10/16/2025 16:14:56 | Major | 29240 | Cell Unavailable | 10/16/2025 16:13:23 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7221 | FLM_TE | [8 empty] | API | 10/16/2025 16:17:59 | 10/16/2025 16:23:13 | 10/16/2025 18:21:40 | 10/16/2025 18:21:58 | 10/16/2025 18:22:00 | 10/16/2025 18:22:39 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251016001016 | PCM-20251016-00001899 | TT-20251016-01956 | Telecom | Region_4 | JED1M8037 | JED2037 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 16:25:12 | 10/16/2025 17:43:42 | 10/17/2025 04:25:12 | BASE STATION SERVICE PROBLEM (Critical BER detected on the optical connection to Radio Module) at JED1M8037-CA-L800-P2-SBTS @ Sceco | 10/16/2025 16:09:24 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 16:09:14 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8037 | FLM_TE |  |  | PCM-20251016-00001882 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/16/2025 16:25:12 | 10/16/2025 17:02:53 | 10/16/2025 17:02:58 | 10/16/2025 17:03:00 | 10/16/2025 17:43:42 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001031 | PCM-20251016-00001926 | TT-20251016-01635 | Telecom | Region_2 | RIY0221 | RIY0221 | Equipment | BSS_HW_fault | Replace RFU | Ejaz Hussain Muhammad Sharif | 10/16/2025 16:35:14 | 10/16/2025 18:21:17 | 10/17/2025 04:35:14 | RF Unit CPRI Interface Error at RIY0221-P2_SRAN @ Sceco | 10/16/2025 13:46:55 | Minor | 26504 | RF Unit CPRI Interface Error | 10/16/2025 13:46:26 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0221 | FLM_TE |  |  | PCM-20251016-00001895 | Dears, approved based on TS done | Dears, approved based on TS done |  |  |  | API | 10/16/2025 16:35:14 | 10/16/2025 16:37:56 | 10/16/2025 17:59:59 | 10/16/2025 18:00:02 | 10/16/2025 18:00:05 | 10/16/2025 18:21:17 |  | Ejaz Hussain Muhammad Sharif |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001033 | PCM-20251016-00001928 | TT-20251016-01997 | Reference_telecom | Region_2 | RIYB6038 | RIYB6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 16:35:42 | 10/18/2025 14:26:57 | 10/16/2025 22:35:42 | RF Unit VSWR Threshold Crossed at RIYB6038-P3_SRAN @ Sceco | 10/16/2025 13:35:36 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/16/2025 13:35:23 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6038 | FLM_TE | [8 empty] | API | 10/16/2025 16:35:42 | 10/18/2025 14:26:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001035 | PCM-20251016-00001930 | TT-20251016-02000 | Telecom | Region_1 | SLW2M8996 | SLW2996 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/16/2025 16:36:22 | 10/16/2025 16:41:25 | 10/16/2025 22:36:22 | Cell Unavailable at SLW2M8996-CA-L800-P3 @ Generator_SG | 10/16/2025 16:31:45 | Major | 29240 | Cell Unavailable | 10/16/2025 16:30:10 | P3 | 4G | hafouf | Generator_SG | LTE SA | SLW2M8996 | FLM_TE | [8 empty] | API | 10/16/2025 16:36:22 | 10/16/2025 16:41:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001042 | PCM-20251016-00001944 | TT-20251016-02006 | Telecom | Region_4 | JED1U6841 | JED6141 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/16/2025 16:45:52 | 10/17/2025 17:21:36 | 10/16/2025 22:45:52 | BASE STATION FAULTY (System Module failure) at JED1U6841-P3 @ Sceco | 10/16/2025 16:32:04 | Major | 7650 | BASE STATION FAULTY | 10/16/2025 16:31:55 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6841 | FLM_TE |  |  | PCM-20251016-00001934 | SM having issue FLM need to check loclly | SM having issue FLM need to check loclly |  |  |  | API | 10/16/2025 16:45:52 | 10/17/2025 02:07:54 | 10/17/2025 17:21:29 |  |  | 10/17/2025 17:21:36 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001047 | PCM-20251016-00001953 | TT-20251016-02017 | EM | Region_4 | JZMA2413 | JZMA2413 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 16:52:01 | 10/16/2025 17:54:15 | 10/16/2025 22:52:01 | 1(2G/LTE) sites down under JZMA2413-P3-CAP/JZMA2413-P3-CAP @ Generator_SG | 10/16/2025 16:43:38 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 16:43:31 | P3 | 2G | jeddah | Generator_SG | 2G_LTE SA | JZMA2413-P3-CAP | FLM_EM | JZMA2413 | Results: DOWN SITE HUB JZMA2413-P3-CAP JZMA2413 Summary: Hub: JZMA2413, Down Count: 1, Down Sites: JZMA2413-P3-CAP Alarm Summary: JZMA2413 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/16/2025 16:52:01 | 10/16/2025 17:54:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016001048 | PCM-20251016-00001954 | TT-20251016-02028 | EM | Region_6 | BHAB1M8940 | BHAB2940 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/16/2025 16:52:14 | 10/19/2025 06:13:10 | 10/17/2025 04:52:14 | COMMERCIAL POWER FAILURE at BHAB1M8940-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/16/2025 16:44:06 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/16/2025 16:44:00 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8940 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/16/2025 16:52:14 | 10/19/2025 06:13:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251016001060 | PCM-20251016-00001972 | TT-20251016-01908 | Telecom | Region_4 | JED2015 | JED2015 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 17:03:59 | 10/20/2025 16:03:37 | 10/16/2025 23:03:59 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at JED2015-P3 @ Sceco | 10/16/2025 15:51:51 | Major | 7607 | TRX OPERATION DEGRADED | 10/12/2025 16:54:40 | P3 | 2G | jeddah | Sceco | 2G_TRX NSA | JED2015 | FLM_TE |  |  | PCM-20251016-00001826 | SA alarm active on BBMOD-3, Please perform HC on SFP, Cable connectivity & HW. | SA alarm active on BBMOD-3, Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/16/2025 17:03:59 | 10/17/2025 10:34:06 | 10/20/2025 15:37:46 | 10/20/2025 15:37:48 | 10/20/2025 16:03:37 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001063 | PCM-20251016-00001978 | TT-20251016-01907 | Telecom | Region_4 | JED6058 | JED6058 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/16/2025 17:05:40 | 10/17/2025 17:20:13 | 10/16/2025 23:05:40 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at JED6058-P3 @ Sceco | 10/16/2025 15:51:51 | Major | 7607 | TRX OPERATION DEGRADED | 10/05/2025 16:47:10 | P3 | 2G | jeddah | Sceco | 2G_TRX NSA | JED6058 | FLM_TE |  |  | PCM-20251016-00001825 | VSWR alarm active on RMOD-1 R-1,Please check ALD HW & all the connectivity from ALD To RMOD. | VSWR alarm active on RMOD-1 R-1,Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/16/2025 17:05:40 | 10/17/2025 02:07:55 | 10/17/2025 17:19:58 |  |  | 10/17/2025 17:20:13 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001065 | PCM-20251016-00001981 | TT-20251016-02048 | Telecom | Region_4 | BHR0310 | BHR0310 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 17:06:42 | 10/19/2025 17:44:29 | 10/16/2025 23:06:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/16/2025 17:05:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 17:05:38 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | BHR0310 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 17:06:42 | 10/16/2025 17:07:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001081 | PCM-20251016-00001999 | TT-20251016-02063 | Telecom | Region_4 | JED0822 | JED0822 | Equipment | SFP_BTS | Replace SFP | Nazeer Mohammed | 10/16/2025 17:16:50 | 10/18/2025 13:32:16 | 10/16/2025 23:16:50 | PT::FLM need to perform HC at JED0822 (Bo request) | 10/16/2025 17:16:36 | Major | 7604 | BASE STATION OPERATION DEGRADED | 10/16/2025 17:16:36 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED0822 | FLM_TE | [8 empty] | API | 10/16/2025 17:16:50 | 10/18/2025 10:14:49 | 10/18/2025 12:50:29 | 10/18/2025 12:50:32 | 10/18/2025 12:50:35 | 10/18/2025 13:32:16 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001088 | PCM-20251016-00002018 | TT-20251016-02066 | EM | Region_4 | TAF0312 | TAF0312 |  |  |  | Rashid Shafique | 10/16/2025 17:23:01 | 10/17/2025 11:02:32 | 10/16/2025 23:23:01 | 1(2G/3G/5G) sites down under TAF0312-P2 @ Sceco | 10/16/2025 17:14:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 17:14:53 | P2 | 2G | taif | Sceco | 5G SA | TAF0312-G9-L8-L18-L21-NR2.6-P2-SBTS | FLM_TE | TAF0312 | Results: DOWN SITE HUB TAF0312-G9-L8-L18-L21-NR2.6-P2-SBTS TAF0312 Summary: Hub: TAF0312, Down Count: 1, Down Sites: TAF0312-G9-L8-L18-L21-NR2.6-P2-SBTS Alarm Summary: TAF0312 No Active Alarm on HUB |  |  |  | No route to host [URL:http://10.98.24.172:8080/NE3S/1.0/] | sites down |  | API | 10/16/2025 17:23:01 | 10/16/2025 17:44:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001090 | PCM-20251016-00002023 | TT-20251016-02087 | EM | Region_6 | ARS0187 | ARS0187 |  |  |  | Khurram Nawaz Muhammad Akram | 10/16/2025 17:26:51 | 10/16/2025 23:38:32 | 10/17/2025 05:26:51 | RECTIFIER MAINS POWER FAILURE at ARS0187-GSM-P2 @ Sceco | 10/16/2025 17:18:41 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/16/2025 17:18:33 | P2 | 2G | jizan | Sceco | 2G NSA | ARS0187 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/16/2025 17:26:51 | 10/16/2025 23:38:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251016001107 | PCM-20251016-00002049 | TT-20251016-02106 | Telecom | [7 empty] | 10/16/2025 17:40:32 | 10/16/2025 17:40:32 | 10/16/2025 23:40:32 | 1(2G) sites down under UQL2722-P3/AR1BSCH01 @ Generator_SG | 10/16/2025 17:32:09 | Major | 21825 | CSL Fault | 10/16/2025 17:32:06 | P3 | 2G |  | Generator_SG | 2G SA | UQL2722-P3 | FLM_TE | UQL2722 | Results: DOWN SITE HUB UQL2722-P3 UQL2722 Summary: Hub: UQL2722, Down Count: 1, Down Sites: UQL2722-P3 Alarm Summary: UQL2722 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/16/2025 17:40:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001112 | PCM-20251016-00002057 | TT-20251016-02120 | Telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 17:45:27 | 10/16/2025 17:51:50 | 10/16/2025 23:45:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8061-CA-L800-SBTS @ Sceco | 10/16/2025 17:44:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 17:44:20 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8061 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 17:45:27 | 10/16/2025 17:51:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001113 | PCM-20251016-00002056 | TT-20251016-02119 | Telecom | Region_4 | JED1MN2045 | JED2045 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 17:45:27 | 10/17/2025 10:34:07 | 10/16/2025 23:45:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2045-NR2.6-P3 @ Sceco | 10/16/2025 17:44:48 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 17:44:42 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2045 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 17:45:27 | 10/17/2025 10:34:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001118 | PCM-20251016-00002062 | TT-20251016-02125 | Telecom | Region_1 | ABQ2889 | ABQ2889 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Imran Ali Yousaf | 10/16/2025 17:48:12 | 10/22/2025 12:30:20 | 10/17/2025 05:48:12 | (As per BO Request) NEC MW HC Observing PM Error and RSL degradation at link ABQ2889 DIR DMV2198 | 10/16/2025 17:45:37 | Minor | 1-631 | MW_LOF | 10/16/2025 17:45:37 | P2 | SRAN | dammam | Sceco | TX NSA | ABQ2889 DIR DMV2198 | FLM_TE | [5 empty] | (As per BO Request) NEC MW HC Observing PM Error and RSL degradation at link ABQ2889 DIR DMV2198 |  |  | API | 10/16/2025 17:48:12 | 10/22/2025 12:30:20 | [5 empty] | Imran Ali Yousaf | MW_Spare |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001119 | PCM-20251016-00002064 | TT-20251016-02117 | EM | Region_4 | MUMA2204 | MUMA2204 |  |  |  | Khizer Hayat | 10/16/2025 17:49:31 | 10/16/2025 18:53:03 | 10/16/2025 23:49:31 | 1(2G/LTE) sites down under MUMA2204-P3-CAP/MUMA2204-P3-CAP @ Generator_SG | 10/16/2025 17:41:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 17:41:01 | P3 | 2G | jeddah | Generator_SG | 2G SA | MUMA2204-P3-CAP | FLM_TE | MUMA2204 | Results: DOWN SITE HUB MUMA2204-P3-CAP MUMA2204 Summary: Hub: MUMA2204, Down Count: 1, Down Sites: MUMA2204-P3-CAP Alarm Summary: MUMA2204 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/16/2025 17:49:31 | 10/16/2025 18:53:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001127 | PCM-20251016-00002077 | TT-20251016-02136 | EM | Region_1 | R1_HF_HWBSC01 | HF1 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/16/2025 17:56:18 | 10/17/2025 17:56:19 | 10/16/2025 21:56:18 | Intruder Alarm(SH1) at R1_HF_HWBSC01 @ Sceco_STB | 10/16/2025 17:55:57 | Critical | 65334 | Intruder Alarm(SH1) | 10/16/2025 17:55:54 | P1 | BSC | hafouf | Sceco_STB | 2G NSA | R1_HF_HWBSC01 | FLM_EM | [8 empty] | API | 10/16/2025 17:56:18 | 10/17/2025 17:50:51 | 10/17/2025 17:56:12 |  |  | 10/17/2025 17:56:19 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251016001130 | PCM-20251016-00002081 | TT-20251016-02142 | Telecom | Region_4 | JED0198 | JED0198 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 18:00:27 | 10/16/2025 18:00:27 | 10/17/2025 00:00:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0198-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/16/2025 17:59:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 17:59:29 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0198 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 18:00:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001138 | PCM-20251016-00002091 | TT-20251016-02148 | EM | Region_4 | MUMA2337 | MUMA2337 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 18:07:33 | 10/17/2025 11:15:31 | 10/17/2025 00:07:33 | 1(2G/LTE) sites down under MUMA2337-P3/MUMA2337-P3 @ Sceco | 10/16/2025 17:59:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 17:59:01 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | MUMA2337-P3 | FLM_EM | MUMA2337 | Results: DOWN SITE HUB MUMA2337-P3 MUMA2337 Summary: Hub: MUMA2337, Down Count: 1, Down Sites: MUMA2337-P3 Alarm Summary: MUMA2337 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/16/2025 18:07:33 | 10/17/2025 11:15:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016001140 | PCM-20251016-00002097 | TT-20251016-02152 | Telecom | Region_4 | MUMA1M8409 | MUMA2409 |  |  |  | Khizer Hayat | 10/16/2025 18:09:31 | 10/16/2025 18:53:04 | 10/17/2025 00:09:31 | 1(LTE) sites down under MUMA2409-G9-L8-L18-SBTS-P3 @ Sceco | 10/16/2025 18:01:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 18:01:09 | P3 | 4G | jeddah | Sceco | LTE SA | MUMA2409-G9-L8-L18-SBTS-P3 | FLM_TE | MUMA2409 | Results: DOWN SITE HUB MUMA2409-G9-L8-L18-SBTS-P3 MUMA2409 Summary: Hub: MUMA2409, Down Count: 1, Down Sites: MUMA2409-G9-L8-L18-SBTS-P3 Alarm Summary: MUMA2409 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.169.93.54:8080] [URL:http://10.169.93.54:8080/NE3S/1.0/] | sites down |  | API | 10/16/2025 18:09:31 | 10/16/2025 18:53:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016001147 | PCM-20251016-00002111 | TT-20251016-02180 | EM | Region_1 | JBKH0110 | JBKH0110 |  |  |  | Ali Ahmed Ali Ahmed | 10/16/2025 18:21:36 | 10/16/2025 18:21:36 | 10/17/2025 00:21:36 | Mains Failure at JBKH0110-P1-HUB_SRAN @ Generator_SG | 10/16/2025 18:11:47 | Major | 65109 | Mains Failure | 10/16/2025 18:11:44 | P1 | SRAN | jubail | Generator_SG | 2G NSA | JBKH0110 | FLM_EM | [8 empty] | API | 10/16/2025 18:21:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016001154 | PCM-20251016-00002126 | TT-20251016-02195 | Telecom | Region_4 | USF0694 | USF0694 |  |  |  | Nazeer Mohammed | 10/16/2025 18:31:24 | 10/18/2025 10:14:50 | 10/17/2025 06:31:24 | Power Supply at USF0694 on 10.154.150.164 @ Sceco | 10/16/2025 18:30:39 | Minor | Power Supply | Power Supply | 10/16/2025 18:27:23 | P2 | 2G | jeddah | Sceco | TX NSA | USF0694 | FLM_TE | [8 empty] | API | 10/16/2025 18:31:24 | 10/18/2025 10:14:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001155 | PCM-20251016-00002127 | TT-20251016-02196 | Reference_telecom | Region_6 | MHL0137 | MHL0137 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/16/2025 18:31:40 | 10/19/2025 12:56:50 | 10/16/2025 22:31:40 | TRX OPERATION DEGRADED at MHL0137-P1-HUB@ Generator_DG | 10/16/2025 03:24:44 | Critical | 7607 | TRX OPERATION DEGRADED | 10/16/2025 03:19:54 | P1 | 2G | mohail | Generator_DG | 2G_TRX NSA | MHL0137 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/16/2025 18:31:40 | 10/16/2025 18:45:23 | 10/16/2025 23:24:07 |  |  | 10/16/2025 23:24:25 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001158 | PCM-20251016-00002131 | TT-20251016-02199 | Reference_telecom | Region_6 | MHL0122 | MHL0122 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/16/2025 18:33:23 | 10/19/2025 12:56:49 | 10/17/2025 00:33:23 | TRX OPERATION DEGRADED at MHL0122-P1-SHOP@ Sceco | 10/16/2025 03:24:41 | Major | 7607 | TRX OPERATION DEGRADED | 10/16/2025 03:19:21 | P1 | 2G | mohail | Sceco | 2G_TRX NSA | MHL0122 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/16/2025 18:33:23 | 10/16/2025 18:45:23 | 10/16/2025 23:26:03 |  |  | 10/16/2025 23:26:22 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001163 | PCM-20251016-00002136 | TT-20251016-02202 | Reference_telecom | Region_5 | MAK2967 | MAK2967 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/16/2025 18:36:33 | 10/18/2025 14:02:55 | 10/17/2025 00:36:33 | BASE STATION SERVICE PROBLEM(No connection to unit) at MAK2967-G9-L8-L18-L21-NR2.6-P3-SBTS (REF. TT-20251016-00304) | 10/16/2025 03:25:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 03:25:13 | P3 | 2G | makkah | Generator_SG | 2G_3G_LTE SA | MAK2967-G9-L8-L18-L21-NR2.6-P3-SBTS | FLM_TE | [8 empty] | API | 10/16/2025 18:36:33 | 10/18/2025 14:02:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001170 | PCM-20251016-00002147 | TT-20251016-02212 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/16/2025 18:46:25 | 10/18/2025 14:26:57 | 10/17/2025 00:46:25 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/16/2025 15:46:22 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/16/2025 15:46:10 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/16/2025 18:46:25 | 10/18/2025 14:26:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001183 | PCM-20251016-00002170 | TT-20251016-02069 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 19:13:22 | 10/17/2025 10:03:30 | 10/17/2025 07:13:22 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/16/2025 17:13:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 17:13:39 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251016-00002010 | Kindly check and perform HC at site to clear the alarm | Kindly check and perform HC at site to clear the alarm |  |  |  | API | 10/16/2025 19:13:22 | 10/17/2025 10:03:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016001186 | PCM-20251016-00002174 | TT-20251016-02132 | Reference_telecom | Region_4 | JED1MN0218 | JED0218 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 19:18:07 | 10/16/2025 19:18:07 | 10/17/2025 07:18:07 | Fronthaul loop back connectivity check failure at JED1MN0218-NR2.6-P1-VIP @ Sceco | 10/16/2025 17:23:59 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/16/2025 17:23:50 | VIP | 5G | jeddah | Sceco | 5G NSA | JED1MN0218 | FLM_TE |  |  | PCM-20251016-00002071 | Kindly check FHL alarm active at site, perform HC at site | Kindly check FHL alarm active at site, perform HC at site |  |  |  | API | 10/16/2025 19:18:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001188 | PCM-20251016-00002176 | TT-20251016-02165 | Reference_telecom | Region_4 | JED0991 | JED0991 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 19:19:14 | 10/17/2025 10:34:07 | 10/17/2025 01:19:14 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0991-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/16/2025 16:15:20 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 16:15:12 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0991 | FLM_TE |  |  | PCM-20251016-00002104 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 19:19:14 | 10/17/2025 10:34:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016001189 | PCM-20251016-00002178 | TT-20251016-02178 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 19:19:39 | 10/16/2025 19:19:39 | 10/17/2025 01:19:39 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/16/2025 18:14:06 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/16/2025 18:13:59 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251016-00002109 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/16/2025 19:19:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001191 | PCM-20251016-00002180 | TT-20251016-02193 | Reference_telecom | Region_6 | ARF0315 | ARF0315 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/16/2025 19:20:15 | 10/16/2025 21:07:03 | 10/17/2025 07:20:15 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ARF0315-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/16/2025 16:29:16 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 16:29:04 | P3 | 2G | khamis mushyet | Sceco | 2G NSA | ARF0315 | FLM_TE |  |  | PCM-20251016-00002124 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 19:20:15 | 10/16/2025 19:37:35 | 10/16/2025 19:39:10 | 10/16/2025 19:39:13 |  | 10/16/2025 21:07:03 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016001193 | PCM-20251016-00002182 | TT-20251016-02224 | Telecom | Region_4 | JED1MN2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 19:20:41 | 10/18/2025 10:32:43 | 10/17/2025 01:20:41 | BASE STATION HARDWARE PROBLEM (SFP Transceiver temperature too high) at JED1MN2979-NR2.6-P1-VIP @ Generator_SG | 10/16/2025 18:52:13 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/16/2025 18:52:04 | VIP | 5G | jeddah | Generator_SG | 5G NSA | JED1MN2979 | FLM_TE |  |  | PCM-20251016-00002158 | Please perform HC on SFP, Cable connectivity & HW. BBMOD R2- SFP-R2 & also check site EM condition. | Please perform HC on SFP, Cable connectivity & HW. BBMOD R2- SFP-R2 & also check site EM condition. |  |  |  | API | 10/16/2025 19:20:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001195 | PCM-20251016-00002184 | TT-20251016-02244 | EM | Region_6 | BLQ1M8192 | BLQ2192 |  |  |  | Muhammad Naeem Taj Din | 10/16/2025 19:21:32 | 10/17/2025 19:09:12 | 10/17/2025 07:21:32 | AIRCON 1 FAILURE at BLQ1M8192-G9-L8- L18- L21-SBTS-P3 @ Generator_SG | 10/16/2025 19:13:13 | Minor | 7103 | AIRCON 1 FAILURE | 10/16/2025 19:13:06 | P3 | 4G | namas | Generator_SG | LTE NSA | BLQ1M8192 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/16/2025 19:21:32 | 10/17/2025 19:09:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001196 | PCM-20251016-00002187 | TT-20251016-02242 | Reference_telecom | Region_6 | ARF1M7237 | ARF0237 | Equipment | SW | Issue was solved after softaware configuration | Muhammad shafiq Muhammad Rasheed | 10/16/2025 19:21:48 | 10/16/2025 21:00:51 | 10/17/2025 01:21:48 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ARF1M7237-CA-L800-P2 @ Sceco | 10/16/2025 17:19:09 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 17:19:00 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | ARF1M7237 | FLM_TE |  |  | PCM-20251016-00002177 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 19:21:48 | 10/16/2025 19:37:36 | 10/16/2025 21:00:32 | 10/16/2025 21:00:37 |  | 10/16/2025 21:00:51 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001201 | PCM-20251016-00002198 | TT-20251016-02245 | Reference_telecom | Region_5 | MAK1M9755 | MAK0755 |  |  |  | Husain Hassan Ishag Omer | 10/16/2025 19:26:49 | 10/16/2025 22:43:16 | 10/17/2025 01:26:49 | 1(LTE) Site down under MAK1M9755-P3-L1800-L800(REF. TT-20251016-02001) | 10/16/2025 16:35:48 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 16:35:48 | P3 | 4G | makkah | Sceco | 2G_3G_LTE SA | MAK1M9755-P3-L1800-L800 | FLM_TE | MAK1M9755 | Results: DOWN SITE HUB MAK1M9755-P3-L1800-L800 MAK1M9755 Summary: Hub: MAK1M9755, Down Count: 1, Down Sites: MAK1M9755-P3-L1800-L800 Alarm Summary: MAK1M9755 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/16/2025 19:26:49 | 10/16/2025 22:43:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001202 | PCM-20251016-00002200 | TT-20251016-02251 | Telecom | Region_5 | MAK0106 | MAK0106 | Equipment | BSS_HW_fault | Replace Antenna | Sher Ali Munir | 10/16/2025 19:27:13 | 10/20/2025 05:42:36 | 10/17/2025 01:27:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0106-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HAJJ-Core-HUB-WDM-HRM @ Sceco_STB | 10/16/2025 19:26:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 19:26:20 | VIP | 2G | makkah | Sceco_STB | 5G_Cell SA | MAK0106 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 19:27:13 | 10/20/2025 05:42:36 | [5 empty] | Sher Ali Munir |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001219 | PCM-20251016-00002225 | TT-20251016-02149 | Telecom | Region_4 | MUMA2204 | MUMA2204 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 19:58:00 | 10/17/2025 11:15:31 | 10/17/2025 01:58:00 | 2(2G) 2(LTE) sites down under MUMA2198-P3-CAP,MUMA2070-P3-P3/MUMA2070-P3-P3 @ Sceco | 10/16/2025 17:59:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 17:59:02 | P3 | 2G | jeddah | Generator_SG | 2G SA | MUMA2070-P3-P3 2G,MUMA2198-P3-CAP 2G | FLM_EM | MUMA2204 | Hub: MUMA2204 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251016-00002211 | Hub: MUMA2204 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: MUMA2204 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/16/2025 19:58:00 | 10/17/2025 11:15:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016001227 | PCM-20251016-00002243 | TT-20251016-02310 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 20:25:05 | 10/19/2025 17:44:29 | 10/17/2025 02:25:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/16/2025 20:24:11 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 20:24:04 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 20:25:05 | 10/17/2025 10:03:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016001228 | PCM-20251016-00002245 | TT-20251016-02312 | Telecom | Region_4 | JED0276 | JED0276 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/16/2025 20:26:09 | 10/16/2025 20:26:09 | 10/17/2025 02:26:09 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0276-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB-WDM-FON @ Sceco | 10/16/2025 20:25:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 20:25:22 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0276 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 20:26:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001241 | PCM-20251016-00002264 | TT-20251016-02299 | Reference_telecom | Region_6 | ABBS1M7166 | ABBS0166 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/16/2025 20:49:32 | 10/17/2025 00:44:02 | 10/17/2025 08:49:32 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABBS1M7166-NL800-P2-SBTS @ Sceco | 10/16/2025 18:26:25 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 18:17:34 | P3 | 4G | namas | Sceco | LTE NSA | ABBS1M7166 | FLM_TE |  |  | PCM-20251016-00002236 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 20:49:32 | 10/16/2025 21:14:25 | 10/17/2025 00:43:34 |  |  | 10/17/2025 00:44:02 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001242 | PCM-20251016-00002265 | TT-20251016-02298 | Reference_telecom | Region_6 | THR1M7181 | THR0181 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/16/2025 20:49:38 | 10/16/2025 21:44:24 | 10/17/2025 08:49:38 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at THR1M7181-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/16/2025 18:26:21 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 18:17:20 | P3 | 4G | makhwa | Sceco | LTE NSA | THR1M7181 | FLM_TE |  |  | PCM-20251016-00002235 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 20:49:38 | 10/16/2025 20:54:21 | 10/16/2025 21:44:14 |  |  | 10/16/2025 21:44:24 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001243 | PCM-20251016-00002266 | TT-20251016-02297 | Reference_telecom | Region_6 | BHAB1M8015 | BHAB2015 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/16/2025 20:49:45 | 10/16/2025 21:02:01 | 10/17/2025 08:49:45 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHAB1M8015-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/16/2025 18:27:01 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 18:17:11 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8015 | FLM_TE |  |  | PCM-20251016-00002234 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 20:49:45 | 10/16/2025 21:00:58 | 10/16/2025 21:01:46 |  |  | 10/16/2025 21:02:01 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001244 | PCM-20251016-00002267 | TT-20251016-02293 | Reference_telecom | Region_6 | DAR1MT0023 | DAR0023 | Equipment | BSS_HW_Stuck | Reset Air Scale | Muhammad Ali | 10/16/2025 20:49:51 | 10/16/2025 21:11:05 | 10/17/2025 00:49:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at DAR1MT0023-P1-DIA @ Generator_SG | 10/16/2025 18:54:40 | Critical | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 18:08:13 | P1 | 4G | dair | Generator_SG | LTE NSA | DAR1MT0023 | FLM_TE |  |  | PCM-20251016-00002230 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 20:49:51 | 10/16/2025 21:10:27 | 10/16/2025 21:10:48 |  |  | 10/16/2025 21:11:05 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001254 | PCM-20251016-00002278 | TT-20251016-02340 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 20:56:01 | 10/17/2025 10:34:08 | 10/17/2025 02:56:01 | 1(5G) sites down under JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/16/2025 20:47:42 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/16/2025 20:47:39 | P3 | 2G | jeddah | Sceco | 5G SA | JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP | FLM_TE | JED2279 | Results: DOWN SITE HUB JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP JED2279 Summary: Hub: JED2279, Down Count: 1, Down Sites: JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP Alarm Summary: JED2279 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.148.204.204:8080] [URL:http://10.148.204.204:8080/NE3S/1.0/] | sites down |  | API | 10/16/2025 20:56:01 | 10/17/2025 10:34:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001264 | PCM-20251016-00002296 | TT-20251016-02366 | Telecom | Region_4 | JED2480 | JED2480 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/16/2025 21:05:23 | 10/19/2025 17:44:30 | 10/17/2025 03:05:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2480-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/16/2025 21:04:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 21:04:27 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2480 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 21:05:23 | 10/18/2025 10:14:50 | 10/18/2025 10:18:12 |  |  | 10/18/2025 10:18:19 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001266 | PCM-20251016-00002299 | TT-20251016-02359 | Telecom | Region_1 | SMN2M1850 | SMN0850 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/16/2025 21:06:03 | 10/16/2025 21:27:30 | 10/17/2025 03:06:03 | 1(2G) sites down under SMN0850-P2-USF/HB1BSCH01 @ Generator_DG | 10/16/2025 20:57:52 | Major | 21825 | CSL Fault | 10/16/2025 20:57:46 | P2 | 2G | hafr | Generator_DG | 2G SA | SMN0850-P2-USF | FLM_TE | SMN0850 | Results: DOWN SITE HUB SMN0850-P2-USF SMN0850 Summary: Hub: SMN0850, Down Count: 1, Down Sites: SMN0850-P2-USF Alarm Summary: SMN0850 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/16/2025 21:06:03 | 10/16/2025 21:27:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251016001271 | PCM-20251016-00002307 | TT-20251016-02374 | Telecom | Region_4 | JED1M8243 | JED2243 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/16/2025 21:11:05 | 10/19/2025 17:44:30 | 10/17/2025 03:11:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8243-L800-CA-SBTS-P3 @ Sceco | 10/16/2025 21:10:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 21:10:12 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8243 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 21:11:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001282 | PCM-20251016-00002332 | TT-20251016-02401 | Telecom | Region_4 | JED0271 | JED0271 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/16/2025 21:29:39 | 10/19/2025 17:44:32 | 10/17/2025 03:29:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/16/2025 21:28:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 21:28:53 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 21:29:39 | 10/17/2025 10:49:29 | 10/19/2025 09:38:52 |  |  | 10/19/2025 09:39:09 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001316 | PCM-20251016-00002387 | TT-20251016-02350 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/16/2025 22:40:29 | 10/19/2025 17:44:50 | 10/17/2025 04:40:29 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/16/2025 20:52:31 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 20:52:26 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2279 | FLM_TE |  |  | PCM-20251016-00002280 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/16/2025 22:40:29 | 10/17/2025 10:34:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001319 | PCM-20251016-00002391 | TT-20251016-02361 | Telecom | Region_4 | RAB0366 | RAB0366 |  |  |  | Khizer Hayat | 10/16/2025 22:41:57 | 10/17/2025 11:11:08 | 10/17/2025 10:41:57 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3 @ Sceco | 10/16/2025 20:57:34 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 20:57:30 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0366 | FLM_TE |  |  | PCM-20251016-00002290 | Please perform HC on SFP, Cable connectivity & HW. as RMOD_R-14 has 15 RX degraded pipe(s) | Please perform HC on SFP, Cable connectivity & HW. as RMOD_R-14 has 15 RX degraded pipe(s) |  |  |  | API | 10/16/2025 22:41:57 | 10/17/2025 11:11:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001325 | PCM-20251016-00002399 | TT-20251016-02465 | Telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/16/2025 22:45:52 | 10/17/2025 18:52:29 | 10/17/2025 10:45:52 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/16/2025 22:21:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 22:20:49 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251016-00002380 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/16/2025 22:45:52 | 10/17/2025 18:52:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001329 | PCM-20251016-00002405 | TT-20251016-01994 | Telecom | Region_5 | MAK0626 | MAK0626 |  |  |  | Mosab Nasr eldeen Mohamed | 10/16/2025 22:52:27 | 10/17/2025 17:58:35 | 10/17/2025 04:52:27 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MAK0626-P2 @ Sceco | 10/16/2025 16:29:54 | Major | 7607 | TRX OPERATION DEGRADED | 10/16/2025 16:29:48 | P2 | 2G | makkah | Sceco | 2G_TRX NSA | MAK0626 | FLM_TE |  |  | PCM-20251016-00001924 | Site down observed in problematic time Please close TT with restoration RC. | Site down observed in problematic time Please close TT with restoration RC. |  |  |  | API | 10/16/2025 22:52:27 | 10/17/2025 17:58:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001339 | PCM-20251016-00002425 | TT-20251016-02468 | Reference_telecom | Region_6 | NJR0018 | NJR0018 | Transsmission | MW_HW_fault | Remade Power Connector | Shahid Ali Roshan Ali | 10/16/2025 23:03:38 | 10/17/2025 02:51:48 | 10/17/2025 11:03:38 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0018-G9-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/16/2025 20:32:28 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 20:32:16 | P2 | 2G | najran | Sceco | 2G NSA | NJR0018 | FLM_TE |  |  | PCM-20251016-00002382 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/16/2025 23:03:38 | 10/17/2025 00:17:08 | 10/17/2025 02:51:18 |  |  | 10/17/2025 02:51:48 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001342 | PCM-20251016-00002428 | TT-20251016-02502 | Telecom | Region_4 | BHMF2143 | BHMF2143 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 23:07:33 | 10/17/2025 11:15:33 | 10/17/2025 05:07:33 | 2(2G) 2(LTE) sites down under BHMF2143-P3,BHMF2373-P3 | 10/16/2025 22:59:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 22:59:06 | P3 | 2G | jeddah | Generator_SG | 2G_LTE SA | BHMF2143-P3 | FLM_EM | BHMF2143 | Results: DOWN SITE HUB BHMF2143-P3 BHMF2143 Summary: Hub: BHMF2143, Down Count: 1, Down Sites: BHMF2143-P3 Alarm Summary: BHMF2143 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/16/2025 23:07:33 | 10/17/2025 11:15:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251016001358 | PCM-20251016-00002459 | TT-20251016-02546 | Telecom | Region_4 | JED0600 | JED0600 |  |  |  | MALIK ATIF ZAMAN | 10/16/2025 23:35:40 | 10/17/2025 10:03:32 | 10/17/2025 05:35:40 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0600-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/16/2025 23:34:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 23:34:26 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0600 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/16/2025 23:35:40 | 10/17/2025 10:03:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251016001359 | PCM-20251016-00002460 | TT-20251016-01906 | Telecom | Region_4 | JDJZ0870 | JDJZ0870 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/16/2025 23:35:48 | 10/17/2025 11:57:59 | 10/17/2025 05:35:48 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at JDJZ0870-P3 @ Sceco | 10/16/2025 15:51:51 | Major | 7607 | TRX OPERATION DEGRADED | 10/16/2025 15:10:52 | P3 | 2G | qunfuddah | Sceco | 2G_TRX NSA | JDJZ0870 | FLM_TE |  |  | PCM-20251016-00001824 | GPs unit in locked state & sly visibility is poor, also site have sync issue. Request to check GPS HW & sky visibility status & confirm. | GPs unit in locked state & sly visibility is poor, also site have sync issue. Request to check GPS HW & sky visibility status & confirm. |  |  |  | API | 10/16/2025 23:35:48 | 10/17/2025 11:57:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001365 | PCM-20251016-00002470 | TT-20251016-02501 | Reference_telecom | Region_6 | NJR0014 | NJR0014 | Transsmission | MW_HW_fault | Remade Power Connector | Shahid Ali Roshan Ali | 10/16/2025 23:51:37 | 10/17/2025 02:50:55 | 10/17/2025 11:51:37 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NJR0014-G9-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/16/2025 21:02:04 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 21:02:00 | P2 | 2G | najran | Sceco | 2G NSA | NJR0014 | FLM_TE |  |  | PCM-20251016-00002421 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 23:51:37 | 10/17/2025 00:17:08 | 10/17/2025 02:50:22 |  |  | 10/17/2025 02:50:55 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001366 | PCM-20251016-00002471 | TT-20251016-02130 | Reference_telecom | Region_6 | SAB1M8078 | SAB2078 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/16/2025 23:51:45 | 10/17/2025 02:43:29 | 10/17/2025 05:51:45 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SAB1M8078-L800-CA-P3 @ Sceco | 10/16/2025 15:53:53 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/16/2025 15:53:43 | P3 | 4G | baish | Sceco | LTE NSA | SAB1M8078 | FLM_TE |  |  | PCM-20251016-00002434 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/16/2025 23:51:45 | 10/17/2025 02:42:07 | 10/17/2025 02:43:05 |  |  | 10/17/2025 02:43:29 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251016001367 | PCM-20251016-00002472 | TT-20251016-02558 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/16/2025 23:52:03 | 10/17/2025 17:18:19 | 10/17/2025 03:52:03 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/16/2025 23:37:31 | Critical | 7654 | CELL OPERATION DEGRADED | 10/16/2025 23:37:27 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251016-00002466 | Check the VSWR alarm at site | Check the VSWR alarm at site |  |  |  | API | 10/16/2025 23:52:03 | 10/17/2025 02:07:55 | 10/17/2025 17:18:11 |  |  | 10/17/2025 17:18:19 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000001 | PCM-20251017-00000001 | TT-20251017-00001 | Telecom | Region_4 | JED2179 | JED2179 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 00:01:30 | 10/19/2025 17:44:33 | 10/17/2025 06:01:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2179-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/17/2025 00:00:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 00:00:36 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2179 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 00:01:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000005 | PCM-20251017-00000008 | TT-20251016-02491 | EM | Region_4 | JED0495 | JED0495 | Transsmission | MW_HW_stuck | Reset Service Interface Board | Khaled Mohammad Abdallah | 10/17/2025 00:08:23 | 10/18/2025 23:04:54 | 10/17/2025 06:08:23 | 1(2G/5G) sites down under JED0495-P3/JED0495-P3 @ Sceco | 10/16/2025 22:50:41 | Major | 7706 | BTS O&M LINK FAILURE | 10/16/2025 22:50:37 | P3 | 2G | jeddah | Sceco | 2G SA | JED0495-P3 | FLM_TE | JED0495 | Results: DOWN SITE HUB JED0495-P3 JED0495 Summary: Hub: JED0495, Down Count: 1, Down Sites: JED0495-P3 Alarm Summary: JED0495 Alarm Active on HUB | PCM-20251016-00002415 | NO power issue /TE checking | NO power issue /TE checking |  | sites down |  | API | 10/17/2025 00:08:23 |  | 10/17/2025 01:14:50 | 10/17/2025 01:14:52 | 10/17/2025 01:14:54 | 10/18/2025 23:04:54 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000007 | PCM-20251017-00000011 | TT-20251017-00011 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 00:09:46 | 10/17/2025 00:09:46 | 10/17/2025 06:09:46 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/17/2025 00:08:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 00:08:31 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 00:09:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251017000008 | PCM-20251017-00000013 | TT-20251016-02060 | Telecom | Region_2 | RIY0201 | RIY0201 |  |  |  | Asad Ali Nadiq Khan | 10/17/2025 00:11:38 | 10/23/2025 16:30:21 | 10/17/2025 04:11:38 | SCECO :: LINK FLAPPED AND AUTO RESTORED B/W RIY0201--RIY0010 | 10/16/2025 17:15:02 | Critical | 1-14579 | POWER_JITTER | 10/16/2025 17:14:51 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0201 | FLM_TE |  |  | PCM-20251016-00002060 | link flapped between RIY0201--RIY0010 and auto restored , link now stable UP | link flapped between RIY0201--RIY0010 and auto restored , link now stable UP |  |  |  | API | 10/17/2025 00:11:38 | 10/17/2025 12:38:53 | 10/23/2025 16:30:21 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000015 | PCM-20251017-00000025 | TT-20251017-00025 | Telecom | Region_4 | JED1W6081 | JED6081 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohamed Farag Abdelbary | 10/17/2025 00:28:12 | 10/17/2025 17:17:38 | 10/17/2025 12:28:12 | JED1W6081 is partial down | 10/17/2025 00:21:52 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/17/2025 00:21:52 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_3-6F-AP04 | FLM_TE | [8 empty] | API | 10/17/2025 00:28:12 | 10/17/2025 02:07:56 | 10/17/2025 17:17:30 |  |  | 10/17/2025 17:17:38 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000023 | PCM-20251017-00000037 | TT-20251017-00037 | Telecom | Region_4 | JED1MN0014 | JED0014 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 00:36:07 | 10/17/2025 00:36:07 | 10/17/2025 06:36:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0014-NR2.6-P2 @ Sceco | 10/17/2025 00:35:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 00:34:59 | P1 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0014 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 00:36:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000026 | PCM-20251017-00000043 | TT-20251017-00044 | EM | Region_6 | TBL1M8297 | TBL2297 |  |  |  | Abdul Rauf Muhammad Aslam | 10/17/2025 00:43:21 | 10/22/2025 12:00:47 | 10/17/2025 12:43:21 | RECTIFIER MODULE FAILURE at TBL1M8297-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/17/2025 00:34:58 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/17/2025 00:34:51 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M8297 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | Manual | 10/17/2025 00:43:21 | 10/22/2025 12:00:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251017000033 | PCM-20251017-00000053 | TT-20251017-00052 | EM | [7 empty] | 10/17/2025 00:49:02 | 10/17/2025 00:49:02 | 10/17/2025 12:49:02 | SHELTER DOOR OPEN at MUMA1M8070-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/17/2025 00:48:45 | Minor | 7103 | SHELTER DOOR OPEN | 10/16/2025 19:32:33 | P3 | 4G |  | Sceco | LTE NSA | MUMA1M8070 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/17/2025 00:49:02 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000034 | PCM-20251017-00000054 | TT-20251017-00053 | Telecom | Region_4 | JED0109 | JED0109 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/17/2025 00:50:05 | 10/21/2025 17:12:37 | 10/17/2025 06:50:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/17/2025 00:49:06 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 00:48:57 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 00:50:05 | 10/17/2025 10:49:29 | 10/19/2025 09:39:20 |  |  | 10/19/2025 09:39:40 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000048 | PCM-20251017-00000079 | TT-20251017-00078 | Telecom | Region_4 | JED1M8066 | JED2066 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/17/2025 01:13:19 | 10/19/2025 17:44:34 | 10/17/2025 07:13:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8066-CA-L800-SBTS-P3 @ Generator_SG | 10/17/2025 01:12:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 01:12:18 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 01:13:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000059 | PCM-20251017-00000104 | TT-20251016-02514 | Reference_telecom | Region_2 | RIYB2U6786 | RIYB6086 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/17/2025 01:34:09 | 10/17/2025 11:39:17 | 10/17/2025 13:34:09 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6786-L1800-CA-P3 @ Sceco | 10/16/2025 20:15:21 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/16/2025 20:15:17 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6786 | FLM_TE |  |  | PCM-20251016-00002433 | Dear FLM, For Cell Rx Channel interference noise power unbalance, please need physical HC to verify below. 1-Jumpers. 2-Connectors. 3-Antenna & RRU ports for damage. 4-Change antenna port if any free port available. 5-Remake connectors. | Dear FLM, For Cell Rx Channel interference noise power unbalance, please need physical HC to verify below. 1-Jumpers. 2-Connectors. 3-Antenna & RRU ports for damage. 4-Change antenna port if any free port available. 5-Remake connectors. |  |  |  | API | 10/17/2025 01:34:09 | 10/17/2025 11:39:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000068 | PCM-20251017-00000116 | TT-20251017-00088 | EM | Region_2 | RIY2925 | RIY2925 |  |  |  | Farmanullah Akbar Jan | 10/17/2025 01:53:09 | 10/17/2025 08:43:49 | 10/17/2025 07:53:09 | 1(2G/LTE) sites down under RIY2989-P3 @ Generator_SG | 10/17/2025 01:19:53 | Major | 301 | NE Is Disconnected | 10/17/2025 01:19:50 | VIP | SRAN | al kharj | Generator_DG | LTE SA | RIY2989-P3_SRAN | FLM_TE | RIY2925 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | PCM-20251017-00000100 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/17/2025 01:53:09 | 10/17/2025 08:43:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000070 | PCM-20251017-00000119 | TT-20251017-00023 | Telecom | Region_2 | RIY2925 | RIY2925 |  |  |  | Farmanullah Akbar Jan | 10/17/2025 01:54:19 | 10/17/2025 08:43:51 | 10/17/2025 05:54:19 | 1(LTE) sites down under RIY2797-P1-CA-L800 @ Generator_SG | 10/17/2025 00:23:51 | Critical | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/17/2025 00:22:18 | VIP | SRAN | al kharj | Generator_DG | LTE SA | RIY2797-P1-CA-L800 | FLM_TE | RIY2925 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | PCM-20251017-00000101 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/17/2025 01:54:19 | 10/17/2025 08:43:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000071 | PCM-20251017-00000120 | TT-20251017-00114 | Reference_telecom | Region_6 | ABDB0841 | ABDB0841 |  |  |  | Muhammad Usman Muhammad Zia ul haq | 10/17/2025 01:54:38 | 10/17/2025 04:29:43 | 10/17/2025 13:54:38 | DemFail observed in ABDB0841 towards 10.10.180.135 @ Generator_SG | 10/16/2025 13:55:28 | Minor |  | DemFail | 10/16/2025 13:54:08 | P3 | 2G | derb | Generator_SG | TX NSA | ABDB0841 | FLM_TE | [8 empty] | API | 10/17/2025 01:54:38 | 10/17/2025 04:29:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000072 | PCM-20251017-00000121 | TT-20251017-00046 | Telecom | Region_2 | RIY2925 | RIY2925 |  |  |  | Farmanullah Akbar Jan | 10/17/2025 01:55:07 | 10/17/2025 08:43:53 | 10/17/2025 05:55:07 | 1(LTE) sites down under RIY2925-P1-VIP-L800-L900 @ Generator_DG | 10/17/2025 00:43:12 | Critical | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/17/2025 00:42:50 | VIP | SRAN | al kharj | Generator_DG | LTE SA | RIY2925-P1-VIP-L800-L900 | FLM_TE | RIY2925 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | PCM-20251017-00000102 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/17/2025 01:55:07 | 10/17/2025 08:43:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000074 | PCM-20251017-00000126 | TT-20251017-00051 | EM | Region_2 | RIY2925 | RIY2925 |  |  |  | Farmanullah Akbar Jan | 10/17/2025 01:55:52 | 10/17/2025 08:43:54 | 10/17/2025 07:55:52 | 1(2G/LTE) sites down under RIY2951-P3 @ Sceco | 10/17/2025 00:45:36 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/17/2025 00:44:34 | VIP | SRAN | al kharj | Generator_DG | LTE SA | RIY2951-L800-CA-P3 | FLM_TE | RIY2925 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | PCM-20251017-00000103 | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . | We are observing PM Error and RSL degradation at link : RIY2925 DIR RYDM0659,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/17/2025 01:55:52 | 10/17/2025 08:43:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000075 | PCM-20251017-00000127 | TT-20251017-00117 | EM | Region_2 | U2000 | RY1 |  |  |  | Farhat Saeed Pirzada | 10/17/2025 01:56:12 | 10/17/2025 01:56:12 | 10/17/2025 13:56:12 | Hardware Information Not Registered at U2000 NFV @ Sceco_STB | 10/17/2025 01:48:45 | Minor | 51101 | Hardware Information Not Registered | 10/17/2025 01:48:41 | P1 | Performance | riyadh | Sceco_STB | 2G NSA | U2000 | FLM_EM | [8 empty] | API | 10/17/2025 01:56:12 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251017000085 | PCM-20251017-00000157 | TT-20251017-00146 | Reference_telecom | Region_4 | JED2144 | JED2144 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 02:26:41 | 10/17/2025 02:26:41 | 10/17/2025 14:26:41 | ReplaceableUnitProblem observed in JED2144 towards 10.10.185.194 @ Sceco | 10/16/2025 14:26:51 | Minor |  | ReplaceableUnitProblem | 10/16/2025 14:26:23 | P3 | 2G | jeddah | Sceco | TX NSA | JED2144 | FLM_TE | [8 empty] | API | 10/17/2025 02:26:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000098 | PCM-20251017-00000189 | TT-20251017-00180 | Telecom | Region_4 | JED2983 | JED2983 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/17/2025 02:46:20 | 10/17/2025 18:52:29 | 10/17/2025 08:46:20 | BASE STATION SERVICE PROBLEM (RX out of order) at JED2983-G9-L8-L18-L21-NR2.6-P3 @ Generator_SG | 10/17/2025 02:41:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 02:41:30 | P3 | 2G | jeddah | Generator_SG | LTE_Cell SA | JED2983 | FLM_TE | [5 empty] | RX out of order |  |  | API | 10/17/2025 02:46:20 | 10/17/2025 18:52:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000100 | PCM-20251017-00000192 | TT-20251017-00172 | Reference_telecom | Region_2 | KHJ2M8304 | KHJ2304 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hakim Ullah Raif Ullah Jan | 10/17/2025 02:54:33 | 10/17/2025 09:31:37 | 10/17/2025 14:54:33 | Cell RX Channel Interference Noise Power Unbalanced at KHJ2M8304-P3-CA-L800 @ Sceco | 10/16/2025 23:39:00 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/16/2025 23:38:57 | P3 | 4G | riyadh | Sceco | 2G NSA | KHJ2M8304 | FLM_TE |  | Dears Kindly check HW | PCM-20251017-00000179 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/17/2025 02:54:33 | 10/17/2025 09:30:33 | 10/17/2025 09:30:59 |  |  | 10/17/2025 09:31:37 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000108 | PCM-20251017-00000213 | TT-20251017-00201 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/17/2025 03:16:17 | 10/17/2025 03:16:17 | 10/17/2025 09:16:17 | Observing BGP Status Changed On RIY1-PE-02 Connected to MOI-LIG-CE6851-48S6Q-HI-01 | 10/17/2025 03:06:55 | Major | 1100476 | BGP Status Changed | 10/17/2025 03:06:55 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | Observing BGP Status Changed On RIY1-PE-02 Connected to MOI-LIG-CE6851-48S6Q-HI-01 | FLM_TE | [5 empty] | Observing BGP Status Changed On RIY1-PE-02 Connected to MOI-LIG-CE6851-48S6Q-HI-01 |  |  | API | 10/17/2025 03:16:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000112 | PCM-20251017-00000217 | TT-20251017-00189 | Reference_telecom | Region_2 | RIYA2U6868 | RIYA6168 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/17/2025 03:19:20 | 10/17/2025 11:39:17 | 10/17/2025 15:19:20 | Cell RX Channel Interference Noise Power Unbalanced at RIYA2U6868-P1-CA-VIP @ Sceco | 10/17/2025 00:01:26 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/17/2025 00:01:23 | VIP | 4G | riyadh | Sceco | 2G NSA | RIYA2U6868 | FLM_TE |  | Dears Kindly check HW | PCM-20251017-00000200 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/17/2025 03:19:20 | 10/17/2025 11:39:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000133 | PCM-20251017-00000257 | TT-20251017-00183 | Telecom | Region_1 | KRS0885 | KRS0885 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/17/2025 03:55:41 | 10/23/2025 17:18:47 | 10/17/2025 09:55:41 | 3(2G) 3(3G) 3(LTE) sites down under KRS0885,KRS0888-P3-USF,YBR0605-P3-USF/R1_HF_HWBSC01 @ Power Cube | 10/17/2025 02:58:38 | Major | 21825 | CSL Fault | 10/17/2025 02:58:36 | P3 | SRAN | dammam | Power Cube | 2G_3G_LTE SA | KRS0888-P3-USF 2G_3G_LTE,YBR0605-P3-USF 2G_3G | FLM_TE | KRS0885 | Site HUB TRM FB YBR0605 YBR0605 We are observing PM Error and RSL degradation at link: YBR0605 dir YBR0604 KRS0888 KRS0885 Suspecting power issue at hub site | PCM-20251017-00000250 | Telecom issue | Telecom issue |  | sites down |  | API | 10/17/2025 03:55:41 | 10/17/2025 10:55:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251017000135 | PCM-20251017-00000259 | TT-20251017-00254 | EM | [7 empty] | 10/17/2025 03:58:08 | 10/17/2025 03:58:08 | 10/17/2025 07:58:08 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/17/2025 03:56:37 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/17/2025 03:56:27 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/17/2025 03:58:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000153 | PCM-20251017-00000285 | TT-20251017-00294 | Telecom | Region_6 | AB1 | AB1 | Transsmission | DWDM_SW | Alarm at DWDM End Flapped and Cleared | Muhammad Mohsin Ali Ghazanfar Ali | 10/17/2025 04:24:42 | 10/18/2025 13:25:22 | 10/17/2025 10:24:42 | Observed a bulk of BGP Status Changed On ABHA-P Connected to IPRAN flapped and restored | 10/17/2025 04:21:03 | Major | 1100476 | BGP Status Changed | 10/17/2025 04:21:03 | P1 | BSC | abha | Sceco_STB | IPBB NSA | Observed a bulk of BGP Status Changed On ABHA-P Connected to IPRAN flapped and restored | FLM_TE | [5 empty] | Observed a bulk of BGP Status Changed On ABHA-P Connected to IPRAN flapped and restored |  |  | API | 10/17/2025 04:24:42 | 10/18/2025 13:19:56 | 10/18/2025 13:25:09 |  |  | 10/18/2025 13:25:22 |  | Muhammad Mohsin Ali Ghazanfar Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000157 | PCM-20251017-00000293 | TT-20251017-00286 | Reference_telecom | Region_2 | RIY2M7419 | RIY0419 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Waseem Shahzad Ghulam Rasool | 10/17/2025 04:36:41 | 10/18/2025 13:39:43 | 10/17/2025 16:36:41 | Cell RX Channel Interference Noise Power Unbalanced at RIY2M7419-P2-L900-L800 @ Sceco | 10/17/2025 01:18:56 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/17/2025 01:18:53 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M7419 | FLM_TE |  | Dears Kindly check HW | PCM-20251017-00000283 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/17/2025 04:36:41 | 10/18/2025 11:45:35 | 10/18/2025 11:58:14 | 10/18/2025 11:58:17 | 10/18/2025 12:35:10 | 10/18/2025 13:39:43 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000174 | PCM-20251017-00000321 | TT-20251017-00338 | Telecom | Region_4 | MLJI1M3187 | MLJI0187 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/17/2025 05:03:01 | 10/17/2025 13:15:51 | 10/17/2025 11:03:01 | 1(3G) sites down under MLJI0187-P2-USF/MLJI1M3187-P2-USF @ Sceco | 10/17/2025 04:55:12 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/17/2025 04:54:32 | P2 | 3G | alaith | Sceco | 3G SA | MLJI0187-P2-USF | FLM_TE | MLJI0187 | Results: DOWN SITE HUB MLJI0187-P2-USF MLJI0187 Summary: Hub: MLJI0187, Down Count: 1, Down Sites: MLJI0187-P2-USF Alarm Summary: MLJI0187 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/17/2025 05:03:01 | 10/17/2025 10:04:48 | 10/17/2025 13:15:37 |  |  | 10/17/2025 13:15:51 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000177 | PCM-20251017-00000325 | TT-20251017-00060 | Telecom | Region_4 | JED1U6831 | JED6131 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/17/2025 05:07:57 | 10/17/2025 17:17:05 | 10/17/2025 11:07:57 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/17/2025 00:47:11 | Major | 7654 | CELL OPERATION DEGRADED | 10/17/2025 00:47:06 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251017-00000060 | FLM need to check VSWR issue at site. | FLM need to check VSWR issue at site. |  |  |  | API | 10/17/2025 05:07:57 | 10/17/2025 17:15:04 | 10/17/2025 17:16:58 |  |  | 10/17/2025 17:17:05 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000186 | PCM-20251017-00000339 | TT-20251017-00360 | EM | Region_1 | ARM2M1714 | ARM0714 |  |  |  | Omer Elfadoul Mohamed Ibrahim | 10/17/2025 05:33:05 | 10/17/2025 05:39:56 | 10/17/2025 09:33:05 | 1(2G/3G/LTE) sites down under ARM0714-P1-DIA/DM1MBSCH01 @ Generator_SG | 10/17/2025 05:25:43 | Critical | 21825 | CSL Fault | 10/17/2025 05:25:40 | P1 | 2G | dammam | Generator_SG | 2G_3G_LTE SA | ARM0714-P1-DIA | FLM_EM | ARM0714 | Results: DOWN SITE HUB ARM0714-P1-DIA ARM0714 Summary: Hub: ARM0714, Down Count: 1, Down Sites: ARM0714-P1-DIA Alarm Summary: ARM0714 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/17/2025 05:33:05 | 10/17/2025 05:39:56 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000191 | PCM-20251017-00000345 | TT-20251017-00372 | EM | Region_1 | HFBD2M5012 | HFBD0012 |  |  |  | Reda Magdi Elmetwalli Ghazi | 10/17/2025 05:40:26 | 10/17/2025 22:47:27 | 10/17/2025 11:40:26 | Mains Failure at HFBD2M5012-P1-HUB @ Generator_SG | 10/17/2025 05:30:30 | Major | 65109 | Mains Failure | 10/17/2025 05:30:28 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5012 | FLM_EM | [8 empty] | API | 10/17/2025 05:40:26 | 10/17/2025 22:47:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000201 | PCM-20251017-00000359 | TT-20251017-00379 | Telecom | Region_1 | HFBD2M5012 | HFBD0012 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/17/2025 05:52:32 | 10/17/2025 09:20:10 | 10/17/2025 09:52:32 | 1(2G) sites down under HFBD0012-P1-HUB/R1_HF_HWBSC01 @ Generator_SG | 10/17/2025 05:44:28 | Critical | 21807 | OML Fault | 10/17/2025 05:44:23 | P1 | 2G | hafouf | Generator_SG | 2G SA | HFBD0012-P1-HUB | FLM_TE | HFBD0012 | Results: DOWN SITE HUB HFBD0012-P1-HUB HFBD0012 Summary: Hub: HFBD0012, Down Count: 1, Down Sites: HFBD0012-P1-HUB Alarm Summary: HFBD0012 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/17/2025 05:52:32 | 10/17/2025 09:20:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000203 | PCM-20251017-00000362 | TT-20251017-00384 | Reference_telecom | Region_6 | KMS0282 | KMS0282 | Transsmission | MW_HW_stuck | Reset Control Card | Ahmed Abdelaziz Hamid Abdelrahman | 10/17/2025 05:53:50 | 10/23/2025 16:19:31 | 10/17/2025 17:53:50 | ReplaceableUnitProblem observed in KMS0282_02 towards 10.10.153.19 @ Sceco | 10/16/2025 17:54:12 | Minor |  | ReplaceableUnitProblem | 10/16/2025 17:53:32 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0282 | FLM_TE | [8 empty] | API | 10/17/2025 05:53:50 | 10/17/2025 12:48:33 | 10/23/2025 16:19:16 |  |  | 10/23/2025 16:19:31 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000207 | PCM-20251017-00000372 | TT-20251017-00394 | EM | Region_4 | JED0294 | JED0294 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/17/2025 06:06:33 | 10/18/2025 10:16:24 | 10/17/2025 12:06:33 | 1(2G/5G) sites down under JED0294-P3 @ Generator_SG | 10/17/2025 05:58:02 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/17/2025 05:57:59 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5461818 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/17/2025 06:06:33 | 10/18/2025 10:14:52 | 10/18/2025 10:16:15 |  |  | 10/18/2025 10:16:24 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000215 | PCM-20251017-00000385 | TT-20251017-00420 | EM | Region_1 | ARM0730 | ARM0730 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/17/2025 06:25:22 | 10/21/2025 11:37:58 | 10/17/2025 18:25:22 | DC power fail at ARM0730-P2_SRAN @ Sceco | 10/17/2025 06:21:09 | Minor | 65106 | DC power fail | 10/17/2025 06:14:56 | P2 | SRAN | dammam | Sceco | 2G NSA | ARM0730 | FLM_EM | [8 empty] | API | 10/17/2025 06:25:22 | 10/17/2025 14:17:01 | [6 empty] | Building Authority |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000224 | PCM-20251017-00000399 | TT-20251017-00435 | Reference_telecom | Region_6 | SAB2078 | SAB2078 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/17/2025 06:37:14 | 10/21/2025 03:50:47 | 10/17/2025 18:37:14 | LossOfSignal observed in SAB2078_01 towards 10.21.79.212 @ Sceco | 10/16/2025 18:37:39 | Minor |  | LossOfSignal | 10/16/2025 18:36:41 | P3 | 2G | baish | Sceco | TX NSA | SAB2078 | FLM_TE | [8 empty] | API | 10/17/2025 06:37:14 | 10/17/2025 12:31:57 | 10/20/2025 19:24:37 | 10/20/2025 19:24:43 | 10/20/2025 19:53:24 | 10/21/2025 03:50:47 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000227 | PCM-20251017-00000404 | TT-20251017-00438 | Reference_telecom | Region_5 | MAK0602 | MAK0602 |  |  |  | Atif Javed Javed Hussain | 10/17/2025 06:42:24 | 10/19/2025 02:39:18 | 10/17/2025 18:42:24 | LagPortDown observed in MAK0602 towards 10.10.190.50 @ Sceco | 10/16/2025 18:42:56 | Minor |  | LagPortDown | 10/16/2025 18:42:00 | P3 | 2G | makkah | Sceco | TX NSA | MAK0602 | FLM_TE | [8 empty] | API | 10/17/2025 06:42:24 | 10/19/2025 02:39:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000234 | PCM-20251017-00000413 | TT-20251017-00448 | Reference_telecom | Region_5 | MDQ0392 | MDQ0392 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/17/2025 06:55:20 | 10/17/2025 06:55:20 | 10/17/2025 18:55:20 | Degrade observed in MDQ0392_01 towards 10.21.74.76 @ Generator_DG | 10/16/2025 18:55:50 | Minor |  | Degrade | 10/16/2025 18:55:13 | P2 | 2G | makkah | Generator_DG | TX NSA | MDQ0392 | FLM_TE | [8 empty] | API | 10/17/2025 06:55:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000246 | PCM-20251017-00000432 | TT-20251017-00460 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/17/2025 07:07:44 | 10/17/2025 19:04:17 | 10/17/2025 19:07:44 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/17/2025 07:01:23 | Minor | 1589 | AC Overfrequency | 10/17/2025 07:01:23 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/17/2025 07:07:44 | 10/17/2025 14:10:36 | 10/17/2025 19:04:04 |  |  | 10/17/2025 19:04:17 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000247 | PCM-20251017-00000433 | TT-20251017-00461 | Telecom | Region_4 | JED1MN2417 | JED2417 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/17/2025 07:07:44 | 10/19/2025 09:40:10 | 10/17/2025 13:07:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2417-NR2.6-P3 @ Sceco | 10/17/2025 07:07:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 07:06:53 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2417 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 07:07:44 | 10/17/2025 10:49:29 | 10/19/2025 09:39:53 |  |  | 10/19/2025 09:40:10 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000252 | PCM-20251017-00000442 | TT-20251017-00464 | Telecom | Region_4 | SJED0731 | SJED0731 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Mohammed Ramadan A Abu Abid | 10/17/2025 07:18:08 | 10/19/2025 09:40:50 | 10/17/2025 19:18:08 | SJED1W0733 is complete down | 10/17/2025 07:03:54 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/17/2025 07:03:54 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0733 | FLM_TE | SJED0731 | HUB: SJED0731 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. | PCM-20251017-00000435 | HUB: SJED0731 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. | HUB: SJED0731 We are observing LAN Link alarm and ETH LOS alarm active at site HUB, kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at site. Kindly update TT under EM, FLM. |  |  |  | API | 10/17/2025 07:18:08 | 10/17/2025 10:49:30 | 10/19/2025 09:40:20 |  |  | 10/19/2025 09:40:50 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000255 | PCM-20251017-00000445 | TT-20251016-02509 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/17/2025 07:22:54 | 10/17/2025 07:22:54 | 10/17/2025 13:22:54 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/16/2025 23:03:09 | Major | 1-12545 | LOCAL_FAULT | 10/16/2025 23:02:57 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE |  |  | PCM-20251017-00000010 | please check in MW | please check in MW |  |  |  | API | 10/17/2025 07:22:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000258 | PCM-20251017-00000448 | TT-20251017-00344 | Telecom | Region_4 | JED1M7901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 07:25:28 | 10/17/2025 10:03:33 | 10/17/2025 13:25:28 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1M7901-CA-L800-P1-VIP-SBTS @ Sceco | 10/17/2025 05:00:32 | Major | 7114 | CELL SERVICE PROBLEM | 10/17/2025 05:00:22 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7901 | FLM_TE |  |  | PCM-20251017-00000323 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:25:28 | 10/17/2025 10:03:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000259 | PCM-20251017-00000449 | TT-20251017-00322 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/17/2025 07:25:38 | 10/21/2025 17:12:37 | 10/17/2025 13:25:38 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/17/2025 04:38:48 | Major | 7114 | CELL SERVICE PROBLEM | 10/17/2025 04:38:42 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251017-00000306 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:25:38 | 10/17/2025 17:15:06 | 10/17/2025 17:16:32 |  |  | 10/17/2025 17:16:38 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000260 | PCM-20251017-00000450 | TT-20251017-00207 | Telecom | Region_4 | FRS2020 | FRS2020 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/17/2025 07:25:46 | 10/17/2025 11:58:01 | 10/17/2025 19:25:46 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at FRS2020-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/17/2025 03:15:21 | Minor | 7114 | CELL SERVICE PROBLEM | 10/17/2025 03:15:09 | P3 | 2G | qunfuddah | Sceco | 5G_Cell SA | FRS2020 | FLM_TE |  |  | PCM-20251017-00000220 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:25:46 | 10/17/2025 11:58:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000267 | PCM-20251017-00000461 | TT-20251017-00482 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/17/2025 07:33:04 | 10/17/2025 11:11:11 | 10/17/2025 13:33:04 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/17/2025 07:25:42 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 07:25:31 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/17/2025 07:33:04 | 10/17/2025 11:11:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000270 | PCM-20251017-00000464 | TT-20251017-00454 | Telecom | Region_4 | JED0492 | JED0492 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 07:34:18 | 10/17/2025 10:03:34 | 10/17/2025 19:34:18 | BASE STATION ANTENNA LINE PROBLEM at JED0492-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/17/2025 06:55:31 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 06:55:27 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0492 | FLM_TE |  |  | PCM-20251017-00000423 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:34:18 | 10/17/2025 10:03:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000271 | PCM-20251017-00000465 | TT-20251017-00402 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 07:34:28 | 10/17/2025 10:03:34 | 10/17/2025 13:34:28 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/17/2025 06:01:46 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 06:01:35 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251017-00000374 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:34:28 | 10/17/2025 10:03:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000272 | PCM-20251017-00000466 | TT-20251017-00356 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/17/2025 07:34:37 | 10/17/2025 15:37:40 | 10/17/2025 13:34:37 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/17/2025 05:17:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 05:17:03 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251017-00000332 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:34:37 | 10/17/2025 15:37:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000276 | PCM-20251017-00000470 | TT-20251017-00010 | Telecom | Region_6 | JIZ6008 | JIZ6008 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Osama Hadi | 10/17/2025 07:35:36 | 10/18/2025 07:02:57 | 10/17/2025 13:35:36 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at JIZ6008-P3 @ Sceco | 10/17/2025 00:03:36 | Major | 7607 | TRX OPERATION DEGRADED | 10/17/2025 00:03:33 | P3 | 2G | jizan | Sceco | 2G_TRX NSA | JIZ6008 | FLM_TE |  |  | PCM-20251017-00000007 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:35:36 | 10/17/2025 20:20:20 | 10/18/2025 07:02:51 |  |  | 10/18/2025 07:02:57 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000278 | PCM-20251017-00000473 | TT-20251017-00489 | Telecom | Region_4 | JED6021 | JED6021 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/17/2025 07:40:22 | 10/17/2025 17:16:28 | 10/17/2025 19:40:22 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6021-G9-L1800-L2100-SBTS-P3 @ Generator_SG | 10/17/2025 07:31:30 | Minor | 7114 | CELL SERVICE PROBLEM | 10/17/2025 07:31:20 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED6021 | FLM_TE |  |  | PCM-20251017-00000471 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 07:40:22 | 10/17/2025 17:15:07 | 10/17/2025 17:16:22 |  |  | 10/17/2025 17:16:28 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000291 | PCM-20251017-00000499 | TT-20251017-00509 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/17/2025 07:48:02 | 10/19/2025 02:39:19 | 10/17/2025 11:48:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/17/2025 07:47:18 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 07:47:12 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 07:48:02 | 10/19/2025 02:39:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000299 | PCM-20251017-00000510 | TT-20251017-00516 | Reference_telecom | Region_5 | MAK0048 | MAK0048 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/17/2025 07:58:52 | 10/21/2025 19:56:59 | 10/17/2025 19:58:52 | Degrade observed in MAK0048 towards 10.10.187.86 @ Sceco | 10/16/2025 19:59:49 | Minor |  | Degrade | 10/16/2025 19:58:35 | P2 | 2G | makkah | Sceco | TX NSA | MAK0048 | FLM_TE | [8 empty] | API | 10/17/2025 07:58:52 | 10/21/2025 19:56:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000300 | PCM-20251017-00000511 | TT-20251017-00517 | Reference_telecom | Region_5 | MAK0611 | MAK0611 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/17/2025 07:58:53 | 10/21/2025 19:57:00 | 10/17/2025 19:58:53 | Degrade observed in MAK0611_03 towards 10.10.187.85 @ Sceco | 10/16/2025 19:59:49 | Minor |  | Degrade | 10/16/2025 19:58:40 | P2 | 2G | makkah | Sceco | TX NSA | MAK0611 | FLM_TE | [8 empty] | API | 10/17/2025 07:58:53 | 10/21/2025 19:57:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000301 | PCM-20251017-00000512 | TT-20251017-00398 | Reference_telecom | Region_6 | TBL1M8293 | TBL2293 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Saddam Hussain Shah Nawaz Khan | 10/17/2025 07:59:05 | 10/18/2025 15:49:48 | 10/17/2025 19:59:05 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8293-L800-CA-SBTS-P3 @ Sceco | 10/17/2025 04:07:47 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 04:03:05 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M8293 | FLM_TE |  | Thanks to check | PCM-20251017-00000491 | Thanks to check | Thanks to check |  |  |  | API | 10/17/2025 07:59:05 | 10/18/2025 14:57:07 | 10/18/2025 15:48:49 |  |  | 10/18/2025 15:49:48 |  | Saddam Hussain Shah Nawaz Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000302 | PCM-20251017-00000513 | TT-20251017-00397 | Reference_telecom | Region_6 | TBL1M8287 | TBL2287 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/17/2025 07:59:36 | 10/17/2025 16:05:33 | 10/17/2025 19:59:36 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8287-G9-L8-L18-L21-SBTS-P3 @ Generator_DG | 10/17/2025 04:07:55 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 04:02:47 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8287 | FLM_TE |  | Thanks to check | PCM-20251017-00000492 | Thanks to check | Thanks to check |  |  |  | API | 10/17/2025 07:59:36 | 10/17/2025 15:22:36 | 10/17/2025 16:05:22 |  |  | 10/17/2025 16:05:33 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000304 | PCM-20251017-00000515 | TT-20251017-00501 | Reference_telecom | Region_4 | JDRS1M7756 | JDRS0756 |  |  |  | Khizer Hayat | 10/17/2025 08:00:57 | 10/17/2025 11:11:11 | 10/17/2025 14:00:57 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JDRS1M7756-G9-NL8-NL18-NL21-SBTS-P1-HUB-USF @ Generator_SG | 10/17/2025 05:43:07 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 05:42:58 | P1 | 4G | jeddah | Generator_SG | LTE NSA | JDRS1M7756 | FLM_TE |  | Thanks to check | PCM-20251017-00000500 | Thanks to check | Thanks to check |  |  |  | API | 10/17/2025 08:00:57 | 10/17/2025 11:11:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000305 | PCM-20251017-00000516 | TT-20251017-00518 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/17/2025 08:00:57 | 10/19/2025 02:39:20 | 10/17/2025 20:00:57 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/17/2025 07:52:30 | Minor | 7115 | BASE STATION INFORMATION | 10/17/2025 07:52:25 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/17/2025 08:00:57 | 10/19/2025 02:39:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000310 | PCM-20251017-00000525 | TT-20251017-00529 | Reference_telecom | Region_6 | TLT0874 | TLT0874 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/17/2025 08:10:15 | 10/19/2025 13:30:27 | 10/17/2025 20:10:15 | LossOfSignal observed in TLT0874_01 towards 10.74.121.82 @ Sceco | 10/16/2025 20:10:25 | Minor |  | LossOfSignal | 10/16/2025 20:09:59 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0874 | FLM_TE | [8 empty] | API | 10/17/2025 08:10:15 | 10/17/2025 09:01:28 | 10/19/2025 13:28:36 |  |  | 10/19/2025 13:30:27 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000315 | PCM-20251017-00000536 | TT-20251017-00539 | Reference_telecom | Region_4 | JED2031 | JED2031 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/17/2025 08:26:15 | 10/17/2025 08:26:15 | 10/17/2025 20:26:15 | ReplaceableUnitProblem observed in JED2031 towards 10.10.177.2 @ Sceco | 10/16/2025 20:26:03 | Minor |  | ReplaceableUnitProblem | 10/16/2025 20:25:59 | VIP | 2G | jeddah | Sceco | TX NSA | JED2031 | FLM_TE | [8 empty] | API | 10/17/2025 08:26:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000316 | PCM-20251017-00000540 | TT-20251017-00544 | Telecom | Region_4 | JED1M7188 | JED0188 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 08:29:53 | 10/19/2025 17:44:36 | 10/17/2025 14:29:53 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7188-P3-CA-L900-L800-SBTS @ Sceco | 10/17/2025 08:29:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 08:29:05 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7188 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 08:29:53 | 10/17/2025 10:03:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000324 | PCM-20251017-00000558 | TT-20251017-00072 | Telecom | Region_4 | JED2903 | JED2903 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 08:45:47 | 10/17/2025 10:03:35 | 10/17/2025 14:45:47 | 1(2G) 1(LTE) 1(5G) sites down under JED2903-P3-CA-L800,JED2886-P3/JED2886-P3 @ Generator_SG | 10/17/2025 01:03:08 | Major | 7706 | BTS O&M LINK FAILURE | 10/17/2025 01:03:07 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED2903-P3-CA-L800 LTE,JED2886-P3 2G | FLM_TE | JED2903 | DOWN SITE HUB TX FB JED2903 JED2903 Observing Link Flapping at HUB , kindly check locally JED2886 JED2886 ODUs Offline | PCM-20251017-00000553 | DOWN SITE HUB TX FB JED2903 JED2903 Observing Link Flapping at HUB , kindly check locally JED2886 JED2886 ODUs Offline | DOWN SITE HUB TX FB JED2903 JED2903 Observing Link Flapping at HUB , kindly check locally JED2886 JED2886 ODUs Offline |  | sites down |  | API | 10/17/2025 08:45:47 | 10/17/2025 10:03:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000335 | PCM-20251017-00000575 | TT-20251017-00583 | EM | Region_4 | HHR0889 | HHR0889 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/17/2025 08:59:19 | 10/23/2025 12:57:12 | 10/17/2025 14:59:19 | GENERATOR1 + GENERATOR2 2 FAILURE at HHR0889-GSM-P1-VIP-HHR @ Generator_SG | 10/17/2025 08:51:18 | Major | 7103 | GENERATOR1 + GENERATOR2 2 FAILURE | 10/17/2025 08:51:06 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0889 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 FAILURE |  |  | API | 10/17/2025 08:59:19 | 10/23/2025 12:57:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000337 | PCM-20251017-00000576 | TT-20251017-00585 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/17/2025 08:59:50 | 10/21/2025 23:22:29 | 10/17/2025 14:59:50 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/17/2025 08:49:36 | Major | 65102 | high temprature 32 | 10/17/2025 08:49:32 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/17/2025 08:59:50 | 10/21/2025 23:22:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000346 | PCM-20251017-00000589 | TT-20251017-00598 | EM | Region_4 | HHR0507 | HHR0507 |  |  |  | Aly Ahmed Aly Sawy | 10/17/2025 09:18:26 | 10/18/2025 06:15:04 | 10/17/2025 15:18:26 | Generator Low Fuel at HHR0507-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/17/2025 09:10:10 | Major | 7103 | Generator Low Fuel | 10/17/2025 09:10:01 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0507 | FLM_EM | [5 empty] | Generator Low Fuel |  |  | API | 10/17/2025 09:18:26 | 10/18/2025 06:15:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251017000350 | PCM-20251017-00000593 | TT-20251017-00600 | Telecom | Region_4 | JED1MC2051 | JED2051 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/17/2025 09:22:04 | 10/17/2025 09:22:04 | 10/17/2025 15:22:04 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connector) at JED1MC2051-NR3.5 @ Sceco | 10/17/2025 09:17:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 09:17:20 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MC2051 | FLM_TE | [5 empty] | Increased BER detected on the optical connector |  |  | API | 10/17/2025 09:22:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000354 | PCM-20251017-00000598 | TT-20251017-00247 | MW_HC | Region_5 | MAK0082 | MAK0082 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/17/2025 09:26:49 | 10/19/2025 14:53:03 | 10/17/2025 21:26:49 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0082-MAK0811 | 10/17/2025 03:53:17 | Minor | 113388 | LOF | 10/17/2025 03:53:20 | P2 | 2G | makkah | Sceco | TX NSA | MAK0082-MAK0811 | FLM_TE |  | Dear FLM, Approved | PCM-20251017-00000390 | Dear FLM, Approved | Dear FLM, Approved |  |  |  | API | 10/17/2025 09:26:49 | 10/19/2025 14:53:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000364 | PCM-20251017-00000613 | TT-20251017-00621 | Telecom | Region_1 | DAM0030 | DAM0030 | Equipment | BTS_Cable | Replace CPRI Cable | Meraj Husain Idd Baksh | 10/17/2025 09:40:40 | 10/17/2025 14:42:38 | 10/17/2025 15:40:40 | NR Cell Unavailable at DAM0030-P2_SRAN @ Sceco | 10/17/2025 09:34:06 | Major | 29841 | NR Cell Unavailable | 10/17/2025 09:32:34 | P2 | SRAN | dammam | Sceco | 5G SA | DAM0030 | FLM_TE | [8 empty] | API | 10/17/2025 09:40:40 | 10/17/2025 10:15:44 | 10/17/2025 14:42:21 |  |  | 10/17/2025 14:42:38 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251017000365 | PCM-20251017-00000614 | TT-20251017-00623 | Telecom | Region_4 | RAB1M7474 | RAB0474 |  |  |  | Khizer Hayat | 10/17/2025 09:42:13 | 10/19/2025 17:44:37 | 10/17/2025 15:42:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at RAB1M7474-G9-NL8-L18-L21-SBTS-P2-USF @ Sceco | 10/17/2025 09:41:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 09:41:21 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | RAB1M7474 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 09:42:13 | 10/17/2025 11:11:12 | 10/18/2025 13:40:32 | 10/18/2025 13:40:34 | 10/18/2025 13:40:37 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000369 | PCM-20251017-00000620 | TT-20251017-00630 | EM | Region_4 | BHMF1M8137 | BHMF2137 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/17/2025 09:46:20 | 10/17/2025 11:15:34 | 10/17/2025 21:46:20 | COMMERCIAL POWER FAILURE at BHMF1M8137-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/17/2025 09:38:16 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/17/2025 09:38:10 | P3 | 4G | jeddah | Generator_SG | LTE NSA | BHMF1M8137 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/17/2025 09:46:20 | 10/17/2025 11:15:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000372 | PCM-20251017-00000623 | TT-20251017-00592 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/17/2025 09:46:41 | 10/17/2025 17:15:45 | 10/17/2025 15:46:41 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/17/2025 09:02:26 | Major | 7654 | CELL OPERATION DEGRADED | 10/17/2025 09:02:13 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251017-00000583 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 09:46:41 | 10/17/2025 17:15:09 | 10/17/2025 17:15:39 |  |  | 10/17/2025 17:15:45 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000374 | PCM-20251017-00000625 | TT-20251017-00537 | Telecom | Region_4 | JED1M8595 | JED2595 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 09:47:38 | 10/17/2025 10:34:14 | 10/17/2025 15:47:38 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at JED1M8595-P3-CA-L800 @ Sceco | 10/17/2025 08:16:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 08:16:16 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8595 | FLM_TE |  |  | PCM-20251017-00000534 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 09:47:38 | 10/17/2025 10:34:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000376 | PCM-20251017-00000627 | TT-20251017-00634 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/17/2025 09:48:56 | 10/17/2025 11:15:34 | 10/17/2025 21:48:56 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/17/2025 09:40:50 | Minor | 7103 | HIGH TEMP | 10/17/2025 09:40:45 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/17/2025 09:48:56 | 10/17/2025 11:15:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000387 | PCM-20251017-00000645 | TT-20251017-00649 | EM | Region_6 | DRB1M7953 | DRB0953 |  |  |  | Aziz Ul Haq Umar Gul | 10/17/2025 10:01:50 | 10/17/2025 17:17:05 | 10/17/2025 22:01:50 | AIRCON 1 FAILURE at DRB1M7953-NCA-L800 @ Sceco | 10/17/2025 09:53:28 | Minor | 7103 | AIRCON 1 FAILURE | 10/17/2025 09:53:18 | P3 | 4G | derb | Sceco | LTE NSA | DRB1M7953 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/17/2025 10:01:50 | 10/17/2025 17:17:05 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251017000400 | PCM-20251017-00000675 | TT-20251017-00687 | Reference_telecom | Region_4 | JED0804 | JED0804 |  |  |  | Abd Elrahman Suliman Mohmed Suliman | 10/17/2025 10:46:44 | 10/21/2025 12:55:11 | 10/17/2025 22:46:44 | Degrade observed in JED0804_01 towards 10.3.227.84 @ Sceco | 10/16/2025 22:46:34 | Minor |  | Degrade | 10/16/2025 22:46:24 | P2 | 2G | jeddah | Sceco | TX NSA | JED0804 | FLM_TE | [8 empty] | API | 10/17/2025 10:46:44 | 10/21/2025 12:53:55 | 10/21/2025 12:55:03 | 10/21/2025 12:55:08 | 10/21/2025 12:55:11 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000401 | PCM-20251017-00000674 | TT-20251017-00686 | Reference_telecom | Region_4 | JED2038 | JED2038 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 10:46:45 | 10/17/2025 13:13:01 | 10/17/2025 22:46:45 | LagPortDown observed in JED2038_03 towards 10.3.227.87 @ Sceco | 10/16/2025 22:46:27 | Minor |  | LagPortDown | 10/16/2025 22:46:23 | P3 | 2G | jeddah | Sceco | TX NSA | JED2038 | FLM_TE | [8 empty] | API | 10/17/2025 10:46:45 | 10/17/2025 13:13:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000412 | PCM-20251017-00000707 | TT-20251016-01909 | Telecom | Region_4 | AQA0152 | AQA0152 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/17/2025 11:06:21 | 10/22/2025 12:24:51 | 10/17/2025 17:06:21 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at AQA0152-P2-USF @ Generator_SG | 10/16/2025 15:51:51 | Major | 7607 | TRX OPERATION DEGRADED | 10/15/2025 10:33:23 | P2 | 2G | adam | Generator_SG | 2G_TRX NSA | AQA0152 | FLM_TE |  |  | PCM-20251017-00000422 | it's whitelisted, why you sent this to IPRAN | it's whitelisted, why you sent this to IPRAN |  |  |  | API | 10/17/2025 11:06:21 | 10/17/2025 13:15:21 | 10/22/2025 12:24:37 |  |  | 10/22/2025 12:24:51 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000426 | PCM-20251017-00000729 | TT-20251017-00696 | Telecom | Region_4 | JED2979 | JED2979 | Transsmission | IPRAN_Fluctuation | Change Port | Abd EL Azeez EL Sayed Soliman | 10/17/2025 11:17:57 | 10/17/2025 14:45:48 | 10/17/2025 15:17:57 | 2(2G) 2(LTE) 2(5G) sites down under JED2979-P1-VIP,JED0948-P3/JED0948-P3 @ Sceco | 10/17/2025 10:50:28 | Critical | 7706 | BTS O&M LINK FAILURE | 10/17/2025 10:50:23 | VIP | 2G | jeddah | Generator_SG | 2G_5G SA | JED2979-P1-VIP 2G_5G,JED0948-P3 2G_5G | FLM_EM | JED2979 | DOWN SITE HUB TX FB JED0948 JED0948 Suspected Power issue at HUB JED2979 JED2979 Suspected Power issue at HUB | PCM-20251017-00000693 | DOWN SITE HUB TX FB JED0948 JED0948 Suspected Power issue at HUB JED2979 JED2979 Suspected Power issue at HUB | DOWN SITE HUB TX FB JED0948 JED0948 Suspected Power issue at HUB JED2979 JED2979 Suspected Power issue at HUB |  | sites down |  | API | 10/17/2025 11:17:57 | 10/17/2025 11:35:41 | 10/17/2025 14:45:38 |  |  | 10/17/2025 14:45:48 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000429 | PCM-20251017-00000733 | TT-20251017-00719 | EM | Region_4 | HAW0328 | HAW0328 |  |  |  | Farghal Ashour Hassan Farghal | 10/17/2025 11:19:50 | 10/17/2025 13:19:10 | 10/17/2025 17:19:50 | TRX FAULTY (FF FF FF FF FF FF shared:S) at HAW0328-P1-DIA @ Sceco | 10/17/2025 11:12:26 | Major | 7606 | TRX FAULTY | 10/17/2025 11:12:23 | P1 | 2G | taif | Sceco | 2G_Cell SA | HAW0328 | FLM_EM | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/17/2025 11:19:50 | 10/17/2025 13:19:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000432 | PCM-20251017-00000743 | TT-20251017-00728 | Telecom | Region_4 | JED1M8596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 11:32:15 | 10/19/2025 09:18:43 | 10/17/2025 15:32:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8596-P1-CA-L800 @ Sceco | 10/17/2025 11:31:29 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 11:31:20 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8596 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 11:32:15 | 10/19/2025 09:18:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000434 | PCM-20251017-00000745 | TT-20251017-00725 | Reference_telecom | Region_1 | DMHF2M7081 | DMHF0081 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/17/2025 11:33:25 | 10/18/2025 10:22:32 | 10/17/2025 23:33:25 | Cell RX Channel Interference Noise Power Unbalanced at DMHF2M7081-P1-HUB-L800-CA @ Generator_SG | 10/17/2025 08:26:11 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/17/2025 08:26:07 | P1 | 4G | hafouf | Generator_SG | 2G NSA | DMHF2M7081 | FLM_TE |  |  | PCM-20251017-00000739 | Need FLM to make RF path HC for RRU 121 | Need FLM to make RF path HC for RRU 121 |  |  |  | API | 10/17/2025 11:33:25 | 10/18/2025 10:22:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000464 | PCM-20251017-00000791 | TT-20251017-00781 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/17/2025 12:15:07 | 10/21/2025 22:26:14 | 10/18/2025 00:15:07 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/17/2025 12:06:50 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/17/2025 12:06:42 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | Manual | 10/17/2025 12:15:07 | 10/21/2025 22:26:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000477 | PCM-20251017-00000813 | TT-20251017-00807 | Reference_telecom | Region_4 | JED2038 | JED2038 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 12:29:33 | 10/17/2025 13:13:02 | 10/18/2025 00:29:33 | FanFailure observed in JED2038_02 towards 10.3.227.86 @ Sceco | 10/17/2025 00:29:34 | Minor |  | FanFailure | 10/17/2025 00:29:15 | P3 | 2G | jeddah | Sceco | TX NSA | JED2038 | FLM_TE | [8 empty] | API | 10/17/2025 12:29:33 | 10/17/2025 13:13:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251017000487 | PCM-20251017-00000827 | TT-20251017-00815 | EM | [7 empty] | 10/17/2025 12:36:49 | 10/17/2025 12:36:49 | 10/18/2025 00:36:49 | RECTIFIER MAINS POWER FAILURE at MUMA1M8070-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/17/2025 12:28:23 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/17/2025 12:28:16 | P3 | 4G |  | Sceco | LTE NSA | MUMA1M8070 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/17/2025 12:36:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251017000492 | PCM-20251017-00000832 | TT-20251017-00820 | Telecom | Region_4 | JED0578 | JED0578 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 12:41:58 | 10/17/2025 12:41:58 | 10/17/2025 18:41:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0578-G9-L8-L18-L21-NR2.6-NR3.5-SBTS @ Sceco | 10/17/2025 12:41:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 12:40:50 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0578 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 12:41:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000515 | PCM-20251017-00000862 | TT-20251017-00852 | Telecom | Region_4 | JED1MN2689 | JED2689 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 13:09:53 | 10/17/2025 13:09:53 | 10/18/2025 01:09:53 | BASE STATION INFORMATION (No module fan detected) at JED1MN2689-NR2.6-P3 @ Sceco | 10/17/2025 13:01:58 | Minor | 7115 | BASE STATION INFORMATION | 10/17/2025 13:01:46 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN2689 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/17/2025 13:09:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000519 | PCM-20251017-00000868 | TT-20251017-00861 | Telecom | Region_1 | DAM2995 | DAM2995 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/17/2025 13:14:01 | 10/17/2025 13:16:37 | 10/18/2025 01:14:01 | RF Unit Temperature Unacceptable at DAM2995-P2_SRAN @ Sceco | 10/17/2025 13:07:05 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/17/2025 13:07:01 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2995 | FLM_TE | [8 empty] | API | 10/17/2025 13:14:01 | 10/17/2025 13:16:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000526 | PCM-20251017-00000879 | TT-20251017-00877 | EM | Region_4 | MUMA1M8198 | MUMA2198 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/17/2025 13:24:21 | 10/18/2025 06:39:34 | 10/18/2025 01:24:21 | COMMERCIAL POWER FAILURE at MUMA1M8198-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/17/2025 13:15:50 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/17/2025 13:15:45 | P3 | 4G | jeddah | Generator_SG | LTE NSA | MUMA1M8198 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/17/2025 13:24:21 | 10/18/2025 06:39:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000528 | PCM-20251017-00000881 | TT-20251017-00878 | Telecom | Region_4 | JED0500 | JED0500 | Equipment | SW | Issue was solved after softaware configuration | Khaled Mohammad Abdallah | 10/17/2025 13:24:51 | 10/21/2025 23:26:06 | 10/17/2025 19:24:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/17/2025 13:24:02 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 13:23:56 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0500 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 13:24:51 |  | 10/20/2025 03:47:27 | 10/20/2025 03:47:36 | 10/20/2025 03:47:38 | 10/21/2025 23:26:06 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000529 | PCM-20251017-00000883 | TT-20251017-00880 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/17/2025 13:25:54 | 10/18/2025 12:13:24 | 10/18/2025 01:25:54 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/17/2025 13:17:44 | Minor | 7103 | AIRCON 2 FAILURE | 10/17/2025 13:17:37 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/17/2025 13:25:54 | 10/18/2025 12:13:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000531 | PCM-20251017-00000885 | TT-20251017-00884 | EM | Region_6 | BHAB1M7901 | BHAB0901 |  |  |  | Sohail Nasir Mir Afzal | 10/17/2025 13:28:28 | 10/19/2025 05:52:20 | 10/18/2025 01:28:28 | Smoke Alarm at BHAB1M7901-G9-U9-L8-L18-L21-SBTS-P3 @ Sceco | 10/17/2025 13:20:25 | Minor | 7103 | Smoke Alarm | 10/17/2025 13:20:19 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7901 | FLM_EM | [5 empty] | Smoke Alarm |  |  | API | 10/17/2025 13:28:28 | 10/19/2025 05:52:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000550 | PCM-20251017-00000908 | TT-20251017-00912 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/17/2025 13:41:23 | 10/18/2025 08:41:06 | 10/17/2025 19:41:23 | high temprature 40 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/17/2025 13:30:56 | Major | 65103 | high temprature 40 | 10/17/2025 13:30:52 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/17/2025 13:41:23 | 10/18/2025 08:41:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000571 | PCM-20251017-00000944 | TT-20251017-00698 | Telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/17/2025 14:07:44 | 10/17/2025 22:53:25 | 10/17/2025 20:07:44 | BBU CPRI Interface Error at RYQ0972-P3_SRAN @ Sceco | 10/17/2025 10:53:07 | Major | 26234 | BBU CPRI Interface Error | 10/17/2025 10:50:29 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0972 | FLM_TE |  |  | PCM-20251017-00000919 | Need FLM to modify CPRI connection to CPRI 0 , 1, 2 on UBBP as agreed | Need FLM to modify CPRI connection to CPRI 0 , 1, 2 on UBBP as agreed |  |  |  | API | 10/17/2025 14:07:44 | 10/17/2025 22:53:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000576 | PCM-20251017-00000950 | TT-20251017-00939 | Telecom | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/17/2025 14:12:09 | 10/18/2025 12:13:25 | 10/17/2025 18:12:09 | 2(2G) 2(LTE) 2(5G) sites down under JED0132-FWA-P1-VIP,JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/17/2025 14:00:24 | Critical | 7706 | BTS O&M LINK FAILURE | 10/17/2025 14:00:22 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED0132-CA-L900-L800-SBTS-FWA-P1-VIP LTE,JED6020-GSM-P3 2G_LTE | FLM_EM | JED6020 | Dear team , DOWN SITE HUB TX FB JED0132 JED0132 LOS to Air Scale JED6020 JED6020 Suspected Power issue at HUB | PCM-20251017-00000942 | Dear team , DOWN SITE HUB TX FB JED0132 JED0132 LOS to Air Scale JED6020 JED6020 Suspected Power issue at HUB | Dear team , DOWN SITE HUB TX FB JED0132 JED0132 LOS to Air Scale JED6020 JED6020 Suspected Power issue at HUB |  | sites down |  | API | 10/17/2025 14:12:09 | 10/18/2025 12:13:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000577 | PCM-20251017-00000951 | TT-20251017-00954 | Telecom | Region_4 | HAW1M8351 | HAW2351 | Enviroment | Rectifier Module | Change rectifer module | Rashid Shafique | 10/17/2025 14:12:54 | 10/18/2025 19:32:28 | 10/17/2025 20:12:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAW1M8351-P3-CA-L800 @ Sceco | 10/17/2025 14:12:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 14:12:05 | P2 | 4G | taif | Sceco | 5G_Cell SA | HAW1M8351 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 14:12:54 | 10/17/2025 15:21:21 | 10/18/2025 13:34:57 | 10/18/2025 13:35:00 | 10/18/2025 13:35:02 | 10/18/2025 19:32:28 |  | Rashid Shafique |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000582 | PCM-20251017-00000956 | TT-20251017-00948 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/17/2025 14:14:32 | 10/18/2025 09:14:09 | 10/17/2025 18:14:32 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/17/2025 14:06:05 | Critical | 301 | NE Is Disconnected | 10/17/2025 14:06:02 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/17/2025 14:14:32 | 10/18/2025 09:13:13 | 10/18/2025 09:14:01 |  |  | 10/18/2025 09:14:09 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000584 | PCM-20251017-00000958 | TT-20251017-00960 | Reference_telecom | Region_4 | JED2641 | JED2641 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 14:16:30 | 10/17/2025 15:03:55 | 10/18/2025 02:16:30 | Degrade observed in JED2641 towards 10.3.227.90 @ Sceco | 10/17/2025 02:16:23 | Minor |  | Degrade | 10/17/2025 02:16:18 | P3 | 2G | jeddah | Sceco | TX NSA | JED2641 | FLM_TE | [8 empty] | API | 10/17/2025 14:16:30 | 10/17/2025 15:03:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000585 | PCM-20251017-00000959 | TT-20251017-00961 | Reference_telecom | Region_4 | JED0804 | JED0804 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 14:16:31 | 10/17/2025 15:03:55 | 10/18/2025 02:16:31 | LossOfSignal observed in JED0804_2 towards 10.3.227.89 @ Sceco | 10/17/2025 02:16:25 | Minor |  | LossOfSignal | 10/17/2025 02:16:15 | P2 | 2G | jeddah | Sceco | TX NSA | JED0804 | FLM_TE | [8 empty] | API | 10/17/2025 14:16:31 | 10/17/2025 15:03:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000595 | PCM-20251017-00000977 | TT-20251017-00985 | Telecom | Region_2 | RIYA2U6760A | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/17/2025 14:30:28 | 10/19/2025 09:44:31 | 10/17/2025 20:30:28 | RF Out of Service at RIYA2U6760A-P3 @ Sceco | 10/17/2025 14:24:55 | Major | 29248 | RF Out of Service | 10/17/2025 14:24:12 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6760A | FLM_TE | [8 empty] | API | 10/17/2025 14:30:28 | 10/19/2025 09:44:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000600 | PCM-20251017-00000986 | TT-20251017-00979 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/17/2025 14:36:41 | 10/18/2025 09:14:31 | 10/18/2025 02:36:41 | MAC Excessive Frame Error Rate at SRIY0183-P1-VIP_SRAN @ Sceco | 10/17/2025 14:24:15 | Minor | 25881 | MAC Excessive Frame Error Rate | 10/17/2025 14:14:15 | VIP | SRAN | riyadh | Sceco | 2G NSA | SRIY0183 | FLM_TE |  |  | PCM-20251017-00000973 | need to check B2B with SRAN port | need to check B2B with SRAN port |  |  |  | API | 10/17/2025 14:36:41 | 10/18/2025 09:13:13 | 10/18/2025 09:14:23 |  |  | 10/18/2025 09:14:31 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000606 | PCM-20251017-00000993 | TT-20251017-01001 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/17/2025 14:40:17 | 10/17/2025 15:21:47 | 10/18/2025 02:40:17 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/17/2025 14:33:36 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/17/2025 14:33:31 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/17/2025 14:40:17 | 10/17/2025 15:21:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000607 | PCM-20251017-00000995 | TT-20251017-01005 | Reference_telecom | Region_4 | JED0397 | JED0397 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 14:43:22 | 10/17/2025 15:03:56 | 10/18/2025 02:43:22 | Degrade observed in JED0397 towards 10.1.224.146 @ Sceco | 10/17/2025 02:42:52 | Minor |  | Degrade | 10/17/2025 02:42:48 | P2 | 2G | jeddah | Sceco | TX NSA | JED0397 | FLM_TE | [8 empty] | API | 10/17/2025 14:43:22 | 10/17/2025 15:03:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000608 | PCM-20251017-00000996 | TT-20251017-00989 | Telecom | Region_2 | SRIY0339 | SRIY0339 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Waseem Shahzad Ghulam Rasool | 10/17/2025 14:43:56 | 10/18/2025 11:43:05 | 10/17/2025 18:43:56 | 1(2G) 1(3G) 2(LTE) sites down under SRIY0339-P3_SRAN,RIY0339-P1,SRIY0340-P3_SRAN @ Sceco | 10/17/2025 14:29:38 | Critical | 301 | NE Is Disconnected | 10/17/2025 14:29:34 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0340-P3_SRAN LTE,SRIY0339-P3_SRAN LTE | FLM_TE | SRIY0339 | Dear FLM, Hub is SRIY0339 We are observing ETH_LINK_DOWN alarm flapped at hub site ,Kindly send to FLM to check cable connection at site. | PCM-20251017-00000987 | Dear FLM, Hub is SRIY0339 We are observing ETH_LINK_DOWN alarm flapped at hub site ,Kindly send to FLM to check cable connection at site. | Dear FLM, Hub is SRIY0339 We are observing ETH_LINK_DOWN alarm flapped at hub site ,Kindly send to FLM to check cable connection at site. |  | sites down |  | API | 10/17/2025 14:43:56 | 10/18/2025 11:00:45 | 10/18/2025 11:00:51 | 10/18/2025 11:00:57 | 10/18/2025 11:01:00 | 10/18/2025 11:43:05 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000620 | PCM-20251017-00001018 | TT-20251017-00469 | Telecom | Region_1 | RST2840 | RST2840 |  |  |  | Meraj Husain Idd Baksh | 10/17/2025 14:53:03 | 10/17/2025 21:31:56 | 10/18/2025 02:53:03 | Maximum Number of X2 Interfaces Reached at RST2840-P3_SRAN @ Sceco | 10/17/2025 00:08:57 | Minor | 29225 | Maximum Number of X2 Interfaces Reached | 10/17/2025 00:08:53 | P3 | SRAN | dammam | Sceco | 2G NSA | RST2840 | FLM_TE | RST2840 | No issue in TX route ,Need check locally | PCM-20251017-00001011 | No issue in TX route ,Need check locally | No issue in TX route ,Need check locally |  |  |  | API | 10/17/2025 14:53:03 | 10/17/2025 21:31:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000636 | PCM-20251017-00001043 | TT-20251017-01051 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/17/2025 15:05:05 | 10/20/2025 21:24:29 | 10/17/2025 21:05:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/17/2025 15:04:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 15:03:56 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 15:05:05 | 10/20/2025 21:24:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000637 | PCM-20251017-00001044 | TT-20251017-01045 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/17/2025 15:06:02 | 10/17/2025 16:47:12 | 10/17/2025 21:06:02 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/17/2025 14:57:36 | Major | 22214 | NodeB Unavailable | 10/17/2025 14:57:32 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/17/2025 15:06:02 | 10/17/2025 16:47:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000638 | PCM-20251017-00001046 | TT-20251017-01046 | Telecom | Region_4 | MLJI0377 | MLJI0377 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/17/2025 15:12:03 | 10/17/2025 16:00:17 | 10/17/2025 21:12:03 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MLJI0377-GSM-UMTS-P2-USF @ Sceco | 10/17/2025 14:56:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 14:56:43 | P2 | 2G | qunfuddah | Sceco | 5G_Cell SA | MLJI0377 | FLM_TE |  |  | PCM-20251017-00001037 | FLM need to check Rx level and perform HC at site. | FLM need to check Rx level and perform HC at site. |  |  |  | API | 10/17/2025 15:12:03 | 10/17/2025 15:59:44 | 10/17/2025 16:00:03 |  |  | 10/17/2025 16:00:17 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000642 | PCM-20251017-00001050 | TT-20251017-01059 | Telecom | Region_4 | JED1MN0196 | JED0196 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 15:14:55 | 10/17/2025 15:14:55 | 10/17/2025 21:14:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0196-NR2.6 @ Sceco | 10/17/2025 15:13:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 15:13:45 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0196 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 15:14:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000643 | PCM-20251017-00001051 | TT-20251017-01060 | Telecom | Region_4 | JED2350 | JED2350 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 15:15:56 | 10/19/2025 17:44:38 | 10/17/2025 21:15:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2350-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-FON @ Sceco | 10/17/2025 15:15:06 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 15:14:56 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED2350 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 15:15:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251015000359 | PCM-20251015-00000620 | TT-20251015-00677 | EM | Region_6 | ABH0157 | ABH0157 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/15/2025 08:18:50 | 10/15/2025 11:02:34 | 10/15/2025 14:18:50 | AIRCON 1 FAILURE at ABH0157-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP @ Sceco | 10/15/2025 08:10:32 | Major | 7103 | AIRCON 1 FAILURE | 10/15/2025 08:10:29 | VIP | 2G | abha | Sceco | 2G NSA | ABH0157 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/15/2025 08:18:50 | 10/15/2025 11:02:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000381 | PCM-20251015-00000680 | TT-20251015-00725 | EM | Region_4 | FYD0320 | FYD0320 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/15/2025 08:56:30 | 10/15/2025 09:00:05 | 10/15/2025 20:56:30 | AIRCON 1 FAILURE at FYD0320-GSM-P3 @ Sceco | 10/15/2025 08:48:18 | Minor | 7103 | AIRCON 1 FAILURE | 10/15/2025 08:48:07 | P3 | 2G | jeddah | Sceco | 2G NSA | FYD0320 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/15/2025 08:56:30 | 10/15/2025 09:00:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000397 | PCM-20251015-00000707 | TT-20251015-00752 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/15/2025 09:13:06 | 10/15/2025 11:40:45 | 10/15/2025 15:13:06 | high temprature 32 at RIY0232-P1_SRAN @ Sceco | 10/15/2025 09:02:27 | Major | 65102 | high temprature 32 | 10/15/2025 09:02:24 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/15/2025 09:13:06 | 10/15/2025 11:40:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000466 | PCM-20251015-00000826 | TT-20251015-00861 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/15/2025 10:16:05 | 10/16/2025 00:14:53 | 10/15/2025 22:16:05 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/15/2025 10:05:49 | Minor | 65102 | high temprature 32 | 10/15/2025 10:05:46 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/15/2025 10:16:05 | 10/16/2025 00:14:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251015000543 | PCM-20251015-00000946 | TT-20251015-00983 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/15/2025 11:16:35 | 10/16/2025 12:15:24 | 10/15/2025 15:16:35 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/15/2025 11:14:35 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/15/2025 11:14:26 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 0-TO DMJR0141(1-A) |  |  | API | 10/15/2025 11:16:35 | 10/15/2025 14:17:14 | 10/16/2025 12:15:11 |  |  | 10/16/2025 12:15:24 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251015000589 | PCM-20251015-00001013 | TT-20251015-01055 | EM | Region_6 | WDS9471 | WDS9471 |  |  |  | Muhammad Aslam Abdul Salam | 10/15/2025 11:34:36 | 10/15/2025 14:16:42 | 10/15/2025 15:34:36 | Door Open (Input-1) at WDS9471-1 on 10.89.222.39 @ Generator_SG | 10/15/2025 11:31:07 | Critical | Door Open (Input-1) | Door Open (Input-1) | 10/15/2025 11:28:57 | P1 | Repeater | wadi dawasar | Generator_SG | TX NSA | WDS9471 | FLM_EM | [8 empty] | API | 10/15/2025 11:34:36 | 10/15/2025 14:16:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251015000637 | PCM-20251015-00001100 | TT-20251015-01138 | EM | Region_4 | MLJI9434 | MLJI9434 |  |  |  | Ghulam Yahya Ghulam Sarwar | 10/15/2025 12:08:10 | 10/16/2025 09:22:02 | 10/15/2025 16:08:10 | LOW BATTERY +REC.MODULE FAILURE (Input-2) at MLJI9434-1 on 10.88.223.34 @ Generator_DG | 10/15/2025 12:06:08 | Critical | LOW BATTERY +REC.MODULE FAILURE (Input-2) | LOW BATTERY +REC.MODULE FAILURE (Input-2) | 10/15/2025 11:45:54 | P1 | Repeater | alaith | Generator_DG | TX NSA | MLJI9434 | FLM_EM | [8 empty] | API | 10/15/2025 12:08:10 | 10/16/2025 09:22:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251015000665 | PCM-20251015-00001138 | TT-20251015-01203 | EM | Region_2 | MZH0527 | MZH0527 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/15/2025 12:30:55 | 10/15/2025 15:51:41 | 10/15/2025 16:30:55 | NE_COMMU_GNE_SWITCH at MZH0527_ELC @ Sceco_STB | 10/15/2025 12:28:56 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/15/2025 12:28:51 | VIP | SRAN | muzamiah | Sceco_STB | DWDM NSA | MZH0527 | FLM_EM | [5 empty] | NE MZH0527_ELC's current GNE has been switched to standby GNE |  |  | API | 10/15/2025 12:30:55 | 10/15/2025 15:51:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251015000670 | PCM-20251015-00001139 | TT-20251015-01204 | EM | Region_2 | MZH0527 | MZH0527 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/15/2025 12:31:30 | 10/15/2025 15:51:41 | 10/15/2025 16:31:30 | NE_COMMU_GNE_SWITCH at MZH0527_OCS @ Sceco_STB | 10/15/2025 12:29:40 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/15/2025 12:29:37 | VIP | SRAN | muzamiah | Sceco_STB | DWDM NSA | MZH0527 | FLM_EM | [5 empty] | NE MZH0527_OCS's current GNE has been switched to standby GNE |  |  | API | 10/15/2025 12:31:30 | 10/15/2025 15:51:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251015000677 | PCM-20251015-00001149 | TT-20251015-01218 | EM | Region_4 | KMMD0740 | KMMD0740 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/15/2025 12:35:06 | 10/18/2025 20:17:12 | 10/16/2025 00:35:06 | AIRCON 2 FAILURE at KMMD0740-GSM-P3 @ Sceco | 10/15/2025 12:26:42 | Minor | 7103 | AIRCON 2 FAILURE | 10/15/2025 12:26:33 | P3 | 2G | jeddah | Sceco | 2G NSA | KMMD0740 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/15/2025 12:35:06 | 10/18/2025 20:17:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000739 | PCM-20251015-00001224 | TT-20251015-01291 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/15/2025 12:52:41 | 10/15/2025 13:17:18 | 10/15/2025 18:52:41 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/15/2025 12:42:06 | Major | 65110 | Low battery voltage | 10/15/2025 12:42:03 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/15/2025 12:52:41 | 10/15/2025 13:17:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000747 | PCM-20251015-00001235 | TT-20251015-01311 | EM | Region_4 | JED0153 | JED0153 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/15/2025 13:02:26 | 10/15/2025 15:09:47 | 10/16/2025 01:02:26 | HIGH TEMPERATURE 32 DEGREE C at JED1M7153-CA-L900-L800-SBTS-P3 @ Sceco | 10/15/2025 12:54:03 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/15/2025 12:54:09 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7153 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/15/2025 13:02:26 | 10/15/2025 15:09:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000784 | PCM-20251015-00001291 | TT-20251015-01373 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/15/2025 13:30:50 | 10/15/2025 18:32:56 | 10/16/2025 01:30:50 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/15/2025 13:20:28 | Minor | 65102 | High temperature 32C alarm | 10/15/2025 13:20:26 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/15/2025 13:30:50 | 10/15/2025 18:32:56 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015000792 | PCM-20251015-00001300 | TT-20251015-01386 | EM | Region_6 | MHL0136 | MHL0136 |  |  |  | Zia Ur Rahamn | 10/15/2025 13:38:35 | 10/15/2025 14:25:35 | 10/16/2025 01:38:35 | AIRCON 2 FAILURE at MHL0136-GSM-P3 @ Sceco | 10/15/2025 13:30:09 | Minor | 7103 | AIRCON 2 FAILURE | 10/15/2025 13:30:01 | P3 | 2G | mohail | Sceco | 2G NSA | MHL0136 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/15/2025 13:38:35 | 10/15/2025 14:25:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251015000821 | PCM-20251015-00001337 | TT-20251015-01430 | EM | Region_6 | KMS0039 | KMS0039 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ezat Mohammed | 10/15/2025 14:04:25 | 10/17/2025 20:47:17 | 10/15/2025 18:04:25 | DOOR OPEN/INTRUDER ALARM at KMS0039_IPASO#9 R4 EAST on 10.154.166.17 @ Sceco_STB | 10/15/2025 13:57:55 | Critical | DOOR OPEN/INTRUDER ALARM | DOOR OPEN/INTRUDER ALARM | 10/15/2025 13:58:42 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | KMS0039 | FLM_EM | [8 empty] | API | 10/15/2025 14:04:25 |  | 10/17/2025 20:47:10 |  |  | 10/17/2025 20:47:17 |  | Ezat Mohammed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251015000908 | PCM-20251015-00001482 | TT-20251015-01610 | EM | Region_6 | WDN0187 | WDN0187 |  |  |  | Khalid Frahan Almesetef | 10/15/2025 15:19:20 | 10/15/2025 21:48:13 | 10/15/2025 21:19:20 | HIGH TEMPERATURE 32 DEGREE C at WDN0187-GSM-P1-HUB-USF @ Sceco_STB | 10/15/2025 15:11:04 | Major | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/15/2025 15:10:53 | P1 | 2G | al harja | Sceco_STB | 2G NSA | WDN0187 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/15/2025 15:19:20 | 10/15/2025 21:48:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251015000931 | PCM-20251015-00001517 | TT-20251015-01649 | Reference_EM | Region_1 | ARR0919 | ARR0919 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Ismail Salah Ismail Elbery | 10/15/2025 15:33:23 | 10/22/2025 13:22:03 | 10/15/2025 21:33:23 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/15/2025 15:23:03 | Major | 65110 | Low battery voltage | 10/15/2025 15:22:59 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/15/2025 15:33:23 | 10/15/2025 21:07:29 | 10/22/2025 13:21:57 |  |  | 10/22/2025 13:22:03 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251015000996 | PCM-20251015-00001628 | TT-20251015-01750 | EM | Region_6 | WDN0187 | WDN0187 |  |  |  | Khalid Frahan Almesetef | 10/15/2025 16:28:05 | 10/15/2025 21:48:14 | 10/15/2025 22:28:05 | SHELTER DOOR OPEN at WDN0187-GSM-P1-HUB-USF @ Sceco_STB | 10/15/2025 16:27:36 | Major | 7103 | SHELTER DOOR OPEN | 10/15/2025 16:27:28 | P1 | 2G | al harja | Sceco_STB | 2G NSA | WDN0187 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/15/2025 16:28:05 | 10/15/2025 21:48:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Preparation | CM20251015001057 | PCM-20251015-00001715 | TT-20251015-01826 | EM | Region_1 | DRN2140 | DRN2140 |  |  |  | Omer Elfadoul Mohamed Ibrahim | 10/15/2025 17:12:01 | 10/22/2025 18:49:07 | 10/16/2025 05:12:01 | NETECO: Load Fuse Broken at DRN2140 @ Generator_SG | 10/15/2025 17:05:22 | Minor | 10169 | Load Fuse Broken | 10/15/2025 17:05:22 | P1 | SRAN | dammam | Generator_SG | 2G NSA | DRN2140 | FLM_EM | [8 empty] | API | 10/15/2025 17:12:01 | 10/15/2025 18:06:38 | 10/22/2025 18:49:02 | 10/22/2025 18:49:05 | 10/22/2025 18:49:07 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015001138 | PCM-20251015-00001861 | TT-20251015-01978 | EM | Region_6 | TLT0753 | TLT0753 |  |  |  | Javad Qadir Bukhsh | 10/15/2025 18:29:25 | 10/15/2025 18:56:47 | 10/16/2025 06:29:25 | RECTIFIER MAINS POWER FAILURE at TLT0753-GSM-UMTS-P3 @ Generator_SG | 10/15/2025 18:20:52 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/15/2025 18:20:39 | P3 | 2G | turaib | Generator_SG | 2G NSA | TLT0753 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/15/2025 18:29:25 | 10/15/2025 18:56:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015001171 | PCM-20251015-00001924 | TT-20251015-01720 | Reference_telecom | Region_6 | ARF0191 | ARF0191 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/15/2025 19:12:21 | 10/15/2025 19:23:58 | 10/16/2025 01:12:21 | RNW O&M SCENARIO FAILURE at ARF1M3191-P2 @ Sceco | 10/15/2025 15:39:47 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/15/2025 15:38:53 | P3 | 3G | khamis mushyet | Sceco | 3G NSA | ARF1M3191 | FLM_EM |  |  | PCM-20251015-00001603 | alarm appeared due to power issue | alarm appeared due to power issue |  |  |  | API | 10/15/2025 19:12:21 | 10/15/2025 19:23:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015001173 | PCM-20251015-00001925 | TT-20251015-01718 | Reference_telecom | Region_6 | ARF0072 | ARF0072 |  |  |  | Muhammad Zamir Muhammad Nazir | 10/15/2025 19:12:55 | 10/15/2025 19:23:59 | 10/16/2025 01:12:55 | RNW O&M SCENARIO FAILURE at ARF1M3072-P3 @ Sceco | 10/15/2025 15:39:55 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/15/2025 15:39:03 | P3 | 3G | khamis mushyet | Sceco | 3G NSA | ARF1M3072 | FLM_EM |  |  | PCM-20251015-00001602 | alarm appeared due to power issue | alarm appeared due to power issue |  |  |  | API | 10/15/2025 19:12:55 | 10/15/2025 19:23:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251015001182 | PCM-20251015-00001940 | TT-20251015-02044 | EM | Region_6 | KMS0460 | KMS0460 |  |  |  | Amir Abbas Arif Raza | 10/15/2025 19:21:35 | 10/16/2025 10:55:57 | 10/16/2025 07:21:35 | FIRE ALARM+FIRE ALARM FAILURE at KMS1M7460-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/15/2025 19:13:02 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/15/2025 19:12:58 | P3 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M7460 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | API | 10/15/2025 19:21:35 | 10/16/2025 10:55:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251015001270 | PCM-20251015-00002063 | TT-20251015-02160 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/15/2025 21:08:31 | 10/16/2025 09:49:30 | 10/16/2025 09:08:31 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/15/2025 21:01:44 | Minor | 40564 | Genset Fault | 10/15/2025 21:01:44 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/15/2025 21:08:31 | 10/16/2025 07:57:56 | 10/16/2025 09:49:19 |  |  | 10/16/2025 09:49:30 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251015001308 | PCM-20251015-00002131 | TT-20251015-02242 | EM | Region_4 | JED0804 | JED0804 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/15/2025 22:21:55 | 10/16/2025 13:38:01 | 10/16/2025 10:21:55 | RECTIFIER MODULE FAILURE at JED1M7804-CA-L900-L800-SBTS @ Sceco | 10/15/2025 22:19:55 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/14/2025 07:13:20 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7804 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/15/2025 22:21:55 | 10/16/2025 13:38:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251015001360 | PCM-20251015-00002211 | TT-20251015-02320 | EM | Region_4 | GMK2154 | GMK2154 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Muhammad Rizwan Basharat Hussain | 10/15/2025 23:38:50 | 10/16/2025 23:50:14 | 10/16/2025 11:38:50 | Fire Alarm at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/15/2025 23:30:35 | Minor | 7103 | Fire Alarm | 10/15/2025 23:30:30 | P3 | 2G | jeddah | Generator_SG | 2G NSA | GMK2154 | FLM_EM | [5 empty] | Fire Alarm |  |  | API | 10/15/2025 23:38:50 | 10/16/2025 16:30:55 | 10/16/2025 23:50:03 |  |  | 10/16/2025 23:50:14 |  | Muhammad Rizwan Basharat Hussain |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000043 | PCM-20251016-00000091 | TT-20251016-00099 | EM | Region_4 | NSH0045 | NSH0045 | Equipment | FAN Cleaning | Reset FAN | Basyouni Kotb Basyouni Eldabsha | 10/16/2025 01:16:25 | 10/20/2025 10:17:12 | 10/16/2025 13:16:25 | SHELTER DOOR OPEN at NSH0045-GSM-UMTS-P2-USF @ Generator_SG | 10/16/2025 01:15:52 | Minor | 7103 | SHELTER DOOR OPEN | 10/16/2025 01:15:40 | P2 | 2G | qunfuddah | Generator_SG | 2G NSA | NSH0045 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/16/2025 01:16:25 | 10/16/2025 05:44:51 | 10/20/2025 10:17:06 |  |  | 10/20/2025 10:17:12 |  | Basyouni Kotb Basyouni Eldabsha |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000045 | PCM-20251016-00000096 | TT-20251016-00108 | EM | Region_6 | TNM2720 | TNM2720 |  |  |  | Zia Ur Rahamn | 10/16/2025 01:28:16 | 10/16/2025 11:17:19 | 10/16/2025 13:28:16 | AIRCON 1FAIL at TNM1M8720-CA-L1800-L800-P3 @ Generator_SG | 10/16/2025 01:19:44 | Minor | 7103 | AIRCON 1FAIL | 10/16/2025 01:19:33 | P3 | 4G | mohail | Generator_SG | LTE NSA | TNM1M8720 | FLM_EM | [5 empty] | AIRCON 1FAIL |  |  | API | 10/16/2025 01:28:16 | 10/16/2025 11:17:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000082 | PCM-20251016-00000159 | TT-20251016-00194 | EM | Region_2 | RIY0164 | RIY0164 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:13:16 | 10/19/2025 13:20:16 | 10/16/2025 14:13:16 | Air condition 1 failure alarm at RIY0164-P2_SRAN @ Sceco | 10/16/2025 02:06:10 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:02:47 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0164 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:16 | 10/16/2025 03:15:09 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000083 | PCM-20251016-00000164 | TT-20251016-00199 | EM | Region_2 | RIY0125 | RIY0125 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/16/2025 02:13:20 | 10/18/2025 08:40:29 | 10/16/2025 08:13:20 | Low battery voltage at RIY0125-P1-DIA_SRAN @ Sceco | 10/16/2025 02:06:58 | Major | 65110 | Low battery voltage | 10/16/2025 02:02:53 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0125 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:20 | 10/18/2025 08:40:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000084 | PCM-20251016-00000163 | TT-20251016-00198 | EM | Region_2 | RIY2609 | RIY2609 |  |  |  | Moin Uddin | 10/16/2025 02:13:21 | 10/16/2025 12:36:49 | 10/16/2025 14:13:21 | Air condition 1 failure alarm at RIY2609-P3_SRAN @ Sceco | 10/16/2025 02:08:15 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:02:55 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2609 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:21 | 10/16/2025 12:36:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000086 | PCM-20251016-00000169 | TT-20251016-00203 | EM | Region_2 | RIY0092 | RIY0092 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:13:45 | 10/19/2025 13:20:17 | 10/16/2025 08:13:45 | Air condition 2 failure alarm at RIY0092-P1-DIA_SRAN @ Sceco | 10/16/2025 02:06:22 | Major | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:26 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0092 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:45 | 10/16/2025 03:15:10 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000087 | PCM-20251016-00000168 | TT-20251016-00202 | EM | Region_2 | RIY0126 | RIY0126 |  |  |  | Vignesh Sivakumar Sivakumar | 10/16/2025 02:13:48 | 10/19/2025 13:20:31 | 10/16/2025 08:13:48 | Air condition 1 failure alarm at RIY0126-P1-DIA_SRAN @ Sceco | 10/16/2025 02:04:51 | Major | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:27 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0126 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:48 | 10/16/2025 15:38:18 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000088 | PCM-20251016-00000166 | TT-20251016-00201 | EM | Region_2 | RIY0121 | RIY0121 | Enviroment | Fire Alarm | Reset Fire Pannel | Adel Abdelaziz Mohamed Ayedi | 10/16/2025 02:13:48 | 10/18/2025 15:20:14 | 10/16/2025 08:13:48 | Fire Alarm at RIY0121-P1-DIA_SRAN-FON @ Sceco | 10/16/2025 02:10:21 | Major | 65119 | Fire Alarm | 10/16/2025 02:03:08 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0121 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:48 | 10/16/2025 09:38:08 | 10/18/2025 14:45:59 | 10/18/2025 14:46:02 | 10/18/2025 15:16:02 | 10/18/2025 15:20:14 |  | Adel Abdelaziz Mohamed Ayedi |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251016000089 | PCM-20251016-00000165 | TT-20251016-00200 | EM | Region_2 | RIY0114 | RIY0114 | Enviroment | Fire Alarm | Reset Fire Pannel | Ahmed Khalifa Amin Aboueltaher | 10/16/2025 02:13:49 | 10/16/2025 21:27:25 | 10/16/2025 08:13:49 | Fire Alarm at RIY0114-P1-SHOP_SRAN @ Sceco | 10/16/2025 02:08:13 | Major | 65119 | Fire Alarm | 10/16/2025 02:03:03 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0114 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:49 | 10/16/2025 21:08:25 | 10/16/2025 21:08:55 | 10/16/2025 21:09:02 | 10/16/2025 21:09:12 | 10/16/2025 21:27:25 |  | Ahmed Khalifa Amin Aboueltaher |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000090 | PCM-20251016-00000171 | TT-20251016-00205 | EM | Region_2 | RIY0134 | RIY0134 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:13:51 | 10/19/2025 13:20:18 | 10/16/2025 14:13:51 | Air condition 2 failure alarm at RIY0134-P2_SRAN @ Sceco | 10/16/2025 02:08:32 | Minor | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:11 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0134 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:51 | 10/16/2025 03:15:10 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000092 | PCM-20251016-00000174 | TT-20251016-00208 | EM | Region_2 | RIY0192 | RIY0192 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/16/2025 02:13:53 | 10/19/2025 13:20:23 | 10/16/2025 14:13:53 | Air condition 2 failure alarm at RIY0192-P2_SRAN @ Sceco | 10/16/2025 02:08:51 | Minor | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:08 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0192 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:53 | 10/16/2025 09:38:08 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000091 | PCM-20251016-00000173 | TT-20251016-00207 | EM | Region_2 | RIY0957 | RIY0957 | Enviroment | Fire Alarm | Reset Fire Pannel | Ahmed Khalifa Amin Aboueltaher | 10/16/2025 02:13:53 | 10/16/2025 23:52:53 | 10/16/2025 14:13:53 | Fire Alarm at RIY0957-P2_SRAN @ Sceco | 10/16/2025 02:05:35 | Minor | 65119 | Fire Alarm | 10/16/2025 02:03:16 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0957 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:53 | 10/16/2025 22:18:49 | 10/16/2025 22:19:33 | 10/16/2025 22:19:43 | 10/16/2025 22:21:27 | 10/16/2025 23:52:53 |  | Ahmed Khalifa Amin Aboueltaher |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000093 | PCM-20251016-00000170 | TT-20251016-00204 | EM | Region_2 | RIY0196 | RIY0196 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:13:56 | 10/19/2025 13:20:19 | 10/16/2025 14:13:56 | Air condition 2 failure alarm at RIY0196-P2_SRAN @ Sceco | 10/16/2025 02:08:49 | Minor | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:15 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0196 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:56 | 10/16/2025 03:15:10 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000095 | PCM-20251016-00000175 | TT-20251016-00209 | EM | Region_2 | RIY0173 | RIY0173 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/16/2025 02:13:58 | 10/19/2025 13:20:37 | 10/16/2025 14:13:58 | Air condition 1 failure alarm at RIY0173-P2_SRAN @ Sceco | 10/16/2025 02:08:27 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:02 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0173 | FLM_EM | [8 empty] | API | 10/16/2025 02:13:58 | 10/19/2025 10:24:23 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000096 | PCM-20251016-00000178 | TT-20251016-00212 | EM | Region_2 | RIY2827 | RIY2827 |  |  |  | RANJEET KUMAR YADAV | 10/16/2025 02:14:15 | 10/16/2025 11:59:27 | 10/16/2025 14:14:15 | Fire Fighting system alarm at RIY2827-P2_SRAN @ Generator_SG | 10/16/2025 02:08:01 | Minor | 65111 | Fire Fighting system alarm | 10/16/2025 02:03:56 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2827 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:15 | 10/16/2025 11:59:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000098 | PCM-20251016-00000177 | TT-20251016-00211 | EM | Region_2 | RIY0142 | RIY0142 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:14:18 | 10/19/2025 13:20:20 | 10/16/2025 14:14:18 | Air condition 1 failure alarm at RIY0142-P2_SRAN @ Sceco | 10/16/2025 02:09:21 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:47 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0142 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:18 | 10/16/2025 03:15:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000099 | PCM-20251016-00000179 | TT-20251016-00213 | EM | Region_2 | RIY0221 | RIY0221 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/16/2025 02:14:19 | 10/19/2025 13:20:34 | 10/16/2025 14:14:19 | Air condition 2 failure alarm at RIY0221-P2_SRAN @ Sceco | 10/16/2025 02:08:16 | Minor | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:32 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0221 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:19 | 10/18/2025 08:40:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000100 | PCM-20251016-00000185 | TT-20251016-00219 | EM | Region_2 | RIY2125 | RIY2125 | Enviroment | Fire Alarm | Reset Fire Pannel | Pawan Virdi Santokh Singh | 10/16/2025 02:14:21 | 10/20/2025 17:50:22 | 10/16/2025 14:14:21 | Fire Fighting system alarm at RIY2125-P2_SRAN @ Sceco | 10/16/2025 02:08:34 | Minor | 65111 | Fire Fighting system alarm | 10/16/2025 02:03:45 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2125 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:21 | 10/16/2025 10:05:09 | 10/20/2025 15:49:46 | 10/20/2025 15:49:50 | 10/20/2025 16:47:33 | 10/20/2025 17:50:22 |  | Pawan Virdi Santokh Singh |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000101 | PCM-20251016-00000181 | TT-20251016-00215 | EM | Region_2 | RIY0257 | RIY0257 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/16/2025 02:14:22 | 10/19/2025 13:20:26 | 10/16/2025 14:14:22 | Air condition 1 failure alarm at RIY0257-P2_SRAN @ Sceco | 10/16/2025 02:08:34 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:56 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0257 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:22 | 10/16/2025 13:09:09 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000102 | PCM-20251016-00000182 | TT-20251016-00217 | EM | Region_2 | RIY2063 | RIY2063 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:14:23 | 10/19/2025 13:20:21 | 10/16/2025 14:14:23 | Air condition 2 failure alarm at RIY2063-P2_SRAN @ Sceco | 10/16/2025 02:06:58 | Minor | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:30 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2063 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:23 | 10/16/2025 03:15:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251016000104 | PCM-20251016-00000180 | TT-20251016-00214 | EM | Region_2 | RIY0181 | RIY0181 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/16/2025 02:14:27 | 10/19/2025 13:20:27 | 10/16/2025 14:14:27 | Air condition 1 failure alarm at RIY0181-P2_SRAN @ Sceco | 10/16/2025 02:09:21 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:45 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0181 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:27 | 10/16/2025 13:09:10 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000105 | PCM-20251016-00000184 | TT-20251016-00218 | EM | Region_2 | RIY0185 | RIY0185 | Enviroment | Rectifier Module | Change rectifer module | Mustansar Ali Mushtaq Ahmad | 10/16/2025 02:14:28 | 10/22/2025 12:38:22 | 10/16/2025 14:14:28 | Minor Rec alarm at RIY0185-P2_SRAN @ Sceco | 10/16/2025 02:10:37 | Minor | 65108 | Minor Rec alarm | 10/16/2025 02:03:38 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0185 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:28 | 10/22/2025 12:02:45 | 10/22/2025 12:03:01 | 10/22/2025 12:03:08 | 10/22/2025 12:03:16 | 10/22/2025 12:38:22 |  | Mustansar Ali Mushtaq Ahmad | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000106 | PCM-20251016-00000187 | TT-20251016-00222 | EM | Region_2 | RIY0260 | RIY0260 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/16/2025 02:14:46 | 10/19/2025 13:20:24 | 10/16/2025 14:14:46 | Air condition 1 failure alarm at RIY0260-P2_SRAN @ Sceco | 10/16/2025 02:12:37 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:46 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0260 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:46 | 10/16/2025 09:38:09 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000107 | PCM-20251016-00000188 | TT-20251016-00223 | EM | Region_2 | RIY0244 | RIY0244 |  |  |  | Adham Adham Hassan Farghal | 10/16/2025 02:14:46 | 10/16/2025 12:40:17 | 10/16/2025 08:14:46 | Air condition 2 failure alarm at RIY0244-P1-VIP_SRAN @ Sceco | 10/16/2025 02:08:31 | Major | 65105 | Air condition 2 failure alarm | 10/16/2025 02:04:22 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0244 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:46 | 10/16/2025 12:40:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000108 | PCM-20251016-00000186 | TT-20251016-00221 | EM | Region_2 | RIY2091 | RIY2091 |  |  |  | Vignesh Sivakumar Sivakumar | 10/16/2025 02:14:49 | 10/16/2025 15:38:19 | 10/16/2025 08:14:49 | Fire Fighting system alarm at RIY2091-FWA-P1-VIP_SRAN @ Sceco | 10/16/2025 02:12:29 | Major | 65111 | Fire Fighting system alarm | 10/16/2025 02:03:07 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2091 | FLM_EM | [8 empty] | API | 10/16/2025 02:14:49 | 10/16/2025 15:38:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000111 | PCM-20251016-00000191 | TT-20251016-00225 | EM | Region_2 | RIY0187 | RIY0187 |  |  |  | Kadri Jalal Mohammed Asmail | 10/16/2025 02:15:51 | 10/19/2025 13:20:21 | 10/16/2025 14:15:51 | Air condition 2 failure alarm at RIY0187-P2_SRAN @ Sceco | 10/16/2025 02:13:57 | Minor | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:44 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0187 | FLM_EM | [8 empty] | API | 10/16/2025 02:15:51 | 10/16/2025 03:15:12 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000114 | PCM-20251016-00000193 | TT-20251016-00227 | EM | Region_2 | RIY0174 | RIY0174 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/16/2025 02:16:20 | 10/19/2025 13:20:29 | 10/16/2025 14:16:20 | Air condition 1 failure alarm at RIY0174-P2_SRAN @ Sceco | 10/16/2025 02:14:19 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:03:21 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0174 | FLM_EM | [8 empty] | API | 10/16/2025 02:16:20 | 10/16/2025 13:09:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000115 | PCM-20251016-00000198 | TT-20251016-00232 | EM | Region_2 | RIY0256 | RIY0256 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/16/2025 02:16:51 | 10/19/2025 13:20:30 | 10/16/2025 14:16:51 | Air condition 1 failure alarm at RIY0256-P2_SRAN @ Sceco | 10/16/2025 02:14:17 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 02:06:14 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0256 | FLM_EM | [8 empty] | API | 10/16/2025 02:16:51 | 10/16/2025 13:09:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000116 | PCM-20251016-00000197 | TT-20251016-00231 | EM | Region_2 | RIY0139 | RIY0139 |  |  |  | Vignesh Sivakumar Sivakumar | 10/16/2025 02:16:51 | 10/16/2025 15:38:19 | 10/16/2025 08:16:51 | Air condition 2 failure alarm at RIY0139-P1-VIP-SHOP-HUB_SRAN-FON @ Sceco | 10/16/2025 02:14:42 | Major | 65105 | Air condition 2 failure alarm | 10/16/2025 02:03:40 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0139 | FLM_EM | [8 empty] | API | 10/16/2025 02:16:51 | 10/16/2025 15:38:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251016000117 | PCM-20251016-00000199 | TT-20251016-00234 | EM | Region_2 | RIY2482 | RIY2482 |  |  |  | Moin Uddin | 10/16/2025 02:17:21 | 10/16/2025 12:36:49 | 10/16/2025 14:17:21 | NETECO: BMU Missing at RIY2482 @ Generator_SG | 10/16/2025 02:10:58 | Minor | 13821 | BMU Missing | 10/16/2025 02:10:58 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2482 | FLM_EM | [8 empty] | API | 10/16/2025 02:17:21 | 10/16/2025 12:36:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000120 | PCM-20251016-00000205 | TT-20251016-00240 | EM | Region_2 | RIY2558 | RIY2558 |  |  |  | Pawan Virdi Santokh Singh | 10/16/2025 02:17:55 | 10/16/2025 10:05:09 | 10/16/2025 14:17:55 | Mains Failure at RIY2558-P3_SRAN-PC @ Sceco | 10/16/2025 02:14:44 | Minor | 65109 | Mains Failure | 10/16/2025 02:07:52 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2558 | FLM_EM | [8 empty] | API | 10/16/2025 02:17:55 | 10/16/2025 10:05:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000121 | PCM-20251016-00000203 | TT-20251016-00241 | EM | Region_2 | RIY2570 | RIY2570 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/16/2025 02:17:57 | 10/19/2025 10:24:24 | 10/16/2025 14:17:57 | Mains Failure at RIY2570-P3_SRAN-PC @ Sceco | 10/16/2025 02:15:37 | Minor | 65109 | Mains Failure | 10/16/2025 02:07:41 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2570 | FLM_EM | [8 empty] | API | 10/16/2025 02:17:57 | 10/19/2025 10:24:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000123 | PCM-20251016-00000210 | TT-20251016-00246 | EM | Region_2 | RIY2508 | RIY2508 | Enviroment | Rectifier_Fault | Change Rectifier controller | Adham Adham Hassan Farghal | 10/16/2025 02:18:25 | 10/18/2025 12:21:32 | 10/16/2025 14:18:25 | Fire Fighting system alarm at RIY2508-P3_SRAN-PC @ Sceco | 10/16/2025 02:09:21 | Minor | 65111 | Fire Fighting system alarm | 10/16/2025 02:07:37 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2508 | FLM_EM | [8 empty] | API | 10/16/2025 02:18:25 | 10/16/2025 12:40:18 | 10/18/2025 11:18:06 | 10/18/2025 11:18:13 | 10/18/2025 11:18:38 | 10/18/2025 12:21:32 |  | Adham Adham Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000125 | PCM-20251016-00000211 | TT-20251016-00247 | EM | Region_2 | RIY0090 | RIY0090 | Enviroment | SCECO_Failure | SCECO auto restored | Kadri Jalal Mohammed Asmail | 10/16/2025 02:18:55 | 10/18/2025 10:43:39 | 10/16/2025 14:18:55 | Mains Failure at RIY0090-P3_SRAN @ Sceco | 10/16/2025 02:13:42 | Minor | 65109 | Mains Failure | 10/16/2025 02:08:27 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY0090 | FLM_EM | [8 empty] | API | 10/16/2025 02:18:55 | 10/16/2025 03:15:12 | 10/18/2025 10:35:59 | 10/18/2025 10:36:23 | 10/18/2025 10:36:40 | 10/18/2025 10:43:39 |  | Kadri Jalal Mohammed Asmail |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000126 | PCM-20251016-00000212 | TT-20251016-00248 | EM | Region_2 | RIY2788 | RIY2788 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/16/2025 02:18:57 | 10/19/2025 10:24:25 | 10/16/2025 14:18:57 | Mains Failure at RIY2788-P3_SRAN-PC @ Sceco | 10/16/2025 02:14:24 | Minor | 65109 | Mains Failure | 10/16/2025 02:08:30 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2788 | FLM_EM | [8 empty] | API | 10/16/2025 02:18:57 | 10/19/2025 10:24:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000135 | PCM-20251016-00000236 | TT-20251016-00306 | EM | Region_4 | JED0125 | JED0125 |  |  |  | AbdAllah Mohammad abd Elgawad Fath Elbab | 10/16/2025 02:47:41 | 10/16/2025 10:05:43 | 10/16/2025 06:47:41 | ALL POWER ALARMS AT JED0125 NCE | 10/16/2025 02:44:20 | Critical | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/16/2025 02:44:20 | P1 | 2G | jeddah | Generator_SG | DWDM NSA | JED0125 | FLM_EM | [8 empty] | API | 10/16/2025 02:47:41 | 10/16/2025 10:05:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Reject_FME | CM20251016000145 | PCM-20251016-00000256 | TT-20251016-00325 | EM | Region_4 | JED0223 | JED0223 |  |  |  | Hussein Sayed Salama Hussein | 10/16/2025 03:01:51 | 10/17/2025 21:21:13 | 10/16/2025 09:01:51 | RECTIFIER MAINS POWER FAILURE at JED1M7223-P1-HUB-CA-L900-L800-SBTS @ Sceco_STB | 10/16/2025 02:53:10 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/16/2025 02:53:06 | P1 | 4G | jeddah | Sceco_STB | LTE NSA | JED1M7223 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/16/2025 03:01:51 | 10/16/2025 12:17:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000221 | PCM-20251016-00000450 | TT-20251016-00518 | EM | Region_4 | BIK0155 | BIK0155 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/16/2025 04:38:56 | 10/18/2025 14:49:07 | 10/16/2025 16:38:56 | RECTIFIER MAINS POWER FAILURE at BIK0155-GSM-UMTS-P3 @ Generator_SG | 10/16/2025 04:30:35 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/16/2025 04:30:25 | P3 | 2G | alaith | Generator_SG | 2G NSA | BIK0155 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/16/2025 04:38:56 | 10/18/2025 14:49:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000230 | PCM-20251016-00000464 | TT-20251016-00530 | EM | Region_4 | QUZ0738 | QUZ0738 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/16/2025 04:52:56 | 10/16/2025 08:54:07 | 10/16/2025 16:52:56 | RECTIFIER MODULE FAILURE at QUZ1M7738-P3-CA-L800 @ Sceco | 10/16/2025 04:44:22 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 04:44:11 | P2 | 4G | qunfuddah | Sceco | LTE NSA | QUZ1M7738 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 04:52:56 | 10/16/2025 08:54:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000239 | PCM-20251016-00000513 | TT-20251016-00575 | EM | Region_4 | JED2333 | JED2333 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/16/2025 05:17:41 | 10/17/2025 04:55:20 | 10/16/2025 17:17:41 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/16/2025 05:09:02 | Minor | 7103 | AIRCON 1 FAILURE | 10/16/2025 05:08:56 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/16/2025 05:17:41 | 10/16/2025 10:57:16 | 10/17/2025 04:55:10 |  |  | 10/17/2025 04:55:20 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000262 | PCM-20251016-00000558 | TT-20251016-00528 | Reference_telecom | Region_4 | JED0145 | JED0145 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/16/2025 05:53:16 | 10/19/2025 12:47:16 | 10/16/2025 17:53:16 | JED1W0145 Complete down (REF:CRQ000000534621) | 10/16/2025 03:35:21 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/16/2025 03:35:21 | P2 | 2G | jeddah | Sceco | Wifi SA | JED1W0145 | FLM_EM |  | JED0145 | PCM-20251016-00000556 | power issue | power issue |  |  |  | API | 10/16/2025 05:53:16 | 10/16/2025 13:05:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251016000269 | PCM-20251016-00000598 | TT-20251016-00660 | Reference_EM | Region_2 | RIY0285 | RIY0285 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Adham Adham Hassan Farghal | 10/16/2025 06:01:00 | 10/18/2025 11:08:52 | 10/16/2025 12:01:00 | Door opening alarm at RIY0285-P1-VIP_SRAN @ Sceco | 10/16/2025 02:09:21 | Major | 65101 | Door opening alarm | 10/16/2025 02:04:25 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0285 | FLM_EM | [8 empty] | API | 10/16/2025 06:01:00 | 10/16/2025 12:40:19 | 10/18/2025 10:17:18 | 10/18/2025 10:17:23 |  | 10/18/2025 11:08:52 |  | Adham Adham Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000274 | PCM-20251016-00000608 | TT-20251016-00670 | EM | Region_6 | SAB0060 | SAB0060 |  |  |  | Khurram Nawaz Muhammad Akram | 10/16/2025 06:07:16 | 10/16/2025 12:06:25 | 10/16/2025 12:07:16 | SHELTER DOOR OPEN at SAB1M7060-P1-HUB-CA-L800 @ Sceco_STB | 10/16/2025 06:06:51 | Major | 7103 | SHELTER DOOR OPEN | 10/16/2025 06:06:43 | P1 | 4G | baish | Sceco_STB | LTE NSA | SAB1M7060 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/16/2025 06:07:16 | 10/16/2025 12:06:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251016000375 | PCM-20251016-00000783 | TT-20251016-00810 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/16/2025 07:45:26 | 10/16/2025 10:50:22 | 10/16/2025 19:45:26 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/16/2025 07:34:52 | Minor | 65102 | high temprature 32 | 10/16/2025 07:34:48 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/16/2025 07:45:26 | 10/16/2025 10:50:22 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000391 | PCM-20251016-00000807 | TT-20251016-00766 | Telecom | Region_2 | RIY0233 | RIY0233 |  |  |  | Adham Adham Hassan Farghal | 10/16/2025 07:58:51 | 10/16/2025 12:40:19 | 10/16/2025 13:58:51 | Fan Stalled at RIY0233-P2_SRAN @ Sceco | 10/16/2025 02:11:44 | Major | 25673 | Fan Stalled | 10/16/2025 02:03:41 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0233 | FLM_EM |  |  | PCM-20251016-00000717 | Alarm due to door open as Mini shelter AC not working , Door open , Under EM | Alarm due to door open as Mini shelter AC not working , Door open , Under EM |  |  |  | API | 10/16/2025 07:58:51 | 10/16/2025 12:40:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000404 | PCM-20251016-00000846 | TT-20251016-00866 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/16/2025 08:24:40 | 10/22/2025 17:49:40 | 10/16/2025 20:24:40 | high temprature 32 at RIY0349-P2_SRAN @ Sceco | 10/16/2025 08:14:05 | Minor | 65102 | high temprature 32 | 10/16/2025 08:14:00 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/16/2025 08:24:40 | 10/22/2025 17:49:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000470 | PCM-20251016-00001000 | TT-20251016-01007 | EM | Region_4 | JDRS0764 | JDRS0764 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/16/2025 09:32:50 | 10/16/2025 12:50:12 | 10/16/2025 21:32:50 | HIGH TEMPERATURE 32 DEGREE C at JDRS1M7764-G9-NL8-L18-NL21-SBTS-P2-USF @ Sceco | 10/16/2025 09:26:05 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/16/2025 09:24:07 | P2 | 4G | jeddah | Sceco | LTE NSA | JDRS1M7764 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/16/2025 09:32:50 | 10/16/2025 12:50:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000489 | PCM-20251016-00001032 | TT-20251016-01058 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/16/2025 09:52:00 | 10/16/2025 12:40:20 | 10/16/2025 15:52:00 | high temprature 40 at RIY0232-P1_SRAN @ Sceco | 10/16/2025 09:41:26 | Major | 65103 | high temprature 40 | 10/16/2025 09:41:23 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/16/2025 09:52:00 | 10/16/2025 12:40:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000507 | PCM-20251016-00001058 | TT-20251016-00999 | Telecom | Region_4 | HAW0300 | HAW0300 |  |  |  | Ragb Ahmed Mohamed Abdelazim | 10/16/2025 10:07:25 | 10/18/2025 10:07:11 | 10/16/2025 22:07:25 | BASE STATION HARDWARE PROBLEM (RU input voltage Low) at HAW0300-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Generator_SG | 10/16/2025 09:19:33 | Minor | 7100 | BASE STATION HARDWARE PROBLEM | 10/16/2025 09:19:24 | P2 | 2G | taif | Generator_SG | 2G NSA | HAW0300 | FLM_EM |  |  | PCM-20251016-00000995 | impacted due to load issue | impacted due to load issue |  |  |  | API | 10/16/2025 10:07:25 | 10/18/2025 10:07:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251016000519 | PCM-20251016-00001078 | TT-20251016-01118 | EM | Region_4 | HAW2414 | HAW2414 | Enviroment | SCECO_Failure | SCECO auto restored | Waheed Ullah Said Haleem | 10/16/2025 10:17:16 | 10/22/2025 11:06:34 | 10/16/2025 22:17:16 | RECTIFIER MODULE FAILURE at HAW1M8414-G9-L18-SBTS-P2 @ Generator_SG | 10/16/2025 10:08:46 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 10:08:38 | P2 | 4G | taif | Generator_SG | LTE NSA | HAW1M8414 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 10:17:16 | 10/16/2025 13:31:16 | 10/22/2025 11:06:23 |  |  | 10/22/2025 11:06:34 |  | Waheed Ullah Said Haleem |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000548 | PCM-20251016-00001130 | TT-20251016-01173 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/16/2025 10:46:11 | 10/16/2025 17:24:19 | 10/16/2025 22:46:11 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/16/2025 10:35:54 | Minor | 65102 | high temprature 32 | 10/16/2025 10:35:49 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/16/2025 10:46:11 | 10/16/2025 17:24:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000556 | PCM-20251016-00001141 | TT-20251016-01181 | EM | Region_4 | JED2998 | JED2998 |  |  |  | Amer Attallah Awadallah | 10/16/2025 10:49:21 | 10/17/2025 05:59:49 | 10/16/2025 22:49:21 | SHELTER DOOR OPEN at JED2998-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/16/2025 10:48:39 | Minor | 7103 | SHELTER DOOR OPEN | 10/16/2025 10:48:32 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2998 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/16/2025 10:49:21 | 10/17/2025 05:59:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016000593 | PCM-20251016-00001208 | TT-20251016-01248 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/16/2025 11:17:40 | 10/17/2025 13:12:49 | 10/16/2025 15:17:40 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/16/2025 11:15:51 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/16/2025 11:15:43 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 2-TO HFR0502(2-A) |  |  | API | 10/16/2025 11:17:40 | 10/16/2025 12:14:59 | 10/17/2025 13:12:39 |  |  | 10/17/2025 13:12:49 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251016000601 | PCM-20251016-00001224 | TT-20251016-01264 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/16/2025 11:23:26 | 10/16/2025 16:09:11 | 10/16/2025 23:23:26 | Generator failure at SMN0805-P3_SRAN @ Generator_DG | 10/16/2025 11:15:02 | Minor | 65114 | Generator failure | 10/16/2025 11:12:41 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/16/2025 11:23:26 | 10/16/2025 16:09:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000633 | PCM-20251016-00001266 | TT-20251016-01309 | EM | Region_4 | RAB0660 | RAB0660 |  |  |  | Alaa Hassan Mohammed Gad | 10/16/2025 11:47:40 | 10/16/2025 18:58:29 | 10/16/2025 23:47:40 | AIRCON 1 FAILURE at RAB0660-GSM-P2-USF @ Sceco | 10/16/2025 11:39:18 | Minor | 7103 | AIRCON 1 FAILURE | 10/16/2025 11:39:14 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/16/2025 11:47:40 | 10/16/2025 18:58:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251016000636 | PCM-20251016-00001270 | TT-20251016-01313 | EM | Region_4 | JED0007 | JED0007 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/16/2025 11:49:46 | 10/16/2025 11:49:47 | 10/16/2025 17:49:46 | RECTIFIER MODULE FAILURE at JED1M7007-P1-DIA-CA-L900-L800 @ Sceco | 10/16/2025 11:41:16 | Major | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 11:41:05 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7007 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 11:49:46 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000640 | PCM-20251016-00001274 | TT-20251016-01340 | EM | Region_4 | KMMD0751 | KMMD0751 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/16/2025 11:51:15 | 10/18/2025 20:17:13 | 10/16/2025 23:51:15 | AIRCON 2 FAILURE at KMMD0751-GSM-P3 @ Sceco | 10/16/2025 11:42:41 | Minor | 7103 | AIRCON 2 FAILURE | 10/16/2025 11:42:37 | P3 | 2G | jeddah | Sceco | 2G NSA | KMMD0751 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/16/2025 11:51:15 | 10/18/2025 20:17:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000641 | PCM-20251016-00001276 | TT-20251016-01342 | EM | Region_4 | KMMD0719 | KMMD0719 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/16/2025 11:51:50 | 10/18/2025 20:17:14 | 10/16/2025 23:51:50 | RECTIFIER MODULE FAILURE at KMMD0719-GSM-P3 @ Sceco | 10/16/2025 11:43:28 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 11:43:17 | P3 | 2G | jeddah | Sceco | 2G NSA | KMMD0719 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 11:51:50 | 10/18/2025 20:17:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251016000751 | PCM-20251016-00001441 | TT-20251016-01528 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/16/2025 13:04:11 | 10/16/2025 13:33:47 | 10/16/2025 19:04:11 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/16/2025 12:53:36 | Major | 65110 | Low battery voltage | 10/16/2025 12:53:31 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/16/2025 13:04:11 | 10/16/2025 13:33:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000824 | PCM-20251016-00001593 | TT-20251016-01682 | Reference_EM | Region_1 | KBR0608 | KBR0608 |  |  |  | Abdul Malik Shaik | 10/16/2025 14:09:46 | 10/16/2025 17:24:20 | 10/17/2025 02:09:46 | Air condition 1 failure alarm at KBR0608-P3_SRAN @ Sceco | 10/16/2025 13:59:08 | Minor | 65104 | Air condition 1 failure alarm | 10/16/2025 13:59:06 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0608 | FLM_EM | [8 empty] | API | 10/16/2025 14:09:46 | 10/16/2025 17:24:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000941 | PCM-20251016-00001775 | TT-20251016-01862 | EM | Region_4 | JED0379 | JED0379 |  |  |  | Amer Attallah Awadallah | 10/16/2025 15:32:56 | 10/17/2025 05:59:50 | 10/16/2025 21:32:56 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M7379-P1-VIP-CA-L800 @ Sceco | 10/16/2025 15:24:31 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/16/2025 15:24:23 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1M7379 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/16/2025 15:32:56 | 10/17/2025 05:59:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016000993 | PCM-20251016-00001855 | TT-20251016-01933 | EM | Region_6 | SAB0060 | SAB0060 |  |  |  | Khurram Nawaz Muhammad Akram | 10/16/2025 16:01:50 | 10/16/2025 17:14:28 | 10/16/2025 22:01:50 | AIRCON 1 FAILURE at SAB1M7060-P1-HUB-CA-L800 @ Sceco_STB | 10/16/2025 15:53:31 | Major | 7103 | AIRCON 1 FAILURE | 10/16/2025 15:53:22 | P1 | 4G | baish | Sceco_STB | LTE NSA | SAB1M7060 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/16/2025 16:01:50 | 10/16/2025 17:14:28 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251016001071 | PCM-20251016-00001985 | TT-20251016-02050 | EM | Region_4 | TURY0826 | TURY0826 |  |  |  | Afzal Hussain Anwar Ul Haq | 10/16/2025 17:07:56 | 10/18/2025 10:52:11 | 10/17/2025 05:07:56 | RECTIFIER MODULE FAILURE at TURY0826-GSM-P2 @ Sceco | 10/16/2025 17:01:11 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/16/2025 16:59:39 | P2 | 2G | taif | Sceco | 2G NSA | TURY0826 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/16/2025 17:07:56 | 10/18/2025 10:52:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016001089 | PCM-20251016-00002019 | TT-20251016-02080 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/16/2025 17:24:01 | 10/22/2025 13:22:20 | 10/17/2025 05:24:01 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/16/2025 17:17:18 | Minor | 40564 | Genset Fault | 10/16/2025 17:17:18 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/16/2025 17:24:01 | 10/16/2025 21:22:29 | 10/22/2025 13:22:14 |  |  | 10/22/2025 13:22:20 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016001098 | PCM-20251016-00002034 | TT-20251016-02097 | EM | Region_4 | JED2298 | JED2298 |  |  |  | Sajid Nazir Muhammad Nazir | 10/16/2025 17:32:15 | 10/16/2025 17:58:11 | 10/17/2025 05:32:15 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at JED1M8298-CA-L800-P3 @ Sceco | 10/16/2025 17:23:35 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/16/2025 17:23:27 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8298 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/16/2025 17:32:15 | 10/16/2025 17:58:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016001143 | PCM-20251016-00002098 | TT-20251016-02157 | EM | Region_2 | WDS9020 | WDS9020 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sher Zamin Nasib Muhammad | 10/16/2025 18:09:55 | 10/21/2025 07:51:49 | 10/16/2025 22:09:55 | RELAY_ALARM_CRITICAL at WDS9020_NE_1 @ Power cube | 10/15/2025 14:16:54 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/16/2025 18:04:12 | P3 | Repeater | aflaj | Power Cube | TX NSA | WDS9020_NE_1 | FLM_EM | [5 empty] | RELAY_ALARM_CRITICAL at WDS9020_NE_1 @ Power cube |  |  | API | 10/16/2025 18:09:55 | 10/20/2025 06:00:19 | 10/21/2025 07:51:33 |  |  | 10/21/2025 07:51:49 |  | Sher Zamin Nasib Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Accept | CM20251016001146 | PCM-20251016-00002105 | TT-20251016-02166 | Reference_EM | Region_1 | DMH0606 | DMH0606 |  |  |  | Shaker Saied Mohamed ElShafie | 10/16/2025 18:16:11 | 10/19/2025 19:22:39 | 10/17/2025 00:16:11 | Minor Rec alarm at DMH0606-P1-HUB_SRAN @ Generator_SG | 10/16/2025 18:05:51 | Major | 65108 | Minor Rec alarm | 10/16/2025 18:05:45 | P1 | SRAN | hafr | Generator_SG | 2G NSA | DMH0606 | FLM_EM | [8 empty] | API | 10/16/2025 18:16:11 | 10/19/2025 19:21:17 | 10/19/2025 19:22:39 | [8 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251016001218 | PCM-20251016-00002224 | TT-20251016-01631 | Reference_telecom | Region_2 | RYQ0957 | RYQ0957 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/16/2025 19:55:21 | 10/19/2025 07:44:28 | 10/17/2025 07:55:21 | External Clock Reference Problem at RYQ0957-P2_SRAN @ Sceco | 10/16/2025 10:56:17 | Minor | 26262 | External Clock Reference Problem | 10/16/2025 10:52:36 | P2 | SRAN | majma | Sceco | 2G NSA | RYQ0957 | FLM_EM |  | Dear Team, Hub:- RYQ0957 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251016-00002222 | Dear Team, Hub:- RYQ0957 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- RYQ0957 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/16/2025 19:55:21 | 10/18/2025 08:26:23 | 10/19/2025 07:44:20 |  |  | 10/19/2025 07:44:28 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251016001306 | PCM-20251016-00002373 | TT-20251016-02458 | EM | Region_6 | BCH0080 | BCH0080 |  |  |  | Sohail Nasir Mir Afzal | 10/16/2025 22:11:41 | 10/19/2025 05:52:19 | 10/17/2025 10:11:41 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at BCH0080-G9-NL8-L9-NL18-NR2.6-SBTS-P3 @ Sceco | 10/16/2025 22:03:20 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/16/2025 22:02:59 | P3 | 2G | Albaha | Sceco | 2G NSA | BCH0080 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/16/2025 22:11:41 | 10/19/2025 05:52:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251016001328 | PCM-20251016-00002404 | TT-20251016-02486 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/16/2025 22:49:55 | 10/17/2025 12:45:04 | 10/17/2025 10:49:55 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/16/2025 22:43:20 | Minor | 40564 | Genset Fault | 10/16/2025 22:43:20 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/16/2025 22:49:55 | 10/17/2025 12:27:57 | 10/17/2025 12:44:50 |  |  | 10/17/2025 12:45:04 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251017000318 | PCM-20251017-00000545 | TT-20251017-00553 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/17/2025 08:35:46 | 10/18/2025 11:08:26 | 10/17/2025 20:35:46 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/17/2025 08:25:18 | Minor | 65102 | high temprature 32 | 10/17/2025 08:25:15 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/17/2025 08:35:46 | 10/18/2025 11:08:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000319 | PCM-20251017-00000547 | TT-20251017-00554 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/17/2025 08:37:20 | 10/22/2025 17:49:40 | 10/17/2025 20:37:20 | high temprature 32 at RIY0349-P2_SRAN @ Sceco | 10/17/2025 08:26:48 | Minor | 65102 | high temprature 32 | 10/17/2025 08:26:45 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/17/2025 08:37:20 | 10/22/2025 17:49:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000331 | PCM-20251017-00000569 | TT-20251017-00577 | Reference_EM | Region_1 | JBKH2154 | JBKH2154 | Enviroment | Genset failure_EFC Frequency | Adjust Fuel pump | Imran Qamar Ghulam Qamar | 10/17/2025 08:55:55 | 10/17/2025 12:43:52 | 10/17/2025 20:55:55 | Mains Failure at JBKH2154-P2-USF_SRAN @ Generator_SG | 10/17/2025 08:45:34 | Minor | 65109 | Mains Failure | 10/17/2025 08:45:30 | P2 | SRAN | hafr | Generator_SG | 2G NSA | JBKH2154 | FLM_EM | [8 empty] | API | 10/17/2025 08:55:55 | 10/17/2025 12:27:58 | 10/17/2025 12:29:35 | 10/17/2025 12:29:39 | 10/17/2025 12:29:43 | 10/17/2025 12:43:52 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251017000336 | PCM-20251017-00000574 | TT-20251017-00584 | Reference_EM | Region_2 | KHJ0469 | KHJ0469 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/17/2025 08:59:30 | 10/20/2025 14:40:46 | 10/17/2025 20:59:30 | High temperature 32C alarm at KHJ2M1469-P3 @ Sceco | 10/17/2025 08:48:47 | Minor | 65102 | High temperature 32C alarm | 10/17/2025 08:48:46 | P3 | 2G | al kharj | Sceco | 2G NSA | KHJ2M1469 | FLM_EM | [8 empty] | API | 10/17/2025 08:59:30 | 10/20/2025 14:40:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000358 | PCM-20251017-00000604 | TT-20251017-00604 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/17/2025 09:29:00 | 10/18/2025 16:43:23 | 10/17/2025 21:29:00 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/17/2025 09:18:17 | Minor | 65102 | high temprature 32 | 10/17/2025 09:18:14 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/17/2025 09:29:00 | 10/18/2025 16:43:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251017000396 | PCM-20251017-00000665 | TT-20251017-00674 | EM | Region_4 | JED2333 | JED2333 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Abd EL Azeez EL Sayed Soliman | 10/17/2025 10:35:06 | 10/17/2025 14:46:06 | 10/17/2025 22:35:06 | AIRCON 1 FAILURE at JED1M8333-P3-CA-L800 @ Generator_SG | 10/17/2025 10:26:59 | Minor | 7103 | AIRCON 1 FAILURE | 10/17/2025 10:26:30 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8333 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/17/2025 10:35:06 | 10/17/2025 11:35:41 | 10/17/2025 14:45:54 |  |  | 10/17/2025 14:46:06 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000404 | PCM-20251017-00000681 | TT-20251017-00695 | EM | Region_4 | JED0449 | JED0449 | Enviroment | Rectifier Module | Adding module due to load issue | Amr Sherif Gabber Ahmed | 10/17/2025 10:53:41 | 10/19/2025 20:54:37 | 10/17/2025 22:53:41 | Generator Failure at JED1M7449-CA-L800-P3-SBTS @ Generator_SG | 10/17/2025 10:45:11 | Minor | 7103 | Generator Failure | 10/17/2025 10:45:04 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M7449 | FLM_EM | [5 empty] | Generator Failure |  |  | API | 10/17/2025 10:53:41 | 10/18/2025 19:13:18 | 10/19/2025 20:54:29 |  |  | 10/19/2025 20:54:37 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000413 | PCM-20251017-00000708 | TT-20251017-00709 | EM | Region_4 | TAF0312 | TAF0312 | Enviroment | SCECO_Failure | SCECO auto restored | Farghal Ashour Hassan Farghal | 10/17/2025 11:07:11 | 10/19/2025 11:13:51 | 10/17/2025 23:07:11 | FIRE ALARM+FIRE ALARM FAILURE at TAF0312-G9-L8-L18-L21-NR2.6-P2-SBTS @ Sceco | 10/17/2025 10:58:30 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/17/2025 10:58:25 | P2 | 2G | taif | Sceco | 2G NSA | TAF0312 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | API | 10/17/2025 11:07:11 | 10/17/2025 13:19:10 | 10/19/2025 11:13:34 |  |  | 10/19/2025 11:13:51 |  | Farghal Ashour Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000431 | PCM-20251017-00000738 | TT-20251017-00724 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/17/2025 11:26:15 | 10/17/2025 14:38:25 | 10/17/2025 23:26:15 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/17/2025 11:15:57 | Minor | 65102 | high temprature 32 | 10/17/2025 11:15:53 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/17/2025 11:26:15 | 10/17/2025 14:38:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Accept | CM20251017000435 | PCM-20251017-00000746 | TT-20251017-00734 | EM | Region_4 | JED0244 | JED0244 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/17/2025 11:34:00 | 10/18/2025 13:53:46 | 10/17/2025 17:34:00 | AIRCON 1 FAILURE at JED1M7244-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/17/2025 11:25:34 | Major | 7103 | AIRCON 1 FAILURE | 10/17/2025 11:25:21 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7244 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/17/2025 11:34:00 | 10/17/2025 14:01:57 | 10/18/2025 13:53:46 | [8 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000442 | PCM-20251017-00000756 | TT-20251017-00753 | EM | Region_4 | NSH0045 | NSH0045 | Equipment | FAN Cleaning | Reset FAN | Basyouni Kotb Basyouni Eldabsha | 10/17/2025 11:47:26 | 10/20/2025 10:17:36 | 10/17/2025 23:47:26 | SHELTER DOOR OPEN at NSH0045-GSM-UMTS-P2-USF @ Generator_SG | 10/17/2025 11:46:48 | Minor | 7103 | SHELTER DOOR OPEN | 10/17/2025 11:46:39 | P2 | 2G | qunfuddah | Generator_SG | 2G NSA | NSH0045 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/17/2025 11:47:26 | 10/20/2025 09:13:42 | 10/20/2025 10:17:28 |  |  | 10/20/2025 10:17:36 |  | Basyouni Kotb Basyouni Eldabsha |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000462 | PCM-20251017-00000788 | TT-20251017-00777 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/17/2025 12:11:40 | 10/20/2025 12:03:59 | 10/17/2025 16:11:40 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/17/2025 12:09:50 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/17/2025 12:09:44 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 2-TO HFR0502(2-A) |  |  | API | 10/17/2025 12:11:40 | 10/17/2025 13:12:30 | 10/20/2025 12:03:47 |  |  | 10/20/2025 12:03:59 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251017000467 | PCM-20251017-00000795 | TT-20251017-00785 | EM | Region_1 | KBR0608 | KBR0608 |  |  |  | Abdul Malik Shaik | 10/17/2025 12:17:26 | 10/17/2025 14:38:26 | 10/18/2025 00:17:26 | NETECO: DIN4 Alarm at KBR0608 @ Sceco | 10/17/2025 12:10:40 | Minor | 21942 | DIN4 Alarm | 10/17/2025 12:10:40 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0608 | FLM_EM | [8 empty] | API | 10/17/2025 12:17:26 | 10/17/2025 14:38:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000488 | PCM-20251017-00000828 | TT-20251017-00816 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/17/2025 12:37:01 | 10/17/2025 14:17:02 | 10/18/2025 00:37:01 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/17/2025 12:26:26 | Minor | 65102 | High temperature 32C alarm | 10/17/2025 12:26:20 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/17/2025 12:37:01 | 10/17/2025 14:17:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000490 | PCM-20251017-00000830 | TT-20251017-00818 | EM | Region_4 | JED2069 | JED2069 | Enviroment | SCECO_Failure | SCECO auto restored | Amr Sherif Gabber Ahmed | 10/17/2025 12:39:35 | 10/19/2025 20:53:06 | 10/18/2025 00:39:35 | RECTIFIER MODULE FAILURE at JED1M8069-L800-CA-SBTS-P3 @ Generator_SG | 10/17/2025 12:33:47 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/17/2025 12:30:51 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8069 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/17/2025 12:39:35 | 10/18/2025 19:13:19 | 10/19/2025 20:52:58 |  |  | 10/19/2025 20:53:06 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000539 | PCM-20251017-00000897 | TT-20251017-00901 | Reference_EM | Region_1 | ARR0919 | ARR0919 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/17/2025 13:34:57 | 10/22/2025 13:22:40 | 10/17/2025 19:34:57 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/17/2025 13:24:34 | Major | 65110 | Low battery voltage | 10/17/2025 13:24:29 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/17/2025 13:34:57 | 10/17/2025 17:41:46 | 10/22/2025 13:22:32 |  |  | 10/22/2025 13:22:40 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251017000622 | PCM-20251017-00001020 | TT-20251017-01025 | EM | Region_4 | JED0707 | JED0707 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/17/2025 14:53:55 | 10/18/2025 12:13:26 | 10/18/2025 02:53:55 | RECTIFIER MODULE FAILURE at JED0707-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/17/2025 14:45:19 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/17/2025 14:45:08 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0707 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/17/2025 14:53:55 | 10/18/2025 12:13:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000647 | PCM-20251017-00001058 | TT-20251017-01069 | Telecom | Region_1 | DAM2M8710 | DAM2710 | Equipment | BTS_Cable | Replace CPRI Cable | Shakeel Ahmed Hafeez Ameen | 10/17/2025 15:21:40 | 10/17/2025 18:26:00 | 10/17/2025 21:21:40 | Cell Unavailable at DAM2M8710-P2-L800 @ Sceco | 10/17/2025 15:21:04 | Major | 29240 | Cell Unavailable | 10/17/2025 15:19:30 | P2 | 4G | dammam | Sceco | LTE SA | DAM2M8710 | FLM_TE | [8 empty] | API | 10/17/2025 15:21:40 | 10/17/2025 15:21:48 | 10/17/2025 16:06:49 | 10/17/2025 16:35:58 | 10/17/2025 16:45:55 | 10/17/2025 18:26:00 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000652 | PCM-20251017-00001065 | TT-20251017-01075 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/17/2025 15:24:12 | 10/20/2025 07:55:09 | 10/18/2025 03:24:12 | RF Unit Maintenance Link Failure at RIYB6158-DCU3 @ Sceco | 10/17/2025 15:19:07 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/17/2025 15:19:04 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/17/2025 15:24:12 | 10/20/2025 07:53:32 | 10/20/2025 07:54:57 |  |  | 10/20/2025 07:55:09 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000665 | PCM-20251017-00001084 | TT-20251017-01093 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/17/2025 15:32:29 | 10/20/2025 07:55:21 | 10/18/2025 03:32:29 | RF Unit CPRI Interface Error at RIYB6158-DCU3 @ Sceco | 10/17/2025 15:25:53 | Minor | 26504 | RF Unit CPRI Interface Error | 10/17/2025 15:25:35 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/17/2025 15:32:29 | 10/20/2025 07:53:24 | 10/20/2025 07:55:14 |  |  | 10/20/2025 07:55:21 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000667 | PCM-20251017-00001086 | TT-20251017-01095 | Reference_telecom | Region_6 | WDS0502 | WDS0502 |  |  |  | Ahmed Mamdouh Helal Helal | 10/17/2025 15:36:05 | 10/17/2025 20:42:34 | 10/18/2025 03:36:05 | LossOfSignal observed in WDS0502 _03 towards 10.10.159.221 @ Sceco | 10/17/2025 03:37:18 | Minor |  | LossOfSignal | 10/17/2025 03:35:39 | P2 | 2G | wadi dawasar | Sceco | TX NSA | WDS0502 | FLM_TE | [8 empty] | API | 10/17/2025 15:36:05 | 10/17/2025 20:42:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000671 | PCM-20251017-00001092 | TT-20251017-01096 | Telecom | Region_4 | BHR0310 | BHR0310 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/17/2025 15:41:31 | 10/17/2025 18:52:31 | 10/17/2025 21:41:31 | 1(5G) sites down under BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/17/2025 15:33:16 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/17/2025 15:33:14 | P2 | 2G | jeddah | Sceco | 5G SA | BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | BHR0310 | Results: DOWN SITE HUB BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 BHR0310 Summary: Hub: BHR0310, Down Count: 1, Down Sites: BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 Alarm Summary: BHR0310 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.97.120.236:8080/NE3S/1.0/] | sites down |  | API | 10/17/2025 15:41:31 | 10/17/2025 18:52:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000678 | PCM-20251017-00001102 | TT-20251017-01115 | Telecom | Region_4 | JZMA1M7824 | JZMA0824 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/17/2025 15:57:47 | 10/21/2025 17:12:38 | 10/17/2025 21:57:47 | BASE STATION SERVICE PROBLEM (No connection to unit) at JZMA1M7824-G9-L8-SBTS-P3 @ Sceco | 10/17/2025 15:56:48 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 15:56:45 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JZMA1M7824 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 15:57:47 | 10/18/2025 11:02:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000685 | PCM-20251017-00001110 | TT-20251017-01118 | EM | Region_5 | JUSH0644 | JUSH0644 |  |  |  | Hosini Saeed Hassn Saeed | 10/17/2025 16:06:05 | 10/17/2025 16:06:05 | 10/17/2025 22:06:05 | 1(2G/3G) sites down under JUSH0644-P3/JUSH0644-P3 @ Generator_SG | 10/17/2025 15:58:16 | Major | 7706 | BTS O&M LINK FAILURE | 10/17/2025 15:58:13 | P3 | 2G | makkah | Generator_SG | 2G_3G SA | JUSH0644-P3 | FLM_EM |  | Results: DOWN SITE HUB JUSH0644-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/17/2025 16:06:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000686 | PCM-20251017-00001111 | TT-20251017-01127 | EM | Region_6 | BHS1M8367 | BHS2367 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/17/2025 16:06:34 | 10/17/2025 16:11:25 | 10/18/2025 04:06:34 | RECTIFIER MAINS POWER FAILURE at BHS1M8367-G9-L8-L18-SBTS @ Sceco | 10/17/2025 15:58:13 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/17/2025 15:58:02 | P3 | 4G | Baha | Sceco | LTE NSA | BHS1M8367 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/17/2025 16:06:34 | 10/17/2025 16:11:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000687 | PCM-20251017-00001113 | TT-20251017-01129 | Reference_telecom | Region_4 | JED0125 | JED0125 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/17/2025 16:09:09 | 10/17/2025 18:52:31 | 10/18/2025 04:09:09 | ReplaceableUnitProblem observed in JED0125_01 towards 10.21.70.100 @ Generator_SG | 10/17/2025 04:09:08 | Minor |  | ReplaceableUnitProblem | 10/17/2025 04:09:03 | P1 | 2G | jeddah | Generator_SG | TX NSA | JED0125 | FLM_TE | [8 empty] | API | 10/17/2025 16:09:09 | 10/17/2025 18:52:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000688 | PCM-20251017-00001114 | TT-20251017-00975 | Telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/17/2025 16:09:38 | 10/17/2025 22:53:31 | 10/17/2025 22:09:38 | 1(LTE) sites down under RYQ0972-P3_SRAN @ Sceco | 10/17/2025 14:20:27 | Major | 301 | NE Is Disconnected | 10/17/2025 14:20:25 | P3 | SRAN | majma | Sceco | LTE SA | RYQ0972-P3_SRAN | FLM_TE | RYQ0972 | Results: DOWN SITE HUB RYQ0972-P3_SRAN RYQ0972 Summary: Hub: RYQ0972, Down Count: 1, Down Sites: RYQ0972-P3_SRAN Alarm Summary: RYQ0972 No Active Alarm on HUB | PCM-20251017-00001099 | Keep TT under FLM till check with team at site | Keep TT under FLM till check with team at site |  | sites down |  | API | 10/17/2025 16:09:38 | 10/17/2025 22:53:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000689 | PCM-20251017-00001115 | TT-20251017-01130 | Reference_telecom | Region_4 | JED0183 | JED0183 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 16:09:39 | 10/17/2025 19:19:04 | 10/18/2025 04:09:39 | DemFail observed in JED0183_02 towards 10.21.70.99 @ Sceco | 10/17/2025 04:09:11 | Minor |  | DemFail | 10/17/2025 04:09:05 | P2 | 2G | jeddah | Sceco | TX NSA | JED0183 | FLM_TE | [8 empty] | API | 10/17/2025 16:09:39 | 10/17/2025 19:19:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000692 | PCM-20251017-00001118 | TT-20251017-01133 | Reference_telecom | Region_4 | JED0712 | JED0712 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 16:11:12 | 10/19/2025 09:18:45 | 10/18/2025 04:11:12 | FanFailure observed in JED0712 towards 10.1.225.132 @ Generator_SG | 10/17/2025 04:13:01 | Minor |  | FanFailure | 10/17/2025 04:10:44 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0712 | FLM_TE | [8 empty] | API | 10/17/2025 16:11:12 | 10/19/2025 09:18:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000700 | PCM-20251017-00001132 | TT-20251017-01150 | Telecom | Region_4 | JED0519 | JED0519 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/17/2025 16:28:48 | 10/19/2025 17:44:39 | 10/17/2025 22:28:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0519-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/17/2025 16:27:44 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 16:27:51 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0519 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 16:28:48 | 10/17/2025 18:22:04 | 10/19/2025 10:34:41 |  |  | 10/19/2025 10:34:55 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000710 | PCM-20251017-00001154 | TT-20251017-00784 | Reference_telecom | Region_4 | JED0947 | JED0947 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 16:56:41 | 10/17/2025 19:19:06 | 10/18/2025 04:56:41 | Fronthaul loop back connectivity check failure at JED0947-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/17/2025 11:45:47 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/17/2025 11:45:39 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0947 | FLM_TE |  |  | PCM-20251017-00000794 | FLM need to check RFM and fronthaul cabling. | FLM need to check RFM and fronthaul cabling. |  |  |  | API | 10/17/2025 16:56:41 | 10/17/2025 19:19:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251017000711 | PCM-20251017-00001155 | TT-20251017-00942 | Telecom | Region_4 | JED0229 | JED0229 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/17/2025 16:57:22 | 10/19/2025 17:26:14 | 10/17/2025 22:57:22 | Fronthaul loop back connectivity check failure at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/17/2025 13:53:43 | Major | 61009 | Fronthaul loop back connectivity check failure | 10/17/2025 13:53:36 | P2 | 2G | jeddah | Sceco | 2G SA | JED0229 | FLM_TE |  |  | PCM-20251017-00000939 | FLM need to check RFM and fronthaul cabling. | FLM need to check RFM and fronthaul cabling. |  |  |  | API | 10/17/2025 16:57:22 | 10/17/2025 18:52:32 | 10/19/2025 17:23:21 | 10/19/2025 17:23:25 | 10/19/2025 17:26:14 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000713 | PCM-20251017-00001159 | TT-20251017-01182 | Reference_telecom | Region_6 | SAB0060 | SAB0060 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Ansir Iqbal Muhammad Iqbal | 10/17/2025 16:59:45 | 10/21/2025 03:50:21 | 10/18/2025 04:59:45 | DemFail observed in SAB0060_02 towards 10.21.79.211 @ Sceco_STB | 10/17/2025 05:00:06 | Minor |  | DemFail | 10/17/2025 04:59:41 | P1 | 2G | baish | Sceco_STB | TX NSA | SAB0060 | FLM_TE | [8 empty] | API | 10/17/2025 16:59:45 | 10/17/2025 23:00:10 | 10/20/2025 19:24:50 | 10/20/2025 19:24:53 | 10/21/2025 00:42:10 | 10/21/2025 03:50:21 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000722 | PCM-20251017-00001183 | TT-20251017-01206 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/17/2025 17:19:22 | 10/18/2025 14:26:59 | 10/17/2025 23:19:22 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/17/2025 14:17:52 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/17/2025 14:19:01 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/17/2025 17:19:22 | 10/18/2025 14:26:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000724 | PCM-20251017-00001186 | TT-20251017-01212 | Reference_telecom | Region_4 | JED0193 | JED0193 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/17/2025 17:24:32 | 10/17/2025 17:24:32 | 10/18/2025 05:24:32 | LossOfSignal observed in JED0193_01 towards 10.10.149.2 @ Sceco | 10/17/2025 05:25:19 | Minor |  | LossOfSignal | 10/17/2025 05:24:06 | P2 | 2G | jeddah | Sceco | TX NSA | JED0193 | FLM_TE | [8 empty] | API | 10/17/2025 17:24:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000744 | PCM-20251017-00001213 | TT-20251017-01236 | Reference_telecom | Region_4 | JED2986 | JED2986 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 17:44:43 | 10/17/2025 19:19:06 | 10/18/2025 05:44:43 | Degrade observed in JED2986 towards 10.1.224.147 @ Generator_SG | 10/17/2025 05:45:45 | Minor |  | Degrade | 10/17/2025 05:44:14 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2986 | FLM_TE | [8 empty] | API | 10/17/2025 17:44:43 | 10/17/2025 19:19:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000747 | PCM-20251017-00001216 | TT-20251017-01213 | Reference_telecom | Region_3 | MDYB0410 | MDYB0410 |  |  |  | Muhammad Sajjad R3 | 10/17/2025 17:47:12 | 10/18/2025 11:04:39 | 10/18/2025 05:47:12 | IP Clock Link Failure at MDYB0410-P1-HUB_SRAN @ Generator_DG | 10/17/2025 14:26:33 | Minor | 26263 | IP Clock Link Failure | 10/17/2025 14:23:58 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB0410 | FLM_TE |  |  | PCM-20251017-00001193 | PM Errors and RSL degradation observed on MDYB0410-ARM0310 FLM Team please perform health check for the mentioned MW link | PM Errors and RSL degradation observed on MDYB0410-ARM0310 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/17/2025 17:47:12 | 10/18/2025 11:04:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000759 | PCM-20251017-00001238 | TT-20251017-01257 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 18:11:01 | 10/17/2025 18:11:01 | 10/17/2025 22:11:01 | 1(LTE) sites down under JED0164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/17/2025 18:02:32 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/17/2025 18:02:29 | P1 | 4G | jeddah | Sceco | LTE SA | JED0164-CA-L900-L800-P1-WDM-SBTS | FLM_TE | JED0164 | Results: DOWN SITE HUB JED0164-CA-L900-L800-P1-WDM-SBTS JED0164 Summary: Hub: JED0164, Down Count: 1, Down Sites: JED0164-CA-L900-L800-P1-WDM-SBTS Alarm Summary: JED0164 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.96.88.236:8080/NE3S/1.0/] | sites down |  | API | 10/17/2025 18:11:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000760 | PCM-20251017-00001239 | TT-20251017-01258 | Telecom | Region_2 | SRIY0386 | SRIY0386 |  |  |  | Asad Ali Nadiq Khan | 10/17/2025 18:11:06 | 10/19/2025 09:20:02 | 10/18/2025 00:11:06 | 1(LTE) sites down under SRIY0386-P3 @ Sceco | 10/17/2025 18:05:08 | Major | 301 | NE Is Disconnected | 10/17/2025 18:01:42 | P3 | SRAN | riyadh | Sceco | LTE SA | SRIY0386-P3_SRAN | FLM_TE | SRIY0386 | Results: DOWN SITE HUB SRIY0386-P3_SRAN SRIY0386 Summary: Hub: SRIY0386, Down Count: 1, Down Sites: SRIY0386-P3_SRAN Alarm Summary: SRIY0386 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/17/2025 18:11:06 | 10/19/2025 09:20:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000764 | PCM-20251017-00001245 | TT-20251017-01267 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | SFP_BTS | Clean SFP | Waseem Shahzad Ghulam Rasool | 10/17/2025 18:17:45 | 10/20/2025 07:57:03 | 10/18/2025 06:17:45 | RF Unit Clock Problem at RIYB6158-DCU3 @ Sceco | 10/17/2025 18:10:12 | Minor | 26538 | RF Unit Clock Problem | 10/17/2025 18:09:37 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/17/2025 18:17:45 | 10/20/2025 07:53:15 | 10/20/2025 07:56:42 |  |  | 10/20/2025 07:57:03 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000772 | PCM-20251017-00001255 | TT-20251017-01274 | EM | Region_6 | BHS2367 | BHS2367 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/17/2025 18:30:04 | 10/18/2025 10:42:29 | 10/18/2025 00:30:04 | 1(2G/LTE) sites down under BHS2367-P3/BHS2367-P3 @ Sceco | 10/17/2025 18:21:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/17/2025 18:21:40 | P3 | 2G | Baha | Sceco | 2G_LTE SA | BHS2367-P3 | FLM_EM | BHS2367 | Results: DOWN SITE HUB BHS2367-P3 BHS2367 Summary: Hub: BHS2367, Down Count: 1, Down Sites: BHS2367-P3 Alarm Summary: BHS2367 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/17/2025 18:30:04 | 10/18/2025 10:42:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000773 | PCM-20251017-00001256 | TT-20251017-01276 | Reference_telecom | Region_6 | TBL2297 | TBL2297 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/17/2025 18:30:30 | 10/21/2025 21:25:03 | 10/18/2025 00:30:30 | 1(2G/3G) sites down under TBL2297-P3 (REF::TT-20251017-00268)@ Sceco | 10/17/2025 09:52:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/17/2025 09:52:32 | P3 | 2G | bisha | Generator_SG | 2G_3G SA | TBL2297 | FLM_TE | TBL2297 | Results: DOWN SITE HUB TBL2297 TBL2297 Summary: Hub: TBL2297, Down Count: 1, Down Sites: TBL2297 Alarm Summary: TBL2297 No Active Alarm on HUB |  |  |  |  | sites down |  | Manual | 10/17/2025 18:30:30 | 10/21/2025 21:24:36 | 10/21/2025 21:24:51 |  |  | 10/21/2025 21:25:03 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000779 | PCM-20251017-00001273 | TT-20251017-01287 | Telecom | Region_6 | AQQ2434 | AQQ2434 |  |  |  | Fathy Mohamed | 10/17/2025 18:40:18 | 10/17/2025 19:02:21 | 10/17/2025 20:40:18 | 12(2G) 12(LTE) sites down under AQQ2427-P3 @ Generator_SG | 10/17/2025 18:29:11 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/17/2025 18:29:08 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | AQQ2430-P3 2G_LTE,AQQ2427-P3 2G_LTE,AQQ2428-P3 2G_LTE,AQQ2429-P3 2G_LTE | FLM_EM | AQQ2434 | Dear team , Hub: AQQ2434 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251017-00001268 | Dear team , Hub: AQQ2434 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: AQQ2434 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/17/2025 18:40:18 | 10/17/2025 19:02:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251017000786 | PCM-20251017-00001283 | TT-20251017-01300 | EM | Region_6 | BHS2361 | BHS2361 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/17/2025 18:44:04 | 10/18/2025 10:42:30 | 10/18/2025 00:44:04 | 1(2G/LTE) sites down under BHS2361-P3/BHS2361-P3 @ Sceco | 10/17/2025 18:35:47 | Major | 7706 | BTS O&M LINK FAILURE | 10/17/2025 18:35:40 | P3 | 2G | Baha | Sceco | 2G_LTE SA | BHS2361-P3 | FLM_EM | BHS2361 | Results: DOWN SITE HUB BHS2361-P3 BHS2361 Summary: Hub: BHS2361, Down Count: 1, Down Sites: BHS2361-P3 Alarm Summary: BHS2361 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/17/2025 18:44:04 | 10/18/2025 10:42:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251017000796 | PCM-20251017-00001295 | TT-20251017-01323 | Telecom | Region_4 | JED1M7236 | JED0236 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 19:02:10 | 10/19/2025 17:44:41 | 10/18/2025 01:02:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7236-P2-CA-L900-L800-SBTS @ Sceco | 10/17/2025 19:01:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 19:00:53 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7236 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 19:02:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000800 | PCM-20251017-00001300 | TT-20251017-01328 | Reference_telecom | Region_4 | BHMF2143 | BHMF2143 |  |  |  | Khizer Hayat | 10/17/2025 19:04:13 | 10/18/2025 00:36:08 | 10/18/2025 07:04:13 | ReplaceableUnitProblem observed in BHMF2143 towards 10.1.226.3 @ Generator_SG | 10/17/2025 07:04:02 | Minor |  | ReplaceableUnitProblem | 10/17/2025 07:03:59 | P3 | 2G | jeddah | Generator_SG | TX NSA | BHMF2143 | FLM_TE | [8 empty] | API | 10/17/2025 19:04:13 | 10/18/2025 00:36:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000806 | PCM-20251017-00001318 | TT-20251017-01357 | EM | Region_6 | BCH1M8203 | BCH2203 |  |  |  | Fathy Mohamed | 10/17/2025 19:32:39 | 10/17/2025 22:02:02 | 10/18/2025 07:32:39 | RECTIFIER MODULE FAILURE at BCH1M8203-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/17/2025 19:24:35 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/17/2025 19:24:30 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8203 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/17/2025 19:32:39 | 10/17/2025 22:02:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000814 | PCM-20251017-00001336 | TT-20251017-01369 | Telecom | Region_4 | JED1M8596 | JED2596 | Equipment | BSS_HW_fault | Replace ALD | MALIK ATIF ZAMAN | 10/17/2025 19:45:02 | 10/19/2025 13:21:17 | 10/17/2025 23:45:02 | 1(LTE) sites down under JED2596-P1-CA-L800 @ Sceco | 10/17/2025 19:36:57 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/17/2025 19:36:54 | P1 | 4G | jeddah | Sceco | LTE SA | JED2596-P1-CA-L800 | FLM_TE | JED2596 | Results: DOWN SITE HUB JED2596-P1-CA-L800 JED2596 Summary: Hub: JED2596, Down Count: 1, Down Sites: JED2596-P1-CA-L800 Alarm Summary: JED2596 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.88.52:8080] [URL:http://10.97.88.52:8080/NE3S/1.0/] | sites down |  | API | 10/17/2025 19:45:02 | 10/19/2025 09:18:47 | 10/19/2025 12:08:48 | 10/19/2025 12:08:50 | 10/19/2025 12:52:02 | 10/19/2025 13:21:17 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000816 | PCM-20251017-00001338 | TT-20251017-01374 | Telecom | Region_4 | JED1M7884 | JED0884 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/17/2025 19:51:03 | 10/19/2025 09:42:51 | 10/18/2025 01:51:03 | 1(LTE) sites down under JED0884-CA-L900-L800-SBTS @ Sceco | 10/17/2025 19:42:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/17/2025 19:42:54 | P2 | 4G | jeddah | Sceco | LTE SA | JED0884-CA-L900-L800-SBTS | FLM_TE | JED0884 | Results: DOWN SITE HUB JED0884-CA-L900-L800-SBTS JED0884 Summary: Hub: JED0884, Down Count: 1, Down Sites: JED0884-CA-L900-L800-SBTS Alarm Summary: JED0884 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.192.68:8080] [URL:http://10.97.192.68:8080/NE3S/1.0/] | sites down |  | API | 10/17/2025 19:51:03 | 10/17/2025 20:14:36 | 10/19/2025 09:42:19 |  |  | 10/19/2025 09:42:51 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000821 | PCM-20251017-00001349 | TT-20251017-01380 | Telecom | Region_4 | JED0415 | JED0415 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/17/2025 20:11:44 | 10/19/2025 17:44:42 | 10/18/2025 02:11:44 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED0415-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/17/2025 19:50:15 | Major | 7114 | CELL SERVICE PROBLEM | 10/17/2025 19:50:03 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0415 | FLM_TE |  |  | PCM-20251017-00001340 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:11:44 | 10/17/2025 20:14:36 | 10/19/2025 09:44:11 |  |  | 10/19/2025 09:44:25 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000822 | PCM-20251017-00001350 | TT-20251017-01331 | Reference_telecom | Region_4 | JED1MN0218 | JED0218 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 20:11:53 | 10/17/2025 20:11:53 | 10/18/2025 08:11:53 | Fronthaul loop back connectivity check failure at JED1MN0218-NR2.6-P1-VIP @ Sceco | 10/17/2025 18:41:28 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/17/2025 18:41:19 | VIP | 5G | jeddah | Sceco | 5G NSA | JED1MN0218 | FLM_TE |  |  | PCM-20251017-00001304 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:11:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000823 | PCM-20251017-00001352 | TT-20251017-01324 | Telecom | Region_4 | JED1MN2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 20:12:10 | 10/18/2025 10:32:44 | 10/18/2025 02:12:10 | BASE STATION HARDWARE PROBLEM (SFP Transceiver temperature too high) at JED1MN2979-NR2.6-P1-VIP @ Generator_SG | 10/17/2025 18:55:24 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/17/2025 18:55:19 | VIP | 5G | jeddah | Generator_SG | 5G NSA | JED1MN2979 | FLM_TE |  |  | PCM-20251017-00001296 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:12:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000825 | PCM-20251017-00001354 | TT-20251017-01299 | Telecom | Region_5 | MAK1U6907 | MAK6007 |  |  |  | Mosab Nasr eldeen Mohamed | 10/17/2025 20:12:27 | 10/20/2025 02:29:12 | 10/18/2025 08:12:27 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at MAK1U6907-CA-SBTS-P3 @ Sceco | 10/17/2025 18:29:21 | Minor | 7654 | CELL OPERATION DEGRADED | 10/17/2025 18:29:15 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6907 | FLM_TE |  |  | PCM-20251017-00001267 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:12:27 | 10/20/2025 02:29:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000827 | PCM-20251017-00001356 | TT-20251017-01283 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 20:12:41 | 10/17/2025 20:12:41 | 10/18/2025 02:12:41 | BASE STATION ANTENNA LINE PROBLEM at JED1M7552-CA-L900-L800-SBTS @ Sceco | 10/17/2025 18:23:27 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 18:23:16 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7552 | FLM_TE |  |  | PCM-20251017-00001257 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:12:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000840 | PCM-20251017-00001371 | TT-20251017-00968 | Telecom | Region_4 | JED1MN0575 | JED0575 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 20:20:25 | 10/19/2025 09:18:47 | 10/18/2025 02:20:25 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at JED1MN0575-NR2.6-P3 @ Sceco | 10/17/2025 14:15:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 14:15:19 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0575 | FLM_TE |  |  | PCM-20251017-00000966 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:20:25 | 10/19/2025 09:18:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000842 | PCM-20251017-00001374 | TT-20251017-00922 | Telecom | Region_4 | JED1M7238 | JED0238 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 20:20:44 | 10/17/2025 21:15:01 | 10/18/2025 02:20:44 | BASE STATION ANTENNA LINE PROBLEM at JED1M7238-P1-WDM-CA-L900-NL800-SBTS @ Sceco | 10/17/2025 13:42:16 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 13:42:09 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7238 | FLM_TE |  |  | PCM-20251017-00000923 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:20:44 | 10/17/2025 21:15:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000844 | PCM-20251017-00001376 | TT-20251017-00849 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/17/2025 20:20:57 | 10/18/2025 00:36:08 | 10/18/2025 08:20:57 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/17/2025 12:57:35 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 12:57:27 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251017-00000859 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:20:57 | 10/18/2025 00:36:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000855 | PCM-20251017-00001388 | TT-20251017-01397 | Reference_telecom | Region_2 | RIYD2U6721 | RIYD6021 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/17/2025 20:25:17 | 10/19/2025 09:44:30 | 10/18/2025 08:25:17 | Cell RX Channel Interference Noise Power Unbalanced at RIYD2U6721-L800-CA-P3 @ Sceco | 10/17/2025 17:23:12 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/17/2025 17:23:10 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYD2U6721 | FLM_TE |  |  | PCM-20251017-00001379 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/17/2025 20:25:17 | 10/19/2025 09:44:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000862 | PCM-20251017-00001397 | TT-20251017-01057 | Reference_telecom | Region_6 | TNM1M3930 | TNM0930 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/17/2025 20:29:05 | 10/17/2025 23:36:18 | 10/18/2025 02:29:05 | RNW O&M SCENARIO FAILURE at TNM1M3930-P3 @ Generator_DG | 10/17/2025 14:41:58 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/17/2025 14:41:07 | P3 | 3G | Tanomah | Generator_DG | 3G NSA | TNM1M3930 | FLM_TE |  |  | PCM-20251017-00001045 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/17/2025 20:29:05 | 10/17/2025 23:30:42 | 10/17/2025 23:35:47 |  |  | 10/17/2025 23:36:18 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000871 | PCM-20251017-00001412 | TT-20251017-00879 | Telecom | Region_4 | JED0391 | JED0391 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 20:33:32 | 10/19/2025 17:44:54 | 10/18/2025 02:33:32 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED0391-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/17/2025 13:20:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 13:20:37 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0391 | FLM_TE |  |  | PCM-20251017-00000882 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:33:32 | 10/17/2025 21:15:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000874 | PCM-20251017-00001415 | TT-20251017-00838 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/17/2025 20:34:53 | 10/21/2025 18:23:12 | 10/18/2025 02:34:53 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/17/2025 12:46:32 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/17/2025 12:46:22 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251017-00000847 | site is down | site is down please handle with same RCA |  |  |  | API | 10/17/2025 20:34:53 | 10/19/2025 15:04:08 | 10/21/2025 18:23:06 |  |  | 10/21/2025 18:23:12 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000884 | PCM-20251017-00001426 | TT-20251017-00754 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/17/2025 20:41:56 | 10/21/2025 18:23:00 | 10/18/2025 02:41:56 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/17/2025 11:41:35 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/17/2025 11:41:31 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251017-00000757 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 20:41:56 | 10/19/2025 15:04:09 | 10/21/2025 18:22:54 |  |  | 10/21/2025 18:23:00 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000889 | PCM-20251017-00001437 | TT-20251017-01433 | Telecom | Region_4 | JED1M8146 | JED2146 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/17/2025 21:07:43 | 10/17/2025 21:07:43 | 10/18/2025 03:07:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8146-P3-CA-L800 @ Sceco | 10/17/2025 21:06:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 21:06:46 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8146 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 21:07:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000891 | PCM-20251017-00001443 | TT-20251017-01068 | Reference_telecom | Region_6 | BHAB1M8006 | BHAB2006 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/17/2025 21:14:17 | 10/17/2025 23:05:55 | 10/18/2025 09:14:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHAB1M8006-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/17/2025 13:31:37 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 13:21:20 | P3 | 4G | mohail | Generator_SG | LTE NSA | BHAB1M8006 | FLM_TE |  | Thanks to check | PCM-20251017-00001395 | Thanks to check | Thanks to check |  |  |  | API | 10/17/2025 21:14:17 | 10/17/2025 23:04:52 | 10/17/2025 23:05:41 |  |  | 10/17/2025 23:05:55 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251017000893 | PCM-20251017-00001445 | TT-20251017-01067 | Reference_telecom | Region_6 | BHAB1M8034 | BHAB2034 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/17/2025 21:15:17 | 10/17/2025 23:06:20 | 10/18/2025 09:15:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHAB1M8034-G9-L8-SBTS-P3 @ Generator_SG | 10/17/2025 13:34:49 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 13:20:53 | P3 | 4G | mohail | Generator_SG | LTE NSA | BHAB1M8034 | FLM_TE |  | Thanks to check | PCM-20251017-00001396 | Thanks to check | Thanks to check |  |  |  | API | 10/17/2025 21:15:17 | 10/17/2025 23:04:53 | 10/17/2025 23:06:06 |  |  | 10/17/2025 23:06:20 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000894 | PCM-20251017-00001452 | TT-20251017-01438 | Reference_telecom | Region_1 | DAM2M8802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/17/2025 21:28:47 | 10/17/2025 23:39:35 | 10/18/2025 09:28:47 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M8802-CA-L800-FWA-P1-VIP @ Sceco | 10/17/2025 18:12:35 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/17/2025 18:12:32 | P3 | 4G | dammam | Sceco | 2G NSA | DAM2M8802 | FLM_TE |  |  | PCM-20251017-00001440 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/17/2025 21:28:47 | 10/17/2025 23:39:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000899 | PCM-20251017-00001460 | TT-20251017-01462 | Reference_telecom | Region_4 | THO0619 | THO0619 |  |  |  | Nazeer Mohammed | 10/17/2025 21:37:38 | 10/18/2025 10:14:54 | 10/18/2025 09:37:38 | FanFailure observed in THO0619_01 towards 10.21.77.242 @ Sceco | 10/17/2025 09:37:55 | Minor |  | FanFailure | 10/17/2025 09:37:29 | P2 | 2G | jeddah | Sceco | TX NSA | THO0619 | FLM_TE | [8 empty] | API | 10/17/2025 21:37:38 | 10/18/2025 10:14:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000914 | PCM-20251017-00001488 | TT-20251017-01398 | Telecom | Region_1 | ARM2753 | ARM2753 |  |  |  | Tahir Mahmood Hafiz Yar | 10/17/2025 22:14:13 | 10/18/2025 05:13:51 | 10/18/2025 04:14:13 | 1(3G) sites down under ARM2753-P3/JB1RNCH01 @ Sceco | 10/17/2025 20:20:11 | Major | 22214 | NodeB Unavailable | 10/17/2025 20:20:08 | P3 | SRAN | jubail | Sceco | 3G SA | ARM2753-P3 | FLM_TE | ARM2753 | single site check locally | PCM-20251017-00001472 | single site check locally | single site check locally |  | sites down |  | API | 10/17/2025 22:14:13 | 10/18/2025 05:13:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000915 | PCM-20251017-00001489 | TT-20251008-01956 | MW_HC | Region_6 | ABH0167 | ABH0167 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/17/2025 22:14:35 | 10/18/2025 02:02:52 | 10/18/2025 10:14:35 | NEC MW HC_P0 Observing Modem Down at ABH0135(10.154.161.154)--ABH0167(10.154.161.171) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P1 | 2G | abha | Sceco | TX NSA | ABH0135(10.154.161.154)--ABH0167(10.154.161.171) | FLM_TE |  | issue repeated at slot 6 every day at same time thanks to check | PCM-20251015-00002117 | issue repeated at slot 6 every day at same time thanks to check | issue repeated at slot 6 every day at same time thanks to check |  |  |  | API | 10/17/2025 22:14:35 | 10/18/2025 02:02:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000931 | PCM-20251017-00001511 | TT-20251017-01492 | Telecom | Region_4 | JED1MN0056 | JED0056 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 22:38:07 | 10/18/2025 11:21:52 | 10/18/2025 04:38:07 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at JED1MN0056-NR2.6-P3 @ Sceco | 10/17/2025 22:26:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 22:25:59 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0056 | FLM_TE |  |  | PCM-20251017-00001496 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 22:38:07 | 10/18/2025 11:21:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000936 | PCM-20251017-00001515 | TT-20251017-01437 | Telecom | Region_4 | JED1M7375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/17/2025 22:38:35 | 10/19/2025 09:18:49 | 10/18/2025 10:38:35 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/17/2025 21:08:11 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 21:08:07 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251017-00001439 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 22:38:35 | 10/19/2025 09:18:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251017000940 | PCM-20251017-00001523 | TT-20251017-01509 | Reference_telecom | Region_4 | JED2388 | JED2388 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/17/2025 22:51:30 | 10/17/2025 22:51:30 | 10/18/2025 10:51:30 | LagPortDown observed in JED2388 towards 10.10.183.235 @ Sceco | 10/17/2025 10:53:20 | Minor |  | LagPortDown | 10/17/2025 10:51:19 | P3 | 2G | jeddah | Sceco | TX NSA | JED2388 | FLM_TE | [8 empty] | API | 10/17/2025 22:51:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000950 | PCM-20251017-00001536 | TT-20251017-01524 | Telecom | Region_4 | JED0053 | JED0053 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 23:08:03 | 10/18/2025 11:21:52 | 10/18/2025 05:08:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0053-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-SHOP @ Sceco | 10/17/2025 23:07:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 23:07:14 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0053 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/17/2025 23:08:03 | 10/18/2025 11:21:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000970 | PCM-20251017-00001571 | TT-20251008-01947 | MW_HC | Region_6 | FUR0101 | FUR0101 |  |  |  | Mohammed Sideag Mohammed Ali | 10/17/2025 23:55:51 | 10/18/2025 01:43:26 | 10/18/2025 11:55:51 | NEC MW HC_P0 Observing Performance Issue at FUR0050(10.1.172.198)--FUR0101(10.1.172.196) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | jizan | Sceco | TX NSA | FUR0050(10.1.172.198)--FUR0101(10.1.172.196) | FLM_TE |  | Thanks to check still counting error | PCM-20251016-00002195 | Thanks to check still counting error | Thanks to check still counting error |  |  |  | API | 10/17/2025 23:55:51 | 10/18/2025 01:43:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000973 | PCM-20251017-00001575 | TT-20251017-01562 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/17/2025 23:57:30 | 10/19/2025 17:44:55 | 10/18/2025 05:57:30 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/17/2025 23:50:28 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/17/2025 23:50:25 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2279 | FLM_TE |  |  | PCM-20251017-00001570 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/17/2025 23:57:30 | 10/18/2025 11:21:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251018000011 | PCM-20251018-00000013 | TT-20251018-00011 | Telecom | [7 empty] | 10/18/2025 00:10:03 | 10/18/2025 00:10:03 | 10/18/2025 04:10:03 | ETH_LOS at FRIY0001-1 @ Sceco | 10/18/2025 00:09:12 | Critical | 1-235 | ETH_LOS | 10/18/2025 00:08:47 | P3 | DWDM |  | Sceco | DWDM NSA | FRIY0001 | FLM_TE | [5 empty] | 0-1-C-14-K1EX10-4(NIH)-MAC:1 |  |  | API | 10/18/2025 00:10:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000013 | PCM-20251018-00000016 | TT-20251018-00012 | EM | Region_5 | SHD0142 | SHD0142 |  |  |  | Hazem Ali Moustafa Ali | 10/18/2025 00:12:57 | 10/19/2025 17:44:42 | 10/18/2025 06:12:57 | TRX FAULTY (FF FF FF FF FF FF shared:S) at SHD0142-P2-USF @ Generator_SG | 10/18/2025 00:03:18 | Major | 7606 | TRX FAULTY | 10/18/2025 00:03:14 | P2 | 2G | makkah | Generator_SG | 2G_Cell SA | SHD0142 | FLM_TE |  |  | PCM-20251018-00000014 | No Power Issue | No Power Issue |  |  |  | API | 10/18/2025 00:12:57 | 10/18/2025 03:16:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000015 | PCM-20251018-00000019 | TT-20251018-00015 | Telecom | Region_4 | JED0271 | JED0271 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/18/2025 00:14:41 | 10/19/2025 17:44:43 | 10/18/2025 06:14:41 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/18/2025 00:14:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 00:13:52 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 00:14:41 | 10/18/2025 07:12:52 | 10/19/2025 09:45:55 |  |  | 10/19/2025 09:46:09 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000016 | PCM-20251018-00000022 | TT-20251018-00013 | EM | Region_4 | JED6010 | JED6010 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/18/2025 00:16:31 | 10/21/2025 18:22:47 | 10/18/2025 06:16:31 | 1(2G/LTE/5G) sites down under JED6010-P3 @ Sceco | 10/18/2025 00:08:27 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/18/2025 00:08:24 | P3 | 2G | jeddah | Sceco | 5G SA | JED6010-GSM-P3 | FLM_TE | JED6010 | Results: DOWN SITE HUB JED6010-GSM-P3 JED6010 Summary: Hub: JED6010, Down Count: 1, Down Sites: JED6010-GSM-P3 Alarm Summary: JED6010 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.194.196:8080] [URL:http://10.97.194.196:8080/NE3S/1.0/] | sites down |  | API | 10/18/2025 00:16:31 | 10/19/2025 15:04:09 | 10/21/2025 18:22:38 |  |  | 10/21/2025 18:22:47 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000022 | PCM-20251018-00000035 | TT-20251017-01563 | EM | Region_1 | HFR2169 | HFR2169 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/18/2025 00:34:08 | 10/18/2025 01:43:28 | 10/18/2025 04:34:08 | 1(2G/3G/LTE) sites down under HFR2169-P1-SHOP/HB1BSCH01 @ Generator_SG | 10/17/2025 23:54:06 | Critical | 21825 | CSL Fault | 10/17/2025 23:54:03 | P1 | SRAN | hafr | Generator_SG | 2G_3G_LTE SA | HFR2169-P1-SHOP | FLM_TE | HFR2169 | Hub : RYH0120 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. | PCM-20251018-00000018 | Hub : RYH0120 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. | Hub : RYH0120 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. |  | sites down |  | API | 10/18/2025 00:34:08 | 10/18/2025 01:43:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000032 | PCM-20251018-00000054 | TT-20251018-00032 | Reference_telecom | Region_5 | SHD1M3142 | SHD0142 |  |  |  | Sher Ali Munir | 10/18/2025 01:00:36 | 10/18/2025 07:27:00 | 10/18/2025 07:00:36 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at SHD1M3142-P2-USF @ Generator_SG | 10/18/2025 00:05:26 | Major | 7771 | WCDMA CELL OUT OF USE | 10/18/2025 00:03:16 | P2 | 3G | makkah | Generator_SG | 3G SA | SHD1M3142 | FLM_TE |  |  | PCM-20251018-00000034 | FLM need to check VSWR issue at site | FLM need to check VSWR issue at site |  |  |  | API | 10/18/2025 01:00:36 | 10/18/2025 07:27:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000039 | PCM-20251018-00000079 | TT-20251018-00088 | Telecom | Region_2 | RIYB6031-CSG-01 | RIYB6031 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/18/2025 01:18:45 | 10/18/2025 14:27:00 | 10/18/2025 05:18:45 | The Device is offline at RIYB6031-CSG-01 @ Sceco | 10/18/2025 01:18:20 | Critical | 101-7 | The Device is offline | 10/18/2025 01:18:18 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6031-CSG-01 | FLM_TE | [8 empty] | API | 10/18/2025 01:18:45 | 10/18/2025 14:27:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000046 | PCM-20251018-00000092 | TT-20251018-00101 | Reference_telecom | Region_1 | HFS2M4025 | HFS2025 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/18/2025 01:29:04 | 10/18/2025 10:22:43 | 10/18/2025 13:29:04 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M4025-P3 @ Generator_SG | 10/17/2025 22:28:53 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/17/2025 22:28:50 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M4025 | FLM_TE | [8 empty] | API | 10/18/2025 01:29:04 | 10/18/2025 10:22:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000052 | PCM-20251018-00000106 | TT-20251017-01239 | Reference_telecom | Region_3 | MDYB2M3312 | MDYB0312 |  |  |  | Muhammad Sajjad R3 | 10/18/2025 01:42:33 | 10/18/2025 11:04:40 | 10/18/2025 13:42:33 | IP Clock Link Failure at MDYB2M3312-P3 @ Generator_DG | 10/17/2025 14:50:12 | Minor | 26263 | IP Clock Link Failure | 10/17/2025 14:47:34 | P3 | 3G | yanbu | Generator_DG | 3G NSA | MDYB2M3312 | FLM_TE |  |  | PCM-20251017-00001228 | Need HC on below link as LOF alarms and other alarms exist during this time YNB0670-MDYB0313 | Need HC on below link as LOF alarms and other alarms exist during this time YNB0670-MDYB0313 |  |  |  | API | 10/18/2025 01:42:33 | 10/18/2025 11:04:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000055 | PCM-20251018-00000109 | TT-20251018-00069 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/18/2025 01:48:32 | 10/21/2025 18:22:34 | 10/18/2025 05:48:32 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/18/2025 01:00:46 | Critical | 7654 | CELL OPERATION DEGRADED | 10/18/2025 01:00:40 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251018-00000063 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 01:48:32 | 10/19/2025 15:04:10 | 10/21/2025 18:22:23 |  |  | 10/21/2025 18:22:34 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000067 | PCM-20251018-00000125 | TT-20251017-01305 | Reference_telecom | Region_2 | RYQ0972 | RYQ0972 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/18/2025 01:58:11 | 10/18/2025 07:36:19 | 10/18/2025 13:58:11 | External Clock Reference Problem at RYQ0972-P3_SRAN @ Sceco | 10/17/2025 17:15:21 | Minor | 26262 | External Clock Reference Problem | 10/17/2025 15:39:54 | P3 | SRAN | majma | Sceco | 2G NSA | RYQ0972 | FLM_TE |  |  | PCM-20251017-00001282 | Kindly need HC on RYQ0972 as ETH LOS alarm exist during this time | Kindly need HC on RYQ0972 as ETH LOS alarm exist during this time |  |  |  | API | 10/18/2025 01:58:11 | 10/18/2025 07:36:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000087 | PCM-20251018-00000161 | TT-20251018-00159 | Reference_telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/18/2025 02:40:53 | 10/18/2025 02:40:53 | 10/18/2025 14:40:53 | RF Unit RX Channel RTWP/RSSI Unbalanced at MAK6018-DCU-P3 @ Sceco | 10/17/2025 23:40:37 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/17/2025 23:40:32 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/18/2025 02:40:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000093 | PCM-20251018-00000167 | TT-20251018-00162 | Telecom | Region_2 | RIYD2U6123 | RIYD6023 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/18/2025 02:51:31 | 10/18/2025 14:27:01 | 10/18/2025 08:51:31 | 1(2G) sites down under RIYD6023-P3/R2_RY3_HWBSC01 @ Sceco | 10/18/2025 02:43:25 | Major | 21825 | CSL Fault | 10/18/2025 02:43:22 | P3 | 2G | riyadh | Sceco | 2G SA | RIYD6023-P3 | FLM_TE | RIYD6023 | Results: DOWN SITE HUB RIYD6023-P3 RIYD6023 Summary: Hub: RIYD6023, Down Count: 1, Down Sites: RIYD6023-P3 Alarm Summary: RIYD6023 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/18/2025 02:51:31 | 10/18/2025 14:27:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251018000100 | PCM-20251018-00000180 | TT-20251018-00188 | Telecom | [7 empty] | 10/18/2025 03:12:56 | 10/18/2025 03:12:56 | 10/18/2025 09:12:56 | LAN_LOC at GHUNAN-SEC0021_ELC @ Sceco | 10/18/2025 03:11:57 | Major | 1-12926 | LAN_LOC | 10/18/2025 03:07:29 | P1 | DWDM |  | Sceco | DWDM NSA | GHUNAN | FLM_TE | [5 empty] | 0-ELC(2-C)-72-G4CXP-9(NMETH1/NMETH1)-COM:1 |  |  | API | 10/18/2025 03:12:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000111 | PCM-20251018-00000201 | TT-20251018-00173 | Telecom | Region_1 | DRN2328 | DRN2328 | Enviroment | SCECO_Failure | SCECO auto restored | Imran Ali Yousaf | 10/18/2025 03:38:18 | 10/19/2025 17:25:24 | 10/18/2025 07:38:18 | 2(2G) 1(LTE) sites down under DRN0110-P1-HUB,ARM0732-P3/DM1MBSCH01 @ Sceco | 10/18/2025 02:56:56 | Critical | 21825 | CSL Fault | 10/18/2025 02:56:53 | P3 | SRAN | dammam | Sceco | 2G_LTE SA | DRN0110-P1-HUB 2G_LTE,ARM0732-P3 2G | FLM_TE | DRN2328 | Hub : DRN2328_NE_7_SDB We are observing HARD_BAD alarm active , kindly visit the site and check the issue. | PCM-20251018-00000177 | Hub : DRN2328_NE_7_SDB We are observing HARD_BAD alarm active , kindly visit the site and check the issue. | Hub : DRN2328_NE_7_SDB We are observing HARD_BAD alarm active , kindly visit the site and check the issue. |  | sites down |  | API | 10/18/2025 03:38:18 | 10/18/2025 08:04:28 | 10/19/2025 17:18:08 |  |  | 10/19/2025 17:25:24 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000118 | PCM-20251018-00000209 | TT-20251018-00233 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/18/2025 03:48:05 | 10/18/2025 03:48:05 | 10/18/2025 07:48:05 | OSC_LOS at KB2_OCS @ Sceco_STB | 10/18/2025 03:47:27 | Critical | 1-12843 | OSC_LOS | 10/18/2025 03:47:15 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE | [5 empty] | 0-TO DAM0311(1-A)-7-G2AST4-3(RM3/TM3(TO GHUNAN-SEC0021_OCS,TNG6WDAPXF(2-A01)-RM2/TM2))-OSC:1 |  |  | API | 10/18/2025 03:48:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000134 | PCM-20251018-00000231 | TT-20251018-00258 | Telecom | Region_4 | JED0341 | JED0341 | Equipment | SFP_BTS | Clean SFP | Khaled Mohammad Abdallah | 10/18/2025 04:11:17 | 10/20/2025 01:18:02 | 10/18/2025 10:11:17 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0341-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/18/2025 04:10:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 04:10:19 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0341 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 04:11:17 |  | 10/20/2025 00:46:14 | 10/20/2025 00:46:16 | 10/20/2025 00:46:18 | 10/20/2025 01:18:02 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000139 | PCM-20251018-00000245 | TT-20251018-00276 | Reference_telecom | Region_6 | ABH0004 | ABH0004 |  |  |  | Amir Sohail | 10/18/2025 04:23:40 | 10/18/2025 12:30:43 | 10/18/2025 16:23:40 | DemFail observed in ABH0004_01 towards 10.89.249.148 @ Sceco | 10/17/2025 16:23:29 | Minor |  | DemFail | 10/17/2025 16:23:25 | P2 | 2G | abha | Sceco | TX NSA | ABH0004 | FLM_TE | [8 empty] | API | 10/18/2025 04:23:40 | 10/18/2025 12:30:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000140 | PCM-20251018-00000246 | TT-20251018-00277 | EM | Region_4 | BHMF1M8137 | BHMF2137 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/18/2025 04:23:41 | 10/18/2025 06:39:34 | 10/18/2025 16:23:41 | COMMERCIAL POWER FAILURE at BHMF1M8137-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/18/2025 04:15:29 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/18/2025 04:15:22 | P3 | 4G | jeddah | Generator_SG | LTE NSA | BHMF1M8137 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/18/2025 04:23:41 | 10/18/2025 06:39:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000145 | PCM-20251018-00000252 | TT-20251018-00167 | Telecom | Region_4 | JED0109 | JED0109 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/18/2025 04:27:54 | 10/21/2025 17:12:39 | 10/18/2025 10:27:54 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/18/2025 02:53:25 | Major | 7114 | CELL SERVICE PROBLEM | 10/18/2025 02:53:16 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE |  |  | PCM-20251018-00000171 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 04:27:54 | 10/18/2025 07:12:52 | 10/19/2025 09:46:20 |  |  | 10/19/2025 09:46:30 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251018000146 | PCM-20251018-00000253 | TT-20251018-00281 | EM | [7 empty] | 10/18/2025 04:30:24 | 10/18/2025 04:30:24 | 10/18/2025 08:30:24 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/18/2025 04:28:57 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/18/2025 04:28:49 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/18/2025 04:30:24 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000158 | PCM-20251018-00000275 | TT-20251018-00311 | Reference_telecom | Region_5 | MAK0273 | MAK0273 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/18/2025 05:02:26 | 10/24/2025 01:40:11 | 10/18/2025 17:02:26 | DemFail observed in MAK0273_01 towards 10.3.224.18 @ Generator_SG | 10/17/2025 17:03:45 | Minor |  | DemFail | 10/17/2025 17:02:02 | P2 | 2G | makkah | Generator_SG | TX NSA | MAK0273 | FLM_TE | [8 empty] | API | 10/18/2025 05:02:26 | 10/24/2025 01:40:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000167 | PCM-20251018-00000285 | TT-20251018-00324 | Telecom | Region_4 | JED0308 | JED0308 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 05:12:46 | 10/18/2025 06:46:51 | 10/18/2025 09:12:46 | STC : LINK DOWN B/W JED0162-JED0308 | 10/18/2025 05:12:18 | Critical | 1-12843 | OSC_LOS | 10/18/2025 05:12:07 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0308 | FLM_TE | [5 empty] | 0-1-C-9-F1AST4-2(RM2/TM2(FROM JED0162))-OSC:1 |  |  | API | 10/18/2025 05:12:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000168 | PCM-20251018-00000287 | TT-20251018-00326 | Telecom | Region_4 | JED2350-ZJe03-CSG-01 | JED2350 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 05:13:19 | 10/18/2025 05:13:19 | 10/18/2025 09:13:19 | DWDM_Physical Port Down at JED2350-ZJe03-CSG-01 @ Sceco | 10/18/2025 05:12:16 | Critical | 101-2505274 | Physical Port Down | 10/18/2025 05:12:08 | P3 | IPRAN | jeddah | Sceco | IPRAN SA | JED2350-ZJe03-CSG-01 | FLM_TE | [8 empty] | API | 10/18/2025 05:13:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000169 | PCM-20251018-00000288 | TT-20251018-00260 | Reference_telecom | Region_2 | KHJ2M8304 | KHJ2304 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hakim Ullah Raif Ullah Jan | 10/18/2025 05:14:28 | 10/18/2025 10:10:55 | 10/18/2025 17:14:28 | Cell RX Channel Interference Noise Power Unbalanced at KHJ2M8304-P3-CA-L800 @ Sceco | 10/18/2025 01:12:22 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/18/2025 01:12:17 | P3 | 4G | riyadh | Sceco | 2G NSA | KHJ2M8304 | FLM_TE |  |  | PCM-20251018-00000232 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/18/2025 05:14:28 | 10/18/2025 10:09:53 | 10/18/2025 10:10:04 |  |  | 10/18/2025 10:10:55 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000186 | PCM-20251018-00000320 | TT-20251018-00302 | Telecom | Region_4 | JED1M7434 | JED0434 |  |  |  | MALIK ATIF ZAMAN | 10/18/2025 05:42:22 | 10/19/2025 09:18:49 | 10/18/2025 11:42:22 | CELL OPERATION DEGRADED (Antenna Line Device failure) at JED1M7434-CA @ Generator_SG | 10/18/2025 04:50:23 | Major | 7654 | CELL OPERATION DEGRADED | 10/18/2025 04:50:12 | P2 | 4G | jeddah | Generator_SG | LTE_Cell SA | JED1M7434 | FLM_TE |  |  | PCM-20251018-00000265 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 05:42:22 | 10/19/2025 09:18:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000187 | PCM-20251018-00000322 | TT-20251018-00353 | EM | Region_4 | JED2191 | JED2191 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/18/2025 05:43:20 | 10/18/2025 09:01:33 | 10/18/2025 09:43:20 | 1(2G/LTE/5G) sites down under JED2191-P1-VIP/JED2191-P1-VIP @ Sceco | 10/18/2025 05:31:45 | Critical | 7706 | BTS O&M LINK FAILURE | 10/18/2025 05:31:42 | VIP | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED2191-P1-VIP | FLM_TE | JED2191 | Results: DOWN SITE HUB JED2191-P1-VIP JED2191 Summary: Hub: JED2191, Down Count: 1, Down Sites: JED2191-P1-VIP Alarm Summary: JED2191 No Active Alarm on HUB | PCM-20251018-00000314 | TE issue | TE issue |  | sites down |  | API | 10/18/2025 05:43:20 | 10/18/2025 09:01:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000188 | PCM-20251018-00000323 | TT-20251018-00330 | Telecom | Region_4 | JED1M7103 | JED0103 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 05:43:53 | 10/19/2025 17:44:57 | 10/18/2025 11:43:53 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7103-P2-CA-L900-L800-SBTS @ Sceco | 10/18/2025 05:12:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 05:12:09 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7103 | FLM_TE |  |  | PCM-20251018-00000291 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 05:43:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000189 | PCM-20251018-00000324 | TT-20251018-00341 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/18/2025 05:44:17 | 10/18/2025 13:26:33 | 10/18/2025 11:44:17 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/18/2025 05:21:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 05:21:48 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251018-00000299 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/18/2025 05:44:17 | 10/18/2025 13:26:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000219 | PCM-20251018-00000382 | TT-20251018-00362 | Reference_telecom | Region_2 | RIYA2U6868 | RIYA6168 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/18/2025 06:19:00 | 10/19/2025 09:44:32 | 10/18/2025 18:19:00 | Cell RX Channel Interference Noise Power Unbalanced at RIYA2U6868-P1-CA-VIP @ Sceco | 10/18/2025 02:41:27 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/18/2025 02:41:23 | VIP | 4G | riyadh | Sceco | 2G NSA | RIYA2U6868 | FLM_TE |  |  | PCM-20251018-00000318 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/18/2025 06:19:00 | 10/19/2025 09:44:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000220 | PCM-20251018-00000385 | TT-20251018-00419 | EM | Region_3 | RUSF9023 | RUSF9023 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/18/2025 06:26:39 | 10/18/2025 06:53:31 | 10/18/2025 10:26:39 | RELAY_ALARM_MAJOR at RUSF9023_NE_1 @ Generator_DG | 10/18/2025 06:25:58 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 08/13/2025 13:08:13 | P3 | Repeater | hail | Generator_DG | TX NSA | RUSF9023 | FLM_EM | [8 empty] | API | 10/18/2025 06:26:39 | 10/18/2025 06:53:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000221 | PCM-20251018-00000386 | TT-20251018-00421 | Telecom | Region_3 | YBDB0284 | YBDB0284 |  |  |  | Muhammad Sajjad R3 | 10/18/2025 06:27:09 | 10/18/2025 11:04:41 | 10/18/2025 12:27:09 | LAN_LOC at YBDB0284_HYB @ Sceco_STB | 10/18/2025 06:22:09 | Major | 1-12926 | LAN_LOC | 10/18/2025 06:22:00 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB0284 | FLM_TE | [5 empty] | 2-LOCAL-1(1-A)-73-E3CTU-6(GE1)-COM:1 |  |  | API | 10/18/2025 06:27:09 | 10/18/2025 11:04:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000222 | PCM-20251018-00000388 | TT-20251018-00422 | Telecom | Region_3 | YBDB0284 | YBDB0284 |  |  |  | Muhammad Sajjad R3 | 10/18/2025 06:27:10 | 10/18/2025 11:04:42 | 10/18/2025 12:27:10 | COMMUN_FAIL at YBDB0284_HYB @ Sceco_STB | 10/18/2025 06:23:18 | Major | 1-199 | COMMUN_FAIL | 10/18/2025 06:23:06 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB0284 | FLM_TE | [5 empty] | 3-TO YBDB2655(1-B)-73-F3AUX-OTHER |  |  | API | 10/18/2025 06:27:10 | 10/18/2025 11:04:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000226 | PCM-20251018-00000392 | TT-20251018-00125 | Reference_telecom | Region_6 | BHAB1M8015 | BHAB2015 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/18/2025 06:31:15 | 10/18/2025 08:42:46 | 10/18/2025 18:31:15 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHAB1M8015-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/18/2025 00:12:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 00:00:27 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8015 | FLM_TE |  | Thanks to check | PCM-20251018-00000338 | Thanks to check | Thanks to check |  |  |  | API | 10/18/2025 06:31:15 | 10/18/2025 08:40:51 | 10/18/2025 08:42:26 |  |  | 10/18/2025 08:42:46 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000236 | PCM-20251018-00000408 | TT-20251018-00442 | Telecom | Region_4 | JED0294 | JED0294 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/18/2025 06:51:32 | 10/18/2025 10:15:46 | 10/18/2025 12:51:32 | 1(5G) sites down under JED0294-GSM-P3 @ Generator_SG | 10/18/2025 06:43:01 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/18/2025 06:42:59 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5624656 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/18/2025 06:51:32 | 10/18/2025 10:14:56 | 10/18/2025 10:15:41 |  |  | 10/18/2025 10:15:46 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000260 | PCM-20251018-00000442 | TT-20251018-00475 | EM | Region_4 | JED0495 | JED0495 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/18/2025 07:21:03 | 10/18/2025 10:17:57 | 10/18/2025 13:21:03 | 1(2G/5G) sites down under JED0495-P3/JED0495-P3 @ Sceco | 10/18/2025 07:12:47 | Major | 7706 | BTS O&M LINK FAILURE | 10/18/2025 07:12:44 | P3 | 2G | jeddah | Sceco | 2G SA | JED0495-P3 | FLM_TE | JED0495 | Results: DOWN SITE HUB JED0495-P3 JED0495 Summary: Hub: JED0495, Down Count: 1, Down Sites: JED0495-P3 Alarm Summary: JED0495 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/18/2025 07:21:03 | 10/18/2025 10:14:57 | 10/18/2025 10:17:48 |  |  | 10/18/2025 10:17:57 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000265 | PCM-20251018-00000449 | TT-20251018-00489 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/18/2025 07:28:06 | 10/20/2025 16:34:28 | 10/18/2025 19:28:06 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/18/2025 07:21:47 | Minor | 1589 | AC Overfrequency | 10/18/2025 07:21:47 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/18/2025 07:28:06 | 10/18/2025 09:13:52 | 10/20/2025 16:34:19 |  |  | 10/20/2025 16:34:28 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000273 | PCM-20251018-00000464 | TT-20251018-00511 | Reference_telecom | Region_4 | JED2629 | JED2629 |  |  |  | Nazeer Mohammed | 10/18/2025 07:45:11 | 10/18/2025 10:14:57 | 10/18/2025 19:45:11 | Degrade observed in JED2629_XE towards 10.21.74.99 @ Sceco | 10/17/2025 19:44:44 | Minor |  | Degrade | 10/17/2025 19:44:36 | P3 | 2G | jeddah | Sceco | TX NSA | JED2629 | FLM_TE | [8 empty] | API | 10/18/2025 07:45:11 | 10/18/2025 10:14:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000289 | PCM-20251018-00000486 | TT-20251018-00530 | Telecom | Region_4 | JED0110 | JED0110 | Equipment | SFP_BTS | Replace SFP | Mohammed Ramadan A Abu Abid | 10/18/2025 08:07:23 | 10/18/2025 11:22:24 | 10/18/2025 14:07:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0110-G9-L8-L18-L21-NR2.6-NNR600-SBTS-P1-VIP @ Sceco | 10/18/2025 08:06:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 08:06:36 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0110 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 08:07:23 | 10/18/2025 08:59:47 | 10/18/2025 10:15:40 | 10/18/2025 10:15:43 | 10/18/2025 10:39:29 | 10/18/2025 11:22:24 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000303 | PCM-20251018-00000518 | TT-20251018-00572 | Telecom | Region_4 | JED1M8595 | JED2595 |  |  |  | BARKAT ALI MAIN HILAL | 10/18/2025 08:26:29 | 10/18/2025 11:21:55 | 10/18/2025 14:26:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8595-P3-CA-L800 @ Sceco | 10/18/2025 08:25:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 08:25:38 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8595 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 08:26:29 | 10/18/2025 11:21:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000306 | PCM-20251018-00000523 | TT-20251017-01527 | Telecom | Region_2 | RY1-OSN7500-(G)-SWAP | RY1 |  |  |  | Saddam hussain muhammad khan | 10/18/2025 08:28:39 | 10/18/2025 08:28:39 | 10/18/2025 14:28:39 | POWER_FAIL Active alarm at RY1-OSN7500-(G)-SWAP 24-GSCC-OTHER | 10/17/2025 22:42:19 | Major | 1-1 | R_LOS | 10/17/2025 22:42:19 | P3 | TX | riyadh | Sceco_STB | TX NSA | RY1-OSN7500 | FLM_TE |  |  | PCM-20251018-00000170 | Kindly need to prepare the card with the same version and same item code and mail shared with details | Kindly need to prepare the card with the same version and same item code and mail shared with details |  |  |  | API | 10/18/2025 08:28:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000313 | PCM-20251018-00000535 | TT-20251012-01989 | MW_HC | Region_1 | JBKH0069 | JBKH0069 |  |  |  | Rafiq Ahmed Elturifi | 10/18/2025 08:32:45 | 10/18/2025 10:04:15 | 10/18/2025 20:32:45 | Huawei MW HC_P2 Observing Errors at JBKH0069-JBL0897 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBKH0069-JBL0897 | FLM_TE | JBKH0069 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251017-00000156 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/18/2025 08:32:45 | 10/18/2025 10:04:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000329 | PCM-20251018-00000570 | TT-20251018-00614 | Reference_EM | Region_2 | RIY2823 | RIY2823 | Enviroment | Air Condition | Change Fan | Ahmed Mohamed Ibrahim Elnagar | 10/18/2025 08:52:49 | 10/20/2025 14:31:40 | 10/18/2025 20:52:49 | Air condition 1 failure alarm at RIY2823-P3_SRAN @ Sceco | 10/18/2025 08:42:18 | Minor | 65104 | Air condition 1 failure alarm | 10/18/2025 08:42:15 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2823 | FLM_EM | [8 empty] | API | 10/18/2025 08:52:49 | 10/18/2025 12:08:06 | 10/20/2025 14:17:50 | 10/20/2025 14:17:57 | 10/20/2025 14:17:59 | 10/20/2025 14:31:40 |  | Ahmed Mohamed Ibrahim Elnagar |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000342 | PCM-20251018-00000613 | TT-20251018-00650 | Telecom | Region_4 | JED0604 | JED0604 |  |  |  | MALIK ATIF ZAMAN | 10/18/2025 09:10:08 | 10/19/2025 09:18:50 | 10/18/2025 13:10:08 | HARD_ERR & BD_STATUS Alarms at JED0604 | 10/18/2025 09:06:32 | Critical | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/18/2025 09:06:32 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0604 | FLM_TE | [8 empty] | API | 10/18/2025 09:10:08 | 10/19/2025 09:18:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000351 | PCM-20251018-00000637 | TT-20251018-00659 | Reference_telecom | Region_1 | KBR2U6764 | KBR6064 |  |  |  | Meraj Husain Idd Baksh | 10/18/2025 09:16:34 | 10/21/2025 11:37:59 | 10/18/2025 15:16:34 | RF Unit VSWR Threshold Crossed at KBR2U6764-P1-VIP @ Sceco | 10/18/2025 06:16:33 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 06:16:21 | VIP | 4G | dammam | Sceco | LTE NSA | KBR2U6764 | FLM_TE | [8 empty] | API | 10/18/2025 09:16:34 | 10/18/2025 09:52:34 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000354 | PCM-20251018-00000643 | TT-20251018-00666 | Reference_telecom | Region_1 | KBR2U6763 | KBR6063 |  |  |  | Meraj Husain Idd Baksh | 10/18/2025 09:17:36 | 10/21/2025 11:38:00 | 10/18/2025 15:17:36 | RF Unit VSWR Threshold Crossed at KBR2U6763-P3 @ Sceco | 10/18/2025 06:17:42 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 06:17:28 | P3 | 4G | dammam | Sceco | LTE NSA | KBR2U6763 | FLM_TE | [8 empty] | API | 10/18/2025 09:17:36 | 10/18/2025 09:52:35 | [6 empty] | Building Authority |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20251018000385 | PCM-20251018-00000686 | TT-20251018-00710 | Telecom | Region_4 | RAB1M7474 | RAB0474 |  |  |  | Khizer Hayat | 10/18/2025 09:43:58 | 10/19/2025 17:44:47 | 10/18/2025 15:43:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at RAB1M7474-G9-NL8-L18-L21-SBTS-P2-USF @ Sceco | 10/18/2025 09:43:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 09:43:00 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | RAB1M7474 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 09:43:58 | 10/18/2025 11:47:49 | 10/18/2025 13:20:53 | 10/18/2025 13:20:55 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000399 | PCM-20251018-00000712 | TT-20251018-00207 | Telecom | Region_3 | YBDB2291 | YBDB2291 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Hossam Ali Ahmed Ali | 10/18/2025 09:52:44 | 10/19/2025 23:03:51 | 10/18/2025 15:52:44 | MW_IS-IS Adjacency Changed at YBDB0291-ASG-02 to RSP0001 | 10/18/2025 03:23:09 | Major | 2601366 | MPLS TE tunnel commit lost | 10/18/2025 03:23:09 | P1 | SRAN | yanbu | Generator_DG | IPRAN_NSA | MW_IS-IS Adjacency Changed at YBDB0291-ASG-02 to RSP0001 | FLM_TE | YBDB2291 | Dear FLM, MW link flapping at YBDB2291,Kindly need HC | PCM-20251018-00000694 | Dear FLM, MW link flapping at YBDB2291,Kindly need HC | Dear FLM, MW link flapping at YBDB2291,Kindly need HC |  |  |  | API | 10/18/2025 09:52:44 | 10/18/2025 10:52:53 | 10/19/2025 23:03:08 |  |  | 10/19/2025 23:03:51 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000402 | PCM-20251018-00000721 | TT-20251018-00737 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/18/2025 09:54:48 | 10/19/2025 12:35:00 | 10/18/2025 21:54:48 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/18/2025 09:46:26 | Minor | 7103 | HIGH TEMP | 10/18/2025 09:46:18 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/18/2025 09:54:48 | 10/19/2025 12:35:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251018000410 | PCM-20251018-00000738 | TT-20251018-00766 | Telecom | Region_4 | JED0157 | JED0157 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/18/2025 10:05:11 | 10/18/2025 10:05:11 | 10/18/2025 16:05:11 | IN_PWR_HIGH Alarm at JED0157 | 10/18/2025 10:00:30 | Major | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/18/2025 10:00:30 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0157 | FLM_TE | [8 empty] | API | 10/18/2025 10:05:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000414 | PCM-20251018-00000742 | TT-20251018-00751 | Telecom | Region_4 | JED1M7552 | JED0552 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 10:07:01 | 10/18/2025 10:07:01 | 10/18/2025 16:07:01 | 1(LTE) sites down under JED0552-CA-L900-L800-SBTS @ Sceco | 10/18/2025 09:58:46 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/18/2025 09:58:44 | P2 | 4G | jeddah | Sceco | LTE SA | JED0552-CA-L900-L800-SBTS | FLM_TE | JED0552 | Results: DOWN SITE HUB JED0552-CA-L900-L800-SBTS JED0552 Summary: Hub: JED0552, Down Count: 1, Down Sites: JED0552-CA-L900-L800-SBTS Alarm Summary: JED0552 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.97.160.100:8080/NE3S/1.0/] | sites down |  | API | 10/18/2025 10:07:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251018000418 | PCM-20251018-00000750 | TT-20251018-00778 | EM | [7 empty] | 10/18/2025 10:10:18 | 10/18/2025 10:10:18 | 10/18/2025 14:10:18 | AMBIENT_TEMP_FLUCT at 8809-SEC0004_OCS @ Sceco | 10/18/2025 10:08:32 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/18/2025 10:08:26 | P1 | DWDM |  | Sceco | DWDM NSA | 8809 | FLM_EM | [5 empty] | 0-TO RAS0098&9006-SEC0005(1-A) |  |  | API | 10/18/2025 10:10:18 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000421 | PCM-20251018-00000755 | TT-20251018-00782 | Reference_telecom | Region_5 | MAK0761 | MAK0761 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/18/2025 10:11:50 | 10/21/2025 19:57:01 | 10/18/2025 22:11:50 | ReplaceableUnitProblem observed in MAK0761 towards 10.10.190.67 @ Sceco | 10/17/2025 22:12:26 | Minor |  | ReplaceableUnitProblem | 10/17/2025 22:11:31 | P2 | 2G | makkah | Sceco | TX NSA | MAK0761 | FLM_TE | [8 empty] | API | 10/18/2025 10:11:50 | 10/21/2025 19:57:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000426 | PCM-20251018-00000760 | TT-20251018-00786 | Telecom | Region_4 | TAF0287 | TAF0287 |  |  |  | Ahmad Kamal Abdelmawla | 10/18/2025 10:15:29 | 10/18/2025 19:31:42 | 10/18/2025 16:15:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF0287-GSM-P3 @ Sceco | 10/18/2025 10:14:31 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 10:14:25 | P3 | 2G | taif | Sceco | 5G_Cell SA | TAF0287 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 10:15:29 | 10/18/2025 19:31:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000453 | PCM-20251018-00000808 | TT-20251018-00815 | Telecom | Region_2 | RIY2M7419 | RIY0419 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Waseem Shahzad Ghulam Rasool | 10/18/2025 10:36:45 | 10/18/2025 14:57:01 | 10/18/2025 22:36:45 | Cell Capability Degraded at RIY2M7419-P2-L900-L800 @ Sceco | 10/18/2025 10:27:22 | Minor | 29243 | Cell Capability Degraded | 10/18/2025 10:27:00 | P2 | 4G | riyadh | Sceco | 2G NSA | RIY2M7419 | FLM_TE |  |  | PCM-20251018-00000805 | Need FLM to make RF path for MRFU 0 4 0 (2102310CEU10CC002666) and swap this MRFU with other sector | Need FLM to make RF path for MRFU 0 4 0 (2102310CEU10CC002666) and swap this MRFU with other sector |  |  |  | API | 10/18/2025 10:36:45 | 10/18/2025 11:46:06 | 10/18/2025 14:10:40 | 10/18/2025 14:10:42 | 10/18/2025 14:10:50 | 10/18/2025 14:57:01 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000456 | PCM-20251018-00000811 | TT-20251018-00820 | EM | Region_4 | MUMA1M8198 | MUMA2198 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/18/2025 10:38:46 | 10/19/2025 12:35:00 | 10/18/2025 22:38:46 | TOWER LIGHT ALARM at MUMA1M8198-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/18/2025 10:30:39 | Minor | 7103 | TOWER LIGHT ALARM | 10/18/2025 10:30:27 | P3 | 4G | jeddah | Generator_SG | LTE NSA | MUMA1M8198 | FLM_EM | [5 empty] | TOWER LIGHT ALARM |  |  | API | 10/18/2025 10:38:46 | 10/19/2025 12:35:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000463 | PCM-20251018-00000823 | TT-20251018-00829 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/18/2025 10:43:52 | 10/21/2025 22:26:15 | 10/18/2025 22:43:52 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/18/2025 10:35:30 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/18/2025 10:35:20 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | Manual | 10/18/2025 10:43:52 | 10/21/2025 22:26:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000473 | PCM-20251018-00000844 | TT-20251018-00847 | EM | Region_3 | MDQS2436 | MDQS2436 |  |  |  | Ayman Mohamed Sayed Ahmed | 10/18/2025 10:54:42 | 10/18/2025 23:25:22 | 10/18/2025 22:54:42 | NETECO: Maintance Reminder at MDQS2436 @ Generator_DG | 10/18/2025 10:48:34 | Minor | 40563 | Maintance Reminder | 10/18/2025 10:48:34 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2436 | FLM_EM | [8 empty] | API | 10/18/2025 10:54:42 | 10/18/2025 23:25:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000494 | PCM-20251018-00000872 | TT-20251018-00874 | Telecom | Region_4 | SHB1M7670 | SHB0670 |  |  |  | Riasat Ali Allah Baksh | 10/18/2025 11:06:05 | 10/20/2025 21:24:34 | 10/18/2025 17:06:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/18/2025 11:05:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 11:05:18 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | SHB1M7670 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 11:06:05 | 10/20/2025 21:24:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000505 | PCM-20251018-00000897 | TT-20251018-00448 | Reference_telecom | Region_4 | JED0300 | JED0300 |  |  |  | MALIK ATIF ZAMAN | 10/18/2025 11:17:08 | 10/19/2025 09:18:52 | 10/18/2025 23:17:08 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0300-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/18/2025 05:01:14 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 04:51:33 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0300 | FLM_TE |  |  | PCM-20251018-00000784 | Dear FLM team, kindly check as IDU not visibile | Dear FLM team, kindly check as IDU not visibile |  |  |  | API | 10/18/2025 11:17:08 | 10/19/2025 09:18:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000509 | PCM-20251018-00000912 | TT-20251018-00910 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/18/2025 11:18:16 | 10/18/2025 11:18:16 | 10/18/2025 17:18:16 | Observing Multiple ALU CIDs flapped and restored B/W MAD - RIY - BUR | 10/18/2025 11:10:35 | Major | 5000003 | Link Down | 10/18/2025 11:10:35 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | RY1 | FLM_TE | [5 empty] | Observing Multiple ALU CIDs flapped and restored B/W MAD - RIY - BUR |  |  | API | 10/18/2025 11:18:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000513 | PCM-20251018-00000917 | TT-20251018-00912 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 11:19:00 | 10/18/2025 11:19:00 | 10/18/2025 17:19:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/18/2025 11:18:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 11:18:06 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7164 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 11:19:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000522 | PCM-20251018-00000928 | TT-20251018-00926 | Telecom | Region_4 | JED0600 | JED0600 |  |  |  | MALIK ATIF ZAMAN | 10/18/2025 11:24:10 | 10/19/2025 09:18:52 | 10/18/2025 17:24:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0600-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-WDM-FON @ Sceco | 10/18/2025 11:23:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 11:23:15 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0600 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 11:24:10 | 10/19/2025 09:18:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000562 | PCM-20251018-00001002 | TT-20251018-00976 | Telecom | Region_4 | JED1M7188 | JED0188 | Equipment | BSS_HW_Stuck | Reset BBU | MALIK ATIF ZAMAN | 10/18/2025 12:06:02 | 10/19/2025 17:44:56 | 10/18/2025 18:06:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7188-P3-CA-L900-L800-SBTS @ Sceco | 10/18/2025 12:05:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 12:05:11 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7188 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 12:06:02 | 10/19/2025 09:18:52 | 10/19/2025 10:30:06 | 10/19/2025 10:30:10 | 10/19/2025 11:45:26 | 10/19/2025 12:07:14 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000564 | PCM-20251018-00001005 | TT-20251018-00982 | Telecom | Region_4 | JED1M7884 | JED0884 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/18/2025 12:07:35 | 10/19/2025 10:29:27 | 10/18/2025 18:07:35 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7884-CA-L900-L800-SBTS @ Sceco | 10/18/2025 12:02:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 12:02:48 | P2 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7884 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/18/2025 12:07:35 | 10/18/2025 13:11:49 | 10/19/2025 10:29:17 |  |  | 10/19/2025 10:29:27 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000567 | PCM-20251018-00001008 | TT-20251018-00987 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/18/2025 12:10:10 | 10/19/2025 02:39:24 | 10/18/2025 16:10:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/18/2025 12:09:27 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 12:09:22 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 12:10:10 | 10/19/2025 02:39:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251018000566 | PCM-20251018-00001007 | TT-20251018-00986 | Telecom | Region_4 | JED0899 | JED0899 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/18/2025 12:10:10 | 10/19/2025 17:44:56 | 10/18/2025 18:10:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0899-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Generator_SG | 10/18/2025 12:09:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 12:09:08 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0899 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 12:10:10 | 10/19/2025 14:03:43 | 10/19/2025 14:03:50 | 10/19/2025 14:05:00 | 10/19/2025 14:18:46 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000590 | PCM-20251018-00001049 | TT-20251018-01026 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/18/2025 12:23:04 | 10/19/2025 02:39:24 | 10/19/2025 00:23:04 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/18/2025 12:14:39 | Minor | 7115 | BASE STATION INFORMATION | 10/18/2025 12:14:33 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/18/2025 12:23:04 | 10/19/2025 02:39:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000603 | PCM-20251018-00001069 | TT-20251018-01050 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/18/2025 12:34:27 | 10/18/2025 13:05:11 | 10/18/2025 18:34:27 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/18/2025 12:26:55 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/18/2025 12:26:51 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/18/2025 12:34:27 | 10/18/2025 13:05:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000607 | PCM-20251018-00001073 | TT-20251018-01054 | Reference_EM | Region_2 | RIYA6073 | RIYA6073 |  |  |  | Vignesh Sivakumar Sivakumar | 10/18/2025 12:37:01 | 10/18/2025 13:33:59 | 10/19/2025 00:37:01 | Low battery voltage at RIYA6073-P3_SRAN @ Sceco | 10/18/2025 12:26:31 | Minor | 65110 | Low battery voltage | 10/18/2025 12:26:26 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6073 | FLM_EM | [8 empty] | API | 10/18/2025 12:37:01 | 10/18/2025 13:33:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000612 | PCM-20251018-00001079 | TT-20251018-01060 | EM | Region_4 | JDJZ1M8418 | JDJZ2418 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/18/2025 12:39:06 | 10/19/2025 12:35:01 | 10/19/2025 00:39:06 | AIRCON 1 FAILURE at JDJZ1M8418-G9-L8-L18-SBTS-CAP @ Generator_SG | 10/18/2025 12:30:53 | Minor | 7103 | AIRCON 1 FAILURE | 10/18/2025 12:30:45 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JDJZ1M8418 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/18/2025 12:39:06 | 10/19/2025 12:35:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000619 | PCM-20251018-00001090 | TT-20251018-01066 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/18/2025 12:43:44 | 10/18/2025 15:27:01 | 10/19/2025 00:43:44 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/18/2025 12:35:35 | Minor | 7103 | AIRCON 2 FAILURE | 10/18/2025 12:35:30 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/18/2025 12:43:44 | 10/18/2025 15:27:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000629 | PCM-20251018-00001109 | TT-20251018-00850 | Telecom | Region_4 | JED2006 | JED2006 | Equipment | BSS_HW_fault | Replace RF Module | Ahmad Mostafa Hamouda Ibrahem | 10/18/2025 12:55:10 | 10/20/2025 11:51:21 | 10/18/2025 18:55:10 | BASE STATION SERVICE PROBLEM (RF Module filter input power missing) at JED2006-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/18/2025 10:50:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 10:49:56 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2006 | FLM_TE |  |  | PCM-20251018-00000847 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/18/2025 12:55:10 | 10/20/2025 10:33:11 | 10/20/2025 10:59:10 | 10/20/2025 10:59:15 | 10/20/2025 10:59:17 | 10/20/2025 11:51:21 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000630 | PCM-20251018-00001110 | TT-20251018-01089 | Reference_telecom | Region_2 | RIYB6038 | RIYB6038 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/18/2025 12:55:37 | 10/18/2025 14:27:01 | 10/18/2025 18:55:37 | RF Unit VSWR Threshold Crossed at RIYB6038-P3_SRAN @ Sceco | 10/18/2025 09:55:36 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 09:55:24 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6038 | FLM_TE | [8 empty] | API | 10/18/2025 12:55:37 | 10/18/2025 14:27:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000635 | PCM-20251018-00001117 | TT-20251018-01092 | Reference_EM | Region_2 | RIY0316 | RIY0316 | Enviroment | Fire Alarm | Reset Fire Pannel | Tanveer Ahmad Fateh Muhammad | 10/18/2025 12:57:41 | 10/19/2025 12:43:18 | 10/19/2025 00:57:41 | Fire Alarm at RIY0316-P3_SRAN @ Sceco | 10/18/2025 12:47:32 | Minor | 65119 | Fire Alarm | 10/18/2025 12:47:28 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY0316 | FLM_EM | [8 empty] | API | 10/18/2025 12:57:41 | 10/19/2025 12:39:13 | 10/19/2025 12:42:40 | 10/19/2025 12:42:42 | 10/19/2025 12:42:44 | 10/19/2025 12:43:18 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251018000640 | PCM-20251018-00001129 | TT-20251008-01969 | MW_HC | Region_5 | USMD0713 | USMD0713 |  |  |  | Amr Abdulla Ali Othman | 10/18/2025 13:03:24 | 10/18/2025 13:03:24 | 10/19/2025 01:03:24 | NEC MW HC_P0 Observing Performance Issue at USMD0704(10.154.140.169)--USMD0713(10.154.140.170) | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P2 | 2G | makkah | Sceco | TX NSA | USMD0704(10.154.140.169)--USMD0713(10.154.140.170) | FLM_TE |  |  | PCM-20251018-00000891 | Dear FLM team, kindly restore visibility for USMD0713 to can check | Dear FLM team, kindly restore visibility for USMD0713 to can check |  |  |  | API | 10/18/2025 13:03:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000643 | PCM-20251018-00001131 | TT-20251018-01095 | Telecom | Region_4 | HAW1M3328 | HAW0328 |  |  |  | Rashid Shafique | 10/18/2025 13:04:31 | 10/18/2025 14:28:57 | 10/18/2025 17:04:31 | 1(3G) sites down under HAW0328-P1-DIA/HAW1M3328-P1-DIA @ Sceco | 10/18/2025 12:57:02 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/18/2025 12:56:25 | P1 | 3G | taif | Sceco | 3G SA | HAW0328-P1-DIA | FLM_TE | HAW0328 | Results: DOWN SITE HUB HAW0328-P1-DIA HAW0328 Summary: Hub: HAW0328, Down Count: 1, Down Sites: HAW0328-P1-DIA Alarm Summary: HAW0328 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/18/2025 13:04:31 | 10/18/2025 14:28:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000649 | PCM-20251018-00001141 | TT-20251008-02100 | MW_HC | Region_5 | MAK0131 | MAK0131 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/18/2025 13:09:50 | 10/19/2025 14:53:07 | 10/19/2025 01:09:50 | Nokia MW HC_P0 Observing Performance Issue at MAK0131-MAK0518-9 | 10/08/2025 15:25:24 | Minor |  | LOF | 10/08/2025 15:25:24 | P2 | 2G | makkah | Sceco | TX NSA | MAK0131-MAK0518-9 | FLM_TE |  | Approved | PCM-20251018-00001056 | Dear FLM team, still observing PM errors over E.Band | Dear FLM team, still observing PM errors over E.Band |  |  |  | API | 10/18/2025 13:09:50 | 10/19/2025 14:53:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000656 | PCM-20251018-00001152 | TT-20251018-01082 | Telecom | Region_4 | ASQ0343 | ASQ0343 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Mudassar Bashir Bashir Ahmad | 10/18/2025 13:13:37 | 10/22/2025 11:18:44 | 10/18/2025 19:13:37 | BASE STATION ANTENNA LINE PROBLEM at ASQ0343-GSM-UMTS-P1-HUB-USF @ Sceco | 10/18/2025 12:43:56 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/18/2025 12:43:50 | P1 | 2G | adam | Sceco | 2G NSA | ASQ0343 | FLM_TE |  |  | PCM-20251018-00001099 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 13:13:37 | 10/19/2025 02:41:20 | 10/20/2025 20:44:35 |  |  | 10/20/2025 20:44:57 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000661 | PCM-20251018-00001162 | TT-20251018-00646 | Reference_telecom | Region_1 | HLHD0707 | HLHD0707 |  |  |  | Almmoez Almmoez | 10/18/2025 13:19:19 | 10/18/2025 13:38:46 | 10/19/2025 01:19:19 | IP Clock Link Failure at HLHD0707-P3_SRAN @ Generator_SG | 10/18/2025 06:08:02 | Minor | 26263 | IP Clock Link Failure | 10/18/2025 06:05:57 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0707 | FLM_TE |  |  | PCM-20251018-00000629 | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 13:19:19 | 10/18/2025 13:38:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000670 | PCM-20251018-00001181 | TT-20251018-01150 | Telecom | Region_2 | RIY2M7419 | RIY0419 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Waseem Shahzad Ghulam Rasool | 10/18/2025 13:25:54 | 10/18/2025 14:57:18 | 10/18/2025 19:25:54 | Cell Unavailable at RIY2M7419-P2-L900-L800 @ Sceco | 10/18/2025 13:24:30 | Major | 29240 | Cell Unavailable | 10/18/2025 13:22:57 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7419 | FLM_TE | [8 empty] | API | 10/18/2025 13:25:54 | 10/18/2025 13:30:01 | 10/18/2025 14:57:06 |  |  | 10/18/2025 14:57:18 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000672 | PCM-20251018-00001184 | TT-20251018-00876 | Reference_telecom | Region_2 | FAD0559 | FAD0559 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/18/2025 13:26:58 | 10/22/2025 18:45:40 | 10/19/2025 01:26:58 | External Clock Reference Problem at FAD0559-P3_SRAN @ Sceco | 10/18/2025 09:00:39 | Minor | 26262 | External Clock Reference Problem | 10/18/2025 08:06:11 | P3 | SRAN | majma | Sceco | 2G NSA | FAD0559 | FLM_EM |  |  | PCM-20251018-00000927 | We are observing RSL -90 at hub site MJAR0877 ,Suspected power issue, Dear EM FLM please check issue and solve | We are observing RSL -90 at hub site MJAR0877 ,Suspected power issue, Dear EM FLM please check issue and solve |  |  |  | API | 10/18/2025 13:26:58 | 10/18/2025 13:30:43 | 10/22/2025 18:45:32 |  |  | 10/22/2025 18:45:40 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000675 | PCM-20251018-00001190 | TT-20251018-01132 | Telecom | Region_1 | HFF2747 | HFF2747 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/18/2025 13:28:38 | 10/23/2025 17:09:24 | 10/18/2025 17:28:38 | 3(2G) 3(3G) sites down under HFF6022,HFF2747-P1-SHOP,HFF0933-P2/R1_HF_HWBSC01 @ Sceco | 10/18/2025 13:13:32 | Critical | 21825 | CSL Fault | 10/18/2025 13:13:29 | P1 | SRAN | hafouf | Sceco | 2G_3G SA | HFF2747-P1-SHOP 2G_3G,HFF0933-P2 2G_3G | FLM_EM | HFF2747 | Dear Team, Hub:- HFF2747 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251018-00001165 | Dear Team, Hub:- HFF2747 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- HFF2747 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/18/2025 13:28:38 | 10/18/2025 13:59:26 | 10/18/2025 14:02:55 |  |  | 10/18/2025 14:03:02 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000679 | PCM-20251018-00001193 | TT-20251018-01154 | Telecom | Region_4 | JED6025 | JED6025 |  |  |  | Mohamed Farag Abdelbary | 10/18/2025 13:29:40 | 10/19/2025 15:04:10 | 10/19/2025 01:29:40 | ODU CPU / Cable Open at JED6025-JED0686 on 10.154.146.13 @ Sceco | 10/18/2025 13:29:03 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/18/2025 12:59:35 | P3 | 2G | jeddah | Sceco | TX NSA | JED6025 | FLM_TE | [8 empty] | API | 10/18/2025 13:29:40 | 10/19/2025 15:04:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000680 | PCM-20251018-00001195 | TT-20251018-01156 | Telecom | Region_2 | RIY0419 | RIY0419 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Waseem Shahzad Ghulam Rasool | 10/18/2025 13:29:41 | 10/18/2025 14:10:34 | 10/18/2025 19:29:41 | BBU CPRI Interface Error at RIY0419-P2_SRAN @ Sceco | 10/18/2025 13:25:17 | Major | 26234 | BBU CPRI Interface Error | 10/18/2025 13:22:44 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0419 | FLM_TE | [8 empty] | API | 10/18/2025 13:29:41 | 10/18/2025 13:36:28 | 10/18/2025 13:39:50 | 10/18/2025 13:39:53 | 10/18/2025 13:39:55 | 10/18/2025 14:10:34 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000690 | PCM-20251018-00001205 | TT-20251018-00970 | Telecom | Region_1 | JBL0469 | JBL0469 |  |  |  | Tahir Mahmood Hafiz Yar | 10/18/2025 13:33:36 | 10/23/2025 17:52:00 | 10/18/2025 17:33:36 | 7(2G) 5(3G) 8(LTE) sites down under R1_JB_HWBSC01 @ Sceco | 10/18/2025 11:56:07 | Critical | 21825 | CSL Fault | 10/18/2025 11:56:05 | P1 | SRAN | jubail | Sceco_STB | 2G_3G_LTE SA | JBL0757-P3 2G_3G_LTE,JBL2939-P2 2G_3G_LTE,JBL2879-P3 2G_3G_LTE,JBL0040-P2 2G_3G_LTE,JBL0468-P2 2G_3G_LTE,JBL2993-P1-HUB 2G_LTE,JBL0421-P2 2G_LTE | FLM_TE | JBL0757 | Results: DOWN SITE HUB JBL0757-P3 JBL0757 JBL2939-P2 JBL0468 JBL2879-P3 JBL0421 JBL0040-P2 JBL0040 JBL0468-P2 JBL0468 JBL2993-P1-HUB JBL2993 JBL0421-P2 JBL0421 Summary: Hub: JBL0757, Down Count: 1, Down Sites: JBL0757-P3 Hub: JBL0468, Down Count: 2, Down Sites: JBL2939-P2, JBL0468-P2 Hub: JBL0421, Down Count: 2, Down Sites: JBL2879-P3, JBL0421-P2 Hub: JBL0040, Down Count: 1, Down Sites: JBL0040-P2 Hub: JBL2993, Down Count: 1, Down Sites: JBL2993-P1-HUB Alarm Summary: JBL0757 No Active Alarm on HUB JBL0468 No Active Alarm on HUB JBL0421 No Active Alarm on HUB JBL0040 No Active Alarm on HUB JBL2993 No Active Alarm on HUB | PCM-20251018-00001124 | As discussed there is no issue from IPRAN side no ISIS flapping and all sites are up and have MAC as replied to the mail No action is done from IPRAN side as well sites are auto restored | As discussed there is no issue from IPRAN side no ISIS flapping and all sites are up and have MAC as replied to the mail No action is done from IPRAN side as well sites are auto restored |  | sites down |  | API | 10/18/2025 13:33:36 | 10/18/2025 14:26:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000697 | PCM-20251018-00001218 | TT-20251018-00971 | Telecom | Region_1 | DMJB2087 | DMJB2087 |  |  |  | Rafiq Ahmed Elturifi | 10/18/2025 13:37:11 | 10/18/2025 13:43:46 | 10/18/2025 17:37:11 | 2(2G) 2(3G) 2(LTE) sites down under DMJB2087-P1-HUB,DAM0350-P3/R1_JB_HWBSC01 @ Sceco | 10/18/2025 11:56:09 | Critical | 21825 | CSL Fault | 10/18/2025 11:56:09 | P1 | SRAN | jubail | Sceco | 2G_3G_LTE SA | DAM0350-P3 2G_3G_LTE,DMJB2087-P1-HUB 2G_3G_LTE | FLM_TE | DAM0350 | Results: DOWN SITE HUB DAM0350-P3 DAM0350 DMJB2087-P1-HUB DMJB2087 Summary: Hub: DAM0350, Down Count: 1, Down Sites: DAM0350-P3 Hub: DMJB2087, Down Count: 1, Down Sites: DMJB2087-P1-HUB Alarm Summary: DAM0350 No Active Alarm on HUB DMJB2087 No Active Alarm on HUB | PCM-20251018-00001122 | Dear Team Kindly share P2 router in order to check if there is any issue from IPRAN side | Dear Team Kindly share P2 router in order to check if there is any issue from IPRAN side |  | sites down |  | API | 10/18/2025 13:37:11 | 10/18/2025 13:43:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000701 | PCM-20251018-00001224 | TT-20251018-00612 | Reference_telecom | Region_1 | HLHD0733 | HLHD0733 |  |  |  | Almmoez Almmoez | 10/18/2025 13:38:28 | 10/18/2025 13:38:47 | 10/19/2025 01:38:28 | IP Clock Link Failure at HLHD0733-P3_SRAN @ Power Cube | 10/18/2025 05:54:38 | Minor | 26263 | IP Clock Link Failure | 10/18/2025 05:52:02 | P3 | SRAN | rafha | Power Cube | 2G NSA | HLHD0733 | FLM_TE |  |  | PCM-20251018-00000589 | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 13:38:28 | 10/18/2025 13:38:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000703 | PCM-20251018-00001226 | TT-20251018-00617 | Reference_telecom | Region_1 | HFHD0704 | HFHD0704 |  |  |  | Almmoez Almmoez | 10/18/2025 13:38:47 | 10/18/2025 13:38:48 | 10/19/2025 01:38:47 | IP Clock Link Failure at HFHD0704-P1-HUB_SRAN @ Sceco_STB | 10/18/2025 05:55:31 | Minor | 26263 | IP Clock Link Failure | 10/18/2025 05:54:15 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | HFHD0704 | FLM_TE |  |  | PCM-20251018-00000584 | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 13:38:47 | 10/18/2025 13:38:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000707 | PCM-20251018-00001233 | TT-20251018-01188 | EM | Region_6 | BHAB1M8126 | BHAB2126 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/18/2025 13:42:36 | 10/19/2025 06:13:20 | 10/19/2025 01:42:36 | SMOKE ALARM at BHAB1M8126-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/18/2025 13:34:21 | Minor | 7103 | SMOKE ALARM | 10/18/2025 13:34:12 | P3 | 4G | Baha | Sceco | LTE NSA | BHAB1M8126 | FLM_EM | [5 empty] | SMOKE ALARM |  |  | API | 10/18/2025 13:42:36 | 10/19/2025 06:13:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018000714 | PCM-20251018-00001246 | TT-20250929-02388 | MW_HC | Region_1 | HFR2169 | HFR2169 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/18/2025 13:47:58 | 10/18/2025 14:03:53 | 10/19/2025 01:47:58 | NEC MW HC_P2 Observing Performance Issue at HFR2169(10.147.11.218)--RYH0120(10.147.11.219) | 09/29/2025 16:35:36 | Minor |  | LOF | 09/29/2025 16:35:36 | P1 | SRAN | hafr | Generator_SG | TX NSA | HFR2169(10.147.11.218)--RYH0120(10.147.11.219) | FLM_TE |  | dear team , link is flapping , kindly check this issue | PCM-20251018-00000173 | Link not clear last 24 H , please check | Link not clear last 24 H , please check |  |  |  | API | 10/18/2025 13:47:58 | 10/18/2025 14:03:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000725 | PCM-20251018-00001266 | TT-20251018-01218 | EM | Region_4 | HHR0889 | HHR0889 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/18/2025 13:55:30 | 10/23/2025 12:57:13 | 10/18/2025 19:55:30 | GENERATOR1 + GENERATOR2 2 FAILURE at HHR0889-GSM-P1-VIP-HHR @ Generator_SG | 10/18/2025 13:47:11 | Major | 7103 | GENERATOR1 + GENERATOR2 2 FAILURE | 10/18/2025 13:47:02 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0889 | FLM_EM | [5 empty] | GENERATOR1 + GENERATOR2 2 FAILURE |  |  | API | 10/18/2025 13:55:30 | 10/23/2025 12:57:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000734 | PCM-20251018-00001282 | TT-20251018-01233 | Reference_telecom | Region_4 | THO0619 | THO0619 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/18/2025 14:05:19 | 10/20/2025 13:54:54 | 10/19/2025 02:05:19 | BASE STATION INFORMATION (Unit temperature is high) at THO0619-GSM-P2 @ Sceco | 10/18/2025 13:25:14 | Minor | 7115 | BASE STATION INFORMATION | 10/18/2025 13:25:08 | P2 | 2G | jeddah | Sceco | 2G NSA | THO0619 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/18/2025 14:05:19 | 10/18/2025 16:31:27 | 10/20/2025 13:54:48 |  |  | 10/20/2025 13:54:54 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000741 | PCM-20251018-00001290 | TT-20251018-01239 | Telecom | Region_5 | JURY0679 | JURY0679 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/18/2025 14:09:12 | 10/19/2025 21:12:32 | 10/19/2025 02:09:12 | AS BO Requested : HC FOR Link , PM errors on JURY0805-JURY0679 | 10/18/2025 14:08:39 | Minor | 113388 | LOF | 10/18/2025 14:08:39 | P1 | 2G | makkah | Generator_SG | TX NSA | JURY0805-JURY0679 | FLM_TE | [5 empty] | AS BO Requested : HC FOR Link , PM errors on JURY0805-JURY0679 |  |  | API | 10/18/2025 14:09:12 | 10/19/2025 21:12:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000754 | PCM-20251018-00001310 | TT-20251018-00613 | Reference_telecom | Region_1 | RAF2582 | RAF2582 |  |  |  | Almmoez Almmoez | 10/18/2025 14:16:32 | 10/18/2025 14:37:57 | 10/19/2025 02:16:32 | IP Clock Link Failure at RAF2582-P1-USF-HUB_SRAN @ Sceco | 10/18/2025 05:54:38 | Minor | 26263 | IP Clock Link Failure | 10/18/2025 05:52:01 | P1 | SRAN | rafha | Sceco | 2G NSA | RAF2582 | FLM_TE |  |  | PCM-20251018-00000580 | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on HFHD0703-RAF2514 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 14:16:32 | 10/18/2025 14:37:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000773 | PCM-20251018-00001344 | TT-20251018-01151 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 14:32:25 | 10/18/2025 14:32:25 | 10/19/2025 02:32:25 | BASE STATION ANTENNA LINE PROBLEM at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/18/2025 13:19:29 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/18/2025 13:19:22 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0539 | FLM_TE |  |  | PCM-20251018-00001183 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 14:32:25 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000774 | PCM-20251018-00001345 | TT-20251018-01155 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/18/2025 14:33:03 | 10/18/2025 22:26:02 | 10/19/2025 02:33:03 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/18/2025 13:22:22 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/18/2025 13:22:16 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251018-00001194 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 14:33:03 | 10/18/2025 22:26:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000776 | PCM-20251018-00001347 | TT-20251008-01763 | MW_HC | Region_1 | JBL0478 | JBL0478 |  |  |  | Tahir Mahmood Hafiz Yar | 10/18/2025 14:33:42 | 10/18/2025 18:03:53 | 10/19/2025 02:33:42 | Huawei MW HC_P1 Observing Errors at JBL0478-JBL2110 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P2 | SRAN | jubail | Generator_SG | TX NSA | JBL0478-JBL2110 | FLM_TE |  |  | PCM-20251018-00000051 | E-Band counting Errors not clear last 24H, please check | E-Band counting Errors not clear last 24H, please check |  |  |  | API | 10/18/2025 14:33:42 | 10/18/2025 18:03:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000781 | PCM-20251018-00001354 | TT-20251018-01179 | Reference_telecom | Region_4 | THO1M7619 | THO0619 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/18/2025 14:36:31 | 10/20/2025 13:54:39 | 10/18/2025 20:36:31 | CELL FAULTY (Failure in optical interface) at THO1M7619-CA-P3 @ Sceco | 10/18/2025 13:00:23 | Major | 7653 | CELL FAULTY | 10/18/2025 13:33:05 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | THO1M7619 | FLM_TE |  |  | PCM-20251018-00001223 | Need to check connectvity between BBMOD to RMOD | Need to check connectvity between BBMOD to RMOD |  |  |  | API | 10/18/2025 14:36:31 | 10/18/2025 16:31:28 | 10/20/2025 13:54:31 |  |  | 10/20/2025 13:54:39 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000783 | PCM-20251018-00001356 | TT-20251018-01328 | Telecom | Region_4 | TAF2115 | TAF2115 | Equipment | SFP_BTS | Replace SFP | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/18/2025 14:39:00 | 10/19/2025 12:24:41 | 10/19/2025 02:39:00 | PT:: FLM need to check SFP degradation at TAF2115/R5 (BO request) | 10/18/2025 14:38:13 | Minor | 7115 | BASE STATION INFORMATION | 10/18/2025 14:38:13 | P2 | 2G | taif | Sceco | 2G_3G_LTE_5G NSA | TAF2115 | FLM_TE | [8 empty] | API | 10/18/2025 14:39:00 | 10/18/2025 17:37:46 | 10/19/2025 11:51:16 | 10/19/2025 11:51:19 | 10/19/2025 11:51:22 | 10/19/2025 12:24:41 |  | SHEHERYAR KHAN MUNAMMAD NAWAZ |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000786 | PCM-20251018-00001362 | TT-20251018-00664 | Reference_telecom | Region_1 | KBR2U6181 | KBR6081 |  |  |  | Meraj Husain Idd Baksh | 10/18/2025 14:44:49 | 10/18/2025 17:36:08 | 10/19/2025 02:44:49 | External Clock Reference Problem at KBR2U6181-P3 @ Sceco | 10/18/2025 06:20:16 | Minor | 26262 | External Clock Reference Problem | 10/18/2025 06:16:54 | P3 | 2G | dammam | Sceco | 2G NSA | KBR2U6181 | FLM_TE |  |  | PCM-20251018-00001305 | MW alarms , PM Errors and RSL degradation observed on KBR6081-KBR0195 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on KBR6081-KBR0195 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 14:44:49 | 10/18/2025 17:36:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000787 | PCM-20251018-00001363 | TT-20251018-01335 | Telecom | Region_1 | DAM0130 | DAM0130 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/18/2025 14:45:08 | 10/18/2025 16:35:52 | 10/19/2025 02:45:08 | RF Unit Temperature Unacceptable at DAM0130-P2_SRAN @ Sceco | 10/18/2025 14:37:56 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/18/2025 14:37:53 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0130 | FLM_TE | [8 empty] | API | 10/18/2025 14:45:08 | 10/18/2025 16:35:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000798 | PCM-20251018-00001378 | TT-20251018-01350 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/18/2025 14:50:47 | 10/18/2025 16:35:52 | 10/19/2025 02:50:47 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/18/2025 14:43:36 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/18/2025 14:43:33 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/18/2025 14:50:47 | 10/18/2025 16:35:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000802 | PCM-20251018-00001390 | TT-20251018-01362 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/18/2025 15:00:06 | 10/19/2025 10:24:36 | 10/19/2025 03:00:06 | Air condition 1 failure alarm at RIY2866-P3_SRAN-PC @ Sceco | 10/18/2025 14:49:54 | Minor | 65104 | Air condition 1 failure alarm | 10/18/2025 14:49:50 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/18/2025 15:00:06 | 10/19/2025 10:24:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251018000807 | PCM-20251018-00001399 | TT-20251018-01339 | Telecom | Region_4 | JED1M8170 | JED2170 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/18/2025 15:04:49 | 10/20/2025 12:23:52 | 10/19/2025 03:04:49 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED1M8170-CA-L1800-L800-P3-SBTS @ Sceco | 10/18/2025 14:42:53 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 14:42:45 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8170 | FLM_TE |  |  | PCM-20251018-00001368 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/18/2025 15:04:49 | 10/18/2025 17:54:47 | 10/20/2025 12:23:47 | 10/20/2025 12:23:49 | 10/20/2025 12:23:52 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000839 | PCM-20251018-00001439 | TT-20251018-01410 | EM | Region_6 | NMS1M7175 | NMS0175 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/18/2025 15:22:18 | 10/22/2025 23:42:21 | 10/19/2025 03:22:18 | RECTIFIER MODULE FAILURE at NMS1M7175-G9-L8-L18-NL21-SBTS-P2-WBB-G3 @ Sceco | 10/18/2025 15:20:22 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/18/2025 13:45:40 | P2 | 4G | namas | Sceco | LTE NSA | NMS1M7175 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/18/2025 15:22:18 | 10/22/2025 23:42:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251018000894 | PCM-20251018-00001529 | TT-20251018-01509 | Reference_telecom | Region_5 | SHD0782 | SHD0782 |  |  |  | Hassan Ezzelarab Ali Mohamed | 10/18/2025 16:05:10 | 10/18/2025 16:05:10 | 10/19/2025 04:05:10 | ReplaceableUnitProblem observed in SHD0782 towards 10.10.151.18 @ Generator_SG | 10/18/2025 04:06:42 | Minor |  | ReplaceableUnitProblem | 10/18/2025 04:04:44 | P2 | 2G | makkah | Generator_SG | TX NSA | SHD0782 | FLM_TE | [8 empty] | API | 10/18/2025 16:05:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000911 | PCM-20251018-00001558 | TT-20251018-01537 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | SFP_BTS | Clean SFP | Waseem Shahzad Ghulam Rasool | 10/18/2025 16:20:41 | 10/20/2025 07:56:15 | 10/19/2025 04:20:41 | RF Unit CPRI Interface Error at RIYB6158-DCU3 @ Sceco | 10/18/2025 16:13:51 | Minor | 26504 | RF Unit CPRI Interface Error | 10/18/2025 16:13:33 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/18/2025 16:20:41 | 10/20/2025 07:53:06 | 10/20/2025 07:56:08 |  |  | 10/20/2025 07:56:15 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000919 | PCM-20251018-00001572 | TT-20251018-01545 | Telecom | Region_4 | JED0519 | JED0519 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/18/2025 16:30:30 | 10/19/2025 17:45:00 | 10/18/2025 22:30:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0519-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/18/2025 16:29:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 16:29:23 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0519 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 16:30:30 | 10/18/2025 17:41:26 | 10/19/2025 10:34:12 |  |  | 10/19/2025 10:34:25 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000926 | PCM-20251018-00001584 | TT-20251018-01562 | Telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/18/2025 16:39:18 | 10/19/2025 09:18:54 | 10/18/2025 22:39:18 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8061-CA-L800-SBTS @ Sceco | 10/18/2025 16:38:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 16:38:10 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8061 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 16:39:18 | 10/19/2025 09:18:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018000927 | PCM-20251018-00001585 | TT-20251018-01565 | Telecom | Region_4 | JED1MN0196 | JED0196 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 16:39:48 | 10/18/2025 16:39:48 | 10/18/2025 22:39:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0196-NR2.6 @ Sceco | 10/18/2025 16:39:01 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 16:38:49 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0196 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 16:39:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000935 | PCM-20251018-00001597 | TT-20251018-01550 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/18/2025 16:44:42 | 10/21/2025 18:22:09 | 10/18/2025 22:44:42 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/18/2025 16:25:45 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/18/2025 16:25:34 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251018-00001576 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/18/2025 16:44:42 | 10/19/2025 15:04:11 | 10/21/2025 18:22:02 |  |  | 10/21/2025 18:22:09 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000952 | PCM-20251018-00001619 | TT-20251018-01588 | Telecom | Region_1 | HFR2873 | HFR2873 | Equipment | SFP_BTS | Replace SFP | Muhammad Anwar Hussain Akhtar Hussain | 10/18/2025 16:56:20 | 10/18/2025 19:40:45 | 10/18/2025 22:56:20 | NR Cell Unavailable at HFR2873-P2_SRAN @ Sceco | 10/18/2025 16:49:30 | Major | 29841 | NR Cell Unavailable | 10/18/2025 16:47:57 | P2 | SRAN | hafr | Sceco | 5G SA | HFR2873 | FLM_TE | [8 empty] | API | 10/18/2025 16:56:20 | 10/18/2025 18:18:27 | 10/18/2025 18:19:02 | 10/18/2025 18:19:05 | 10/18/2025 18:41:35 | 10/18/2025 19:40:45 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000953 | PCM-20251018-00001620 | TT-20251018-01575 | EM | Region_4 | MKYL0916 | MKYL0916 |  |  |  | Mohamed Ibrahim Mohamed Batn | 10/18/2025 16:56:33 | 10/20/2025 14:22:01 | 10/18/2025 22:56:33 | 1(2G/3G/5G) sites down under MKYL0916-P3/MKYL0916-P3 @ Generator_SG | 10/18/2025 16:48:31 | Major | 7706 | BTS O&M LINK FAILURE | 10/18/2025 16:48:24 | P3 | 2G | alaith | Generator_SG | 2G_3G SA | MKYL0916-P3 | FLM_EM | MKYL0916 | Results: DOWN SITE HUB MKYL0916-P3 MKYL0916 Summary: Hub: MKYL0916, Down Count: 1, Down Sites: MKYL0916-P3 Alarm Summary: MKYL0916 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/18/2025 16:56:33 | 10/20/2025 14:22:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000970 | PCM-20251018-00001641 | TT-20251018-00027 | Reference_telecom | Region_6 | HRD1M7778 | HRD0778 | Equipment | SW | Issue was solved after softaware configuration | Muhammad Usman Muhammad Zia ul haq | 10/18/2025 17:06:50 | 10/18/2025 22:19:49 | 10/18/2025 23:06:50 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at HRD1M7778-CA-L800-P1-VIP-SBTS @ Generator_SG | 10/17/2025 22:28:43 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 22:27:15 | VIP | 4G | derb | Generator_SG | LTE NSA | HRD1M7778 | FLM_TE |  |  | PCM-20251018-00000863 | Please check and update PL observed in site | Please check and update PL observed in site |  |  |  | API | 10/18/2025 17:06:50 | 10/18/2025 22:18:30 | 10/18/2025 22:19:42 |  |  | 10/18/2025 22:19:49 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000974 | PCM-20251018-00001647 | TT-20251018-01465 | Reference_telecom | Region_2 | RIYB2U6786 | RIYB6086 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/18/2025 17:09:04 | 10/19/2025 09:44:33 | 10/19/2025 05:09:04 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6786-L1800-CA-P3 @ Sceco | 10/18/2025 12:48:40 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/18/2025 12:48:37 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6786 | FLM_TE |  |  | PCM-20251018-00001495 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/18/2025 17:09:04 | 10/19/2025 09:44:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018000989 | PCM-20251018-00001683 | TT-20251006-01620 | MW_HC | Region_3 | HQL2038 | HQL2038 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Hossam Ali Ahmed Ali | 10/18/2025 17:28:31 | 10/22/2025 18:41:33 | 10/19/2025 05:28:31 | (As per BO Request) NEC MW HC Observing PM errors and RSL degradation at MW link HQL2038 dir HQL0980 | 10/06/2025 15:02:06 | Minor | 1-631 | MW_LOF | 10/06/2025 15:02:06 | P3 | SRAN | tabouk | Sceco | TX NSA | HQL2038 | FLM_TE | HQL2038 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251018-00001670 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/18/2025 17:28:31 | 10/18/2025 22:24:21 | 10/22/2025 18:41:21 |  |  | 10/22/2025 18:41:33 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000990 | PCM-20251018-00001684 | TT-20251008-01770 | MW_HC | Region_3 | HAL2265 | HAL2265 |  |  |  | Mazin Meshary AlEnzi | 10/18/2025 17:29:06 | 10/18/2025 19:17:59 | 10/19/2025 05:29:06 | Huawei MW HC_P2 Observing Errors at HAL2265-HAL0091 | 10/08/2025 15:20:17 | Minor |  | LOF | 10/08/2025 15:20:17 | P3 | SRAN | hail | Sceco | TX NSA | HAL2265-HAL0091 | FLM_TE | HAL2265 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251018-00001673 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/18/2025 17:29:06 | 10/18/2025 19:17:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018000993 | PCM-20251018-00001688 | TT-20251018-01649 | EM | Region_1 | RST0087 | RST0087 |  |  |  | Omer Elfadoul Mohamed Ibrahim | 10/18/2025 17:31:58 | 10/18/2025 20:54:22 | 10/19/2025 05:31:58 | Generator failure at RST0087-P3-USF_SRAN-PC @ Power Cube | 10/18/2025 17:21:58 | Minor | 65114 | Generator failure | 10/18/2025 17:21:54 | P3 | SRAN | dammam | Power Cube | 2G NSA | RST0087 | FLM_EM | [8 empty] | API | 10/18/2025 17:31:58 | 10/18/2025 20:54:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251018000995 | PCM-20251018-00001691 | TT-20251018-01653 | Telecom | Region_2 | RY2 | RY2 |  |  |  | Saddam hussain muhammad khan | 10/18/2025 17:34:16 | 10/18/2025 17:34:16 | 10/18/2025 23:34:16 | Observing multiple ALU CIDs flapped and resorted B/W RIY - MAK - TF | 10/18/2025 17:30:36 | Major | 5000003 | Link Down | 10/18/2025 17:30:36 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | RY2 | FLM_TE | [5 empty] | Observing multiple ALU CIDs flapped and resorted B/W RIY - MAK - TF |  |  | API | 10/18/2025 17:34:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001009 | PCM-20251018-00001719 | TT-20251018-01678 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/18/2025 17:48:31 | 10/18/2025 18:35:38 | 10/18/2025 23:48:31 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/18/2025 14:48:26 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 14:48:12 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/18/2025 17:48:31 | 10/18/2025 18:35:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001020 | PCM-20251018-00001744 | TT-20251018-01696 | Telecom | Region_4 | BHR0310 | BHR0310 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/18/2025 17:55:45 | 10/19/2025 17:45:02 | 10/18/2025 23:55:45 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/18/2025 17:55:06 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 17:55:02 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | BHR0310 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 17:55:45 | 10/19/2025 09:38:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001029 | PCM-20251018-00001755 | TT-20251018-01702 | Telecom | Region_4 | JED1U6777 | JED6077 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/18/2025 18:02:54 | 10/21/2025 18:20:56 | 10/19/2025 00:02:54 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6777-P3 @ Sceco | 10/18/2025 17:52:10 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/18/2025 17:52:04 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6777 | FLM_TE |  |  | PCM-20251018-00001749 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/18/2025 18:02:54 | 10/19/2025 15:04:11 | 10/21/2025 18:20:48 |  |  | 10/21/2025 18:20:56 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001030 | PCM-20251018-00001757 | TT-20251018-01709 | Telecom | Region_4 | JED2629 | JED2629 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/18/2025 18:03:00 | 10/20/2025 13:54:11 | 10/19/2025 00:03:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2629-G9-L8-L18-L21-NR2.6-P3-SBTS-CAP @ Sceco | 10/18/2025 18:02:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 18:02:01 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2629 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 18:03:00 | 10/20/2025 13:30:25 | 10/20/2025 13:54:05 |  |  | 10/20/2025 13:54:11 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001036 | PCM-20251018-00001778 | TT-20251018-00888 | Telecom | Region_6 | BDN1M7056 | BDN0056 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/18/2025 18:09:34 | 10/18/2025 20:35:37 | 10/19/2025 06:09:34 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at BDN1M7056-G9-L8-NL18-NL21-SBTS-P3 @ Sceco | 10/18/2025 11:09:35 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 03:02:06 | P2 | 4G | Albaha | Sceco | LTE NSA | BDN1M7056 | FLM_TE |  |  | PCM-20251018-00001653 | Dear FLM team, kindly perform HC for MW BDN0056-BAH0836 | Dear FLM team, kindly perform HC for MW BDN0056-BAH0836 |  |  |  | API | 10/18/2025 18:09:34 | 10/18/2025 18:53:02 | 10/18/2025 20:35:21 |  |  | 10/18/2025 20:35:37 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018001037 | PCM-20251018-00001782 | TT-20251018-01722 | Reference_telecom | Region_4 | JED0739 | JED0739 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/18/2025 18:13:39 | 10/18/2025 18:13:39 | 10/19/2025 06:13:39 | Fronthaul loop back connectivity check failure at JED0739-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/18/2025 17:41:38 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/18/2025 17:41:28 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0739 | FLM_TE |  |  | PCM-20251018-00001780 | FLM need to check locally | FLM need to check locally |  |  |  | API | 10/18/2025 18:13:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001038 | PCM-20251018-00001791 | TT-20251018-01727 | Reference_telecom | Region_2 | RIYB2U6756 | RIYB6056 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/18/2025 18:16:32 | 10/19/2025 09:44:33 | 10/19/2025 06:16:32 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6756-CA-L800-P3 @ Sceco | 10/18/2025 15:13:36 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/18/2025 15:13:32 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6756 | FLM_TE |  |  | PCM-20251018-00001783 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/18/2025 18:16:32 | 10/19/2025 09:44:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001040 | PCM-20251018-00001792 | TT-20251018-01733 | Reference_telecom | Region_2 | RIYB2U6754 | RIYB6054 | Equipment | BSS_HW_fault | Replace GPS Antenna | Waseem Shahzad Ghulam Rasool | 10/18/2025 18:16:46 | 10/20/2025 07:54:21 | 10/19/2025 06:16:46 | GNSS Antenna Fault at RIYB2U6754-P3 @ Sceco | 10/18/2025 14:20:39 | Minor | 26125 | GNSS Antenna Fault | 10/18/2025 14:19:05 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6754 | FLM_TE | [8 empty] | API | 10/18/2025 18:16:46 | 10/20/2025 07:51:20 | 10/20/2025 07:53:54 |  |  | 10/20/2025 07:54:21 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001042 | PCM-20251018-00001794 | TT-20251018-01735 | Telecom | Region_4 | JED1M8602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/18/2025 18:17:58 | 10/19/2025 09:18:54 | 10/19/2025 00:17:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8602-CA-L800-P3 @ Sceco | 10/18/2025 18:17:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 18:17:08 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8602 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 18:17:58 | 10/19/2025 09:18:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001045 | PCM-20251018-00001799 | TT-20251018-01743 | Telecom | Region_4 | HAW1M8351 | HAW2351 |  |  |  | Rashid Shafique | 10/18/2025 18:21:34 | 10/18/2025 19:54:53 | 10/19/2025 00:21:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAW1M8351-P3-CA-L800 @ Sceco | 10/18/2025 18:20:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 18:20:34 | P2 | 4G | taif | Sceco | 5G_Cell SA | HAW1M8351 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 18:21:34 | 10/18/2025 19:54:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001049 | PCM-20251018-00001805 | TT-20251018-01009 | Telecom | Region_6 | BHAB1M7816 | BHAB0816 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/18/2025 18:23:30 | 10/19/2025 02:57:25 | 10/19/2025 00:23:30 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at BHAB1M7816-L800-SBTS @ Sceco_STB | 10/18/2025 12:13:09 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 03:02:41 | P3 | 4G | abha | Sceco_STB | LTE NSA | BHAB1M7816 | FLM_TE |  |  | PCM-20251018-00001763 | Dear access BO, TX path clear from our side | Dear access BO, TX path clear from our side |  |  |  | API | 10/18/2025 18:23:30 | 10/19/2025 00:14:32 | 10/19/2025 02:57:05 |  |  | 10/19/2025 02:57:25 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001055 | PCM-20251018-00001819 | TT-20251018-01759 | Reference_telecom | Region_5 | MAK2967 | MAK2967 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Israr Ahmed Muhammad Ghauri | 10/18/2025 18:32:05 | 10/21/2025 15:03:29 | 10/19/2025 00:32:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2967-G9-L8-L18-L21-NR2.6-P3-SBTS (Ref:TT-20251016-00304) @ Generator_SG | 10/16/2025 03:25:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/16/2025 03:25:13 | P3 | 2G | makkah | Generator_SG | 5G_Cell SA | MAK2967 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 18:32:05 | 10/21/2025 10:01:05 | 10/21/2025 10:01:15 | 10/21/2025 10:01:18 |  | 10/21/2025 15:03:29 |  | Israr Ahmed Muhammad Ghauri |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001058 | PCM-20251018-00001824 | TT-20251018-01758 | Telecom | Region_1 | JBL2M7998 | JBL0998 |  |  |  | Tahir Mahmood Hafiz Yar | 10/18/2025 18:33:49 | 10/18/2025 22:00:24 | 10/19/2025 06:33:49 | Cell Capability Degraded at JBL2M7998-P3 @ Sceco | 10/18/2025 18:26:42 | Minor | 29243 | Cell Capability Degraded | 10/18/2025 18:24:47 | P3 | 4G | jubail | Sceco | 2G NSA | JBL2M7998 | FLM_TE |  |  | PCM-20251018-00001818 | Dear FLM, thanks to check | Dear FLM, thanks to check |  |  |  | API | 10/18/2025 18:33:49 | 10/18/2025 22:00:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001060 | PCM-20251018-00001826 | TT-20251018-01755 | EM | Region_4 | JED2979 | JED2979 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/18/2025 18:34:03 | 10/18/2025 21:47:26 | 10/18/2025 22:34:03 | 1(2G/LTE/5G) sites down under JED2979-P1-VIP/JED2979-P1-VIP @ Generator_SG | 10/18/2025 18:28:04 | Critical | 7706 | BTS O&M LINK FAILURE | 10/18/2025 18:27:57 | VIP | 2G | jeddah | Generator_SG | 2G_5G SA | JED2979-P1-VIP | FLM_EM | JED2979 | Results: DOWN SITE HUB JED2979-P1-VIP JED2979 Summary: Hub: JED2979, Down Count: 1, Down Sites: JED2979-P1-VIP Alarm Summary: JED2979 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/18/2025 18:34:03 | 10/18/2025 19:14:28 | 10/18/2025 21:47:10 |  |  | 10/18/2025 21:47:26 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001064 | PCM-20251018-00001834 | TT-20251018-01775 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | SFP_BTS | Re-Plug SFP | Waseem Shahzad Ghulam Rasool | 10/18/2025 18:39:09 | 10/20/2025 07:56:34 | 10/19/2025 06:39:09 | RF Unit Maintenance Link Failure at RIYB6158-DCU3 @ Sceco | 10/18/2025 18:33:41 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/18/2025 18:33:38 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/18/2025 18:39:09 | 10/20/2025 07:52:58 | 10/20/2025 07:56:24 |  |  | 10/20/2025 07:56:34 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001067 | PCM-20251018-00001841 | TT-20251018-01778 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | SFP_BTS | Clean SFP | Waseem Shahzad Ghulam Rasool | 10/18/2025 18:43:48 | 10/20/2025 07:56:02 | 10/19/2025 06:43:48 | RF Unit Clock Problem at RIYB6158-DCU3 @ Sceco | 10/18/2025 18:36:11 | Minor | 26538 | RF Unit Clock Problem | 10/18/2025 18:35:39 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/18/2025 18:43:48 | 10/20/2025 07:52:49 | 10/20/2025 07:55:51 |  |  | 10/20/2025 07:56:02 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001069 | PCM-20251018-00001844 | TT-20251018-01784 | Reference_telecom | Region_4 | TAF2405 | TAF2405 |  |  |  | Ahmad Kamal Abdelmawla | 10/18/2025 18:52:08 | 10/18/2025 19:31:43 | 10/19/2025 06:52:08 | BASE STATION INFORMATION (No module fan detected) at TAF2405-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 (Ref:CM20251005000594) @ Sceco | 10/18/2025 13:53:41 | Minor | 7115 | BASE STATION INFORMATION | 10/18/2025 13:53:35 | P2 | 2G | taif | Sceco | 5G NSA | TAF2405 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/18/2025 18:52:08 | 10/18/2025 19:31:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001076 | PCM-20251018-00001856 | TT-20251018-00025 | Reference_telecom | Region_6 | JDJZ1M7781 | JDJZ0781 | Equipment | SW | Issue was solved after softaware configuration | Muhammad Usman Muhammad Zia ul haq | 10/18/2025 18:56:56 | 10/18/2025 22:19:10 | 10/19/2025 00:56:56 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JDJZ1M7781-P2 @ Sceco | 10/17/2025 22:28:43 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 22:26:42 | P3 | 4G | derb | Sceco | LTE NSA | JDJZ1M7781 | FLM_TE |  |  | PCM-20251018-00001764 | Dear FLM team, kindly perform HC for MW JDJZ0781 -JDJZ0782 | Dear FLM team, kindly perform HC for MW JDJZ0781 -JDJZ0782 |  |  |  | API | 10/18/2025 18:56:56 | 10/18/2025 22:18:31 | 10/18/2025 22:18:57 |  |  | 10/18/2025 22:19:10 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001082 | PCM-20251018-00001867 | TT-20251018-01803 | Telecom | Region_6 | SAB0058 | SAB0058 | Transsmission | MW_HW_fault | Replace IDU | Ansir Iqbal Muhammad Iqbal | 10/18/2025 19:02:55 | 10/18/2025 22:15:00 | 10/19/2025 07:02:55 | Visibility Down at SAB0058 | 10/18/2025 19:02:11 | Minor | 113388 | LOF | 10/18/2025 19:02:11 | P1 | 2G | baish | Sceco | TX NSA | SAB0058 | FLM_TE | [5 empty] | Visibility Down at SAB0058 |  |  | API | 10/18/2025 19:02:55 | 10/18/2025 20:23:49 | 10/18/2025 20:24:34 | 10/18/2025 20:24:38 |  | 10/18/2025 22:15:00 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018001084 | PCM-20251018-00001871 | TT-20251018-01801 | EM | Region_4 | JED1M8619 | JED2619 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 19:07:31 | 10/19/2025 16:59:31 | 10/19/2025 01:07:31 | 1(LTE/5G) sites down under JED2619-NR3.5-P3 @ Sceco | 10/18/2025 18:59:26 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/18/2025 18:59:24 | P3 | 4G | jeddah | Sceco | LTE SA | JED2619-P3-CA-L800 | FLM_TE | JED2619 | Results: DOWN SITE HUB JED2619-P3-CA-L800 JED2619 Summary: Hub: JED2619, Down Count: 1, Down Sites: JED2619-P3-CA-L800 Alarm Summary: JED2619 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.48.100:8080] [URL:http://10.97.48.100:8080/NE3S/1.0/] | sites down |  | API | 10/18/2025 19:07:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001085 | PCM-20251018-00001873 | TT-20251018-01217 | Reference_telecom | Region_6 | AQQ1M8424 | AQQ2424 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/18/2025 19:10:56 | 10/19/2025 00:18:00 | 10/19/2025 01:10:56 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at AQQ1M8424-G9-L8-L18-SBTS @ Generator_SG | 10/18/2025 12:03:32 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 11:54:46 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8424 | FLM_TE |  |  | PCM-20251018-00001769 | Dear FLM team, kindly perform HC for MW AQQ2424-AQQ2157 | Dear FLM team, kindly perform HC for MW AQQ2424-AQQ2157 |  |  |  | API | 10/18/2025 19:10:56 | 10/19/2025 00:16:32 | 10/19/2025 00:16:56 |  |  | 10/19/2025 00:18:00 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001087 | PCM-20251018-00001875 | TT-20251018-01216 | Reference_telecom | Region_6 | BDN1M8169 | BDN2169 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/18/2025 19:12:09 | 10/18/2025 19:53:22 | 10/19/2025 07:12:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BDN1M8169-L800-L1800-SBTS-P3 @ Sceco | 10/18/2025 12:03:38 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 11:54:21 | P3 | 4G | Baha | Sceco | LTE NSA | BDN1M8169 | FLM_TE |  |  | PCM-20251018-00001772 | Dear FLM team, kindly perform HC for MW BDN2169-GHM9724 | Dear FLM team, kindly perform HC for MW BDN2169-GHM9724 |  |  |  | API | 10/18/2025 19:12:09 | 10/18/2025 19:52:57 | 10/18/2025 19:53:09 |  |  | 10/18/2025 19:53:22 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001095 | PCM-20251018-00001893 | TT-20251018-01752 | Telecom | Region_2 | RIY2415 | RIY2415 |  |  |  | Farmanullah Akbar Jan | 10/18/2025 19:22:17 | 10/19/2025 00:08:33 | 10/19/2025 07:22:17 | HC TT for RIY2415 | 10/18/2025 18:26:35 | Minor | 676767672 | Health Check-WO to TE FME | 10/18/2025 18:26:35 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2415 | FLM_TE |  |  | PCM-20251018-00001821 | HW alarms , MW alarms , PM Errors and RSL degradation observed on RIY0289-RIY0443 FLM Team please perform health check for the mentioned MW link | HW alarms , MW alarms , PM Errors and RSL degradation observed on RIY0289-RIY0443 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 19:22:17 | 10/19/2025 00:08:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001100 | PCM-20251018-00001902 | TT-20251017-01264 | Reference_telecom | Region_2 | RYQ0955 | RYQ0955 |  |  |  | Muhammad Tahir Abdulrazzaq | 10/18/2025 19:25:57 | 10/20/2025 11:58:51 | 10/19/2025 07:25:57 | IP Link Performance Measurement Fault at RYQ0955-P2_SRAN @ Generator_DG | 10/17/2025 11:52:29 | Minor | 25904 | IP Link Performance Measurement Fault | 10/17/2025 11:51:56 | P2 | SRAN | majma | Generator_DG | 2G NSA | RYQ0955 | FLM_TE |  |  | PCM-20251018-00001593 | MW alarms , PM Errors and RSL degradation observed on MAS0558-RYQ0964 FLM Team please perform health check for the mentioned MW link | MW alarms , PM Errors and RSL degradation observed on MAS0558-RYQ0964 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/18/2025 19:25:57 | 10/20/2025 11:58:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001105 | PCM-20251018-00001911 | TT-20251018-01846 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/18/2025 19:32:52 | 10/19/2025 13:40:07 | 10/19/2025 01:32:52 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/18/2025 16:31:28 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 16:32:36 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/18/2025 19:32:52 | 10/19/2025 13:40:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018001107 | PCM-20251018-00001913 | TT-20251018-01848 | Telecom | Region_4 | JED1M8243 | JED2243 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 19:33:24 | 10/19/2025 17:45:05 | 10/19/2025 01:33:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8243-L800-CA-SBTS-P3 @ Sceco | 10/18/2025 19:32:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 19:32:26 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8243 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 19:33:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001116 | PCM-20251018-00001927 | TT-20251018-01862 | Telecom | Region_5 | MAK0643 | MAK0643 | Equipment | SFP_BTS | Replace SFP | Israr Ahmed Muhammad Ghauri | 10/18/2025 19:42:10 | 10/19/2025 17:45:05 | 10/19/2025 01:42:10 | CELL SERVICE PROBLEM (BTS configuration error (not enough HW for LCR)) at MAK0643-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/18/2025 19:37:38 | Major | 7114 | CELL SERVICE PROBLEM | 10/18/2025 19:37:33 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0643 | FLM_TE | [5 empty] | BTS configuration error (not enough HW for LCR) |  |  | API | 10/18/2025 19:42:10 | 10/19/2025 09:59:25 | 10/19/2025 10:11:04 | 10/19/2025 10:11:10 | 10/19/2025 10:48:08 | 10/19/2025 12:08:56 |  | Israr Ahmed Muhammad Ghauri |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001120 | PCM-20251018-00001936 | TT-20251018-01860 | Telecom | Region_4 | ASQ1M3343 | ASQ0343 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/18/2025 19:46:32 | 10/20/2025 20:43:57 | 10/18/2025 23:46:32 | 1(3G) sites down under ASQ0343-P1-HUB-USF/ASQ1M3343-P1-HUB-USF @ Sceco | 10/18/2025 19:38:35 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/18/2025 19:37:57 | P1 | 3G | adam | Sceco | 3G SA | ASQ0343-P1-HUB-USF | FLM_TE | ASQ0343 | Results: DOWN SITE HUB ASQ0343-P1-HUB-USF ASQ0343 Summary: Hub: ASQ0343, Down Count: 1, Down Sites: ASQ0343-P1-HUB-USF Alarm Summary: ASQ0343 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/18/2025 19:46:32 | 10/19/2025 02:41:21 | 10/20/2025 20:43:52 |  |  | 10/20/2025 20:43:57 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001135 | PCM-20251018-00001964 | TT-20251018-01899 | Telecom | Region_1 | HFR2M8379 | HFR2379 | Equipment | BSS_HW_fault | Replace RFU | Muhammad Anwar Hussain Akhtar Hussain | 10/18/2025 20:07:07 | 10/18/2025 21:24:19 | 10/19/2025 02:07:07 | Cell Unavailable at HFR2M8379-P2 @ Sceco | 10/18/2025 20:04:31 | Major | 29240 | Cell Unavailable | 10/18/2025 20:04:28 | P2 | 4G | hafr | Sceco | LTE SA | HFR2M8379 | FLM_TE | [8 empty] | API | 10/18/2025 20:07:07 | 10/18/2025 20:34:44 | 10/18/2025 20:43:58 | 10/18/2025 20:44:02 | 10/18/2025 21:13:42 | 10/18/2025 21:24:19 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001140 | PCM-20251018-00001970 | TT-20251018-01890 | Telecom | Region_1 | DRN2328 | DRN2328 | Enviroment | SCECO_Failure | SCECO auto restored | Imran Ali Yousaf | 10/18/2025 20:11:19 | 10/20/2025 11:33:24 | 10/19/2025 00:11:19 | 2(2G) 1(LTE) sites down under DRN0110-P1-HUB,ARM0732-P3/DM1MBSCH01 @ Sceco | 10/18/2025 19:57:10 | Critical | 21825 | CSL Fault | 10/18/2025 19:57:08 | P3 | SRAN | dammam | Sceco | 2G_LTE SA | DRN0110-P1-HUB 2G_LTE,ARM0732-P3 2G | FLM_TE | DRN2328 | Dear FLM EM Team, Hub site is DRN2328 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. Kindly update TT under FLM EM | PCM-20251018-00001962 | Dear FLM EM Team, Hub site is DRN2328 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. Kindly update TT under FLM EM | Dear FLM EM Team, Hub site is DRN2328 We are observing ETH_LINK_DOWN alarm flapped , kindly visit the site and check the issue as we are suspecting power issue or check the cable connection at hub site. Kindly update TT under FLM EM |  | sites down |  | API | 10/18/2025 20:11:19 | 10/19/2025 10:17:29 | 10/19/2025 17:14:09 |  |  | 10/20/2025 11:33:24 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001145 | PCM-20251018-00001976 | TT-20251018-01910 | Telecom | Region_1 | DAM2743 | DAM2743 | Equipment | BSS_HW_Stuck | Reset RRU | AbdalHafiz Sirageldin Mohamed Yasin | 10/18/2025 20:16:16 | 10/20/2025 07:23:50 | 10/19/2025 02:16:16 | cell unavailable at DAM2743-P3_SRAN @ Sceco | 10/18/2025 20:13:19 | Major | 26234 | BBU CPRI Interface Error | 10/18/2025 20:10:45 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2743 | FLM_TE | [8 empty] | API | 10/18/2025 20:16:16 | 10/19/2025 05:47:50 | 10/20/2025 07:23:36 |  |  | 10/20/2025 07:23:50 |  | AbdalHafiz Sirageldin Mohamed Yasin |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001147 | PCM-20251018-00001981 | TT-20251018-01919 | Telecom | Region_4 | JED2480 | JED2480 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/18/2025 20:20:54 | 10/20/2025 13:54:23 | 10/19/2025 02:20:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2480-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/18/2025 20:19:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 20:19:50 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2480 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 20:20:54 | 10/20/2025 13:30:26 | 10/20/2025 13:54:18 |  |  | 10/20/2025 13:54:23 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018001157 | PCM-20251018-00002001 | TT-20251018-01941 | Telecom | Region_4 | JED2179 | JED2179 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 20:46:13 | 10/19/2025 17:45:06 | 10/19/2025 02:46:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2179-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/18/2025 20:45:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 20:45:09 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2179 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 20:46:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001159 | PCM-20251018-00002004 | TT-20251018-01945 | EM | Region_6 | TBL1M8297 | TBL2297 |  |  |  | Abdul Rauf Muhammad Aslam | 10/18/2025 20:51:23 | 10/22/2025 12:00:49 | 10/19/2025 08:51:23 | SHELTER DOOR OPEN at TBL1M8297-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/18/2025 20:50:57 | Minor | 7103 | SHELTER DOOR OPEN | 10/18/2025 20:50:48 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M8297 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | Manual | 10/18/2025 20:51:23 | 10/22/2025 12:00:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018001163 | PCM-20251018-00002008 | TT-20251018-01951 | EM | Region_6 | TBL1M8297 | TBL2297 |  |  |  | Abdul Rauf Muhammad Aslam | 10/18/2025 20:57:05 | 10/22/2025 12:00:49 | 10/19/2025 08:57:05 | RECTIFIER MODULE FAILURE at TBL1M8297-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/18/2025 20:50:10 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/18/2025 20:48:47 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M8297 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | Manual | 10/18/2025 20:57:05 | 10/22/2025 12:00:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018001173 | PCM-20251018-00002023 | TT-20251018-01968 | EM | Region_4 | BHMF1M8137 | BHMF2137 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/18/2025 21:15:39 | 10/19/2025 12:35:01 | 10/19/2025 09:15:39 | COMMERCIAL POWER FAILURE at BHMF1M8137-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/18/2025 21:07:30 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/18/2025 21:07:23 | P3 | 4G | jeddah | Generator_SG | LTE NSA | BHMF1M8137 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/18/2025 21:15:39 | 10/19/2025 12:35:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251018001181 | PCM-20251018-00002039 | TT-20251018-01974 | EM | Region_5 | JUSH0644 | JUSH0644 |  |  |  | Hosini Saeed Hassn Saeed | 10/18/2025 21:24:40 | 10/18/2025 21:24:40 | 10/19/2025 03:24:40 | 1(2G/3G) sites down under JUSH0644-P3/JUSH0644-P3 @ Generator_SG | 10/18/2025 21:16:45 | Major | 7706 | BTS O&M LINK FAILURE | 10/18/2025 21:16:40 | P3 | 2G | makkah | Generator_SG | 2G_3G SA | JUSH0644-P3 | FLM_EM |  | Results: DOWN SITE HUB JUSH0644-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/18/2025 21:24:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018001182 | PCM-20251018-00002040 | TT-20251018-01926 | Telecom | Region_1 | YBR0725 | YBR0725 |  |  |  | Mohamed Magdy Fouad Zayed | 10/18/2025 21:25:05 | 10/18/2025 21:53:02 | 10/18/2025 23:25:05 | 14(2G) 9(3G) 15(LTE) sites down under R1_HF_HWBSC01 @ Power Cube | 10/18/2025 20:23:52 | Emergency | 21825 | CSL Fault | 10/18/2025 20:23:47 | P2 | SRAN | hafouf | Power Cube | 2G_3G_LTE SA | YBR0602-P3-PC LTE,YBR0604-P3-USF 2G_3G_LTE,YBR0669-P3-USF 2G_3G_LTE,YBR0682-P2-USF 2G_LTE,YBR0607-P3-USF 2G_LTE,YBR0725-P2-USF 2G_3G_LTE,YBR0615-P3-USF 2G_LTE,YBR0609-P3-USF 2G_3G_LTE,YBR0617-P3-USF 2G_3G_LTE,YBR0614-P3-USF 2G_3G_LTE,YBR0606-P3-USF 2G_3G_LTE,YBR0603-P3-USF 2G_3G_LTE,YBR0683-P2-USF 2G_LTE,YBR0619-USF-P3-USF 2G_LTE,YBR0605-P3-USF 2G_3G_LTE | FLM_TE | YBR0725 | dear team , Kindly check site locally | PCM-20251018-00002036 | dear team , Kindly check site locally | dear team , Kindly check site locally |  | sites down |  | API | 10/18/2025 21:25:05 | 10/18/2025 21:53:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001188 | PCM-20251018-00002048 | TT-20251018-01984 | EM | Region_1 | JBL0998 | JBL0998 |  |  |  | Mohamed Samir Farahat Allam | 10/18/2025 21:31:39 | 10/19/2025 19:16:09 | 10/19/2025 09:31:39 | Door opening alarm at JBL0998-P3_SRAN @ Sceco | 10/18/2025 21:31:04 | Minor | 65101 | Door opening alarm | 10/18/2025 21:07:01 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL0998 | FLM_EM | [8 empty] | API | 10/18/2025 21:31:39 | 10/19/2025 19:16:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251018001191 | PCM-20251018-00002051 | TT-20251018-01989 | Telecom | Region_1 | JBL0998 | JBL0998 |  |  |  | Tahir Mahmood Hafiz Yar | 10/18/2025 21:33:12 | 10/18/2025 22:00:25 | 10/19/2025 09:33:12 | ALD Maintenance Link Failure at JBL0998-P3_SRAN @ Sceco | 10/18/2025 21:31:10 | Minor | 26541 | ALD Maintenance Link Failure | 10/18/2025 21:07:01 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL0998 | FLM_TE | [8 empty] | API | 10/18/2025 21:33:12 | 10/18/2025 22:00:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251018001196 | PCM-20251018-00002058 | TT-20251018-01997 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/18/2025 21:39:55 | 10/19/2025 17:45:08 | 10/19/2025 03:39:55 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/18/2025 21:39:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 21:39:07 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 21:39:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251018001204 | PCM-20251018-00002068 | TT-20251018-02007 | EM | [7 empty] | 10/18/2025 21:50:46 | 10/18/2025 21:50:46 | 10/19/2025 01:50:46 | RECTIFIER ALARM at HHR1-SEC0039_HYB @ Sceco | 10/18/2025 21:49:18 | Critical | 1-12307 | RECTIFIER ALARM | 10/18/2025 21:49:06 | P1 | DWDM |  | Sceco | DWDM NSA | HHR1 | FLM_EM | [5 empty] | 0-TO JD2(1-A)-72-E1EFI-[RECTIFIER ALARM]:1 |  |  | API | 10/18/2025 21:50:46 | [10 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251018001233 | PCM-20251018-00002119 | TT-20251018-02053 | Reference_telecom | Region_4 | JED0495 | JED0495 |  |  |  | Nazeer Mohammed | 10/18/2025 22:33:38 | 10/20/2025 14:00:21 | 10/19/2025 10:33:38 | LagPortDown observed in JED0495 towards 10.10.188.151 @ Sceco | 10/18/2025 10:33:16 | Minor |  | LagPortDown | 10/18/2025 10:33:12 | P3 | 2G | jeddah | Sceco | TX NSA | JED0495 | FLM_TE | [8 empty] | API | 10/18/2025 22:33:38 | 10/20/2025 13:30:27 | 10/20/2025 14:00:15 | 10/20/2025 14:00:18 | 10/20/2025 14:00:21 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001242 | PCM-20251018-00002131 | TT-20251018-01995 | Reference_telecom | Region_1 | DAM2M8802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/18/2025 22:43:14 | 10/18/2025 22:59:11 | 10/19/2025 10:43:14 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M8802-CA-L800-FWA-P1-VIP @ Sceco | 10/18/2025 18:39:15 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/18/2025 18:39:12 | P3 | 4G | dammam | Sceco | 2G NSA | DAM2M8802 | FLM_TE |  |  | PCM-20251018-00002057 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/18/2025 22:43:14 | 10/18/2025 22:59:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001250 | PCM-20251018-00002150 | TT-20251018-02076 | Telecom | Region_3 | MDN0261 | MDN0261 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/18/2025 23:00:32 | 10/19/2025 08:34:27 | 10/19/2025 11:00:32 | RF Unit Maintenance Link Failure at MDN0261-P3_SRAN @ Sceco | 10/18/2025 17:23:07 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/18/2025 17:21:24 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN0261 | FLM_TE | [8 empty] | API | 10/18/2025 23:00:32 | 10/19/2025 08:34:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001257 | PCM-20251018-00002166 | TT-20251018-02097 | Telecom | Region_4 | JED0345 | JED0345 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/18/2025 23:13:57 | 10/19/2025 17:45:08 | 10/19/2025 05:13:57 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0345-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/18/2025 23:12:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 23:12:49 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0345 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/18/2025 23:13:57 | 10/19/2025 01:33:32 | 10/19/2025 09:48:30 |  |  | 10/19/2025 09:48:40 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001260 | PCM-20251018-00002175 | TT-20251018-02087 | Telecom | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/18/2025 23:26:29 | 10/19/2025 15:36:17 | 10/19/2025 05:26:29 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at TURY0688-GSM-P3 @ Sceco | 10/18/2025 23:06:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/18/2025 23:06:05 | P3 | 2G | taif | Sceco | 5G_Cell SA | TURY0688 | FLM_TE |  |  | PCM-20251018-00002160 | Perform HC | Perform HC |  |  |  | API | 10/18/2025 23:26:29 | 10/19/2025 15:36:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251018001270 | PCM-20251018-00002191 | TT-20251018-02132 | Telecom | Region_1 | HFF2M8244 | HFF2244 | Equipment | BTS_Cable | Replace Fiber Cable | Mohamed Magdy Fouad Zayed | 10/18/2025 23:48:02 | 10/21/2025 04:09:06 | 10/19/2025 05:48:02 | Cell Unavailable at HFF2M8244-P2-L800 @ Sceco | 10/18/2025 23:47:12 | Major | 29240 | Cell Unavailable | 10/18/2025 23:45:38 | P2 | 4G | hafouf | Sceco | LTE SA | HFF2M8244 | FLM_TE | [8 empty] | API | 10/18/2025 23:48:02 | 10/19/2025 09:03:28 | 10/21/2025 04:06:48 | 10/21/2025 04:08:48 |  | 10/21/2025 04:09:06 |  | Mohamed Magdy Fouad Zayed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001274 | PCM-20251018-00002197 | TT-20251018-02138 | Reference_telecom | Region_5 | MAK0815 | MAK0815 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/18/2025 23:54:45 | 10/19/2025 14:53:09 | 10/19/2025 11:54:45 | FanFailure observed in MAK0815 - 01 towards 10.10.186.168 @ Sceco | 10/18/2025 11:54:43 | Minor |  | FanFailure | 10/18/2025 11:54:15 | P1 | 2G | makkah | Sceco | TX NSA | MAK0815 | FLM_TE | [8 empty] | API | 10/18/2025 23:54:45 | 10/19/2025 14:53:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251018001278 | PCM-20251018-00002202 | TT-20251018-02043 | Reference_telecom | Region_1 | SHB0689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/18/2025 23:59:59 | 10/21/2025 11:38:00 | 10/19/2025 03:59:59 | IP PM Activation Failure at R2_RY2_HWBSC01 @ Sceco_STB | 10/18/2025 19:23:28 | Critical | 21341 | IP PM Activation Failure | 10/18/2025 19:22:47 | P3 | SRAN | hafouf | Power Cube | 2G NSA | R2_RY2_HWBSC01 | FLM_TE | SHB0689 | Dear Team , Site is Under SKYBAND , Not found in the Topology | PCM-20251018-00002135 | Dear Team , Site is Under SKYBAND , Not found in the Topology | Dear Team , Site is Under SKYBAND , Not found in the Topology |  |  |  | API | 10/18/2025 23:59:59 | 10/19/2025 09:03:32 | [6 empty] | Skyband |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000002 | PCM-20251019-00000004 | TT-20251019-00002 | Reference_telecom | Region_1 | JBL0998 | JBL0998 |  |  |  | Tahir Mahmood Hafiz Yar | 10/19/2025 00:07:41 | 10/19/2025 06:04:22 | 10/19/2025 06:07:41 | RF Unit VSWR Threshold Crossed at JBL0998-P3_SRAN @ Sceco | 10/18/2025 21:31:04 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 21:07:11 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL0998 | FLM_TE | [8 empty] | API | 10/19/2025 00:07:41 | 10/19/2025 06:04:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000003 | PCM-20251019-00000005 | TT-20251019-00003 | Reference_telecom | Region_1 | JBL6006 | JBL6006 |  |  |  | Tahir Mahmood Hafiz Yar | 10/19/2025 00:09:46 | 10/19/2025 06:04:24 | 10/19/2025 06:09:46 | RF Unit VSWR Threshold Crossed at JBL6006-P3_SRAN @ Sceco | 10/18/2025 21:29:19 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/18/2025 21:09:31 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL6006 | FLM_TE | [8 empty] | API | 10/19/2025 00:09:46 | 10/19/2025 06:04:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000007 | PCM-20251019-00000018 | TT-20251019-00024 | Reference_telecom | Region_4 | HHR0507 | HHR0507 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/19/2025 00:29:24 | 10/20/2025 13:40:39 | 10/19/2025 12:29:24 | BASE STATION INFORMATION (Unit temperature is high) at HHR0507-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/18/2025 23:49:00 | Minor | 7115 | BASE STATION INFORMATION | 10/18/2025 23:48:53 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0507 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/19/2025 00:29:24 | 10/20/2025 13:30:27 | 10/20/2025 13:40:33 |  |  | 10/20/2025 13:40:39 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000011 | PCM-20251019-00000025 | TT-20251018-02100 | Reference_telecom | Region_4 | MLJI1M3204 | MLJI0204 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 00:35:01 | 10/21/2025 19:39:52 | 10/19/2025 06:35:01 | RNW O&M SCENARIO FAILURE at MLJI1M3204-P3 @ Generator_SG | 10/18/2025 22:50:21 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/18/2025 22:49:30 | P3 | 3G | alaith | Generator_SG | 3G NSA | MLJI1M3204 | FLM_TE |  |  | PCM-20251018-00002171 | Site is down, kindly check and support to restore | Site is down, kindly check and support to restore |  |  |  | API | 10/19/2025 00:35:01 | 10/19/2025 08:03:14 | 10/21/2025 19:39:40 |  |  | 10/21/2025 19:39:52 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000022 | PCM-20251019-00000045 | TT-20251019-00017 | Reference_telecom | Region_1 | HFF2M7052 | HFF0052 |  |  |  | Mohamed Magdy Fouad Zayed | 10/19/2025 00:48:24 | 10/19/2025 09:03:33 | 10/19/2025 12:48:24 | Cell RX Channel Interference Noise Power Unbalanced at HFF2M7052-P2-L800 @ Sceco | 10/18/2025 21:20:54 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/18/2025 21:20:51 | P2 | 4G | hafouf | Sceco | 2G NSA | HFF2M7052 | FLM_TE |  |  | PCM-20251019-00000012 | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. | Dear FLM, Kindly check below step. 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. Noted if you did any step just skip and do another. |  |  |  | API | 10/19/2025 00:48:24 | 10/19/2025 09:03:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000027 | PCM-20251019-00000055 | TT-20251019-00071 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 00:55:13 | 10/19/2025 09:18:56 | 10/19/2025 12:55:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/19/2025 00:54:19 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 00:54:11 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 00:55:13 | 10/19/2025 09:18:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000028 | PCM-20251019-00000056 | TT-20251019-00072 | EM | Region_6 | JEC0377 | JEC0377 |  |  |  | Fizan Ahmed | 10/19/2025 00:55:13 | 10/21/2025 11:30:02 | 10/19/2025 06:55:13 | AIRCON 1 FAILURE at JEC0377-GSM-P1-VIP @ Generator_SG | 10/19/2025 00:46:56 | Major | 7103 | AIRCON 1 FAILURE | 10/19/2025 00:46:51 | VIP | 2G | baish | Generator_SG | 2G NSA | JEC0377 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/19/2025 00:55:13 | 10/21/2025 11:30:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000029 | PCM-20251019-00000057 | TT-20251019-00075 | EM | Region_1 | SAK0585 | SAK0585 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/19/2025 00:58:19 | 10/20/2025 15:38:07 | 10/19/2025 04:58:19 | Door opening alarm at SAK0585-P1-Core-SHOP-HUB-WDM_SRAN-FON @ Sceco | 10/19/2025 00:57:47 | Critical | 65101 | Door opening alarm | 10/19/2025 00:57:44 | P1 | SRAN | sakaka | Sceco | 2G NSA | SAK0585 | FLM_EM | [8 empty] | API | 10/19/2025 00:58:19 | 10/20/2025 15:38:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251019000047 | PCM-20251019-00000096 | TT-20251019-00139 | Telecom | [7 empty] | 10/19/2025 01:37:35 | 10/19/2025 01:37:35 | 10/19/2025 05:37:35 | OSC_LOS at YANBU3-SEC0020_HYB @ Sceco_STB | 10/19/2025 01:37:25 | Critical | 1-12843 | OSC_LOS | 10/19/2025 01:37:13 | P1 | DWDM |  | Sceco_STB | DWDM NSA | YANBU3 | FLM_TE | [5 empty] | 0-TO YB2(1-A)-10-G2AST4-1(RM1/TM1(TO MDYB0073_OCS,TNG6WDAPXF(1-C09)-RM2/TM2))-OSC:1 |  |  | API | 10/19/2025 01:37:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000048 | PCM-20251019-00000097 | TT-20251019-00137 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 01:37:35 | 10/19/2025 09:18:57 | 10/19/2025 07:37:35 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/19/2025 01:27:31 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 01:27:26 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251019-00000093 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/19/2025 01:37:35 | 10/19/2025 09:18:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000052 | PCM-20251019-00000113 | TT-20251019-00148 | Telecom | Region_4 | JED1M7987 | JED0987 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Mohammed Ramadan A Abu Abid | 10/19/2025 01:47:39 | 10/19/2025 11:04:31 | 10/19/2025 07:47:39 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7987-P3-CA-L800 @ Generator_SG | 10/19/2025 01:38:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 01:38:21 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7987 | FLM_TE |  |  | PCM-20251019-00000109 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/19/2025 01:47:39 | 10/19/2025 05:54:12 | 10/19/2025 09:58:30 | 10/19/2025 09:58:34 | 10/19/2025 10:19:59 | 10/19/2025 11:04:31 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000069 | PCM-20251019-00000154 | TT-20251019-00201 | Telecom | Region_3 | MDN2945 | MDN2945 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/19/2025 02:20:57 | 10/19/2025 08:34:28 | 10/19/2025 14:20:57 | RF Unit Maintenance Link Failure at MDN2945-P2_SRAN @ Sceco | 10/19/2025 02:17:29 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/19/2025 02:15:46 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2945 | FLM_TE | [8 empty] | API | 10/19/2025 02:20:57 | 10/19/2025 08:34:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000074 | PCM-20251019-00000165 | TT-20251019-00212 | EM | Region_2 | RIY2977 | RIY2977 |  |  |  | Adham Adham Hassan Farghal | 10/19/2025 02:30:16 | 10/19/2025 09:17:30 | 10/19/2025 14:30:16 | Door opening alarm at RIY2977-P3_SRAN-PC @ Sceco | 10/19/2025 02:29:57 | Minor | 65101 | Door opening alarm | 10/19/2025 02:28:31 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2977 | FLM_EM | [8 empty] | API | 10/19/2025 02:30:16 | 10/19/2025 09:17:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000075 | PCM-20251019-00000166 | TT-20251019-00213 | Telecom | Region_4 | RAB1M7720 | RAB0720 |  |  |  | Khizer Hayat | 10/19/2025 02:30:47 | 10/19/2025 03:44:20 | 10/19/2025 08:30:47 | BASE STATION SERVICE PROBLEM (No connection to unit) at RAB1M7720-CA-L800 @ Sceco | 10/19/2025 02:29:58 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 02:29:53 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | RAB1M7720 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 02:30:47 | 10/19/2025 03:44:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000080 | PCM-20251019-00000180 | TT-20251019-00236 | EM | [7 empty] | 10/19/2025 02:37:30 | 10/19/2025 02:37:30 | 10/19/2025 14:37:30 | Minor Rec alarm at RIYB6076-P3_SRAN @ Sceco | 10/19/2025 02:32:05 | Minor | 65108 | Minor Rec alarm | 10/19/2025 02:27:16 | P3 | SRAN |  | Sceco | 2G NSA | RIYB6076 | FLM_EM | [8 empty] | API | 10/19/2025 02:37:30 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000083 | PCM-20251019-00000184 | TT-20251019-00240 | EM | Region_2 | RIY2977 | RIY2977 |  |  |  | Adham Adham Hassan Farghal | 10/19/2025 02:38:32 | 10/19/2025 09:17:30 | 10/19/2025 14:38:32 | Mains Failure at RIY2977-P3_SRAN-PC @ Sceco | 10/19/2025 02:29:57 | Minor | 65109 | Mains Failure | 10/19/2025 02:28:31 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2977 | FLM_EM | [8 empty] | API | 10/19/2025 02:38:32 | 10/19/2025 09:17:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000098 | PCM-20251019-00000199 | TT-20251019-00258 | EM | Region_2 | RIYA6199 | RIYA6199 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/19/2025 02:43:11 | 10/19/2025 10:24:37 | 10/19/2025 14:43:11 | Mains Failure at RIYA6199-P3_SRAN @ Sceco | 10/19/2025 02:36:36 | Minor | 65109 | Mains Failure | 10/19/2025 02:32:59 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6199 | FLM_EM | [8 empty] | API | 10/19/2025 02:43:11 | 10/19/2025 10:24:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000101 | PCM-20251019-00000205 | TT-20251019-00266 | EM | Region_2 | RIY2668 | RIY2668 |  |  |  | Pawan Virdi Santokh Singh | 10/19/2025 02:45:47 | 10/20/2025 08:00:06 | 10/19/2025 08:45:47 | Fire Fighting system alarm at RIY2668-P1-VIP-RIYSEASON_SRAN @ Sceco | 10/19/2025 02:36:39 | Major | 65111 | Fire Fighting system alarm | 10/19/2025 02:35:24 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2668 | FLM_EM | [8 empty] | API | 10/19/2025 02:45:47 | 10/20/2025 08:00:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000102 | PCM-20251019-00000204 | TT-20251019-00265 | EM | Region_2 | RIY2839 | RIY2839 | Enviroment | Fire Alarm | Reset Fire Pannel | Tanveer Ahmad Fateh Muhammad | 10/19/2025 02:45:47 | 10/20/2025 12:14:50 | 10/19/2025 14:45:47 | Fire Fighting system alarm at RIY2839-P3_SRAN @ Sceco | 10/19/2025 02:36:40 | Minor | 65111 | Fire Fighting system alarm | 10/19/2025 02:35:36 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2839 | FLM_EM | [8 empty] | API | 10/19/2025 02:45:47 | 10/19/2025 10:24:39 | 10/20/2025 11:27:43 | 10/20/2025 11:27:47 | 10/20/2025 11:27:52 | 10/20/2025 12:14:50 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000104 | PCM-20251019-00000208 | TT-20251019-00279 | Reference_telecom | Region_6 | RTH0954 | RTH0954 |  |  |  | Muhammad Ali | 10/19/2025 02:49:53 | 10/19/2025 11:15:58 | 10/19/2025 14:49:53 | ReplaceableUnitMissing observed in RTH0954_01 towards 10.21.79.232 @ Sceco | 10/18/2025 14:49:40 | Minor |  | ReplaceableUnitMissing | 10/18/2025 14:49:27 | P2 | 2G | raith | Sceco | TX NSA | RTH0954 | FLM_TE | [8 empty] | API | 10/19/2025 02:49:53 | 10/19/2025 11:15:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000105 | PCM-20251019-00000211 | TT-20251019-00282 | EM | Region_6 | RYAB0623 | RYAB0623 | Enviroment | Air Condition | Change compressor | Muhammad Bilal Niamat Ali | 10/19/2025 02:49:55 | 10/20/2025 20:10:27 | 10/19/2025 08:49:55 | AIRCON 2 FAILURE at RYAB0623-GSM-UMTS-P1-HUB-USF @ Sceco_STB | 10/19/2025 02:41:39 | Major | 7103 | AIRCON 2 FAILURE | 10/19/2025 02:41:34 | P1 | 2G | sulail | Sceco_STB | 2G NSA | RYAB0623 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/19/2025 02:49:55 | 10/19/2025 12:17:32 | 10/20/2025 20:10:05 |  |  | 10/20/2025 20:10:27 |  | Muhammad Bilal Niamat Ali |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000106 | PCM-20251019-00000214 | TT-20251019-00285 | Telecom | Region_2 | KHJ0120 | KHJ0120 | Equipment | SFP_BTS | Replace SFP | Hakim Ullah Raif Ullah Jan | 10/19/2025 02:53:00 | 10/19/2025 07:13:40 | 10/19/2025 14:53:00 | RF Unit CPRI Interface Error at KHJ0120-P3_SRAN @ Generator_SG | 10/19/2025 02:47:46 | Minor | 26504 | RF Unit CPRI Interface Error | 10/19/2025 02:46:13 | P3 | SRAN | al kharj | Generator_SG | 2G NSA | KHJ0120 | FLM_TE | [8 empty] | API | 10/19/2025 02:53:00 | 10/19/2025 06:50:18 | 10/19/2025 06:51:57 | 10/19/2025 06:51:59 | 10/19/2025 07:01:55 | 10/19/2025 07:13:40 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000109 | PCM-20251019-00000221 | TT-20251019-00297 | Reference_telecom | Region_1 | SAK0585 | SAK0585 |  |  |  | Syed Fawad Ali | 10/19/2025 03:03:20 | 10/19/2025 04:52:37 | 10/19/2025 09:03:20 | R_LOS & REM_SF ALARMS AT SAK0585-LH & BUR0019-LH | 10/19/2025 01:06:24 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/19/2025 01:06:24 | P1 | SRAN | sakaka | Sceco | DWDM NSA | SAK0585-LH & BUR0019-LH | FLM_TE | [8 empty] | API | 10/19/2025 03:03:20 | 10/19/2025 04:52:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000112 | PCM-20251019-00000225 | TT-20251019-00301 | EM | Region_6 | JDJZ1M7787 | JDJZ0787 |  |  |  | Aziz Ul Haq Umar Gul | 10/19/2025 03:06:57 | 10/19/2025 17:12:49 | 10/19/2025 15:06:57 | AIRCON 1 FAILURE at JDJZ1M7787-L800-P3-SBTS @ Sceco | 10/19/2025 02:58:50 | Minor | 7103 | AIRCON 1 FAILURE | 10/19/2025 02:58:40 | P3 | 4G | derb | Sceco | LTE NSA | JDJZ1M7787 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/19/2025 03:06:57 | 10/19/2025 17:12:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000114 | PCM-20251019-00000238 | TT-20251019-00298 | EM | Region_4 | HHR0507 | HHR0507 |  |  |  | Khizer Hayat | 10/19/2025 03:10:33 | 10/19/2025 03:14:35 | 10/19/2025 07:10:33 | 1(2G/3G) sites down under HHR0507-P1-VIP-HHR/HHR0507-P1-VIP-HHR @ Generator_SG | 10/19/2025 03:02:27 | Critical | 7706 | BTS O&M LINK FAILURE | 10/19/2025 03:02:22 | VIP | 2G | jeddah | Generator_SG | 2G_3G SA | HHR0507-P1-VIP-HHR | FLM_EM | HHR0507 | Results: DOWN SITE HUB HHR0507-P1-VIP-HHR HHR0507 Summary: Hub: HHR0507, Down Count: 1, Down Sites: HHR0507-P1-VIP-HHR Alarm Summary: HHR0507 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 03:10:33 | 10/19/2025 03:14:35 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000115 | PCM-20251019-00000243 | TT-20251019-00314 | EM | Region_4 | HHR0507 | HHR0507 |  |  |  | Aly Ahmed Aly Sawy | 10/19/2025 03:14:42 | 10/19/2025 22:29:24 | 10/19/2025 09:14:42 | Generator Low Fuel at HHR0507-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/19/2025 03:06:31 | Major | 7103 | Generator Low Fuel | 10/19/2025 03:06:20 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0507 | FLM_EM | [5 empty] | Generator Low Fuel |  |  | API | 10/19/2025 03:14:42 | 10/19/2025 22:29:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000120 | PCM-20251019-00000250 | TT-20251019-00290 | Telecom | Region_4 | JED0284 | JED0284 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/19/2025 03:22:51 | 10/19/2025 09:51:35 | 10/19/2025 15:22:51 | BASE STATION ANTENNA LINE PROBLEM at JED0284-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/19/2025 02:53:44 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 02:53:40 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0284 | FLM_TE |  |  | PCM-20251019-00000219 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/19/2025 03:22:51 | 10/19/2025 05:54:12 | 10/19/2025 09:50:57 |  |  | 10/19/2025 09:51:35 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000122 | PCM-20251019-00000251 | TT-20251019-00287 | Telecom | Region_4 | JED2040 | JED2040 | Equipment | BSS_HW_Stuck | Reset Interface Card | Ahmad Mostafa Hamouda Ibrahem | 10/19/2025 03:23:38 | 10/21/2025 17:12:41 | 10/19/2025 09:23:38 | BASE STATION SERVICE PROBLEM (Baseband card crash has been detected) at JED2040-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/19/2025 02:54:05 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 02:53:57 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2040 | FLM_TE |  |  | PCM-20251019-00000217 | Please perform HC on SFP, Cable connectivity & HW BBMOD-1 | Please perform HC on SFP, Cable connectivity & HW BBMOD-1 |  |  |  | API | 10/19/2025 03:23:38 | 10/19/2025 12:53:22 | 10/19/2025 13:24:23 | 10/19/2025 13:24:25 | 10/19/2025 13:24:27 | 10/19/2025 13:51:42 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000125 | PCM-20251019-00000255 | TT-20251019-00269 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/19/2025 03:24:47 | 10/21/2025 18:20:34 | 10/19/2025 07:24:47 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/19/2025 02:39:51 | Critical | 7654 | CELL OPERATION DEGRADED | 10/19/2025 02:39:42 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251019-00000207 | Please check ALD HW & all the connectivity from ALD To RMOD R3 Ant-2,1 | Please check ALD HW & all the connectivity from ALD To RMOD R3 Ant-2,1 |  |  |  | API | 10/19/2025 03:24:47 | 10/19/2025 15:04:12 | 10/21/2025 18:20:27 |  |  | 10/21/2025 18:20:34 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000126 | PCM-20251019-00000256 | TT-20251019-00325 | Telecom | Region_1 | JBKH2M3603 | JBKH0603 | Equipment | SFP_BTS | Clean SFP | Meraj Husain Idd Baksh | 10/19/2025 03:27:07 | 10/19/2025 12:19:15 | 10/19/2025 15:27:07 | RF Unit Maintenance Link Failure at JBKH2M3603-P2 @ Sceco | 10/19/2025 03:23:28 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/19/2025 03:21:45 | P2 | 3G | dammam | Sceco | 2G NSA | JBKH2M3603 | FLM_TE | [8 empty] | API | 10/19/2025 03:27:07 | 10/19/2025 09:03:55 | 10/19/2025 12:19:03 |  |  | 10/19/2025 12:19:15 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000127 | PCM-20251019-00000272 | TT-20251019-00353 | EM | Region_6 | ARS0187 | ARS0187 |  |  |  | Khurram Nawaz Muhammad Akram | 10/19/2025 03:38:59 | 10/19/2025 09:10:35 | 10/19/2025 15:38:59 | RECTIFIER LOW BATTERY VOLTAGE 46.3V at ARS0187-GSM-P2 @ Sceco | 10/19/2025 03:31:29 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3V | 10/19/2025 03:30:41 | P2 | 2G | jizan | Sceco | 2G NSA | ARS0187 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/19/2025 03:38:59 | 10/19/2025 09:10:35 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000130 | PCM-20251019-00000277 | TT-20251019-00357 | EM | Region_4 | HHR0507 | HHR0507 |  |  |  | Aly Ahmed Aly Sawy | 10/19/2025 03:48:48 | 10/19/2025 22:29:24 | 10/19/2025 09:48:48 | SHELTER DOOR OPEN at HHR0507-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/19/2025 03:48:30 | Major | 7103 | SHELTER DOOR OPEN | 10/19/2025 03:48:27 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0507 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/19/2025 03:48:48 | 10/19/2025 22:29:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000131 | PCM-20251019-00000278 | TT-20251019-00358 | Telecom | Region_5 | MAK0106 | MAK0106 | Equipment | SFP_BTS | Re-Plug SFP | Jawad Ali Bakht Sher Khan | 10/19/2025 03:49:19 | 10/19/2025 05:40:51 | 10/19/2025 09:49:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0106-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HAJJ-Core-HUB-WDM-HRM @ Sceco_STB | 10/19/2025 03:48:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 03:48:11 | VIP | 2G | makkah | Sceco_STB | 5G_Cell SA | MAK0106 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 03:49:19 | 10/19/2025 04:22:52 | 10/19/2025 04:23:12 | 10/19/2025 04:23:20 | 10/19/2025 04:45:39 | 10/19/2025 05:40:51 |  | Jawad Ali Bakht Sher Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000133 | PCM-20251019-00000284 | TT-20251019-00288 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/19/2025 03:57:43 | 10/21/2025 18:20:13 | 10/19/2025 09:57:43 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/19/2025 02:53:53 | Major | 7114 | CELL SERVICE PROBLEM | 10/19/2025 02:53:42 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251019-00000218 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/19/2025 03:57:43 | 10/19/2025 15:04:12 | 10/21/2025 18:20:07 |  |  | 10/21/2025 18:20:13 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000135 | PCM-20251019-00000288 | TT-20251018-01466 | Reference_telecom | Region_6 | ABBS2160 | ABBS2160 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 04:00:36 | 10/19/2025 12:01:35 | 10/19/2025 10:00:36 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABBS2160-G9-L9-NNR2.6-SBTS-P1-VIP @ Sceco | 10/18/2025 13:54:01 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 13:49:10 | VIP | 2G | namas | Sceco | 2G NSA | ABBS2160 | FLM_TE |  |  | PCM-20251018-00001786 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/19/2025 04:00:36 | 10/19/2025 10:19:44 | 10/19/2025 12:00:51 |  |  | 10/19/2025 12:01:35 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000138 | PCM-20251019-00000295 | TT-20251019-00375 | Telecom | Region_4 | JED1MN2045 | JED2045 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 04:05:20 | 10/20/2025 11:00:23 | 10/19/2025 10:05:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2045-NR2.6-P3 @ Sceco | 10/19/2025 04:04:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 04:04:09 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2045 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 04:05:20 | 10/20/2025 11:00:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000139 | PCM-20251019-00000296 | TT-20251019-00366 | Reference_telecom | Region_4 | JED2040 | JED2040 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 04:05:52 | 10/19/2025 04:05:52 | 10/19/2025 16:05:52 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED2040-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/19/2025 03:28:15 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 03:28:05 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2040 | FLM_TE |  |  | PCM-20251019-00000286 | Kindly check the HW alarms active at site | Kindly check the HW alarms active at site |  |  |  | API | 10/19/2025 04:05:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000140 | PCM-20251019-00000298 | TT-20251019-00364 | Reference_telecom | Region_6 | TLT1M7752 | TLT0752 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/19/2025 04:06:19 | 10/19/2025 11:47:46 | 10/19/2025 16:06:19 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TLT1M7752-G9-L9-NL18-SBTS-P3 @ Generator_SG | 10/19/2025 02:11:42 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 01:57:23 | P3 | 4G | tathleeth | Generator_SG | LTE NSA | TLT1M7752 | FLM_TE |  |  | PCM-20251019-00000283 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/19/2025 04:06:19 | 10/19/2025 11:02:43 | 10/19/2025 11:47:40 |  |  | 10/19/2025 11:47:46 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000141 | PCM-20251019-00000300 | TT-20251019-00373 | Telecom | Region_1 | RAF2M4580 | RAF2580 |  |  |  | Almmoez Almmoez | 10/19/2025 04:08:32 | 10/19/2025 13:14:20 | 10/19/2025 10:08:32 | 1(3G) sites down under RAF2580-P3/HB1RNCH01 @ Sceco | 10/19/2025 04:00:17 | Major | 22214 | NodeB Unavailable | 10/19/2025 04:00:16 | P3 | 3G | rafha | Sceco | 3G SA | RAF2580-P3 | FLM_TE | RAF2580 | Results: DOWN SITE HUB RAF2580-P3 RAF2580 Summary: Hub: RAF2580, Down Count: 1, Down Sites: RAF2580-P3 Alarm Summary: RAF2580 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/19/2025 04:08:32 | 10/19/2025 13:14:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000143 | PCM-20251019-00000302 | TT-20251018-01876 | Telecom | Region_4 | JED1MN0351 | JED0351 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 04:10:04 | 10/19/2025 04:10:04 | 10/19/2025 10:10:04 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED1MN0351-NR2.6-P2 @ Sceco | 10/18/2025 19:43:01 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 19:42:55 | P1 | 5G | jeddah | Sceco | 5G NSA | JED1MN0351 | FLM_TE |  |  | PCM-20251018-00001943 | Kindly check the HW alarm active at site, Not able to synchronize baseband bus alarm active | Kindly check the HW alarm active at site, Not able to synchronize baseband bus alarm active |  |  |  | API | 10/19/2025 04:10:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000151 | PCM-20251019-00000311 | TT-20251019-00392 | Reference_telecom | Region_6 | ABBS0168 | ABBS0168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Manzoor Ahmed | 10/19/2025 04:20:18 | 10/23/2025 23:04:53 | 10/19/2025 16:20:18 | LossOfSignal observed in ABBS0168_03 towards 10.221.243.185 @ Sceco | 10/18/2025 16:21:37 | Minor |  | LossOfSignal | 10/18/2025 16:19:51 | P3 | 2G | Albaha | Sceco | TX NSA | ABBS0168 | FLM_TE | [8 empty] | API | 10/19/2025 04:20:18 | 10/19/2025 12:55:53 | 10/23/2025 23:04:41 |  |  | 10/23/2025 23:04:53 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000152 | PCM-20251019-00000312 | TT-20251019-00384 | EM | Region_1 | DMAR2M2011 | DMAR2011 |  |  |  | Dileesh Muringothil Devarajan | 10/19/2025 04:22:32 | 10/19/2025 04:43:41 | 10/19/2025 10:22:32 | 1(2G/LTE) sites down under DMAR2011-P3/R1_JB_HWBSC01 @ Sceco | 10/19/2025 04:14:26 | Major | 21825 | CSL Fault | 10/19/2025 04:14:24 | P3 | 2G | jubail | Sceco | 2G_LTE SA | DMAR2011-P3 | FLM_EM | DMAR2011 | Results: DOWN SITE HUB DMAR2011-P3 DMAR2011 Summary: Hub: DMAR2011, Down Count: 1, Down Sites: DMAR2011-P3 Alarm Summary: DMAR2011 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 04:22:32 | 10/19/2025 04:43:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251019000154 | PCM-20251019-00000314 | TT-20251019-00393 | EM | [7 empty] | 10/19/2025 04:23:25 | 10/19/2025 04:23:25 | 10/19/2025 08:23:25 | NE_COMMU_GNE_SWITCH at 8760-SEC0042_ELC @ Sceco | 10/19/2025 04:21:46 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/19/2025 04:21:43 | P1 | DWDM |  | Sceco | DWDM NSA | 8760 | FLM_EM | [5 empty] | NE 8760-SEC0042_ELC's current GNE has been switched to standby GNE |  |  | API | 10/19/2025 04:23:25 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000156 | PCM-20251019-00000316 | TT-20251019-00397 | EM | Region_2 | KHJ0301 | KJ1 |  |  |  | Ajmal Hafeez Hafeez Ahmed Awan | 10/19/2025 04:23:56 | 10/19/2025 17:19:47 | 10/19/2025 08:23:56 | NE_COMMU_GNE_SWITCH at KHJ0301_ELC @ Sceco_STB | 10/19/2025 04:21:57 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/19/2025 04:21:53 | P1 | SRAN | al kharj | Sceco_STB | DWDM NSA | KHJ0301 | FLM_EM | [5 empty] | NE KHJ0301_ELC's current GNE has been switched to standby GNE |  |  | API | 10/19/2025 04:23:56 | 10/19/2025 17:19:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251019000157 | PCM-20251019-00000317 | TT-20251019-00396 | EM | [7 empty] | 10/19/2025 04:23:57 | 10/19/2025 04:23:57 | 10/19/2025 08:23:57 | NE_COMMU_GNE_SWITCH at 8760-SEC0042_OCS @ Sceco | 10/19/2025 04:21:57 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/19/2025 04:21:53 | P1 | DWDM |  | Sceco | DWDM NSA | 8760 | FLM_EM | [5 empty] | NE 8760-SEC0042_OCS's current GNE has been switched to standby GNE |  |  | API | 10/19/2025 04:23:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000158 | PCM-20251019-00000318 | TT-20251019-00398 | EM | Region_2 | KHJ0301 | KJ1 |  |  |  | Ajmal Hafeez Hafeez Ahmed Awan | 10/19/2025 04:23:57 | 10/19/2025 17:19:48 | 10/19/2025 08:23:57 | NE_COMMU_GNE_SWITCH at KHJ0301_OCS @ Sceco_STB | 10/19/2025 04:22:08 | Critical | 0-25 | NE_COMMU_GNE_SWITCH | 10/19/2025 04:22:04 | P1 | SRAN | al kharj | Sceco_STB | DWDM NSA | KHJ0301 | FLM_EM | [5 empty] | NE KHJ0301_OCS's current GNE has been switched to standby GNE |  |  | API | 10/19/2025 04:23:57 | 10/19/2025 17:19:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251019000162 | PCM-20251019-00000324 | TT-20251019-00413 | EM | [7 empty] | 10/19/2025 04:33:17 | 10/19/2025 04:33:17 | 10/19/2025 08:33:17 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/19/2025 04:31:39 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/19/2025 04:31:31 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/19/2025 04:33:17 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000163 | PCM-20251019-00000325 | TT-20251019-00414 | Telecom | Region_2 | RIY0078 | RIY0078 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/19/2025 04:33:45 | 10/19/2025 08:56:29 | 10/19/2025 08:33:45 | OSC_LOS at RIY0078_HYB @ Sceco | 10/19/2025 04:33:13 | Critical | 1-12843 | OSC_LOS | 10/19/2025 04:33:01 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0078 | FLM_TE | [5 empty] | 0-TO RY2(1-A)-6-G2AST4-3(RM3/TM3(TO RY2_OCS,TNG6WDAPXF(1-A02)-RM2/TM2) ADD 5DB)-OSC:1 |  |  | API | 10/19/2025 04:33:45 | 10/19/2025 08:56:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000164 | PCM-20251019-00000326 | TT-20251019-00415 | Telecom | Region_2 | RIY0298 | RIY0298 | Transsmission | DWDM_SW | SW,Alarm Cleared | Waseem Shahzad Ghulam Rasool | 10/19/2025 04:33:45 | 10/19/2025 09:52:21 | 10/19/2025 08:33:45 | OSC_LOS at RIY0298 (RY4)_OCS @ Sceco_STB | 10/19/2025 04:33:13 | Critical | 1-12843 | OSC_LOS | 10/19/2025 04:33:01 | P1 | SRAN | riyadh | Sceco_STB | DWDM NSA | RIY0298 | FLM_TE | [5 empty] | 0-TO 8065-SEC0003(1-A)-8-G2AST4-4(RM4/TM4(TO RIY0300 (RY2)_OCS,TNG6WDAPXF(2-B02)-RM1/TM1))-OSC:1 |  |  | API | 10/19/2025 04:33:45 | 10/19/2025 09:51:39 | 10/19/2025 09:52:09 |  |  | 10/19/2025 09:52:21 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000165 | PCM-20251019-00000327 | TT-20251019-00416 | Telecom | Region_2 | KHJ0301 | KJ1 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hakim Ullah Raif Ullah Jan | 10/19/2025 04:33:45 | 10/19/2025 06:51:00 | 10/19/2025 08:33:45 | OSC_LOS at KHJ0301_OCS @ Sceco_STB | 10/19/2025 04:33:13 | Critical | 1-12843 | OSC_LOS | 10/19/2025 04:33:02 | P1 | SRAN | al kharj | Sceco_STB | DWDM NSA | KHJ0301 | FLM_TE | [5 empty] | 0-TO HAWTA8712-SEC0040(2-A)-7-G2AST4-1(RM1/TM1(TO RIY0300 (RY2)_OCS,TNG2SRAPXF(1-B09)-RM2/TM2))-OSC:1 |  |  | API | 10/19/2025 04:33:45 | 10/19/2025 06:50:18 | 10/19/2025 06:50:31 |  |  | 10/19/2025 06:51:00 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000173 | PCM-20251019-00000343 | TT-20251019-00433 | Reference_telecom | Region_5 | MAK0455 | MAK0455 |  |  |  | Atif Javed Javed Hussain | 10/19/2025 04:46:09 | 10/20/2025 15:45:22 | 10/19/2025 16:46:09 | ReplaceableUnitProblem observed in MAK0455 towards 10.10.141.166 @ Sceco | 10/18/2025 16:47:13 | Minor |  | ReplaceableUnitProblem | 10/18/2025 16:45:37 | VIP | 2G | makkah | Sceco | TX NSA | MAK0455 | FLM_TE | [8 empty] | API | 10/19/2025 04:46:09 | 10/20/2025 15:45:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000176 | PCM-20251019-00000360 | TT-20251019-00450 | Reference_telecom | Region_2 | RIYA6199 | RIYA6199 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/19/2025 04:57:36 | 10/19/2025 13:40:08 | 10/19/2025 10:57:36 | RF Unit VSWR Threshold Crossed at RIYA6199-P3_SRAN @ Sceco | 10/19/2025 04:02:45 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/19/2025 04:02:32 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6199 | FLM_TE | [8 empty] | API | 10/19/2025 04:57:36 | 10/19/2025 13:40:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000178 | PCM-20251019-00000403 | TT-20251019-00494 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/19/2025 04:59:04 | 10/19/2025 09:03:55 | 10/19/2025 16:59:04 | RF Unit Maintenance Link Failure at DAM6027-DCU1 @ Sceco | 10/19/2025 04:53:57 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/19/2025 04:53:42 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/19/2025 04:59:04 | 10/19/2025 09:03:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000181 | PCM-20251019-00000408 | TT-20251019-00434 | Reference_telecom | Region_1 | ARM2M7767 | ARM0767 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Imran Ali Yousaf | 10/19/2025 05:06:32 | 10/19/2025 16:34:08 | 10/19/2025 17:06:32 | Cell RX Channel Interference Noise Power Unbalanced at ARM2M7767-P3-CA-L800 @ Sceco | 10/19/2025 01:48:20 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/19/2025 01:48:17 | P3 | 4G | dammam | Sceco | 2G NSA | ARM2M7767 | FLM_TE |  |  | PCM-20251019-00000344 | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/19/2025 05:06:32 | 10/19/2025 10:17:29 | 10/19/2025 16:33:53 |  |  | 10/19/2025 16:34:08 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000186 | PCM-20251019-00000415 | TT-20251019-00503 | Telecom | Region_1 | DAM6012 | DAM6012 |  |  |  | Meraj Husain Idd Baksh | 10/19/2025 05:16:38 | 10/19/2025 09:03:56 | 10/19/2025 17:16:38 | DCU Optical Module Transmit/Receive Fault at DAM6012-DCU3 @ Sceco | 10/19/2025 05:04:09 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/19/2025 05:09:40 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6012 | FLM_TE | [8 empty] | API | 10/19/2025 05:16:38 | 10/19/2025 09:03:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000188 | PCM-20251019-00000418 | TT-20251019-00367 | Telecom | Region_3 | MDUL0541 | MDUL0541 |  |  |  | Junaid Eisa | 10/19/2025 05:23:07 | 10/22/2025 19:04:48 | 10/19/2025 09:23:07 | 6(2G) 3(3G) 6(LTE) sites down under R3_MD_HWBSC02 @ Generator_DG | 10/19/2025 03:58:06 | Critical | 21825 | CSL Fault | 10/19/2025 03:58:03 | P3 | SRAN | madinah | Generator_DG | 2G_3G_LTE SA | MDUL0541-P3 2G_LTE,MDUL2515-P3 2G_LTE,MDU0526-P2 2G_3G_LTE,MDV0075-P2 2G_3G_LTE,MDUL0542-P1 2G_LTE,MDU0525-P2 2G_3G_LTE | FLM_TE | MDUL0541 | Dear Team, Hub:- MDUL0541 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251019-00000297 | No Power Issue | No Power Issue |  | sites down |  | API | 10/19/2025 05:23:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000189 | PCM-20251019-00000421 | TT-20251019-00493 | Reference_telecom | Region_6 | KMS1M7471 | KMS0471 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/19/2025 05:25:13 | 10/19/2025 13:17:34 | 10/19/2025 11:25:13 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KMS1M7471-CA-P1-VIP-SBTS @ Generator_SG | 10/19/2025 03:25:26 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 02:57:36 | VIP | 4G | khamis mushyet | Generator_SG | LTE NSA | KMS1M7471 | FLM_TE |  |  | PCM-20251019-00000402 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/19/2025 05:25:13 | 10/19/2025 13:16:46 | 10/19/2025 13:17:25 |  |  | 10/19/2025 13:17:34 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000190 | PCM-20251019-00000422 | TT-20251019-00509 | Reference_telecom | Region_6 | KMS0250 | KMS0250 | Transsmission | MW_HW_fault | Replace Ethernet Cable | Muhammad shafiq Muhammad Rasheed | 10/19/2025 05:25:25 | 10/19/2025 08:14:32 | 10/19/2025 17:25:25 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KMS0250-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/19/2025 03:25:23 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 03:23:12 | P2 | 2G | khamis mushyet | Sceco | 2G NSA | KMS0250 | FLM_TE |  |  | PCM-20251019-00000419 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/19/2025 05:25:25 | 10/19/2025 08:12:12 | 10/19/2025 08:12:34 | 10/19/2025 08:12:38 |  | 10/19/2025 08:14:32 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000192 | PCM-20251019-00000425 | TT-20251019-00505 | Telecom | Region_4 | JED1MN2910 | JED2910 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 05:27:39 | 10/20/2025 11:00:24 | 10/19/2025 11:27:39 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/19/2025 05:13:55 | Major | 7114 | CELL SERVICE PROBLEM | 10/19/2025 05:13:45 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE |  |  | PCM-20251019-00000416 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/19/2025 05:27:39 | 10/20/2025 11:00:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000193 | PCM-20251019-00000426 | TT-20251019-00419 | Telecom | Region_4 | JED1M7901 | JED0901 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 05:28:30 | 10/19/2025 09:18:57 | 10/19/2025 11:28:30 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1M7901-CA-L800-P1-VIP-SBTS @ Sceco | 10/19/2025 04:30:34 | Major | 7114 | CELL SERVICE PROBLEM | 10/19/2025 04:30:22 | VIP | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7901 | FLM_TE |  |  | PCM-20251019-00000331 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/19/2025 05:28:30 | 10/19/2025 09:18:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000196 | PCM-20251019-00000438 | TT-20251019-00523 | Reference_telecom | Region_4 | JED6010 | JED6010 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/19/2025 05:31:05 | 10/21/2025 18:19:33 | 10/19/2025 11:31:05 | D-CHANNEL FAILURE at JED6010-P3(Ref:TT-20251019-00162) @ Sceco | 10/19/2025 03:01:34 | Major | 7705 | D-CHANNEL FAILURE | 10/19/2025 03:01:31 | P3 | 2G | jeddah | Sceco | 2G_Cell SA | JED6010 | FLM_TE | [8 empty] | API | 10/19/2025 05:31:05 | 10/19/2025 15:04:13 | 10/21/2025 18:19:24 |  |  | 10/21/2025 18:19:33 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000200 | PCM-20251019-00000448 | TT-20251018-01913 | Telecom | Region_4 | MKMD0561 | MKMD0561 |  |  |  | Khizer Hayat | 10/19/2025 05:33:59 | 10/19/2025 06:05:48 | 10/19/2025 11:33:59 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MKMD0561-P2 @ Sceco | 10/18/2025 20:13:36 | Major | 7607 | TRX OPERATION DEGRADED | 10/18/2025 20:13:28 | P2 | 2G | jeddah | Sceco | 2G_TRX NSA | MKMD0561 | FLM_TE |  |  | PCM-20251018-00001978 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/19/2025 05:33:59 | 10/19/2025 06:05:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000203 | PCM-20251019-00000452 | TT-20251018-01915 | Telecom | Region_4 | MKMD0558 | MKMD0558 |  |  |  | Khizer Hayat | 10/19/2025 05:36:17 | 10/19/2025 06:05:49 | 10/19/2025 11:36:17 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MKMD0558-P2 @ Generator_DG | 10/18/2025 20:13:36 | Major | 7607 | TRX OPERATION DEGRADED | 10/18/2025 20:13:27 | P2 | 2G | jeddah | Generator_DG | 2G_TRX NSA | MKMD0558 | FLM_TE |  |  | PCM-20251018-00001979 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/19/2025 05:36:17 | 10/19/2025 06:05:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Reject_FME | CM20251019000205 | PCM-20251019-00000455 | TT-20251019-00537 | EM | Region_6 | AQQ2425 | AQQ2425 |  |  |  | Muhammad Raees | 10/19/2025 05:39:04 | 10/21/2025 20:22:08 | 10/19/2025 11:39:04 | 1(2G/LTE) sites down under AQQ2425-P3/AQQ2425-P3 @ Generator_SG | 10/19/2025 05:30:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 05:30:28 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | AQQ2425-P3 | FLM_EM | AQQ2425 | Results: DOWN SITE HUB AQQ2425-P3 AQQ2425 Summary: Hub: AQQ2425, Down Count: 1, Down Sites: AQQ2425-P3 Alarm Summary: AQQ2425 Alarm Active on HUB |  |  |  |  | sites down |  | Manual | 10/19/2025 05:39:04 | 10/21/2025 20:21:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000206 | PCM-20251019-00000456 | TT-20251019-00540 | Reference_telecom | Region_6 | KMS0593 | KMS0593 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/19/2025 05:39:21 | 10/19/2025 13:16:46 | 10/19/2025 17:39:21 | LossOfSignal observed in KMS0593_01 towards 10.21.71.55 @ Sceco | 10/18/2025 17:39:15 | Minor |  | LossOfSignal | 10/18/2025 17:38:59 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0593 | FLM_TE | [8 empty] | API | 10/19/2025 05:39:21 | 10/19/2025 13:16:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000207 | PCM-20251019-00000457 | TT-20251019-00541 | Telecom | [7 empty] | 10/19/2025 05:39:22 | 10/19/2025 05:39:22 | 10/19/2025 09:39:22 | OSC_LOS at RPTRA-SEC0008_OCS @ Sceco | 10/19/2025 05:38:57 | Critical | 1-12843 | OSC_LOS | 10/19/2025 05:38:46 | P1 | DWDM |  | Sceco | DWDM NSA | RPTRA | FLM_TE | [5 empty] | 0-TO 8065-SEC0003&MJM0495(1-A)-7-G2AST4-3(RM3/TM3(TO MJM0495_OCS,TNG6WDAPXF(1-A09)-RM2/TM2))-OSC:1 |  |  | API | 10/19/2025 05:39:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000208 | PCM-20251019-00000460 | TT-20251019-00546 | Telecom | Region_3 | HLQS0643 | HLQS0643 |  |  |  | Ameer Ul Hassan | 10/19/2025 05:50:13 | 10/20/2025 11:48:05 | 10/19/2025 11:50:13 | LAN_LOC at HLQS0643_ELC @ Sceco_STB | 10/19/2025 05:45:13 | Major | 1-12926 | LAN_LOC | 10/19/2025 05:45:04 | P1 | SRAN | hail | Sceco_STB | DWDM NSA | HLQS0643 | FLM_TE | [5 empty] | 0-ELC(1-C)-72-G3CXP-11(ETH2/ETH2)-COM:1 |  |  | API | 10/19/2025 05:50:13 | 10/20/2025 11:48:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000209 | PCM-20251019-00000461 | TT-20251019-00431 | Telecom | Region_1 | DAM2M8495 | DAM2495 | Equipment | BSS_HW_Stuck | Reset RFU | Shakeel Ahmed Hafeez Ameen | 10/19/2025 05:50:36 | 10/19/2025 21:51:37 | 10/19/2025 11:50:36 | Cell Unavailable at DAM2M8495-P2-L800 @ Sceco | 10/19/2025 04:42:04 | Major | 29240 | Cell Unavailable | 10/19/2025 04:41:08 | P2 | 4G | dammam | Sceco | LTE SA | DAM2M8495 | FLM_TE |  |  | PCM-20251019-00000459 | Dear FLM, kindly share what TS done from your side before send to BO for RCA as cell flapped with HW alarms | Dear FLM, kindly share what TS done from your side before send to BO for RCA as cell flapped with HW alarms |  |  |  | API | 10/19/2025 05:50:36 | 10/19/2025 09:13:04 | 10/19/2025 21:51:23 |  |  | 10/19/2025 21:51:37 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000215 | PCM-20251019-00000470 | TT-20251019-00553 | Telecom | Region_4 | JED0341 | JED0341 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 05:59:50 | 10/19/2025 05:59:50 | 10/19/2025 11:59:50 | IN_PWR_HIGH ALARM AT JED0341 | 10/19/2025 05:57:22 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/19/2025 05:57:22 | P1 | 2G | jeddah | Sceco | DWDM NSA | JED0341 | FLM_TE | [8 empty] | API | 10/19/2025 05:59:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000216 | PCM-20251019-00000472 | TT-20251019-00555 | Telecom | Region_2 | RIYA2U6760A | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/19/2025 06:00:03 | 10/19/2025 09:44:36 | 10/19/2025 12:00:03 | RF Out of Service at RIYA2U6760A-P3 @ Sceco | 10/19/2025 05:53:47 | Major | 29248 | RF Out of Service | 10/19/2025 05:53:28 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6760A | FLM_TE | [8 empty] | API | 10/19/2025 06:00:03 | 10/19/2025 09:44:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000217 | PCM-20251019-00000473 | TT-20251019-00508 | Telecom | Region_2 | KHJ0120 | KHJ0120 | Equipment | SFP_BTS | Replace SFP | Hakim Ullah Raif Ullah Jan | 10/19/2025 06:04:44 | 10/19/2025 07:16:33 | 10/19/2025 12:04:44 | NR Cell Unavailable at KHJ0120-P3_SRAN @ Generator_SG | 10/19/2025 05:14:17 | Major | 29841 | NR Cell Unavailable | 10/19/2025 05:13:11 | P3 | SRAN | al kharj | Generator_SG | 5G SA | KHJ0120 | FLM_TE |  |  | PCM-20251019-00000463 | Dears, Approved as per TS done by FLM. HW:- SFP Item # 34061940 | Dears, Approved as per TS done by FLM. HW:- SFP Item # 34061940 |  |  |  | API | 10/19/2025 06:04:44 | 10/19/2025 06:50:19 | 10/19/2025 07:13:47 | 10/19/2025 07:13:49 | 10/19/2025 07:13:53 | 10/19/2025 07:16:33 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000231 | PCM-20251019-00000502 | TT-20251019-00599 | Telecom | [7 empty] | 10/19/2025 06:36:42 | 10/19/2025 06:36:42 | 10/19/2025 10:36:42 | OSC_LOS at 9010-9011-SEC0006_OCS @ Sceco | 10/19/2025 06:36:18 | Critical | 1-12843 | OSC_LOS | 10/19/2025 06:36:08 | P1 | DWDM |  | Sceco | DWDM NSA | 9010 | FLM_TE | [5 empty] | 0-TO BUR0019 (BR1)&ZLF0510(1-A)-7-G2AST4-1(RM1/TM1(TO ZLF0510_OCS,TNG6WDAPXF(1-A05)-RM2/TM2))-OSC:1 |  |  | API | 10/19/2025 06:36:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000234 | PCM-20251019-00000506 | TT-20251019-00606 | EM | [7 empty] | 10/19/2025 06:40:19 | 10/19/2025 06:40:19 | 10/19/2025 18:40:19 | RECTIFIER MAINS POWER FAILURE at MUMA1M8070-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/19/2025 06:32:07 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/19/2025 06:31:59 | P3 | 4G |  | Sceco | LTE NSA | MUMA1M8070 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/19/2025 06:40:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000236 | PCM-20251019-00000511 | TT-20251019-00602 | Telecom | Region_2 | SRIY2S7386 | SRIY0386 |  |  |  | Asad Ali Nadiq Khan | 10/19/2025 06:43:31 | 10/19/2025 09:20:04 | 10/19/2025 12:43:31 | 1(LTE) sites down under SRIY0386-P3 @ Sceco | 10/19/2025 06:36:37 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/19/2025 06:35:04 | P3 | 4G | riyadh | Sceco | LTE SA | SRIY0386-P3 | FLM_TE | SRIY0386 | Results: DOWN SITE HUB SRIY0386-P3 SRIY0386 Summary: Hub: SRIY0386, Down Count: 1, Down Sites: SRIY0386-P3 Alarm Summary: SRIY0386 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 06:43:31 | 10/19/2025 09:20:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000237 | PCM-20251019-00000512 | TT-20251019-00571 | Telecom | Region_1 | HFR-0502-NE40E-X8-PE-01 | HFR0502 | Transsmission | MW_HW_stuck | Reset FAN | Ahsan Ul Haq Amtiaz Ali | 10/19/2025 06:44:14 | 10/20/2025 05:31:40 | 10/19/2025 18:44:14 | Dust Net Clean Alarm at HFR-0502-NE40E-X8-PE-01 @ Sceco_STB | 10/19/2025 06:17:13 | Minor | 101-3067995 | Dust Net Clean Alarm | 10/19/2025 06:17:09 | P1 | IPRAN | hafr | Sceco_STB | IPRAN NSA | HFR-0502-NE40E-X8-PE-01 | FLM_TE |  |  | PCM-20251019-00000484 | Kindly check | Kindly check |  |  |  | API | 10/19/2025 06:44:14 | 10/20/2025 03:03:41 | 10/20/2025 03:04:01 | 10/20/2025 03:04:22 | 10/20/2025 04:53:08 | 10/20/2025 05:31:40 |  | Ahsan Ul Haq Amtiaz Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000252 | PCM-20251019-00000559 | TT-20251019-00650 | Telecom | Region_2 | RAS0098 | RAS0098 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/19/2025 07:14:25 | 10/19/2025 15:17:54 | 10/19/2025 11:14:25 | OSC_LOS at RAS0098_OCS @ Sceco_STB | 10/19/2025 07:14:14 | Critical | 1-12843 | OSC_LOS | 10/19/2025 07:14:03 | P1 | SRAN | al rass | Sceco_STB | DWDM NSA | RAS0098 | FLM_TE | [5 empty] | 0-TO QSMD0595(1-A)-7-G2AST4-3(RM3/TM3(TO QSMD0595_HYB,TNG6WDAPXF(1-A03)-RM2/TM2))-OSC:1 |  |  | API | 10/19/2025 07:14:25 | 10/19/2025 15:17:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000253 | PCM-20251019-00000558 | TT-20251019-00651 | Telecom | Region_2 | QSMD0599 | QSMD0599 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/19/2025 07:14:25 | 10/19/2025 15:17:55 | 10/19/2025 11:14:25 | OSC_LOS at QSMD0599_HYB @ Generator_DG | 10/19/2025 07:14:14 | Critical | 1-12843 | OSC_LOS | 10/19/2025 07:14:04 | P3 | SRAN | buraidah | Generator_DG | DWDM NSA | QSMD0599 | FLM_TE | [5 empty] | 0-TO MDQS0459(1-A)-8-G2AST4-1(RM1/TM1(TO QSMD0595, G6WDAPXF(1-B02)-RM2/TM2))-OSC:1 |  |  | API | 10/19/2025 07:14:25 | 10/19/2025 15:17:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000258 | PCM-20251019-00000565 | TT-20251019-00659 | Reference_telecom | Region_1 | DAM2743 | DAM2743 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Shakeel Ahmed Hafeez Ameen | 10/19/2025 07:20:36 | 10/19/2025 12:56:24 | 10/19/2025 13:20:36 | 1(2G) sector down under Dam2743 REF(TT-20251018-01910) | 10/18/2025 20:10:59 | Major | 28016 | GSM Local Cell Unusable | 10/18/2025 20:10:59 | P3 | SRAN | dammam | Sceco | 2G SA | Dam2743 | FLM_TE | [6 empty] | sector down |  | API | 10/19/2025 07:20:36 | 10/19/2025 09:13:05 | 10/19/2025 10:16:17 | 10/19/2025 11:03:26 | 10/19/2025 12:00:18 | 10/19/2025 12:56:24 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000259 | PCM-20251019-00000567 | TT-20251019-00654 | Telecom | Region_4 | JED0294 | JED0294 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/19/2025 07:21:16 | 10/20/2025 13:56:07 | 10/19/2025 13:21:16 | 1(5G) sites down under JED0294-GSM-P3 @ Generator_SG | 10/19/2025 07:13:01 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/19/2025 07:12:59 | P3 | 2G | jeddah | Generator_SG | 5G SA | JED0294-GSM-P3 | FLM_TE | JED0294 | Results: DOWN SITE HUB JED0294-GSM-P3 JED0294 Summary: Hub: JED0294, Down Count: 1, Down Sites: JED0294-GSM-P3 Alarm Summary: JED0294 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-5784788 [ACTIVE] [URL:http://10.97.62.4:8080/NE3S/1.0/] | sites down |  | API | 10/19/2025 07:21:16 | 10/20/2025 13:30:29 | 10/20/2025 13:56:01 |  |  | 10/20/2025 13:56:07 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000261 | PCM-20251019-00000571 | TT-20251019-00670 | Telecom | Region_2 | BUR0019 | BUR0019 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Raise Ahmed Nisar Ahmed | 10/19/2025 07:28:52 | 10/20/2025 13:15:02 | 10/19/2025 11:28:52 | OSC_LOS at BUR0019_OCS @ Sceco_STB | 10/19/2025 07:28:23 | Critical | 1-12843 | OSC_LOS | 10/19/2025 07:28:13 | P1 | SRAN | buraidah | Sceco_STB | DWDM NSA | BUR0019 | FLM_TE | [5 empty] | 0-TO QSHL0737(1-A)-9-G2AST4-2(RM2/TM2(TO 9010-9011-SEC0006_OCS,TNG6WDAPXF(2-A08)-RM1/TM1))-OSC:1 |  |  | API | 10/19/2025 07:28:52 | 10/19/2025 13:36:38 | 10/20/2025 13:14:36 |  |  | 10/20/2025 13:15:02 |  | Raise Ahmed Nisar Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000264 | PCM-20251019-00000574 | TT-20251019-00671 | Reference_EM | Region_1 | HLHD0705 | HLHD0705 | Enviroment | Genset failure_High Temperature | Change Generator water pump | Ibrahim Khaled Shendy Khaled | 10/19/2025 07:29:23 | 10/20/2025 02:31:53 | 10/19/2025 19:29:23 | Mains Failure at HLHD0705-P3_SRAN @ Generator_SG | 10/19/2025 07:19:16 | Minor | 65109 | Mains Failure | 10/19/2025 07:19:12 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0705 | FLM_EM | [8 empty] | API | 10/19/2025 07:29:23 | 10/20/2025 02:30:25 | 10/20/2025 02:31:42 |  |  | 10/20/2025 02:31:53 |  | Ibrahim Khaled Shendy Khaled |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000266 | PCM-20251019-00000579 | TT-20251019-00676 | Telecom | Region_1 | HFR6002 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/19/2025 07:30:57 | 10/19/2025 08:44:29 | 10/19/2025 13:30:57 | BBU CPRI Interface Error at HFR6002-P3_SRAN @ Sceco | 10/19/2025 07:26:50 | Major | 26234 | BBU CPRI Interface Error | 10/19/2025 07:24:11 | P3 | SRAN | hafr | Sceco | 2G NSA | HFR6002 | FLM_TE | [8 empty] | API | 10/19/2025 07:30:57 | 10/19/2025 08:44:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000269 | PCM-20251019-00000588 | TT-20251019-00690 | Telecom | [7 empty] | 10/19/2025 07:37:40 | 10/19/2025 07:37:40 | 10/19/2025 13:37:40 | SPAN_LOSS_EXCEED_EOL at 9010-9011-SEC0006_OCS @ Sceco | 10/19/2025 07:33:13 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/19/2025 07:33:07 | P1 | DWDM |  | Sceco | DWDM NSA | 9010 | FLM_TE | [5 empty] | 0-TO BUR0019 (BR1)&ZLF0510(1-A)-8-G6WDAPXF-11(LINEIN/LINEOUT(TO BUR0019 (BR1)_OCS-TNG6WDAPXF(2-A08)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/19/2025 07:37:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000273 | PCM-20251019-00000596 | TT-20251019-00704 | Telecom | Region_4 | JED1M8066 | JED2066 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 07:48:30 | 10/21/2025 17:12:41 | 10/19/2025 13:48:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8066-CA-L800-SBTS-P3 @ Generator_SG | 10/19/2025 07:47:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 07:47:27 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M8066 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 07:48:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000293 | PCM-20251019-00000635 | TT-20251019-00576 | Telecom | Region_4 | NSH0195 | NSH0195 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/19/2025 08:08:07 | 10/19/2025 10:08:20 | 10/19/2025 10:08:07 | 14(2G) 1(LTE) sites down under NSH0218-USF-P3 @ Generator_SG | 10/19/2025 06:23:12 | Emergency | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/19/2025 06:23:09 | P2 | 2G | adam | Sceco_STB | LTE SA | NSH0218-USF-P3 | FLM_TE | NSH0195 | Hub: NSH0195 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251019-00000610 | Need More Information | Need More Information Wrong TRM Feedback |  | sites down |  | API | 10/19/2025 08:08:07 | 10/19/2025 10:08:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019000298 | PCM-20251019-00000642 | TT-20251013-00060 | Reference_telecom | Region_4 | JED2191 | JED2191 |  |  |  | Nazeer Mohammed | 10/19/2025 08:15:03 | 10/23/2025 17:53:10 | 10/19/2025 20:15:03 | Degrade observed in JED2191_02 towards 10.10.188.148 @ Sceco | 10/12/2025 12:48:12 | Minor |  | Degrade | 10/12/2025 12:47:22 | VIP | 2G | jeddah | Sceco | TX NSA | JED2191 | FLM_TE |  |  | PCM-20251019-00000634 | approved | approved |  |  |  | API | 10/19/2025 08:15:03 | 10/20/2025 13:30:30 | 10/23/2025 17:53:05 | 10/23/2025 17:53:08 | 10/23/2025 17:53:10 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019000299 | PCM-20251019-00000643 | TT-20251013-02057 | MW_HC | Region_6 | JIZ0074 | JIZ0074 |  |  |  | Osama Hadi | 10/19/2025 08:15:13 | 10/21/2025 18:50:48 | 10/19/2025 20:15:13 | Nokia MW HC_P0 Observing Performance Issue at JIZ0074_01-JIZ0005_15 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | VIP | 2G | jizan | Sceco_STB | TX NSA | JIZ0074_01-JIZ0005_15 | FLM_TE |  | Dear FLM , kindly share Full HC report | PCM-20251019-00000271 | Dear FLM , kindly share Full HC report | Dear FLM , kindly share Full HC report |  |  |  | API | 10/19/2025 08:15:13 | 10/19/2025 11:42:36 | 10/21/2025 18:36:58 | 10/21/2025 18:37:02 | 10/21/2025 18:50:48 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000306 | PCM-20251019-00000656 | TT-20251019-00761 | EM | [7 empty] | 10/19/2025 08:20:01 | 10/19/2025 08:20:01 | 10/19/2025 12:20:01 | AIR CONDITION 1&2 at RPTRA-SEC0008_OCS @ Sceco | 10/19/2025 08:18:34 | Critical | 1-12307 | AIR CONDITION 1&2 | 10/19/2025 08:18:26 | P1 | DWDM |  | Sceco | DWDM NSA | RPTRA | FLM_EM | [5 empty] | 0-TO 8065-SEC0003&MJM0495(1-A)-71-E1EFI-[AIR CONDITION 1&2]:4 |  |  | API | 10/19/2025 08:20:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000307 | PCM-20251019-00000659 | TT-20251019-00739 | Telecom | Region_1 | HLHD0705 | HLHD0705 | Enviroment | Genset failure_High Temperature | Change Generator water pump | Ibrahim Khaled Shendy Khaled | 10/19/2025 08:21:03 | 10/20/2025 02:32:07 | 10/19/2025 14:21:03 | 3(2G) 1(3G) 3(LTE) sites down under HLHD0707-P3,HLHD0705-P3,RAF2584-P3-USF/HB1BSCH01 @ Generator_SG | 10/19/2025 08:10:44 | Major | 21825 | CSL Fault | 10/19/2025 08:10:42 | P3 | SRAN | rafha | Generator_SG | 2G_3G_LTE SA | HLHD0707-P3 2G_LTE,HLHD0705-P3 2G_LTE,RAF2584-P3-USF 2G_3G_LTE | FLM_EM | HLHD0705 | Dear Team, Hub:- HLHD0705 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251019-00000652 | Dear Team, Hub:- HLHD0705 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- HLHD0705 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/19/2025 08:21:03 | 10/20/2025 02:30:26 | 10/20/2025 02:31:59 |  |  | 10/20/2025 02:32:07 |  | Ibrahim Khaled Shendy Khaled |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000310 | PCM-20251019-00000671 | TT-20251019-00771 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/19/2025 08:24:08 | 10/20/2025 16:34:12 | 10/19/2025 20:24:08 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/19/2025 08:17:45 | Minor | 1589 | AC Overfrequency | 10/19/2025 08:17:45 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/19/2025 08:24:08 | 10/19/2025 09:52:37 | 10/20/2025 16:34:04 |  |  | 10/20/2025 16:34:12 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000311 | PCM-20251019-00000672 | TT-20251017-01508 | Reference_telecom | Region_4 | JED0449 | JED0449 | Transsmission | SFP_Transmission | Replace SFP | Abdulraqib Abdo Saif Abdulaleem | 10/19/2025 08:24:24 | 10/21/2025 13:25:05 | 10/19/2025 20:24:24 | LossOfSignal observed in JED0449_02 towards 10.10.183.234 @ Generator_SG | 10/17/2025 10:49:27 | Minor |  | LossOfSignal | 10/17/2025 10:48:57 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0449 | FLM_TE |  |  | PCM-20251019-00000630 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/19/2025 08:24:24 | 10/20/2025 14:46:08 | 10/20/2025 14:47:24 | 10/20/2025 14:47:26 | 10/20/2025 14:47:28 | 10/21/2025 13:25:05 |  | Abdulraqib Abdo Saif Abdulaleem |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000312 | PCM-20251019-00000673 | TT-20251011-01803 | Reference_telecom | Region_4 | JED0063 | JED0063 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 08:24:51 | 10/19/2025 08:24:51 | 10/19/2025 20:24:51 | ReplaceableUnitProblem observed in JED0063_DIA towards 10.221.226.134 @ Sceco | 10/11/2025 07:12:01 | Minor |  | ReplaceableUnitProblem | 10/11/2025 07:11:54 | P2 | 2G | jeddah | Sceco | TX NSA | JED0063 | FLM_TE |  |  | PCM-20251019-00000632 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/19/2025 08:24:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000334 | PCM-20251019-00000715 | TT-20251019-00804 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 08:45:19 | 10/19/2025 08:45:19 | 10/19/2025 12:45:19 | Air Condition 1 FA SH2 at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 08:44:50 | Critical | 65352 | Air Condition 1 FA SH2 | 10/19/2025 08:44:45 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 08:45:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000335 | PCM-20251019-00000714 | TT-20251019-00803 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 08:45:19 | 10/19/2025 08:45:19 | 10/19/2025 12:45:19 | Air-Condition #2 FA(SH2) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 08:44:50 | Critical | 65353 | Air-Condition #2 FA(SH2) | 10/19/2025 08:44:45 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 08:45:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000336 | PCM-20251019-00000716 | TT-20251019-00805 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 08:45:19 | 10/19/2025 08:45:19 | 10/19/2025 12:45:19 | Gen set running(SH1) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 08:44:48 | Critical | 65344 | Gen set running(SH1) | 10/19/2025 08:44:41 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 08:45:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000337 | PCM-20251019-00000717 | TT-20251019-00806 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Shahid Ahmed Shah Nawaz | 10/19/2025 08:45:50 | 10/19/2025 10:17:41 | 10/19/2025 12:45:50 | Commercial Power Fail(SH2) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 08:45:18 | Critical | 65357 | Commercial Power Fail(SH2) | 10/19/2025 08:45:13 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 08:45:50 | 10/19/2025 08:58:59 | 10/19/2025 08:59:14 | 10/19/2025 08:59:17 | 10/19/2025 09:01:21 | 10/19/2025 10:17:41 |  | Shahid Ahmed Shah Nawaz |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000345 | PCM-20251019-00000734 | TT-20251019-00824 | Reference_telecom | Region_1 | DAM0311 | DAM0311 | Transsmission | MW_HW_fault | Replace ODU | Shakeel Ahmed Hafeez Ameen | 10/19/2025 08:57:12 | 10/19/2025 19:35:39 | 10/19/2025 20:57:12 | HARD_BAD at DAM0311_NE_7_V @ Sceco_STB | 10/19/2025 07:56:52 | Minor | 1-236 | HARD_BAD | 10/19/2025 07:56:43 | VIP | SRAN | dammam | Sceco_STB | TX NSA | DAM0311 | FLM_TE | [8 empty] | API | 10/19/2025 08:57:12 | 10/19/2025 09:13:05 | 10/19/2025 17:30:13 | 10/19/2025 17:51:26 | 10/19/2025 17:51:29 | 10/19/2025 19:35:39 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000348 | PCM-20251019-00000738 | TT-20251019-00828 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/19/2025 08:59:16 | 10/21/2025 23:22:30 | 10/19/2025 14:59:16 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/19/2025 08:49:03 | Major | 65102 | high temprature 32 | 10/19/2025 08:48:59 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/19/2025 08:59:16 | 10/21/2025 23:22:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000355 | PCM-20251019-00000757 | TT-20251019-00847 | EM | Region_1 | DMJR0136 | DMJR0136 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Ibrahim Ù Abdulfttah Ibrahim | 10/19/2025 09:10:07 | 10/22/2025 22:12:23 | 10/19/2025 21:10:07 | Major Rec alarm at DMJR0136-P3_SRAN @ Sceco | 10/19/2025 09:01:44 | Minor | 65107 | Major Rec alarm | 10/19/2025 08:59:55 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR0136 | FLM_EM | [8 empty] | API | 10/19/2025 09:10:07 | 10/22/2025 20:23:58 | 10/22/2025 21:27:16 | 10/22/2025 21:27:18 | 10/22/2025 21:27:21 | 10/22/2025 22:12:23 |  | Ibrahim Ù Abdulfttah Ibrahim |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000372 | PCM-20251019-00000789 | TT-20251017-01311 | Telecom | Region_4 | JED0325 | JED0325 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/19/2025 09:25:29 | 10/19/2025 09:38:36 | 10/19/2025 21:25:29 | AS BO Requested : Thanks to rectify JED0008-JED0325 | 10/17/2025 18:46:15 | Minor | 113388 | LOF | 10/17/2025 18:46:15 | P2 | 2G | jeddah | Sceco | TX NSA | JED0008-JED0325 | FLM_TE |  |  | PCM-20251019-00000583 | Mail shared to planning team | Mail shared to planning team |  |  |  | API | 10/19/2025 09:25:29 | 10/19/2025 09:38:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000380 | PCM-20251019-00000802 | TT-20251019-00886 | Reference_telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/19/2025 09:33:53 | 10/19/2025 09:33:53 | 10/19/2025 21:33:53 | RF Unit RX Channel RTWP/RSSI Unbalanced at MAK6018-DCU-P3 @ Sceco | 10/19/2025 06:33:45 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/19/2025 06:33:42 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/19/2025 09:33:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000383 | PCM-20251019-00000812 | TT-20251019-00894 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/19/2025 09:39:04 | 10/19/2025 12:35:02 | 10/19/2025 21:39:04 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/19/2025 09:30:58 | Minor | 7103 | HIGH TEMP | 10/19/2025 09:30:51 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/19/2025 09:39:04 | 10/19/2025 12:35:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000384 | PCM-20251019-00000814 | TT-20251018-01627 | Telecom | Region_6 | RJL0128 | RJL0128 | Transsmission | MW_HW_fault | Replace ODU | Muhammad Jamal Khan Abbas Ali | 10/19/2025 09:40:24 | 10/21/2025 00:05:26 | 10/19/2025 21:40:24 | AS BO Requested MW HC For Link RJL0128- ABDB9020 | 10/18/2025 17:19:29 | Minor | 113388 | LOF | 10/18/2025 17:19:29 | P2 | 2G | mohail | Sceco | TX NSA | RJL0128- ABDB9020 | FLM_TE |  |  | PCM-20251019-00000105 | Approved | Approved |  |  |  | API | 10/19/2025 09:40:24 | 10/19/2025 09:53:06 | 10/21/2025 00:05:13 |  |  | 10/21/2025 00:05:26 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000392 | PCM-20251019-00000841 | TT-20251012-01949 | MW_HC | Region_6 | KHS0929 | KHS0929 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/19/2025 09:47:04 | 10/19/2025 13:16:47 | 10/19/2025 21:47:04 | NEC MW HC_P1 Observing Performance Issue at KHS0929(10.154.166.38)--YAR0135(10.154.166.41) | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | 2G | khamis mushyet | Generator_DG | TX NSA | KHS0929(10.154.166.38)--YAR0135(10.154.166.41) | FLM_TE |  |  | PCM-20251019-00000241 | YAR0135(10.154.166.41) still not clear today (performance & active alarms & update IDU time nok) to check | YAR0135(10.154.166.41) still not clear today (performance & active alarms & update IDU time nok) to check |  |  |  | API | 10/19/2025 09:47:04 | 10/19/2025 13:16:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000393 | PCM-20251019-00000843 | TT-20251019-00858 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/19/2025 09:47:40 | 10/21/2025 18:19:09 | 10/19/2025 15:47:40 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/19/2025 09:09:56 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/19/2025 09:09:45 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251019-00000767 | please the intermedia connection between JED1U6720 and JED1U6920 | please the intermedia connection between JED1U6720 and JED1U6920 |  |  |  | API | 10/19/2025 09:47:40 | 10/19/2025 15:04:13 | 10/21/2025 18:18:58 |  |  | 10/21/2025 18:19:09 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000394 | PCM-20251019-00000845 | TT-20251019-00902 | EM | [7 empty] | 10/19/2025 09:48:33 | 10/19/2025 09:48:33 | 10/19/2025 15:48:33 | 1(2G/LTE) sites down under MUMA2070-P3-P3/MUMA2070-P3-P3 @ Sceco | 10/19/2025 09:40:12 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 09:40:07 | P3 | 2G |  | Sceco | 2G_LTE SA | MUMA2070-P3-P3 | FLM_EM | MUMA2070 | Results: DOWN SITE HUB MUMA2070-P3-P3 MUMA2070 Summary: Hub: MUMA2070, Down Count: 1, Down Sites: MUMA2070-P3-P3 Alarm Summary: MUMA2070 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 09:48:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000398 | PCM-20251019-00000853 | TT-20251019-00932 | EM | Region_4 | JED1MN2979 | JED2979 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Abd EL Azeez EL Sayed Soliman | 10/19/2025 09:55:02 | 10/19/2025 12:01:01 | 10/19/2025 13:55:02 | 1(2G/LTE/5G) sites down under JED2979-P1-VIP @ Generator_SG | 10/19/2025 09:46:42 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/19/2025 09:46:39 | VIP | 5G | jeddah | Generator_SG | 2G_LTE_5G SA | JED2979-P1-VIP | FLM_EM | JED2979 | Results: DOWN SITE HUB JED2979-P1-VIP JED2979 Summary: Hub: JED2979, Down Count: 1, Down Sites: JED2979-P1-VIP Alarm Summary: JED2979 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.244.29.60:8080] [URL:http://10.244.29.60:8080/NE3S/1.0/] | sites down |  | API | 10/19/2025 09:55:02 | 10/19/2025 10:46:27 | 10/19/2025 12:00:53 |  |  | 10/19/2025 12:01:01 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000406 | PCM-20251019-00000869 | TT-20251019-00953 | Telecom | Region_4 | JED2040 | JED2040 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 10:05:14 | 10/19/2025 10:05:14 | 10/19/2025 22:05:14 | PT::FLM need to perform HC at JED2040 (BO request) | 10/19/2025 10:05:05 | Minor | 676767671 | Health Check-WO to TE FME | 10/19/2025 10:05:05 | P2 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED2040 | FLM_TE | [8 empty] | API | 10/19/2025 10:05:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000408 | PCM-20251019-00000871 | TT-20251019-00945 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/19/2025 10:05:32 | 10/19/2025 12:18:00 | 10/19/2025 14:05:32 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/19/2025 09:57:02 | Critical | 301 | NE Is Disconnected | 10/19/2025 09:56:58 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 10:05:32 | 10/19/2025 11:57:58 | 10/19/2025 12:17:53 |  |  | 10/19/2025 12:18:00 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000420 | PCM-20251019-00000908 | TT-20251019-01000 | EM | Region_4 | JED1M8979 | JED2979 | Transsmission | IPRAN_Fluctuation | Change Port | Abd EL Azeez EL Sayed Soliman | 10/19/2025 10:26:04 | 10/19/2025 12:00:46 | 10/19/2025 16:26:04 | SHELTER DOOR OPEN at JED1M8979-L800-CA-P1-VIP @ Generator_SG | 10/19/2025 10:25:50 | Major | 7103 | SHELTER DOOR OPEN | 10/19/2025 10:24:21 | VIP | 4G | jeddah | Generator_SG | LTE NSA | JED1M8979 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/19/2025 10:26:04 | 10/19/2025 10:46:28 | 10/19/2025 12:00:36 |  |  | 10/19/2025 12:00:46 |  | Abd EL Azeez EL Sayed Soliman |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000423 | PCM-20251019-00000911 | TT-20251019-01002 | Telecom | Region_4 | SQSH1M7150 | SQSH0150 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/19/2025 10:27:07 | 10/21/2025 17:12:44 | 10/19/2025 16:27:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at SQSH1M7150-G9-NL8-L18-SBTS-P2-USF @ Sceco_STB | 10/19/2025 10:26:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 10:26:14 | P2 | 4G | qunfuddah | Sceco_STB | 5G_Cell SA | SQSH1M7150 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 10:27:07 | 10/19/2025 11:04:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000424 | PCM-20251019-00000913 | TT-20251019-01005 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/19/2025 10:27:37 | 10/19/2025 10:27:37 | 10/19/2025 14:27:37 | Gen set running(SH1) at R2_RY2_HWBSC01 @ Sceco_STB | 10/19/2025 10:26:58 | Critical | 65344 | Gen set running(SH1) | 10/19/2025 10:26:54 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 10:27:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000425 | PCM-20251019-00000914 | TT-20251018-00024 | Reference_telecom | Region_6 | HRD1M7779 | HRD0779 | Equipment | SW | Issue was solved after softaware configuration | Muhammad Usman Muhammad Zia ul haq | 10/19/2025 10:28:44 | 10/19/2025 15:06:06 | 10/19/2025 16:28:44 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at HRD1M7779-P3-CA-L800 @ Sceco | 10/17/2025 22:28:39 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/17/2025 22:25:32 | P2 | 4G | derb | Sceco | LTE NSA | HRD1M7779 | FLM_TE |  |  | PCM-20251018-00002105 | Dear FLM team, kindly check MW HRD0779 -JDJZ0885 | Dear FLM team, kindly check MW HRD0779 -JDJZ0885 |  |  |  | API | 10/19/2025 10:28:44 | 10/19/2025 13:27:16 | 10/19/2025 15:05:59 |  |  | 10/19/2025 15:06:06 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000431 | PCM-20251019-00000933 | TT-20251019-01026 | Telecom | Region_3 | MDN0261 | MDN0261 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/19/2025 10:40:02 | 10/19/2025 20:05:37 | 10/19/2025 16:40:02 | NR Cell Unavailable at MDN0261-P3_SRAN @ Sceco | 10/19/2025 10:33:05 | Major | 29841 | NR Cell Unavailable | 10/19/2025 10:31:31 | P3 | SRAN | madinah | Sceco | 5G SA | MDN0261 | FLM_TE | [8 empty] | API | 10/19/2025 10:40:02 | 10/19/2025 20:05:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019000444 | PCM-20251019-00000960 | TT-20251019-01055 | Telecom | Region_4 | JED1M8178 | JED2178 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/19/2025 10:52:56 | 10/20/2025 03:51:36 | 10/19/2025 16:52:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8178-P3-CA-L800 @ Sceco | 10/19/2025 10:52:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 10:52:05 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8178 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 10:52:56 | 10/20/2025 03:50:59 | 10/20/2025 03:51:30 | 10/20/2025 03:51:34 | 10/20/2025 03:51:36 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000447 | PCM-20251019-00000964 | TT-20251019-01058 | Reference_telecom | Region_5 | MAK0053 | MAK0053 |  |  |  | Muhammad Shabbir Muhammad | 10/19/2025 10:54:59 | 10/19/2025 10:54:59 | 10/19/2025 22:54:59 | DemXpicLOS observed in MAK0053 -19 towards 10.3.224.17 @ Sceco_STB | 10/18/2025 22:57:00 | Minor |  | DemXpicLOS | 10/18/2025 22:54:38 | P1 | 2G | makkah | Sceco_STB | TX NSA | MAK0053 | FLM_TE | [8 empty] | API | 10/19/2025 10:54:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000449 | PCM-20251019-00000966 | TT-20251019-01060 | EM | Region_5 | MK4_CORE | MK4 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/19/2025 10:55:00 | 10/20/2025 08:32:23 | 10/19/2025 16:55:00 | AC UNIT-2 FAULTY IN CORE ROOM at MK4_CORE-P1-VIP @ Sceco_STB | 10/19/2025 10:54:40 | Major | 7103 | AC UNIT-2 FAULTY IN CORE ROOM | 10/19/2025 10:54:31 | P1 | 4G | makkah | Sceco_STB | 2G NSA | MK4_CORE | FLM_EM | [5 empty] | AC UNIT-2 FAULTY IN CORE ROOM |  |  | API | 10/19/2025 10:55:00 | 10/20/2025 08:32:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000450 | PCM-20251019-00000971 | TT-20251019-01065 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/19/2025 10:56:33 | 10/19/2025 10:56:33 | 10/19/2025 14:56:33 | Air Condition 1 FA SH2 at R2_RY2_HWBSC01 @ Sceco_STB | 10/19/2025 10:56:20 | Critical | 65352 | Air Condition 1 FA SH2 | 10/19/2025 10:56:16 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 10:56:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000451 | PCM-20251019-00000972 | TT-20251019-01066 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/19/2025 10:56:34 | 10/19/2025 10:56:34 | 10/19/2025 14:56:34 | Air-condition #1 FA(SH1) at R2_RY2_HWBSC01 @ Sceco_STB | 10/19/2025 10:56:20 | Critical | 65361 | Air-condition #1 FA(SH1) | 10/19/2025 10:56:16 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 10:56:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000452 | PCM-20251019-00000973 | TT-20251019-01067 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/19/2025 10:56:35 | 10/19/2025 10:56:35 | 10/19/2025 14:56:35 | Air-Condition #2 FA(SH1) at R2_RY2_HWBSC01 @ Sceco_STB | 10/19/2025 10:56:20 | Critical | 65337 | Air-Condition #2 FA(SH1) | 10/19/2025 10:56:16 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 10:56:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000453 | PCM-20251019-00000975 | TT-20251019-01069 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/19/2025 10:56:37 | 10/19/2025 10:56:37 | 10/19/2025 14:56:37 | Air-Condition #2 FA(SH2) at R2_RY2_HWBSC01 @ Sceco_STB | 10/19/2025 10:56:20 | Critical | 65353 | Air-Condition #2 FA(SH2) | 10/19/2025 10:56:16 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 10:56:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000457 | PCM-20251019-00000982 | TT-20251019-01023 | Telecom | Region_4 | JED1MC0407 | JED0407 | Equipment | SFP_BTS | Clean SFP | Mohammed Ramadan A Abu Abid | 10/19/2025 11:00:04 | 10/19/2025 11:49:25 | 10/19/2025 17:00:04 | BASE STATION SERVICE PROBLEM (RF module configuring failed) at JED1MC0407-NR3.5-P3 @ Sceco | 10/19/2025 10:33:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 10:33:01 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MC0407 | FLM_TE |  |  | PCM-20251019-00000929 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/19/2025 11:00:04 | 10/19/2025 11:13:10 | 10/19/2025 11:13:23 | 10/19/2025 11:13:26 | 10/19/2025 11:13:29 | 10/19/2025 11:49:25 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000458 | PCM-20251019-00000983 | TT-20251019-01017 | EM | Region_1 | JBL0913 | JBL0913 |  |  |  | Hamid Bilal Bashir Ahmed | 10/19/2025 11:00:05 | 10/23/2025 17:15:26 | 10/19/2025 15:00:05 | 2(2G/3G/LTE) sites down under JBL0913,JBAP0137-P1/R1_JB_HWBSC01 @ Sceco | 10/19/2025 10:33:08 | Critical | 21825 | CSL Fault | 10/19/2025 10:33:06 | P2 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBAP0137-P1 | FLM_EM | JBL0913 | Dear Team, Hub:- JBL0913 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | PCM-20251019-00000980 | Dear Team, Hub:- JBL0913 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | Dear Team, Hub:- JBL0913 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. |  | sites down |  | API | 10/19/2025 11:00:05 | 10/19/2025 16:35:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000475 | PCM-20251019-00001023 | TT-20251018-01642 | Telecom | Region_2 | RIY0010 | RIY0010 |  |  |  | Farmanullah Akbar Jan | 10/19/2025 11:11:53 | 10/19/2025 16:14:22 | 10/19/2025 15:11:53 | POWER_JITTER at RIY0010_OCS @ Sceco | 10/18/2025 17:26:16 | Critical | 1-14579 | POWER_JITTER | 10/18/2025 17:26:04 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0010 | FLM_TE |  |  | PCM-20251018-00001829 | Cleared check with FO and Close. | Cleared check with FO and Close. |  |  |  | API | 10/19/2025 11:11:53 | 10/19/2025 16:14:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000480 | PCM-20251019-00001035 | TT-20251018-01459 | Reference_telecom | Region_6 | NMS1M7175 | NMS0175 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 11:13:52 | 10/19/2025 15:55:09 | 10/19/2025 23:13:52 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NMS1M7175-G9-L8-L18-NL21-SBTS-P2-WBB-G3 @ Sceco | 10/18/2025 15:20:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 13:46:18 | P2 | 4G | namas | Sceco | LTE NSA | NMS1M7175 | FLM_TE |  |  | PCM-20251018-00002106 | Dear FLM team, kindly perform HC for MW NMS0175-ABBS2161 | Dear FLM team, kindly perform HC for MW NMS0175-ABBS2161 |  |  |  | API | 10/19/2025 11:13:52 | 10/19/2025 12:02:22 | 10/19/2025 15:54:18 |  |  | 10/19/2025 15:55:09 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000481 | PCM-20251019-00001038 | TT-20251019-01127 | EM | [7 empty] | 10/19/2025 11:16:11 | 10/19/2025 11:16:11 | 10/19/2025 15:16:11 | DOOR OPEN at MUHAYIL-SEC0048_OCS @ Sceco | 10/19/2025 11:15:42 | Critical | 1-12307 | DOOR OPEN | 10/19/2025 11:15:32 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/19/2025 11:16:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000490 | PCM-20251019-00001066 | TT-20251019-01146 | Telecom | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/19/2025 11:31:19 | 10/22/2025 21:40:41 | 10/19/2025 17:31:19 | 4(2G) 1(3G) 4(LTE) sites down under JBKH0143-P3-USF,KFKM0783-P3,KFKM0782-P3,KFKM0784-P3/HB1BSCH01 @ Generator_SG | 10/19/2025 11:22:05 | Major | 21825 | CSL Fault | 10/19/2025 11:22:03 | P3 | SRAN | hafr | Generator_SG | 2G_3G_LTE SA | JBKH0143-P3-USF 2G_3G_LTE,KFKM0783-P3 2G_LTE,KFKM0782-P3 2G_LTE | FLM_EM | KFKM0784 | Dear Team, Hub:- KFKM0784 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251019-00001063 | Dear Team, Hub:- KFKM0784 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- KFKM0784 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/19/2025 11:31:19 | 10/22/2025 21:40:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000493 | PCM-20251019-00001072 | TT-20251019-01163 | Reference_telecom | Region_5 | HAJ0315 | HAJ0315 |  |  |  | Ahmed Mohamed Soliman Mohamed | 10/19/2025 11:35:18 | 10/19/2025 11:35:18 | 10/19/2025 23:35:18 | ReplaceableUnitProblem observed in HAJ0315 towards 10.10.142.198 @ Sceco | 10/18/2025 23:35:09 | Minor |  | ReplaceableUnitProblem | 10/18/2025 23:35:05 | P2 | 2G | makkah | Sceco | TX NSA | HAJ0315 | FLM_TE | [8 empty] | API | 10/19/2025 11:35:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000505 | PCM-20251019-00001102 | TT-20251019-01187 | Telecom | Region_4 | JED1MN0575 | JED0575 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 11:48:14 | 10/20/2025 16:09:46 | 10/19/2025 17:48:14 | BASE STATION SERVICE PROBLEM (RF BB bus connection transmission error) at JED1MN0575-NR2.6-P3 @ Sceco | 10/19/2025 11:41:42 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 11:41:30 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0575 | FLM_TE |  |  | PCM-20251019-00001095 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/19/2025 11:48:14 | 10/20/2025 16:09:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000524 | PCM-20251019-00001147 | TT-20251019-01235 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/19/2025 12:06:19 | 10/19/2025 16:34:58 | 10/19/2025 18:06:19 | LOCAL_FAULT at YBDB2655_ELC @ Sceco_STB | 10/19/2025 12:02:39 | Major | 1-12545 | LOCAL_FAULT | 10/19/2025 12:02:29 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE | [5 empty] | 0-ELC(1-C)-4-G1M520S-3(RX1/TX1)-CLIENT:1 |  |  | API | 10/19/2025 12:06:19 | 10/19/2025 16:34:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000548 | PCM-20251019-00001212 | TT-20251019-01305 | Telecom | Region_4 | MLJI1M3204 | MLJI0204 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 12:28:50 | 10/21/2025 19:34:42 | 10/19/2025 18:28:50 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at MLJI1M3204-P3 @ Generator_SG | 10/19/2025 12:24:43 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 23:02:42 | P3 | 3G | alaith | Generator_SG | 3G NSA | MLJI1M3204 | FLM_TE |  |  | PCM-20251019-00001203 | Site had no OAM connectivity ,FLM need to check and close with RC. | Site had no OAM connectivity ,FLM need to check and close with RC. |  |  |  | API | 10/19/2025 12:28:50 | 10/19/2025 23:01:38 | 10/21/2025 19:34:29 |  |  | 10/21/2025 19:34:42 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000549 | PCM-20251019-00001213 | TT-20251019-01302 | Telecom | Region_4 | MLJI1M3196 | MLJI0196 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 12:29:00 | 10/21/2025 19:35:13 | 10/19/2025 18:29:00 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at MLJI1M3196-P3 @ Generator_SG | 10/19/2025 12:24:20 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 23:02:40 | P3 | 3G | alaith | Generator_SG | 3G NSA | MLJI1M3196 | FLM_TE |  |  | PCM-20251019-00001199 | Site had no OAM connectivity ,FLM need to check and close with RC. | Site had no OAM connectivity ,FLM need to check and close with RC. |  |  |  | API | 10/19/2025 12:29:00 | 10/19/2025 23:01:39 | 10/21/2025 19:35:03 |  |  | 10/21/2025 19:35:13 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000552 | PCM-20251019-00001217 | TT-20251019-01312 | Reference_telecom | Region_4 | JD3 | JD3 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/19/2025 12:30:04 | 10/21/2025 02:00:29 | 10/20/2025 00:30:04 | Degrade observed in JD3_03 towards 10.10.146.81 @ Sceco_STB | 10/19/2025 00:30:00 | Minor |  | Degrade | 10/19/2025 00:29:47 | P1 | DWDM | jeddah | Sceco_STB | TX NSA | JD3 | FLM_TE | [8 empty] | API | 10/19/2025 12:30:04 | 10/21/2025 02:00:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000553 | PCM-20251019-00001218 | TT-20251019-01313 | Reference_telecom | Region_4 | JED0217 | JED0217 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 12:30:04 | 10/19/2025 12:30:04 | 10/20/2025 00:30:04 | LossOfSignal observed in JED0217 towards 10.10.146.82 @ Sceco | 10/19/2025 00:30:02 | Minor |  | LossOfSignal | 10/19/2025 00:29:55 | P2 | 2G | jeddah | Sceco | TX NSA | JED0217 | FLM_TE | [8 empty] | API | 10/19/2025 12:30:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000559 | PCM-20251019-00001229 | TT-20251019-01336 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/19/2025 12:39:53 | 10/19/2025 13:24:29 | 10/19/2025 18:39:53 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/19/2025 12:32:41 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 12:32:32 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/19/2025 12:39:53 | 10/19/2025 13:24:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000562 | PCM-20251019-00001234 | TT-20251013-00690 | Telecom | Region_6 | TNM2230 | TNM2230 | Equipment | BSS_HW_fault | Replace GPS Antenna | Muhammad Jamal Khan Abbas Ali | 10/19/2025 12:43:07 | 10/19/2025 17:25:49 | 10/19/2025 18:43:07 | BCF NOTIFICATION (FF FF FF FF FF FF) at TNM2230-P3-CAP @ Sceco | 10/13/2025 04:17:08 | Major | 7602 | BCF NOTIFICATION | 10/13/2025 04:16:55 | P3 | 2G | namas | Sceco | 2G NSA | TNM2230 | FLM_TE |  |  | PCM-20251014-00001220 | Approved | Approved |  |  |  | API | 10/19/2025 12:43:07 | 10/19/2025 17:24:34 | 10/19/2025 17:25:28 |  |  | 10/19/2025 17:25:49 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000566 | PCM-20251019-00001245 | TT-20251019-01350 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 12:47:37 | 10/19/2025 12:47:37 | 10/19/2025 16:47:37 | Gen set running(SH1) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 12:47:17 | Critical | 65344 | Gen set running(SH1) | 10/19/2025 12:47:12 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 12:47:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000567 | PCM-20251019-00001246 | TT-20251019-01351 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 12:47:38 | 10/19/2025 12:47:38 | 10/19/2025 16:47:38 | Air-Condition #2 FA(SH2) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 12:47:18 | Critical | 65353 | Air-Condition #2 FA(SH2) | 10/19/2025 12:47:14 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 12:47:38 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000568 | PCM-20251019-00001247 | TT-20251019-01352 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 12:47:39 | 10/19/2025 12:47:39 | 10/19/2025 16:47:39 | Air Condition 1 FA SH2 at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 12:47:18 | Critical | 65352 | Air Condition 1 FA SH2 | 10/19/2025 12:47:14 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 12:47:39 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000569 | PCM-20251019-00001249 | TT-20251019-01353 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 12:48:09 | 10/19/2025 12:48:09 | 10/19/2025 16:48:09 | Commercial Power Fail(SH2) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 12:47:56 | Critical | 65357 | Commercial Power Fail(SH2) | 10/19/2025 12:47:50 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 12:48:09 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000587 | PCM-20251019-00001286 | TT-20251019-01393 | Telecom | Region_4 | JED1M8596 | JED2596 | Equipment | SFP_BTS | Replace SFP | MALIK ATIF ZAMAN | 10/19/2025 13:02:04 | 10/22/2025 15:29:42 | 10/19/2025 17:02:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8596-P1-CA-L800 @ Sceco | 10/19/2025 13:01:13 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 13:01:05 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8596 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 13:02:04 | 10/20/2025 16:09:47 | 10/21/2025 17:40:33 | 10/21/2025 17:40:35 | 10/21/2025 18:25:20 | 10/22/2025 15:29:42 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000592 | PCM-20251019-00001295 | TT-20251019-01368 | Telecom | Region_4 | JED2297 | JED2297 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 13:08:47 | 10/20/2025 16:09:48 | 10/19/2025 19:08:47 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED2297-P3 @ Sceco | 10/19/2025 12:46:55 | Major | 7602 | BCF NOTIFICATION | 10/19/2025 12:46:40 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2297 | FLM_TE |  |  | PCM-20251019-00001264 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/19/2025 13:08:47 | 10/20/2025 16:09:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000593 | PCM-20251019-00001296 | TT-20251019-01348 | Telecom | Region_4 | JED2352 | JED2352 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 13:08:55 | 10/19/2025 13:08:55 | 10/19/2025 19:08:55 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED2352-P2 @ Sceco | 10/19/2025 12:39:30 | Major | 7602 | BCF NOTIFICATION | 10/19/2025 12:39:15 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2352 | FLM_TE |  |  | PCM-20251019-00001242 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/19/2025 13:08:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019000595 | PCM-20251019-00001300 | TT-20251019-01406 | Telecom | Region_4 | JED0899 | JED0899 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 13:10:21 | 10/21/2025 17:12:45 | 10/19/2025 19:10:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0899-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Generator_SG | 10/19/2025 13:09:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 13:09:25 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0899 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 13:10:21 | 10/20/2025 11:00:25 | 10/20/2025 17:36:45 | 10/20/2025 17:36:47 | 10/20/2025 17:42:31 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000596 | PCM-20251019-00001304 | TT-20251018-01654 | Telecom | Region_2 | RY1-ASG-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/19/2025 13:14:05 | 10/19/2025 13:14:05 | 10/20/2025 01:14:05 | DWDM Link down at RY1-ASG-01 | 10/18/2025 17:30:37 | Minor | 15269 | LOS | 10/18/2025 17:30:37 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | DWDM Link down at RY1-ASG-01 | FLM_TE |  |  | PCM-20251019-00001169 | due to SEC link flapped and auto restored between RIY0201--RIY0010 link stable UP no no need actions | due to SEC link flapped and auto restored between RIY0201--RIY0010 link stable UP no no need actions |  |  |  | API | 10/19/2025 13:14:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000598 | PCM-20251019-00001307 | TT-20251019-01407 | Reference_telecom | Region_6 | TLT0933 | TLT0933 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/19/2025 13:15:38 | 10/19/2025 15:19:37 | 10/19/2025 17:15:38 | 8(2G/3G/LTE) sites down under TLT0933 (REF::TT-20251019-00742)@ Sceco | 10/19/2025 10:57:27 | Critical | 7706 | BTS O&M LINK FAILURE | 10/19/2025 10:57:27 | P3 | 2G | tathleeth | Sceco_STB | 2G_3G_LTE SA | TLT0324-P3,TLT0752-P3,TLT0366-P2-USF,TLT0390-P2-USF,TLT0933-P3,TLT0367-P2,TLT0653-P3,TLT0365-P3 | FLM_TE | TLT0324 | Results: DOWN SITE HUB TLT0324-P3 TLT0324 TLT0752-P3 Need to check TLT0366-P2-USF TLT0366 TLT0390-P2-USF TLT0390 TLT0933-P3 TLT0933 TLT0367-P2 TLT0933 TLT0653-P3 TLT0933 TLT0365-P3 TLT0933 Summary: Hub: TLT0324, Down Count: 1, Down Sites: TLT0324-P3 Hub: TLT0366, Down Count: 1, Down Sites: TLT0366-P2-USF Hub: TLT0390, Down Count: 1, Down Sites: TLT0390-P2-USF Hub: TLT0933, Down Count: 4, Down Sites: TLT0933-P3, TLT0367-P2, TLT0653-P3, TLT0365-P3 Alarm Summary: TLT0324 No Active Alarm on HUB HUB site not found TLT0366 No Active Alarm on HUB TLT0390 No Active Alarm on HUB TLT0933 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 13:15:38 | 10/19/2025 13:17:27 | 10/19/2025 15:19:29 |  |  | 10/19/2025 15:19:37 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000599 | PCM-20251019-00001308 | TT-20251019-01431 | Telecom | Region_6 | TLT0722 | TLT0722 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/19/2025 13:16:01 | 10/19/2025 13:35:41 | 10/20/2025 01:16:01 | ODU CPU / Cable Open at TLT0722-1 on 10.89.224.46 @ Sceco | 10/19/2025 13:15:02 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/19/2025 13:10:16 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0722 | FLM_TE | [8 empty] | API | 10/19/2025 13:16:01 | 10/19/2025 13:17:28 | 10/19/2025 13:35:34 |  |  | 10/19/2025 13:35:41 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000600 | PCM-20251019-00001309 | TT-20251019-01433 | EM | [7 empty] | 10/19/2025 13:16:02 | 10/19/2025 13:16:02 | 10/19/2025 17:16:02 | MAIN AC POWER FAILURE at 8065-SEC0003_OCS @ Sceco_STB | 10/19/2025 13:14:29 | Critical | 1-12307 | MAIN AC POWER FAILURE | 10/19/2025 13:14:19 | P1 | DWDM |  | Sceco_STB | DWDM NSA | 8065 | FLM_EM | [5 empty] | 0-TO RIY0298 (RY4)&RPTRA-SEC0008(1-A)-72-E1EFI-[MAIN AC POWER FAILURE]:2 |  |  | API | 10/19/2025 13:16:02 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000606 | PCM-20251019-00001327 | TT-20251018-02046 | Reference_telecom | Region_4 | HHR1M7494 | HHR0494 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/19/2025 13:22:40 | 10/20/2025 13:37:49 | 10/19/2025 19:22:40 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at HHR1M7494-G9-U9-L8-NL18-SBTS-VIP-HHR @ Generator_SG | 10/18/2025 20:25:16 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 20:25:08 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7494 | FLM_TE |  |  | PCM-20251019-00000904 | Alarm cleared. FLM need to check and close with RCA. | Alarm cleared. FLM need to check and close with RCA. |  |  |  | API | 10/19/2025 13:22:40 | 10/20/2025 13:30:31 | 10/20/2025 13:37:42 |  |  | 10/20/2025 13:37:49 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000610 | PCM-20251019-00001338 | TT-20251019-01462 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/19/2025 13:29:59 | 10/20/2025 15:45:24 | 10/19/2025 17:29:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/19/2025 13:29:18 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 13:29:15 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 13:29:59 | 10/20/2025 15:45:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000613 | PCM-20251019-00001342 | TT-20251019-01343 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 13:31:01 | 10/19/2025 13:31:01 | 10/19/2025 19:31:01 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/19/2025 12:38:41 | Major | 7114 | CELL SERVICE PROBLEM | 10/19/2025 12:38:32 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251019-00001235 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/19/2025 13:31:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000622 | PCM-20251019-00001363 | TT-20251019-01487 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/19/2025 13:42:24 | 10/20/2025 15:45:24 | 10/20/2025 01:42:24 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/19/2025 13:34:22 | Minor | 7115 | BASE STATION INFORMATION | 10/19/2025 13:34:18 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/19/2025 13:42:24 | 10/20/2025 15:45:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000625 | PCM-20251019-00001368 | TT-20251019-01491 | Telecom | Region_6 | RYAB0639 | RYAB0639 | Transsmission | MW_HW_fault | Remade Power Connector | Muhammad Afzal Muhammad Aslam | 10/19/2025 13:43:55 | 10/19/2025 14:55:31 | 10/20/2025 01:43:55 | ODU CPU / Cable Open at RYAB0639-2 on 10.89.220.243 @ Sceco | 10/19/2025 13:42:55 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/19/2025 13:27:02 | P2 | 2G | tathleeth | Sceco | TX NSA | RYAB0639 | FLM_TE | [8 empty] | API | 10/19/2025 13:43:55 | 10/19/2025 13:56:38 | 10/19/2025 14:41:24 | 10/19/2025 14:41:27 | 10/19/2025 14:41:29 | 10/19/2025 14:55:31 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000629 | PCM-20251019-00001378 | TT-20251019-01488 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 13:47:08 | 10/19/2025 13:47:08 | 10/20/2025 01:47:08 | BASE STATION ANTENNA LINE PROBLEM at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/19/2025 13:35:46 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 13:35:38 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0539 | FLM_TE |  |  | PCM-20251019-00001366 | Please check VSWR locally | Please check VSWR locally |  |  |  | API | 10/19/2025 13:47:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000631 | PCM-20251019-00001381 | TT-20251019-01279 | Reference_telecom | Region_4 | JED0947 | JED0947 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 13:49:12 | 10/20/2025 11:00:25 | 10/20/2025 01:49:12 | LossOfSignal observed in JED0947_03 towards 10.10.154.141 @ Sceco | 10/19/2025 00:14:32 | Minor |  | LossOfSignal | 10/19/2025 00:13:58 | P2 | 2G | jeddah | Sceco | TX NSA | JED0947 | FLM_TE |  |  | PCM-20251019-00001375 | please check with TT owner | please check with TT owner |  |  |  | API | 10/19/2025 13:49:12 | 10/20/2025 11:00:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000635 | PCM-20251019-00001388 | TT-20251019-01517 | Telecom | [7 empty] | 10/19/2025 13:54:16 | 10/19/2025 13:54:16 | 10/19/2025 19:54:16 | LAN_LOC at MUHAYIL-SEC0048_ELC1 @ Sceco | 10/19/2025 13:48:59 | Major | 1-12926 | LAN_LOC | 10/19/2025 13:48:51 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_TE | [5 empty] | 0-ELC(1-C)-7-T1SCC-6(EXT2/EXT2)-COM:1 |  |  | API | 10/19/2025 13:54:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000636 | PCM-20251019-00001387 | TT-20251019-01518 | Telecom | [7 empty] | 10/19/2025 13:54:17 | 10/19/2025 13:54:17 | 10/19/2025 19:54:17 | LAN_LOC at MUHAYIL-SEC0048_OCS1 @ Sceco | 10/19/2025 13:49:05 | Major | 1-12926 | LAN_LOC | 10/19/2025 13:48:55 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_TE | [5 empty] | 0-TO MHL0123(1-A)-8-T1SCC-6(EXT2/EXT2)-COM:1 |  |  | API | 10/19/2025 13:54:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000641 | PCM-20251019-00001413 | TT-20251019-01274 | Telecom | Region_6 | TBL1M8293 | TBL2293 |  |  |  | Saddam Hussain Shah Nawaz Khan | 10/19/2025 14:04:25 | 10/20/2025 16:28:27 | 10/20/2025 02:04:25 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8293-L800-CA-SBTS-P3 @ Sceco | 10/19/2025 12:10:08 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 09:48:07 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M8293 | FLM_TE |  |  | PCM-20251019-00001225 | Dear FLM team, kindly restore TBL9723 &BSA0450 | Dear FLM team, kindly restore TBL9723 &BSA0450 |  |  |  | API | 10/19/2025 14:04:25 | 10/20/2025 16:28:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000644 | PCM-20251019-00001425 | TT-20251019-01537 | Telecom | Region_4 | JED0619 | JED0619 |  |  |  | Anas Mohamedelamin Abbas Mustafa | 10/19/2025 14:09:27 | 10/19/2025 14:37:05 | 10/19/2025 18:09:27 | 3(2G) 1(LTE) 3(5G) sites down under JED2348-P3,JED0619-P1-HUB,JED0930-FWA-P1-VIP/JED0930-FWA-P1-VIP @ Sceco | 10/19/2025 13:59:26 | Critical | 7706 | BTS O&M LINK FAILURE | 10/19/2025 13:59:23 | P1 | 2G | jeddah | Generator_SG | 2G_LTE_5G SA | JED0619-P1-HUB 2G_LTE_5G,JED0930-FWA-P1-VIP 2G_5G,JED2348-P3 2G | FLM_EM | JED0619 | Dear team , Hub: JED0619 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251019-00001420 | Dear team , Hub: JED0619 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: JED0619 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/19/2025 14:09:27 | 10/19/2025 14:37:05 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000650 | PCM-20251019-00001436 | TT-20251019-01568 | Telecom | Region_1 | HFR2872 | HFR2872 | Equipment | SFP_BTS | Clean SFP | Muhammad Anwar Hussain Akhtar Hussain | 10/19/2025 14:12:51 | 10/19/2025 21:25:12 | 10/20/2025 02:12:51 | RF Unit CPRI Interface Error at HFR2872-P2_SRAN @ Sceco | 10/19/2025 14:07:28 | Minor | 26504 | RF Unit CPRI Interface Error | 10/19/2025 14:05:56 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR2872 | FLM_TE | [8 empty] | API | 10/19/2025 14:12:51 | 10/19/2025 15:35:12 | 10/19/2025 21:25:00 |  |  | 10/19/2025 21:25:12 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000653 | PCM-20251019-00001445 | TT-20251019-01564 | EM | Region_4 | HHR0447 | HHR0447 | Enviroment | Genset failure_AVR | Change Generator AVR | Hussein Sayed Salama Hussein | 10/19/2025 14:16:31 | 10/19/2025 15:33:51 | 10/19/2025 18:16:31 | 1(2G/LTE) sites down under HHR0447-P1-VIP-HHR/HHR0447-P1-VIP-HHR @ Generator_SG | 10/19/2025 14:08:24 | Critical | 7706 | BTS O&M LINK FAILURE | 10/19/2025 14:08:21 | VIP | 2G | jeddah | Generator_SG | 2G_LTE SA | HHR0447-P1-VIP-HHR | FLM_EM | HHR0447 | Results: DOWN SITE HUB HHR0447-P1-VIP-HHR HHR0447 Summary: Hub: HHR0447, Down Count: 1, Down Sites: HHR0447-P1-VIP-HHR Alarm Summary: HHR0447 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 14:16:31 | 10/19/2025 15:11:52 | 10/19/2025 15:11:55 | 10/19/2025 15:11:57 | 10/19/2025 15:11:59 | 10/19/2025 15:33:51 |  | Hussein Sayed Salama Hussein |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251019000657 | PCM-20251019-00001454 | TT-20251019-01586 | Telecom | Region_4 | JED1MN0755 | JED0755 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 14:19:34 | 10/19/2025 14:19:34 | 10/19/2025 18:19:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0755-NR2.6-P1-VIP @ Generator_SG | 10/19/2025 14:18:42 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 14:18:38 | VIP | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN0755 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 14:19:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251019000659 | PCM-20251019-00001459 | TT-20251019-01589 | Telecom | Region_1 | DAM2409 | DAM2409 |  |  |  | Meraj Husain Idd Baksh | 10/19/2025 14:21:08 | 10/19/2025 15:36:27 | 10/20/2025 02:21:08 | RF Unit Maintenance Link Failure at DAM2409-P2_SRAN @ Sceco | 10/19/2025 14:16:37 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/19/2025 14:15:50 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2409 | FLM_TE | [8 empty] | API | 10/19/2025 14:21:08 | 10/19/2025 15:25:08 | 10/19/2025 15:36:27 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000668 | PCM-20251019-00001475 | TT-20251019-01600 | EM | Region_6 | BLQ1M8192 | BLQ2192 |  |  |  | Muhammad Naeem Taj Din | 10/19/2025 14:24:44 | 10/19/2025 18:55:00 | 10/20/2025 02:24:44 | Tower light Alarm at BLQ1M8192-G9-L8- L18- L21-SBTS-P3 @ Generator_SG | 10/19/2025 14:17:32 | Minor | 7103 | Tower light Alarm | 10/19/2025 14:16:14 | P3 | 4G | namas | Generator_SG | LTE NSA | BLQ1M8192 | FLM_EM | [5 empty] | Tower light Alarm |  |  | API | 10/19/2025 14:24:44 | 10/19/2025 18:55:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000680 | PCM-20251019-00001497 | TT-20251019-01621 | EM | Region_4 | MUMA1M8198 | MUMA2198 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/19/2025 14:32:30 | 10/19/2025 14:33:18 | 10/20/2025 02:32:30 | TOWER LIGHT ALARM at MUMA1M8198-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/19/2025 14:24:29 | Minor | 7103 | TOWER LIGHT ALARM | 10/19/2025 14:24:24 | P3 | 4G | jeddah | Generator_SG | LTE NSA | MUMA1M8198 | FLM_EM | [5 empty] | TOWER LIGHT ALARM |  |  | API | 10/19/2025 14:32:30 | 10/19/2025 14:33:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000683 | PCM-20251019-00001501 | TT-20251019-00935 | Telecom | Region_2 | RIY2003 | RIY2003 | Equipment | BSS_HW_fault | Replace RCU | Touseef Iqbal Mazhar Iqbal | 10/19/2025 14:33:28 | 10/22/2025 15:13:39 | 10/19/2025 20:33:28 | BBU CPRI Interface Error at RIY2003-P3_SRAN @ Generator_SG | 10/19/2025 09:48:35 | Major | 26234 | BBU CPRI Interface Error | 10/19/2025 09:45:51 | P3 | SRAN | muzamiah | Generator_SG | 2G NSA | RIY2003 | FLM_TE |  |  | PCM-20251019-00001324 | 3G deleted ,please close TT | 3G deleted ,please close TT |  |  |  | API | 10/19/2025 14:33:28 | 10/19/2025 21:36:38 | 10/22/2025 15:13:07 | 10/22/2025 15:13:09 | 10/22/2025 15:13:12 | 10/22/2025 15:13:39 |  | Touseef Iqbal Mazhar Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000684 | PCM-20251019-00001504 | TT-20251019-01628 | Telecom | Region_2 | RIY0419 | RIY0419 | Equipment | BSS_HW_fault | Replace RFU | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/19/2025 14:36:38 | 10/19/2025 14:52:17 | 10/19/2025 20:36:38 | BBU CPRI Interface Error at RIY0419-P2_SRAN @ Sceco | 10/19/2025 14:33:51 | Major | 26234 | BBU CPRI Interface Error | 10/19/2025 14:31:19 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0419 | FLM_TE | [8 empty] | API | 10/19/2025 14:36:38 | 10/19/2025 14:49:47 | 10/19/2025 14:51:35 |  |  | 10/19/2025 14:52:17 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000686 | PCM-20251019-00001507 | TT-20251019-01630 | EM | [7 empty] | 10/19/2025 14:37:08 | 10/19/2025 14:37:08 | 10/20/2025 02:37:08 | RECTIFIER MAINS POWER FAILURE at JDJZ1M8181-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/19/2025 14:29:03 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/19/2025 14:28:51 | P3 | 4G |  | Generator_SG | LTE NSA | JDJZ1M8181 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/19/2025 14:37:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000687 | PCM-20251019-00001508 | TT-20251019-01631 | Telecom | Region_2 | RIY2M7419 | RIY0419 | Equipment | BSS_HW_fault | Replace RFU | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/19/2025 14:37:22 | 10/19/2025 14:57:21 | 10/19/2025 20:37:22 | Cell Unavailable at RIY2M7419-P2-L900-L800 @ Sceco | 10/19/2025 14:32:44 | Major | 29240 | Cell Unavailable | 10/19/2025 14:31:27 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7419 | FLM_TE | [8 empty] | API | 10/19/2025 14:37:22 | 10/19/2025 14:50:14 | 10/19/2025 14:56:51 |  |  | 10/19/2025 14:57:21 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000689 | PCM-20251019-00001513 | TT-20251019-01638 | EM | Region_2 | R2_BR1_HWBSC01 | BR1 |  |  |  | Mohamed HUSSIEN OMER HUSSIEN | 10/19/2025 14:39:43 | 10/19/2025 14:39:43 | 10/19/2025 18:39:43 | Air-Condition #2 FA(SH1) at R2_BR1_HWBSC01 @ Sceco_STB | 10/19/2025 14:39:11 | Critical | 65337 | Air-Condition #2 FA(SH1) | 10/19/2025 14:39:06 | P1 | BSC | buraidah | Sceco_STB | 2G NSA | R2_BR1_HWBSC01 | FLM_EM | [8 empty] | API | 10/19/2025 14:39:43 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000690 | PCM-20251019-00001514 | TT-20251019-01625 | Telecom | Region_6 | BRQ0084 | BRQ0084 | Equipment | BTS_Cable | Replace CPRI Cable | Muhammad Jamal Khan Abbas Ali | 10/19/2025 14:40:32 | 10/19/2025 15:50:29 | 10/19/2025 20:40:32 | 1(2G) sites down under BRQ0084-P2-WBB-G3/BRQ0084-P2-WBB-G3 @ Sceco | 10/19/2025 14:32:23 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 14:32:20 | P2 | 2G | mohail | Sceco | 2G SA | BRQ0084-P2-WBB-G3 | FLM_TE | BRQ0084 | Results: DOWN SITE HUB BRQ0084-P2-WBB-G3 BRQ0084 Summary: Hub: BRQ0084, Down Count: 1, Down Sites: BRQ0084-P2-WBB-G3 Alarm Summary: BRQ0084 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 14:40:32 | 10/19/2025 15:23:35 | 10/19/2025 15:49:59 |  |  | 10/19/2025 15:50:29 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000692 | PCM-20251019-00001522 | TT-20251019-01651 | Telecom | [7 empty] | 10/19/2025 14:45:55 | 10/19/2025 14:45:55 | 10/19/2025 20:45:55 | LAN_LOC at MUHAYIL-SEC0048_OCS2 @ Sceco | 10/19/2025 14:40:38 | Major | 1-12926 | LAN_LOC | 10/19/2025 14:40:28 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_TE | [5 empty] | 0-TO JDJZ0781(1-B)-8-T1SCC-6(EXT2/EXT2)-COM:1 |  |  | API | 10/19/2025 14:45:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000700 | PCM-20251019-00001535 | TT-20251019-01665 | Telecom | Region_6 | SDA0425 | SDA0425 | Transsmission | MW_HW_fault | Replace IF Board/Modem Card | Muhammad Jamshaid Muhammad Ashraf | 10/19/2025 14:54:41 | 10/19/2025 15:24:37 | 10/20/2025 02:54:41 | ODU CPU / Cable Open at SDA0425_4 on 10.154.163.203 @ Sceco | 10/19/2025 14:53:37 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/19/2025 14:51:27 | P3 | 2G | abha | Sceco | TX NSA | SDA0425 | FLM_TE | [8 empty] | API | 10/19/2025 14:54:41 | 10/19/2025 15:24:01 | 10/19/2025 15:24:21 |  |  | 10/19/2025 15:24:37 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000703 | PCM-20251019-00001541 | TT-20251019-01673 | Telecom | Region_4 | JED0930 | JED0930 | Equipment | BSS_HW_fault | Replace RF Module | Nazeer Mohammed | 10/19/2025 14:59:21 | 10/22/2025 10:27:40 | 10/19/2025 20:59:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0930-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/19/2025 14:58:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 14:58:13 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0930 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 14:59:21 | 10/20/2025 13:30:31 | 10/21/2025 11:22:44 | 10/21/2025 11:22:47 | 10/21/2025 11:22:49 | 10/22/2025 10:27:40 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000705 | PCM-20251019-00001545 | TT-20251019-01675 | EM | [7 empty] | 10/19/2025 15:00:54 | 10/19/2025 15:00:54 | 10/20/2025 03:00:54 | SHELTER DOOR OPEN at TFBH1M8218-G9-L8-L18-L21-SBTS-P3-CAP @ Sceco | 10/19/2025 15:00:28 | Minor | 7103 | SHELTER DOOR OPEN | 10/19/2025 15:00:17 | P2 | 4G |  | Sceco | LTE NSA | TFBH1M8218 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/19/2025 15:00:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000709 | PCM-20251019-00001549 | TT-20251019-01682 | Reference_telecom | Region_4 | HAW1M4360 | HAW2360 |  |  |  | Rashid Shafique | 10/19/2025 15:04:00 | 10/19/2025 15:36:20 | 10/20/2025 03:04:00 | BASE STATION NOTIFICATION (Fan failure) at HAW1M4360-P2 @ Sceco | 10/19/2025 14:34:06 | Minor | 7652 | BASE STATION NOTIFICATION | 10/19/2025 14:33:46 | P2 | 3G | taif | Sceco | 3G NSA | HAW1M4360 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/19/2025 15:04:00 | 10/19/2025 15:36:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000716 | PCM-20251019-00001570 | TT-20251019-01701 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/19/2025 15:15:07 | 10/19/2025 15:42:43 | 10/20/2025 03:15:07 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/19/2025 15:04:48 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 15:04:42 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251019-00001565 | Please check VSWR locally | Please check VSWR locally |  |  |  | API | 10/19/2025 15:15:07 | 10/19/2025 15:42:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000729 | PCM-20251019-00001609 | TT-20251019-01735 | EM | Region_6 | MKW2051 | MKW2051 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/19/2025 15:29:10 | 10/23/2025 13:53:28 | 10/19/2025 21:29:10 | 3(2G) 3(LTE) sites down under BHAB2053,BHAB2023,MKW2051-P3/MKW2051-P3 @ Generator_SG | 10/19/2025 15:20:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 15:20:44 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | MKW2051-P3 | FLM_EM | MKW2051 | Results: DOWN SITE HUB MKW2051-P3 MKW2051 Summary: Hub: MKW2051, Down Count: 1, Down Sites: MKW2051-P3 Alarm Summary: MKW2051 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/19/2025 15:29:10 | 10/20/2025 10:21:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000732 | PCM-20251019-00001612 | TT-20251019-01737 | EM | Region_1 | RSK2M2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/19/2025 15:29:33 | 10/19/2025 16:03:37 | 10/19/2025 21:29:33 | 1(2G/3G/LTE) sites down under RSK2086-P2/R1_JB_HWBSC01 @ Sceco | 10/19/2025 15:22:49 | Major | 21825 | CSL Fault | 10/19/2025 15:22:46 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | RSK2086-P2 | FLM_EM | RSK2086 | Results: DOWN SITE HUB RSK2086-P2 RSK2086 Summary: Hub: RSK2086, Down Count: 1, Down Sites: RSK2086-P2 Alarm Summary: RSK2086 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 15:29:33 | 10/19/2025 16:03:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000738 | PCM-20251019-00001625 | TT-20251019-01767 | EM | Region_4 | BHMF1M8137 | BHMF2137 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/19/2025 15:34:28 | 10/19/2025 16:17:14 | 10/20/2025 03:34:28 | COMMERCIAL POWER FAILURE at BHMF1M8137-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/19/2025 15:26:09 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/19/2025 15:26:04 | P3 | 4G | jeddah | Generator_SG | LTE NSA | BHMF1M8137 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/19/2025 15:34:28 | 10/19/2025 16:17:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000748 | PCM-20251019-00001655 | TT-20250907-01714 | MW_HC | Region_3 | AHT2057 | AHT2057 |  |  |  | Mohamed Naveed | 10/19/2025 15:43:39 | 10/19/2025 18:23:03 | 10/20/2025 03:43:39 | Huawei MW HC_P2 Observing Errors at AHT2057-AHT0972 | 09/07/2025 17:02:01 | Minor |  | LOF | 09/07/2025 17:02:01 | P3 | SRAN | hail | Sceco | TX NSA | AHT2057-AHT0972 | FLM_TE | AHT2057 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251019-00001651 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/19/2025 15:43:39 | 10/19/2025 18:23:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000750 | PCM-20251019-00001657 | TT-20251012-01995 | MW_HC | Region_3 | HAL0966 | HAL0966 |  |  |  | Mohamed Naveed | 10/19/2025 15:44:16 | 10/19/2025 18:23:04 | 10/20/2025 03:44:16 | Huawei MW HC_P2 Observing Errors at HAL0966-HAL0957 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P1 | SRAN | hail | Sceco_STB | TX NSA | HAL0966-HAL0957 | FLM_TE | HAL0966 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251019-00001653 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/19/2025 15:44:16 | 10/19/2025 18:23:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000752 | PCM-20251019-00001669 | TT-20251019-01813 | Telecom | Region_6 | BAH0017 | BAH0017 | Transsmission | MW_HW_fault | Remade Power Connector | SHAH KHALID | 10/19/2025 15:53:03 | 10/20/2025 18:00:36 | 10/20/2025 03:53:03 | ODU CPU / Cable Open at BAH0017-BAH0004 on 10.154.175.100 @ Sceco | 10/19/2025 15:52:25 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/19/2025 15:36:35 | P1 | 2G | Albaha | Sceco | TX NSA | BAH0017 | FLM_TE | [8 empty] | API | 10/19/2025 15:53:03 | 10/19/2025 16:52:56 | 10/20/2025 17:59:33 |  |  | 10/20/2025 18:00:36 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000754 | PCM-20251019-00001673 | TT-20251017-01313 | Telecom | Region_4 | JED0052 | JED0052 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 15:55:07 | 10/20/2025 11:00:26 | 10/20/2025 03:55:07 | AS BO Requested : Thanks to check JED0132-JED0052 | 10/17/2025 18:48:21 | Minor | 113388 | LOF | 10/17/2025 18:48:21 | P1 | 2G | jeddah | Sceco | TX NSA | JED0132-JED0052 | FLM_TE |  |  | PCM-20251018-00001186 | Dear FLM team, kindly check JED0132 down many times yesterday and today | Dear FLM team, kindly check JED0132 down many times yesterday and today |  |  |  | API | 10/19/2025 15:55:07 | 10/20/2025 11:00:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000758 | PCM-20251019-00001681 | TT-20251019-01797 | Reference_telecom | Region_4 | UKZ1M3071 | UKZ0071 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 15:58:42 | 10/19/2025 23:10:32 | 10/19/2025 21:58:42 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at UKZ1M3071-P2-USF @ Generator_SG | 10/19/2025 15:17:13 | Major | 7771 | WCDMA CELL OUT OF USE | 10/19/2025 15:15:04 | P2 | 3G | adam | Generator_SG | 3G SA | UKZ1M3071 | FLM_TE |  |  | PCM-20251019-00001658 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/19/2025 15:58:42 | 10/19/2025 23:01:41 | 10/19/2025 23:10:12 |  |  | 10/19/2025 23:10:32 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000763 | PCM-20251019-00001687 | TT-20251019-01720 | Telecom | Region_4 | UKZ1M7071 | UKZ0071 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 16:00:57 | 10/19/2025 23:11:09 | 10/19/2025 22:00:57 | CELL FAULTY (Failure in optical interface) at UKZ1M7071-USF-P3 @ Generator_SG | 10/19/2025 15:15:56 | Major | 7653 | CELL FAULTY | 10/19/2025 15:15:48 | P2 | 4G | adam | Generator_SG | LTE_Cell SA | UKZ1M7071 | FLM_TE |  |  | PCM-20251019-00001583 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/19/2025 16:00:57 | 10/19/2025 23:01:43 | 10/19/2025 23:10:46 |  |  | 10/19/2025 23:11:09 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000766 | PCM-20251019-00001690 | TT-20251019-01832 | Telecom | Region_4 | JED2127 | JED2127 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/19/2025 16:04:57 | 10/21/2025 17:12:49 | 10/19/2025 22:04:57 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2127-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/19/2025 16:03:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 16:03:43 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2127 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 16:04:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000772 | PCM-20251019-00001699 | TT-20251019-01660 | Telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/19/2025 16:06:43 | 10/19/2025 17:22:56 | 10/20/2025 04:06:43 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/19/2025 14:46:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 14:45:55 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251019-00001532 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/19/2025 16:06:43 | 10/19/2025 17:22:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000776 | PCM-20251019-00001712 | TT-20251019-01850 | EM | Region_6 | BHAB1M8041 | BHAB2041 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/19/2025 16:10:38 | 10/20/2025 10:21:08 | 10/20/2025 04:10:38 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at BHAB1M8041-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/19/2025 16:02:29 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/19/2025 16:02:24 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8041 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/19/2025 16:10:38 | 10/20/2025 10:21:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000778 | PCM-20251019-00001722 | TT-20251019-01860 | Reference_telecom | Region_4 | JDJZ0769 | JDJZ0769 |  |  |  | Riasat Ali Allah Baksh | 10/19/2025 16:17:21 | 10/20/2025 21:24:39 | 10/20/2025 04:17:21 | LossOfSignal observed in JDJZ0769_01 towards 10.74.121.130 @ Sceco_STB | 10/19/2025 04:17:12 | Minor |  | LossOfSignal | 10/19/2025 04:17:07 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0769 | FLM_TE | [8 empty] | API | 10/19/2025 16:17:21 | 10/20/2025 21:24:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000780 | PCM-20251019-00001726 | TT-20251012-01967 | MW_HC | Region_3 | SML2332 | SML2332 |  |  |  | Mohamed Naveed | 10/19/2025 16:19:48 | 10/19/2025 18:23:04 | 10/20/2025 04:19:48 | Huawei MW HC_P2 Observing Errors at SML2332-RUSF9023 | 10/12/2025 17:58:16 | Minor |  | LOF | 10/12/2025 17:58:16 | P3 | SRAN | hail | Generator_SG | TX NSA | SML2332-RUSF9023 | FLM_TE | SML2332 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | PCM-20251019-00001725 | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. | Dear FLM, As per our new process to close PCMs need required data : 1- Action duration ( Start & END ) 2- Clearance Evidence duration 3- 1 h Clearance Snapshot 4- RCA to close with it. |  |  |  | API | 10/19/2025 16:19:48 | 10/19/2025 18:23:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251019000781 | PCM-20251019-00001728 | TT-20251019-01849 | Reference_telecom | [7 empty] | 10/19/2025 16:20:08 | 10/19/2025 16:20:08 | 10/20/2025 04:20:08 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at TBL1M8284-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/19/2025 14:19:16 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 14:10:22 | P3 | 4G |  | Generator_SG | LTE NSA | TBL1M8284 | FLM_TE |  | site was down and restored ,kindly check | PCM-20251019-00001717 | site was down and restored ,kindly check | site was down and restored ,kindly check |  |  |  | API | 10/19/2025 16:20:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000786 | PCM-20251019-00001750 | TT-20251019-01898 | Telecom | Region_4 | JED1MN0014 | JED0014 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 16:29:18 | 10/19/2025 16:29:18 | 10/19/2025 22:29:18 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0014-NR2.6-P2 @ Sceco | 10/19/2025 16:28:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 16:28:14 | P1 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0014 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 16:29:18 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000787 | PCM-20251019-00001755 | TT-20251019-01902 | Telecom | Region_6 | BHAB1M7903 | BHAB0903 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/19/2025 16:31:04 | 10/21/2025 17:12:49 | 10/19/2025 22:31:04 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at BHAB1M7903-L800-P3-SBTS @ Sceco | 10/19/2025 16:24:57 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 16:24:46 | P3 | 4G | abha | Sceco | 5G_Cell SA | BHAB1M7903 | FLM_TE |  |  | PCM-20251019-00001754 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/19/2025 16:31:04 | 10/19/2025 23:48:40 | 10/20/2025 01:36:25 |  |  | 10/20/2025 01:36:33 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000790 | PCM-20251019-00001760 | TT-20251019-01906 | EM | Region_6 | BSA9004 | BSA9004 |  |  |  | Asad Saddiq | 10/19/2025 16:32:09 | 10/20/2025 01:01:21 | 10/19/2025 20:32:09 | NEC observing Rectifier Main Fail at BSA9004 | 10/19/2025 16:26:16 | Critical | Fire alarm Shelter 1 (Input-3) | Fire alarm Shelter 1 (Input-3) | 10/19/2025 16:26:16 | P3 | Repeater | bisha | Sceco | TX NSA | BSA9004 | FLM_EM | [5 empty] | NEC observing Rectifier Main Fail at BSA9004 |  |  | API | 10/19/2025 16:32:09 | 10/20/2025 01:01:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000794 | PCM-20251019-00001768 | TT-20251019-00987 | Reference_telecom | Region_6 | TLT1M7367 | TLT0367 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/19/2025 16:33:08 | 10/19/2025 17:17:36 | 10/20/2025 04:33:08 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TLT1M7367-P2-NCA-L800-SBTS @ Generator_SG | 10/19/2025 08:21:48 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 08:19:07 | P2 | 4G | tathleeth | Generator_SG | LTE NSA | TLT1M7367 | FLM_TE |  |  | PCM-20251019-00000895 | Alarm Cleared. FLM need to check and close with RCA. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/19/2025 16:33:08 | 10/19/2025 16:48:54 | 10/19/2025 17:17:29 |  |  | 10/19/2025 17:17:36 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000796 | PCM-20251019-00001773 | TT-20251018-01633 | Reference_telecom | Region_6 | NMS0094 | NMS0094 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 16:35:23 | 10/19/2025 23:06:18 | 10/20/2025 04:35:23 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NMS0094-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco_STB | 10/18/2025 15:40:20 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 15:22:17 | P2 | 2G | namas | Sceco_STB | 2G NSA | NMS0094 | FLM_TE |  |  | PCM-20251019-00000967 | Alarm Cleared. Please check and close with RCA. | Alarm Cleared. Please check and close with RCA. |  |  |  | API | 10/19/2025 16:35:23 | 10/19/2025 19:05:58 | 10/19/2025 23:05:44 |  |  | 10/19/2025 23:06:18 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000797 | PCM-20251019-00001782 | TT-20251018-01684 | Telecom | Region_6 | ABBS1M8177 | ABBS2177 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 16:36:57 | 10/19/2025 23:05:10 | 10/19/2025 22:36:57 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at ABBS1M8177-G9-L8-L18-L21-SBTS @ Generator_SG | 10/18/2025 17:48:36 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/18/2025 03:01:40 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8177 | FLM_TE |  |  | PCM-20251019-00001037 | Alarm cleared. FLM need to check and close with RCA. | Alarm cleared. FLM need to check and close with RCA. |  |  |  | API | 10/19/2025 16:36:57 | 10/19/2025 19:05:59 | 10/19/2025 23:04:42 |  |  | 10/19/2025 23:05:10 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000798 | PCM-20251019-00001785 | TT-20251019-01858 | Telecom | Region_4 | JED1M7434 | JED0434 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 16:38:07 | 10/20/2025 16:09:49 | 10/19/2025 22:38:07 | CELL OPERATION DEGRADED (Antenna Line Device failure) at JED1M7434-CA @ Generator_SG | 10/19/2025 16:07:52 | Major | 7654 | CELL OPERATION DEGRADED | 10/19/2025 16:07:42 | P2 | 4G | jeddah | Generator_SG | LTE_Cell SA | JED1M7434 | FLM_TE |  |  | PCM-20251019-00001720 | FLM need to check ALD and close with RCA. | FLM need to check ALD and close with RCA. |  |  |  | API | 10/19/2025 16:38:07 | 10/20/2025 16:09:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000803 | PCM-20251019-00001809 | TT-20251019-01938 | Telecom | Region_4 | BHR1M7332 | BHR0332 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/19/2025 16:43:56 | 10/19/2025 17:22:57 | 10/20/2025 04:43:56 | PT::FLM need to check BASE STATION SERVICE PROBLEM (FSP overheating) flapping at BHR1M7332-P3-L800-CA | 10/19/2025 16:43:47 | Minor | 676767671 | Health Check-WO to TE FME | 10/19/2025 16:43:47 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | BHR1M7332-P3-L800-CA | FLM_TE | [8 empty] | API | 10/19/2025 16:43:56 | 10/19/2025 17:22:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000811 | PCM-20251019-00001834 | TT-20251019-01925 | Telecom | Region_4 | HJR2233 | HJR2233 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/19/2025 16:52:08 | 10/20/2025 14:35:52 | 10/19/2025 22:52:08 | 1(2G) 2(5G) sites down under JED0313-NR3.5-P2,HJR2233-P3/HJR2233-P3 @ Generator_SG | 10/19/2025 16:35:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 16:34:57 | P3 | 2G | jeddah | Generator_SG | 2G_5G SA | JED0313-NR3.5-P2 5G,HJR2233-P3 2G | FLM_EM | HJR2233 | DOWN SITE HUB TX FB JED0313 JED0313 LOS to Air Scale HJR2233 HJR2233 Suspected Power issue at HUB | PCM-20251019-00001808 | DOWN SITE HUB TX FB JED0313 JED0313 LOS to Air Scale HJR2233 HJR2233 Suspected Power issue at HUB | DOWN SITE HUB TX FB JED0313 JED0313 LOS to Air Scale HJR2233 HJR2233 Suspected Power issue at HUB |  | sites down |  | API | 10/19/2025 16:52:08 | 10/20/2025 14:35:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000819 | PCM-20251019-00001851 | TT-20251019-01962 | Telecom | Region_2 | RIY2C8003 | RIY2003 | Equipment | BSS_HW_fault | Replace RCU | Touseef Iqbal Mazhar Iqbal | 10/19/2025 16:59:15 | 10/22/2025 15:12:59 | 10/20/2025 04:59:15 | Cell Capability Degraded at RIY2C8003-P3 @ Generator_SG | 10/19/2025 16:47:00 | Minor | 29243 | Cell Capability Degraded | 10/19/2025 16:45:43 | P3 | 4G | muzamiah | Generator_SG | 2G NSA | RIY2C8003 | FLM_TE |  |  | PCM-20251019-00001837 | Dear FLM, Need to check locally | Dear FLM, Need to check locally |  |  |  | API | 10/19/2025 16:59:15 | 10/19/2025 21:36:39 | 10/22/2025 15:10:58 | 10/22/2025 15:11:00 | 10/22/2025 15:11:03 | 10/22/2025 15:12:59 |  | Touseef Iqbal Mazhar Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019000826 | PCM-20251019-00001868 | TT-20251019-01946 | Reference_telecom | Region_4 | JED1MN0218 | JED0218 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 17:03:57 | 10/19/2025 17:03:57 | 10/20/2025 05:03:57 | Fronthaul loop back connectivity check failure at JED1MN0218-NR2.6-P1-VIP @ Sceco | 10/19/2025 16:18:10 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/19/2025 16:17:59 | VIP | 5G | jeddah | Sceco | 5G NSA | JED1MN0218 | FLM_TE |  |  | PCM-20251019-00001823 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/19/2025 17:03:57 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000844 | PCM-20251019-00001914 | TT-20251019-02046 | Reference_telecom | Region_1 | HFS2M3068 | HFS0068 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/19/2025 17:29:10 | 10/21/2025 05:43:46 | 10/20/2025 05:29:10 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M3068-P3 @ Generator_SG | 10/19/2025 14:29:07 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/19/2025 14:29:02 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M3068 | FLM_TE | [8 empty] | API | 10/19/2025 17:29:10 | 10/21/2025 05:43:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251019000849 | PCM-20251019-00001923 | TT-20251019-02056 | Telecom | Region_4 | JED1M7244 | JED0244 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 17:34:20 | 10/20/2025 16:15:40 | 10/19/2025 23:34:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7244-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/19/2025 17:33:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 17:33:08 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7244 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 17:34:20 | 10/20/2025 16:09:50 | 10/20/2025 16:15:37 | 10/20/2025 16:15:40 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000855 | PCM-20251019-00001936 | TT-20251019-02070 | MW_HC | Region_4 | TFBH0890 | TFBH0890 |  |  |  | Ahmad Kamal Abdelmawla | 10/19/2025 17:41:13 | 10/19/2025 20:55:05 | 10/20/2025 05:41:13 | NEC MW HC_P0 Observing Modem Down at TFBH0890(10.154.143.74)--TFBH0893(10.154.143.66) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | taif | Sceco_STB | TX NSA | TFBH0890(10.154.143.74)--TFBH0893(10.154.143.66) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:13 | 10/19/2025 20:55:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000856 | PCM-20251019-00001937 | TT-20251019-02071 | MW_HC | Region_4 | SIR0172 | SIR0172 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 17:41:15 | 10/19/2025 23:01:51 | 10/20/2025 05:41:15 | NEC MW HC_P0 Observing Modem Down at SIR0172(10.88.221.243)--SIR0197(10.88.221.249) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | adam | Generator_SG | TX NSA | SIR0172(10.88.221.243)--SIR0197(10.88.221.249) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:15 | 10/19/2025 23:01:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000857 | PCM-20251019-00001938 | TT-20251019-02072 | MW_HC | Region_4 | RYMK0664 | RYMK0664 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/19/2025 17:41:16 | 10/20/2025 19:42:51 | 10/20/2025 05:41:16 | NEC MW HC_P0 Observing Modem Down at RYMK0664(10.154.118.71)--RYMK0671(10.154.118.76) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | taif | Generator_DG | TX NSA | RYMK0664(10.154.118.71)--RYMK0671(10.154.118.76) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:16 | 10/20/2025 19:42:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000859 | PCM-20251019-00001940 | TT-20251019-02074 | MW_HC | Region_4 | RYMK0549 | RYMK0549 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/19/2025 17:41:19 | 10/20/2025 19:42:52 | 10/20/2025 05:41:19 | NEC MW HC_P0 Observing Performance Issue at RYMK0549(10.154.118.162)--TAF0170(10.154.118.161) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | taif | Generator_SG | TX NSA | RYMK0549(10.154.118.162)--TAF0170(10.154.118.161) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:19 | 10/20/2025 19:42:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000860 | PCM-20251019-00001941 | TT-20251019-02075 | MW_HC | Region_4 | NNL0100 | NNL0100 |  |  |  | Riasat Ali Allah Baksh | 10/19/2025 17:41:20 | 10/20/2025 21:24:40 | 10/20/2025 05:41:20 | NEC MW HC_P0 Observing Performance Issue at NNL0100(10.88.223.52)--NNL0146(10.88.223.53) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | alaith | Generator_SG | TX NSA | NNL0100(10.88.223.52)--NNL0146(10.88.223.53) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:20 | 10/20/2025 21:24:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000861 | PCM-20251019-00001942 | TT-20251019-02077 | MW_HC | Region_5 | MKTF0831 | MKTF0831 |  |  |  | Husain Hassan Ishag Omer | 10/19/2025 17:41:21 | 10/19/2025 18:00:31 | 10/20/2025 05:41:21 | NEC MW HC_P0 Observing RSL Issue at MKTF0831(10.154.126.151)--SHD0142(10.154.126.152) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | makkah | Generator_SG | TX NSA | MKTF0831(10.154.126.151)--SHD0142(10.154.126.152) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:21 | 10/19/2025 18:00:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000862 | PCM-20251019-00001943 | TT-20251019-02078 | MW_HC | Region_5 | MKJD0569 | MKJD0569 |  |  |  | Amjad Ali Muhammad Parves | 10/19/2025 17:41:22 | 10/19/2025 18:53:53 | 10/20/2025 05:41:22 | NEC MW HC_P0 Observing Modem Down at MKJD0569(10.99.249.65)--MKJD0651(10.99.249.66) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | makkah | Sceco_STB | TX NSA | MKJD0569(10.99.249.65)--MKJD0651(10.99.249.66) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:22 | 10/19/2025 18:53:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000863 | PCM-20251019-00001944 | TT-20251019-02079 | MW_HC | Region_4 | JED0400 | JED0400 |  |  |  | Mohammed Ramadan A Abu Abid | 10/19/2025 17:41:23 | 10/19/2025 19:33:14 | 10/20/2025 05:41:23 | NEC MW HC_P2 Observing Modem Down at JED0400(10.1.165.169)--JED6035(10.1.165.170) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | jeddah | Sceco | TX NSA | JED0400(10.1.165.169)--JED6035(10.1.165.170) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:23 | 10/19/2025 19:33:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000864 | PCM-20251019-00001945 | TT-20251019-02080 | MW_HC | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/19/2025 17:41:24 | 10/19/2025 19:33:15 | 10/20/2025 05:41:24 | NEC MW HC_P0 VIP Observing Modem Down at JED0110(10.1.165.89)--JED6101(10.1.165.90) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | VIP | 2G | jeddah | Sceco | TX NSA | JED0110(10.1.165.89)--JED6101(10.1.165.90) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:24 | 10/19/2025 19:33:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000865 | PCM-20251019-00001946 | TT-20251019-02081 | MW_HC | Region_4 | JED0049 | JED0049 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 17:41:25 | 10/20/2025 11:00:26 | 10/20/2025 05:41:25 | NEC MW HC_P0 Observing Modem Down at JED0049(10.99.249.244)--JED0052(10.99.249.243) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | jeddah | Sceco | TX NSA | JED0049(10.99.249.244)--JED0052(10.99.249.243) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:25 | 10/20/2025 11:00:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251017000690 | PCM-20251017-00001116 | TT-20251017-01131 | EM | Region_6 | BHAB0823 | BHAB0823 |  |  |  | Sohail Nasir Mir Afzal | 10/17/2025 16:10:26 | 10/19/2025 05:52:20 | 10/18/2025 04:10:26 | SHELTER DOOR OPEN at BHAB1M7823-G9-L8-L18-SBTSP2-USF @ Generator_SG | 10/17/2025 16:09:50 | Minor | 7103 | SHELTER DOOR OPEN | 10/17/2025 16:09:45 | P3 | 4G | makhwa | Generator_SG | LTE NSA | BHAB1M7823 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/17/2025 16:10:26 | 10/19/2025 05:52:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000728 | PCM-20251017-00001190 | TT-20251017-01215 | EM | Region_4 | JED0804 | JED0804 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/17/2025 17:28:25 | 10/18/2025 12:13:26 | 10/18/2025 05:28:25 | RECTIFIER MODULE FAILURE at JED1M7804-CA-L900-L800-SBTS @ Sceco | 10/17/2025 17:20:49 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/17/2025 17:19:52 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7804 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/17/2025 17:28:25 | 10/18/2025 12:13:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000788 | PCM-20251017-00001287 | TT-20251017-01312 | EM | Region_6 | ABH2166 | ABH2166 |  |  |  | Khalid Frahan Almesetef | 10/17/2025 18:48:26 | 10/18/2025 02:59:57 | 10/18/2025 06:48:26 | AIRCON 2 FAILURE at ABH2166-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/17/2025 18:40:13 | Minor | 7103 | AIRCON 2 FAILURE | 10/17/2025 18:40:04 | P3 | 2G | abha | Sceco | 2G NSA | ABH2166 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/17/2025 18:48:26 | 10/18/2025 02:59:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000793 | PCM-20251017-00001292 | TT-20251017-01314 | EM | Region_4 | JED0236 | JED0236 |  |  |  | Ahmed Gamal Mohamed Farag | 10/17/2025 18:53:36 | 10/18/2025 00:16:55 | 10/18/2025 06:53:36 | RECTIFIER MODULE FAILURE at JED1M7236-P2-CA-L900-L800-SBTS @ Sceco | 10/17/2025 18:46:13 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/17/2025 18:44:56 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7236 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/17/2025 18:53:36 | 10/18/2025 00:16:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251017000933 | PCM-20251017-00001510 | TT-20251017-01501 | EM | Region_4 | JED2153 | JED2153 | Enviroment | Rectifier Module | Change rectifer module | Amr Sherif Gabber Ahmed | 10/17/2025 22:38:21 | 10/19/2025 20:52:28 | 10/18/2025 04:38:21 | BATTERY DISCHARGE at JED2153-G9-L8-L18-L21-NR2.6-FWA-P1-VIP @ Generator_SG | 10/17/2025 22:29:53 | Major | 7103 | BATTERY DISCHARGE | 10/17/2025 22:29:43 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2153 | FLM_EM | [5 empty] | BATTERY DISCHARGE |  |  | API | 10/17/2025 22:38:21 | 10/18/2025 19:13:20 | 10/19/2025 20:52:21 |  |  | 10/19/2025 20:52:28 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251017000964 | PCM-20251017-00001556 | TT-20251017-01548 | EM | Region_1 | DAM0377 | DAM0377 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/17/2025 23:41:50 | 10/18/2025 11:08:27 | 10/18/2025 11:41:50 | DC power fail at DAM0377-P2_SRAN @ Sceco | 10/17/2025 23:33:33 | Minor | 65106 | DC power fail | 10/17/2025 23:31:03 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0377 | FLM_EM | [8 empty] | API | 10/17/2025 23:41:50 | 10/18/2025 11:08:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000036 | PCM-20251018-00000066 | TT-20251018-00072 | EM | Region_4 | JED0416 | JED0416 | Enviroment | SCECO_Failure | SCECO auto restored | Amer Attallah Awadallah | 10/18/2025 01:10:46 | 10/18/2025 05:33:45 | 10/18/2025 13:10:46 | COMMERCIAL POWER FAILURE at JED1M7416-CA-L900-L800-SBTS @ Sceco | 10/18/2025 01:02:29 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/18/2025 01:02:21 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7416 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/18/2025 01:10:46 | 10/18/2025 01:12:54 | 10/18/2025 01:14:50 | 10/18/2025 01:14:52 | 10/18/2025 01:27:32 | 10/18/2025 05:33:45 |  | Amer Attallah Awadallah |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000171 | PCM-20251018-00000293 | TT-20251018-00332 | EM | Region_4 | HAW2414 | HAW2414 | Enviroment | SCECO_Failure | SCECO auto restored | Waheed Ullah Said Haleem | 10/18/2025 05:19:11 | 10/22/2025 11:05:58 | 10/18/2025 17:19:11 | RECTIFIER MODULE FAILURE at HAW1M8414-G9-L18-SBTS-P2 @ Generator_SG | 10/18/2025 05:10:54 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/18/2025 05:10:42 | P2 | 4G | taif | Generator_SG | LTE NSA | HAW1M8414 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/18/2025 05:19:11 | 10/18/2025 18:36:22 | 10/22/2025 11:05:47 |  |  | 10/22/2025 11:05:58 |  | Waheed Ullah Said Haleem |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000259 | PCM-20251018-00000439 | TT-20251018-00477 | EM | Region_4 | HJR0142 | HJR0142 |  |  |  | Ibrahim Fawzy Mohamed Elbers | 10/18/2025 07:19:01 | 10/21/2025 23:26:13 | 10/18/2025 19:19:01 | SHELTER DOOR OPEN at HJR0142-GSM-UMTS-P2-USF @ Generator_SG | 10/18/2025 07:18:19 | Minor | 7103 | SHELTER DOOR OPEN | 10/18/2025 07:17:44 | P2 | 2G | adam | Generator_SG | 2G NSA | HJR0142 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/18/2025 07:19:01 | 10/21/2025 23:26:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000264 | PCM-20251018-00000447 | TT-20251018-00486 | EM | Region_4 | HJR0142 | HJR0142 |  |  |  | Ibrahim Fawzy Mohamed Elbers | 10/18/2025 07:26:16 | 10/21/2025 23:26:15 | 10/18/2025 19:26:16 | RECTIFIER MODULE FAILURE at HJR0142-GSM-UMTS-P2-USF @ Generator_SG | 10/18/2025 07:18:19 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/18/2025 07:17:44 | P2 | 2G | adam | Generator_SG | 2G NSA | HJR0142 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/18/2025 07:26:16 | 10/21/2025 23:26:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000327 | PCM-20251018-00000564 | TT-20251018-00609 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/18/2025 08:49:26 | 10/18/2025 11:17:36 | 10/18/2025 14:49:26 | high temprature 32 at RIY0232-P1_SRAN @ Sceco | 10/18/2025 08:39:03 | Major | 65102 | high temprature 32 | 10/18/2025 08:39:01 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/18/2025 08:49:26 | 10/18/2025 11:17:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000501 | PCM-20251018-00000889 | TT-20251018-00892 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/18/2025 11:13:31 | 10/18/2025 11:31:05 | 10/18/2025 23:13:31 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/18/2025 11:07:05 | Minor | 40564 | Genset Fault | 10/18/2025 11:07:05 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/18/2025 11:13:31 | 10/18/2025 11:30:42 | 10/18/2025 11:30:55 |  |  | 10/18/2025 11:31:05 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251018000502 | PCM-20251018-00000890 | TT-20251018-00893 | EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/18/2025 11:14:06 | 10/22/2025 17:49:41 | 10/18/2025 23:14:06 | high temprature 32 at RIY0447-P2_SRAN @ Sceco | 10/18/2025 11:05:02 | Minor | 65102 | high temprature 32 | 10/18/2025 11:03:35 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/18/2025 11:14:06 | 10/22/2025 17:49:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000543 | PCM-20251018-00000966 | TT-20251018-00947 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/18/2025 11:44:35 | 10/18/2025 14:11:59 | 10/18/2025 23:44:35 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/18/2025 11:33:49 | Minor | 65102 | high temprature 32 | 10/18/2025 11:33:47 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/18/2025 11:44:35 | 10/18/2025 14:11:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000551 | PCM-20251018-00000986 | TT-20251018-00960 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/18/2025 11:53:51 | 10/18/2025 17:40:20 | 10/18/2025 23:53:51 | high temprature 40 at KBR2223-P3_SRAN @ Sceco | 10/18/2025 11:43:15 | Minor | 65103 | high temprature 40 | 10/18/2025 11:43:11 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/18/2025 11:53:51 | 10/18/2025 17:40:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000610 | PCM-20251018-00001076 | TT-20251018-01058 | EM | Region_2 | RIY0249 | RIY0249 |  |  |  | Pawan Virdi Santokh Singh | 10/18/2025 12:38:50 | 10/19/2025 00:29:00 | 10/18/2025 18:38:50 | Door opening alarm at RIY0249-P1-SHOP_SRAN @ Sceco | 10/18/2025 12:38:00 | Major | 65101 | Door opening alarm | 10/18/2025 12:37:57 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0249 | FLM_EM | [8 empty] | API | 10/18/2025 12:38:50 | 10/19/2025 00:29:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000615 | PCM-20251018-00001085 | TT-20251018-01064 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/18/2025 12:41:56 | 10/18/2025 13:57:01 | 10/19/2025 00:41:56 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/18/2025 12:31:23 | Minor | 65102 | High temperature 32C alarm | 10/18/2025 12:31:20 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/18/2025 12:41:56 | 10/18/2025 13:57:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000671 | PCM-20251018-00001182 | TT-20251018-00863 | Reference_telecom | Region_2 | ZLH0229 | ZLH0229 |  |  |  | Saeed Ud Din Muhammad Yousaf | 10/18/2025 13:26:45 | 10/19/2025 20:54:55 | 10/19/2025 01:26:45 | External Clock Reference Problem at ZLH0229-P2_SRAN @ Generator_SG | 10/18/2025 09:00:03 | Minor | 26262 | External Clock Reference Problem | 10/18/2025 08:02:17 | P2 | SRAN | majma | Generator_SG | 2G NSA | ZLH0229 | FLM_EM |  |  | PCM-20251018-00000920 | We are observing RSL -90 at hub site MJAR0877 ,Suspected power issue, Dear EM FLM please check issue and solve | We are observing RSL -90 at hub site MJAR0877 ,Suspected power issue, Dear EM FLM please check issue and solve |  |  |  | API | 10/18/2025 13:26:45 | 10/19/2025 20:54:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000727 | PCM-20251018-00001272 | TT-20251018-01221 | EM | Region_4 | HAW2351 | HAW2351 |  |  |  | Farghal Ashour Hassan Farghal | 10/18/2025 13:59:20 | 10/20/2025 01:07:02 | 10/19/2025 01:59:20 | RECTIFIER MAINS POWER FAILURE at HAW1M8351-P3-CA-L800 @ Sceco | 10/18/2025 13:50:38 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/18/2025 13:50:33 | P2 | 4G | taif | Sceco | LTE NSA | HAW1M8351 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/18/2025 13:59:20 | 10/20/2025 01:07:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000731 | PCM-20251018-00001277 | TT-20251018-01225 | EM | Region_1 | KBR0608 | KBR0608 |  |  |  | Abdul Malik Shaik | 10/18/2025 14:02:56 | 10/18/2025 14:12:01 | 10/19/2025 02:02:56 | NETECO: DIN4 Alarm at KBR0608 @ Sceco | 10/18/2025 13:56:08 | Minor | 21942 | DIN4 Alarm | 10/18/2025 13:56:08 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0608 | FLM_EM | [8 empty] | API | 10/18/2025 14:02:56 | 10/18/2025 14:12:01 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000735 | PCM-20251018-00001284 | TT-20251018-01234 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/18/2025 14:06:00 | 10/22/2025 13:22:52 | 10/19/2025 02:06:00 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/18/2025 13:59:15 | Minor | 40564 | Genset Fault | 10/18/2025 13:59:15 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/18/2025 14:06:00 | 10/22/2025 13:20:32 | 10/22/2025 13:22:46 |  |  | 10/22/2025 13:22:52 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000745 | PCM-20251018-00001297 | TT-20251018-01246 | EM | Region_4 | JED2069 | JED2069 | Enviroment | Rectifier Module | Change rectifer module | Amr Sherif Gabber Ahmed | 10/18/2025 14:11:45 | 10/19/2025 20:51:53 | 10/19/2025 02:11:45 | RECTIFIER MODULE FAILURE at JED1M8069-L800-CA-SBTS-P3 @ Generator_SG | 10/18/2025 14:06:11 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/18/2025 14:03:14 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JED1M8069 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/18/2025 14:11:45 | 10/18/2025 19:13:21 | 10/19/2025 20:51:46 |  |  | 10/19/2025 20:51:53 |  | Amr Sherif Gabber Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000797 | PCM-20251018-00001377 | TT-20251018-01349 | EM | Region_4 | JED2279 | JED2279 |  |  |  | Sajid Nazir Muhammad Nazir | 10/18/2025 14:50:31 | 10/18/2025 15:52:39 | 10/19/2025 02:50:31 | RECTIFIER MODULE FAILURE at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/18/2025 14:42:27 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/18/2025 14:42:05 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2279 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/18/2025 14:50:31 | 10/18/2025 15:52:39 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000808 | PCM-20251018-00001398 | TT-20251018-01309 | Reference_telecom | Region_2 | MJAR0877 | MJAR0877 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Saeed Ud Din Muhammad Yousaf | 10/18/2025 15:05:00 | 10/19/2025 21:21:13 | 10/19/2025 03:05:00 | IP Clock Link Failure at MJAR0877-P3_SRAN @ Generator_SG | 10/18/2025 11:31:13 | Minor | 26263 | IP Clock Link Failure | 10/18/2025 11:25:42 | P3 | SRAN | majma | Generator_SG | 2G NSA | MJAR0877 | FLM_EM |  |  | PCM-20251018-00001358 | We are observing RSL -90 at hub site MJAR0877 ,Suspected power issue, Dear EM FLM please check issue and solve | We are observing RSL -90 at hub site MJAR0877 ,Suspected power issue, Dear EM FLM please check issue and solve |  |  |  | API | 10/18/2025 15:05:00 | 10/19/2025 20:54:55 | 10/19/2025 21:21:00 |  |  | 10/19/2025 21:21:13 |  | Saeed Ud Din Muhammad Yousaf |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018000829 | PCM-20251018-00001424 | TT-20251018-01386 | EM | Region_4 | JED0153 | JED0153 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/18/2025 15:15:20 | 10/18/2025 18:58:54 | 10/19/2025 03:15:20 | HIGH TEMPERATURE 32 DEGREE C at JED1M7153-CA-L900-L800-SBTS-P3 @ Sceco | 10/18/2025 15:07:04 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/18/2025 15:06:53 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7153 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/18/2025 15:15:20 | 10/18/2025 18:58:54 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018000853 | PCM-20251018-00001460 | TT-20251018-01381 | Telecom | Region_2 | BUR2110 | BUR2110 | Equipment | FAN Cleaning | Reset FAN | Farman Ullah Muhammad Nazir | 10/18/2025 15:29:26 | 10/22/2025 16:40:50 | 10/19/2025 03:29:26 | RF Unit Maintenance Link Failure at BUR2M4110-P2 @ Sceco | 10/18/2025 15:08:08 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/18/2025 15:06:24 | P2 | 3G | buraidah | Sceco | 3G NSA | BUR2M4110 | FLM_EM |  |  | PCM-20251018-00001418 | power issue at site | power issue at site |  |  |  | API | 10/18/2025 15:29:26 | 10/18/2025 16:17:46 | 10/22/2025 16:40:39 |  |  | 10/22/2025 16:40:50 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251018000855 | PCM-20251018-00001463 | TT-20251018-01380 | Telecom | Region_2 | BUR2110 | BUR2110 | Equipment | FAN Cleaning | Reset FAN | Farman Ullah Muhammad Nazir | 10/18/2025 15:30:05 | 10/22/2025 16:40:21 | 10/19/2025 03:30:05 | BBU CPRI Optical Module Fault at BUR2M4110-P2 @ Sceco | 10/18/2025 15:06:38 | Minor | 26230 | BBU CPRI Optical Module Fault | 10/18/2025 15:05:05 | P2 | 3G | buraidah | Sceco | 3G NSA | BUR2M4110 | FLM_EM |  |  | PCM-20251018-00001419 | power issue at site | power issue at site |  |  |  | API | 10/18/2025 15:30:05 | 10/18/2025 16:17:47 | 10/22/2025 16:40:12 |  |  | 10/22/2025 16:40:21 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251018000862 | PCM-20251018-00001472 | TT-20251018-01441 | EM | Region_6 | HEQ2026 | HEQ2026 |  |  |  | Fizan Ahmed | 10/18/2025 15:35:26 | 10/18/2025 15:54:02 | 10/19/2025 03:35:26 | AIRCON 1 FAILURE at HEQ1M8026-G9-L18-L21-SBTS-P3 @ Sceco | 10/18/2025 15:27:01 | Minor | 7103 | AIRCON 1 FAILURE | 10/18/2025 15:26:50 | P3 | 4G | raith | Sceco | LTE NSA | HEQ1M8026 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/18/2025 15:35:26 | 10/18/2025 15:54:02 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251018001008 | PCM-20251018-00001715 | TT-20251018-01675 | EM | Region_6 | RTH0607 | RTH0607 |  |  |  | Muhammad Usman Aslam | 10/18/2025 17:46:40 | 10/19/2025 07:05:05 | 10/19/2025 05:46:40 | SHELTER DOOR OPEN at RTH0607-GSM-UMTS-P2 @ Generator_DG | 10/18/2025 17:45:55 | Minor | 7103 | SHELTER DOOR OPEN | 10/18/2025 17:45:38 | P2 | 2G | raith | Generator_DG | 2G NSA | RTH0607 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/18/2025 17:46:40 | 10/19/2025 07:05:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018001097 | PCM-20251018-00001895 | TT-20251018-01800 | Reference_telecom | Region_2 | RYQ0957 | RYQ0957 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/18/2025 19:24:20 | 10/22/2025 18:45:53 | 10/19/2025 07:24:20 | External Clock Reference Problem at RYQ0957-P2_SRAN @ Sceco | 10/18/2025 16:02:38 | Minor | 26262 | External Clock Reference Problem | 10/18/2025 16:01:39 | P2 | SRAN | majma | Sceco | 2G NSA | RYQ0957 | FLM_EM |  |  | PCM-20251018-00001878 | We are observing RSL -90 at hub site RYQ0957 ,Suspected power issue, Dear EM FLM please check issue and solve | We are observing RSL -90 at hub site RYQ0957 ,Suspected power issue, Dear EM FLM please check issue and solve |  |  |  | API | 10/18/2025 19:24:20 | 10/19/2025 07:23:48 | 10/22/2025 18:45:46 |  |  | 10/22/2025 18:45:53 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251018001124 | PCM-20251018-00001942 | TT-20251018-01874 | EM | Region_1 | YBR0725 | YBR0725 | Enviroment | Air Condition | Change Fan | Kenawy Abdalla Tawfik Abdalla | 10/18/2025 19:50:18 | 10/18/2025 21:43:29 | 10/19/2025 07:50:18 | Door opening alarm at YBR0725-P2-USF_SRAN-PC @ Power Cube | 10/18/2025 19:49:19 | Minor | 65101 | Door opening alarm | 10/18/2025 19:49:15 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0725 | FLM_EM | [8 empty] | API | 10/18/2025 19:50:18 | 10/18/2025 21:35:30 | 10/18/2025 21:35:42 | 10/18/2025 21:35:56 | 10/18/2025 21:36:00 | 10/18/2025 21:43:29 |  | Kenawy Abdalla Tawfik Abdalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251018001136 | PCM-20251018-00001963 | TT-20251018-01898 | Reference_EM | Region_1 | YBR0725 | YBR0725 | Enviroment | Fire Alarm | Reset Fire Pannel | Kenawy Abdalla Tawfik Abdalla | 10/18/2025 20:07:11 | 10/18/2025 21:49:59 | 10/19/2025 08:07:11 | Major Rec alarm at YBR0725-P2-USF_SRAN-PC @ Power Cube | 10/18/2025 19:56:35 | Minor | 65107 | Major Rec alarm | 10/18/2025 19:56:32 | P2 | SRAN | hafouf | Power Cube | 2G NSA | YBR0725 | FLM_EM | [8 empty] | API | 10/18/2025 20:07:11 | 10/18/2025 21:35:34 | 10/18/2025 21:44:37 | 10/18/2025 21:44:43 | 10/18/2025 21:44:46 | 10/18/2025 21:49:59 |  | Kenawy Abdalla Tawfik Abdalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251018001224 | PCM-20251018-00002096 | TT-20251018-02029 | EM | Region_4 | JED2601 | JED2601 |  |  |  | Sajid Nazir Muhammad Nazir | 10/18/2025 22:12:40 | 10/19/2025 00:08:36 | 10/19/2025 10:12:40 | SHELTER DOOR OPEN at JED1M8601-CA-L800-P3 @ Sceco | 10/18/2025 22:12:06 | Minor | 7103 | SHELTER DOOR OPEN | 10/18/2025 22:11:58 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8601 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/18/2025 22:12:40 | 10/19/2025 00:08:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251018001228 | PCM-20251018-00002100 | TT-20251018-02037 | EM | Region_4 | JED0599 | JED0599 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/18/2025 22:20:25 | 10/18/2025 22:20:25 | 10/19/2025 10:20:25 | AIRCON 1 FAILURE at JED1M7599-CA-L900-L800-SBTS @ Sceco | 10/18/2025 22:13:42 | Minor | 7103 | AIRCON 1 FAILURE | 10/18/2025 22:11:39 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7599 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/18/2025 22:20:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000062 | PCM-20251019-00000140 | TT-20251019-00186 | EM | Region_2 | RIY0172 | RIY0172 |  |  |  | Adham Adham Hassan Farghal | 10/19/2025 02:09:51 | 10/19/2025 09:17:30 | 10/19/2025 08:09:51 | Air condition 1 failure alarm at RIY0172-P1-SHOP_SRAN @ Sceco | 10/19/2025 01:59:54 | Major | 65104 | Air condition 1 failure alarm | 10/19/2025 01:59:05 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0172 | FLM_EM | [8 empty] | API | 10/19/2025 02:09:51 | 10/19/2025 09:17:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000081 | PCM-20251019-00000183 | TT-20251019-00239 | EM | Region_2 | RIY0247 | RIY0247 |  |  |  | Kadri Jalal Mohammed Asmail | 10/19/2025 02:38:16 | 10/20/2025 12:32:10 | 10/19/2025 14:38:16 | Air condition 2 failure alarm at RIY0247-P2_SRAN @ Sceco | 10/19/2025 02:30:58 | Minor | 65105 | Air condition 2 failure alarm | 10/19/2025 02:27:50 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0247 | FLM_EM | [8 empty] | API | 10/19/2025 02:38:16 | 10/19/2025 10:56:13 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000082 | PCM-20251019-00000182 | TT-20251019-00238 | EM | Region_2 | RIY0133 | RIY0133 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/19/2025 02:38:16 | 10/19/2025 11:23:51 | 10/19/2025 14:38:16 | Air condition 1 failure alarm at RIY0133-P2_SRAN @ Sceco | 10/19/2025 02:33:43 | Minor | 65104 | Air condition 1 failure alarm | 10/19/2025 02:27:43 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0133 | FLM_EM | [8 empty] | API | 10/19/2025 02:38:16 | 10/19/2025 11:23:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000087 | PCM-20251019-00000188 | TT-20251019-00244 | EM | Region_2 | RIY0226 | RIY0226 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/19/2025 02:38:50 | 10/20/2025 12:32:12 | 10/19/2025 08:38:50 | Air condition 1 failure alarm at RIY0226-P1-DIA_SRAN-FON @ Sceco | 10/19/2025 02:30:30 | Major | 65104 | Air condition 1 failure alarm | 10/19/2025 02:28:16 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0226 | FLM_EM | [8 empty] | API | 10/19/2025 02:38:50 | 10/19/2025 11:23:51 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251019000088 | PCM-20251019-00000189 | TT-20251019-00245 | EM | Region_2 | RIY0225 | RIY0225 |  |  |  | Adel Abdelaziz Mohamed Ayedi | 10/19/2025 02:38:52 | 10/20/2025 12:32:13 | 10/19/2025 14:38:52 | Air condition 2 failure alarm at RIY0225-P2_SRAN @ Sceco | 10/19/2025 02:30:27 | Minor | 65105 | Air condition 2 failure alarm | 10/19/2025 02:28:23 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0225 | FLM_EM | [8 empty] | API | 10/19/2025 02:38:52 | 10/19/2025 12:50:02 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000089 | PCM-20251019-00000193 | TT-20251019-00249 | EM | Region_2 | RIY2637 | RIY2637 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/19/2025 02:39:15 | 10/20/2025 12:32:12 | 10/19/2025 14:39:15 | Air condition 2 failure alarm at RIY2637-P3_SRAN @ Sceco | 10/19/2025 02:35:47 | Minor | 65105 | Air condition 2 failure alarm | 10/19/2025 02:28:53 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2637 | FLM_EM | [8 empty] | API | 10/19/2025 02:39:15 | 10/19/2025 11:23:52 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251019000090 | PCM-20251019-00000191 | TT-20251019-00247 | EM | Region_2 | RIY0096 | RIY0096 | Enviroment | Fire Alarm | Reset Fire Pannel | Pawan Virdi Santokh Singh | 10/19/2025 02:39:16 | 10/22/2025 13:31:12 | 10/19/2025 08:39:16 | Fire Alarm at RIY0096-P1-DIA_SRAN @ Sceco | 10/19/2025 02:32:18 | Major | 65119 | Fire Alarm | 10/19/2025 02:28:32 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0096 | FLM_EM | [8 empty] | API | 10/19/2025 02:39:16 | 10/20/2025 08:00:05 | 10/22/2025 12:48:19 | 10/22/2025 13:03:01 | 10/22/2025 13:07:13 | 10/22/2025 13:31:12 |  | Pawan Virdi Santokh Singh |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000091 | PCM-20251019-00000190 | TT-20251019-00246 | EM | Region_2 | RIY0022 | RIY0022 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/19/2025 02:39:18 | 10/22/2025 17:49:41 | 10/19/2025 08:39:18 | Air condition 2 failure alarm at RIY0022-P1_SRAN @ Sceco | 10/19/2025 02:33:37 | Major | 65105 | Air condition 2 failure alarm | 10/19/2025 02:28:40 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0022 | FLM_EM | [8 empty] | API | 10/19/2025 02:39:18 | 10/22/2025 17:49:41 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251019000092 | PCM-20251019-00000192 | TT-20251019-00248 | EM | Region_2 | RIY0398 | RIY0398 | Enviroment | Air Condition | Change Fan | Tanveer Ahmad Fateh Muhammad | 10/19/2025 02:39:20 | 10/19/2025 19:12:10 | 10/19/2025 14:39:20 | Air condition 1 failure alarm at RIY0398-P2_SRAN @ Sceco | 10/19/2025 02:35:38 | Minor | 65104 | Air condition 1 failure alarm | 10/19/2025 02:28:35 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0398 | FLM_EM | [8 empty] | API | 10/19/2025 02:39:20 | 10/19/2025 18:36:37 | 10/19/2025 18:50:54 | 10/19/2025 18:50:57 | 10/19/2025 18:51:01 | 10/19/2025 19:12:10 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251019000095 | PCM-20251019-00000195 | TT-20251019-00251 | EM | Region_2 | RIY2789 | RIY2789 |  |  |  | Pawan Virdi Santokh Singh | 10/19/2025 02:39:48 | 10/20/2025 08:00:06 | 10/19/2025 14:39:48 | Fire Alarm at RIY2789-P2_SRAN @ Sceco | 10/19/2025 02:33:20 | Minor | 65119 | Fire Alarm | 10/19/2025 02:29:07 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2789 | FLM_EM | [8 empty] | API | 10/19/2025 02:39:48 | 10/20/2025 08:00:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000096 | PCM-20251019-00000197 | TT-20251019-00253 | EM | Region_2 | RIY0111 | RIY0111 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/19/2025 02:40:23 | 10/22/2025 17:49:42 | 10/19/2025 08:40:23 | Fire Alarm at RIY0111-P1-DIA-SHOP_SRAN @ Sceco | 10/19/2025 02:33:46 | Major | 65119 | Fire Alarm | 10/19/2025 02:29:31 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0111 | FLM_EM | [8 empty] | API | 10/19/2025 02:40:23 | 10/22/2025 17:49:42 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000097 | PCM-20251019-00000198 | TT-20251019-00255 | EM | Region_2 | RIY0858 | RIY0858 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/19/2025 02:41:51 | 10/19/2025 11:23:52 | 10/19/2025 08:41:51 | Fire Fighting system alarm at RIY0858-P1-SHOP_SRAN-FON @ Sceco | 10/19/2025 02:35:41 | Major | 65111 | Fire Fighting system alarm | 10/19/2025 02:31:19 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0858 | FLM_EM | [8 empty] | API | 10/19/2025 02:41:51 | 10/19/2025 11:23:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251019000100 | PCM-20251019-00000202 | TT-20251019-00262 | EM | Region_2 | RIY0427 | RIY0427 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/19/2025 02:44:56 | 10/20/2025 12:32:08 | 10/19/2025 08:44:56 | Air condition 1 failure alarm at RIY0427-P1-VIP_SRAN @ Sceco | 10/19/2025 02:36:35 | Major | 65104 | Air condition 1 failure alarm | 10/19/2025 02:34:32 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0427 | FLM_EM | [8 empty] | API | 10/19/2025 02:44:56 | 10/19/2025 10:24:38 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000224 | PCM-20251019-00000483 | TT-20251019-00568 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/19/2025 06:17:20 | 10/22/2025 21:40:40 | 10/19/2025 18:17:20 | Generator failure at SMN0805-P3_SRAN @ Generator_DG | 10/19/2025 06:09:33 | Minor | 65114 | Generator failure | 10/19/2025 06:06:56 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/19/2025 06:17:20 | 10/22/2025 21:40:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000356 | PCM-20251019-00000758 | TT-20251019-00848 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/19/2025 09:10:51 | 10/19/2025 09:17:31 | 10/19/2025 15:10:51 | high temprature 40 at RIY0232-P1_SRAN @ Sceco | 10/19/2025 09:00:27 | Major | 65103 | high temprature 40 | 10/19/2025 09:00:23 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/19/2025 09:10:51 | 10/19/2025 09:17:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000374 | PCM-20251019-00000794 | TT-20251019-00876 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/19/2025 09:26:51 | 10/19/2025 17:23:50 | 10/19/2025 21:26:51 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/19/2025 09:16:19 | Minor | 65102 | high temprature 32 | 10/19/2025 09:16:16 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/19/2025 09:26:51 | 10/19/2025 17:23:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251019000386 | PCM-20251019-00000819 | TT-20251019-00898 | EM | Region_2 | NUK0126 | NUK0126 |  |  |  | Shahid Ahmed Shah Nawaz | 10/19/2025 09:41:20 | 10/20/2025 12:32:05 | 10/19/2025 21:41:20 | Air condition 1 failure alarm at NUK0126-P2_SRAN @ Sceco | 10/19/2025 09:34:45 | Minor | 65104 | Air condition 1 failure alarm | 10/19/2025 09:30:38 | P2 | SRAN | buraidah | Sceco | 2G NSA | NUK0126 | FLM_EM | [8 empty] | API | 10/19/2025 09:41:20 | 10/19/2025 09:50:10 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000390 | PCM-20251019-00000832 | TT-20251019-00916 | EM | Region_2 | BUR0029 | BUR0029 |  |  |  | Shahid Ahmed Shah Nawaz | 10/19/2025 09:46:36 | 10/20/2025 12:32:06 | 10/19/2025 21:46:36 | Air condition 1 failure alarm at BUR0029-P2_SRAN @ Sceco | 10/19/2025 09:40:40 | Minor | 65104 | Air condition 1 failure alarm | 10/19/2025 09:36:11 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0029 | FLM_EM | [8 empty] | API | 10/19/2025 09:46:36 | 10/19/2025 09:50:11 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251019000436 | PCM-20251019-00000941 | TT-20251019-01028 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change compressor | Emad Mahmoud Ahmed Mohamed | 10/19/2025 10:41:45 | 10/20/2025 12:04:21 | 10/19/2025 14:41:45 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/19/2025 10:40:06 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/19/2025 10:39:58 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 1-(1-B) |  |  | API | 10/19/2025 10:41:45 | 10/20/2025 12:01:21 | 10/20/2025 12:04:11 |  |  | 10/20/2025 12:04:21 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251019000446 | PCM-20251019-00000948 | TT-20251019-01039 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/19/2025 10:54:41 | 10/19/2025 15:26:40 | 10/19/2025 16:54:41 | high temprature 40 at DAM2066-P1-HUB_SRAN @ Sceco | 10/19/2025 10:34:25 | Major | 65103 | high temprature 40 | 10/19/2025 10:34:22 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/19/2025 10:54:41 | 10/19/2025 15:26:40 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000608 | PCM-20251019-00001331 | TT-20251019-01455 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/19/2025 13:24:31 | 10/19/2025 13:51:18 | 10/20/2025 01:24:31 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/19/2025 13:13:48 | Minor | 65102 | high temprature 32 | 10/19/2025 13:13:44 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/19/2025 13:24:31 | 10/19/2025 13:51:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000654 | PCM-20251019-00001444 | TT-20251019-01579 | EM | Region_2 | RIY2755 | RIY2755 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/19/2025 14:16:41 | 10/19/2025 15:28:26 | 10/19/2025 18:16:41 | Door opening alarm at RIY2755-P1-VVVIP-WDM_SRAN-FON @ Sceco | 10/19/2025 14:16:14 | Critical | 65101 | Door opening alarm | 10/19/2025 14:16:11 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2755 | FLM_EM | [8 empty] | API | 10/19/2025 14:16:41 | 10/19/2025 15:28:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251019000658 | PCM-20251019-00001456 | TT-20251019-01588 | EM | Region_1 | KBR0608 | KBR0608 |  |  |  | Mohamed Samir Farahat Allam | 10/19/2025 14:20:51 | 10/21/2025 14:56:35 | 10/20/2025 02:20:51 | NETECO: DIN4 Alarm at KBR0608 @ Sceco | 10/19/2025 14:14:10 | Minor | 21942 | DIN4 Alarm | 10/19/2025 14:14:10 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0608 | FLM_EM | [8 empty] | API | 10/19/2025 14:20:51 | 10/21/2025 14:56:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251019000698 | PCM-20251019-00001531 | TT-20251019-01661 | Reference_EM | Region_1 | ARR0919 | ARR0919 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/19/2025 14:50:46 | 10/22/2025 13:23:05 | 10/19/2025 20:50:46 | Low battery voltage at ARR0919-P1-USF-HUB_SRAN @ Sceco_STB | 10/19/2025 14:40:31 | Major | 65110 | Low battery voltage | 10/19/2025 14:40:27 | P1 | SRAN | rafha | Sceco_STB | 2G NSA | ARR0919 | FLM_EM | [8 empty] | API | 10/19/2025 14:50:46 | 10/22/2025 13:20:34 | 10/22/2025 13:22:58 |  |  | 10/22/2025 13:23:05 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251019000825 | PCM-20251019-00001864 | TT-20251019-01986 | EM | Region_2 | KHJ0846 | KHJ0846 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/19/2025 17:02:06 | 10/20/2025 14:40:50 | 10/20/2025 05:02:06 | Air condition 2 failure alarm at KHJ0846-P2_SRAN @ Sceco | 10/19/2025 16:55:23 | Minor | 65105 | Air condition 2 failure alarm | 10/19/2025 16:51:15 | P2 | SRAN | al kharj | Sceco | 2G NSA | KHJ0846 | FLM_EM | [8 empty] | API | 10/19/2025 17:02:06 | 10/20/2025 14:40:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251019000866 | PCM-20251019-00001947 | TT-20251019-02082 | MW_HC | Region_4 | JDRS0756 | JDRS0756 |  |  |  | Khizer Hayat | 10/19/2025 17:41:27 | 10/19/2025 17:47:53 | 10/20/2025 05:41:27 | NEC MW HC_P0 Observing Performance Issue at JDRS0756(10.154.113.83)--JDRS0757(10.154.113.82) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | jeddah | Generator_SG | TX NSA | JDRS0756(10.154.113.83)--JDRS0757(10.154.113.82) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:27 | 10/19/2025 17:47:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000867 | PCM-20251019-00001948 | TT-20251019-02083 | MW_HC | Region_4 | JDMD0859 | JDMD0859 |  |  |  | Nazeer Mohammed | 10/19/2025 17:41:28 | 10/20/2025 13:30:32 | 10/20/2025 05:41:28 | NEC MW HC_P0 Observing Performance Issue at JDMD0859(10.154.153.209)--JED0224(10.154.153.213) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDMD0859(10.154.153.209)--JED0224(10.154.153.213) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:28 | 10/20/2025 13:30:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000868 | PCM-20251019-00001949 | TT-20251019-02084 | MW_HC | Region_4 | JDMD0859 | JDMD0859 |  |  |  | Nazeer Mohammed | 10/19/2025 17:41:29 | 10/20/2025 13:30:32 | 10/20/2025 05:41:29 | NEC MW HC_P0 Observing Performance Issue at JDMD0859(10.154.115.34)--JDMD0861(10.154.115.6) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDMD0859(10.154.115.34)--JDMD0861(10.154.115.6) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:29 | 10/20/2025 13:30:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000869 | PCM-20251019-00001950 | TT-20251019-02085 | MW_HC | Region_4 | JDJZ0776 | JDJZ0776 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/19/2025 17:41:31 | 10/19/2025 17:57:17 | 10/20/2025 05:41:31 | NEC MW HC_P0 Observing Modem Down at JDJZ0776(10.157.105.241)--QUN0334(10.157.105.243) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0776(10.157.105.241)--QUN0334(10.157.105.243) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:31 | 10/19/2025 17:57:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000870 | PCM-20251019-00001951 | TT-20251019-02086 | MW_HC | Region_4 | HHR0459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 17:41:32 | 10/20/2025 16:09:50 | 10/20/2025 05:41:32 | NEC MW HC_P0 Observing Modem Down at HHR0459(10.154.153.18)--JED0017(10.154.153.17) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | VIP | 2G | jeddah | Sceco | TX NSA | HHR0459(10.154.153.18)--JED0017(10.154.153.17) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:32 | 10/20/2025 16:09:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000871 | PCM-20251019-00001952 | TT-20251019-02087 | MW_HC | Region_6 | WDS0770 | WDS0770 |  |  |  | Ahmed Mamdouh Helal Helal | 10/19/2025 17:41:33 | 10/19/2025 22:42:18 | 10/20/2025 05:41:33 | NEC MW HC_P0 VIP Observing RSL Issue at WDS0770(10.89.222.166)--WDS9509(10.89.222.162) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P3 | 2G | wadi dawasar | Sceco | TX NSA | WDS0770(10.89.222.166)--WDS9509(10.89.222.162) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:33 | 10/19/2025 22:42:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000872 | PCM-20251019-00001953 | TT-20251019-02089 | MW_HC | Region_6 | WDS0230 | WDS0230 |  |  |  | Ahmed Mamdouh Helal Helal | 10/19/2025 17:41:34 | 10/19/2025 22:42:21 | 10/20/2025 05:41:34 | NEC MW HC_P0 VIP Observing Modem Down at WDS0230(10.1.171.243)--WDS0498(10.1.171.241) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | wadi dawasar | Sceco | TX NSA | WDS0230(10.1.171.243)--WDS0498(10.1.171.241) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:34 | 10/19/2025 22:42:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000873 | PCM-20251019-00001954 | TT-20251019-02090 | MW_HC | Region_4 | TFBH9446 | TFBH9446 |  |  |  | Ahmad Kamal Abdelmawla | 10/19/2025 17:41:35 | 10/19/2025 20:55:06 | 10/20/2025 05:41:35 | NEC MW HC_P0 Observing Modem Down at TFBH9446(10.88.221.34)--TFBH9451(10.88.221.41) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9446(10.88.221.34)--TFBH9451(10.88.221.41) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:35 | 10/19/2025 20:55:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000874 | PCM-20251019-00001955 | TT-20251019-02092 | MW_HC | Region_4 | SIR0172 | SIR0172 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 17:41:36 | 10/19/2025 23:01:53 | 10/20/2025 05:41:36 | NEC MW HC_P0 Observing Modem Down at SIR0172(10.88.221.244)--SIR0189(10.88.221.245) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | adam | Generator_SG | TX NSA | SIR0172(10.88.221.244)--SIR0189(10.88.221.245) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:36 | 10/19/2025 23:01:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000875 | PCM-20251019-00001956 | TT-20251019-02093 | MW_HC | Region_6 | SDA0425 | SDA0425 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/19/2025 17:41:37 | 10/19/2025 23:48:40 | 10/20/2025 05:41:37 | NEC MW HC_P0 Observing Modem Down at SDA0425(10.154.163.203)--SDA0426(10.154.163.197) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P3 | 2G | abha | Sceco | TX NSA | SDA0425(10.154.163.203)--SDA0426(10.154.163.197) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:37 | 10/19/2025 23:48:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000877 | PCM-20251019-00001958 | TT-20251019-02095 | MW_HC | Region_6 | KHS0563 | KHS0563 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/19/2025 17:41:39 | 10/19/2025 18:41:44 | 10/20/2025 05:41:39 | NEC MW HC_P0 Observing RSL Issue at KHS0563(10.89.220.83)--KHS0993(10.89.220.86) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KHS0563(10.89.220.83)--KHS0993(10.89.220.86) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:39 | 10/19/2025 18:41:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000878 | PCM-20251019-00001959 | TT-20251019-02096 | MW_HC | Region_6 | JEC0088 | JEC0088 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/19/2025 17:41:40 | 10/19/2025 19:05:16 | 10/20/2025 05:41:40 | NEC MW HC_P0 VIP Observing Performance Issue at JEC0088(10.199.24.88)--JEC0090(10.199.24.84) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P2 | 2G | baish | Sceco_STB | TX NSA | JEC0088(10.199.24.88)--JEC0090(10.199.24.84) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:40 | 10/19/2025 19:05:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000879 | PCM-20251019-00001960 | TT-20251019-02097 | MW_HC | Region_6 | JDSM0791 | JDSM0791 |  |  |  | Zeshan Ali Adnan | 10/19/2025 17:41:41 | 10/19/2025 18:22:40 | 10/20/2025 05:41:41 | NEC MW HC_P0 Observing RSL Issue at JDSM0791(10.157.253.129)--JIZ0093(10.157.253.140) | 10/19/2025 17:41:00 | Minor |  | LOF | 10/19/2025 17:41:00 | P1 | 2G | jizan | Sceco_STB | TX NSA | JDSM0791(10.157.253.129)--JIZ0093(10.157.253.140) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:41 | 10/19/2025 18:22:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000882 | PCM-20251019-00001963 | TT-20251019-02100 | MW_HC | Region_1 | ARM2759 | ARM2759 |  |  |  | Tahir Mahmood Hafiz Yar | 10/19/2025 17:41:45 | 10/19/2025 19:27:31 | 10/20/2025 05:41:45 | NEC MW HC_P0 Observing Performance Issue at ARM2759(10.76.117.59)--JBKH0095(10.76.117.58) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P1 | SRAN | jubail | Power Cube | TX NSA | ARM2759(10.76.117.59)--JBKH0095(10.76.117.58) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:45 | 10/19/2025 19:27:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000883 | PCM-20251019-00001964 | TT-20251019-02101 | MW_HC | Region_1 | HFF0937 | HFF0937 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/19/2025 17:41:45 | 10/21/2025 05:43:47 | 10/20/2025 05:41:45 | NEC MW HC_P0 Observing Modem Down at HFF0937(10.158.221.106)--HFF6030(10.158.221.107) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P3 | SRAN | hafouf | Sceco | TX NSA | HFF0937(10.158.221.106)--HFF6030(10.158.221.107) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:45 | 10/21/2025 05:43:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000885 | PCM-20251019-00001966 | TT-20251019-02103 | MW_HC | Region_1 | HFF0933 | HFF0933 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/19/2025 17:41:47 | 10/21/2025 05:43:47 | 10/20/2025 05:41:47 | NEC MW HC_P0 Observing Modem Down at HFF0933(10.74.80.154)--HFF6022(10.74.80.155) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P2 | SRAN | hafouf | Sceco | TX NSA | HFF0933(10.74.80.154)--HFF6022(10.74.80.155) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:47 | 10/21/2025 05:43:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000886 | PCM-20251019-00001967 | TT-20251019-02104 | MW_HC | Region_6 | BSH0197 | BSH0197 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/19/2025 17:41:49 | 10/19/2025 19:05:16 | 10/20/2025 05:41:49 | NEC MW HC_P0 VIP Observing Performance Issue at BSH0197(10.199.24.83)--JEC0090(10.199.24.82) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P2 | 2G | baish | Sceco | TX NSA | BSH0197(10.199.24.83)--JEC0090(10.199.24.82) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:49 | 10/19/2025 19:05:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000887 | PCM-20251019-00001968 | TT-20251019-02105 | MW_HC | Region_1 | DMH0104 | DMH0104 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/19/2025 17:41:50 | 10/19/2025 21:20:29 | 10/20/2025 05:41:50 | NEC MW HC_P1 Observing Performance Issue at DMH0104(10.159.105.138)--DMH0606(10.159.105.140) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0104(10.159.105.138)--DMH0606(10.159.105.140) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:50 | 10/19/2025 21:20:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000890 | PCM-20251019-00001971 | TT-20251019-02108 | MW_HC | Region_1 | DMHF0072 | DMHF0072 |  |  |  | Mohamed Magdy Fouad Zayed | 10/19/2025 17:41:53 | 10/19/2025 19:01:04 | 10/20/2025 05:41:53 | NEC MW HC_P0 Observing Performance Issue at DMHF0072(10.147.8.37)--DMHF0079(10.147.8.38) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P3 | SRAN | hafouf | Generator_SG | TX NSA | DMHF0072(10.147.8.37)--DMHF0079(10.147.8.38) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:53 | 10/19/2025 19:01:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000892 | PCM-20251019-00001973 | TT-20251019-02110 | MW_HC | Region_6 | BAH0002 | BAH0002 |  |  |  | SHAH KHALID | 10/19/2025 17:41:56 | 10/19/2025 18:37:30 | 10/20/2025 05:41:56 | NEC MW HC_P0 Observing Modem Down at BAH0002(10.1.174.33)--BHAB0820(10.1.174.36) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0002(10.1.174.33)--BHAB0820(10.1.174.36) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:56 | 10/19/2025 18:37:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000894 | PCM-20251019-00001975 | TT-20251019-02112 | MW_HC | Region_6 | DAR0923 | DAR0923 |  |  |  | Muhammad Ali | 10/19/2025 17:41:57 | 10/19/2025 17:53:21 | 10/20/2025 05:41:57 | NEC MW HC_P2 Observing Modem Down at DAR0923(10.1.173.14)--DAR2022(10.1.173.13) | 10/19/2025 17:40:59 | Minor |  | LOF | 10/19/2025 17:40:59 | P1 | 2G | dair | Generator_DG | TX NSA | DAR0923(10.1.173.14)--DAR2022(10.1.173.13) | FLM_TE | [8 empty] | API | 10/19/2025 17:41:57 | 10/19/2025 17:53:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000902 | PCM-20251019-00001995 | TT-20251019-02123 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/19/2025 17:49:51 | 10/21/2025 18:18:52 | 10/19/2025 23:49:51 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/19/2025 17:37:46 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 17:37:42 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251019-00001984 | Please check VSWR locally | Please check VSWR locally |  |  |  | API | 10/19/2025 17:49:51 | 10/20/2025 14:29:20 | 10/21/2025 18:18:46 |  |  | 10/21/2025 18:18:52 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000907 | PCM-20251019-00002012 | TT-20251019-02152 | Telecom | Region_6 | HSM0238 | HSM0238 | Transsmission | MW_HW_stuck | Reset FAN | Zeshan Ali Adnan | 10/19/2025 17:52:55 | 10/19/2025 19:29:31 | 10/20/2025 05:52:55 | FAN FAIL at HSM0238 on 10.1.170.10 @ Generator_SG | 10/19/2025 17:51:52 | Minor | FAN FAIL | FAN FAIL | 10/19/2025 17:46:46 | P2 | 2G | jizan | Generator_SG | TX NSA | HSM0238 | FLM_TE | [8 empty] | API | 10/19/2025 17:52:55 | 10/19/2025 18:22:41 | 10/19/2025 19:24:54 | 10/19/2025 19:25:00 |  | 10/19/2025 19:29:31 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000909 | PCM-20251019-00002017 | TT-20251019-02147 | Reference_telecom | Region_5 | MAK0674 | MAK0674 |  |  |  | Amjad Ali Muhammad Parves | 10/19/2025 17:53:59 | 10/19/2025 18:53:53 | 10/20/2025 05:53:59 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at MAK0674-G9-L8-L18-L21-NNR2.6-SBTS-P2-USF @ Sceco | 10/19/2025 17:21:26 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 17:21:17 | P2 | 2G | makkah | Sceco | 2G NSA | MAK0674 | FLM_TE |  |  | PCM-20251019-00002006 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/19/2025 17:53:59 | 10/19/2025 18:53:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000912 | PCM-20251019-00002021 | TT-20251019-02160 | Telecom | Region_4 | BLH0044 | BLH0044 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/19/2025 17:56:09 | 10/19/2025 17:57:18 | 10/20/2025 05:56:09 | Requested For MW HC For Link BLH0044-LTH0330 , Need to perform MW HC | 10/19/2025 17:55:09 | Minor | 113388 | LOF | 10/19/2025 17:55:09 | P2 | 2G | qunfuddah | Generator_DG | TX NSA | BLH0044-LTH0330 | FLM_TE | [5 empty] | Requested For MW HC For Link BLH0044-LTH0330 , Need to perform MW HC |  |  | API | 10/19/2025 17:56:09 | 10/19/2025 17:57:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000914 | PCM-20251019-00002027 | TT-20251019-02166 | Telecom | Region_4 | JDJZ0770 | JDJZ0770 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/19/2025 17:58:16 | 10/19/2025 18:10:39 | 10/20/2025 05:58:16 | Requested For MW HC For Link JDJZ0770-BLH0044 , Link counting performance errors | 10/19/2025 17:57:33 | Minor | 113388 | LOF | 10/19/2025 17:57:33 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0770-BLH0044 | FLM_TE | [5 empty] | Requested For MW HC For Link JDJZ0770-BLH0044 , Link counting performance errors |  |  | API | 10/19/2025 17:58:16 | 10/19/2025 18:10:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000917 | PCM-20251019-00002034 | TT-20251019-02172 | EM | Region_4 | JED1U6729 | JED6029 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/19/2025 18:01:12 | 10/19/2025 21:04:41 | 10/20/2025 06:01:12 | Rectifier Low battery voltage at JED1U6729-G9-L18-L21-SBTS-P3 @ Sceco | 10/19/2025 17:53:01 | Minor | 7103 | Rectifier Low battery voltage | 10/19/2025 17:52:56 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6729 | FLM_EM | [5 empty] | Rectifier Low battery voltage |  |  | API | 10/19/2025 18:01:12 | 10/19/2025 21:04:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000929 | PCM-20251019-00002068 | TT-20251019-02221 | EM | Region_1 | RSK2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/19/2025 18:19:17 | 10/20/2025 09:37:50 | 10/20/2025 06:19:17 | Door opening alarm at RSK2086-P2_SRAN @ Sceco | 10/19/2025 18:18:45 | Minor | 65101 | Door opening alarm | 10/19/2025 18:16:20 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2086 | FLM_EM | [8 empty] | API | 10/19/2025 18:19:17 | 10/20/2025 09:37:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000931 | PCM-20251019-00002072 | TT-20251019-02224 | Telecom | Region_4 | JED1MN2417 | JED2417 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/19/2025 18:21:20 | 10/20/2025 06:48:35 | 10/20/2025 00:21:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2417-NR2.6-P3 @ Sceco | 10/19/2025 18:20:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 18:20:13 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2417 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 18:21:20 | 10/19/2025 19:33:15 | 10/20/2025 06:48:22 |  |  | 10/20/2025 06:48:35 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019000935 | PCM-20251019-00002078 | TT-20251019-02232 | Telecom | Region_1 | QTF0491 | QTF0491 |  |  |  | Meraj Husain Idd Baksh | 10/19/2025 18:23:55 | 10/21/2025 16:53:01 | 10/20/2025 00:23:55 | Inter-BBU Port Failure at QTF0491-P2_SRAN @ Generator_SG | 10/19/2025 08:00:13 | Major | 26314 | Inter-BBU Port Failure | 10/19/2025 07:57:09 | P2 | SRAN | dammam | Generator_SG | 2G NSA | QTF0491 | FLM_TE | [8 empty] | API | 10/19/2025 18:23:55 | 10/19/2025 19:58:53 | 10/21/2025 16:52:56 | 10/21/2025 16:52:59 | 10/21/2025 16:53:01 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000938 | PCM-20251019-00002081 | TT-20251019-02235 | EM | Region_1 | RSK2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/19/2025 18:26:31 | 10/20/2025 09:37:50 | 10/20/2025 06:26:31 | Mains Failure at RSK2086-P2_SRAN @ Sceco | 10/19/2025 18:18:45 | Minor | 65109 | Mains Failure | 10/19/2025 18:16:20 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2086 | FLM_EM | [8 empty] | API | 10/19/2025 18:26:31 | 10/20/2025 09:37:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019000940 | PCM-20251019-00002095 | TT-20251019-02246 | Reference_telecom | Region_2 | RYQS2010 | RYQS2010 |  |  |  | Raise Ahmed Nisar Ahmed | 10/19/2025 18:37:53 | 10/20/2025 13:13:16 | 10/20/2025 06:37:53 | MW_LOF at RYQS2010_NE_1 @ Power Cube | 10/19/2025 14:42:33 | Minor | 1-631 | MW_LOF | 10/19/2025 14:37:30 | P3 | SRAN | riyadh | Power Cube | TX NSA | RYQS2010 | FLM_TE | [8 empty] | API | 10/19/2025 18:37:53 | 10/20/2025 13:13:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000941 | PCM-20251019-00002096 | TT-20251019-02247 | Reference_telecom | Region_2 | RYQS2015 | RYQS2015 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/19/2025 18:37:53 | 10/19/2025 21:25:02 | 10/20/2025 06:37:53 | MW_LOF at RYQS2015_NE_1 @ Power Cube | 10/19/2025 14:37:40 | Minor | 1-631 | MW_LOF | 10/19/2025 14:37:30 | P3 | SRAN | riyadh | Power Cube | TX NSA | RYQS2015 | FLM_TE | [8 empty] | API | 10/19/2025 18:37:53 | 10/19/2025 21:23:53 | 10/19/2025 21:24:55 |  |  | 10/19/2025 21:25:02 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000945 | PCM-20251019-00002113 | TT-20251019-02266 | Telecom | Region_4 | JED0271 | JED0271 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/19/2025 18:46:39 | 10/21/2025 17:12:52 | 10/20/2025 00:46:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/19/2025 18:45:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 18:45:33 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 18:46:39 | 10/19/2025 19:33:16 | 10/20/2025 06:48:44 |  |  | 10/20/2025 06:48:58 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000946 | PCM-20251019-00002115 | TT-20251019-02175 | EM | Region_1 | DAM0311 | DAM0311 | Transsmission | MW_HW_fault | Replace ODU | Shakeel Ahmed Hafeez Ameen | 10/19/2025 18:47:03 | 10/19/2025 19:36:12 | 10/20/2025 00:47:03 | 1(2G/3G/LTE) sites down under DAM0290-P2/R1_DM_HWBSC01 @ Sceco | 10/19/2025 18:00:55 | Major | 21825 | CSL Fault | 10/19/2025 18:00:52 | VIP | SRAN | dammam | Sceco_STB | 2G_3G_LTE SA | DAM0290-P2 | FLM_TE | DAM0311 | Observing PLA_MEMBER_DOWN & MW_LOF ,XPIC_LOS alarms active at DAM0311 | PCM-20251019-00002103 | Observing PLA_MEMBER_DOWN & MW_LOF ,XPIC_LOS alarms active at DAM0311 | Observing PLA_MEMBER_DOWN & MW_LOF ,XPIC_LOS alarms active at DAM0311 |  | sites down |  | API | 10/19/2025 18:47:03 | 10/19/2025 19:35:48 | 10/19/2025 19:36:04 |  |  | 10/19/2025 19:36:12 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000952 | PCM-20251019-00002144 | TT-20251019-02290 | Telecom | Region_6 | JIZ0094 | JIZ0094 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohammed Sideag Mohammed Ali | 10/19/2025 18:54:24 | 10/20/2025 01:16:38 | 10/20/2025 06:54:24 | ODU CPU / Cable Open at JIZ0094 on 10.154.169.66 @ Sceco | 10/19/2025 18:53:23 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/19/2025 18:45:59 | P3 | 2G | jizan | Sceco | TX NSA | JIZ0094 | FLM_TE | [8 empty] | API | 10/19/2025 18:54:24 | 10/20/2025 01:15:56 | 10/20/2025 01:16:18 |  |  | 10/20/2025 01:16:38 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000953 | PCM-20251019-00002149 | TT-20251019-02296 | Telecom | Region_1 | DMV0098 | DMV0098 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Mohamed Magdy Fouad Zayed | 10/19/2025 18:58:02 | 10/21/2025 04:07:49 | 10/20/2025 06:58:02 | ALD Maintenance Link Failure at DMV0098-P1_SRAN @ Sceco_STB | 10/19/2025 18:55:08 | Minor | 26541 | ALD Maintenance Link Failure | 10/19/2025 18:53:31 | P1 | SRAN | hafouf | Sceco_STB | 2G NSA | DMV0098 | FLM_TE | [8 empty] | API | 10/19/2025 18:58:02 | 10/19/2025 19:01:05 | 10/21/2025 04:07:40 |  |  | 10/21/2025 04:07:49 |  | Mohamed Magdy Fouad Zayed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000956 | PCM-20251019-00002153 | TT-20251019-02300 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/19/2025 18:59:35 | 10/20/2025 07:55:46 | 10/20/2025 06:59:35 | RF Unit Maintenance Link Failure at RIYB6158-DCU3 @ Sceco | 10/19/2025 18:54:25 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/19/2025 18:54:22 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/19/2025 18:59:35 | 10/20/2025 07:52:39 | 10/20/2025 07:55:37 |  |  | 10/20/2025 07:55:46 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000964 | PCM-20251019-00002176 | TT-20251019-02316 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | BSS_HW_fault | Replace GPS Antenna | Waseem Shahzad Ghulam Rasool | 10/19/2025 19:08:53 | 10/20/2025 07:54:46 | 10/20/2025 07:08:53 | RF Unit CPRI Interface Error at RIYB6158-DCU3 @ Sceco | 10/19/2025 19:02:16 | Minor | 26504 | RF Unit CPRI Interface Error | 10/19/2025 19:01:57 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/19/2025 19:08:53 | 10/20/2025 07:52:30 | 10/20/2025 07:54:27 |  |  | 10/20/2025 07:54:46 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000972 | PCM-20251019-00002193 | TT-20251019-01580 | Reference_telecom | Region_6 | TBL1M8324 | TBL2324 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/19/2025 19:15:13 | 10/19/2025 23:02:45 | 10/20/2025 07:15:13 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8324-G9-L8-SBTS-P3 @ Generator_DG | 10/19/2025 13:41:31 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 12:17:00 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8324 | FLM_TE |  | site was down and restored , kindly check | PCM-20251019-00002155 | Please check BSA0450 Down due to power issue | Please check BSA0450 Down due to power issue |  |  |  | API | 10/19/2025 19:15:13 | 10/19/2025 23:02:23 | 10/19/2025 23:02:30 |  |  | 10/19/2025 23:02:45 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000973 | PCM-20251019-00002196 | TT-20251019-01854 | Reference_telecom | Region_6 | TBL1M8332 | TBL2332 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/19/2025 19:16:33 | 10/19/2025 23:03:19 | 10/20/2025 07:16:33 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8332-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/19/2025 14:26:29 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 14:11:55 | P3 | 4G | bisha | Generator_SG | LTE NSA | TBL1M8332 | FLM_TE |  |  | PCM-20251019-00002157 | HUB: AQQ2433 Observing Node Rebooted , Kindly visit the site & check the issue as we are suspecting power issue. Kindly update TT under FLM & EM | HUB: AQQ2433 Observing Node Rebooted , Kindly visit the site & check the issue as we are suspecting power issue. Kindly update TT under FLM & EM |  |  |  | API | 10/19/2025 19:16:33 | 10/19/2025 23:02:24 | 10/19/2025 23:03:06 |  |  | 10/19/2025 23:03:19 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000974 | PCM-20251019-00002197 | TT-20251019-01851 | Reference_telecom | Region_6 | TBL1M8295 | TBL2295 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/19/2025 19:17:42 | 10/19/2025 23:03:02 | 10/20/2025 07:17:42 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8295-G9-L8-L18-L21-SBTS-P3 @ Generator_DG | 10/19/2025 14:19:14 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 14:10:06 | P3 | 4G | bisha | Generator_DG | LTE NSA | TBL1M8295 | FLM_TE |  | kindly check site was down and restored | PCM-20251019-00002156 | Please check BSA0450 Down due to power issue | Please check BSA0450 Down due to power issue |  |  |  | API | 10/19/2025 19:17:42 | 10/19/2025 23:02:25 | 10/19/2025 23:02:50 |  |  | 10/19/2025 23:03:02 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000990 | PCM-20251019-00002267 | TT-20251019-02364 | Telecom | Region_1 | DMH0099 | DMH0099 | Transsmission | MW_Problematic | Interference Issue | Muhammad Anwar Hussain Akhtar Hussain | 10/19/2025 19:37:25 | 10/23/2025 17:52:25 | 10/19/2025 21:37:25 | 9(2G) 10(3G) 9(LTE) sites down under HB1BSCH01 @ Generator_SG | 10/19/2025 19:23:22 | Emergency | 21825 | CSL Fault | 10/19/2025 19:23:19 | P3 | SRAN | hafr | Generator_SG | 2G_3G_LTE SA | DMH0606-P1-L800 LTE,DMH0102-P1-L800 LTE,SRA0012-P3-PC LTE,SMN0803-P2 2G_3G_LTE,SMN0802-P2 2G_3G_LTE,DMH0103-P1-HUB 3G,SMN0838-P2 3G,SMN0804-P2 3G | FLM_TE | DMH0099 | Dear Team, We are observing MW_RDI alarms flapping and HU issue at MW LINK DMH0099 DIR DMH2098 | PCM-20251019-00002240 | Dear Team, We are observing MW_RDI alarms flapping and HU issue at MW LINK DMH0099 DIR DMH2098 | Dear Team, We are observing MW_RDI alarms flapping and HU issue at MW LINK DMH0099 DIR DMH2098 |  | sites down |  | API | 10/19/2025 19:37:25 | 10/19/2025 21:20:30 | 10/20/2025 23:16:52 |  |  | 10/20/2025 23:17:05 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000993 | PCM-20251019-00002273 | TT-20251019-02384 | Telecom | Region_2 | RIYA6015 | RIYA6015 | Enviroment | Circuit Breaker/Owner | Change owner circuit breaker | Muhammad Waqas Ashraf Muhammad Ashraf | 10/19/2025 19:37:48 | 10/20/2025 11:38:00 | 10/20/2025 01:37:48 | BBU CPRI Interface Error at RIYA6015-P3_SRAN @ Sceco | 10/19/2025 19:34:59 | Major | 26234 | BBU CPRI Interface Error | 10/19/2025 19:32:23 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6015 | FLM_TE | [8 empty] | API | 10/19/2025 19:37:48 | 10/20/2025 08:57:49 | 10/20/2025 11:37:37 | 10/20/2025 11:37:39 | 10/20/2025 11:37:41 | 10/20/2025 11:38:00 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000997 | PCM-20251019-00002278 | TT-20251019-02389 | Telecom | Region_2 | RIYA2U6115 | RIYA6015 | Enviroment | Circuit Breaker/Owner | Change owner circuit breaker | Muhammad Waqas Ashraf Muhammad Ashraf | 10/19/2025 19:38:50 | 10/20/2025 11:37:31 | 10/20/2025 07:38:50 | RF Unit Maintenance Link Failure at RIYA2U6115-P3 @ Sceco | 10/19/2025 19:34:13 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/19/2025 19:32:32 | P3 | 2G | riyadh | Sceco | 2G NSA | RIYA2U6115 | FLM_TE | [8 empty] | API | 10/19/2025 19:38:50 | 10/20/2025 08:57:49 | 10/20/2025 11:37:09 | 10/20/2025 11:37:11 | 10/20/2025 11:37:13 | 10/20/2025 11:37:31 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019000999 | PCM-20251019-00002281 | TT-20251019-02390 | Telecom | Region_2 | RIYA2U6715 | RIYA6015 | Enviroment | Circuit Breaker/Owner | Change owner circuit breaker | Muhammad Waqas Ashraf Muhammad Ashraf | 10/19/2025 19:39:16 | 10/20/2025 11:36:56 | 10/20/2025 01:39:16 | Cell Unavailable at RIYA2U6715-P3 @ Sceco | 10/19/2025 19:34:08 | Major | 29240 | Cell Unavailable | 10/19/2025 19:32:34 | P3 | 4G | riyadh | Sceco | LTE SA | RIYA2U6715 | FLM_TE | [8 empty] | API | 10/19/2025 19:39:16 | 10/20/2025 08:57:50 | 10/20/2025 08:58:11 | 10/20/2025 08:58:17 | 10/20/2025 09:45:02 | 10/20/2025 11:36:56 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001013 | PCM-20251019-00002309 | TT-20251019-02415 | EM | Region_6 | BHAB1M8442 | BHAB2442 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/19/2025 19:49:10 | 10/20/2025 10:21:10 | 10/20/2025 07:49:10 | RECTIFIER MODULE FAILURE at BHAB1M8442-G9-L8-SBTS-P3-WBB-G3 @ Generator_SG | 10/19/2025 19:41:13 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/19/2025 19:41:03 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8442 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/19/2025 19:49:10 | 10/20/2025 10:21:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019001014 | PCM-20251019-00002311 | TT-20251019-02416 | EM | Region_6 | BCH1M8213 | BCH2213 |  |  |  | Fathy Mohamed | 10/19/2025 19:50:43 | 10/20/2025 01:13:16 | 10/20/2025 07:50:43 | RECTIFIER MAINS POWER FAILURE at BCH1M8213-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/19/2025 19:42:40 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/19/2025 19:42:36 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8213 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/19/2025 19:50:43 | 10/20/2025 01:13:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019001016 | PCM-20251019-00002320 | TT-20251019-02425 | Telecom | Region_4 | JED1M7188 | JED0188 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 19:57:58 | 10/21/2025 17:12:52 | 10/20/2025 01:57:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7188-P3-CA-L900-L800-SBTS @ Sceco | 10/19/2025 19:56:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 19:56:52 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7188 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 19:57:58 | 10/20/2025 16:09:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001019 | PCM-20251019-00002334 | TT-20251019-01910 | Reference_telecom | Region_6 | BRQ1M7084 | BRQ0084 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/19/2025 20:02:39 | 10/19/2025 22:35:58 | 10/20/2025 08:02:39 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BRQ1M7084-G9-NL8-L18-L21-SBTS-P2 @ Sceco | 10/19/2025 14:32:39 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 14:32:18 | P3 | 4G | mohail | Sceco | LTE NSA | BRQ1M7084 | FLM_TE |  |  | PCM-20251019-00002314 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:02:39 | 10/19/2025 22:35:08 | 10/19/2025 22:35:37 |  |  | 10/19/2025 22:35:58 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001020 | PCM-20251019-00002335 | TT-20251019-01889 | Reference_telecom | Region_4 | JED2857 | JED2857 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/19/2025 20:02:47 | 10/20/2025 10:05:56 | 10/20/2025 08:02:47 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2857-G9-L8-L18-L21-NR2.6-P3-SBTS @ Sceco | 10/19/2025 14:32:49 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 14:28:08 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2857 | FLM_TE |  |  | PCM-20251019-00002310 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:02:47 | 10/20/2025 10:05:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019001021 | PCM-20251019-00002336 | TT-20251019-02295 | Reference_telecom | Region_4 | JED0714 | JED0714 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/19/2025 20:02:55 | 10/22/2025 16:29:41 | 10/20/2025 02:02:55 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED0714-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/19/2025 17:00:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 16:57:17 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0714 | FLM_TE |  |  | PCM-20251019-00002308 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:02:55 | 10/22/2025 16:20:25 | 10/22/2025 16:29:35 | 10/22/2025 16:29:37 | 10/22/2025 16:29:41 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001023 | PCM-20251019-00002339 | TT-20251019-02294 | Reference_telecom | Region_4 | JED2030 | JED2030 |  |  |  | Mohammed Ramadan A Abu Abid | 10/19/2025 20:03:09 | 10/19/2025 22:21:15 | 10/20/2025 02:03:09 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2030-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/19/2025 17:01:35 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 16:56:32 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2030 | FLM_TE |  |  | PCM-20251019-00002291 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:03:09 | 10/19/2025 22:21:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001024 | PCM-20251019-00002340 | TT-20251019-02222 | Reference_telecom | Region_6 | SAB0062 | SAB0062 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/19/2025 20:03:22 | 10/20/2025 01:15:19 | 10/20/2025 08:03:22 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SAB0062-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/19/2025 16:20:54 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 16:18:46 | P2 | 2G | baish | Sceco | 2G NSA | SAB0062 | FLM_TE |  |  | PCM-20251019-00002306 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:03:22 | 10/19/2025 22:06:30 | 10/20/2025 01:14:56 |  |  | 10/20/2025 01:15:19 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001025 | PCM-20251019-00002342 | TT-20251019-02438 | Reference_telecom | Region_4 | JED6010 | JED6010 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/19/2025 20:05:42 | 10/21/2025 18:18:40 | 10/20/2025 08:05:42 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6010-DCU @ Sceco | 10/19/2025 17:05:12 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/19/2025 17:05:08 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6010 | FLM_TE | [8 empty] | API | 10/19/2025 20:05:42 | 10/20/2025 14:29:20 | 10/21/2025 18:18:34 |  |  | 10/21/2025 18:18:40 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001026 | PCM-20251019-00002345 | TT-20251019-02436 | Telecom | Region_4 | JED1M7375 | JED0375 | Equipment | BSS_HW_fault | Replace RRU | MALIK ATIF ZAMAN | 10/19/2025 20:07:23 | 10/22/2025 15:29:10 | 10/20/2025 08:07:23 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED1M7375-CA-L800-P3-SBTS @ Generator_SG | 10/19/2025 19:59:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 19:58:56 | P3 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7375 | FLM_TE |  |  | PCM-20251019-00002341 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:07:23 | 10/20/2025 16:09:52 | 10/22/2025 09:43:48 | 10/22/2025 09:43:50 | 10/22/2025 10:34:25 | 10/22/2025 15:29:10 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019001030 | PCM-20251019-00002349 | TT-20251019-02393 | Telecom | Region_4 | JED1MN2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 20:07:49 | 10/22/2025 11:18:43 | 10/20/2025 02:07:49 | BASE STATION HARDWARE PROBLEM (SFP Transceiver temperature too high) at JED1MN2979-NR2.6-P1-VIP @ Generator_SG | 10/19/2025 19:32:17 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/19/2025 19:32:13 | VIP | 5G | jeddah | Generator_SG | 5G NSA | JED1MN2979 | FLM_TE |  |  | PCM-20251019-00002282 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:07:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001034 | PCM-20251019-00002354 | TT-20251019-02324 | Reference_telecom | Region_4 | MAS0063 | MAS0063 |  |  |  | Khizer Hayat | 10/19/2025 20:08:41 | 10/19/2025 21:09:27 | 10/20/2025 02:08:41 | BASE STATION HARDWARE PROBLEM (Connection Unstable At 6Gbps) at MAS0063-GSM-UMTS-P3 (Ref::CRQ000000535034) @ Generator_SG | 10/19/2025 11:29:09 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/19/2025 11:29:00 | P3 | 2G | jeddah | Generator_SG | 2G NSA | MAS0063 | FLM_TE |  |  | PCM-20251019-00002183 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:08:41 | 10/19/2025 21:09:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251019001037 | PCM-20251019-00002359 | TT-20251019-02427 | Telecom | Region_4 | JED0993 | JED0993 |  |  |  | Abdullah Ahmad Mohammad Abdelsheekh | 10/19/2025 20:10:05 | 10/20/2025 11:07:31 | 10/20/2025 02:10:05 | 2(2G) 2(LTE) 1(5G) sites down under JED0993-P3,JED6029-P3/JED6029-P3 @ Sceco | 10/19/2025 19:54:53 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 19:54:52 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED6029-P3 2G_LTE,JED0993-P3 2G | FLM_TE | JED0993 | JED0993 Observing no issue at HUB , kindly check locally | PCM-20251019-00002338 | JED0993 Observing no issue at HUB , kindly check locally | JED0993 Observing no issue at HUB , kindly check locally |  | sites down |  | API | 10/19/2025 20:10:05 | 10/20/2025 10:36:19 | 10/20/2025 10:42:38 | 10/20/2025 10:42:42 | 10/20/2025 10:42:44 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001038 | PCM-20251019-00002360 | TT-20251019-02451 | Reference_telecom | Region_2 | JAM0548 | JAM0548 | Transsmission | MW_RSL_fading | Fading issue | Zakir Muhammad Yar Muhammad | 10/19/2025 20:10:21 | 10/21/2025 07:14:43 | 10/20/2025 08:10:21 | DemFail observed in JAM0548 towards 10.88.106.178 @ Sceco | 10/19/2025 08:12:09 | Minor |  | DemFail | 10/19/2025 08:10:07 | P2 | SRAN | dawadmi | Sceco | TX NSA | JAM0548 | FLM_TE | [8 empty] | API | 10/19/2025 20:10:21 | 10/20/2025 05:32:00 | 10/20/2025 20:42:29 |  |  | 10/21/2025 07:14:43 |  | Zakir Muhammad Yar Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001039 | PCM-20251019-00002364 | TT-20251019-02455 | Telecom | Region_1 | RYDM0062 | RYDM0062 | Equipment | SFP_BTS | Clean SFP | Shakeel Ahmed Hafeez Ameen | 10/19/2025 20:10:52 | 10/20/2025 09:06:53 | 10/20/2025 02:10:52 | NR Cell Unavailable at RYDM0062-P1-HUB_SRAN @ Sceco | 10/19/2025 20:04:15 | Major | 29841 | NR Cell Unavailable | 10/19/2025 20:02:42 | P1 | SRAN | dammam | Sceco | 5G SA | RYDM0062 | FLM_TE | [8 empty] | API | 10/19/2025 20:10:52 | 10/19/2025 21:49:55 | 10/20/2025 09:06:15 |  |  | 10/20/2025 09:06:53 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001045 | PCM-20251019-00002373 | TT-20251019-02180 | Reference_telecom | Region_6 | SHF1M7272 | SHF0272 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/19/2025 20:14:21 | 10/20/2025 01:34:37 | 10/20/2025 08:14:21 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at SHF1M7272-G9-L8-SBTS-P3 @ Generator_SG | 10/19/2025 16:14:59 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 16:06:10 | P3 | 4G | al harja | Generator_SG | LTE NSA | SHF1M7272 | FLM_TE |  |  | PCM-20251019-00002124 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:14:21 | 10/19/2025 23:48:41 | 10/20/2025 01:34:29 |  |  | 10/20/2025 01:34:37 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001047 | PCM-20251019-00002375 | TT-20251019-02444 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/19/2025 20:14:35 | 10/20/2025 10:21:11 | 10/20/2025 02:14:35 | 2(2G) 2(LTE) sites down under BHAB2103-P3,BHAB2091-P3/BHAB2091-P3 @ Generator_SG | 10/19/2025 20:03:41 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 20:03:37 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2091-P3 2G_LTE,BHAB2103-P3 2G_LTE | FLM_EM | BHAB2091 | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251019-00002365 | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/19/2025 20:14:35 | 10/20/2025 10:21:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251019001051 | PCM-20251019-00002382 | TT-20251019-02487 | Telecom | [7 empty] | 10/19/2025 20:20:10 | 10/19/2025 20:20:10 | 10/20/2025 00:20:10 | ETH_LOS at FRIY0001-1 @ Sceco | 10/19/2025 20:19:06 | Critical | 1-235 | ETH_LOS | 10/19/2025 20:18:38 | P3 | DWDM |  | Sceco | DWDM NSA | FRIY0001 | FLM_TE | [5 empty] | 0-1-C-4-K1EX10-3(Awqaf)-MAC:1 |  |  | API | 10/19/2025 20:20:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001053 | PCM-20251019-00002387 | TT-20251019-02445 | Telecom | Region_1 | HFF2747 | HFF2747 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/19/2025 20:25:39 | 10/20/2025 19:01:47 | 10/20/2025 00:25:39 | 2(2G) 2(3G) 2(LTE) sites down under HFF0933-P2,HFF2747-P1-SHOP/R1_HF_HWBSC01 @ Sceco | 10/19/2025 20:05:39 | Critical | 21825 | CSL Fault | 10/19/2025 20:05:36 | P1 | SRAN | hafouf | Sceco | 2G_3G_LTE SA | HFF0933-P2 2G_3G_LTE,HFF2747-P1-SHOP 2G_3G | FLM_EM | HFF2747 | Dear Team, Hub:- HFF2747 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251019-00002366 | Dear Team, Hub:- HFF2747 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- HFF2747 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/19/2025 20:25:39 | 10/20/2025 18:58:29 | 10/20/2025 19:01:39 |  |  | 10/20/2025 19:01:47 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001069 | PCM-20251019-00002417 | TT-20251019-02154 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/19/2025 20:44:34 | 10/21/2025 18:18:24 | 10/20/2025 02:44:34 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/19/2025 17:45:22 | Major | 7654 | CELL OPERATION DEGRADED | 10/19/2025 17:45:10 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251019-00002015 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:44:34 | 10/20/2025 14:29:21 | 10/21/2025 18:18:17 |  |  | 10/21/2025 18:18:24 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001073 | PCM-20251019-00002422 | TT-20251019-02498 | Reference_telecom | Region_4 | TAF1M4453 | TAF2453 | Equipment | BSS_HW_Stuck | Reset System Module | Ahmad Kamal Abdelmawla | 10/19/2025 20:45:02 | 10/20/2025 12:47:13 | 10/20/2025 02:45:02 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TAF1M4453-P3 @ Sceco | 10/19/2025 19:58:43 | Major | 7771 | WCDMA CELL OUT OF USE | 10/19/2025 19:56:36 | P3 | 3G | jeddah | Sceco | 3G SA | TAF1M4453 | FLM_TE |  |  | PCM-20251019-00002388 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:45:02 | 10/19/2025 20:55:06 | 10/20/2025 12:47:04 |  |  | 10/20/2025 12:47:13 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001074 | PCM-20251019-00002423 | TT-20251019-01955 | Telecom | Region_6 | NJR6014 | NJR6014 | Equipment | BSS_HW_Stuck | Reset RF Module | TALEH MUHAMMAD | 10/19/2025 20:45:17 | 10/19/2025 20:48:58 | 10/20/2025 02:45:17 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at NJR6014-P3 @ Sceco | 10/19/2025 16:47:08 | Major | 7607 | TRX OPERATION DEGRADED | 10/19/2025 16:46:40 | P3 | 2G | najran | Sceco | 2G_TRX NSA | NJR6014 | FLM_TE |  |  | PCM-20251019-00002177 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:45:17 | 10/19/2025 20:47:24 | 10/19/2025 20:47:42 |  |  | 10/19/2025 20:48:58 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001078 | PCM-20251019-00002428 | TT-20251019-02527 | Telecom | Region_4 | HAW1M8351 | HAW2351 |  |  |  | Rashid Shafique | 10/19/2025 20:47:02 | 10/20/2025 10:07:34 | 10/20/2025 02:47:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at HAW1M8351-P3-CA-L800 @ Sceco | 10/19/2025 20:46:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 20:46:09 | P2 | 4G | taif | Sceco | 5G_Cell SA | HAW1M8351 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 20:47:02 | 10/20/2025 10:07:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001079 | PCM-20251019-00002429 | TT-20251019-02189 | Reference_telecom | Region_4 | TAF1M4362 | TAF2362 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/19/2025 20:47:49 | 10/20/2025 19:42:54 | 10/20/2025 02:47:49 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TAF1M4362-P3 @ Sceco | 10/19/2025 17:42:05 | Major | 7771 | WCDMA CELL OUT OF USE | 10/19/2025 17:39:57 | P3 | 3G | taif | Sceco | 3G SA | TAF1M4362 | FLM_TE |  |  | PCM-20251019-00002051 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 20:47:49 | 10/20/2025 19:42:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001080 | PCM-20251019-00002430 | TT-20251019-02518 | Reference_telecom | Region_6 | ARF1M7899 | ARF0899 | Equipment | SW | Issue was solved after softaware configuration | Muhammad shafiq Muhammad Rasheed | 10/19/2025 20:50:47 | 10/20/2025 16:31:03 | 10/20/2025 08:50:47 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at ARF1M7899-P2-USF-SBTS @ Sceco | 10/19/2025 19:05:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 18:43:43 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | ARF1M7899 | FLM_TE |  |  | PCM-20251019-00002415 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/19/2025 20:50:47 | 10/19/2025 22:38:38 | 10/20/2025 16:30:38 | 10/20/2025 16:30:44 |  | 10/20/2025 16:31:03 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001082 | PCM-20251019-00002438 | TT-20251019-02537 | Reference_telecom | Region_1 | SMN0850 | SMN0850 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/19/2025 20:58:53 | 10/19/2025 21:20:32 | 10/20/2025 02:58:53 | RF Unit VSWR Threshold Crossed at SMN0850-P2-USF_SRAN @ Generator_DG | 10/19/2025 17:58:46 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/19/2025 17:58:31 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0850 | FLM_TE | [8 empty] | API | 10/19/2025 20:58:53 | 10/19/2025 21:20:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001089 | PCM-20251019-00002457 | TT-20251019-02545 | Telecom | Region_4 | ASQ1M3343 | ASQ0343 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/19/2025 21:12:02 | 10/20/2025 20:44:15 | 10/20/2025 01:12:02 | 1(3G) sites down under ASQ0343-P1-HUB-USF/ASQ1M3343-P1-HUB-USF @ Sceco | 10/19/2025 21:04:07 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/19/2025 21:03:27 | P1 | 3G | adam | Sceco | 3G SA | ASQ0343-P1-HUB-USF | FLM_TE | ASQ0343 | Results: DOWN SITE HUB ASQ0343-P1-HUB-USF ASQ0343 Summary: Hub: ASQ0343, Down Count: 1, Down Sites: ASQ0343-P1-HUB-USF Alarm Summary: ASQ0343 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 21:12:02 | 10/20/2025 09:16:37 | 10/20/2025 20:44:10 |  |  | 10/20/2025 20:44:15 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001095 | PCM-20251019-00002469 | TT-20251019-02311 | Reference_telecom | Region_4 | SQR0163 | SQR0163 | Equipment | SFP_BTS | Replace SFP | TOSIF AHMED - MUHAMMAD SHARIF | 10/19/2025 21:21:03 | 10/19/2025 23:12:04 | 10/20/2025 03:21:03 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at SQR1M7163-G9-U9-NL8-SBTS-P3 (Ref::TT-20251019-01994) | 10/19/2025 17:35:45 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 17:35:45 | P3 | 2G | adam | Generator_SG | 2G_3G_LTE SA | SQR1M7163-G9-U9-NL8-SBTS-P3 | FLM_TE |  |  | PCM-20251019-00002435 | site was down please handle with same RCA | TT-20251019-01994 ELEMENT NAME:SQR1M3163-P3 START DATE TIME:2025-10-19 17:02:09 IMPACT:3G SA DESCRIPTION:1(3G) sites down under SQR0163-P3 SQR1M3163-P3 @ Generator_SG OWNER:FLM |  |  |  | API | 10/19/2025 21:21:03 |  | 10/19/2025 23:11:52 |  |  | 10/19/2025 23:12:04 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001097 | PCM-20251019-00002471 | TT-20251019-02534 | Telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/19/2025 21:21:13 | 10/20/2025 21:24:43 | 10/20/2025 03:21:13 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MKYL0914-GSM-UMTS-P3 @ Sceco | 10/19/2025 20:52:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 20:52:21 | P3 | 2G | alaith | Sceco | 5G_Cell SA | MKYL0914 | FLM_TE |  |  | PCM-20251019-00002434 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 21:21:13 | 10/20/2025 21:24:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001103 | PCM-20251019-00002482 | TT-20251019-02452 | Reference_telecom | Region_6 | NMS1M7096 | NMS0096 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 21:28:11 | 10/20/2025 01:07:18 | 10/20/2025 03:28:11 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NMS1M7096-P3-CA-L800 @ Sceco | 10/19/2025 18:24:15 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 18:09:56 | P2 | 4G | namas | Sceco | LTE NSA | NMS1M7096 | FLM_TE |  |  | PCM-20251019-00002455 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:28:11 | 10/20/2025 01:01:03 | 10/20/2025 01:06:37 |  |  | 10/20/2025 01:07:18 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001106 | PCM-20251019-00002485 | TT-20251019-02542 | Reference_telecom | Region_6 | JIZ0156 | JIZ0156 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/19/2025 21:28:51 | 10/20/2025 01:37:29 | 10/20/2025 09:28:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0156-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/19/2025 19:05:36 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 19:05:24 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0156 | FLM_TE |  |  | PCM-20251019-00002465 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:28:51 | 10/20/2025 01:15:57 | 10/20/2025 01:37:12 |  |  | 10/20/2025 01:37:29 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001107 | PCM-20251019-00002486 | TT-20251019-02453 | Reference_telecom | Region_6 | ABBS1M8180 | ABBS2180 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 21:29:40 | 10/20/2025 01:08:02 | 10/20/2025 09:29:40 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABBS1M8180-G9-L800-L1800-SBTS-P3-WBB-G3 @ Generator_SG | 10/19/2025 18:24:14 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 18:10:27 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8180 | FLM_TE |  |  | PCM-20251019-00002454 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:29:40 | 10/20/2025 01:01:04 | 10/20/2025 01:07:32 |  |  | 10/20/2025 01:08:02 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001108 | PCM-20251019-00002487 | TT-20251019-02450 | Reference_telecom | Region_6 | NMS1M8184 | NMS2184 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 21:30:29 | 10/20/2025 01:09:08 | 10/20/2025 09:30:29 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NMS1M8184-G9-L8-SBTS-P3 @ Generator_SG | 10/19/2025 18:24:14 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 18:09:32 | P3 | 4G | namas | Generator_SG | LTE NSA | NMS1M8184 | FLM_TE |  |  | PCM-20251019-00002456 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:30:29 | 10/20/2025 01:01:04 | 10/20/2025 01:08:41 |  |  | 10/20/2025 01:09:08 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001109 | PCM-20251019-00002488 | TT-20251019-02541 | Reference_telecom | Region_6 | JIZ1M7244 | JIZ0244 | Transsmission | SFP_Transmission | Reset SFP | Zeshan Ali Adnan | 10/19/2025 21:31:13 | 10/19/2025 22:00:48 | 10/20/2025 03:31:13 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1M7244-G9-L8-L18-L21-SBTS-P1-DIA-HUB @ Sceco | 10/19/2025 19:03:27 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 19:03:20 | P1 | 4G | jizan | Sceco | LTE NSA | JIZ1M7244 | FLM_TE |  |  | PCM-20251019-00002466 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:31:13 | 10/19/2025 21:35:00 | 10/19/2025 21:58:47 |  |  | 10/19/2025 22:00:48 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001111 | PCM-20251019-00002491 | TT-20251019-02454 | Reference_telecom | Region_6 | ABBS1M8181 | ABBS2181 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/19/2025 21:31:56 | 10/20/2025 01:09:51 | 10/20/2025 09:31:56 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABBS1M8181-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/19/2025 18:24:22 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 18:10:29 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8181 | FLM_TE |  |  | PCM-20251019-00002453 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:31:56 | 10/20/2025 01:01:05 | 10/20/2025 01:09:23 |  |  | 10/20/2025 01:09:51 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001112 | PCM-20251019-00002492 | TT-20251019-02550 | Reference_telecom | Region_6 | BLG1M7228 | BLG0228 | Transsmission | MW_bad_Weather | Heavy Rain | Muhammad Ali | 10/19/2025 21:32:37 | 10/20/2025 02:53:21 | 10/20/2025 03:32:37 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BLG1M7228-P3-CA-L800 @ Generator_SG | 10/19/2025 19:08:19 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 19:08:07 | P3 | 4G | jizan | Generator_SG | LTE NSA | BLG1M7228 | FLM_TE |  |  | PCM-20251019-00002464 | Thanks to check | Thanks to check |  |  |  | API | 10/19/2025 21:32:37 | 10/19/2025 23:12:30 | 10/20/2025 02:53:09 |  |  | 10/20/2025 02:53:21 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001113 | PCM-20251019-00002494 | TT-20251019-02570 | Telecom | Region_4 | ASQ0343 | ASQ0343 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Mudassar Bashir Bashir Ahmad | 10/19/2025 21:34:36 | 10/22/2025 11:18:44 | 10/20/2025 03:34:36 | BASE STATION ANTENNA LINE PROBLEM at ASQ0343-GSM-UMTS-P1-HUB-USF @ Sceco | 10/19/2025 21:24:30 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/19/2025 21:24:20 | P1 | 2G | adam | Sceco | 2G NSA | ASQ0343 | FLM_TE |  |  | PCM-20251019-00002489 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/19/2025 21:34:36 | 10/20/2025 09:16:43 | 10/20/2025 15:28:00 | 10/20/2025 15:28:17 | 10/20/2025 15:28:34 | 10/20/2025 16:30:16 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001115 | PCM-20251019-00002496 | TT-20251019-02568 | Telecom | Region_4 | HBI1M7353 | HBI0353 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/19/2025 21:35:01 | 10/20/2025 09:16:54 | 10/20/2025 03:35:01 | 1(LTE) sites down under HBI0353-G9-L8-L18-SBTS-P3 @ Sceco | 10/19/2025 21:26:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/19/2025 21:26:54 | P3 | 4G | qunfuddah | Sceco | LTE SA | HBI0353-G9-L8-L18-SBTS-P3 | FLM_TE | HBI0353 | Results: DOWN SITE HUB HBI0353-G9-L8-L18-SBTS-P3 HBI0353 Summary: Hub: HBI0353, Down Count: 1, Down Sites: HBI0353-G9-L8-L18-SBTS-P3 Alarm Summary: HBI0353 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.98.0.180:8080] [URL:http://10.98.0.180:8080/NE3S/1.0/] | sites down |  | API | 10/19/2025 21:35:01 | 10/20/2025 09:16:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019001124 | PCM-20251019-00002509 | TT-20251019-02589 | Telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 21:53:39 | 10/21/2025 17:12:56 | 10/20/2025 03:53:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2074-G9-L8-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/19/2025 21:52:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 21:52:48 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2074 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 21:53:39 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251019001128 | PCM-20251019-00002522 | TT-20251019-02602 | Telecom | Region_4 | JED2179 | JED2179 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/19/2025 22:04:00 | 10/21/2025 17:12:55 | 10/20/2025 04:04:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2179-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/19/2025 22:03:04 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 22:02:55 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2179 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 22:04:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001130 | PCM-20251019-00002523 | TT-20251019-02604 | EM | Region_1 | HFF6022 | HFF6022 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/19/2025 22:05:32 | 10/20/2025 19:13:26 | 10/20/2025 10:05:32 | Fan Monitoring Failure at HFF6022-P3_SRAN @ Sceco | 10/19/2025 22:03:51 | Minor | 65121 | Fan Monitoring Failure | 10/19/2025 20:47:58 | P3 | SRAN | hafr | Sceco | 2G NSA | HFF6022 | FLM_EM | [8 empty] | API | 10/19/2025 22:05:32 | 10/20/2025 18:58:30 | 10/20/2025 19:13:18 |  |  | 10/20/2025 19:13:26 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251019001131 | PCM-20251019-00002534 | TT-20251019-02618 | Reference_telecom | Region_6 | ABH0014 | ABH0014 |  |  |  | Amir Sohail | 10/19/2025 22:19:57 | 10/20/2025 11:46:30 | 10/20/2025 10:19:57 | LagPortDown observed in ABH0014 towards 10.10.155.39 @ Sceco | 10/19/2025 10:20:50 | Minor |  | LagPortDown | 10/19/2025 10:19:30 | P2 | 2G | abha | Sceco | TX NSA | ABH0014 | FLM_TE | [8 empty] | API | 10/19/2025 22:19:57 | 10/20/2025 00:46:27 | 10/20/2025 11:32:26 | 10/20/2025 11:32:33 | 10/20/2025 11:46:30 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001132 | PCM-20251019-00002535 | TT-20251019-02619 | Reference_telecom | Region_6 | ABH0502 | ABH0502 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/19/2025 22:19:57 | 10/19/2025 23:48:42 | 10/20/2025 10:19:57 | Degrade observed in ABH0502 towards 10.10.155.35 @ Sceco | 10/19/2025 10:20:50 | Minor |  | Degrade | 10/19/2025 10:19:31 | P3 | 2G | abha | Sceco | TX NSA | ABH0502 | FLM_TE | [8 empty] | API | 10/19/2025 22:19:57 | 10/19/2025 23:48:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001142 | PCM-20251019-00002561 | TT-20251019-02642 | EM | Region_6 | BCH2213 | BCH2213 |  |  |  | Fathy Mohamed | 10/19/2025 22:47:03 | 10/20/2025 01:13:17 | 10/20/2025 04:47:03 | 1(2G/LTE) sites down under BCH2213-P3/BCH2213-P3 @ Generator_SG | 10/19/2025 22:38:43 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 22:38:39 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BCH2213-P3 | FLM_EM | BCH2213 | Results: DOWN SITE HUB BCH2213-P3 BCH2213 Summary: Hub: BCH2213, Down Count: 1, Down Sites: BCH2213-P3 Alarm Summary: BCH2213 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 22:47:03 | 10/20/2025 01:13:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001143 | PCM-20251019-00002566 | TT-20251019-02649 | Telecom | Region_4 | JED0909 | JED0909 | Equipment | BSS_HW_Stuck | Reset RF Module | Fawzi Muneer Fawzi Mahmoud | 10/19/2025 22:59:13 | 10/21/2025 17:12:57 | 10/20/2025 04:59:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0909-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/19/2025 22:58:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 22:58:03 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0909 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/19/2025 22:59:13 | 10/20/2025 06:51:31 | 10/20/2025 06:51:36 | 10/20/2025 06:51:38 | 10/20/2025 06:51:40 | 10/20/2025 20:26:01 |  | Fawzi Muneer Fawzi Mahmoud |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001149 | PCM-20251019-00002575 | TT-20251019-02623 | Reference_telecom | Region_2 | KHJ2M8304 | KHJ2304 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hakim Ullah Raif Ullah Jan | 10/19/2025 23:15:26 | 10/20/2025 07:53:46 | 10/20/2025 11:15:26 | Cell RX Channel Interference Noise Power Unbalanced at KHJ2M8304-P3-CA-L800 @ Sceco | 10/19/2025 19:25:41 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/19/2025 19:25:37 | P3 | 4G | riyadh | Sceco | 2G NSA | KHJ2M8304 | FLM_TE |  |  | PCM-20251019-00002540 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/19/2025 23:15:26 | 10/19/2025 23:54:58 | 10/20/2025 07:52:36 |  |  | 10/20/2025 07:53:46 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001151 | PCM-20251019-00002581 | TT-20251019-02668 | Reference_telecom | Region_4 | JED0608 | JED0608 |  |  |  | MALIK ATIF ZAMAN | 10/19/2025 23:24:30 | 10/20/2025 16:09:53 | 10/20/2025 11:24:30 | Degrade observed in JED0608_02 towards 10.3.225.36 @ Sceco | 10/19/2025 11:24:13 | Minor |  | Degrade | 10/19/2025 11:24:08 | P3 | 2G | jeddah | Sceco | TX NSA | JED0608 | FLM_TE | [8 empty] | API | 10/19/2025 23:24:30 | 10/20/2025 16:09:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001155 | PCM-20251019-00002588 | TT-20251019-02675 | Telecom | Region_1 | JBKH2M3093 | JBKH0093 |  |  |  | Rafiq Ahmed Elturifi | 10/19/2025 23:31:31 | 10/20/2025 06:34:25 | 10/20/2025 03:31:31 | 1(3G) sites down under JBKH0093-P1-HUB/JB1RNCH01 @ Generator_DG | 10/19/2025 23:23:18 | Critical | 22214 | NodeB Unavailable | 10/19/2025 23:23:15 | P1 | 3G | jubail | Generator_DG | 3G SA | JBKH0093-P1-HUB | FLM_TE | JBKH0093 | Results: DOWN SITE HUB JBKH0093-P1-HUB JBKH0093 Summary: Hub: JBKH0093, Down Count: 1, Down Sites: JBKH0093-P1-HUB Alarm Summary: JBKH0093 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 23:31:31 | 10/20/2025 06:34:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001156 | PCM-20251019-00002590 | TT-20251019-02614 | Telecom | Region_4 | RAB0366 | RAB0366 |  |  |  | Khizer Hayat | 10/19/2025 23:32:35 | 10/20/2025 13:50:44 | 10/20/2025 11:32:35 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0366-G9-L8-L18-L21-NR2.6-SBTS-P2-USF-WBB-G3 @ Sceco | 10/19/2025 22:12:39 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 22:12:32 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0366 | FLM_TE |  |  | PCM-20251019-00002532 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/19/2025 23:32:35 | 10/20/2025 13:50:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251019001157 | PCM-20251019-00002591 | TT-20251019-02595 | Telecom | Region_4 | JED0310 | JED0310 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/19/2025 23:33:28 | 10/20/2025 06:52:28 | 10/20/2025 11:33:28 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Generator_SG | 10/19/2025 21:54:23 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 21:54:13 | VIP | 2G | jeddah | Generator_SG | LTE NSA | JED0310 | FLM_TE |  |  | PCM-20251019-00002515 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/19/2025 23:33:28 | 10/20/2025 04:35:28 | 10/20/2025 06:52:12 |  |  | 10/20/2025 06:52:28 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001158 | PCM-20251019-00002592 | TT-20251019-02615 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/19/2025 23:34:11 | 10/20/2025 13:20:56 | 10/20/2025 05:34:11 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-CAP @ Sceco | 10/19/2025 22:13:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 22:13:07 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2279 | FLM_TE |  |  | PCM-20251019-00002533 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/19/2025 23:34:11 | 10/20/2025 11:00:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001161 | PCM-20251019-00002601 | TT-20251019-02685 | EM | Region_6 | BHAB2041 | BHAB2041 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/19/2025 23:47:03 | 10/20/2025 10:21:12 | 10/20/2025 05:47:03 | 1(2G/LTE) sites down under BHAB2041-P3/BHAB2041-P3 @ Generator_SG | 10/19/2025 23:38:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/19/2025 23:38:44 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2041-P3 | FLM_EM | BHAB2041 | Results: DOWN SITE HUB BHAB2041-P3 BHAB2041 Summary: Hub: BHAB2041, Down Count: 1, Down Sites: BHAB2041-P3 Alarm Summary: BHAB2041 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/19/2025 23:47:03 | 10/20/2025 10:21:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251019001164 | PCM-20251019-00002606 | TT-20251019-02695 | Telecom | Region_1 | HFR2U6102 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/19/2025 23:53:44 | 10/20/2025 00:26:16 | 10/20/2025 05:53:44 | GSM Local Cell Unusable at HFR2U6102-P3 @ Sceco | 10/19/2025 23:52:55 | Major | 28016 | GSM Local Cell Unusable | 10/19/2025 23:51:21 | P3 | 2G | hafr | Sceco | 2G SA | HFR2U6102 | FLM_TE | [8 empty] | API | 10/19/2025 23:53:44 | 10/20/2025 00:26:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019001165 | PCM-20251019-00002608 | TT-20251019-02698 | EM | Region_6 | MRD2071 | MRD2071 |  |  |  | Zia Ur Rahamn | 10/19/2025 23:57:35 | 10/20/2025 10:45:39 | 10/20/2025 11:57:35 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at MRD2071-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/19/2025 23:50:15 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/19/2025 23:49:11 | P3 | 2G | mohail | Generator_SG | 2G NSA | MRD2071 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/19/2025 23:57:35 | 10/20/2025 10:45:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000001 | PCM-20251020-00000003 | TT-20251018-00656 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/20/2025 00:01:13 | 10/20/2025 00:01:13 | 10/20/2025 06:01:13 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/18/2025 09:10:09 | Major | 1-12545 | LOCAL_FAULT | 10/18/2025 09:09:57 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE |  |  | PCM-20251019-00002332 | Fix the RX low power issue on DWDM from router end. | Fix the RX low power issue on DWDM from router end. |  |  |  | API | 10/20/2025 00:01:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000003 | PCM-20251020-00000005 | TT-20251019-02652 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/20/2025 00:01:50 | 10/20/2025 00:01:50 | 10/20/2025 06:01:50 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/19/2025 23:03:05 | Major | 1-12545 | LOCAL_FAULT | 10/19/2025 23:02:54 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE |  |  | PCM-20251019-00002587 | Fix the RX low power issue on DWDM from router end. | Fix the RX low power issue on DWDM from router end. |  |  |  | API | 10/20/2025 00:01:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000006 | PCM-20251020-00000008 | TT-20251019-02660 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 00:03:31 | 10/20/2025 19:42:55 | 10/20/2025 06:03:31 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TURY0826-P2 @ Sceco | 10/19/2025 23:12:48 | Major | 7607 | TRX OPERATION DEGRADED | 10/19/2025 23:12:44 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TURY0826 | FLM_TE |  |  | PCM-20251019-00002577 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 00:03:31 | 10/20/2025 19:42:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000010 | PCM-20251020-00000013 | TT-20251019-02696 | Telecom | Region_1 | RYHF2042 | RYHF2042 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 00:04:25 | 10/21/2025 05:43:49 | 10/20/2025 06:04:25 | 2(3G) sites down under RYHF2042-P2,RYHF2041-P2/HF1RNCH01 @ Generator_SG | 10/19/2025 23:52:02 | Major | 22214 | NodeB Unavailable | 10/19/2025 23:52:00 | P2 | SRAN | hafouf | Generator_SG | 3G SA | RYHF2041-P2 3G,RYHF2042-P2 3G | FLM_TE | RYHF2042 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : RYHF2042 DIR RYHF2041 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM | PCM-20251020-00000001 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : RYHF2042 DIR RYHF2041 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : RYHF2042 DIR RYHF2041 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM |  | sites down |  | API | 10/20/2025 00:04:25 | 10/21/2025 05:43:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000016 | PCM-20251020-00000028 | TT-20251020-00010 | Reference_telecom | Region_1 | DAM2M8135 | DAM2135 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/20/2025 00:21:11 | 10/20/2025 08:37:00 | 10/20/2025 12:21:11 | Cell RX Channel Interference Noise Power Unbalanced at DAM2M8135-L800-P2 @ Sceco | 10/19/2025 21:11:59 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/19/2025 21:11:56 | P2 | 4G | dammam | Sceco | 2G NSA | DAM2M8135 | FLM_TE |  |  | PCM-20251020-00000019 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/20/2025 00:21:11 | 10/20/2025 08:37:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000017 | PCM-20251020-00000029 | TT-20251019-00536 | Telecom | Region_2 | MJM0495 | MJM0495 |  |  |  | Muhammad Tahir Abdulrazzaq | 10/20/2025 00:24:16 | 10/20/2025 11:58:53 | 10/20/2025 06:24:16 | SPAN_LOSS_EXCEED_EOL at MJM0495_OCS @ Sceco_STB | 10/19/2025 05:30:52 | Major | 1-13629 | SPAN_LOSS_EXCEED_EOL | 10/19/2025 05:29:21 | P1 | SRAN | majma | Sceco_STB | DWDM NSA | MJM0495 | FLM_TE |  |  | PCM-20251019-00002328 | High losses on fiber. Perform OTDR and provide to FO to follow up with SEC | High losses on fiber. Perform OTDR and provide to FO to follow up with SEC |  |  |  | API | 10/20/2025 00:24:16 | 10/20/2025 11:58:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000018 | PCM-20251020-00000030 | TT-20251019-02632 | EM | Region_1 | JBL2377 | JBL2377 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Tahir Mahmood Hafiz Yar | 10/20/2025 00:25:00 | 10/20/2025 02:40:33 | 10/20/2025 06:25:00 | 1(2G/3G) sites down under JBL2377-P2/JB1RNCH01 @ Sceco | 10/19/2025 22:29:38 | Major | 22214 | NodeB Unavailable | 10/19/2025 22:29:36 | P2 | SRAN | jubail | Sceco | 3G SA | JBL2377-P2 | FLM_TE | JBL2377 | Results: DOWN SITE HUB JBL2377-P2 JBL2377 Summary: Hub: JBL2377, Down Count: 1, Down Sites: JBL2377-P2 Alarm Summary: JBL2377 No Active Alarm on HUB | PCM-20251020-00000015 | Effected modem muted PM Errors and RSL degradation observed on JBL2377-JBL2380 FLM Team please perform health check for the mentioned MW link | Effected modem muted PM Errors and RSL degradation observed on JBL2377-JBL2380 FLM Team please perform health check for the mentioned MW link |  | sites down |  | API | 10/20/2025 00:25:00 | 10/20/2025 00:31:30 | 10/20/2025 01:21:56 | 10/20/2025 01:21:59 |  | 10/20/2025 02:40:33 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000020 | PCM-20251020-00000042 | TT-20251020-00039 | Reference_telecom | Region_1 | SMN0795 | SMN0795 | Equipment | BSS_HW_Stuck | Reset RRU | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 00:36:51 | 10/20/2025 23:15:24 | 10/20/2025 12:36:51 | RF Unit RX Channel RTWP/RSSI Unbalanced at SMN0795-P1-HUB_SRAN @ Sceco | 10/19/2025 21:36:30 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/19/2025 21:36:25 | P1 | SRAN | hafr | Sceco | 2G NSA | SMN0795 | FLM_TE | [8 empty] | API | 10/20/2025 00:36:51 | 10/20/2025 01:30:57 | 10/20/2025 23:15:16 |  |  | 10/20/2025 23:15:24 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000022 | PCM-20251020-00000045 | TT-20251020-00038 | Telecom | Region_2 | RIY2M8925 | RIY2925 |  |  |  | Farmanullah Akbar Jan | 10/20/2025 00:40:02 | 10/20/2025 08:27:33 | 10/20/2025 04:40:02 | 1(LTE) sites down under RIY2925-P1-VIP-L800-L900 @ Generator_DG | 10/20/2025 00:33:06 | Critical | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/20/2025 00:31:30 | VIP | 4G | al kharj | Generator_DG | LTE SA | RIY2925-P1-VIP-L800-L900 | FLM_TE | RIY2925 | Results: DOWN SITE HUB RIY2925-P1-VIP-L800-L900 RIY2925 Summary: Hub: RIY2925, Down Count: 1, Down Sites: RIY2925-P1-VIP-L800-L900 Alarm Summary: RIY2925 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 00:40:02 | 10/20/2025 08:27:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000025 | PCM-20251020-00000049 | TT-20251020-00048 | Reference_EM | [7 empty] | 10/20/2025 00:43:35 | 10/20/2025 00:43:35 | 10/20/2025 12:43:35 | Minor Rec alarm at RIYA6110-P3_SRAN @ Sceco | 10/20/2025 00:33:31 | Minor | 65108 | Minor Rec alarm | 10/20/2025 00:33:27 | P3 | SRAN |  | Sceco | 2G NSA | RIYA6110 | FLM_EM | [8 empty] | API | 10/20/2025 00:43:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000026 | PCM-20251020-00000052 | TT-20251020-00053 | Telecom | Region_1 | HF1-ASG-01 | HF1 | Transsmission | MW_HW_stuck | Reset FAN | Mohamed Magdy Fouad Zayed | 10/20/2025 00:45:39 | 10/21/2025 04:07:34 | 10/20/2025 12:45:39 | Chassis Fail at HF1-ASG-01 @ Sceco_STB | 10/20/2025 00:45:06 | Minor | 101-2505202 | Chassis Fail | 10/20/2025 00:45:00 | P1 | IPRAN | hafouf | Sceco_STB | IPRAN NSA | HF1-ASG-01 | FLM_TE | [8 empty] | API | 10/20/2025 00:45:39 | 10/20/2025 00:47:57 | 10/21/2025 04:07:14 |  |  | 10/21/2025 04:07:34 |  | Mohamed Magdy Fouad Zayed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000027 | PCM-20251020-00000055 | TT-20251020-00056 | Telecom | Region_4 | TAF0312 | TAF0312 |  |  |  | Rashid Shafique | 10/20/2025 00:47:42 | 10/21/2025 17:12:57 | 10/20/2025 06:47:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF0312-G9-L8-L18-L21-NR2.6-P2-SBTS @ Sceco | 10/20/2025 00:46:50 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 00:46:44 | P2 | 2G | taif | Sceco | 5G_Cell SA | TAF0312 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 00:47:42 | 10/20/2025 10:07:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000030 | PCM-20251020-00000064 | TT-20251020-00050 | EM | Region_1 | HFB0027 | HFB0027 |  |  |  | Mohamed Magdy Fouad Zayed | 10/20/2025 00:55:18 | 10/20/2025 02:55:05 | 10/20/2025 06:55:18 | 1(3G/LTE) sites down under ARM0991-P2/HF1RNCH01 @ Power Cube | 10/20/2025 00:41:02 | Major | 22214 | NodeB Unavailable | 10/20/2025 00:41:00 | P2 | SRAN | hafouf | Generator_SG | 3G_LTE SA | ARM0991-P2 | FLM_TE | HFB0027 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : ARM0991 DIR HFB0027 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM | PCM-20251020-00000061 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : ARM0991 DIR HFB0027 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : ARM0991 DIR HFB0027 ,Kindly visit the link and perform the HC at mentioned link . Kindly update TT under FLM |  | sites down |  | API | 10/20/2025 00:55:18 | 10/20/2025 02:55:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000033 | PCM-20251020-00000072 | TT-20251020-00063 | Telecom | Region_1 | SKK-ASG-02 | SK1 |  |  |  | Syed Fawad Ali | 10/20/2025 01:02:10 | 10/20/2025 04:40:37 | 10/20/2025 13:02:10 | Chassis Fail at SKK-ASG-02 @ Sceco | 10/20/2025 01:01:49 | Minor | 101-2505202 | Chassis Fail | 10/20/2025 01:01:44 | P1 | IPRAN | sakaka | Sceco | IPRAN NSA | SKK-ASG-02 | FLM_TE | [8 empty] | API | 10/20/2025 01:02:10 | 10/20/2025 04:40:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000035 | PCM-20251020-00000073 | TT-20251020-00065 | EM | Region_5 | MK1_CORE | MK1 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/20/2025 01:02:11 | 10/20/2025 08:32:24 | 10/20/2025 07:02:11 | CORE ROOM DOOR ALARM at MK1_CORE-P1-VIP @ Sceco_STB | 10/20/2025 01:01:59 | Major | 7103 | CORE ROOM DOOR ALARM | 10/20/2025 01:01:50 | P1 | 4G | makkah | Sceco_STB | 2G NSA | MK1_CORE | FLM_EM | [5 empty] | CORE ROOM DOOR ALARM |  |  | API | 10/20/2025 01:02:11 | 10/20/2025 08:32:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000038 | PCM-20251020-00000080 | TT-20251020-00072 | Telecom | Region_1 | HF1-ASG-02 | HF1 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 01:09:55 | 10/21/2025 05:43:49 | 10/20/2025 13:09:55 | Chassis Fail at HF1-ASG-02 @ Sceco_STB | 10/20/2025 01:09:31 | Minor | 101-2505202 | Chassis Fail | 10/20/2025 01:09:28 | P1 | IPRAN | hafouf | Sceco_STB | IPRAN NSA | HF1-ASG-02 | FLM_TE | [8 empty] | API | 10/20/2025 01:09:55 | 10/21/2025 05:43:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000043 | PCM-20251020-00000094 | TT-20251020-00084 | EM | Region_6 | RYAB1M3650 | RYAB0650 | Equipment | BSS_HW_Stuck | Reset Air Scale | Ahmed Abdelaziz Hamid Abdelrahman | 10/20/2025 01:18:03 | 10/21/2025 20:40:02 | 10/20/2025 05:18:03 | 1(3G/LTE) sites down under RYAB0650-P1-HUB-USF/RYAB1M3650-P1-HUB-USF @ Sceco_STB | 10/20/2025 01:10:15 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/20/2025 01:09:37 | P1 | 3G | khamis mushyet | Sceco_STB | 3G_LTE SA | RYAB0650-P1-HUB-USF | FLM_EM | RYAB0650 | Results: DOWN SITE HUB RYAB0650-P1-HUB-USF RYAB0650 Summary: Hub: RYAB0650, Down Count: 1, Down Sites: RYAB0650-P1-HUB-USF Alarm Summary: RYAB0650 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 01:18:03 | 10/21/2025 18:29:08 | 10/21/2025 20:39:51 |  |  | 10/21/2025 20:40:02 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | EM | Zain |  | Running |  | OWS
Stuck | CM20251020000047 | PCM-20251020-00000103 | TT-20251020-00105 | EM | [7 empty] | 10/20/2025 01:22:19 | 10/20/2025 01:22:19 | 10/20/2025 13:22:19 | Minor Rec alarm at RIYD6022-P3_SRAN @ Sceco | 10/20/2025 01:13:28 | Minor | 65108 | Minor Rec alarm | 10/20/2025 01:12:06 | P3 | SRAN |  | Sceco | 2G NSA | RIYD6022 | FLM_EM | [8 empty] | API | 10/20/2025 01:22:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000072 | PCM-20251020-00000131 | TT-20251020-00131 | EM | Region_2 | RIY2109 | RIY2109 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/20/2025 01:28:00 | 10/20/2025 11:17:33 | 10/20/2025 13:28:00 | Mains Failure at RIY2109-P3_SRAN-PC @ Sceco | 10/20/2025 01:20:23 | Minor | 65109 | Mains Failure | 10/20/2025 01:18:07 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY2109 | FLM_EM | [8 empty] | API | 10/20/2025 01:28:00 | 10/20/2025 11:17:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000075 | PCM-20251020-00000134 | TT-20251020-00134 | Reference_telecom | Region_5 | MAK0254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/20/2025 01:29:01 | 10/20/2025 13:34:26 | 10/20/2025 13:29:01 | ReplaceableUnitProblem observed in MAK0254 towards 10.10.141.55 @ Sceco | 10/19/2025 13:30:40 | Minor |  | ReplaceableUnitProblem | 10/19/2025 13:28:47 | P1 | 2G | makkah | Sceco | TX NSA | MAK0254 | FLM_TE | [8 empty] | API | 10/20/2025 01:29:01 | 10/20/2025 13:34:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000079 | PCM-20251020-00000140 | TT-20251020-00102 | Reference_telecom | Region_1 | HFF2M7052 | HFF0052 |  |  |  | Mohamed Magdy Fouad Zayed | 10/20/2025 01:31:05 | 10/20/2025 02:55:05 | 10/20/2025 13:31:05 | Cell RX Channel Interference Noise Power Unbalanced at HFF2M7052-P2-L800 @ Sceco | 10/19/2025 22:20:56 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/19/2025 22:20:51 | P2 | 4G | hafouf | Sceco | 2G NSA | HFF2M7052 | FLM_TE |  |  | PCM-20251020-00000100 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/20/2025 01:31:05 | 10/20/2025 02:55:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000080 | PCM-20251020-00000141 | TT-20251020-00141 | Reference_telecom | Region_2 | RIY2415 | RIY2415 |  |  |  | Farmanullah Akbar Jan | 10/20/2025 01:31:05 | 10/20/2025 08:27:34 | 10/20/2025 13:31:05 | MW_LOF at RIY2415_NE_3_SDB @ Sceco | 10/19/2025 21:33:49 | Minor | 1-631 | MW_LOF | 10/19/2025 21:30:58 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY2415 | FLM_TE | [8 empty] | API | 10/20/2025 01:31:05 | 10/20/2025 08:27:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000093 | PCM-20251020-00000169 | TT-20251020-00171 | Reference_telecom | Region_6 | JEC1M7313 | JEC0313 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/20/2025 02:00:59 | 10/20/2025 02:56:38 | 10/20/2025 06:00:59 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JEC1M7313-P1-VIP-CA-L800 @ Generator_SG | 10/19/2025 23:52:21 | Critical | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 23:52:14 | VIP | 4G | baish | Generator_SG | LTE NSA | JEC1M7313 | FLM_TE |  |  | PCM-20251020-00000163 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/20/2025 02:00:59 | 10/20/2025 02:41:10 | 10/20/2025 02:56:16 |  |  | 10/20/2025 02:56:38 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000094 | PCM-20251020-00000170 | TT-20251020-00183 | Telecom | Region_4 | UKHA0344 | UKHA0344 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/20/2025 02:01:34 | 10/20/2025 11:08:10 | 10/20/2025 14:01:34 | ODU CPU / Cable Open at UKHA0344-2 on 10.154.113.41 @ Generator_SG | 10/20/2025 01:58:24 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/20/2025 02:00:19 | P1 | 2G | adam | Generator_SG | TX NSA | UKHA0344 | FLM_TE | [8 empty] | API | 10/20/2025 02:01:34 | 10/20/2025 11:08:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000100 | PCM-20251020-00000178 | TT-20251020-00062 | Telecom | Region_4 | JDMD0859 | JDMD0859 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/20/2025 02:05:05 | 10/20/2025 13:35:16 | 10/20/2025 08:05:05 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDMD0859-G9-L8-L18-L21-NR2.6-SBTS-P1-HUB @ Sceco_STB | 10/20/2025 00:55:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 00:55:11 | P1 | 2G | jeddah | Sceco_STB | 5G_Cell SA | JDMD0859 | FLM_TE |  |  | PCM-20251020-00000068 | RSSI alarm active at site, kindly check | RSSI alarm active at site, kindly check |  |  |  | API | 10/20/2025 02:05:05 | 10/20/2025 13:30:35 | 10/20/2025 13:35:10 |  |  | 10/20/2025 13:35:16 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000102 | PCM-20251020-00000181 | TT-20251020-00037 | Reference_telecom | Region_4 | JED0310 | JED0310 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 02:06:39 | 10/20/2025 06:53:19 | 10/20/2025 08:06:39 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Generator_SG | 10/19/2025 20:34:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/19/2025 20:34:12 | VIP | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0310 | FLM_TE |  |  | PCM-20251020-00000041 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/20/2025 02:06:39 | 10/20/2025 04:35:29 | 10/20/2025 06:52:55 |  |  | 10/20/2025 06:53:19 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000106 | PCM-20251020-00000191 | TT-20251020-00197 | Telecom | Region_1 | HFS2M1099 | HFS0099 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Mohamed Magdy Fouad Zayed | 10/20/2025 02:16:34 | 10/21/2025 04:08:06 | 10/20/2025 14:16:34 | ALD Maintenance Link Failure at HFS2M1099-P3 @ Generator_SG | 10/20/2025 02:13:48 | Minor | 26541 | ALD Maintenance Link Failure | 10/20/2025 02:12:16 | P3 | 2G | hafouf | Generator_SG | 2G NSA | HFS2M1099 | FLM_TE | [8 empty] | API | 10/20/2025 02:16:34 | 10/20/2025 02:54:17 | 10/21/2025 04:07:59 |  |  | 10/21/2025 04:08:06 |  | Mohamed Magdy Fouad Zayed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000109 | PCM-20251020-00000196 | TT-20251020-00204 | Telecom | Region_1 | SKK-ASG-01 | SK1 |  |  |  | Syed Fawad Ali | 10/20/2025 02:19:39 | 10/20/2025 04:40:38 | 10/20/2025 14:19:39 | Chassis Fail at SKK-ASG-01 @ Sceco | 10/20/2025 02:19:11 | Minor | 101-2505202 | Chassis Fail | 10/20/2025 02:19:06 | P1 | IPRAN | sakaka | Sceco | IPRAN NSA | SKK-ASG-01 | FLM_TE | [8 empty] | API | 10/20/2025 02:19:39 | 10/20/2025 04:40:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000114 | PCM-20251020-00000204 | TT-20251020-00191 | Telecom | Region_6 | ABH0029 | ABH0029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 02:25:37 | 10/20/2025 18:53:58 | 10/20/2025 08:25:37 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at ABH0029-P2 @ Sceco | 10/20/2025 02:06:15 | Major | 7607 | TRX OPERATION DEGRADED | 10/20/2025 02:06:11 | P2 | 2G | abha | Sceco | 2G_TRX NSA | ABH0029 | FLM_TE |  |  | PCM-20251020-00000184 | RET antenna having alarm, kindly check | RET antenna having alarm, kindly check |  |  |  | API | 10/20/2025 02:25:37 | 10/20/2025 13:38:57 | 10/20/2025 18:53:50 |  |  | 10/20/2025 18:53:58 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000115 | PCM-20251020-00000205 | TT-20251020-00208 | Reference_telecom | Region_4 | HJR1M7113 | HJR0113 |  |  |  | Khizer Hayat | 10/20/2025 02:27:17 | 10/20/2025 13:50:45 | 10/20/2025 08:27:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at HJR1M7113-G9-U9-NL8-NL18-SBTS-P1-VIP @ Sceco | 10/20/2025 00:21:58 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 00:21:51 | VIP | 4G | jeddah | Sceco | LTE NSA | HJR1M7113 | FLM_TE |  |  | PCM-20251020-00000199 | PLR alarm active at site, kindly check | PLR alarm active at site, kindly check |  |  |  | API | 10/20/2025 02:27:17 | 10/20/2025 13:50:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000124 | PCM-20251020-00000221 | TT-20251020-00233 | Telecom | Region_1 | JBL2380 | JBL2380 |  |  |  | Tahir Mahmood Hafiz Yar | 10/20/2025 02:37:43 | 10/20/2025 11:26:14 | 10/20/2025 14:37:43 | ODU CPU / Cable Open at JBL2380 on 10.248.33.26 @ Generator_SG | 10/20/2025 02:36:41 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/20/2025 02:30:03 | P2 | SRAN | jubail | Generator_SG | TX NSA | JBL2380 | FLM_TE | [8 empty] | API | 10/20/2025 02:37:43 | 10/20/2025 11:26:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000125 | PCM-20251020-00000223 | TT-20251020-00235 | Telecom | Region_1 | KBR2M7155 | KBR0155 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Imran Ali Yousaf | 10/20/2025 02:41:42 | 10/20/2025 11:32:03 | 10/20/2025 08:41:42 | Cell Unavailable at KBR2M7155-P3-L800 @ Sceco | 10/20/2025 02:40:55 | Major | 29240 | Cell Unavailable | 10/20/2025 02:40:27 | P3 | 4G | dammam | Sceco | LTE SA | KBR2M7155 | FLM_TE | [8 empty] | API | 10/20/2025 02:41:42 | 10/20/2025 09:01:13 | 10/20/2025 11:31:47 |  |  | 10/20/2025 11:32:03 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000130 | PCM-20251020-00000235 | TT-20251020-00244 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/20/2025 02:48:04 | 10/21/2025 22:26:18 | 10/20/2025 14:48:04 | SHELTER DOOR OPEN at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/20/2025 02:47:40 | Minor | 7103 | SHELTER DOOR OPEN | 10/20/2025 02:46:35 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | Manual | 10/20/2025 02:48:04 | 10/21/2025 22:26:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000135 | PCM-20251020-00000248 | TT-20251020-00255 | EM | Region_6 | QLW1M8370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/20/2025 02:54:47 | 10/21/2025 22:26:22 | 10/20/2025 14:54:47 | Tower light Alarm at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/20/2025 02:47:46 | Minor | 7103 | Tower light Alarm | 10/20/2025 02:46:36 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_EM | [5 empty] | Tower light Alarm |  |  | Manual | 10/20/2025 02:54:47 | 10/21/2025 22:26:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000138 | PCM-20251020-00000251 | TT-20251020-00258 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/20/2025 02:54:49 | 10/21/2025 22:26:22 | 10/20/2025 14:54:49 | AIRCON 1 FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/20/2025 02:47:40 | Minor | 7103 | AIRCON 1 FAILURE | 10/20/2025 02:46:35 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | Manual | 10/20/2025 02:54:49 | 10/21/2025 22:26:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000141 | PCM-20251020-00000262 | TT-20251020-00271 | Reference_telecom | Region_2 | DAR2854 | DAR2854 |  |  |  | Zakir Muhammad Yar Muhammad | 10/20/2025 03:03:34 | 10/20/2025 05:32:02 | 10/20/2025 15:03:34 | ETH_LOS at DAR2854_NE_1 @ Sceco | 10/20/2025 02:20:21 | Minor | 1-235 | ETH_LOS | 10/20/2025 02:20:08 | P2 | SRAN | al rass | Sceco | TX NSA | DAR2854 | FLM_TE | [8 empty] | API | 10/20/2025 03:03:34 | 10/20/2025 05:32:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000148 | PCM-20251020-00000279 | TT-20251020-00288 | EM | Region_6 | MKW1M8128 | MKW2128 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/20/2025 03:20:06 | 10/21/2025 19:55:41 | 10/20/2025 15:20:06 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at MKW1M8128-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/20/2025 03:12:00 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/20/2025 03:11:35 | P3 | 4G | Baha | Generator_SG | LTE NSA | MKW1M8128 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/20/2025 03:20:06 | 10/21/2025 19:55:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000149 | PCM-20251020-00000280 | TT-20251020-00289 | EM | Region_6 | BKR1M8214 | BKR2214 |  |  |  | Fathy Mohamed | 10/20/2025 03:20:06 | 10/20/2025 09:58:31 | 10/20/2025 15:20:06 | AIRCON 1 FAILURE at BKR1M8214-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/20/2025 03:13:01 | Minor | 7103 | AIRCON 1 FAILURE | 10/20/2025 03:11:47 | P3 | 4G | Baha | Generator_SG | LTE NSA | BKR1M8214 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/20/2025 03:20:06 | 10/20/2025 09:58:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000150 | PCM-20251020-00000281 | TT-20251020-00290 | EM | Region_6 | BHAB1M8126 | BHAB2126 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/20/2025 03:20:37 | 10/21/2025 19:55:45 | 10/20/2025 15:20:37 | SMOKE ALARM at BHAB1M8126-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/20/2025 03:13:19 | Minor | 7103 | SMOKE ALARM | 10/20/2025 03:12:05 | P3 | 4G | Baha | Sceco | LTE NSA | BHAB1M8126 | FLM_EM | [5 empty] | SMOKE ALARM |  |  | API | 10/20/2025 03:20:37 | 10/21/2025 19:55:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000155 | PCM-20251020-00000300 | TT-20251020-00310 | Reference_telecom | Region_4 | JED2569 | JED2569 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 03:32:29 | 10/20/2025 16:09:53 | 10/20/2025 15:32:29 | DemFail observed in JED2569 towards 10.21.75.82 @ Sceco | 10/19/2025 15:34:00 | Minor |  | DemFail | 10/19/2025 15:32:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2569 | FLM_TE | [8 empty] | API | 10/20/2025 03:32:29 | 10/20/2025 16:09:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000158 | PCM-20251020-00000312 | TT-20251020-00334 | EM | Region_6 | ABBS1M8095 | ABBS2095 |  |  |  | Muhammad Naeem Taj Din | 10/20/2025 03:41:18 | 10/20/2025 07:17:13 | 10/20/2025 15:41:18 | Smoke Alarm at ABBS1M8095-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/20/2025 03:34:06 | Minor | 7103 | Smoke Alarm | 10/20/2025 03:32:59 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8095 | FLM_EM | [5 empty] | Smoke Alarm |  |  | API | 10/20/2025 03:41:18 | 10/20/2025 07:17:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000160 | PCM-20251020-00000315 | TT-20251020-00336 | EM | Region_6 | RYAB0620 | RYAB0620 | Enviroment | Air Condition | Change Outdoor motor | Muhammad Bilal Niamat Ali | 10/20/2025 03:42:19 | 10/20/2025 20:09:58 | 10/20/2025 15:42:19 | AIRCON 2 FAILURE at RYAB0620-GSM-UMTS-P3-USF @ Generator_SG | 10/20/2025 03:34:05 | Minor | 7103 | AIRCON 2 FAILURE | 10/20/2025 03:34:01 | P3 | 2G | sulail | Generator_SG | 2G NSA | RYAB0620 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/20/2025 03:42:19 | 10/20/2025 16:33:56 | 10/20/2025 20:09:46 |  |  | 10/20/2025 20:09:58 |  | Muhammad Bilal Niamat Ali |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000161 | PCM-20251020-00000316 | TT-20251020-00339 | EM | Region_6 | RYAB0617 | RYAB0617 | Enviroment | Air Condition | Change indoor motor | Muhammad Bilal Niamat Ali | 10/20/2025 03:42:19 | 10/20/2025 20:09:35 | 10/20/2025 15:42:19 | AIRCON 2 FAILURE at RYAB0617-GSM-UMTS-P2-USF @ Sceco | 10/20/2025 03:33:56 | Minor | 7103 | AIRCON 2 FAILURE | 10/20/2025 03:33:49 | P2 | 2G | sulail | Sceco | 2G NSA | RYAB0617 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/20/2025 03:42:19 | 10/20/2025 16:33:57 | 10/20/2025 16:34:23 | 10/20/2025 16:34:28 | 10/20/2025 16:34:39 | 10/20/2025 20:09:35 |  | Muhammad Bilal Niamat Ali |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000163 | PCM-20251020-00000323 | TT-20251020-00328 | Reference_telecom | Region_5 | QUB1M8348 | QUB2348 |  |  |  | Amr Abdulla Ali Othman | 10/20/2025 03:48:23 | 10/20/2025 03:48:23 | 10/20/2025 15:48:23 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at QUB1M8348-G9-NL8-L18-SBTS-P2-USF @ Generator_DG | 10/20/2025 01:44:21 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 01:39:06 | P2 | 4G | makkah | Generator_DG | LTE NSA | QUB1M8348 | FLM_TE |  |  | PCM-20251020-00000309 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/20/2025 03:48:23 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000164 | PCM-20251020-00000325 | TT-20251020-00341 | Reference_telecom | Region_6 | JIZ0090 | JIZ0090 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/20/2025 03:48:39 | 10/20/2025 16:02:19 | 10/20/2025 15:48:39 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0090-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/20/2025 01:51:26 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 01:43:16 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0090 | FLM_TE |  |  | PCM-20251020-00000317 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/20/2025 03:48:39 | 10/20/2025 12:00:38 | 10/20/2025 16:02:07 |  |  | 10/20/2025 16:02:19 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000170 | PCM-20251020-00000332 | TT-20251020-00355 | Reference_telecom | Region_6 | DAR0916 | DAR0916 |  |  |  | Muhammad Ali | 10/20/2025 03:50:18 | 10/20/2025 10:43:33 | 10/20/2025 15:50:18 | NSP MW observing visibility down at 1 NE at DAR0916 due to power issue | 10/20/2025 03:40:08 | Minor | 113388 | LOF | 10/20/2025 03:40:10 | P2 | 2G | dair | Sceco | TX NSA | DAR0916(10.74.120.156) | FLM_TE | [8 empty] | API | 10/20/2025 03:50:18 | 10/20/2025 10:43:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000172 | PCM-20251020-00000338 | TT-20251020-00348 | Reference_telecom | Region_6 | JIZ0094 | JIZ0094 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/20/2025 03:52:46 | 10/20/2025 16:02:44 | 10/20/2025 15:52:46 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0094-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/20/2025 01:49:25 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 01:47:25 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0094 | FLM_TE |  |  | PCM-20251020-00000322 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/20/2025 03:52:46 | 10/20/2025 12:00:39 | 10/20/2025 16:02:31 |  |  | 10/20/2025 16:02:44 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000177 | PCM-20251020-00000344 | TT-20251020-00276 | Telecom | Region_1 | ARM0708 | ARM0708 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 03:57:23 | 10/21/2025 05:43:50 | 10/20/2025 09:57:23 | 1(3G) 1(LTE) sites down under ARM0747-P2,ARM0708-P3/HF1RNCH01 @ Sceco | 10/20/2025 03:06:30 | Major | 22214 | NodeB Unavailable | 10/20/2025 03:06:28 | P3 | SRAN | hafouf | Sceco | 3G_LTE SA | ARM0747-P2 LTE,ARM0708-P3 3G | FLM_TE | ARM0708 | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20251020-00000330 | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally | Dear FLM EM Team, We are not observing any issue at TX end. Kindly visit the site and check issue locally |  | sites down |  | API | 10/20/2025 03:57:23 | 10/21/2025 05:43:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000179 | PCM-20251020-00000349 | TT-20251020-00369 | Reference_telecom | Region_1 | SMN0851 | SMN0851 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 04:01:26 | 10/20/2025 04:22:04 | 10/20/2025 16:01:26 | RF Unit RX Channel RTWP/RSSI Unbalanced at SMN0851-P2-USF_SRAN @ Generator_SG | 10/20/2025 01:00:56 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/20/2025 01:00:51 | P2 | SRAN | hafr | Generator_SG | 2G NSA | SMN0851 | FLM_TE | [8 empty] | API | 10/20/2025 04:01:26 | 10/20/2025 04:22:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000181 | PCM-20251020-00000350 | TT-20251020-00367 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/20/2025 04:02:03 | 10/21/2025 18:17:53 | 10/20/2025 08:02:03 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/20/2025 03:50:08 | Critical | 7654 | CELL OPERATION DEGRADED | 10/20/2025 03:49:59 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251020-00000346 | Kindly check the VSWR alarm active at site | Kindly check the VSWR alarm active at site |  |  |  | API | 10/20/2025 04:02:03 | 10/20/2025 14:29:21 | 10/21/2025 18:17:44 |  |  | 10/21/2025 18:17:53 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000186 | PCM-20251020-00000360 | TT-20251020-00278 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/20/2025 04:09:30 | 10/21/2025 18:17:38 | 10/20/2025 10:09:30 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/20/2025 03:08:50 | Major | 7114 | CELL SERVICE PROBLEM | 10/20/2025 03:08:42 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251020-00000271 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/20/2025 04:09:30 | 10/20/2025 14:29:22 | 10/21/2025 18:17:31 |  |  | 10/21/2025 18:17:38 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000187 | PCM-20251020-00000362 | TT-20251020-00384 | Reference_telecom | Region_6 | BHMF0856 | BHMF0856 |  |  |  | SHAH KHALID | 10/20/2025 04:11:46 | 10/20/2025 10:48:05 | 10/20/2025 16:11:46 | NSP MW observing visibility down at 2 NE at BHMF0859 due to power issue | 10/20/2025 03:40:08 | Minor | 113388 | LOF | 10/20/2025 03:40:10 | P3 | 2G | makhwa | Sceco | TX NSA | BHMF0856(10.221.244.85), BHMF0859 (10.221.244.84) | FLM_TE | [8 empty] | API | 10/20/2025 04:11:46 | 10/20/2025 10:48:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000188 | PCM-20251020-00000363 | TT-20251020-00379 | Telecom | [7 empty] | 10/20/2025 04:12:02 | 10/20/2025 04:12:02 | 10/20/2025 10:12:02 | 1(LTE) sites down under BUR0335-P3_SRAN @ Generator_SG | 10/20/2025 04:03:51 | Major | 301 | NE Is Disconnected | 10/20/2025 04:03:49 | P3 | SRAN |  | Generator_SG | LTE SA | BUR0335-P3_SRAN | FLM_TE | BUR0335 | Results: DOWN SITE HUB BUR0335-P3_SRAN BUR0335 Summary: Hub: BUR0335, Down Count: 1, Down Sites: BUR0335-P3_SRAN Alarm Summary: BUR0335 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 04:12:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000190 | PCM-20251020-00000370 | TT-20251020-00392 | Reference_telecom | Region_6 | ABH0162 | ABH0162 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 04:21:35 | 10/20/2025 15:43:33 | 10/20/2025 16:21:35 | LossOfSignal observed in ABH0162_03 towards 10.10.155.44 @ Sceco_STB | 10/19/2025 16:21:23 | Minor |  | LossOfSignal | 10/19/2025 16:21:17 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0162 | FLM_TE | [8 empty] | API | 10/20/2025 04:21:35 | 10/20/2025 13:38:58 | 10/20/2025 14:20:46 | 10/20/2025 14:20:49 | 10/20/2025 14:22:54 | 10/20/2025 15:43:33 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000192 | PCM-20251020-00000372 | TT-20251020-00394 | EM | Region_6 | MKW2335 | MKW2335 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/20/2025 04:23:08 | 10/21/2025 17:13:01 | 10/20/2025 10:23:08 | TRX FAULTY (FF FF FF FF FF FF shared:S) at MKW2335-P3 @ Generator_SG | 10/20/2025 04:15:58 | Major | 7606 | TRX FAULTY | 10/20/2025 04:15:54 | P3 | 2G | Albaha | Generator_SG | 2G_Cell SA | MKW2335 | FLM_EM | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/20/2025 04:23:08 | 10/21/2025 16:56:30 | 10/21/2025 17:01:18 |  |  | 10/21/2025 17:01:32 |  | SHAH KHALID |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000194 | PCM-20251020-00000375 | TT-20251020-00398 | EM | Region_6 | BAH1M7012 | BAH0012 | Enviroment | SCECO_Failure | SCECO auto restored | Arif Ullah Shah | 10/20/2025 04:27:47 | 10/21/2025 00:22:34 | 10/20/2025 16:27:47 | AIRCON 2 FAILURE at BAH1M7012-G9-L8-SBTS-P3 @ Sceco | 10/20/2025 04:19:16 | Minor | 7103 | AIRCON 2 FAILURE | 10/20/2025 04:19:12 | P3 | 4G | Albaha | Sceco | LTE NSA | BAH1M7012 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/20/2025 04:27:47 | 10/20/2025 07:17:00 | 10/21/2025 00:22:24 |  |  | 10/21/2025 00:22:34 |  | Arif Ullah Shah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000195 | PCM-20251020-00000378 | TT-20251020-00404 | Reference_telecom | Region_6 | MRD0108 | MRD0108 |  |  |  | Fawad Khan | 10/20/2025 04:32:26 | 10/20/2025 09:09:53 | 10/20/2025 16:32:26 | NSP MW observing visibility down at 1 NE at MRD2079 due to power issue | 10/20/2025 03:40:08 | Minor | 113388 | LOF | 10/20/2025 03:40:10 | P2 | 2G | mohail | Sceco | TX NSA | MRD2079(10.221.243.101) | FLM_TE | [8 empty] | API | 10/20/2025 04:32:26 | 10/20/2025 09:09:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000198 | PCM-20251020-00000381 | TT-20251020-00412 | Reference_telecom | Region_6 | TNM0727 | TNM0727 | Transsmission | SFP_Transmission | Replace SFP | Fawad Khan | 10/20/2025 04:36:03 | 10/20/2025 22:58:44 | 10/20/2025 16:36:03 | DemFail observed in TNM0727_02 towards 10.221.247.85 @ Sceco | 10/19/2025 16:35:51 | Minor |  | DemFail | 10/19/2025 16:35:27 | P2 | 2G | mohail | Sceco | TX NSA | TNM0727 | FLM_TE | [8 empty] | API | 10/20/2025 04:36:03 | 10/20/2025 09:09:54 | 10/20/2025 22:58:06 |  |  | 10/20/2025 22:58:44 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000199 | PCM-20251020-00000385 | TT-20251020-00402 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Ahmad Mostafa Hamouda Ibrahem | 10/20/2025 04:39:07 | 10/21/2025 17:12:58 | 10/20/2025 10:39:07 | BASE STATION SERVICE PROBLEM (RF Module configuring failed) at JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/20/2025 04:25:32 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 04:25:26 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0500 | FLM_TE |  |  | PCM-20251020-00000377 | Kindly check as HW alarm active at site | Kindly check as HW alarm active at site |  |  |  | API | 10/20/2025 04:39:07 | 10/20/2025 15:25:50 | 10/20/2025 16:12:50 | 10/20/2025 16:12:53 | 10/20/2025 16:12:58 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000203 | PCM-20251020-00000389 | TT-20251020-00413 | Telecom | Region_4 | JED6021 | JED6021 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/20/2025 04:43:16 | 10/21/2025 18:17:03 | 10/20/2025 16:43:16 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6021-G9-L1800-L2100-SBTS-P3 @ Generator_SG | 10/20/2025 04:31:32 | Minor | 7114 | CELL SERVICE PROBLEM | 10/20/2025 04:31:20 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED6021 | FLM_TE |  |  | PCM-20251020-00000382 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/20/2025 04:43:16 | 10/20/2025 14:29:23 | 10/21/2025 18:16:57 |  |  | 10/21/2025 18:17:03 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000204 | PCM-20251020-00000390 | TT-20251020-00424 | Reference_telecom | Region_6 | BAH0313 | BAH0313 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 10/20/2025 04:43:48 | 10/20/2025 10:50:03 | 10/20/2025 16:43:48 | Degrade observed in BAH0313 towards 10.221.240.104 @ Sceco | 10/19/2025 16:45:46 | Minor |  | Degrade | 10/19/2025 16:43:43 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0313 | FLM_TE | [8 empty] | API | 10/20/2025 04:43:48 | 10/20/2025 10:48:06 | 10/20/2025 10:49:46 |  |  | 10/20/2025 10:50:03 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000205 | PCM-20251020-00000391 | TT-20251020-00425 | Reference_telecom | Region_6 | BAH0017 | BAH0017 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 10/20/2025 04:43:48 | 10/20/2025 10:52:35 | 10/20/2025 16:43:48 | Degrade observed in BAH0017 towards 10.221.240.103 @ Sceco | 10/19/2025 16:45:44 | Minor |  | Degrade | 10/19/2025 16:43:43 | P1 | 2G | Albaha | Sceco | TX NSA | BAH0017 | FLM_TE | [8 empty] | API | 10/20/2025 04:43:48 | 10/20/2025 10:48:06 | 10/20/2025 10:52:11 |  |  | 10/20/2025 10:52:35 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000207 | PCM-20251020-00000396 | TT-20251020-00429 | Reference_telecom | Region_5 | MAK0686 | MAK0686 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/20/2025 04:51:01 | 10/21/2025 19:57:01 | 10/20/2025 16:51:01 | ReplaceableUnitProblem observed in MAK0686 towards 10.10.143.200 @ Sceco | 10/19/2025 16:51:20 | Minor |  | ReplaceableUnitProblem | 10/19/2025 16:50:32 | P2 | 2G | makkah | Sceco | TX NSA | MAK0686 | FLM_TE | [8 empty] | API | 10/20/2025 04:51:01 | 10/21/2025 19:57:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000208 | PCM-20251020-00000398 | TT-20251020-00431 | Reference_telecom | Region_6 | QIS0031 | QIS0031 |  |  |  | Muhammad Ali | 10/20/2025 04:52:35 | 10/20/2025 10:43:34 | 10/20/2025 16:52:35 | LagPortDown observed in QIS0031_2 towards 10.74.121.177 @ Sceco | 10/19/2025 16:52:20 | Minor |  | LagPortDown | 10/19/2025 16:52:10 | P1 | 2G | jizan | Sceco | TX NSA | QIS0031 | FLM_TE | [8 empty] | API | 10/20/2025 04:52:35 | 10/20/2025 10:43:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000211 | PCM-20251020-00000405 | TT-20251020-00436 | Reference_telecom | Region_6 | FIF0047 | FIF0047 | Transsmission | MW_HW_stuck | Reset ODU | Muhammad Ali | 10/20/2025 05:02:24 | 10/21/2025 17:10:26 | 10/20/2025 17:02:24 | LagPortDown observed in FIF0047_01 towards 10.74.120.162 @ Sceco | 10/19/2025 17:02:16 | Minor |  | LagPortDown | 10/19/2025 17:02:08 | P2 | 2G | dair | Sceco | TX NSA | FIF0047 | FLM_TE | [8 empty] | API | 10/20/2025 05:02:24 | 10/20/2025 10:43:34 | 10/21/2025 17:09:59 |  |  | 10/21/2025 17:10:26 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000213 | PCM-20251020-00000407 | TT-20251020-00438 | Reference_telecom | Region_6 | QIS0031 | QIS0031 |  |  |  | Muhammad Ali | 10/20/2025 05:02:54 | 10/20/2025 10:43:35 | 10/20/2025 17:02:54 | LagPortDown observed in QIS0031_04 towards 10.74.120.161 @ Sceco | 10/19/2025 17:02:32 | Minor |  | LagPortDown | 10/19/2025 17:02:25 | P1 | 2G | jizan | Sceco | TX NSA | QIS0031 | FLM_TE | [8 empty] | API | 10/20/2025 05:02:54 | 10/20/2025 10:43:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000219 | PCM-20251020-00000416 | TT-20251020-00451 | Reference_telecom | Region_4 | MKSH0170 | MKSH0170 |  |  |  | Riasat Ali Allah Baksh | 10/20/2025 05:17:57 | 10/20/2025 21:24:49 | 10/20/2025 11:17:57 | BCCH MISSING at MKSH0170-P2-USF(Ref:TT-20251019-02509) @ Generator_SG | 10/20/2025 03:02:12 | Major | 7767 | BCCH MISSING | 10/20/2025 03:02:08 | P2 | 2G | makkah | Generator_SG | 2G_Cell SA | MKSH0170 | FLM_TE | [5 empty] | 07 |  |  | API | 10/20/2025 05:17:57 | 10/20/2025 21:24:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000225 | PCM-20251020-00000455 | TT-20251020-00497 | Reference_telecom | Region_2 | RIYD6013 | RIYD6013 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/20/2025 05:46:48 | 10/20/2025 09:46:01 | 10/20/2025 11:46:48 | RF Unit VSWR Threshold Crossed at RIYD6013-P3_SRAN @ Sceco | 10/20/2025 01:19:43 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/20/2025 01:15:17 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYD6013 | FLM_TE | [8 empty] | API | 10/20/2025 05:46:48 | 10/20/2025 09:46:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000226 | PCM-20251020-00000463 | TT-20251020-00505 | Reference_telecom | Region_2 | RIYD6111 | RIYD6111 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable Connector | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/20/2025 05:46:54 | 10/23/2025 14:52:01 | 10/20/2025 11:46:54 | RF Unit VSWR Threshold Crossed at RIYD6111-P2_SRAN @ Sceco | 10/20/2025 01:17:51 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/20/2025 01:13:50 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYD6111 | FLM_TE | [8 empty] | API | 10/20/2025 05:46:54 | 10/20/2025 09:46:01 | 10/23/2025 14:45:54 |  |  | 10/23/2025 14:52:01 |  | Ali Raza Abdi Syed Muhammad Taqi Abdi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000228 | PCM-20251020-00000481 | TT-20251020-00525 | Telecom | Region_4 | JED6103 | JED6103 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Mohamed Farag Abdelbary | 10/20/2025 05:51:59 | 10/21/2025 18:16:18 | 10/20/2025 17:51:59 | ODU CPU / Cable Open at JED6103 on 10.1.169.114 @ Sceco | 10/20/2025 05:51:09 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/20/2025 05:25:26 | P3 | 2G | jeddah | Sceco | TX NSA | JED6103 | FLM_TE | [8 empty] | API | 10/20/2025 05:51:59 | 10/20/2025 14:29:24 | 10/21/2025 18:16:12 |  |  | 10/21/2025 18:16:18 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000232 | PCM-20251020-00000503 | TT-20251020-00151 | Telecom | Region_5 | MAK1M9386 | MAK0386 |  |  |  | Mustafa Mohammed Badawi Khalil | 10/20/2025 06:03:13 | 10/20/2025 16:33:16 | 10/20/2025 18:03:13 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure;Default System Time) at MAK1M9386-G9-L8-L18-L21-SBTS-P2 @ Generator_SG | 10/20/2025 01:33:37 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/19/2025 03:02:23 | P2 | 4G | makkah | Generator_SG | LTE NSA | MAK1M9386 | FLM_TE |  |  | PCM-20251020-00000166 | Thanks to check | Thanks to check |  |  |  | API | 10/20/2025 06:03:13 | 10/20/2025 16:33:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000237 | PCM-20251020-00000510 | TT-20251020-00550 | Telecom | Region_2 | RIYA2U6760A | RIYA6060 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/20/2025 06:13:42 | 10/20/2025 08:57:52 | 10/20/2025 12:13:42 | RF Out of Service at RIYA2U6760A-P3 @ Sceco | 10/20/2025 06:08:41 | Major | 29248 | RF Out of Service | 10/20/2025 06:07:07 | P3 | 4G | riyadh | Sceco | 2G SA | RIYA2U6760A | FLM_TE | [8 empty] | API | 10/20/2025 06:13:42 | 10/20/2025 08:57:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000244 | PCM-20251020-00000525 | TT-20251020-00563 | Telecom | Region_1 | DAM6012 | DAM6012 |  |  |  | Meraj Husain Idd Baksh | 10/20/2025 06:23:01 | 10/20/2025 08:06:06 | 10/20/2025 18:23:01 | DCU Optical Module Transmit/Receive Fault at DAM6012-DCU3 @ Sceco | 10/20/2025 06:10:25 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/20/2025 06:15:50 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6012 | FLM_TE | [8 empty] | API | 10/20/2025 06:23:01 | 10/20/2025 08:06:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000245 | PCM-20251020-00000526 | TT-20251020-00567 | EM | [7 empty] | 10/20/2025 06:24:34 | 10/20/2025 06:24:34 | 10/20/2025 10:24:34 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/20/2025 06:23:01 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/20/2025 06:22:53 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/20/2025 06:24:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000247 | PCM-20251020-00000530 | TT-20251020-00554 | Telecom | Region_4 | JED1MN2910 | JED2910 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 06:30:04 | 10/20/2025 11:00:30 | 10/20/2025 12:30:04 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/20/2025 06:13:56 | Major | 7114 | CELL SERVICE PROBLEM | 10/20/2025 06:13:45 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE |  |  | PCM-20251020-00000515 | Kindly check below alarms active at site, support to clear | Kindly check below alarms active at site, support to clear |  |  |  | API | 10/20/2025 06:30:04 | 10/20/2025 11:00:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000254 | PCM-20251020-00000548 | TT-20251020-00591 | Reference_telecom | Region_4 | JED2108 | JED2108 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 06:48:53 | 10/20/2025 11:00:30 | 10/20/2025 18:48:53 | ReplaceableUnitMissing observed in JED2108 towards 10.21.75.227 @ Sceco | 10/19/2025 18:49:34 | Minor |  | ReplaceableUnitMissing | 10/19/2025 18:48:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2108 | FLM_TE | [8 empty] | API | 10/20/2025 06:48:53 | 10/20/2025 11:00:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000257 | PCM-20251020-00000557 | TT-20251020-00600 | Telecom | Region_6 | TLT0722 | TLT0722 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/20/2025 06:59:40 | 10/20/2025 08:09:58 | 10/20/2025 18:59:40 | ODU CPU / Cable Open at TLT0722-2 on 10.89.224.45 @ Sceco | 10/20/2025 06:51:10 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/20/2025 06:58:16 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0722 | FLM_TE | [8 empty] | API | 10/20/2025 06:59:40 | 10/20/2025 08:09:36 | 10/20/2025 08:09:50 |  |  | 10/20/2025 08:09:58 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000258 | PCM-20251020-00000559 | TT-20251020-00599 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 07:03:13 | 10/20/2025 16:09:53 | 10/20/2025 13:03:13 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/20/2025 06:52:03 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/20/2025 06:51:56 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251020-00000556 | Kindly check the Antenna line alarm active at site | Kindly check the Antenna line alarm active at site |  |  |  | API | 10/20/2025 07:03:13 | 10/20/2025 16:09:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000265 | PCM-20251020-00000578 | TT-20251020-00622 | Reference_EM | Region_1 | DMJR0662 | DMJR0662 | Enviroment | Rectifier Module | Adding module due to load issue | Emad Mahmoud Ahmed Mohamed | 10/20/2025 07:27:05 | 10/22/2025 18:04:16 | 10/20/2025 19:27:05 | low fuel alarm at DMJR0662-P2_SRAN @ Generator_SG | 10/20/2025 07:16:36 | Minor | 65115 | low fuel alarm | 10/20/2025 07:16:33 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJR0662 | FLM_EM | [8 empty] | API | 10/20/2025 07:27:05 | 10/20/2025 12:01:21 | 10/22/2025 18:04:03 |  |  | 10/22/2025 18:04:16 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000267 | PCM-20251020-00000583 | TT-20251020-00631 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/20/2025 07:29:39 | 10/20/2025 08:06:07 | 10/20/2025 19:29:39 | RF Unit Maintenance Link Failure at DAM6027-DCU1 @ Sceco | 10/20/2025 07:24:46 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/20/2025 07:24:31 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/20/2025 07:29:39 | 10/20/2025 08:06:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000271 | PCM-20251020-00000593 | TT-20251020-00089 | Telecom | Region_2 | RIY0340-ZRi02-1-CSG-02 | RIY0340 | Transsmission | IPRAN_Fluctuation | Reset port | DILSHAD ALI ABDUL HAMEED | 10/20/2025 07:34:10 | 10/21/2025 01:56:23 | 10/20/2025 19:34:10 | Bad Package Error Rising at RIY0340-ZRi02-1-CSG-02 @ Sceco | 10/20/2025 01:14:10 | Minor | 101-2501403 | Bad Package Error Rising | 10/20/2025 01:14:02 | VIP | IPRAN | riyadh | Sceco | IPRAN NSA | RIY0340-ZRi02-1-CSG-02 | FLM_TE |  |  | PCM-20251020-00000576 | port gi0-11-3 To_OptiX RTN 380AX_RIY0340_NE_5_V_10GE_P3 | port gi0-11-3 To_OptiX RTN 380AX_RIY0340_NE_5_V_10GE_P3 |  |  |  | API | 10/20/2025 07:34:10 | 10/20/2025 23:51:55 | 10/20/2025 23:55:19 | 10/20/2025 23:55:22 | 10/21/2025 00:21:38 | 10/21/2025 01:56:23 |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000273 | PCM-20251020-00000595 | TT-20251020-00229 | Telecom | Region_4 | JED1MN0973 | JED0973 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 07:34:19 | 10/22/2025 06:36:25 | 10/20/2025 13:34:19 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED1MN0973-NR2.6-P2 @ Sceco | 10/20/2025 02:28:06 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 02:27:56 | P2 | 5G | taif | Sceco | 5G NSA | JED1MN0973 | FLM_TE |  |  | PCM-20251020-00000217 | Anchor site JED0085 is down, Please close TT with restoration RC. | Anchor site JED0085 is down, Please close TT with restoration RC. |  |  |  | API | 10/20/2025 07:34:19 | 10/20/2025 08:35:56 | 10/22/2025 06:36:13 |  |  | 10/22/2025 06:36:25 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000275 | PCM-20251020-00000596 | TT-20251020-00645 | EM | Region_6 | ABDB1M8238 | ABDB2238 |  |  |  | Aziz Ul Haq Umar Gul | 10/20/2025 07:34:49 | 10/20/2025 07:49:33 | 10/20/2025 19:34:49 | RECTIFIER MAINS POWER FAILURE at ABDB1M8238-L800-SBTS-P3 @ Sceco | 10/20/2025 07:28:43 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/20/2025 07:26:31 | P3 | 4G | derb | Sceco | LTE NSA | ABDB1M8238 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/20/2025 07:34:49 | 10/20/2025 07:49:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000279 | PCM-20251020-00000611 | TT-20251020-00356 | Telecom | Region_6 | ABBS2107 | ABBS2107 | Equipment | BSS_HW_Stuck | Reset Air Scale | Fawad Khan | 10/20/2025 07:42:19 | 10/20/2025 09:13:49 | 10/20/2025 13:42:19 | BCF NOTIFICATION (FF FF FF FF FF FF) at ABBS2107-P3 @ Sceco | 10/20/2025 03:43:19 | Major | 7602 | BCF NOTIFICATION | 10/20/2025 03:43:07 | P3 | 2G | namas | Sceco | 2G NSA | ABBS2107 | FLM_TE |  |  | PCM-20251020-00000333 | Request to check GPS Hw, cable connectivity & relocating the GPS where sky visibility will show excellent. | Request to check GPS Hw, cable connectivity & relocating the GPS where sky visibility will show excellent. |  |  |  | API | 10/20/2025 07:42:19 | 10/20/2025 09:09:55 | 10/20/2025 09:12:47 |  |  | 10/20/2025 09:13:49 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000283 | PCM-20251020-00000617 | TT-20251020-00647 | Telecom | Region_6 | ABDB2238 | ABDB2238 |  |  |  | AKHTAR ALI MASIN ZADA | 10/20/2025 07:44:55 | 10/20/2025 07:44:55 | 10/20/2025 13:44:55 | BASE STATION CONNECTIVITY PROBLEM (OMU signaling connection failure in Abis interface) at ABDB2238-P3 @ Sceco | 10/20/2025 07:28:39 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 07:28:50 | P3 | 2G | derb | Sceco | 2G NSA | ABDB2238 | FLM_TE |  |  | PCM-20251020-00000598 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/20/2025 07:44:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000284 | PCM-20251020-00000618 | TT-20251020-00613 | Reference_telecom | Region_6 | JIZ1M7258 | JIZ0258 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/20/2025 07:47:03 | 10/21/2025 12:52:57 | 10/20/2025 19:47:03 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1M7258-P3-NCA-L800-SBTS @ Sceco | 10/20/2025 05:17:03 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 05:16:52 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1M7258 | FLM_TE |  |  | PCM-20251020-00000570 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/20/2025 07:47:03 | 10/20/2025 14:20:29 | 10/21/2025 12:52:35 |  |  | 10/21/2025 12:52:57 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000285 | PCM-20251020-00000619 | TT-20251020-00663 | Reference_telecom | Region_1 | KBR2U6710 | KBR6010 |  |  |  | Meraj Husain Idd Baksh | 10/20/2025 07:47:36 | 10/20/2025 08:06:07 | 10/20/2025 19:47:36 | Cell RX Channel Interference Noise Power Unbalanced at KBR2U6710-P3-L1800-CA @ Sceco | 10/20/2025 04:44:02 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/20/2025 04:44:00 | P3 | 4G | dammam | Sceco | 2G NSA | KBR2U6710 | FLM_TE |  |  | PCM-20251020-00000615 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/20/2025 07:47:36 | 10/20/2025 08:06:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000287 | PCM-20251020-00000621 | TT-20251020-00667 | Reference_telecom | Region_6 | BHAB2442 | BHAB2442 |  |  |  | SHAH KHALID | 10/20/2025 07:49:15 | 10/20/2025 10:48:08 | 10/20/2025 19:49:15 | ReplaceableUnitMissing observed in BHAB2442_02 towards 10.221.243.55 @ Generator_SG | 10/19/2025 19:50:49 | Minor |  | ReplaceableUnitMissing | 10/19/2025 19:49:00 | P3 | 2G | Albaha | Generator_SG | TX NSA | BHAB2442 | FLM_TE | [8 empty] | API | 10/20/2025 07:49:15 | 10/20/2025 10:48:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000294 | PCM-20251020-00000639 | TT-20251020-00665 | Telecom | Region_4 | JED0909 | JED0909 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 08:00:43 | 10/20/2025 10:05:59 | 10/20/2025 12:00:43 | 2(2G) 1(LTE) 1(5G) sites down under JED0909-P2,JED2574-P1/JED2574-P1 @ Sceco | 10/20/2025 07:42:45 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 07:42:42 | P2 | 2G | jeddah | Sceco | 2G_LTE SA | JED2574-P1 2G_LTE,JED0909-P2 2G | FLM_TE | JED0909 | Scattered sites: JED0909, JED2574 We are observing LOS TO AIRSCALE kindly send team to check locally | PCM-20251020-00000626 | Scattered sites: JED0909, JED2574 We are observing LOS TO AIRSCALE kindly send team to check locally | Scattered sites: JED0909, JED2574 We are observing LOS TO AIRSCALE kindly send team to check locally |  | sites down |  | API | 10/20/2025 08:00:43 | 10/20/2025 10:05:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000298 | PCM-20251020-00000644 | TT-20251020-00673 | Telecom | Region_4 | JED2178 | JED2178 | Equipment | BSS_HW_fault | Replace RF Module | Ahmad Mostafa Hamouda Ibrahem | 10/20/2025 08:02:32 | 10/23/2025 19:32:22 | 10/20/2025 14:02:32 | 1(2G) sites down under JED2178-P3/JED2178-P3 @ Sceco | 10/20/2025 07:54:12 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 07:54:10 | P3 | 2G | jeddah | Sceco | 2G SA | JED2178-P3 | FLM_TE | JED2178 | Results: DOWN SITE HUB JED2178-P3 JED2178 Summary: Hub: JED2178, Down Count: 1, Down Sites: JED2178-P3 Alarm Summary: JED2178 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 08:02:32 | 10/23/2025 11:28:18 | 10/23/2025 13:30:24 | 10/23/2025 13:30:45 | 10/23/2025 13:31:06 | 10/23/2025 19:32:22 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000299 | PCM-20251020-00000645 | TT-20251020-00682 | Reference_telecom | Region_6 | BHAB0883 | BHAB0883 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/20/2025 08:03:12 | 10/20/2025 11:06:28 | 10/20/2025 20:03:12 | LossOfSignal observed in BHAB0883_03 towards 10.221.242.150 @ Sceco | 10/19/2025 20:03:03 | Minor |  | LossOfSignal | 10/19/2025 20:03:00 | P3 | 2G | makhwa | Sceco | TX NSA | BHAB0883 | FLM_TE | [8 empty] | API | 10/20/2025 08:03:12 | 10/20/2025 11:05:10 | 10/20/2025 11:06:08 |  |  | 10/20/2025 11:06:28 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000307 | PCM-20251020-00000660 | TT-20251020-00695 | EM | Region_5 | MINA_HWBSC01 | HM1 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Aly Abdelkarim Abdel Rahman | 10/20/2025 08:10:57 | 10/20/2025 22:51:32 | 10/20/2025 12:10:57 | AIRCONDITION #1 FAULT ALARM EQUIPMENT ROOM at MINA_HWBSC01 @ Sceco_STB | 10/20/2025 08:10:34 | Critical | 65348 | AIRCONDITION #1 FAULT ALARM EQUIPMENT ROOM | 10/20/2025 08:10:32 | P1 | BSC | makkah | Sceco_STB | 2G NSA | MINA_HWBSC01 | FLM_EM | [8 empty] | API | 10/20/2025 08:10:57 | 10/20/2025 08:32:25 | 10/20/2025 22:46:10 | 10/20/2025 22:46:14 | 10/20/2025 22:46:29 | 10/20/2025 22:51:32 |  | Mohamed Aly Abdelkarim Abdel Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000308 | PCM-20251020-00000661 | TT-20251020-00696 | EM | Region_5 | MINA_HWBSC01 | HM1 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Aly Abdelkarim Abdel Rahman | 10/20/2025 08:10:57 | 10/20/2025 09:23:48 | 10/20/2025 12:10:57 | AIRCONDITION #2 FAULT ALARM EQUIPMENT ROOM at MINA_HWBSC01 @ Sceco_STB | 10/20/2025 08:10:34 | Critical | 65349 | AIRCONDITION #2 FAULT ALARM EQUIPMENT ROOM | 10/20/2025 08:10:32 | P1 | BSC | makkah | Sceco_STB | 2G NSA | MINA_HWBSC01 | FLM_EM | [8 empty] | API | 10/20/2025 08:10:57 | 10/20/2025 08:32:25 | 10/20/2025 08:34:49 | 10/20/2025 08:35:06 | 10/20/2025 08:47:28 | 10/20/2025 09:23:48 |  | Mohamed Aly Abdelkarim Abdel Rahman |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000309 | PCM-20251020-00000662 | TT-20251020-00697 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 08:10:58 | 10/20/2025 16:09:54 | 10/20/2025 20:10:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/20/2025 08:10:14 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 08:10:02 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 08:10:58 | 10/20/2025 16:09:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000313 | PCM-20251020-00000675 | TT-20251015-01034 | Reference_telecom | Region_4 | JED0888 | JED0888 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 08:19:02 | 10/20/2025 16:09:54 | 10/20/2025 20:19:02 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at JED0888-1-10.10.185.18 | 10/14/2025 08:09:51 | Minor |  | LOF | 10/14/2025 08:09:51 | P2 | 2G | jeddah | Sceco | TX NSA | JED0888-1-10.10.185.18 | FLM_TE |  |  | PCM-20251020-00000630 | Dear FLM team, approve | Dear FLM team, approve |  |  |  | API | 10/20/2025 08:19:02 | 10/20/2025 16:09:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000315 | PCM-20251020-00000679 | TT-20250929-02320 | MW_HC | Region_4 | JED0187 | JED0187 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 08:20:22 | 10/20/2025 16:09:55 | 10/20/2025 20:20:22 | Nokia MW HC_P2 Observing Modem Down at JED0187-3-JED0953 | 09/29/2025 16:35:37 | Minor |  | LOF | 09/29/2025 16:35:37 | P1 | 2G | jeddah | Sceco | TX NSA | JED0187-3-JED0953 | FLM_TE |  |  | PCM-20251020-00000635 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/20/2025 08:20:22 | 10/20/2025 16:09:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000317 | PCM-20251020-00000684 | TT-20251013-02084 | MW_HC | Region_4 | JED0171 | JED0171 |  |  |  | Mohammed Ramadan A Abu Abid | 10/20/2025 08:21:35 | 10/20/2025 08:35:56 | 10/20/2025 20:21:35 | Nokia MW HC_P2 Observing Modem Down at JED0171_03-JED0085 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0171_03-JED0085 | FLM_TE |  |  | PCM-20251020-00000629 | Dear FLM team, approve | Dear FLM team, approve |  |  |  | API | 10/20/2025 08:21:35 | 10/20/2025 08:35:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000318 | PCM-20251020-00000685 | TT-20251020-00716 | Reference_telecom | Region_1 | HFS2M3067 | HFS0067 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 08:21:49 | 10/21/2025 05:43:50 | 10/20/2025 20:21:49 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M3067-P3 @ Generator_SG | 10/20/2025 05:21:40 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/20/2025 05:21:28 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M3067 | FLM_TE | [8 empty] | API | 10/20/2025 08:21:49 | 10/21/2025 05:43:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000319 | PCM-20251020-00000686 | TT-20250929-02759 | MW_HC | Region_4 | JED2592 | JED2592 | Equipment | CB_BTS | Switch on CB on Rectifier | Khaled Mohammad Abdallah | 10/20/2025 08:22:17 | 10/21/2025 23:25:03 | 10/20/2025 20:22:17 | As per bo request Nokia MW HC FLM need to check link JED2592-JED2041 V ODU down at JED2592 | 09/29/2025 18:58:10 | Minor | 113388 | LOF | 09/29/2025 18:58:07 | P3 | 2G | jeddah | Sceco | TX NSA | ED2592-JED2041 | FLM_TE |  |  | PCM-20251020-00000632 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/20/2025 08:22:17 | 10/20/2025 23:22:32 | 10/21/2025 23:24:27 |  |  | 10/21/2025 23:25:03 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000324 | PCM-20251020-00000695 | TT-20251020-00610 | Reference_telecom | Region_5 | HAJ0247 | HAJ0247 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/20/2025 08:28:38 | 10/24/2025 01:40:11 | 10/20/2025 20:28:38 | IP Clock Link Failure at HAJ0247-P3_SRAN @ Sceco | 10/20/2025 04:20:21 | Minor | 26263 | IP Clock Link Failure | 10/20/2025 04:13:10 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ0247 | FLM_TE |  |  | PCM-20251020-00000601 | PM Errors and RSL degradation observed on MW link HAJ0247 <> MAK0184 | PM Errors and RSL degradation observed on MW link HAJ0247 <> MAK0184 |  |  |  | API | 10/20/2025 08:28:38 | 10/24/2025 01:40:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000332 | PCM-20251020-00000706 | TT-20251020-00734 | EM | Region_1 | ARM0735 | ARM0735 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/20/2025 08:34:11 | 10/20/2025 16:33:59 | 10/20/2025 20:34:11 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/20/2025 08:27:50 | Minor | 1589 | AC Overfrequency | 10/20/2025 08:27:50 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/20/2025 08:34:11 | 10/20/2025 10:00:59 | 10/20/2025 16:33:50 |  |  | 10/20/2025 16:33:59 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000337 | PCM-20251020-00000715 | TT-20251020-00746 | Reference_telecom | Region_4 | JED0198 | JED0198 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 08:38:50 | 10/20/2025 08:38:50 | 10/20/2025 20:38:50 | Degrade observed in JED0198 - 5 towards 10.10.182.129 @ Sceco | 10/19/2025 20:38:39 | Minor |  | Degrade | 10/19/2025 20:38:34 | P1 | 2G | jeddah | Sceco | TX NSA | JED0198 | FLM_TE | [8 empty] | API | 10/20/2025 08:38:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000338 | PCM-20251020-00000716 | TT-20251020-00747 | Reference_telecom | Region_4 | JED2063 | JED2063 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 08:38:51 | 10/20/2025 08:38:51 | 10/20/2025 20:38:51 | LagPortDown observed in JED2063 towards 10.10.182.130 @ Sceco | 10/19/2025 20:38:42 | Minor |  | LagPortDown | 10/19/2025 20:38:36 | P2 | 2G | jeddah | Sceco | TX NSA | JED2063 | FLM_TE | [8 empty] | API | 10/20/2025 08:38:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000339 | PCM-20251020-00000718 | TT-20251020-00686 | Telecom | Region_4 | MLJI0377 | MLJI0377 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/20/2025 08:39:20 | 10/21/2025 19:32:50 | 10/20/2025 14:39:20 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at MLJI0377-GSM-UMTS-P2-USF @ Sceco | 10/20/2025 08:00:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 08:00:04 | P2 | 2G | qunfuddah | Sceco | 5G_Cell SA | MLJI0377 | FLM_TE |  |  | PCM-20251020-00000648 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/20/2025 08:39:20 | 10/20/2025 13:58:43 | 10/21/2025 19:32:39 |  |  | 10/21/2025 19:32:50 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000347 | PCM-20251020-00000743 | TT-20251020-00757 | Telecom | Region_4 | JED2619 | JED2619 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 08:50:51 | 10/21/2025 00:54:02 | 10/20/2025 14:50:51 | 2(2G) 2(LTE) 2(5G) sites down under JED2592-P3,JED2619-P3 @ Sceco | 10/20/2025 08:41:13 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 08:41:09 | P3 | 2G | jeddah | Sceco | 5G SA | JED2619-NR3.5-P3 5G,JED2592-NR2.6-P3 5G | FLM_TE | JED2619 | HUB: JED2592, JED2619 We are observing LOS TO AIRSCALE kindly check locally | PCM-20251020-00000740 | HUB: JED2592, JED2619 We are observing LOS TO AIRSCALE kindly check locally | HUB: JED2592, JED2619 We are observing LOS TO AIRSCALE kindly check locally |  | sites down |  | API | 10/20/2025 08:50:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000348 | PCM-20251020-00000747 | TT-20251020-00775 | Telecom | Region_1 | DAM2M8072 | DAM2072 | Enviroment | Circuit Breaker/Rectifier | Change rectifier main breaker | Meraj Husain Idd Baksh | 10/20/2025 08:51:52 | 10/20/2025 10:53:17 | 10/20/2025 14:51:52 | Cell Unavailable at DAM2M8072-L800-L1800-CA-P3 @ Generator_SG | 10/20/2025 08:45:08 | Major | 29240 | Cell Unavailable | 10/20/2025 08:43:34 | P3 | 4G | dammam | Generator_SG | LTE SA | DAM2M8072 | FLM_TE | [8 empty] | API | 10/20/2025 08:51:52 | 10/20/2025 10:01:56 | 10/20/2025 10:52:29 |  |  | 10/20/2025 10:53:17 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000349 | PCM-20251020-00000750 | TT-20251020-00763 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/20/2025 08:52:31 | 10/20/2025 20:07:39 | 10/20/2025 14:52:31 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/20/2025 08:44:23 | Major | 22214 | NodeB Unavailable | 10/20/2025 08:44:21 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 08:52:31 | 10/20/2025 20:07:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000353 | PCM-20251020-00000754 | TT-20251020-00759 | EM | Region_1 | JBL0913 | JBL0913 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Hamid Bilal Bashir Ahmed | 10/20/2025 08:54:05 | 10/20/2025 14:52:55 | 10/20/2025 12:54:05 | 1(2G/3G/LTE) sites down under JBAP0137-P1/R1_JB_HWBSC01 @ Sceco | 10/20/2025 08:43:00 | Critical | 21825 | CSL Fault | 10/20/2025 08:42:56 | P2 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBAP0137-P1 | FLM_EM | JBL0913 | Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251020-00000745 | Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/20/2025 08:54:05 | 10/20/2025 12:14:25 | 10/20/2025 12:14:56 | 10/20/2025 12:15:02 | 10/20/2025 12:15:05 | 10/20/2025 14:52:55 |  | Hamid Bilal Bashir Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000356 | PCM-20251020-00000759 | TT-20251020-00773 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | SCECO_Failure | SCECO auto restored | Waseem Shahzad Ghulam Rasool | 10/20/2025 08:56:32 | 10/20/2025 10:26:30 | 10/20/2025 12:56:32 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/20/2025 08:48:16 | Critical | 301 | NE Is Disconnected | 10/20/2025 08:48:14 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 08:56:32 | 10/20/2025 10:24:49 | 10/20/2025 10:26:18 |  |  | 10/20/2025 10:26:30 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000357 | PCM-20251020-00000767 | TT-20251020-00789 | Reference_telecom | Region_1 | HFS2M4025 | HFS2025 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 08:59:31 | 10/21/2025 05:43:51 | 10/20/2025 20:59:31 | RF Unit RX Channel RTWP/RSSI Unbalanced at HFS2M4025-P3 @ Generator_SG | 10/20/2025 05:59:25 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/20/2025 05:59:22 | P3 | 3G | hafouf | Generator_SG | 3G NSA | HFS2M4025 | FLM_TE | [8 empty] | API | 10/20/2025 08:59:31 | 10/21/2025 05:43:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000359 | PCM-20251020-00000770 | TT-20251020-00791 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/20/2025 09:01:36 | 10/21/2025 23:22:31 | 10/20/2025 15:01:36 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/20/2025 08:51:19 | Major | 65102 | high temprature 32 | 10/20/2025 08:51:15 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/20/2025 09:01:36 | 10/21/2025 23:22:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000366 | PCM-20251020-00000792 | TT-20251020-00794 | Telecom | Region_4 | RNRY0339 | RNRY0339 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 10/20/2025 09:15:45 | 10/21/2025 10:09:14 | 10/20/2025 15:15:45 | 1(2G) 2(3G) 2(5G) sites down under TAF2349-P2,RNRY0442-P3/RNRY0442-P3 @ Sceco | 10/20/2025 09:01:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 09:00:57 | P1 | 2G | taif | Sceco_STB | 2G_3G_5G SA | TAF2349-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 5G,RNRY0442-P3 2G_3G | FLM_TE | RNRY0339 | HUB: RNRY0339 We are observing MW visibility down at HUB, kindly check locally. HUB: TAF2349 We are Observing Link flapping at HUB , kindly check locally. | PCM-20251020-00000779 | HUB: RNRY0339 We are observing MW visibility down at HUB, kindly check locally. HUB: TAF2349 We are Observing Link flapping at HUB , kindly check locally. | HUB: RNRY0339 We are observing MW visibility down at HUB, kindly check locally. HUB: TAF2349 We are Observing Link flapping at HUB , kindly check locally. |  | sites down |  | API | 10/20/2025 09:15:45 | 10/20/2025 23:38:45 | 10/21/2025 10:09:08 |  |  | 10/21/2025 10:09:14 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000368 | PCM-20251020-00000798 | TT-20251020-00815 | Telecom | Region_1 | KBR2M7155 | KBR0155 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Imran Ali Yousaf | 10/20/2025 09:17:45 | 10/20/2025 11:26:34 | 10/20/2025 15:17:45 | Cell Unavailable at KBR2M7155-P3-L800 @ Sceco | 10/20/2025 09:17:17 | Major | 29240 | Cell Unavailable | 10/20/2025 09:16:46 | P3 | 4G | dammam | Sceco | LTE SA | KBR2M7155 | FLM_TE | [8 empty] | API | 10/20/2025 09:17:45 | 10/20/2025 10:43:59 | 10/20/2025 10:44:16 | 10/20/2025 10:44:43 | 10/20/2025 10:44:57 | 10/20/2025 11:26:34 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000372 | PCM-20251020-00000805 | TT-20251020-00820 | EM | Region_1 | HFB2M5001 | HFB0001 |  |  |  | Reda Magdi Elmetwalli Ghazi | 10/20/2025 09:21:44 | 10/20/2025 13:21:48 | 10/20/2025 15:21:44 | Mains Failure at HFB2M5001-P1-DIA @ Generator_SG | 10/20/2025 09:11:52 | Major | 65109 | Mains Failure | 10/20/2025 09:11:50 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5001 | FLM_EM | [8 empty] | API | 10/20/2025 09:21:44 | 10/20/2025 13:21:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000395 | PCM-20251020-00000862 | TT-20251020-00881 | Telecom | Region_4 | LTH1M3330 | LTH0330 |  |  |  | Riasat Ali Allah Baksh | 10/20/2025 09:58:02 | 10/20/2025 21:24:50 | 10/20/2025 13:58:02 | 1(3G) sites down under LTH0330-P1-HUB/LTH1M3330-P1-HUB @ Sceco_STB | 10/20/2025 09:50:17 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/20/2025 09:49:37 | P1 | 3G | qunfuddah | Sceco_STB | 3G SA | LTH0330-P1-HUB | FLM_TE | LTH0330 | Results: DOWN SITE HUB LTH0330-P1-HUB LTH0330 Summary: Hub: LTH0330, Down Count: 1, Down Sites: LTH0330-P1-HUB Alarm Summary: LTH0330 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 09:58:02 | 10/20/2025 21:24:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000398 | PCM-20251020-00000864 | TT-20251020-00888 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/20/2025 10:01:02 | 10/20/2025 10:07:18 | 10/20/2025 22:01:02 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/20/2025 09:52:52 | Minor | 7103 | HIGH TEMP | 10/20/2025 09:52:43 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/20/2025 10:01:02 | 10/20/2025 10:07:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000406 | PCM-20251020-00000886 | TT-20251020-00908 | Telecom | Region_4 | JED0097-ZJe06-CSG-03 | JED0097 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 10:10:50 | 10/20/2025 10:10:50 | 10/20/2025 14:10:50 | DWDM Link Down at JED0097-ZJe06-CSG-03 @ Sceco | 10/20/2025 10:04:13 | Critical | 101-2505274 | Physical Port Down | 10/20/2025 10:04:04 | P1 | IPRAN | jeddah | Sceco | IPRAN SA | JED0097-ZJe06-CSG-03 | FLM_TE | [8 empty] | API | 10/20/2025 10:10:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000410 | PCM-20251020-00000895 | TT-20251020-00917 | Reference_EM | Region_1 | RYDM0904 | RYDM0904 |  |  |  | Muhammed Asif Riaz Riaz Hussain Akhgar | 10/20/2025 10:15:59 | 10/21/2025 14:49:33 | 10/20/2025 16:15:59 | Mains Failure at RYDM0904-P1-HUB_SRAN @ Sceco | 10/20/2025 10:05:53 | Major | 65109 | Mains Failure | 10/20/2025 10:05:50 | P1 | SRAN | dammam | Sceco | 2G NSA | RYDM0904 | FLM_EM | [8 empty] | API | 10/20/2025 10:15:59 | 10/21/2025 14:49:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000415 | PCM-20251020-00000904 | TT-20251020-00914 | Telecom | Region_4 | TURY0688 | TURY0688 |  |  |  | Rashid Shafique | 10/20/2025 10:19:03 | 10/20/2025 11:57:57 | 10/20/2025 16:19:03 | 1(5G) sites down under TURY0688-GSM-P3 @ Sceco | 10/20/2025 10:10:43 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 10:10:38 | P3 | 2G | taif | Sceco | 5G SA | TURY0688-GSM-P3 | FLM_TE | TURY0688 | Results: DOWN SITE HUB TURY0688-GSM-P3 TURY0688 Summary: Hub: TURY0688, Down Count: 1, Down Sites: TURY0688-GSM-P3 Alarm Summary: TURY0688 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.98.98.108:8080/NE3S/1.0/] | sites down |  | API | 10/20/2025 10:19:03 | 10/20/2025 11:57:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000424 | PCM-20251020-00000922 | TT-20251020-00897 | Telecom | Region_4 | TAF0312 | TAF0312 |  |  |  | Rashid Shafique | 10/20/2025 10:31:35 | 10/20/2025 17:30:02 | 10/20/2025 16:31:35 | 2(2G) 2(3G) 1(LTE) sites down under RYMK0763-P2-USF,TAF0312-P2/TAF0312-P2 @ Sceco | 10/20/2025 10:02:53 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 10:02:48 | P2 | 2G | taif | Sceco | 2G_3G SA | RYMK0763-P2-USF 3G,TAF0312-P2 2G_3G | FLM_TE | TAF0312 | HUB: RYMK0763, TAF0312 We are observing LOS TO AIRSCALE kindly check locally | PCM-20251020-00000882 | HUB: RYMK0763, TAF0312 We are observing LOS TO AIRSCALE kindly check locally | HUB: RYMK0763, TAF0312 We are observing LOS TO AIRSCALE kindly check locally |  | sites down |  | API | 10/20/2025 10:31:35 | 10/20/2025 11:57:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000430 | PCM-20251020-00000932 | TT-20251020-00956 | EM | [7 empty] | 10/20/2025 10:40:16 | 10/20/2025 10:40:16 | 10/20/2025 14:40:16 | DOOR OPEN at HHR6-SEC0038_OCS @ Sceco | 10/20/2025 10:40:07 | Critical | 1-12307 | DOOR OPEN | 10/20/2025 10:39:58 | P1 | DWDM |  | Sceco | DWDM NSA | HHR6 | FLM_EM | [5 empty] | 0-TO MD1&HHR5-SEC0037(1-A)-71-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/20/2025 10:40:16 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000438 | PCM-20251020-00000965 | TT-20251020-00985 | MW_HC | Region_6 | QJF0051 | QJF0051 |  |  |  | Zeshan Ali Adnan | 10/20/2025 10:56:29 | 10/20/2025 14:20:30 | 10/20/2025 22:56:29 | As BO Requested MW Nokia Observing modem 4 count continuous PM errors QJF0051-QJF0075 | 10/20/2025 10:54:01 | Minor | 113388 | LOF | 10/20/2025 10:54:03 | P2 | 2G | baish | Sceco | TX NSA | QJF0051-QJF0075 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing modem 4 count continuous PM errors QJF0051-QJF0075 |  |  | API | 10/20/2025 10:56:29 | 10/20/2025 14:20:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000442 | PCM-20251020-00000978 | TT-20251020-00999 | Telecom | Region_4 | JED1M8574 | JED2574 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 10:58:52 | 10/20/2025 13:30:29 | 10/20/2025 16:58:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8574-CA-L900-P1-L800-SBTS @ Sceco | 10/20/2025 10:57:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 10:57:49 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8574 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 10:58:52 | 10/20/2025 11:37:53 | 10/20/2025 13:30:25 | 10/20/2025 13:30:27 | 10/20/2025 13:30:29 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000443 | PCM-20251020-00000980 | TT-20251020-01001 | MW_HC | Region_6 | WDS9457 | WDS9457 |  |  |  | Ahmed Mamdouh Helal Helal | 10/20/2025 10:59:23 | 10/20/2025 15:21:36 | 10/20/2025 22:59:23 | As BO Requested MW Nokia Observing counting continuous PM errors in daily basis WDS9457-WDS9471 | 10/20/2025 10:58:28 | Minor | 113388 | LOF | 10/20/2025 10:58:30 | P1 | Repeater | wadi dawasar | Generator_DG | TX NSA | WDS9457-WDS9471 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing counting continuous PM errors in daily basis WDS9457-WDS9471 |  |  | API | 10/20/2025 10:59:23 | 10/20/2025 15:21:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000444 | PCM-20251020-00000994 | TT-20251020-01015 | Reference_telecom | Region_1 | HFF0052 | HFF0052 | Equipment | Jumper_Cable | Replace Indoor Jumper Cable | Imran Ali Yousaf | 10/20/2025 11:04:33 | 10/22/2025 15:02:31 | 10/20/2025 17:04:33 | RF Unit VSWR Threshold Crossed at HFF0052-P2_SRAN @ Sceco | 10/20/2025 08:04:25 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/20/2025 08:04:13 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0052 | FLM_TE | [8 empty] | API | 10/20/2025 11:04:33 | 10/22/2025 12:42:42 | 10/22/2025 13:33:33 | 10/22/2025 13:33:38 | 10/22/2025 13:34:33 | 10/22/2025 15:02:31 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000451 | PCM-20251020-00001007 | TT-20251020-01026 | MW_HC | Region_4 | MKYL0916 | MKYL0916 |  |  |  | Riasat Ali Allah Baksh | 10/20/2025 11:10:27 | 10/20/2025 21:24:52 | 10/20/2025 23:10:27 | As BO Requested MW Nokia Observing counting PM errors in daily basis MKYL0916-JDJZ0768 | 10/20/2025 11:09:24 | Minor | 113388 | LOF | 10/20/2025 11:09:26 | P3 | 2G | alaith | Generator_SG | TX NSA | MKYL0916-JDJZ0768 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing counting PM errors in daily basis MKYL0916-JDJZ0768 |  |  | API | 10/20/2025 11:10:27 | 10/20/2025 21:24:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000453 | PCM-20251020-00001009 | TT-20251020-01027 | EM | Region_1 | HFB2M5002 | HFB0002 |  |  |  | Reda Magdi Elmetwalli Ghazi | 10/20/2025 11:11:17 | 10/20/2025 13:21:48 | 10/20/2025 23:11:17 | Door opening alarm at HFB2M5002-P2 @ Generator_SG | 10/20/2025 11:10:58 | Minor | 65101 | Door opening alarm | 10/20/2025 11:10:55 | P2 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5002 | FLM_EM | [8 empty] | API | 10/20/2025 11:11:17 | 10/20/2025 13:21:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000457 | PCM-20251020-00001018 | TT-20251020-01038 | Telecom | Region_1 | KBR6054 | KBR6054 |  |  |  | Meraj Husain Idd Baksh | 10/20/2025 11:14:22 | 10/20/2025 12:52:03 | 10/20/2025 23:14:22 | RF Unit Maintenance Link Failure at KBR6054-DCU1 @ Sceco | 10/20/2025 11:09:01 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/20/2025 11:08:57 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR6054 | FLM_TE | [8 empty] | API | 10/20/2025 11:14:22 | 10/20/2025 12:52:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000459 | PCM-20251020-00001021 | TT-20251020-01041 | EM | Region_6 | RYAB0648 | RYAB0648 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Amir Arif Ali | 10/20/2025 11:16:57 | 10/21/2025 09:55:18 | 10/20/2025 17:16:57 | SHELTER DOOR OPEN at RYAB0648-GSM-UMTS-P1-HUB-USF @ Sceco_STB | 10/20/2025 11:16:34 | Major | 7103 | SHELTER DOOR OPEN | 10/20/2025 11:16:26 | P1 | 2G | turaib | Sceco_STB | 2G NSA | RYAB0648 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/20/2025 11:16:57 | 10/20/2025 14:31:37 | 10/21/2025 09:54:53 | 10/21/2025 09:54:58 |  | 10/21/2025 09:55:18 |  | Amir Arif Ali |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000462 | PCM-20251020-00001028 | TT-20251020-00954 | Telecom | Region_3 | MDHL9054 | MDHL9054 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Sami Mohammed Jad Shahatah | 10/20/2025 11:19:52 | 10/23/2025 05:12:45 | 10/20/2025 13:19:52 | 5(2G) 6(LTE) sites down under R3_HL_HWBSC01 @ Sceco_STB | 10/20/2025 10:36:11 | Emergency | 21807 | OML Fault | 10/20/2025 10:36:03 | P3 | Repeater | hail | Generator_DG | 2G_LTE SA | MDHL0378-P1-HUB_SRAN LTE,AHT0971-P1-HUB_SRAN LTE,HLV0569-P3_SRAN LTE,HLV0568-P3_SRAN LTE,HDB0359-P3 2G_LTE,MDHL0376-P2_SRAN LTE,MDHL0385-P1-HUB 2G,HLV0571-P3 2G,HLV0572-P3 2G,HLV0570-P3 2G | FLM_EM | MDHL9054 | Hub:- MDHL9054 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251020-00000936 | Hub:- MDHL9054 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- MDHL9054 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/20/2025 11:19:52 | 10/21/2025 08:25:12 | 10/23/2025 05:12:37 |  |  | 10/23/2025 05:12:45 |  | Sami Mohammed Jad Shahatah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000463 | PCM-20251020-00001029 | TT-20251020-01021 | Telecom | Region_4 | JED0560 | JED0560 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 11:20:10 | 10/20/2025 16:09:56 | 10/20/2025 15:20:10 | 1(2G) 1(LTE) 2(5G) sites down under JED6027-GSM-P3,JED0560-PI-VIP-ARP-SHOP/JED0560-PI-VIP-ARP-SHOP @ Sceco | 10/20/2025 11:04:28 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 11:04:25 | VIP | 2G | jeddah | Sceco | 2G_5G SA | JED6027-GSM-P3 5G,JED0560-PI-VIP-ARP-SHOP 2G | FLM_TE | JED0560 | HUB: JED0560 We are Observing Link flapping at HUB , kindly check locally. HUB: JED6027 We are observing MW visibility down at HUB, kindly check locally. | PCM-20251020-00001012 | HUB: JED0560 We are Observing Link flapping at HUB , kindly check locally. HUB: JED6027 We are observing MW visibility down at HUB, kindly check locally. | HUB: JED0560 We are Observing Link flapping at HUB , kindly check locally. HUB: JED6027 We are observing MW visibility down at HUB, kindly check locally. |  | sites down |  | API | 10/20/2025 11:20:10 | 10/20/2025 16:09:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000464 | PCM-20251020-00001032 | TT-20251020-01048 | EM | Region_1 | RSK2233 | RSK2233 |  |  |  | Ali Ahmed Ali Ahmed | 10/20/2025 11:21:05 | 10/20/2025 11:21:05 | 10/20/2025 23:21:05 | Door opening alarm at RSK2233-P3_SRAN @ Generator_SG | 10/20/2025 11:20:47 | Minor | 65101 | Door opening alarm | 10/20/2025 11:20:43 | P3 | SRAN | jubail | Generator_SG | 2G NSA | RSK2233 | FLM_EM | [8 empty] | API | 10/20/2025 11:21:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000465 | PCM-20251020-00001033 | TT-20251020-00980 | Telecom | Region_3 | MDHL9054 | MDHL9054 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Sami Mohammed Jad Shahatah | 10/20/2025 11:21:07 | 10/23/2025 05:12:33 | 10/20/2025 23:21:07 | WMDHL0001 Complete down | 10/20/2025 10:49:08 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/20/2025 10:49:08 | P3 | Repeater | hail | Generator_DG | Wifi SA | WMDHL0001 | FLM_EM | MDHL9054 | Hub:- MDHL9054 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251020-00000958 | Hub:- MDHL9054 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- MDHL9054 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/20/2025 11:21:07 | 10/21/2025 08:25:12 | 10/23/2025 05:12:22 |  |  | 10/23/2025 05:12:33 |  | Sami Mohammed Jad Shahatah |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000471 | PCM-20251020-00001044 | TT-20251020-01049 | EM | Region_4 | JED6132 | JED6132 |  |  |  | Hamza Ahmed Aly Sawy | 10/20/2025 11:26:33 | 10/23/2025 17:55:46 | 10/20/2025 17:26:33 | 1(2G/3G/LTE) sites down under JED6132-P3/JED6132-P3 @ Sceco | 10/20/2025 11:18:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 11:18:41 | P3 | 2G | jeddah | Sceco | 2G_3G SA | JED6132-P3 | FLM_EM | JED6132 | Results: DOWN SITE HUB JED6132-P3 JED6132 Summary: Hub: JED6132, Down Count: 1, Down Sites: JED6132-P3 Alarm Summary: JED6132 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 11:26:33 | 10/23/2025 17:55:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000473 | PCM-20251020-00001048 | TT-20251020-01055 | EM | Region_1 | ARM2M2657 | ARM2657 |  |  |  | Dileesh Muringothil Devarajan | 10/20/2025 11:29:33 | 10/21/2025 09:05:01 | 10/20/2025 17:29:33 | 1(2G/3G/LTE) sites down under ARM2657-P3/DM1MBSCH01 @ Sceco | 10/20/2025 11:22:37 | Major | 21825 | CSL Fault | 10/20/2025 11:22:35 | P3 | 2G | khafji | Sceco | 2G_3G SA | ARM2657-P3 | FLM_EM | ARM2657 | Results: DOWN SITE HUB ARM2657-P3 ARM2657 Summary: Hub: ARM2657, Down Count: 1, Down Sites: ARM2657-P3 Alarm Summary: ARM2657 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 11:29:33 | 10/20/2025 16:39:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000475 | PCM-20251020-00001061 | TT-20251020-01067 | Telecom | Region_4 | JED0129 | JED0129 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/20/2025 11:37:02 | 10/20/2025 11:37:02 | 10/20/2025 15:37:02 | 1(2G) sites down under JED0129-P1-WDM-FON/JED0129-P1-WDM-FON @ Sceco | 10/20/2025 11:28:33 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 11:28:29 | P1 | 2G | jeddah | Sceco | 2G SA | JED0129-P1-WDM-FON | FLM_TE | JED0129 | Results: DOWN SITE HUB JED0129-P1-WDM-FON JED0129 Summary: Hub: JED0129, Down Count: 1, Down Sites: JED0129-P1-WDM-FON Alarm Summary: JED0129 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 11:37:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000478 | PCM-20251020-00001064 | TT-20251020-01080 | Reference_telecom | Region_6 | BHAB2041 | BHAB2041 | Transsmission | SFP_Transmission | Reset SFP | SHAH KHALID | 10/20/2025 11:38:39 | 10/20/2025 17:07:00 | 10/20/2025 23:38:39 | LossOfSignal observed in BHAB2041 towards 10.221.243.213 @ Generator_SG | 10/19/2025 23:38:12 | Minor |  | LossOfSignal | 10/19/2025 23:38:08 | P3 | 2G | Baha | Generator_SG | TX NSA | BHAB2041 | FLM_TE | [8 empty] | API | 10/20/2025 11:38:39 | 10/20/2025 12:33:58 | 10/20/2025 17:06:41 |  |  | 10/20/2025 17:07:00 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000479 | PCM-20251020-00001067 | TT-20251020-01082 | MW_HC | Region_5 | MAK0322 | MAK0322 | Equipment | SW | Issue was solved after softaware configuration | KAMRAN AAMIR | 10/20/2025 11:41:03 | 10/20/2025 20:32:08 | 10/20/2025 23:41:03 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0322-MAK0105 | 10/20/2025 11:39:24 | Minor | 113388 | LOF | 10/20/2025 11:39:26 | P2 | 2G | makkah | Sceco | TX NSA | MAK0322-MAK0105 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0322-MAK0105 |  |  | API | 10/20/2025 11:41:03 | 10/20/2025 19:22:36 | 10/20/2025 19:23:02 | 10/20/2025 19:23:07 | 10/20/2025 19:43:55 | 10/20/2025 20:32:08 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000482 | PCM-20251020-00001076 | TT-20251020-01093 | MW_HC | Region_5 | MAK0654 | MAK0654 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/20/2025 11:46:14 | 10/21/2025 19:57:02 | 10/20/2025 23:46:14 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0654-MAK0564 | 10/20/2025 11:44:29 | Minor | 113388 | LOF | 10/20/2025 11:44:31 | P2 | 2G | makkah | Sceco | TX NSA | MAK0654-MAK0564 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0654-MAK0564 |  |  | API | 10/20/2025 11:46:14 | 10/21/2025 19:57:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000484 | PCM-20251020-00001080 | TT-20251020-01085 | EM | [7 empty] | 10/20/2025 11:47:05 | 10/20/2025 11:47:05 | 10/20/2025 17:47:05 | 1(2G/LTE) sites down under BAH2152-P3-CAP/BAH2152-P3-CAP @ Generator_SG | 10/20/2025 11:38:55 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 11:38:51 | P3 | 2G |  | Generator_SG | 2G_LTE SA | BAH2152-P3-CAP | FLM_EM | BAH2152 | Results: DOWN SITE HUB BAH2152-P3-CAP BAH2152 Summary: Hub: BAH2152, Down Count: 1, Down Sites: BAH2152-P3-CAP Alarm Summary: BAH2152 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 11:47:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000485 | PCM-20251020-00001083 | TT-20251020-01098 | Telecom | Region_1 | HFF6029 | HFF6029 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 11:47:27 | 10/21/2025 05:43:51 | 10/20/2025 23:47:27 | RF Unit CPRI Interface Error at HFF6029-DCU1 @ Sceco | 10/20/2025 11:41:15 | Minor | 26504 | RF Unit CPRI Interface Error | 10/20/2025 11:40:31 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/20/2025 11:47:27 | 10/21/2025 05:43:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000487 | PCM-20251020-00001084 | TT-20251020-01099 | Telecom | Region_1 | HFF6029 | HFF6029 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/20/2025 11:48:28 | 10/21/2025 05:43:52 | 10/20/2025 23:48:28 | RF Unit Clock Problem at HFF6029-DCU1 @ Sceco | 10/20/2025 11:41:12 | Minor | 26538 | RF Unit Clock Problem | 10/20/2025 11:40:13 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/20/2025 11:48:28 | 10/21/2025 05:43:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000498 | PCM-20251020-00001103 | TT-20251020-01118 | MW_HC | Region_5 | MAK0688 | MAK0688 | Equipment | BTS_Cable | Replace Ethernet Cable | Muhammad Saleem Iqbal | 10/20/2025 11:53:31 | 10/21/2025 08:36:04 | 10/20/2025 23:53:31 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0688-MAK0767 | 10/20/2025 11:52:33 | Minor | 113388 | LOF | 10/20/2025 11:52:35 | P2 | 2G | makkah | Sceco | TX NSA | MAK0688-MAK0767 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0688-MAK0767 |  |  | API | 10/20/2025 11:53:31 | 10/21/2025 07:04:12 | 10/21/2025 07:17:09 | 10/21/2025 07:17:42 | 10/21/2025 07:21:42 | 10/21/2025 08:36:04 |  | Muhammad Saleem Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000500 | PCM-20251020-00001105 | TT-20251020-01121 | Reference_telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/20/2025 11:54:10 | 10/20/2025 11:54:10 | 10/20/2025 23:54:10 | RF Unit RX Channel RTWP/RSSI Unbalanced at MAK6018-DCU-P3 @ Sceco | 10/20/2025 08:53:51 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/20/2025 08:53:47 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/20/2025 11:54:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000507 | PCM-20251020-00001119 | TT-20251020-01122 | EM | Region_1 | JBL2M7913 | JBL0913 |  |  |  | Tahir Mahmood Hafiz Yar | 10/20/2025 12:00:32 | 10/20/2025 12:21:32 | 10/20/2025 18:00:32 | 1(2G/3G/LTE) sites down under JBL0913-P2 @ Sceco | 10/20/2025 11:54:28 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/20/2025 11:39:57 | P2 | 4G | jubail | Sceco | LTE SA | JBL0913-P2 | FLM_TE | JBL0913 | Results: DOWN SITE HUB JBL0913-P2 JBL0913 Summary: Hub: JBL0913, Down Count: 1, Down Sites: JBL0913-P2 Alarm Summary: JBL0913 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 12:00:32 | 10/20/2025 12:16:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000511 | PCM-20251020-00001132 | TT-20251020-01138 | Reference_telecom | [7 empty] | 10/20/2025 12:09:03 | 10/20/2025 12:09:03 | 10/20/2025 18:09:03 | CSL FAULT at BDR2M1548 refTT-20251019-01440 | 10/20/2025 12:03:32 | Major | 21825 | CSL Fault | 10/20/2025 12:03:33 | P3 | DIA |  | Sceco | 2G SA | BDR2M1548 | FLM_TE | BDR2M1548 | Results: DOWN SITE HUB BDR2M1548 BDR2M1548 Summary: Hub: BDR2M1548, Down Count: 1, Down Sites: BDR2M1548 Alarm Summary: BDR2M1548 No Active Alarm on HUB | [6 empty] | API | 10/20/2025 12:09:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000512 | PCM-20251020-00001133 | TT-20251020-01141 | Reference_telecom | Region_5 | MAK0641 | MAK0641 |  |  |  | Husain Hassan Ishag Omer | 10/20/2025 12:09:07 | 10/20/2025 14:54:57 | 10/21/2025 00:09:07 | ReplaceableUnitMissing observed in MAK0641 towards 10.221.240.194 @ Sceco | 10/20/2025 00:12:44 | Minor |  | ReplaceableUnitMissing | 10/20/2025 00:08:51 | P2 | 2G | makkah | Sceco | TX NSA | MAK0641 | FLM_TE | [8 empty] | API | 10/20/2025 12:09:07 | 10/20/2025 14:54:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000513 | PCM-20251020-00001134 | TT-20251020-01133 | Telecom | Region_6 | AQQ2427 | AQQ2427 |  |  |  | Abdul Shakor Abassi | 10/20/2025 12:09:15 | 10/20/2025 12:09:15 | 10/20/2025 18:09:15 | 2(2G) 2(LTE) sites down under AQQ2427-P3,AQQ2428-P3/AQQ2428-P3 @ Generator_SG | 10/20/2025 11:58:25 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 11:58:19 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | AQQ2427-P3 2G_LTE,AQQ2428-P3 2G_LTE | FLM_EM | AQQ2427 | Hub: AQQ2427 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251020-00001131 | Hub: AQQ2427 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: AQQ2427 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/20/2025 12:09:15 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000518 | PCM-20251020-00001156 | TT-20251020-01167 | Telecom | Region_4 | SQSH1M7150 | SQSH0150 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/20/2025 12:19:59 | 10/21/2025 17:13:06 | 10/20/2025 18:19:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at SQSH1M7150-G9-NL8-L18-SBTS-P2-USF @ Sceco_STB | 10/20/2025 12:19:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 12:19:10 | P2 | 4G | qunfuddah | Sceco_STB | 5G_Cell SA | SQSH1M7150 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 12:19:59 | 10/20/2025 16:30:50 | 10/20/2025 20:46:13 |  |  | 10/20/2025 20:46:19 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000523 | PCM-20251020-00001162 | TT-20251020-01172 | Telecom | Region_4 | JED1M7692 | JED0692 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 12:22:04 | 10/20/2025 16:09:56 | 10/20/2025 18:22:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7692-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/20/2025 12:21:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 12:21:13 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7692 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 12:22:04 | 10/20/2025 16:09:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000526 | PCM-20251020-00001167 | TT-20251020-01175 | Telecom | Region_4 | JED0345 | JED0345 | Equipment | SFP_BTS | Replace SFP | Mohammed Ramadan A Abu Abid | 10/20/2025 12:24:07 | 10/21/2025 17:13:05 | 10/20/2025 18:24:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0345-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/20/2025 12:23:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 12:23:16 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0345 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 12:24:07 | 10/20/2025 12:56:13 | 10/20/2025 13:53:56 | 10/20/2025 13:55:40 | 10/20/2025 14:10:22 | 10/20/2025 15:28:46 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000542 | PCM-20251020-00001200 | TT-20251020-01161 | Reference_telecom | Region_4 | HHR1M7459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 12:36:45 | 10/20/2025 16:09:57 | 10/20/2025 16:36:45 | CELL NOTIFICATION (Temperature alarm) at HHR1M7459-L800-P1-VIP @ Sceco | 10/20/2025 12:09:50 | Critical | 7655 | CELL NOTIFICATION | 10/20/2025 12:09:38 | VIP | 4G | jeddah | Sceco | LTE NSA | HHR1M7459 | FLM_TE |  |  | PCM-20251020-00001152 | pls check high temp | pls check high temp |  |  |  | API | 10/20/2025 12:36:45 | 10/20/2025 16:09:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000549 | PCM-20251020-00001207 | TT-20251020-01208 | Telecom | Region_4 | JED0751 | JED0751 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 12:40:03 | 10/22/2025 06:37:07 | 10/20/2025 16:40:03 | 1(5G) sites down under JED0751-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/20/2025 12:31:41 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 12:31:39 | P2 | 2G | jeddah | Sceco | 5G SA | JED0751-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP | FLM_TE | JED0751 | Results: DOWN SITE HUB JED0751-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP JED0751 Summary: Hub: JED0751, Down Count: 1, Down Sites: JED0751-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP Alarm Summary: JED0751 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.144.156:8080] [URL:http://10.97.144.156:8080/NE3S/1.0/] | sites down |  | API | 10/20/2025 12:40:03 | 10/20/2025 12:56:13 | 10/22/2025 06:36:46 |  |  | 10/22/2025 06:37:07 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000551 | PCM-20251020-00001210 | TT-20251020-01222 | Telecom | Region_1 | KFKM0793 | KFKM0793 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 12:41:40 | 10/22/2025 04:53:50 | 10/21/2025 00:41:40 | ODU CPU / Cable Open at KFKM0793 on 10.147.11.226 @ Generator_SG | 10/20/2025 12:41:01 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/20/2025 12:18:58 | P3 | SRAN | hafr | Generator_SG | TX NSA | KFKM0793 | FLM_TE | [8 empty] | API | 10/20/2025 12:41:40 | 10/20/2025 13:30:46 | 10/21/2025 12:33:40 | 10/21/2025 12:33:44 |  | 10/22/2025 04:53:50 |  | Muhammad Anwar Hussain Akhtar Hussain |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000556 | PCM-20251020-00001217 | TT-20251018-02141 | Reference_telecom | Region_4 | JED0488 | JED0488 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 12:45:46 | 10/20/2025 16:09:57 | 10/21/2025 00:45:46 | ReplaceableUnitProblem observed in JED0488 towards 10.10.185.39 @ Sceco | 10/18/2025 11:59:49 | Minor |  | ReplaceableUnitProblem | 10/18/2025 11:58:48 | P2 | 2G | jeddah | Sceco | TX NSA | JED0488 | FLM_TE |  |  | PCM-20251020-00001151 | thanks to share more details | thanks to share more details |  |  |  | API | 10/20/2025 12:45:46 | 10/20/2025 16:09:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000559 | PCM-20251020-00001223 | TT-20251020-01105 | Telecom | Region_3 | DBQL0249 | DBQL0249 |  |  |  | Waqas Shah | 10/20/2025 12:48:21 | 10/20/2025 14:22:54 | 10/20/2025 16:48:21 | OSC_LOS at DBQL0249_OCS @ Generator_SG | 10/20/2025 11:49:47 | Critical | 1-12843 | OSC_LOS | 10/20/2025 11:49:35 | P3 | SRAN | tabouk | Generator_SG | DWDM NSA | DBQL0249 | FLM_TE |  |  | PCM-20251020-00001188 | issue will auto clear after link restored between DBQL0249 and DBQL0250 , Salam already sent OSP team to check . | issue will auto clear after link restored between DBQL0249 and DBQL0250 , Salam already sent OSP team to check . |  |  |  | API | 10/20/2025 12:48:21 | 10/20/2025 14:22:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000563 | PCM-20251020-00001230 | TT-20251020-00219 | Telecom | Region_4 | JED0085 | JED0085 | Transsmission | MW_HW_stuck | Reset IDU | Mohammed Ramadan A Abu Abid | 10/20/2025 12:52:13 | 10/20/2025 15:29:44 | 10/20/2025 18:52:13 | 2(2G) 2(LTE) 2(5G) sites down under JED0085-P2,JED6149-P3/JED6149-P3 @ Sceco | 10/20/2025 02:27:21 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 02:27:16 | P2 | 2G | jeddah | Sceco | 2G_5G SA | JED0085-P2 2G_5G,JED6149-P3 2G | FLM_TE | JED0085 | Hub: JED0085 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251020-00000227 | No Power Issue | No Power Issue |  | sites down |  | API | 10/20/2025 12:52:13 | 10/20/2025 12:56:14 | 10/20/2025 13:14:23 | 10/20/2025 13:14:26 | 10/20/2025 13:16:35 | 10/20/2025 15:29:44 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000567 | PCM-20251020-00001239 | TT-20251020-01229 | Telecom | Region_1 | KFKM0793 | KFKM0793 | Equipment | PMR_Power_Cable_RRU | Replace DCDU Fuse | Mahmoud Youssef Mohamed Ahmed | 10/20/2025 12:56:46 | 10/22/2025 06:03:58 | 10/20/2025 16:56:46 | 5(2G) 5(LTE) sites down under HB1BSCH01 @ Sceco | 10/20/2025 12:43:08 | Critical | 21825 | CSL Fault | 10/20/2025 12:43:06 | P3 | SRAN | hafr | Generator_SG | 2G_LTE SA | KFKM0789-P3 2G_LTE,KFKM0790-P3 2G_LTE,KFKM0793-P3 2G_LTE,KFKM0791-P3 2G_LTE,KFKM0792-P3 2G_LTE | FLM_EM | KFKM0793 | Hub:- KFKM0793 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251020-00001228 | Hub:- KFKM0793 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- KFKM0793 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/20/2025 12:56:46 | 10/20/2025 13:04:24 | 10/22/2025 06:03:45 |  |  | 10/22/2025 06:03:58 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Stuck | CM20251020000568 | PCM-20251020-00001244 | TT-20251020-01250 | EM | [7 empty] | 10/20/2025 12:58:45 | 10/20/2025 12:58:45 | 10/20/2025 16:58:45 | AIR CONDITION FAIL ALARM at BISHA-SEC0012_OCS @ Sceco | 10/20/2025 12:57:07 | Critical | 1-12307 | AIR CONDITION FAIL ALARM | 10/20/2025 12:56:56 | P1 | DWDM |  | Sceco | DWDM NSA | BISHA | FLM_EM | [5 empty] | 0-TO AL-ALAYA-SEC0011(1-A)-72-E1EFI-[AIR CONDITION FAIL ALARM]:2 |  |  | API | 10/20/2025 12:58:45 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000573 | PCM-20251020-00001253 | TT-20251020-01260 | Reference_telecom | Region_4 | JED2189 | JED2189 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 13:04:24 | 10/21/2025 10:51:33 | 10/21/2025 01:04:24 | LagPortDown observed in JED2189_01 towards 10.21.74.148 @ Generator_SG | 10/20/2025 01:04:38 | Minor |  | LagPortDown | 10/20/2025 01:03:53 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2189 | FLM_TE | [8 empty] | API | 10/20/2025 13:04:24 | 10/21/2025 10:51:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000578 | PCM-20251020-00001262 | TT-20251020-01267 | EM | Region_2 | HRQ2869 | HRQ2869 |  |  |  | Kazi Jalil Allimiya | 10/20/2025 13:09:04 | 10/20/2025 13:25:36 | 10/21/2025 01:09:04 | Door opening alarm at HRQ2869-P2_SRAN @ Sceco | 10/20/2025 13:08:38 | Minor | 65101 | Door opening alarm | 10/20/2025 13:02:53 | P2 | SRAN | al kharj | Sceco | 2G NSA | HRQ2869 | FLM_EM | [8 empty] | API | 10/20/2025 13:09:04 | 10/20/2025 13:25:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000580 | PCM-20251020-00001264 | TT-20251020-01269 | Telecom | Region_5 | MAK2523 | MAK2523 | Equipment | SFP_BTS | Replace SFP | Israr Ahmed Muhammad Ghauri | 10/20/2025 13:10:54 | 10/21/2025 15:49:28 | 10/20/2025 19:10:54 | PT::FLM need to perform HC at MAK2523 (BO request) | 10/20/2025 13:10:42 | Major | 676767671 | Health Check-WO to TE FME | 10/20/2025 13:10:42 | P3 | 2G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK2523 | FLM_TE | [8 empty] | API | 10/20/2025 13:10:54 | 10/20/2025 13:24:18 | 10/20/2025 13:44:37 | 10/20/2025 13:44:42 | 10/20/2025 14:22:11 | 10/20/2025 15:55:12 |  | Israr Ahmed Muhammad Ghauri |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000585 | PCM-20251020-00001275 | TT-20251020-01280 | EM | Region_2 | HRQ2869 | HRQ2869 |  |  |  | Kazi Jalil Allimiya | 10/20/2025 13:16:19 | 10/20/2025 13:25:36 | 10/21/2025 01:16:19 | Air condition 1 failure alarm at HRQ2869-P2_SRAN @ Sceco | 10/20/2025 13:08:38 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 13:06:08 | P2 | SRAN | al kharj | Sceco | 2G NSA | HRQ2869 | FLM_EM | [8 empty] | API | 10/20/2025 13:16:19 | 10/20/2025 13:25:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000588 | PCM-20251020-00001278 | TT-20251020-01251 | Telecom | Region_4 | JED0024 | JED0024 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 13:16:34 | 10/21/2025 10:51:33 | 10/20/2025 19:16:34 | BASE STATION HARDWARE PROBLEM (RX Power too low) at JED0024-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/20/2025 12:51:25 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/20/2025 12:51:14 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0024 | FLM_TE |  |  | PCM-20251020-00001243 | Please check The RX power on the lane of the SFP transceiver is too low. SFP optical part as the receiver part may be dirty or damaged , Please change if damaged . | Please check The RX power on the lane of the SFP transceiver is too low. SFP optical part as the receiver part may be dirty or damaged , Please change if damaged . |  |  |  | API | 10/20/2025 13:16:34 | 10/21/2025 10:51:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000591 | PCM-20251020-00001282 | TT-20251020-01291 | Telecom | Region_3 | MDN2M8945 | MDN2945 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/20/2025 13:18:03 | 10/20/2025 21:01:57 | 10/20/2025 19:18:03 | Cell Unavailable at MDN2M8945-P2-L800 @ Sceco | 10/20/2025 13:15:42 | Major | 29240 | Cell Unavailable | 10/20/2025 13:14:09 | P2 | 4G | madinah | Sceco | LTE SA | MDN2M8945 | FLM_TE | [8 empty] | API | 10/20/2025 13:18:03 | 10/20/2025 21:01:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000592 | PCM-20251020-00001283 | TT-20251020-01292 | Telecom | Region_4 | JZMA1M7824 | JZMA0824 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/20/2025 13:18:23 | 10/21/2025 17:13:06 | 10/20/2025 19:18:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JZMA1M7824-G9-L8-SBTS-P3 @ Sceco | 10/20/2025 13:17:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 13:17:29 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JZMA1M7824 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 13:18:23 | 10/20/2025 16:30:51 | 10/20/2025 20:45:45 |  |  | 10/20/2025 20:45:52 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000594 | PCM-20251020-00001292 | TT-20251020-01304 | EM | Region_6 | BCH1M8203 | BCH2203 |  |  |  | Fathy Mohamed | 10/20/2025 13:22:30 | 10/20/2025 15:38:50 | 10/21/2025 01:22:30 | RECTIFIER MODULE FAILURE at BCH1M8203-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/20/2025 13:13:59 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/20/2025 13:13:55 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8203 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/20/2025 13:22:30 | 10/20/2025 15:38:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000600 | PCM-20251020-00001306 | TT-20251020-01315 | Reference_EM | Region_1 | HFBD2M2007 | HFBD2007 |  |  |  | Ayman Ibrahim Mohamed Elayad | 10/20/2025 13:30:47 | 10/20/2025 13:30:47 | 10/20/2025 19:30:47 | Low fuel alarm at HFBD2M2007-P1-HUB @ Generator_SG | 10/20/2025 13:20:18 | Major | 65115 | Low fuel alarm | 10/20/2025 13:20:15 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M2007 | FLM_EM | [8 empty] | API | 10/20/2025 13:30:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251020000602 | PCM-20251020-00001313 | TT-20251020-01327 | Reference_EM | Region_1 | RYDM2054 | RYDM2054 |  |  |  | Mohamed Samir Farahat Allam | 10/20/2025 13:35:26 | 10/23/2025 15:57:46 | 10/21/2025 01:35:26 | Air condition 1 failure alarm at RYDM2054-P2_SRAN @ Generator_SG | 10/20/2025 13:25:22 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 13:25:19 | P2 | SRAN | dammam | Generator_SG | 2G NSA | RYDM2054 | FLM_EM | [8 empty] | API | 10/20/2025 13:35:26 | 10/23/2025 12:23:19 | 10/23/2025 15:57:25 | 10/23/2025 15:57:42 | 10/23/2025 15:57:46 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000609 | PCM-20251020-00001327 | TT-20251020-01340 | EM | Region_1 | RSK2800 | RSK2800 |  |  |  | Dileesh Muringothil Devarajan | 10/20/2025 13:42:08 | 10/20/2025 16:39:55 | 10/21/2025 01:42:08 | Door opening alarm at RSK2800-P2_SRAN @ Sceco | 10/20/2025 13:41:45 | Minor | 65101 | Door opening alarm | 10/20/2025 13:41:41 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2800 | FLM_EM | [8 empty] | API | 10/20/2025 13:42:08 | 10/20/2025 16:39:55 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000613 | PCM-20251020-00001339 | TT-20251020-01355 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 13:48:19 | 10/20/2025 13:48:19 | 10/21/2025 01:48:19 | BASE STATION ANTENNA LINE PROBLEM at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/20/2025 13:38:58 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/20/2025 13:38:53 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0539 | FLM_TE |  |  | PCM-20251020-00001337 | Please check VSWR locally | Please check VSWR locally |  |  |  | API | 10/20/2025 13:48:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000614 | PCM-20251020-00001340 | TT-20251020-01356 | Reference_telecom | Region_6 | BHAB0828 | BHAB0828 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/20/2025 13:48:20 | 10/20/2025 14:10:34 | 10/21/2025 01:48:20 | DemFail observed in BHAB0828_02 towards 10.221.243.211 @ Sceco | 10/20/2025 01:50:25 | Minor |  | DemFail | 10/20/2025 01:48:09 | P3 | 2G | makhwa | Sceco | TX NSA | BHAB0828 | FLM_TE | [8 empty] | API | 10/20/2025 13:48:20 | 10/20/2025 14:07:52 | 10/20/2025 14:10:19 |  |  | 10/20/2025 14:10:34 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000615 | PCM-20251020-00001341 | TT-20251020-01357 | Telecom | Region_4 | JED0109 | JED0109 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 13:48:21 | 10/22/2025 06:37:36 | 10/20/2025 19:48:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0109-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/20/2025 13:47:19 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 13:47:11 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0109 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 13:48:21 | 10/20/2025 13:53:46 | 10/22/2025 06:37:26 |  |  | 10/22/2025 06:37:36 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000616 | PCM-20251020-00001343 | TT-20251020-01350 | Telecom | Region_6 | BSA2211 | BSA2211 |  |  |  | Asad Saddiq | 10/20/2025 13:50:05 | 10/21/2025 17:19:23 | 10/20/2025 19:50:05 | 3(2G/LTE/5G) sites down under BSA2211-P3,BSA2210-P3,BSA2291-P3 @ Generator_SG | 10/20/2025 13:42:16 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 13:42:14 | P3 | 2G | bisha | Generator_SG | 2G_5G SA | BSA2211-P3 | FLM_EM | BSA2211 | Results: DOWN SITE HUB BSA2211-P3 BSA2211 Summary: Hub: BSA2211, Down Count: 1, Down Sites: BSA2211-P3 Alarm Summary: BSA2211 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 13:50:05 | 10/20/2025 13:55:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000619 | PCM-20251020-00001351 | TT-20251020-01367 | Reference_telecom | Region_6 | ABH2166 | ABH2166 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 13:52:28 | 10/20/2025 14:00:45 | 10/21/2025 01:52:28 | ReplaceableUnitProblem observed in ABH2166 towards 10.10.155.50 @ Sceco | 10/20/2025 01:52:11 | Minor |  | ReplaceableUnitProblem | 10/20/2025 01:52:07 | P3 | 2G | abha | Sceco | TX NSA | ABH2166 | FLM_TE | [8 empty] | API | 10/20/2025 13:52:28 | 10/20/2025 14:00:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000622 | PCM-20251020-00001357 | TT-20251020-01303 | Telecom | Region_2 | RIYA6085 | RIYA6085 | Equipment | BTS_Cable | Replace Fiber Cable | Muhammad Waqas Ashraf Muhammad Ashraf | 10/20/2025 13:55:02 | 10/20/2025 21:21:20 | 10/20/2025 17:55:02 | 1(2G) sites down under RIYA6085-P1-SHOP/R2_RY1_HWBSC01 @ Sceco | 10/20/2025 13:18:39 | Critical | 21807 | OML Fault | 10/20/2025 13:18:31 | P1 | SRAN | riyadh | Sceco | 2G SA | RIYA6085-P1-SHOP | FLM_TE | RIYA6085 | Hub : RIYA6085 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. | PCM-20251020-00001329 | Hub : RIYA6085 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. | Hub : RIYA6085 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. |  | sites down |  | API | 10/20/2025 13:55:02 | 10/20/2025 16:36:57 | 10/20/2025 16:37:04 | 10/20/2025 16:37:06 | 10/20/2025 17:52:59 | 10/20/2025 21:21:20 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000629 | PCM-20251020-00001368 | TT-20251020-01366 | EM | Region_1 | JBRK2M1914 | JBRK0914 | Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue | Dileesh Muringothil Devarajan | 10/20/2025 13:57:05 | 10/21/2025 08:36:23 | 10/20/2025 19:57:05 | 1(2G/3G/LTE) sites down under JBRK0914-P2/R1_JB_HWBSC01 @ Sceco | 10/20/2025 13:49:54 | Major | 21825 | CSL Fault | 10/20/2025 13:49:51 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | JBRK0914-P2 | FLM_EM | JBRK0914 | Results: DOWN SITE HUB JBRK0914-P2 JBRK0914 Summary: Hub: JBRK0914, Down Count: 1, Down Sites: JBRK0914-P2 Alarm Summary: JBRK0914 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 13:57:05 | 10/20/2025 16:39:56 | 10/21/2025 06:58:42 | 10/21/2025 06:58:47 | 10/21/2025 06:58:50 | 10/21/2025 08:36:23 |  | Dileesh Muringothil Devarajan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000635 | PCM-20251020-00001380 | TT-20251020-01390 | Telecom | Region_4 | JED2820 | JED2820 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 14:01:15 | 10/20/2025 16:09:58 | 10/21/2025 02:01:15 | BASE STATION INFORMATION (Cooling fan has reduced from the set speed) at JED2820-G900-CA-NR2.6-SBTS-P3 @ Generator_SG | 10/20/2025 13:52:50 | Minor | 7115 | BASE STATION INFORMATION | 10/20/2025 13:52:44 | P4 | 2G | jeddah | Generator_SG | LTE NSA | JED2820 | FLM_TE | [5 empty] | Cooling fan has reduced from the set speed |  |  | API | 10/20/2025 14:01:15 | 10/20/2025 16:09:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000650 | PCM-20251020-00001425 | TT-20251020-01443 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/20/2025 14:15:42 | 10/20/2025 15:45:28 | 10/21/2025 02:15:42 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/20/2025 14:07:18 | Minor | 7115 | BASE STATION INFORMATION | 10/20/2025 14:07:11 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/20/2025 14:15:42 | 10/20/2025 15:45:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000658 | PCM-20251020-00001441 | TT-20251020-01457 | Telecom | Region_5 | MAK1M8086 | MAK2086 |  |  |  | Mosab Nasr eldeen Mohamed | 10/20/2025 14:22:25 | 10/21/2025 17:13:07 | 10/20/2025 20:22:25 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M8086-L800-CA-SBTS-P3 @ Sceco | 10/20/2025 14:21:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 14:21:29 | P3 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M8086 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 14:22:25 | 10/20/2025 19:24:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000659 | PCM-20251020-00001444 | TT-20251020-01460 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/20/2025 14:22:29 | 10/20/2025 16:09:28 | 10/21/2025 02:22:29 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/20/2025 14:19:16 | Minor | 7103 | AIRCON 2 FAILURE | 10/20/2025 14:14:02 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/20/2025 14:22:29 | 10/20/2025 16:09:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000661 | PCM-20251020-00001447 | TT-20251020-01464 | Telecom | Region_1 | DAM2802 | DAM2802 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/20/2025 14:22:57 | 10/20/2025 14:29:50 | 10/21/2025 02:22:57 | RF Unit Temperature Unacceptable at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/20/2025 14:16:03 | Minor | 26525 | RF Unit Temperature Unacceptable | 10/20/2025 14:15:59 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_TE | [8 empty] | API | 10/20/2025 14:22:57 | 10/20/2025 14:29:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000663 | PCM-20251020-00001449 | TT-20251020-01416 | Telecom | Region_4 | JED0495 | JED0495 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/20/2025 14:24:30 | 10/21/2025 11:50:23 | 10/20/2025 20:24:30 | 2(5G) sites down under JED0345-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2,JED0495-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/20/2025 14:08:41 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 14:08:39 | P3 | 2G | jeddah | Sceco | 2G_5G SA | JED0345-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 5G,JED0495-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 5G | FLM_TE | JED0495 | HUB: JED0345, JED0495 We are observing LOS TO AIRSCALE kindly check locally | PCM-20251020-00001426 | HUB: JED0345, JED0495 We are observing LOS TO AIRSCALE kindly check locally | HUB: JED0345, JED0495 We are observing LOS TO AIRSCALE kindly check locally |  | sites down |  | API | 10/20/2025 14:24:30 | 10/20/2025 15:01:49 | 10/21/2025 11:50:15 |  |  | 10/21/2025 11:50:23 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000665 | PCM-20251020-00001458 | TT-20251020-01474 | Telecom | Region_4 | JED0193 | JED0193 | Equipment | BTS_Cable | Replace Fiber Cable | Ahmad Mostafa Hamouda Ibrahem | 10/20/2025 14:28:06 | 10/21/2025 17:13:08 | 10/20/2025 20:28:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0193-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/20/2025 14:27:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 14:27:22 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0193 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 14:28:06 | 10/20/2025 18:43:19 | 10/20/2025 18:56:34 | 10/20/2025 18:56:39 | 10/20/2025 18:56:43 | 10/20/2025 20:25:21 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000670 | PCM-20251020-00001464 | TT-20251020-01414 | Reference_telecom | Region_4 | HJR1M7110 | HJR0110 | Equipment | SFP_BTS | Replace SFP | Khizer Hayat | 10/20/2025 14:31:51 | 10/20/2025 23:13:54 | 10/20/2025 20:31:51 | CELL FAULTY (Failure in optical interface) at HJR1M7110-USF-P3 @ Generator_DG | 10/20/2025 13:51:46 | Major | 7653 | CELL FAULTY | 10/20/2025 14:06:22 | P2 | 4G | jeddah | Generator_DG | LTE_Cell SA | HJR1M7110 | FLM_TE |  |  | PCM-20251020-00001400 | Please check the SFP, Optical issue at site | Please check the SFP, Optical issue at site |  |  |  | API | 10/20/2025 14:31:51 | 10/20/2025 15:46:52 | 10/20/2025 17:01:49 | 10/20/2025 17:01:53 | 10/20/2025 17:01:55 | 10/20/2025 23:13:54 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000671 | PCM-20251020-00001465 | TT-20251020-01480 | Telecom | Region_4 | RYMK0528-LL-CSG | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 14:32:14 | 10/20/2025 19:42:58 | 10/20/2025 18:32:14 | The Device is offline at RYMK0528-LL-CSG @ Generator_SG | 10/20/2025 14:31:57 | Critical | 101-7 | The Device is offline | 10/20/2025 14:31:55 | P1 | IPRAN | taif | Generator_SG | IPRAN SA | RYMK0528-LL-CSG | FLM_TE | [8 empty] | API | 10/20/2025 14:32:14 | 10/20/2025 19:42:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000672 | PCM-20251020-00001467 | TT-20251020-01083 | Reference_telecom | Region_6 | SAB0053 | SAB0053 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/20/2025 14:32:56 | 10/21/2025 02:23:05 | 10/21/2025 02:32:56 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SAB0053-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/20/2025 09:42:19 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 09:40:55 | P2 | 2G | baish | Sceco | 2G NSA | SAB0053 | FLM_TE |  |  | PCM-20251020-00001088 | Dear FLM team, kindly check Airscale port was flapping | Dear FLM team, kindly check Airscale port was flapping |  |  |  | API | 10/20/2025 14:32:56 | 10/20/2025 15:49:14 | 10/21/2025 02:22:43 |  |  | 10/21/2025 02:23:05 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000674 | PCM-20251020-00001469 | TT-20251020-01485 | EM | Region_4 | JED1M8574 | JED2574 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/20/2025 14:33:47 | 10/20/2025 14:33:47 | 10/20/2025 20:33:47 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M8574-CA-L900-P1-L800-SBTS @ Sceco | 10/20/2025 14:25:20 | Major | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/20/2025 14:25:26 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M8574 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/20/2025 14:33:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000679 | PCM-20251020-00001484 | TT-20251020-01501 | Reference_EM | Region_1 | DMJB0086 | DMJB0086 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Omer Elfadoul Mohamed Ibrahim | 10/20/2025 14:38:57 | 10/20/2025 17:01:44 | 10/20/2025 20:38:57 | DC power fail at DMJB0086-P1-HUB_SRAN @ Generator_SG | 10/20/2025 14:28:47 | Major | 65106 | DC power fail | 10/20/2025 14:28:44 | P1 | SRAN | dammam | Generator_SG | 2G NSA | DMJB0086 | FLM_EM | [8 empty] | API | 10/20/2025 14:38:57 | 10/20/2025 15:06:16 | 10/20/2025 15:06:22 |  |  | 10/20/2025 17:01:44 |  | Omer Elfadoul Mohamed Ibrahim |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000680 | PCM-20251020-00001488 | TT-20251020-01506 | Telecom | Region_3 | MDN0701 | MDN0701 | Equipment | SW | Issue was solved after softaware configuration | Ibrahim Mohammad AbdulMalik alraee | 10/20/2025 14:41:01 | 10/20/2025 19:12:56 | 10/20/2025 20:41:01 | NR Cell Unavailable at MDN0701-P2_SRAN @ Sceco | 10/20/2025 14:34:29 | Major | 29841 | NR Cell Unavailable | 10/20/2025 14:32:56 | P2 | SRAN | madinah | Sceco | 5G SA | MDN0701 | FLM_TE | [8 empty] | API | 10/20/2025 14:41:01 | 10/20/2025 19:11:19 | 10/20/2025 19:12:45 |  |  | 10/20/2025 19:12:56 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000683 | PCM-20251020-00001492 | TT-20251020-01508 | EM | Region_1 | DMHF2M5072 | DMHF0072 | Enviroment | Rectifier_Fault | Change LVD contactor | Emad fawzi eldebsi | 10/20/2025 14:42:34 | 10/24/2025 00:48:34 | 10/21/2025 02:42:34 | Door opening alarm at DMHF2M5072-P3 @ Generator_SG | 10/20/2025 14:42:14 | Minor | 65101 | Door opening alarm | 10/20/2025 14:42:11 | P3 | 2G | hafouf | Generator_SG | 2G NSA | DMHF2M5072 | FLM_EM | [8 empty] | API | 10/20/2025 14:42:34 | 10/20/2025 16:04:31 | 10/24/2025 00:48:07 |  |  | 10/24/2025 00:48:34 |  | Emad fawzi eldebsi |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000684 | PCM-20251020-00001494 | TT-20251020-01487 | Telecom | Region_4 | RYMK0528 | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 14:42:43 | 10/20/2025 19:42:58 | 10/20/2025 18:42:43 | 2(2G) 2(3G) 2(LTE) sites down under RYMK0528-P1,RYMK0665-P3/RYMK0665-P3 @ Generator_DG | 10/20/2025 14:31:49 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 14:31:47 | P1 | 2G | taif | Generator_SG | 2G_3G_LTE SA | RYMK0665-P3 2G_3G_LTE,RYMK0528-P1 2G_3G | FLM_TE | RYMK0528 | HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . | PCM-20251020-00001487 | HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . | HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . |  | sites down |  | API | 10/20/2025 14:42:43 | 10/20/2025 19:42:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000688 | PCM-20251020-00001511 | TT-20251020-01529 | Telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 14:51:30 | 10/21/2025 13:17:56 | 10/21/2025 02:51:30 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/20/2025 14:46:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 14:45:54 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251020-00001508 | Please perform the HC for RSSI issue | Please perform the HC for RSSI issue |  |  |  | API | 10/20/2025 14:51:30 | 10/21/2025 13:17:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000691 | PCM-20251020-00001518 | TT-20250914-01974 | MW_HC | Region_6 | ABDB9019 | ABDB9019 |  |  |  | Amir Sohail | 10/20/2025 14:53:33 | 10/20/2025 14:55:47 | 10/21/2025 02:53:33 | NEC MW HC_P0 Observing Modem Down at ABDB9019(10.154.175.117)--SDA0425(10.154.166.114) | 09/14/2025 18:54:52 | Minor |  | LOF | 09/14/2025 18:54:52 | P1 | Repeater | abha | Sceco_STB | TX NSA | ABDB9019(10.154.175.117)--SDA0425(10.154.166.114) | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251020-00001496 | thanks to check below : - IPASO as exist - Modems as exist - ODU as Exist | thanks to check below : - IPASO as exist - Modems as exist - ODU as Exist |  |  |  | API | 10/20/2025 14:53:33 | 10/20/2025 14:55:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000695 | PCM-20251020-00001533 | TT-20251020-01545 | Telecom | Region_5 | MAK1M9254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/20/2025 15:00:50 | 10/20/2025 15:00:50 | 10/20/2025 21:00:50 | BASE STATION ANTENNA LINE PROBLEM at MAK1M9254-P1-SHOP-CA-L800-SBTS @ Sceco | 10/20/2025 14:52:12 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/20/2025 14:52:03 | P1 | 4G | makkah | Sceco | LTE NSA | MAK1M9254 | FLM_TE |  |  | PCM-20251020-00001530 | Please check VSWR locally | Please check VSWR locally |  |  |  | API | 10/20/2025 15:00:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000697 | PCM-20251020-00001544 | TT-20251020-01558 | Telecom | Region_3 | MDN2903 | MDN2903 | Equipment | SW | Issue was solved after softaware configuration | Ibrahim Mohammad AbdulMalik alraee | 10/20/2025 15:07:53 | 10/20/2025 19:13:16 | 10/21/2025 03:07:53 | ALD Maintenance Link Failure at MDN2903-P2_SRAN @ Sceco | 10/20/2025 15:05:03 | Minor | 26541 | ALD Maintenance Link Failure | 10/20/2025 15:03:21 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2903 | FLM_TE | [8 empty] | API | 10/20/2025 15:07:53 | 10/20/2025 19:11:19 | 10/20/2025 19:13:08 |  |  | 10/20/2025 19:13:16 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000700 | PCM-20251020-00001549 | TT-20251020-01562 | EM | [7 empty] | 10/20/2025 15:08:57 | 10/20/2025 15:08:57 | 10/20/2025 19:08:57 | DOOR OPEN at MUHAYIL-SEC0048_OCS @ Sceco | 10/20/2025 15:08:33 | Critical | 1-12307 | DOOR OPEN | 10/20/2025 15:08:24 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/20/2025 15:08:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251020000701 | PCM-20251020-00001550 | TT-20251020-01552 | Telecom | [7 empty] | 10/20/2025 15:09:01 | 10/20/2025 15:09:01 | 10/20/2025 21:09:01 | 1(2G) sites down under HAW2897-P3/HAW2897-P3 @ Sceco | 10/20/2025 15:00:37 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 15:00:34 | VIP | 2G |  | Sceco | 2G SA | HAW2897-P3 | FLM_TE | HAW2897 | Results: DOWN SITE HUB HAW2897-P3 HAW2897 Summary: Hub: HAW2897, Down Count: 1, Down Sites: HAW2897-P3 Alarm Summary: HAW2897 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 15:09:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000702 | PCM-20251020-00001551 | TT-20251020-01565 | Reference_EM | Region_1 | ARM2759 | ARM2759 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/20/2025 15:09:57 | 10/22/2025 02:05:04 | 10/20/2025 21:09:57 | Generator failure at ARM2759-P1_SRAN-PC @ Power Cube | 10/20/2025 14:59:42 | Major | 65114 | Generator failure | 10/20/2025 14:59:38 | P1 | SRAN | jubail | Power Cube | 2G NSA | ARM2759 | FLM_EM | [8 empty] | API | 10/20/2025 15:09:57 | 10/22/2025 02:05:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000707 | PCM-20251020-00001559 | TT-20251020-01345 | Telecom | Region_2 | RIY0670 | RIY0670 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/20/2025 15:12:55 | 10/21/2025 07:39:11 | 10/21/2025 03:12:55 | po_Link Down at RIY0792-RYQS0573 | 10/20/2025 13:43:08 | Minor | 15269 | LOS | 10/20/2025 13:43:08 | VIP | SRAN | riyadh | Sceco | IPRAN NSA | RIY0792 | FLM_TE | RIY0670 | We are observing PM Error and RSL degradation at link : RIY0670 DIR RIY2755 Kindly visit the link and perform the HC at mentioned link . also need to check power status at RIY0639 | PCM-20251020-00001528 | We are observing PM Error and RSL degradation at link : RIY0670 DIR RIY2755 Kindly visit the link and perform the HC at mentioned link . also need to check power status at RIY0639 | We are observing PM Error and RSL degradation at link : RIY0670 DIR RIY2755 Kindly visit the link and perform the HC at mentioned link . also need to check power status at RIY0639 |  |  |  | API | 10/20/2025 15:12:55 | 10/20/2025 18:08:48 | 10/21/2025 07:39:03 |  |  | 10/21/2025 07:39:11 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000710 | PCM-20251020-00001567 | TT-20251020-01583 | Telecom | Region_4 | JED0833 | JED0833 | Equipment | BSS_HW_Stuck | Reset RF Module | Fawzi Muneer Fawzi Mahmoud | 10/20/2025 15:17:42 | 10/21/2025 17:13:09 | 10/20/2025 21:17:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0833-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Generator_SG | 10/20/2025 15:16:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 15:16:32 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0833 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 15:17:42 | 10/21/2025 04:18:45 | 10/21/2025 04:18:53 | 10/21/2025 04:18:55 | 10/21/2025 04:19:02 | 10/21/2025 07:48:22 |  | Fawzi Muneer Fawzi Mahmoud |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000713 | PCM-20251020-00001579 | TT-20251020-01593 | Reference_telecom | Region_6 | ABBS0156 | ABBS0156 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 15:20:45 | 10/20/2025 15:44:17 | 10/21/2025 03:20:45 | Nokia Eband Observing ReplaceableUnitMissing-Card - 1 at ABBS0156_VRRP-10.74.122.132 | 07/07/2025 13:00:42 | Minor |  | LOF | 07/07/2025 13:00:42 | P3 | 2G | namas | Sceco | TX NSA | ABBS0156_VRRP-10.74.122.132 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:45 | 10/20/2025 15:44:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000715 | PCM-20251020-00001581 | TT-20251020-01595 | Reference_telecom | Region_6 | ABH0162 | ABH0162 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 15:20:48 | 10/20/2025 15:46:02 | 10/21/2025 03:20:48 | Nokia Eband Observing InternalCommunicationProblem-Port 7/3,LossOfSignal at ABH0162_03-10.10.155.44 | 10/19/2025 16:21:16 | Minor |  | LOF | 10/19/2025 16:21:16 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0162_03-10.10.155.44 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:48 | 10/20/2025 15:44:17 | 10/20/2025 15:45:43 |  |  | 10/20/2025 15:46:02 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000716 | PCM-20251020-00001582 | TT-20251020-01596 | Reference_telecom | Region_6 | ABSD0704 | ABSD0704 | Transsmission | MW_HW_stuck | Reset FAN | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 15:20:49 | 10/20/2025 15:46:26 | 10/21/2025 03:20:49 | Nokia Eband Observing HouseKeeping-auxIn-14,HouseKeeping-auxIn-13,HouseK at ABSD0704 _03-10.10.158.93 | 09/27/2025 08:57:46 | Minor |  | LOF | 09/27/2025 08:57:46 | P3 | 2G | abha | Sceco | TX NSA | ABSD0704 _03-10.10.158.93 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:49 | 10/20/2025 15:44:18 | 10/20/2025 15:46:11 |  |  | 10/20/2025 15:46:26 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000717 | PCM-20251020-00001584 | TT-20251020-01598 | Reference_telecom | Region_6 | BAH0948 | BAH0948 |  |  |  | Manzoor Ahmed | 10/20/2025 15:20:50 | 10/20/2025 16:36:22 | 10/21/2025 03:20:50 | Nokia Eband Observing LagPortDown-Port 1/3,DemFail-Port 1/3 at BAH0948-10.221.245.124 | 09/08/2025 14:54:26 | Minor |  | LOF | 09/08/2025 14:54:26 | P3 | 2G | Baha | Sceco | TX NSA | BAH0948-10.221.245.124 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:50 | 10/20/2025 16:36:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000718 | PCM-20251020-00001585 | TT-20251020-01599 | Reference_telecom | Region_6 | BHAB0828 | BHAB0828 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/20/2025 15:20:51 | 10/20/2025 18:27:44 | 10/21/2025 03:20:51 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A,LagPortDown- at BHAB0828-10.221.243.210 | 08/30/2025 16:05:55 | Minor |  | LOF | 08/30/2025 16:05:55 | P3 | 2G | makhwa | Sceco | TX NSA | BHAB0828-10.221.243.210 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:51 | 10/20/2025 18:27:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000719 | PCM-20251020-00001586 | TT-20251020-01600 | Reference_telecom | Region_6 | BHAB2041 | BHAB2041 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 10/20/2025 15:20:52 | 10/20/2025 17:07:40 | 10/21/2025 03:20:52 | Nokia Eband Observing LossOfSignal-Port 1/5 at BHAB2041-10.221.243.213 | 10/19/2025 23:38:08 | Minor |  | LOF | 10/19/2025 23:38:08 | P3 | 2G | Baha | Generator_SG | TX NSA | BHAB2041-10.221.243.213 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:52 | 10/20/2025 16:06:42 | 10/20/2025 17:07:18 |  |  | 10/20/2025 17:07:40 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000720 | PCM-20251020-00001587 | TT-20251020-01601 | Reference_telecom | Region_6 | BHAB2442 | BHAB2442 | Transsmission | SFP_Transmission | Reset SFP | SHAH KHALID | 10/20/2025 15:20:53 | 10/20/2025 17:08:27 | 10/21/2025 03:20:53 | Nokia Eband Observing Degrade-LAG 1,DemFail-Channel 1B,LagPortDown-Port at BHAB2442_02-10.221.243.55 | 10/19/2025 19:49:00 | Minor |  | LOF | 10/19/2025 19:49:00 | P3 | 2G | Albaha | Generator_SG | TX NSA | BHAB2442_02-10.221.243.55 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:53 | 10/20/2025 16:06:42 | 10/20/2025 17:07:52 |  |  | 10/20/2025 17:08:27 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251020000721 | PCM-20251020-00001588 | TT-20251020-01602 | Reference_telecom | Region_4 | BHMF0858 | BHMF0858 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/20/2025 15:20:54 | 10/20/2025 20:43:12 | 10/21/2025 03:20:54 | Nokia Eband Observing BatteryFail-BHMF0858_02,SecondaryBatteryFail-BHMF0 at BHMF0858_02-10.10.137.195 | 09/02/2025 17:41:52 | Minor |  | LOF | 09/02/2025 17:41:52 | P3 | 2G | qunfuddah | Generator_SG | TX NSA | BHMF0858_02-10.10.137.195 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:54 | 10/20/2025 16:30:52 | 10/20/2025 20:43:12 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000722 | PCM-20251020-00001589 | TT-20251020-01603 | Reference_telecom | Region_1 | DAM0274 | DAM0274 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/20/2025 15:20:55 | 10/20/2025 15:30:38 | 10/21/2025 03:20:55 | Nokia Eband Observing DemFail-Port 1/1 at DAM0274-10.3.126.74 | 04/29/2025 11:32:13 | Minor |  | LOF | 04/29/2025 11:32:13 | P1 | SRAN | dammam | Sceco | TX NSA | DAM0274-10.3.126.74 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:55 | 10/20/2025 15:30:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000723 | PCM-20251020-00001590 | TT-20251020-01604 | Reference_telecom | Region_6 | FIF0047 | FIF0047 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Ali | 10/20/2025 15:20:56 | 10/21/2025 17:08:56 | 10/21/2025 03:20:56 | Nokia Eband Observing Degrade-LAG 1,Degrade-LAG 2,DemFail-Channel 1B (SP at FIF0047_01-10.74.120.162 | 10/19/2025 17:02:08 | Minor |  | LOF | 10/19/2025 17:02:08 | P2 | 2G | dair | Sceco | TX NSA | FIF0047_01-10.74.120.162 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:56 | 10/20/2025 15:50:04 | 10/21/2025 17:08:26 |  |  | 10/21/2025 17:08:56 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000724 | PCM-20251020-00001591 | TT-20251020-01605 | Reference_telecom | Region_4 | HAW0331 | HAW0331 |  |  |  | Rashid Shafique | 10/20/2025 15:20:58 | 10/23/2025 17:30:54 | 10/21/2025 03:20:58 | Nokia Eband Observing LagPortDown-Port 4/1,LagPortDown-Port 3/1,DemFail- at HAW0331-02-10.21.68.213 | 10/18/2025 17:09:24 | Minor |  | LOF | 10/18/2025 17:09:24 | P2 | 2G | taif | Sceco | TX NSA | HAW0331-02-10.21.68.213 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:58 | 10/20/2025 18:25:17 | 10/23/2025 17:30:49 | 10/23/2025 17:30:51 | 10/23/2025 17:30:54 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000725 | PCM-20251020-00001592 | TT-20251020-01606 | Reference_telecom | Region_4 | HAW2371 | HAW2371 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 15:20:58 | 10/20/2025 19:42:59 | 10/21/2025 03:20:58 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.3.2 at HAW2371-10.3.225.198 | 08/28/2025 18:10:36 | Minor |  | LOF | 08/28/2025 18:10:36 | P3 | 2G | taif | Sceco | TX NSA | HAW2371-10.3.225.198 | FLM_TE | [8 empty] | API | 10/20/2025 15:20:58 | 10/20/2025 19:42:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000726 | PCM-20251020-00001593 | TT-20251020-01607 | Reference_telecom | Region_4 | JDJZ0761 | JDJZ0761 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 15:21:00 | 10/21/2025 10:51:34 | 10/21/2025 03:21:00 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 2 at JDJZ0761-NE_13-10.21.72.65 | 09/04/2025 14:48:08 | Minor |  | LOF | 09/04/2025 14:48:08 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JDJZ0761-NE_13-10.21.72.65 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:00 | 10/21/2025 10:51:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000727 | PCM-20251020-00001594 | TT-20251020-01608 | Reference_telecom | Region_4 | JED0001 | JED0001 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 15:21:01 | 10/21/2025 13:17:57 | 10/21/2025 03:21:01 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.21. at JED0001 _12-10.21.77.129 | 08/30/2025 19:37:07 | Minor |  | LOF | 08/30/2025 19:37:07 | P1 | 2G | jeddah | Sceco | TX NSA | JED0001 _12-10.21.77.129 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:01 | 10/21/2025 13:17:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000728 | PCM-20251020-00001595 | TT-20251020-01609 | Reference_telecom | Region_4 | JED0008 | JED0008 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 15:21:02 | 10/21/2025 13:17:58 | 10/21/2025 03:21:02 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.10. at JED0008-9 -10.10.148.65 | 09/22/2025 21:29:53 | Minor |  | LOF | 09/22/2025 21:29:53 | VIP | 2G | jeddah | Sceco | TX NSA | JED0008-9 -10.10.148.65 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:02 | 10/21/2025 13:17:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000729 | PCM-20251020-00001596 | TT-20251020-01610 | Reference_telecom | Region_4 | JED0014 | JED0014 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:21:04 | 10/20/2025 15:21:04 | 10/21/2025 03:21:04 | Nokia Eband Observing HouseKeeping-auxIn-14,HouseKeeping-auxIn-12,HouseK at JED0014_06-10.10.150.81 | 05/17/2025 00:15:39 | Minor |  | LOF | 05/17/2025 00:15:39 | VIP | 2G | jeddah | Sceco | TX NSA | JED0014_06-10.10.150.81 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000730 | PCM-20251020-00001597 | TT-20251020-01611 | Reference_telecom | Region_4 | JED0052 | JED0052 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 15:21:05 | 10/21/2025 10:51:34 | 10/21/2025 03:21:05 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 2 at JED0052-9-10.3.227.81 | 10/18/2025 16:48:25 | Minor |  | LOF | 10/18/2025 16:48:25 | P1 | 2G | jeddah | Sceco | TX NSA | JED0052-9-10.3.227.81 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:05 | 10/21/2025 10:51:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000732 | PCM-20251020-00001598 | TT-20251020-01612 | Reference_telecom | Region_4 | JED0198 | JED0198 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:21:06 | 10/20/2025 15:21:06 | 10/21/2025 03:21:06 | Nokia Eband Observing DemFail-Port 4/5,LagPortDown-Port 4/5,Degrade-LAG at JED0198 - 5-10.10.182.129 | 10/19/2025 20:38:34 | Minor |  | LOF | 10/19/2025 20:38:34 | P1 | 2G | jeddah | Sceco | TX NSA | JED0198 - 5-10.10.182.129 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:06 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000733 | PCM-20251020-00001599 | TT-20251020-01613 | Reference_telecom | Region_4 | JED0198 | JED0198 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:21:08 | 10/20/2025 15:21:08 | 10/21/2025 03:21:08 | Nokia Eband Observing DemFail-Channel 1A,DemFail-Channel 1B,BandwidthDeg at JED0198-8-10.10.182.177 | 10/18/2025 14:26:57 | Minor |  | LOF | 10/18/2025 14:26:57 | P1 | 2G | jeddah | Sceco | TX NSA | JED0198-8-10.10.182.177 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000734 | PCM-20251020-00001600 | TT-20251020-01614 | Reference_telecom | Region_4 | JED0218 | JED0218 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:21:09 | 10/20/2025 15:21:09 | 10/21/2025 03:21:09 | Nokia Eband Observing InternalCommunicationProblem-Port 4/5,ReplaceableU at JED0218_1-10.10.145.73 | 07/17/2025 15:28:41 | Minor |  | LOF | 07/17/2025 15:28:41 | VIP | 2G | jeddah | Sceco | TX NSA | JED0218_1-10.10.145.73 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000735 | PCM-20251020-00001601 | TT-20251020-01615 | Reference_telecom | Region_4 | JED0245 | JED0245 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 15:21:10 | 10/20/2025 16:09:58 | 10/21/2025 03:21:10 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.10. at JED0245-17-10.10.141.225 | 08/30/2025 11:55:21 | Minor |  | LOF | 08/30/2025 11:55:21 | P1 | 2G | jeddah | Sceco | TX NSA | JED0245-17-10.10.141.225 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:10 | 10/20/2025 16:09:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000736 | PCM-20251020-00001602 | TT-20251020-01616 | Reference_telecom | Region_4 | JED0330 | JED0330 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 15:21:11 | 10/20/2025 16:09:58 | 10/21/2025 03:21:11 | Nokia Eband Observing FanFailure-fanTray-1 at JED0330-7-10.1.230.113 | 07/09/2025 06:57:46 | Minor |  | LOF | 07/09/2025 06:57:46 | P1 | 2G | jeddah | Sceco | TX NSA | JED0330-7-10.1.230.113 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:11 | 10/20/2025 16:09:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000737 | PCM-20251020-00001603 | TT-20251020-01617 | Reference_telecom | Region_4 | JED0600 | JED0600 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 15:21:13 | 10/20/2025 16:09:59 | 10/21/2025 03:21:13 | Nokia Eband Observing DemXpicLOS-Port 4/5,DemFail-Port 4/5,DemXpicLOS-Po at JED0600-14-10.3.234.164 | 08/28/2025 14:11:27 | Minor |  | LOF | 08/28/2025 14:11:27 | P1 | 2G | jeddah | Sceco | TX NSA | JED0600-14-10.3.234.164 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:13 | 10/20/2025 16:09:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000738 | PCM-20251020-00001604 | TT-20251020-01618 | Reference_telecom | Region_4 | JED0604 | JED0604 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 15:21:14 | 10/20/2025 16:09:59 | 10/21/2025 03:21:14 | Nokia Eband Observing Degrade-LAG 3,LagPortDown-Port 4/5 at JED0604-7-10.10.178.177 | 09/22/2025 09:08:15 | Minor |  | LOF | 09/22/2025 09:08:15 | P1 | 2G | jeddah | Sceco | TX NSA | JED0604-7-10.10.178.177 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:14 | 10/20/2025 16:09:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000739 | PCM-20251020-00001605 | TT-20251020-01619 | Reference_telecom | Region_4 | JED0607 | JED0607 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:21:15 | 10/20/2025 15:21:15 | 10/21/2025 03:21:15 | Nokia Eband Observing LossOfSignal-Port 5/5 at JED0607-10.1.225.146 | 09/18/2025 18:09:51 | Minor |  | LOF | 09/18/2025 18:09:51 | P2 | 2G | jeddah | Sceco | TX NSA | JED0607-10.1.225.146 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000740 | PCM-20251020-00001606 | TT-20251020-01620 | Reference_telecom | Region_4 | JED0767 | JED0767 |  |  |  | Mohammed Ramadan A Abu Abid | 10/20/2025 15:21:16 | 10/20/2025 15:30:06 | 10/21/2025 03:21:16 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at JED0767-1-10.1.228.35 | 10/15/2025 00:41:40 | Minor |  | LOF | 10/15/2025 00:41:40 | P2 | 2G | jeddah | Sceco | TX NSA | JED0767-1-10.1.228.35 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:16 | 10/20/2025 15:30:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000741 | PCM-20251020-00001607 | TT-20251020-01621 | Reference_telecom | Region_4 | JED0841 | JED0841 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 15:21:17 | 10/23/2025 10:50:31 | 10/21/2025 03:21:17 | Nokia Eband Observing DemXpicLOS-Port 3/5,LossOfSignal-Port 7/3,LossOfSi at JED0841_01-10.21.76.98 | 09/02/2025 09:37:41 | Minor |  | LOF | 09/02/2025 09:37:41 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0841_01-10.21.76.98 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:17 | 10/21/2025 13:17:59 | 10/23/2025 10:28:41 | 10/23/2025 10:50:28 | 10/23/2025 10:50:31 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000742 | PCM-20251020-00001608 | TT-20251020-01622 | Reference_telecom | Region_4 | JED0841 | JED0841 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 15:21:18 | 10/23/2025 10:50:44 | 10/21/2025 03:21:18 | Nokia Eband Observing DialogFailure-Port 3/5,DialogFailure-Port 7/3,DemX at JED0841_02-10.21.76.99 | 09/02/2025 09:37:41 | Minor |  | LOF | 09/02/2025 09:37:41 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0841_02-10.21.76.99 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:18 | 10/21/2025 13:17:59 | 10/23/2025 10:14:53 | 10/23/2025 10:50:42 | 10/23/2025 10:50:44 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000743 | PCM-20251020-00001609 | TT-20251020-01623 | Reference_telecom | Region_4 | JED0919 | JED0919 |  |  |  | Nazeer Mohammed | 10/20/2025 15:21:19 | 10/21/2025 11:49:36 | 10/21/2025 03:21:19 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.21. at JED0919_07-10.21.77.177 | 09/21/2025 05:47:51 | Minor |  | LOF | 09/21/2025 05:47:51 | VIP | 2G | jeddah | Generator_DG | TX NSA | JED0919_07-10.21.77.177 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:19 | 10/21/2025 11:49:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000744 | PCM-20251020-00001610 | TT-20251020-01624 | Reference_telecom | Region_4 | JED0919 | JED0919 |  |  |  | Nazeer Mohammed | 10/20/2025 15:21:20 | 10/21/2025 11:49:36 | 10/21/2025 03:21:20 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at JED0919-10-10.1.236.225 | 10/19/2025 13:09:29 | Minor |  | LOF | 10/19/2025 13:09:29 | VIP | 2G | jeddah | Generator_DG | TX NSA | JED0919-10-10.1.236.225 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:20 | 10/21/2025 11:49:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000745 | PCM-20251020-00001611 | TT-20251020-01625 | Reference_telecom | Region_4 | JED2063 | JED2063 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:21:21 | 10/20/2025 15:21:21 | 10/21/2025 03:21:21 | Nokia Eband Observing DemXpicLOS-Port 3/5,LossOfSignal-Port 3/5,Internal at JED2063 -10.10.182.130 | 10/19/2025 20:38:36 | Minor |  | LOF | 10/19/2025 20:38:36 | P2 | 2G | jeddah | Sceco | TX NSA | JED2063 -10.10.182.130 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000746 | PCM-20251020-00001612 | TT-20251020-01626 | Reference_telecom | Region_4 | JED2108 | JED2108 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 15:21:22 | 10/21/2025 10:51:35 | 10/21/2025 03:21:22 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at JED2108-10.21.75.227 | 10/19/2025 18:48:25 | Minor |  | LOF | 10/19/2025 18:48:25 | P3 | 2G | jeddah | Sceco | TX NSA | JED2108-10.21.75.227 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:22 | 10/21/2025 10:51:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000747 | PCM-20251020-00001613 | TT-20251020-01627 | Reference_telecom | Region_4 | JED2297 | JED2297 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 15:21:24 | 10/22/2025 17:41:39 | 10/21/2025 03:21:24 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at JED2297-10.10.146.131 | 10/15/2025 21:41:04 | Minor |  | LOF | 10/15/2025 21:41:04 | P3 | 2G | jeddah | Sceco | TX NSA | JED2297-10.10.146.131 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:24 | 10/20/2025 16:10:00 | 10/22/2025 17:00:07 | 10/22/2025 17:00:09 | 10/22/2025 17:41:39 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000748 | PCM-20251020-00001614 | TT-20251020-01628 | Reference_telecom | Region_4 | JED2886 | JED2886 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 15:21:24 | 10/21/2025 10:51:35 | 10/21/2025 03:21:24 | Nokia Eband Observing LagPortDown-Port 1/3,DemFail-Port 1/3,Degrade-LAG at JED2886-10.10.154.142 | 10/16/2025 05:03:47 | Minor |  | LOF | 10/16/2025 05:03:47 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2886-10.10.154.142 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:24 | 10/21/2025 10:51:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000749 | PCM-20251020-00001615 | TT-20251020-01629 | Reference_telecom | Region_6 | JIZ0002 | JIZ0002 |  |  |  | Osama Hadi | 10/20/2025 15:21:25 | 10/20/2025 16:36:46 | 10/21/2025 03:21:25 | Nokia Eband Observing NodeVersionMismatch-JIZ0002 at JIZ0002-10.221.227.12 | 10/16/2025 15:18:38 | Minor |  | LOF | 10/16/2025 15:18:38 | P1 | 2G | jizan | Sceco | TX NSA | JIZ0002-10.221.227.12 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:25 | 10/20/2025 16:36:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000750 | PCM-20251020-00001617 | TT-20251020-01630 | Reference_telecom | Region_6 | JIZ0012 | JIZ0012 |  |  |  | Osama Hadi | 10/20/2025 15:21:27 | 10/20/2025 16:36:47 | 10/21/2025 03:21:27 | Nokia Eband Observing Degrade-LAG 1,LagPortDown-Port 4/5 at JIZ0012-10.10.154.98 | 09/30/2025 20:18:56 | Minor |  | LOF | 09/30/2025 20:18:56 | P1 | 2G | jizan | Sceco | TX NSA | JIZ0012-10.10.154.98 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:27 | 10/20/2025 16:36:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000751 | PCM-20251020-00001618 | TT-20251020-01631 | Reference_telecom | Region_4 | TAF0154 | TAF0154 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 15:21:29 | 10/20/2025 19:43:01 | 10/21/2025 03:21:29 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 1 at TAF0154-6-10.10.187.209 | 09/02/2025 09:31:10 | Minor |  | LOF | 09/02/2025 09:31:10 | P1 | 2G | taif | Sceco | TX NSA | TAF0154-6-10.10.187.209 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:29 | 10/20/2025 19:43:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000752 | PCM-20251020-00001619 | TT-20251020-01632 | Reference_telecom | Region_2 | TUM0578 | TUM0578 |  |  |  | Muhammad Tahir Abdulrazzaq | 10/20/2025 15:21:29 | 10/21/2025 14:50:44 | 10/21/2025 03:21:29 | Nokia Eband Observing DemFail-Port 1/1 at TUM0578-10.3.126.234 | 09/30/2025 10:32:07 | Minor |  | LOF | 09/30/2025 10:32:07 | P2 | SRAN | rumah | Sceco | TX NSA | TUM0578-10.3.126.234 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:29 | 10/21/2025 14:50:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000753 | PCM-20251020-00001620 | TT-20251020-01633 | Reference_telecom | Region_4 | TAF0176 | TAF0176 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Asad Ullah Rahim Said | 10/20/2025 15:21:31 | 10/23/2025 15:21:28 | 10/21/2025 03:21:31 | Nokia Eband Observing Degrade-LAG 1,LagPortDown-Port 4/5 at TAF0176-8-10.10.186.113 | 09/20/2025 15:36:38 | Minor |  | LOF | 09/20/2025 15:36:38 | P1 | 2G | taif | Generator_DG | TX NSA | TAF0176-8-10.10.186.113 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:31 | 10/23/2025 14:18:38 | 10/23/2025 14:19:26 | 10/23/2025 14:19:29 | 10/23/2025 14:19:33 | 10/23/2025 15:21:28 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Accept | CM20251020000754 | PCM-20251020-00001621 | TT-20251020-01634 | Reference_telecom | Region_6 | QIS0031 | QIS0031 |  |  |  | Muhammad Ali | 10/20/2025 15:21:32 | 10/21/2025 17:11:18 | 10/21/2025 03:21:32 | Nokia Eband Observing Degrade-LAG 2,ReplaceableUnitProblem-Card - 3 at QIS0031_2-10.74.121.177 | 10/19/2025 16:52:10 | Minor |  | LOF | 10/19/2025 16:52:10 | P1 | 2G | jizan | Sceco | TX NSA | QIS0031_2-10.74.121.177 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:32 | 10/20/2025 15:50:04 | 10/21/2025 17:11:18 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000755 | PCM-20251020-00001622 | TT-20251020-01635 | Reference_telecom | Region_5 | MAK0928 | MAK0928 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/20/2025 15:21:33 | 10/21/2025 19:57:03 | 10/21/2025 03:21:33 | Nokia Eband Observing ReplaceableUnitProblem-Card - 2 at MAK0928-RADIO-10.10.139.83 | 06/14/2025 03:03:27 | Minor |  | LOF | 06/14/2025 03:03:27 | P3 | 2G | makkah | Sceco | TX NSA | MAK0928-RADIO-10.10.139.83 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:33 | 10/21/2025 19:57:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000756 | PCM-20251020-00001623 | TT-20251020-01636 | Reference_telecom | Region_5 | MAK0014 | MAK0014 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/20/2025 15:21:34 | 10/21/2025 19:57:04 | 10/21/2025 03:21:34 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 2 at MAK0014_16-10.21.75.49 | 09/27/2025 15:56:08 | Minor |  | LOF | 09/27/2025 15:56:08 | P1 | 2G | makkah | Sceco | TX NSA | MAK0014_16-10.21.75.49 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:34 | 10/21/2025 19:57:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000757 | PCM-20251020-00001624 | TT-20251020-01637 | Reference_telecom | Region_5 | MAK0066 | MAK0066 |  |  |  | Atif Javed Javed Hussain | 10/20/2025 15:21:35 | 10/20/2025 15:45:29 | 10/21/2025 03:21:35 | Nokia Eband Observing Degrade-LAG 1,LagPortDown-Port 4/5 at MAK0066-13-10.10.143.33 | 10/07/2025 15:02:02 | Minor |  | LOF | 10/07/2025 15:02:02 | P1 | 2G | makkah | Sceco | TX NSA | MAK0066-13-10.10.143.33 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:35 | 10/20/2025 15:45:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000759 | PCM-20251020-00001626 | TT-20251020-01639 | Reference_telecom | [7 empty] | 10/20/2025 15:21:37 | 10/20/2025 15:21:37 | 10/21/2025 03:21:37 | Nokia Eband Observing LossOfSignal-Port 1/5 at TFBH2218-10.10.143.244 | 09/14/2025 17:40:27 | Minor |  | LOF | 09/14/2025 17:40:27 | P3 | 2G |  | Sceco | TX NSA | TFBH2218-10.10.143.244 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000760 | PCM-20251020-00001627 | TT-20251020-01640 | Reference_telecom | Region_5 | MAK0588 | MAK0588 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/20/2025 15:21:38 | 10/20/2025 15:21:38 | 10/21/2025 03:21:38 | Nokia Eband Observing DemFail-Port 5/5,LagPortDown-Port 5/5,Degrade-LAG at MAK0588-1-10.10.186.163 | 10/18/2025 15:51:25 | Minor |  | LOF | 10/18/2025 15:51:25 | P1 | 2G | makkah | Sceco | TX NSA | MAK0588-1-10.10.186.163 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000761 | PCM-20251020-00001628 | TT-20251020-01641 | Reference_telecom | Region_5 | MAK0011 | MAK0011 |  |  |  | Atif Javed Javed Hussain | 10/20/2025 15:21:40 | 10/20/2025 15:45:29 | 10/21/2025 03:21:40 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 1 at MAK0011-7-10.10.147.81 | 09/08/2025 06:34:53 | Minor |  | LOF | 09/08/2025 06:34:53 | VIP | 2G | makkah | Sceco | TX NSA | MAK0011-7-10.10.147.81 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:40 | 10/20/2025 15:45:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000762 | PCM-20251020-00001629 | TT-20251020-01642 | Reference_telecom | Region_5 | MAK0686 | MAK0686 | Transsmission | MW_HW_stuck | Reset FAN | Muhammad Saleem Iqbal | 10/20/2025 15:21:41 | 10/22/2025 23:21:37 | 10/21/2025 03:21:41 | Nokia Eband Observing FanFailure-fanTray-1,ReplaceableUnitProblem-fanTra at MAK0686-10.10.143.200 | 10/19/2025 16:50:32 | Minor |  | LOF | 10/19/2025 16:50:32 | P2 | 2G | makkah | Sceco | TX NSA | MAK0686-10.10.143.200 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:41 | 10/22/2025 21:35:32 | 10/22/2025 22:09:26 | 10/22/2025 22:09:36 | 10/22/2025 22:20:05 | 10/22/2025 23:21:37 |  | Muhammad Saleem Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000763 | PCM-20251020-00001630 | TT-20251020-01643 | Reference_telecom | Region_5 | MAK0258 | MAK0258 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/20/2025 15:21:42 | 10/21/2025 19:57:05 | 10/21/2025 03:21:42 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A,DemFail-Port at MAK0258_01-10.3.235.52 | 10/10/2025 14:48:01 | Minor |  | LOF | 10/10/2025 14:48:01 | P3 | 2G | makkah | Sceco | TX NSA | MAK0258_01-10.3.235.52 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:42 | 10/21/2025 19:57:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000764 | PCM-20251020-00001631 | TT-20251020-01644 | Reference_telecom | Region_6 | QIS0031 | QIS0031 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Ali | 10/20/2025 15:21:43 | 10/21/2025 17:03:45 | 10/21/2025 03:21:43 | Nokia Eband Observing LossOfSignal-Port 4/5,LossOfSignal-Port 3/8,Intern at QIS0031_04-10.74.120.161 | 10/19/2025 17:02:25 | Minor |  | LOF | 10/19/2025 17:02:25 | P1 | 2G | jizan | Sceco | TX NSA | QIS0031_04-10.74.120.161 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:43 | 10/20/2025 15:50:05 | 10/21/2025 14:39:03 | 10/21/2025 14:39:07 | 10/21/2025 15:20:00 | 10/21/2025 17:03:45 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000765 | PCM-20251020-00001632 | TT-20251020-01645 | Reference_telecom | Region_5 | JUSH9060 | JUSH9060 |  |  |  | Amr Abdulla Ali Othman | 10/20/2025 15:21:44 | 10/20/2025 15:21:44 | 10/21/2025 03:21:44 | Nokia Eband Observing SecondaryBatteryFail-JUSH9060 at JUSH9060-10.3.229.222 | 10/05/2025 16:28:36 | Minor |  | LOF | 10/05/2025 16:28:36 | P3 | Repeater | makkah | Generator_SG | TX NSA | JUSH9060-10.3.229.222 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000766 | PCM-20251020-00001633 | TT-20251020-01646 | Reference_telecom | Region_6 | TNM0727 | TNM0727 |  |  |  | Fawad Khan | 10/20/2025 15:21:46 | 10/20/2025 17:11:29 | 10/21/2025 03:21:46 | Nokia Eband Observing DemFail-Channel 1B,DemFail-Channel 1A at TNM0727_02-10.221.247.85 | 10/19/2025 16:35:27 | Minor |  | LOF | 10/19/2025 16:35:27 | P2 | 2G | mohail | Sceco | TX NSA | TNM0727_02-10.221.247.85 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:46 | 10/20/2025 17:11:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000767 | PCM-20251020-00001634 | TT-20251020-01647 | Reference_telecom | Region_5 | MAK0654 | MAK0654 | Transsmission | MW_HW_stuck | Reset Service Interface Board | Sher Ali Munir | 10/20/2025 15:21:47 | 10/23/2025 00:16:22 | 10/21/2025 03:21:47 | Nokia Eband Observing ReplaceableUnitMissing-Card - 2 at MAK0654_04-10.3.227.10 | 09/25/2025 13:18:35 | Minor |  | LOF | 09/25/2025 13:18:35 | P2 | 2G | makkah | Sceco | TX NSA | MAK0654_04-10.3.227.10 | FLM_TE | [8 empty] | API | 10/20/2025 15:21:47 | 10/22/2025 21:39:38 | 10/22/2025 22:19:02 | 10/22/2025 22:19:07 | 10/22/2025 22:19:12 | 10/23/2025 00:16:22 |  | Sher Ali Munir |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020000771 | PCM-20251020-00001645 | TT-20251020-01656 | EM | [7 empty] | 10/20/2025 15:24:56 | 10/20/2025 15:24:56 | 10/20/2025 19:24:56 | HIGH TEMP 32 + HIGH TEMP 40 + FIRE ALARM at SWAMLA-SEC0023_HYB @ Sceco | 10/20/2025 15:23:26 | Critical | 1-12307 | HIGH TEMP 32 + HIGH TEMP 40 + FIRE ALARM | 10/20/2025 15:23:17 | P1 | DWDM |  | Sceco | DWDM NSA | SWAMLA | FLM_EM | [5 empty] | 0-TO SHB-SEC0018(1-A)-72-E1EFI-[HIGH TEMP 32 + HIGH TEMP 40 + FIRE ALARM]:1 |  |  | API | 10/20/2025 15:24:56 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000774 | PCM-20251020-00001649 | TT-20251020-01564 | Telecom | Region_4 | RYMK0528 | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 15:26:50 | 10/20/2025 19:43:01 | 10/20/2025 21:26:50 | 1(2G) 2(5G) sites down under TURY0830-GSM-P3,QSDH0723-P3/QSDH0723-P3 @ Generator_SG | 10/20/2025 15:06:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 15:06:01 | P1 | 2G | taif | Generator_SG | 2G SA | TURY0830-GSM-P3 5G,QSDH0723-P3 2G_5G | FLM_TE | RYMK0528 | HUB: TURY0830 We are observing no issue from our end at HUB ,kindly check locally. HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . | PCM-20251020-00001560 | HUB: TURY0830 We are observing no issue from our end at HUB ,kindly check locally. HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . | HUB: TURY0830 We are observing no issue from our end at HUB ,kindly check locally. HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . |  | sites down |  | API | 10/20/2025 15:26:50 | 10/20/2025 19:43:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000777 | PCM-20251020-00001653 | TT-20251020-01660 | EM | Region_1 | JBL0465 | JBL0465 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/20/2025 15:28:02 | 10/20/2025 16:45:38 | 10/20/2025 19:28:02 | Door opening alarm at JBL0465-RPT2-P1-Core-DIA-WDM @ Sceco_STB | 10/20/2025 15:27:49 | Critical | 65101 | Door opening alarm | 10/20/2025 15:27:45 | P1 | SRAN | jubail | Sceco_STB | 3G NSA | JBL0465 | FLM_EM | [8 empty] | API | 10/20/2025 15:28:02 | 10/20/2025 16:45:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000780 | PCM-20251020-00001663 | TT-20251020-01667 | Telecom | Region_4 | JED1MC2130 | JED2130 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 15:31:08 | 10/20/2025 15:31:08 | 10/20/2025 21:31:08 | CELL SERVICE PROBLEM (BTS configuration error (not enough HW for LCR)) at JED1MC2130-NR3.5-P3 @ Sceco | 10/20/2025 15:26:27 | Major | 7114 | CELL SERVICE PROBLEM | 10/20/2025 15:26:13 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MC2130 | FLM_TE | [5 empty] | BTS configuration error (not enough HW for LCR) |  |  | API | 10/20/2025 15:31:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000781 | PCM-20251020-00001664 | TT-20251020-01668 | Telecom | Region_1 | DMM-BDR-02 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/20/2025 15:31:40 | 10/20/2025 15:31:40 | 10/21/2025 03:31:40 | Bad Package Error Rising at DMM-BDR-02 @ Sceco_STB | 10/20/2025 15:31:04 | Minor | 101-2501403 | Bad Package Error Rising | 10/20/2025 15:30:54 | P1 | IPBB | dammam | Sceco_STB | IPRAN NSA | DMM-BDR-02 | FLM_TE | [8 empty] | API | 10/20/2025 15:31:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000794 | PCM-20251020-00001694 | TT-20251020-01683 | Telecom | Region_4 | RNRY0660 | RNRY0660 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmad Kamal Abdelmawla | 10/20/2025 15:41:01 | 10/21/2025 10:09:59 | 10/20/2025 21:41:01 | 1(5G) sites down under RNRY0660-GSM-P3 @ Generator_SG | 10/20/2025 15:32:51 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 15:32:48 | P3 | 2G | taif | Generator_SG | 5G SA | RNRY0660-GSM-P3 | FLM_TE | RNRY0660 | Results: DOWN SITE HUB RNRY0660-GSM-P3 RNRY0660 Summary: Hub: RNRY0660, Down Count: 1, Down Sites: RNRY0660-GSM-P3 Alarm Summary: RNRY0660 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.90.12:8080] [URL:http://10.98.90.12:8080/NE3S/1.0/] | sites down |  | API | 10/20/2025 15:41:01 | 10/20/2025 23:38:47 | 10/21/2025 10:09:52 |  |  | 10/21/2025 10:09:59 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000796 | PCM-20251020-00001695 | TT-20251020-01694 | EM | Region_1 | JB1 | JB1 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/20/2025 15:41:28 | 10/20/2025 16:45:38 | 10/20/2025 19:41:28 | Door opening alarm BSC New shelter at JB1-Shelter 6-WDM-Core-P1 @ Sceco_STB | 10/20/2025 15:40:53 | Critical | 65134 | Door opening alarm BSC New shelter | 10/20/2025 15:40:50 | P1 | BSC | jubail | Sceco_STB | 2G NSA | JB1 | FLM_EM | [8 empty] | API | 10/20/2025 15:41:28 | 10/20/2025 16:45:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251020000809 | PCM-20251020-00001724 | TT-20251020-01720 | EM | [7 empty] | 10/20/2025 15:51:49 | 10/20/2025 15:51:49 | 10/20/2025 19:51:49 | DOOR OPEN at BISHA-SEC0012_OCS @ Sceco | 10/20/2025 15:51:36 | Critical | 1-12307 | DOOR OPEN | 10/20/2025 15:51:26 | P1 | DWDM |  | Sceco | DWDM NSA | BISHA | FLM_EM | [5 empty] | 0-TO AL-ALAYA-SEC0011(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/20/2025 15:51:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000812 | PCM-20251020-00001746 | TT-20251020-01738 | Reference_telecom | Region_5 | MLK1M3705 | MLK0705 |  |  |  | Hassan Ezzelarab Ali Mohamed | 10/20/2025 15:58:31 | 10/20/2025 15:58:31 | 10/21/2025 03:58:31 | BASE STATION NOTIFICATION (Fan failure) at MLK1M3705-P2-USF @ Generator_SG | 10/20/2025 15:28:43 | Minor | 7652 | BASE STATION NOTIFICATION | 10/20/2025 15:28:26 | P2 | 3G | makkah | Generator_SG | 3G NSA | MLK1M3705 | FLM_TE | [5 empty] | Fan failure |  |  | API | 10/20/2025 15:58:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000813 | PCM-20251020-00001747 | TT-20251020-01743 | EM | Region_1 | DAM2M3636 | DAM0636 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/20/2025 15:59:33 | 10/20/2025 16:23:54 | 10/21/2025 03:59:33 | Mains Failure at DAM2M3636-P2 @ Sceco | 10/20/2025 15:49:40 | Minor | 65109 | Mains Failure | 10/20/2025 15:49:36 | P2 | 3G | dammam | Sceco | 3G NSA | DAM2M3636 | FLM_EM | [8 empty] | API | 10/20/2025 15:59:33 | 10/20/2025 16:23:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000816 | PCM-20251020-00001753 | TT-20251020-01748 | EM | Region_1 | KFKM0793 | KFKM0793 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mahmoud Youssef Mohamed Ahmed | 10/20/2025 16:00:36 | 10/22/2025 06:04:17 | 10/21/2025 04:00:36 | Mains Failure at KFKM0793-P3_SRAN @ Generator_SG | 10/20/2025 15:58:47 | Minor | 65109 | Mains Failure | 10/20/2025 15:46:50 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0793 | FLM_EM | [8 empty] | API | 10/20/2025 16:00:36 | 10/22/2025 06:02:22 | 10/22/2025 06:04:05 |  |  | 10/22/2025 06:04:17 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000817 | PCM-20251020-00001754 | TT-20251020-01718 | Telecom | Region_4 | YLM0756 | YLM0756 |  |  |  | Riasat Ali Allah Baksh | 10/20/2025 16:01:12 | 10/20/2025 21:24:54 | 10/20/2025 20:01:12 | 4(2G) 4(3G) 2(5G) sites down under MLJI0744-P3,YLM0746-P3,YLM0391-P1,YLM0735-P3/YLM1M3735-P3 @ Generator_SG | 10/20/2025 15:48:20 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/20/2025 15:47:41 | P1 | 2G | alaith | Generator_DG | 3G_5G SA | MLJI0744-GSM-UMTS-P3 5G,YLM0735-P3 3G,YLM0391-P1 3G,YLM0746-P3 3G | FLM_TE | YLM0756 | HUB: YLM0756 We observing PM errors and RSL degradation at HUB DIR FE ,kindly check locally | PCM-20251020-00001740 | HUB: YLM0756 We observing PM errors and RSL degradation at HUB DIR FE ,kindly check locally | HUB: YLM0756 We observing PM errors and RSL degradation at HUB DIR FE ,kindly check locally |  | sites down |  | API | 10/20/2025 16:01:12 | 10/20/2025 21:24:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000818 | PCM-20251020-00001755 | TT-20251020-01733 | EM | Region_1 | HFR2U6398 | HFR6098 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 16:01:32 | 10/20/2025 16:10:01 | 10/20/2025 22:01:32 | 1(3G/LTE) sites down under HFR6098-P3/HB1RNCH01 @ Sceco | 10/20/2025 15:53:17 | Major | 22214 | NodeB Unavailable | 10/20/2025 15:53:14 | P3 | 3G | hafr | Sceco | 3G SA | HFR6098-P3 | FLM_TE | HFR6098 | Results: DOWN SITE HUB HFR6098-P3 HFR6098 Summary: Hub: HFR6098, Down Count: 1, Down Sites: HFR6098-P3 Alarm Summary: HFR6098 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 16:01:32 | 10/20/2025 16:03:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000825 | PCM-20251020-00001766 | TT-20251020-01716 | EM | Region_4 | JED2015 | JED2015 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 16:07:16 | 10/21/2025 10:51:36 | 10/20/2025 22:07:16 | 1(2G/5G) sites down under JED2015-P3/JED2015-P3 @ Sceco | 10/20/2025 15:46:10 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 15:46:07 | P3 | 2G | jeddah | Sceco | 2G_5G SA | JED2015-P3 | FLM_TE | JED2015 | Results: DOWN SITE HUB JED2015-P3 JED2015 Summary: Hub: JED2015, Down Count: 1, Down Sites: JED2015-P3 Alarm Summary: JED2015 No Active Alarm on HUB | PCM-20251020-00001737 | No Power Issue | No Power Issue |  | sites down |  | API | 10/20/2025 16:07:16 | 10/21/2025 10:51:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000826 | PCM-20251020-00001768 | TT-20251020-01762 | EM | Region_6 | BCH1M8207 | BCH2207 |  |  |  | Fathy Mohamed | 10/20/2025 16:08:20 | 10/20/2025 16:41:35 | 10/21/2025 04:08:20 | RECTIFIER MAINS POWER FAILURE at BCH1M8207-G9-L8-SBTS-P3 @ Generator_SG | 10/20/2025 16:00:07 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/20/2025 15:59:54 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BCH1M8207 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/20/2025 16:08:20 | 10/20/2025 16:41:35 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000830 | PCM-20251020-00001777 | TT-20251020-01757 | EM | Region_6 | BKR2283 | BKR2283 |  |  |  | Fathy Mohamed | 10/20/2025 16:11:04 | 10/20/2025 16:41:36 | 10/20/2025 22:11:04 | 1(2G/LTE) sites down under BKR2283-P3/BKR2283-P3 @ Sceco | 10/20/2025 16:03:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 16:02:59 | P3 | 2G | Baha | Sceco | 2G_LTE SA | BKR2283-P3 | FLM_EM | BKR2283 | Results: DOWN SITE HUB BKR2283-P3 BKR2283 Summary: Hub: BKR2283, Down Count: 1, Down Sites: BKR2283-P3 Alarm Summary: BKR2283 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 16:11:04 | 10/20/2025 16:41:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000831 | PCM-20251020-00001778 | TT-20251020-01758 | EM | Region_6 | BCH2207 | BCH2207 |  |  |  | Fathy Mohamed | 10/20/2025 16:11:11 | 10/20/2025 16:41:36 | 10/20/2025 22:11:11 | 1(2G/LTE) sites down under BCH2207-P3/BCH2207-P3 @ Generator_SG | 10/20/2025 16:03:05 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 16:02:59 | P3 | 2G | Albaha | Generator_SG | 2G_LTE SA | BCH2207-P3 | FLM_EM | BCH2207 | Results: DOWN SITE HUB BCH2207-P3 BCH2207 Summary: Hub: BCH2207, Down Count: 1, Down Sites: BCH2207-P3 Alarm Summary: BCH2207 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 16:11:11 | 10/20/2025 16:41:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000832 | PCM-20251020-00001779 | TT-20251020-01760 | EM | Region_6 | BKR2214 | BKR2214 |  |  |  | Fathy Mohamed | 10/20/2025 16:11:18 | 10/23/2025 13:11:45 | 10/20/2025 22:11:18 | 2(2G/LTE) sites down under BCH2213,BKR2214-P3/BKR2214-P3 @ Generator_SG | 10/20/2025 16:03:02 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 16:02:59 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BKR2214-P3 | FLM_EM | BKR2214 | Results: DOWN SITE HUB BKR2214-P3 BKR2214 Summary: Hub: BKR2214, Down Count: 1, Down Sites: BKR2214-P3 Alarm Summary: BKR2214 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 16:11:18 | 10/20/2025 16:41:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000833 | PCM-20251020-00001780 | TT-20251020-01752 | Telecom | Region_4 | YLM0756 | YLM0756 |  |  |  | Riasat Ali Allah Baksh | 10/20/2025 16:11:25 | 10/20/2025 21:24:57 | 10/20/2025 20:11:25 | 5(2G) 5(3G) 1(LTE) 5(5G) sites down under YLM2368-P3 @ Generator_DG | 10/20/2025 16:01:15 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 16:01:10 | P1 | 2G | alaith | Generator_DG | 2G_3G SA | YLM0768-P3 2G_3G,YLM0789-P3 2G_3G,YLM0745-P3 2G_3G,YLM0756-P1 2G_3G,YLM2368-P3 2G_3G | FLM_TE | YLM0756 | HUB: YLM0756 We observing PM errors and RSL degradation at HUB DIR FE ,kindly check locally | PCM-20251020-00001770 | HUB: YLM0756 We observing PM errors and RSL degradation at HUB DIR FE ,kindly check locally | HUB: YLM0756 We observing PM errors and RSL degradation at HUB DIR FE ,kindly check locally |  | sites down |  | API | 10/20/2025 16:11:25 | 10/20/2025 21:24:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000834 | PCM-20251020-00001782 | TT-20251020-00437 | Telecom | Region_1 | JBKH2M3603 | JBKH0603 |  |  |  | Meraj Husain Idd Baksh | 10/20/2025 16:12:22 | 10/20/2025 17:29:14 | 10/21/2025 04:12:22 | RF Unit Maintenance Link Failure at JBKH2M3603-P2 @ Sceco | 10/20/2025 04:58:50 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/20/2025 04:57:07 | P2 | 3G | dammam | Sceco | 2G NSA | JBKH2M3603 | FLM_TE |  |  | PCM-20251020-00001716 | Dear FLM, Kindly check locally as alarm repeated 5 times | Dear FLM, Kindly check locally as alarm repeated 5 times |  |  |  | API | 10/20/2025 16:12:22 | 10/20/2025 17:29:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000837 | PCM-20251020-00001788 | TT-20251020-01778 | Telecom | Region_1 | RST0351 | RST0351 |  |  |  | Rafiq Ahmed Elturifi | 10/20/2025 16:15:08 | 10/20/2025 17:16:45 | 10/21/2025 04:15:08 | RTN MW HC for link RST0351-RST0089 Modem Down | 10/20/2025 16:14:23 | Minor | 1-631 | MW_LOF | 10/20/2025 16:14:29 | P1 | SRAN | jubail | Sceco | TX NSA | RST0351-RST0089 | FLM_TE | [8 empty] | API | 10/20/2025 16:15:08 | 10/20/2025 17:16:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000838 | PCM-20251020-00001789 | TT-20251020-01550 | Telecom | Region_5 | MAK0231 | MAK0231 |  |  |  | Atif Javed Javed Hussain | 10/20/2025 16:15:24 | 10/20/2025 19:29:23 | 10/20/2025 18:15:24 | 9(2G) 8(LTE) 2(5G) sites down under MAK0217-P1-VIP-HRM @ Sceco | 10/20/2025 14:58:51 | Emergency | 7706 | BTS O&M LINK FAILURE | 10/20/2025 14:58:48 | VIP | 2G | makkah | Sceco | 2G_LTE_5G SA | MAK6074-P1-VIP-HRM 2G_LTE,MAK6054-P1-VIP-HRM 2G_LTE,MAK6073-P1-VIP-HRM 2G_LTE,MAK6072-P1-HRM-VIP 2G_LTE,MAK0217-P1-VIP-HRM 2G_LTE_5G,MAK6085-P1-HRM 2G_LTE,MAK0231-P1-VIP-HRM 2G_5G,MAK6051-P1-VIP-HRM 2G,MAK6053-P1-VIP-HRM 2G | FLM_TE | MAK0231 | Results: DOWN SITE HUB MAK6074-P1-VIP-HRM MAK6074 MAK6054-P1-VIP-HRM MAK6054 MAK6073-P1-VIP-HRM MAK6073 MAK6072-P1-HRM-VIP MAK6072 MAK0217-P1-VIP-HRM MAK0217 MAK6085-P1-HRM MAK6085 MAK0231-P1-VIP-HRM MAK0231 MAK6051-P1-VIP-HRM MAK6051 MAK6053-P1-VIP-HRM MAK6053 Summary: Hub: MAK6074, Down Count: 1, Down Sites: MAK6074-P1-VIP-HRM Hub: MAK6054, Down Count: 1, Down Sites: MAK6054-P1-VIP-HRM Hub: MAK6073, Down Count: 1, Down Sites: MAK6073-P1-VIP-HRM Hub: MAK6072, Down Count: 1, Down Sites: MAK6072-P1-HRM-VIP Hub: MAK0217, Down Count: 1, Down Sites: MAK0217-P1-VIP-HRM Hub: MAK6085, Down Count: 1, Down Sites: MAK6085-P1-HRM Hub: MAK0231, Down Count: 1, Down Sites: MAK0231-P1-VIP-HRM Hub: MAK6051, Down Count: 1, Down Sites: MAK6051-P1-VIP-HRM Hub: MAK6053, Down Count: 1, Down Sites: MAK6053-P1-VIP-HRM Alarm Summary: MAK6074 No Active Alarm on HUB MAK6054 No Active Alarm on HUB MAK6073 No Active Alarm on HUB MAK6072 No Active Alarm on HUB MAK0217 No Active Alarm on HUB MAK6085 No Active Alarm on HUB MAK0231 No Active Alarm on HUB MAK6051 No Active Alarm on HUB MAK6053 No Active Alarm on HUB | PCM-20251020-00001774 | Dear FLM team, kindly perform usual TS for not login if still try with new HW | Dear FLM team, kindly perform usual TS for not login if still try with new HW |  | sites down |  | API | 10/20/2025 16:15:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000839 | PCM-20251020-00001793 | TT-20251020-01781 | Telecom | Region_1 | SLW0915 | SLW0915 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Mohamed Magdy Fouad Zayed | 10/20/2025 16:17:17 | 10/22/2025 02:11:48 | 10/21/2025 04:17:17 | RTN MW HC for link SLW0915<> SLW0921 | 10/20/2025 16:16:47 | Minor | 1-631 | MW_LOF | 10/20/2025 16:16:53 | P2 | SRAN | hafouf | Power Cube | TX NSA | SLW0915<> SLW0921 | FLM_TE | [8 empty] | API | 10/20/2025 16:17:17 | 10/20/2025 20:07:40 | 10/21/2025 21:29:04 | 10/21/2025 21:29:15 | 10/21/2025 23:53:30 | 10/22/2025 02:11:48 |  | Mohamed Magdy Fouad Zayed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000844 | PCM-20251020-00001805 | TT-20251020-01274 | Telecom | Region_6 | TFBH0887-LL-CSG-01 | TFBH0887 |  |  |  | SHAH KHALID | 10/20/2025 16:21:31 | 10/20/2025 17:08:32 | 10/21/2025 04:21:31 | p0_MW_Link Down at TFBH0887-BAH0005 | 10/20/2025 13:04:46 | Minor | 15269 | LOS | 10/20/2025 13:04:46 | P3 | IPRAN | makhwa | Sceco_STB | IPRAN NSA | TFBH0887-LL-CSG-01 | FLM_TE |  |  | PCM-20251020-00001271 | Dear FLM team, Observing PM errors on MW BAH0004-BAH0017 modem 7&8 (10.154.175.100) | Dear FLM team, Observing PM errors on MW BAH0004-BAH0017 modem 7&8 (10.154.175.100) |  |  |  | API | 10/20/2025 16:21:31 | 10/20/2025 17:08:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000845 | PCM-20251020-00001807 | TT-20251020-01768 | Telecom | Region_1 | JBL0531 | JBL0531 |  |  |  | Tahir Mahmood Hafiz Yar | 10/20/2025 16:22:47 | 10/20/2025 17:02:44 | 10/20/2025 22:22:47 | 2(2G) 2(3G) sites down under JBL0531-P3,JBL0296-P3-USF/R1_JB_HWBSC01 @ Power Cube | 10/20/2025 16:10:19 | Major | 21825 | CSL Fault | 10/20/2025 16:10:15 | P3 | SRAN | jubail | Power Cube | 2G_3G SA | JBL0296-P3-USF 2G_3G,JBL0531-P3 2G_3G | FLM_TE | JBL0531 | We are observing RSL degradation at link : JBL0531 DIR JBL0553 ,Kindly visit the link and perform the HC at mentioned link . | PCM-20251020-00001792 | We are observing RSL degradation at link : JBL0531 DIR JBL0553 ,Kindly visit the link and perform the HC at mentioned link . | We are observing RSL degradation at link : JBL0531 DIR JBL0553 ,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/20/2025 16:22:47 | 10/20/2025 17:02:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000846 | PCM-20251020-00001808 | TT-20251020-01717 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 16:23:48 | 10/20/2025 16:23:48 | 10/20/2025 22:23:48 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/20/2025 15:46:08 | Major | 7114 | CELL SERVICE PROBLEM | 10/20/2025 15:45:57 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251020-00001723 | Please check the HW issue at site | Please check the HW issue at site |  |  |  | API | 10/20/2025 16:23:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000850 | PCM-20251020-00001822 | TT-20251020-01807 | EM | Region_6 | HEQ1M7284 | HEQ0284 |  |  |  | Fizan Ahmed | 10/20/2025 16:27:26 | 10/21/2025 11:30:04 | 10/21/2025 04:27:26 | RECTIFIER MODULE FAILURE at HEQ1M7284-G9-L18-L21-SBTS-P3 @ Sceco | 10/20/2025 16:19:27 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/20/2025 16:19:16 | P3 | 4G | baish | Sceco | LTE NSA | HEQ1M7284 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/20/2025 16:27:26 | 10/21/2025 11:30:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020000859 | PCM-20251020-00001839 | TT-20251020-01794 | Telecom | Region_4 | JED0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 16:31:52 | 10/20/2025 16:31:52 | 10/20/2025 22:31:52 | 1(2G) 1(LTE) sites down under JED2170-CA-L1800-L800-P3-SBTS,JED0035-P2/JED0035-P2 @ Sceco | 10/20/2025 16:23:07 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 16:23:00 | P2 | 2G | jeddah | Sceco | 2G_LTE SA | JED2170-CA-L1800-L800-P3-SBTS LTE,JED0035-P2 2G | FLM_TE | JED0035 | HUB: JED0035, JED2170 We are observing LOS TO AIRSCALE kindly check locally | PCM-20251020-00001830 | HUB: JED0035, JED2170 We are observing LOS TO AIRSCALE kindly check locally | HUB: JED0035, JED2170 We are observing LOS TO AIRSCALE kindly check locally |  | sites down |  | API | 10/20/2025 16:31:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000861 | PCM-20251020-00001843 | TT-20251020-01046 | Telecom | Region_4 | JED0919-LL-CSG-01 | JED0919 |  |  |  | Nazeer Mohammed | 10/20/2025 16:34:10 | 10/21/2025 11:49:37 | 10/21/2025 04:34:10 | p0_MW_Link Down at JED0919-JED0540 | 10/20/2025 11:18:39 | Minor | 15269 | LOS | 10/20/2025 11:18:39 | P1 | IPRAN | jeddah | Generator_DG | IPRAN NSA | JED0919-LL-CSG-01 | FLM_TE |  |  | PCM-20251020-00001031 | observing ACM degraded on MW JED0954-JED0540 kindly rectify | observing ACM degraded on MW JED0954-JED0540 kindly rectify |  |  |  | API | 10/20/2025 16:34:10 | 10/21/2025 11:49:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000866 | PCM-20251020-00001853 | TT-20251020-01821 | Telecom | Region_4 | JED2015 | JED2015 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 16:40:02 | 10/21/2025 10:51:36 | 10/20/2025 22:40:02 | Fronthaul loop back connectivity check failure at JED2015-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P3 @ Sceco | 10/20/2025 16:20:37 | Major | 61009 | Fronthaul loop back connectivity check failure | 10/20/2025 16:20:29 | P3 | 2G | jeddah | Sceco | 2G SA | JED2015 | FLM_TE |  |  | PCM-20251020-00001836 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/20/2025 16:40:02 | 10/21/2025 10:51:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000869 | PCM-20251020-00001858 | TT-20251020-01791 | Telecom | Region_4 | JED0807 | JED0807 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 16:41:24 | 10/20/2025 16:41:24 | 10/20/2025 22:41:24 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0807-P2 @ Sceco | 10/20/2025 16:14:31 | Major | 7602 | BCF NOTIFICATION | 10/20/2025 16:14:19 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0807 | FLM_TE |  |  | PCM-20251020-00001806 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/20/2025 16:41:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000870 | PCM-20251020-00001861 | TT-20251020-01852 | Telecom | Region_4 | JED0751 | JED0751 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 16:43:03 | 10/22/2025 06:38:09 | 10/20/2025 22:43:03 | CELL SERVICE PROBLEM (Incorrect cell parameter configuration) at JED0751-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/20/2025 16:36:30 | Major | 7114 | CELL SERVICE PROBLEM | 10/20/2025 16:36:17 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0751 | FLM_TE |  |  | PCM-20251020-00001854 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/20/2025 16:43:03 | 10/20/2025 17:28:03 | 10/22/2025 06:37:59 |  |  | 10/22/2025 06:38:09 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000875 | PCM-20251020-00001871 | TT-20251020-01789 | Reference_telecom | Region_2 | ZLH0228 | ZLH0228 |  |  |  | Saeed Ud Din Muhammad Yousaf | 10/20/2025 16:47:32 | 10/20/2025 17:55:10 | 10/21/2025 04:47:32 | IP Clock Link Failure at ZLH0228-P3_SRAN @ Generator_SG | 10/20/2025 13:31:15 | Minor | 26263 | IP Clock Link Failure | 10/20/2025 13:20:57 | P3 | SRAN | majma | Generator_SG | 2G NSA | ZLH0228 | FLM_EM |  |  | PCM-20251020-00001842 | suspected power issue at site within fault time | suspected power issue at site within fault time |  |  |  | API | 10/20/2025 16:47:32 | 10/20/2025 17:55:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000876 | PCM-20251020-00001872 | TT-20251020-01867 | Telecom | Region_2 | RIYA6168C | RIYA6168 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/20/2025 16:49:40 | 10/21/2025 11:31:47 | 10/21/2025 04:49:40 | RF Unit Maintenance Link Failure at RIYA6168C-P1-VIP_SRAN @ Sceco | 10/20/2025 16:46:03 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/20/2025 16:44:21 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYA6168C | FLM_TE | [8 empty] | API | 10/20/2025 16:49:40 | 10/21/2025 11:31:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000878 | PCM-20251020-00001876 | TT-20251020-01871 | Telecom | Region_2 | RIYA6168C | RIYA6168 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/20/2025 16:52:45 | 10/21/2025 12:22:03 | 10/20/2025 22:52:45 | NR Cell Unavailable at RIYA6168C-P1-VIP_SRAN @ Sceco | 10/20/2025 16:45:57 | Major | 29841 | NR Cell Unavailable | 10/20/2025 16:44:24 | VIP | SRAN | riyadh | Sceco | 5G SA | RIYA6168C | FLM_TE | [8 empty] | API | 10/20/2025 16:52:45 | 10/21/2025 12:22:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000880 | PCM-20251020-00001885 | TT-20251020-01876 | Telecom | Region_4 | BHR0310 | BHR0310 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 16:58:25 | 10/21/2025 17:13:13 | 10/20/2025 22:58:25 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/20/2025 16:57:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 16:57:29 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | BHR0310 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 16:58:25 | 10/21/2025 13:18:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000887 | PCM-20251020-00001896 | TT-20251014-00543 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 10/20/2025 17:01:02 | 10/20/2025 17:01:02 | 10/20/2025 23:01:02 | Observing Multiple ALU CIDs flapped and restored B/W MK - HA | 10/14/2025 06:10:59 | Major | 5000003 | Link Down | 10/14/2025 06:10:59 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE |  |  | PCM-20251020-00001548 | link now stable and all services UP , no need actions | link now stable and all services UP , no need actions |  |  |  | API | 10/20/2025 17:01:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000889 | PCM-20251020-00001897 | TT-20251011-01600 | Telecom | Region_5 | MK4 | MK4 |  |  |  | Muhammad Zubair | 10/20/2025 17:01:44 | 10/20/2025 17:01:44 | 10/20/2025 23:01:44 | Observing multiple ALUB/W MAK - RIY - JED - KMS | 10/11/2025 17:38:44 | Major | 5000003 | Link Down | 10/11/2025 17:38:44 | P1 | BSC | makkah | Sceco | IPBB NSA | MK4 | FLM_TE |  |  | PCM-20251020-00001545 | link now stable and all services UP , no need actions | link now stable and all services UP , no need actions |  |  |  | API | 10/20/2025 17:01:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000890 | PCM-20251020-00001901 | TT-20251020-01895 | Telecom | Region_3 | MDN2923 | MDN2923 |  |  |  | Hussain Ahmad Sultan Muhammad | 10/20/2025 17:03:04 | 10/20/2025 21:01:58 | 10/20/2025 23:03:04 | NR Cell Unavailable at MDN2923-P3_SRAN @ Sceco | 10/20/2025 16:56:18 | Major | 29841 | NR Cell Unavailable | 10/20/2025 16:54:43 | P2 | SRAN | madinah | Sceco | 5G SA | MDN2923 | FLM_TE | [8 empty] | API | 10/20/2025 17:03:04 | 10/20/2025 21:01:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000894 | PCM-20251020-00001906 | TT-20251020-01889 | Reference_telecom | Region_4 | JED1MN0218 | JED0218 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 17:05:19 | 10/20/2025 17:05:19 | 10/21/2025 05:05:19 | Fronthaul loop back connectivity check failure at JED1MN0218-NR2.6-P1-VIP @ Sceco | 10/20/2025 16:30:40 | Minor | 61009 | Fronthaul loop back connectivity check failure | 10/20/2025 16:30:31 | VIP | 5G | jeddah | Sceco | 5G NSA | JED1MN0218 | FLM_TE |  |  | PCM-20251020-00001895 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/20/2025 17:05:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000901 | PCM-20251020-00001920 | TT-20251020-01914 | Telecom | Region_1 | HFR2U6102 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 17:09:58 | 10/20/2025 18:00:28 | 10/20/2025 23:09:58 | GSM Local Cell Unusable at HFR2U6102-P3 @ Sceco | 10/20/2025 17:07:53 | Major | 28016 | GSM Local Cell Unusable | 10/20/2025 17:07:22 | P3 | 2G | hafr | Sceco | 2G SA | HFR2U6102 | FLM_TE | [8 empty] | API | 10/20/2025 17:09:58 | 10/20/2025 18:00:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000903 | PCM-20251020-00001922 | TT-20251020-01915 | Telecom | Region_6 | JDS0802 | JDS0802 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Osama Hadi | 10/20/2025 17:10:47 | 10/20/2025 20:59:35 | 10/21/2025 05:10:47 | ODU CPU / Cable Open at JDS0802-2 on 10.154.172.70 @ Sceco_STB | 10/20/2025 17:09:55 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/20/2025 16:57:59 | P1 | 2G | jizan | Sceco_STB | TX NSA | JDS0802 | FLM_TE | [8 empty] | API | 10/20/2025 17:10:47 | 10/20/2025 20:24:01 | 10/20/2025 20:59:22 |  |  | 10/20/2025 20:59:35 |  | Osama Hadi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000917 | PCM-20251020-00001958 | TT-20251020-01948 | Reference_EM | Region_1 | SMN0796 | SMN0796 |  |  |  | Shaker Saied Mohamed ElShafie | 10/20/2025 17:34:02 | 10/22/2025 09:01:34 | 10/20/2025 23:34:02 | Minor Rec alarm at SMN0796-P1-HUB_SRAN @ Sceco | 10/20/2025 17:23:42 | Major | 65108 | Minor Rec alarm | 10/20/2025 17:23:37 | P1 | SRAN | hafr | Sceco | 2G NSA | SMN0796 | FLM_EM | [8 empty] | API | 10/20/2025 17:34:02 | 10/22/2025 09:01:34 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000919 | PCM-20251020-00001964 | TT-20251020-01951 | Telecom | Region_4 | JED2965 | JED2965 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 17:37:09 | 10/21/2025 10:51:37 | 10/20/2025 23:37:09 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2965-G9-L8-L18-L21-NR2.6-FWA-P1-VIP-SBTS @ Generator_SG | 10/20/2025 17:36:24 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 17:36:14 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED2965 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 17:37:09 | 10/21/2025 10:51:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000920 | PCM-20251020-00001965 | TT-20251020-01132 | Telecom | Region_1 | DAM0350 | DAM0350 |  |  |  | Tahir Mahmood Hafiz Yar | 10/20/2025 17:37:14 | 10/20/2025 22:56:40 | 10/21/2025 05:37:14 | IKE Negotiation Failure at DAM0350-P3_SRAN @ Sceco | 10/20/2025 11:58:29 | Minor | 25891 | IKE Negotiation Failure | 10/20/2025 11:34:55 | P3 | SRAN | jubail | Sceco | 2G NSA | DAM0350 | FLM_TE |  |  | PCM-20251020-00001721 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 |  |  |  | API | 10/20/2025 17:37:14 | 10/20/2025 22:56:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000921 | PCM-20251020-00001966 | TT-20251020-01075 | Telecom | Region_1 | JBL2201 | JBL2201 |  |  |  | Rafiq Ahmed Elturifi | 10/20/2025 17:37:45 | 10/20/2025 21:14:56 | 10/21/2025 05:37:45 | IKE Negotiation Failure at JBL2201-P2_SRAN @ Sceco | 10/20/2025 11:30:15 | Minor | 25891 | IKE Negotiation Failure | 10/20/2025 11:28:11 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL2201 | FLM_TE |  |  | PCM-20251020-00001574 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 |  |  |  | API | 10/20/2025 17:37:45 | 10/20/2025 21:14:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000925 | PCM-20251020-00001972 | TT-20251020-01946 | Telecom | Region_4 | JED1M7376 | JED0376 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 17:39:52 | 10/21/2025 17:13:13 | 10/20/2025 23:39:52 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7376-CA-L900-L800-SBTS-P3 @ Generator_SG | 10/20/2025 17:28:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 17:28:19 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7376 | FLM_TE |  |  | PCM-20251020-00001956 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 17:39:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000929 | PCM-20251020-00001981 | TT-20251020-01072 | Telecom | Region_1 | JBL0421 | JBL0421 |  |  |  | Tahir Mahmood Hafiz Yar | 10/20/2025 17:42:17 | 10/20/2025 22:56:41 | 10/21/2025 05:42:17 | IKE Negotiation Failure at JBL0421-P2_SRAN @ Sceco | 10/20/2025 11:29:48 | Minor | 25891 | IKE Negotiation Failure | 10/20/2025 11:27:44 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0421 | FLM_TE |  |  | PCM-20251020-00001573 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 |  |  |  | API | 10/20/2025 17:42:17 | 10/20/2025 22:56:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000931 | PCM-20251020-00001986 | TT-20251020-01036 | Telecom | Region_1 | JBL2993 | JBL2993 |  |  |  | Rafiq Ahmed Elturifi | 10/20/2025 17:43:25 | 10/23/2025 17:19:40 | 10/20/2025 19:43:25 | 10(2G) 7(3G) 10(LTE) sites down under R1_JB_HWBSC01 @ Sceco | 10/20/2025 11:11:33 | Emergency | 21825 | CSL Fault | 10/20/2025 11:11:31 | P1 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBL0421-P2 LTE,JBL2939-P2 2G_3G_LTE,JBL0757-P3 2G_3G_LTE,JBL0040-P2 2G_3G_LTE,JBL0468-P2 2G_3G_LTE,JBL2879-P3 2G_3G_LTE,JBL2993-P1-HUB 2G_LTE,JBL2201-P2-L800 LTE | FLM_TE | JBL2993 | Results: DOWN SITE HUB JBL0421-P2 JBL2993 JBL2939-P2 JBL2993 JBL0757-P3 JBL0757 JBL0040-P2 JBL0040 JBL0468-P2 JBL2993 JBL2879-P3 JBL2993 JBL2993-P1-HUB JBL2993 JBL2201-P2-L800 JBL2993 Summary: Hub: JBL2993, Down Count: 6, Down Sites: JBL0421-P2, JBL2939-P2, JBL0468-P2, JBL2879-P3, JBL2993-P1-HUB, JBL2201-P2-L800 Hub: JBL0757, Down Count: 1, Down Sites: JBL0757-P3 Hub: JBL0040, Down Count: 1, Down Sites: JBL0040-P2 Alarm Summary: JBL2993 No Active Alarm on HUB JBL0757 No Active Alarm on HUB JBL0040 No Active Alarm on HUB | PCM-20251020-00001662 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance JBL2993 <> DMJB2087 |  | sites down |  | API | 10/20/2025 17:43:25 | 10/20/2025 21:14:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000937 | PCM-20251020-00002000 | TT-20251020-01982 | EM | Region_1 | ARM2759 | ARM2759 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/20/2025 17:49:02 | 10/22/2025 02:05:04 | 10/20/2025 23:49:02 | Door opening alarm at ARM2759-P1_SRAN-PC @ Power Cube | 10/20/2025 17:48:51 | Major | 65101 | Door opening alarm | 10/20/2025 17:48:46 | P1 | SRAN | jubail | Power Cube | 2G NSA | ARM2759 | FLM_EM | [8 empty] | API | 10/20/2025 17:49:02 | 10/22/2025 02:05:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000938 | PCM-20251020-00002001 | TT-20251019-01968 | Telecom | Region_2 | RIY2003 | RIY2003 | Equipment | BSS_HW_fault | Replace RCU | Touseef Iqbal Mazhar Iqbal | 10/20/2025 17:49:14 | 10/22/2025 15:10:15 | 10/21/2025 05:49:14 | RET Antenna Motor Fault at RIY2003-P3_SRAN @ Generator_SG | 10/19/2025 16:47:12 | Minor | 26751 | RET Antenna Motor Fault | 10/19/2025 16:47:08 | P3 | SRAN | muzamiah | Generator_SG | 2G NSA | RIY2003 | FLM_TE |  |  | PCM-20251020-00001949 | Dear FLM, Approved as per FLM TS & Below Error. | Dear FLM, Approved as per FLM TS & Below Error. |  |  |  | API | 10/20/2025 17:49:14 | 10/20/2025 19:04:40 | 10/22/2025 11:04:12 | 10/22/2025 11:04:16 | 10/22/2025 11:59:21 | 10/22/2025 15:10:15 |  | Touseef Iqbal Mazhar Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000941 | PCM-20251020-00002006 | TT-20251020-01114 | Telecom | Region_6 | NJR0030-ZNa01-CSG-01 | NJR0030 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shahid Ali Roshan Ali | 10/20/2025 17:52:54 | 10/21/2025 00:06:34 | 10/21/2025 05:52:54 | p0_MW_Link Down at NJR0030-NJR0008 | 10/20/2025 11:50:57 | Minor | 15269 | LOS | 10/20/2025 11:50:57 | P1 | IPRAN | najran | Sceco_STB | IPRAN NSA | NJR0030-ZNa01-CSG-01 | FLM_TE |  |  | PCM-20251020-00001100 | Dear FLM team, observing PM errors on MW NJR0020-NJR0008 | Dear FLM team, observing PM errors on MW NJR0020-NJR0008 |  |  |  | API | 10/20/2025 17:52:54 | 10/20/2025 21:29:25 | 10/21/2025 00:06:19 |  |  | 10/21/2025 00:06:34 |  | Shahid Ali Roshan Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000942 | PCM-20251020-00002007 | TT-20251020-01989 | Telecom | Region_3 | RSP0001-MDC-NE8K-M14-02 | RSP0001 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Hossam Ali Ahmed Ali | 10/20/2025 17:53:09 | 10/22/2025 18:42:13 | 10/21/2025 05:53:09 | Bad Package Error Rising at RSP0001-MDC-NE8K-M14-02 @ Sceco | 10/20/2025 17:52:47 | Minor | 101-2501403 | Bad Package Error Rising | 10/20/2025 17:52:40 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | RSP0001-MDC-NE8K-M14-02 | FLM_TE | [8 empty] | API | 10/20/2025 17:53:09 | 10/20/2025 22:37:46 | 10/22/2025 18:41:48 |  |  | 10/22/2025 18:42:13 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000948 | PCM-20251020-00002026 | TT-20251020-02015 | EM | Region_1 | ARM0890 | ARM0890 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/20/2025 18:04:31 | 10/23/2025 11:12:36 | 10/21/2025 06:04:31 | Door opening alarm at ARM0890-P2_SRAN @ Sceco | 10/20/2025 18:03:56 | Minor | 65101 | Door opening alarm | 10/20/2025 18:03:02 | P2 | SRAN | hafouf | Sceco | 2G NSA | ARM0890 | FLM_EM | [8 empty] | API | 10/20/2025 18:04:31 | 10/23/2025 11:12:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020000951 | PCM-20251020-00002031 | TT-20251020-01335 | Telecom | Region_1 | RYH-0119-NE40E-X2-M8-PE-01 | RYHR0119 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 18:07:40 | 10/20/2025 18:59:10 | 10/21/2025 06:07:40 | p0_MW_Link Down at RYH0119 - DAM3091 | 10/20/2025 13:37:41 | Minor | 15269 | LOS | 10/20/2025 13:37:41 | P3 | IPRAN | hafr | Generator_DG | IPRAN NSA | RYH-0119-NE40E-X2-M8-PE-01 | FLM_TE |  | vlan 21 in VRRP Road FLM have to check link from RYHR0121 dir HFR0503 if exist or not. | PCM-20251020-00001989 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance KKM2174 <> KKM2163 | kindly need Health check for MW link , as it suffer from hardware and microwave alarms caused link count errors and suffer bad performance KKM2174 <> KKM2163 |  |  |  | API | 10/20/2025 18:07:40 | 10/20/2025 18:59:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000952 | PCM-20251020-00002033 | TT-20251020-02017 | Telecom | Region_4 | JED1U6739 | JED6039 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/20/2025 18:09:13 | 10/21/2025 18:12:41 | 10/21/2025 00:09:13 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/20/2025 17:58:26 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/20/2025 17:58:22 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251020-00002028 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 18:09:13 | 10/21/2025 10:49:22 | 10/21/2025 18:12:34 |  |  | 10/21/2025 18:12:41 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000954 | PCM-20251020-00002036 | TT-20251020-02026 | Telecom | Region_4 | RAB0660 | RAB0660 |  |  |  | Khizer Hayat | 10/20/2025 18:10:13 | 10/20/2025 18:11:33 | 10/21/2025 00:10:13 | BASE STATION ANTENNA LINE PROBLEM at RAB0660-GSM-P2-USF @ Sceco | 10/20/2025 18:03:05 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/20/2025 18:02:56 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0660 | FLM_TE | [5 empty] | VSWR minor alarm |  |  | API | 10/20/2025 18:10:13 | 10/20/2025 18:11:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000959 | PCM-20251020-00002048 | TT-20251020-02038 | Telecom | Region_3 | MDN0384 | MDN0384 | Equipment | SFP_BTS | Clean SFP | TAUSEEF ILYAS | 10/20/2025 18:18:28 | 10/20/2025 19:41:18 | 10/21/2025 00:18:28 | BBU CPRI Interface Error at MDN0384-P2_SRAN-PC @ Sceco | 10/20/2025 18:15:48 | Major | 26234 | BBU CPRI Interface Error | 10/20/2025 18:13:14 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0384 | FLM_TE | [8 empty] | API | 10/20/2025 18:18:28 | 10/20/2025 18:21:00 | 10/20/2025 19:41:09 |  |  | 10/20/2025 19:41:18 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000970 | PCM-20251020-00002067 | TT-20251020-02069 | Telecom | Region_4 | JED6010 | JED6010 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Farag Abdelbary | 10/20/2025 18:38:02 | 10/21/2025 18:12:22 | 10/21/2025 00:38:02 | 1(LTE) sites down under JED6010-DCU @ Sceco | 10/20/2025 18:29:39 | Major | 301 | NE Is Disconnected | 10/20/2025 18:29:36 | P3 | 2G | jeddah | Sceco | LTE SA | JED6010-DCU | FLM_TE | JED6010 | Results: DOWN SITE HUB JED6010-DCU JED6010 Summary: Hub: JED6010, Down Count: 1, Down Sites: JED6010-DCU Alarm Summary: JED6010 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 18:38:02 | 10/21/2025 10:49:22 | 10/21/2025 18:12:05 |  |  | 10/21/2025 18:12:22 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020000971 | PCM-20251020-00002068 | TT-20251020-01998 | Telecom | Region_4 | JED0376 | JED0376 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 18:39:07 | 10/20/2025 18:39:07 | 10/20/2025 22:39:07 | 3(2G) 1(LTE) sites down under JED0376-P2,JED6090-P3,JED0704-P1-VIP/JED0704-P1-VIP @ Sceco | 10/20/2025 17:55:21 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 17:55:15 | P2 | 2G | jeddah | Generator_SG | 2G SA | JED0704-P1-VIP 2G,JED0376-P2 2G,JED6090-P3 2G | FLM_TE | JED0376 | HUB: JED0376 Observing Node Rebooted , Kindly visit the site & check the issue as we are suspecting power issue. Kindly update TT under FLM & EM | PCM-20251020-00002032 | No Power Issue | No Power Issue |  | sites down |  | API | 10/20/2025 18:39:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000974 | PCM-20251020-00002078 | TT-20251020-02081 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/20/2025 18:44:48 | 10/21/2025 09:04:30 | 10/21/2025 00:44:48 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/20/2025 15:44:46 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/20/2025 15:44:34 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/20/2025 18:44:48 | 10/21/2025 09:04:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251020000976 | PCM-20251020-00002085 | TT-20251020-02085 | Reference_telecom | Region_2 | RIY0788 | RIY0788 | Transsmission | Fiber CUT | STC LL cut | Asad Ali Nadiq Khan | 10/20/2025 18:47:23 | 10/23/2025 16:32:12 | 10/21/2025 06:47:23 | ETH_LOS at RIY0788_NE_9_V @ Sceco_STB | 10/20/2025 14:47:20 | Minor | 1-235 | ETH_LOS | 10/20/2025 14:47:10 | P1 | SRAN | riyadh | Sceco_STB | TX NSA | RIY0788 | FLM_TE | [8 empty] | API | 10/20/2025 18:47:23 | 10/23/2025 16:31:50 | 10/23/2025 16:32:02 | 10/23/2025 16:32:05 | 10/23/2025 16:32:12 |  |  | DILSHAD ALI ABDUL HAMEED |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000978 | PCM-20251020-00002088 | TT-20251020-02089 | Reference_telecom | Region_6 | JEC1M7323 | JEC0323 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Ansir Iqbal Muhammad Iqbal | 10/20/2025 18:50:36 | 10/21/2025 21:48:02 | 10/21/2025 00:50:36 | BASE STATION ANTENNA LINE PROBLEM (VSWR upper threshold exceeded) at JEC1M7323-P1-VIP-CA-L800 (Ref:TT-20251018-01256) @ Generator_SG | 10/18/2025 14:19:47 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/18/2025 14:19:38 | VIP | 4G | baish | Generator_SG | LTE SA | JEC1M7323 | FLM_TE | [5 empty] | VSWR upper threshold exceeded |  |  | API | 10/20/2025 18:50:36 | 10/21/2025 00:40:16 | 10/21/2025 00:47:17 | 10/21/2025 19:23:30 | 10/21/2025 20:08:19 | 10/21/2025 21:48:02 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020000982 | PCM-20251020-00002099 | TT-20251013-01026 | MW_HC | Region_5 | MAK0274 | MAK0274 |  |  |  | Husain Hassan Ishag Omer | 10/20/2025 18:54:52 | 10/22/2025 01:12:55 | 10/21/2025 06:54:52 | As BO Requested MW Nokia Observing Air scale port counting TRSEF errors at MAK0274 | 10/13/2025 08:35:04 | Minor | 113388 | LOF | 10/13/2025 08:35:06 | P2 | 2G | makkah | Sceco | TX NSA | MAK0274 | FLM_TE |  |  | PCM-20251020-00001945 | clear and under monitoring | clear and under monitoring |  |  |  | API | 10/20/2025 18:54:52 | 10/22/2025 01:12:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000991 | PCM-20251020-00002113 | TT-20251020-02113 | Telecom | Region_1 | KBR2U6763 | KBR6063 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Meraj Husain Idd Baksh | 10/20/2025 19:04:13 | 10/21/2025 09:48:05 | 10/21/2025 01:04:13 | Cell Unavailable at KBR2U6763-P3 @ Sceco | 10/20/2025 16:25:34 | Major | 29240 | Cell Unavailable | 10/20/2025 16:24:02 | P3 | 4G | dammam | Sceco | LTE SA | KBR2U6763 | FLM_TE | [8 empty] | API | 10/20/2025 19:04:13 | 10/20/2025 22:08:57 | 10/21/2025 09:36:16 | 10/21/2025 09:41:52 | 10/21/2025 09:42:02 | 10/21/2025 09:48:05 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000992 | PCM-20251020-00002116 | TT-20251020-02116 | Reference_telecom | Region_6 | TNM0723 | TNM0723 | Equipment | CB_BTS | Change Port on FPFH | Muhammad Jamal Khan Abbas Ali | 10/20/2025 19:05:08 | 10/21/2025 00:10:55 | 10/21/2025 01:05:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at TNM1M7723-G9-NL8-NL18-SBTS-P3 (Ref:TT-20251009-01473) @ Generator_SG | 10/10/2025 06:33:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/10/2025 06:33:20 | P3 | 2G | mohail | Generator_SG | 5G_Cell SA | TNM1M7723 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 19:05:08 | 10/21/2025 00:06:17 | 10/21/2025 00:10:47 |  |  | 10/21/2025 00:10:55 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000994 | PCM-20251020-00002118 | TT-20251020-01799 | Telecom | Region_1 | HFR2797 | HFR2797 | Equipment | BSS_HW_Stuck | Reset Interface Card | Ahsan Ul Haq Amtiaz Ali | 10/20/2025 19:05:19 | 10/21/2025 00:04:40 | 10/21/2025 01:05:19 | Board Software Program Error at HFR2797-P2_SRAN @ Sceco | 10/20/2025 16:16:55 | Major | 26203 | Board Software Program Error | 10/20/2025 16:16:52 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR2797 | FLM_TE |  |  | PCM-20251020-00002091 | Approved for TS purpose , please return if not used. Board Name UBBP Board Type WD22UBBPg3 BOM Code 03058627 SN(Bar Code) 210305862710L8001384 | Approved for TS purpose , please return if not used. Board Name UBBP Board Type WD22UBBPg3 BOM Code 03058627 SN(Bar Code) 210305862710L8001384 |  |  |  | API | 10/20/2025 19:05:19 | 10/20/2025 22:00:46 | 10/20/2025 23:16:25 | 10/20/2025 23:16:28 | 10/20/2025 23:46:04 | 10/21/2025 00:04:40 |  | Ahsan Ul Haq Amtiaz Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020000997 | PCM-20251020-00002125 | TT-20251020-02123 | Telecom | Region_4 | JED0271 | JED0271 | Enviroment | Rectifier Module | Adding module due to load issue | Mohammed Ramadan A Abu Abid | 10/20/2025 19:08:34 | 10/23/2025 09:13:00 | 10/21/2025 01:08:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/20/2025 19:07:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 19:07:44 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 19:08:34 | 10/20/2025 19:33:58 | 10/23/2025 09:12:48 |  |  | 10/23/2025 09:13:00 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001001 | PCM-20251020-00002132 | TT-20251020-02070 | Reference_telecom | Region_3 | MDN2M1384 | MDN0384 | Equipment | BTS_Cable | Replace CPRI Cable | TAUSEEF ILYAS | 10/20/2025 19:14:45 | 10/20/2025 19:41:04 | 10/21/2025 01:14:45 | GSM Local Cell Unusable at MDN2M1384-P29(REF:TT-20251020-02038) @ Sceco | 10/20/2025 18:15:03 | Major | 28016 | GSM Local Cell Unusable | 10/20/2025 18:13:30 | P2 | 2G | madinah | Sceco | 2G SA | MDN2M1384 | FLM_TE |  |  | PCM-20251020-00002122 | Approved as per FLM TS. #14130618 | Approved as per FLM TS. #14130618 |  |  |  | API | 10/20/2025 19:14:45 | 10/20/2025 19:40:13 | 10/20/2025 19:40:19 |  |  | 10/20/2025 19:41:04 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001003 | PCM-20251020-00002134 | TT-20251020-02131 | Reference_EM | Region_1 | DMAP2U6160 | DMAP6060 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/20/2025 19:16:50 | 10/21/2025 13:03:26 | 10/21/2025 01:16:50 | High temperature 32C alarm at DMAP2U6160-P1-VIP @ Sceco | 10/20/2025 19:06:34 | Major | 65102 | High temperature 32C alarm | 10/20/2025 19:06:30 | VIP | 2G | dammam | Sceco | 2G NSA | DMAP2U6160 | FLM_EM | [8 empty] | API | 10/20/2025 19:16:50 | 10/21/2025 13:03:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001004 | PCM-20251020-00002136 | TT-20251020-02127 | Telecom | Region_4 | HHR0459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 19:17:01 | 10/21/2025 18:52:47 | 10/20/2025 23:17:01 | 1(2G) sites down under HHR0459-P1-VIP/HHR0459-P1-VIP @ Sceco | 10/20/2025 19:08:40 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 19:08:38 | VIP | 2G | jeddah | Sceco | 2G SA | HHR0459-P1-VIP | FLM_TE | HHR0459 | Results: DOWN SITE HUB HHR0459-P1-VIP HHR0459 Summary: Hub: HHR0459, Down Count: 1, Down Sites: HHR0459-P1-VIP Alarm Summary: HHR0459 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 19:17:01 | 10/21/2025 18:52:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001006 | PCM-20251020-00002138 | TT-20251020-01112 | MW_HC | Region_5 | MAK0190 | MAK0190 |  |  |  | Amr Abdulla Ali Othman | 10/20/2025 19:19:24 | 10/20/2025 19:19:24 | 10/21/2025 07:19:24 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0190-MAK2091 | 10/20/2025 11:50:23 | Minor | 113388 | LOF | 10/20/2025 11:50:25 | P2 | 2G | makkah | Sceco | TX NSA | MAK0190-MAK2091 | FLM_TE |  |  | PCM-20251020-00001794 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/20/2025 19:19:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001007 | PCM-20251020-00002139 | TT-20251020-02137 | Telecom | Region_4 | JED1M8609 | JED2609 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 19:20:27 | 10/21/2025 10:51:37 | 10/21/2025 01:20:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8609-P3-L800-CA @ Sceco | 10/20/2025 19:19:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 19:19:42 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8609 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 19:20:27 | 10/21/2025 10:51:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001010 | PCM-20251020-00002145 | TT-20251020-02143 | Telecom | Region_4 | JED1M8061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 19:25:37 | 10/21/2025 18:52:47 | 10/21/2025 01:25:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8061-CA-L800-SBTS @ Sceco | 10/20/2025 19:24:51 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 19:24:41 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8061 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 19:25:37 | 10/21/2025 18:52:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001011 | PCM-20251020-00002146 | TT-20251020-02138 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 19:26:02 | 10/20/2025 21:12:50 | 10/20/2025 23:26:02 | 1(LTE) sites down under JED0164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/20/2025 19:17:32 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 19:17:29 | P1 | 4G | jeddah | Sceco | LTE SA | JED0164-CA-L900-L800-P1-WDM-SBTS | FLM_TE | JED0164 | Results: DOWN SITE HUB JED0164-CA-L900-L800-P1-WDM-SBTS JED0164 Summary: Hub: JED0164, Down Count: 1, Down Sites: JED0164-CA-L900-L800-P1-WDM-SBTS Alarm Summary: JED0164 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.96.88.236:8080/NE3S/1.0/] | sites down |  | API | 10/20/2025 19:26:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001015 | PCM-20251020-00002157 | TT-20251020-02151 | EM | Region_3 | MDQS2432 | MDQS2432 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/20/2025 19:33:10 | 10/21/2025 12:03:57 | 10/21/2025 07:33:10 | NETECO: Under Fuel Level at MDQS2432 @ Generator_DG | 10/20/2025 19:22:01 | Minor | 301 | Under Fuel Level | 10/20/2025 19:22:01 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2432 | FLM_EM | MDQS2432 | Results: DOWN SITE HUB MDQS2432 MDQS2432 Summary: Hub: MDQS2432, Down Count: 1, Down Sites: MDQS2432 Alarm Summary: MDQS2432 No Active Alarm on HUB | [6 empty] | API | 10/20/2025 19:33:10 | 10/21/2025 12:03:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001016 | PCM-20251020-00002161 | TT-20251018-01630 | Telecom | Region_6 | ABDB9020 | ABDB9020 | Transsmission | MW_HW_fault | Replace ODU | Muhammad Jamal Khan Abbas Ali | 10/20/2025 19:36:09 | 10/24/2025 02:07:52 | 10/21/2025 07:36:09 | AS BO Requested MW HC For Link ABDB9020- ABDB9019 | 10/18/2025 17:20:44 | Minor | 113388 | LOF | 10/18/2025 17:20:44 | P3 | Repeater | mohail | Sceco | TX NSA | ABDB9020- ABDB9019 | FLM_TE |  |  | PCM-20251020-00002130 | where data | where data |  |  |  | API | 10/20/2025 19:36:09 | 10/21/2025 00:06:18 | 10/24/2025 02:07:39 |  |  | 10/24/2025 02:07:52 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020001017 | PCM-20251020-00002164 | TT-20251020-02174 | Telecom | [7 empty] | 10/20/2025 19:37:15 | 10/20/2025 19:37:15 | 10/21/2025 07:37:15 | JED1W6081 Partial Down | 10/20/2025 19:31:21 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/20/2025 19:31:21 | P1 | WIFI |  | Sceco | Wifi SA | JED1W6081_3-6F-AP04 | FLM_TE | [8 empty] | API | 10/20/2025 19:37:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001018 | PCM-20251020-00002166 | TT-20251020-02176 | EM | Region_1 | HFBD2M5010 | HFBD0010 | Equipment | FAN Cleaning | Clean FAN | Mohamed Ramadan Mohamed Gomaa | 10/20/2025 19:38:32 | 10/23/2025 11:11:49 | 10/21/2025 01:38:32 | Door opening alarm at HFBD2M5010-P1-HUB @ Generator_SG | 10/20/2025 19:38:03 | Major | 65101 | Door opening alarm | 10/20/2025 19:37:59 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5010 | FLM_EM | [8 empty] | API | 10/20/2025 19:38:32 | 10/21/2025 05:03:38 | 10/23/2025 11:11:40 |  |  | 10/23/2025 11:11:49 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001019 | PCM-20251020-00002167 | TT-20251020-02142 | Telecom | Region_4 | SQSH0023 | SQSH0023 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/20/2025 19:38:49 | 10/20/2025 20:42:56 | 10/21/2025 01:38:49 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at SQSH0023-GSM-UMTS-P2-USF @ Generator_DG | 10/20/2025 19:19:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 19:19:11 | P2 | 2G | qunfuddah | Generator_DG | 5G_Cell SA | SQSH0023 | FLM_TE |  |  | PCM-20251020-00002144 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 19:38:49 | 10/20/2025 20:42:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001020 | PCM-20251020-00002168 | TT-20251020-02124 | Telecom | Region_4 | JED1U6831 | JED6131 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/20/2025 19:38:58 | 10/21/2025 18:10:26 | 10/21/2025 01:38:58 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/20/2025 19:01:48 | Major | 7654 | CELL OPERATION DEGRADED | 10/20/2025 19:01:43 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251020-00002127 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 19:38:58 | 10/21/2025 10:49:23 | 10/21/2025 18:10:18 |  |  | 10/21/2025 18:10:26 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001023 | PCM-20251020-00002175 | TT-20251020-02111 | Reference_telecom | Region_6 | TBL1M8333 | TBL2333 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hamid Ullah Muhammad Alam Khan | 10/20/2025 19:43:14 | 10/20/2025 20:52:47 | 10/21/2025 01:43:14 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TBL1M8333-G9-L8-L18-L21-SBTS @ Sceco | 10/20/2025 17:10:50 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 17:02:32 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M8333 | FLM_TE |  |  | PCM-20251020-00002170 | Dear Team, Hub: AQQ2433 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear Team, Hub: AQQ2433 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/20/2025 19:43:14 | 10/20/2025 19:50:59 | 10/20/2025 20:52:36 |  |  | 10/20/2025 20:52:47 |  | Hamid Ullah Muhammad Alam Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001026 | PCM-20251020-00002178 | TT-20251020-02182 | Reference_EM | Region_1 | HFBD2M5010 | HFBD0010 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/20/2025 19:45:16 | 10/23/2025 11:12:05 | 10/21/2025 01:45:16 | Major Rec. alarm at HFBD2M5010-P1-HUB @ Generator_SG | 10/20/2025 19:34:46 | Major | 65107 | Major Rec. alarm | 10/20/2025 19:34:41 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M5010 | FLM_EM | [8 empty] | API | 10/20/2025 19:45:16 | 10/21/2025 05:03:38 | 10/23/2025 11:11:57 |  |  | 10/23/2025 11:12:05 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001034 | PCM-20251020-00002198 | TT-20251020-01230 | Reference_telecom | Region_2 | RIY0794 | RIY0794 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mubashar Farooq Abdul Majeed | 10/20/2025 20:04:06 | 10/21/2025 07:38:28 | 10/21/2025 00:04:06 | 1(2G/LTE) site down under RIY0794-P1-VIP (REF:TT-20251020-01030) | 10/20/2025 11:13:11 | Critical | 21825 | CSL Fault | 10/20/2025 11:13:11 | VIP | SRAN | riyadh | Sceco | 2G_LTE SA | RIY0794 | FLM_TE | RIY0794 | Results: DOWN SITE HUB RIY0794 RIY0794 Summary: Hub: RIY0794, Down Count: 1, Down Sites: RIY0794 Alarm Summary: RIY0794 No Active Alarm on HUB | PCM-20251020-00002040 | No issue at IPRAN side , Please check Access and Tx side. | No issue at IPRAN side , Please check Access and Tx side. |  | site down |  | API | 10/20/2025 20:04:06 | 10/20/2025 20:30:14 | 10/21/2025 07:38:20 |  |  | 10/21/2025 07:38:28 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001035 | PCM-20251020-00002206 | TT-20251020-02212 | Reference_telecom | Region_6 | BCH2213 | BCH2213 |  |  |  | SHAH KHALID | 10/20/2025 20:09:32 | 10/20/2025 20:52:11 | 10/21/2025 08:09:32 | ReplaceableUnitProblem observed in BCH2213_01 towards 10.221.244.189 @ Generator_SG | 10/20/2025 08:10:57 | Minor |  | ReplaceableUnitProblem | 10/20/2025 08:09:23 | P3 | 2G | Baha | Generator_SG | TX NSA | BCH2213 | FLM_TE | [8 empty] | API | 10/20/2025 20:09:32 | 10/20/2025 20:52:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001036 | PCM-20251020-00002208 | TT-20251020-02213 | Telecom | Region_3 | MDN0133 | MDN0133 | Equipment | BTS_Cable | Reconnect CPRI Cable | TAUSEEF ILYAS | 10/20/2025 20:10:03 | 10/20/2025 23:16:33 | 10/21/2025 08:10:03 | RF Unit Maintenance Link Failure at MDN0133-P2_SRAN @ Sceco | 10/20/2025 20:06:18 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/20/2025 20:04:35 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0133 | FLM_TE | [8 empty] | API | 10/20/2025 20:10:03 | 10/20/2025 21:43:21 | 10/20/2025 23:16:20 |  |  | 10/20/2025 23:16:33 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001037 | PCM-20251020-00002211 | TT-20251020-02217 | Telecom | Region_3 | MDN0133 | MDN0133 | Equipment | BTS_Cable | Reconnect CPRI Cable | TAUSEEF ILYAS | 10/20/2025 20:13:09 | 10/20/2025 23:16:02 | 10/21/2025 02:13:09 | NR Cell Unavailable at MDN0133-P2_SRAN @ Sceco | 10/20/2025 20:06:11 | Major | 29841 | NR Cell Unavailable | 10/20/2025 20:04:38 | P2 | SRAN | madinah | Sceco | 5G SA | MDN0133 | FLM_TE | [8 empty] | API | 10/20/2025 20:13:09 | 10/20/2025 21:43:21 | 10/20/2025 21:43:50 | 10/20/2025 21:43:59 | 10/20/2025 21:50:49 | 10/20/2025 23:16:02 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001038 | PCM-20251020-00002215 | TT-20251020-02221 | Telecom | Region_3 | MDN0133 | MDN0133 | Equipment | SFP_BTS | Clean SFP | TAUSEEF ILYAS | 10/20/2025 20:16:16 | 10/20/2025 23:16:42 | 10/21/2025 02:16:16 | BBU CPRI Interface Error at MDN0133-P2_SRAN @ Sceco | 10/20/2025 20:12:00 | Major | 26234 | BBU CPRI Interface Error | 10/20/2025 20:09:26 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN0133 | FLM_TE | [8 empty] | API | 10/20/2025 20:16:16 | 10/20/2025 21:43:22 | 10/20/2025 23:16:36 |  |  | 10/20/2025 23:16:42 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001042 | PCM-20251020-00002226 | TT-20251020-02231 | Telecom | Region_4 | JED1M8243 | JED2243 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 20:23:29 | 10/21/2025 17:13:19 | 10/21/2025 02:23:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8243-L800-CA-SBTS-P3 @ Sceco | 10/20/2025 20:22:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:22:31 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8243 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 20:23:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001046 | PCM-20251020-00002233 | TT-20251020-02192 | Reference_telecom | Region_5 | SHD1M3142 | SHD0142 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable Connector | Jawad Ali Bakht Sher Khan | 10/20/2025 20:29:04 | 10/21/2025 02:18:17 | 10/21/2025 02:29:04 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at SHD1M3142-P2-USF @ Generator_SG | 10/20/2025 19:28:27 | Major | 7771 | WCDMA CELL OUT OF USE | 10/20/2025 19:26:20 | P2 | 3G | makkah | Generator_SG | 3G SA | SHD1M3142 | FLM_TE |  |  | PCM-20251020-00002188 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 20:29:04 | 10/20/2025 20:42:12 | 10/20/2025 21:53:08 | 10/20/2025 21:53:14 | 10/20/2025 22:38:38 | 10/21/2025 02:18:17 |  | Jawad Ali Bakht Sher Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001048 | PCM-20251020-00002235 | TT-20251020-02177 | Telecom | Region_4 | JED1MN2979 | JED2979 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 20:29:15 | 10/22/2025 11:18:45 | 10/21/2025 02:29:15 | BASE STATION HARDWARE PROBLEM (SFP Transceiver temperature too high) at JED1MN2979-NR2.6-P1-VIP @ Generator_SG | 10/20/2025 19:34:09 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/20/2025 19:34:02 | VIP | 5G | jeddah | Generator_SG | 5G NSA | JED1MN2979 | FLM_TE |  |  | PCM-20251020-00002171 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 20:29:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001051 | PCM-20251020-00002239 | TT-20251020-02204 | Reference_telecom | Region_3 | MDN2M7175 | MDN0175 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Hussain Ahmad Sultan Muhammad | 10/20/2025 20:29:51 | 10/21/2025 13:38:07 | 10/21/2025 08:29:51 | Cell RX Channel Interference Noise Power Unbalanced at MDN2M7175-P2-L800 @ Sceco | 10/20/2025 17:04:01 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/20/2025 17:03:57 | P2 | 4G | madinah | Sceco | 2G NSA | MDN2M7175 | FLM_TE |  |  | PCM-20251020-00002199 | Need FLM to make RF path HC for MRFU 0 5 0 | Need FLM to make RF path HC for MRFU 0 5 0 |  |  |  | API | 10/20/2025 20:29:51 | 10/20/2025 21:01:59 | 10/21/2025 12:26:03 | 10/21/2025 12:26:07 | 10/21/2025 12:34:08 | 10/21/2025 13:38:07 |  | Hussain Ahmad Sultan Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001055 | PCM-20251020-00002242 | TT-20251020-02240 | Reference_EM | Region_1 | RSK2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/20/2025 20:34:20 | 10/21/2025 07:19:16 | 10/21/2025 08:34:20 | high temprature 40 at RSK2086-P2_SRAN @ Sceco | 10/20/2025 20:23:52 | Minor | 65103 | high temprature 40 | 10/20/2025 20:23:47 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2086 | FLM_EM | [8 empty] | API | 10/20/2025 20:34:20 | 10/21/2025 07:19:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001061 | PCM-20251020-00002250 | TT-20251020-02244 | EM | Region_6 | QLW1M8364 | QLW2364 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/20/2025 20:35:22 | 10/21/2025 08:19:51 | 10/21/2025 08:35:22 | RECTIFIER MODULE FAILURE at QLW1M8364-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/20/2025 20:27:22 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/20/2025 20:27:12 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8364 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/20/2025 20:35:22 | 10/21/2025 08:19:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001064 | PCM-20251020-00002256 | TT-20251020-02246 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/20/2025 20:39:09 | 10/21/2025 17:13:18 | 10/21/2025 02:39:09 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/20/2025 20:32:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:32:19 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0483 | FLM_TE |  |  | PCM-20251020-00002254 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 20:39:09 | 10/20/2025 23:14:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001067 | PCM-20251020-00002272 | TT-20251020-02243 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/20/2025 20:54:11 | 10/21/2025 08:19:51 | 10/21/2025 02:54:11 | 2(2G) 2(LTE) sites down under BHAB2103-P3,BHAB2091-P3/BHAB2091-P3 @ Generator_SG | 10/20/2025 20:31:41 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 20:31:38 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2103-P3 2G_LTE,BHAB2091-P3 2G_LTE | FLM_EM | BHAB2091 | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251020-00002258 | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: BHAB2091 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/20/2025 20:54:11 | 10/21/2025 08:19:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251020001069 | PCM-20251020-00002275 | TT-20251020-02267 | Telecom | Region_4 | JED0044 | JED0044 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/20/2025 20:55:30 | 10/21/2025 07:48:39 | 10/21/2025 02:55:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0044-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1 @ Sceco | 10/20/2025 20:54:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:54:16 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0044 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 20:55:30 | 10/21/2025 07:48:26 | 10/21/2025 07:48:35 | 10/21/2025 07:48:37 | 10/21/2025 07:48:39 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001070 | PCM-20251020-00002278 | TT-20251020-02262 | EM | Region_6 | BHAB1M3903 | BHAB0903 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/20/2025 20:58:03 | 10/21/2025 17:30:29 | 10/21/2025 02:58:03 | 1(3G/LTE) sites down under BHAB0903-P3/BHAB1M3903-P3 @ Sceco | 10/20/2025 20:50:31 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/20/2025 20:49:55 | P3 | 3G | abha | Sceco | 3G_LTE SA | BHAB0903-P3 | FLM_EM | BHAB0903 | Results: DOWN SITE HUB BHAB0903-P3 BHAB0903 Summary: Hub: BHAB0903, Down Count: 1, Down Sites: BHAB0903-P3 Alarm Summary: BHAB0903 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 20:58:03 | 10/21/2025 17:20:19 | 10/21/2025 17:30:18 |  |  | 10/21/2025 17:30:29 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001071 | PCM-20251020-00002281 | TT-20251020-02237 | Telecom | Region_4 | JED2140 | JED2140 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 20:59:20 | 10/21/2025 18:52:48 | 10/21/2025 00:59:20 | 1(2G) 2(5G) sites down under JED0726-FWA-P1-VIP,JED2140-NR2.6-P2 @ Sceco | 10/20/2025 20:26:41 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/20/2025 20:26:39 | P2 | 2G | jeddah | Sceco | 2G_5G SA | JED2140-NR2.6-P2 5G,JED0726-FWA-P1-VIP 2G | FLM_TE | JED2140 | DOWN SITE HUB TX FB JED0726 JED0726 LOS to Air Scale JED2140 JED2140 LOS to Air Scale | PCM-20251020-00002246 | DOWN SITE HUB TX FB JED0726 JED0726 LOS to Air Scale JED2140 JED2140 LOS to Air Scale | DOWN SITE HUB TX FB JED0726 JED0726 LOS to Air Scale JED2140 JED2140 LOS to Air Scale |  | sites down |  | API | 10/20/2025 20:59:20 | 10/21/2025 18:52:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001072 | PCM-20251020-00002284 | TT-20251020-02268 | Telecom | Region_4 | HAW1M7308 | HAW0308 |  |  |  | Rashid Shafique | 10/20/2025 21:01:36 | 10/21/2025 09:56:43 | 10/21/2025 03:01:36 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at HAW1M7308-CA-L800-P3 @ Generator_SG | 10/20/2025 20:52:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:52:19 | P3 | 4G | taif | Generator_SG | 5G_Cell SA | HAW1M7308 | FLM_TE |  |  | PCM-20251020-00002276 | Please check RSSI at the site | Please check RSSI at the site |  |  |  | API | 10/20/2025 21:01:36 | 10/21/2025 09:56:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251019000947 | PCM-20251019-00002116 | TT-20251019-02270 | EM | Region_2 | BUR2110 | BUR2110 |  |  |  | Farman Ullah Muhammad Nazir | 10/19/2025 18:47:25 | 10/19/2025 19:38:19 | 10/20/2025 06:47:25 | Door opening alarm at BUR2110-P2_SRAN @ Sceco | 10/19/2025 18:46:54 | Minor | 65101 | Door opening alarm | 10/19/2025 18:46:49 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR2110 | FLM_EM | [8 empty] | API | 10/19/2025 18:47:25 | 10/19/2025 19:38:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251019000969 | PCM-20251019-00002186 | TT-20251019-02331 | Reference_EM | Region_1 | TRF2501 | TRF2501 | Enviroment | Genset failure_Starting Battery | Change Generator battery | Elsayed Moustafa Elsayed Khodir | 10/19/2025 19:13:46 | 10/19/2025 20:09:34 | 10/20/2025 07:13:46 | Low battery voltage at TRF2501-P3-USF_SRAN @ Generator_SG | 10/19/2025 19:03:09 | Minor | 65110 | Low battery voltage | 10/19/2025 19:03:06 | P3 | SRAN | arar | Generator_SG | 2G NSA | TRF2501 | FLM_EM | [8 empty] | API | 10/19/2025 19:13:46 | 10/19/2025 19:18:15 | 10/19/2025 20:09:00 | 10/19/2025 20:09:12 | 10/19/2025 20:09:17 | 10/19/2025 20:09:34 |  | Elsayed Moustafa Elsayed Khodir |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251019001110 | PCM-20251019-00002490 | TT-20251019-02571 | Reference_EM | Region_1 | HRBD0123 | HRBD0123 | Equipment | PMR_Power_Cable_RRU | Replace Power Cable | Mahmoud Youssef Mohamed Ahmed | 10/19/2025 21:31:40 | 10/19/2025 23:17:48 | 10/20/2025 03:31:40 | Mains Failure at HRBD0123-P1-HUB_SRAN @ Generator_SG | 10/19/2025 21:21:22 | Major | 65109 | Mains Failure | 10/19/2025 21:21:19 | P1 | SRAN | hafr | Generator_SG | 2G NSA | HRBD0123 | FLM_EM | [8 empty] | API | 10/19/2025 21:31:40 | 10/19/2025 21:47:15 | 10/19/2025 22:34:29 | 10/19/2025 22:34:31 | 10/19/2025 22:34:38 | 10/19/2025 23:17:48 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000042 | PCM-20251020-00000092 | TT-20251020-00095 | EM | Region_2 | RIY0785 | RIY0785 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:15:51 | 10/22/2025 11:33:13 | 10/20/2025 13:15:51 | Door opening alarm at RIY0785-P2_SRAN @ Sceco | 10/20/2025 01:15:14 | Minor | 65101 | Door opening alarm | 10/20/2025 01:13:33 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0785 | FLM_EM | [8 empty] | API | 10/20/2025 01:15:51 | 10/20/2025 08:42:55 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251020000046 | PCM-20251020-00000101 | TT-20251020-00104 | Reference_EM | Region_1 | HDT0951 | HDT0951 |  |  |  | Mabrouk Mohamed Mabrouk Kandil | 10/20/2025 01:22:01 | 10/20/2025 01:22:01 | 10/20/2025 07:22:01 | Mains Failure at HDT0951-P1-DIA_SRAN @ Sceco | 10/20/2025 01:11:42 | Major | 65109 | Mains Failure | 10/20/2025 01:11:38 | P1 | SRAN | quriyat | Sceco | 2G NSA | HDT0951 | FLM_EM | [8 empty] | API | 10/20/2025 01:22:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000049 | PCM-20251020-00000105 | TT-20251020-00107 | EM | Region_2 | RIY0081 | RIY0081 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/20/2025 01:23:35 | 10/22/2025 11:33:18 | 10/20/2025 07:23:35 | Minor Rec alarm at RIY0081-P1-DIA_SRAN @ Sceco | 10/20/2025 01:21:10 | Major | 65108 | Minor Rec alarm | 10/20/2025 01:12:55 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0081 | FLM_EM | [8 empty] | API | 10/20/2025 01:23:35 | 10/20/2025 13:14:18 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000050 | PCM-20251020-00000106 | TT-20251020-00108 | EM | Region_2 | RIY0384 | RIY0384 | Enviroment | Air Condition | Change Fan | Ahmed Khalifa Amin Aboueltaher | 10/20/2025 01:23:36 | 10/23/2025 00:38:32 | 10/20/2025 07:23:36 | Air condition 1 failure alarm at RIY0384-P1-SHOP_SRAN @ Sceco | 10/20/2025 01:19:36 | Major | 65104 | Air condition 1 failure alarm | 10/20/2025 01:13:13 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0384 | FLM_EM | [8 empty] | API | 10/20/2025 01:23:36 | 10/23/2025 00:38:32 | [5 empty] | Ahmed Khalifa Amin Aboueltaher | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000051 | PCM-20251020-00000108 | TT-20251020-00111 | EM | Region_2 | RIY0379 | RIY0379 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/20/2025 01:24:06 | 10/22/2025 11:33:19 | 10/20/2025 07:24:06 | Air condition 1 failure alarm at RIY0379-P1-SHOP_SRAN @ Sceco | 10/20/2025 01:18:55 | Major | 65104 | Air condition 1 failure alarm | 10/20/2025 01:13:37 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0379 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:06 | 10/20/2025 13:14:19 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000052 | PCM-20251020-00000107 | TT-20251020-00109 | EM | Region_2 | RIY0359 | RIY0359 |  |  |  | Vignesh Sivakumar Sivakumar | 10/20/2025 01:24:07 | 10/20/2025 16:26:14 | 10/20/2025 07:24:07 | high temprature 40 at RIY0359-P1_SRAN @ Sceco | 10/20/2025 01:21:50 | Major | 65103 | high temprature 40 | 10/20/2025 01:13:40 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0359 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:07 | 10/20/2025 16:26:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000053 | PCM-20251020-00000110 | TT-20251020-00110 | EM | Region_2 | RIY0518 | RIY0518 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/20/2025 01:24:07 | 10/22/2025 17:49:43 | 10/20/2025 13:24:07 | high temprature 40 at RIY0518-P2_SRAN @ Sceco | 10/20/2025 01:21:25 | Minor | 65103 | high temprature 40 | 10/20/2025 01:13:41 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0518 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:07 | 10/22/2025 17:49:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000054 | PCM-20251020-00000109 | TT-20251020-00112 | EM | Region_2 | RIY2037 | RIY2037 |  |  |  | Pawan Virdi Santokh Singh | 10/20/2025 01:24:10 | 10/20/2025 08:00:07 | 10/20/2025 13:24:10 | DC power fail at RIY2037-P2_SRAN @ Sceco | 10/20/2025 01:18:44 | Minor | 65106 | DC power fail | 10/20/2025 01:13:35 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2037 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:10 | 10/20/2025 08:00:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000055 | PCM-20251020-00000116 | TT-20251020-00118 | EM | Region_2 | RIY2068 | RIY2068 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:24:11 | 10/20/2025 08:42:56 | 10/20/2025 13:24:11 | Air condition 2 failure alarm at RIY2068-P3_SRAN @ Sceco | 10/20/2025 01:18:26 | Minor | 65105 | Air condition 2 failure alarm | 10/20/2025 01:13:38 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2068 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:11 | 10/20/2025 08:42:56 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000056 | PCM-20251020-00000111 | TT-20251020-00113 | EM | Region_2 | RIY0874 | RIY0874 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Tanveer Ahmad Muhammad Ishaq | 10/20/2025 01:24:13 | 10/23/2025 15:53:29 | 10/20/2025 13:24:13 | Minor Rec alarm at RIY0874-P2_SRAN @ Sceco | 10/20/2025 01:17:49 | Minor | 65108 | Minor Rec alarm | 10/20/2025 01:13:39 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0874 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:13 | 10/22/2025 17:49:43 | 10/23/2025 14:43:12 | 10/23/2025 14:43:14 | 10/23/2025 15:32:52 | 10/23/2025 15:53:29 |  | Tanveer Ahmad Muhammad Ishaq | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000058 | PCM-20251020-00000115 | TT-20251020-00117 | EM | Region_2 | RIY0419 | RIY0419 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/20/2025 01:24:15 | 10/22/2025 11:33:11 | 10/20/2025 13:24:15 | Major Rec alarm at RIY0419-P2_SRAN @ Sceco | 10/20/2025 01:14:20 | Minor | 65107 | Major Rec alarm | 10/20/2025 01:13:22 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0419 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:15 | 10/20/2025 06:49:41 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000059 | PCM-20251020-00000114 | TT-20251020-00116 | EM | Region_2 | RIY0375 | RIY0375 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/20/2025 01:24:16 | 10/22/2025 17:49:44 | 10/20/2025 13:24:16 | Fire Alarm at RIY0375-P2_SRAN @ Sceco | 10/20/2025 01:16:23 | Minor | 65119 | Fire Alarm | 10/20/2025 01:13:25 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0375 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:16 | 10/22/2025 17:49:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000060 | PCM-20251020-00000113 | TT-20251020-00115 | EM | Region_2 | RIY0409 | RIY0409 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/20/2025 01:24:17 | 10/22/2025 11:33:20 | 10/20/2025 07:24:17 | Air condition 2 failure alarm at RIY0409-P1-VIP_SRAN @ Sceco | 10/20/2025 01:15:51 | Major | 65105 | Air condition 2 failure alarm | 10/20/2025 01:13:34 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0409 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:17 | 10/20/2025 13:14:19 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000061 | PCM-20251020-00000119 | TT-20251020-00121 | EM | Region_2 | RIY0599 | RIY0599 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:24:35 | 10/22/2025 11:33:14 | 10/20/2025 13:24:35 | Air condition 1 failure alarm at RIY0599-P2_SRAN @ Sceco | 10/20/2025 01:18:53 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 01:13:56 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0599 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:35 | 10/20/2025 08:42:56 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000062 | PCM-20251020-00000118 | TT-20251020-00120 | EM | Region_2 | RIY0104 | RIY0104 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:24:36 | 10/20/2025 08:42:57 | 10/20/2025 07:24:36 | DC power fail at RIY0104-P1-DIA_SRAN @ Sceco | 10/20/2025 01:21:13 | Major | 65106 | DC power fail | 10/20/2025 01:14:02 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0104 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:36 | 10/20/2025 08:42:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000063 | PCM-20251020-00000117 | TT-20251020-00119 | EM | Region_2 | RIY0455 | RIY0455 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:24:37 | 10/22/2025 11:33:15 | 10/20/2025 13:24:37 | Air condition 2 failure alarm at RIY0455-P2_SRAN @ Sceco | 10/20/2025 01:19:18 | Minor | 65105 | Air condition 2 failure alarm | 10/20/2025 01:14:11 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0455 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:37 | 10/20/2025 08:42:57 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000065 | PCM-20251020-00000121 | TT-20251020-00123 | EM | Region_2 | RIY0378 | RIY0378 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:24:40 | 10/22/2025 11:33:16 | 10/20/2025 07:24:40 | Minor Rec alarm at RIY0378-P1-VIP_SRAN @ Sceco | 10/20/2025 01:18:48 | Major | 65108 | Minor Rec alarm | 10/20/2025 01:13:49 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0378 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:40 | 10/20/2025 08:42:58 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000064 | PCM-20251020-00000120 | TT-20251020-00122 | EM | Region_2 | RYQS2574 | RYQS2574 | Enviroment | Rectifier Module | Change rectifer module | Pawan Virdi Santokh Singh | 10/20/2025 01:24:40 | 10/22/2025 15:55:34 | 10/20/2025 13:24:40 | Minor Rec alarm at RYQS2574-P2_SRAN @ Generator_SG | 10/20/2025 01:17:47 | Minor | 65108 | Minor Rec alarm | 10/20/2025 01:13:50 | P2 | SRAN | rumah | Generator_SG | 2G NSA | RYQS2574 | FLM_EM | [8 empty] | API | 10/20/2025 01:24:40 | 10/22/2025 14:27:53 | 10/22/2025 14:28:54 | 10/22/2025 14:28:57 | 10/22/2025 14:39:03 | 10/22/2025 15:55:34 |  | Pawan Virdi Santokh Singh | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000067 | PCM-20251020-00000122 | TT-20251020-00125 | EM | Region_2 | RIY0158 | RIY0158 |  |  |  | Kadri Jalal Mohammed Asmail | 10/20/2025 01:25:06 | 10/22/2025 11:33:17 | 10/20/2025 13:25:06 | Air condition 1 failure alarm at RIY0158-P2_SRAN @ Sceco | 10/20/2025 01:19:18 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 01:14:20 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0158 | FLM_EM | [8 empty] | API | 10/20/2025 01:25:06 | 10/20/2025 08:42:58 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000068 | PCM-20251020-00000123 | TT-20251020-00126 | EM | Region_1 | DAM0371 | DAM0371 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/20/2025 01:25:06 | 10/20/2025 14:14:36 | 10/20/2025 05:25:06 | Major Rec alarm at DAM0371-P1-WDM_SRAN-FON @ Sceco | 10/20/2025 01:23:09 | Critical | 65107 | Major Rec alarm | 10/20/2025 01:20:48 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0371 | FLM_EM | [8 empty] | API | 10/20/2025 01:25:06 | 10/20/2025 14:14:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000069 | PCM-20251020-00000124 | TT-20251020-00124 | EM | Region_2 | RIY0116 | RIY0116 |  |  |  | Vignesh Sivakumar Sivakumar | 10/20/2025 01:25:11 | 10/20/2025 16:26:14 | 10/20/2025 07:25:11 | Fire Alarm at RIY0116-P1-SHOP_SRAN @ Sceco | 10/20/2025 01:17:47 | Major | 65119 | Fire Alarm | 10/20/2025 01:14:42 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0116 | FLM_EM | [8 empty] | API | 10/20/2025 01:25:11 | 10/20/2025 16:26:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000070 | PCM-20251020-00000126 | TT-20251020-00127 | EM | Region_2 | RIY0598 | RIY0598 |  |  |  | Vignesh Sivakumar Sivakumar | 10/20/2025 01:25:40 | 10/20/2025 16:26:15 | 10/20/2025 13:25:40 | Air condition 1 failure alarm at RIY0598-P2_SRAN-FON @ Sceco | 10/20/2025 01:17:44 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 01:14:56 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0598 | FLM_EM | [8 empty] | API | 10/20/2025 01:25:40 | 10/20/2025 16:26:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000071 | PCM-20251020-00000127 | TT-20251020-00128 | EM | Region_2 | RIY0462 | RIY0462 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/20/2025 01:25:41 | 10/22/2025 17:49:44 | 10/20/2025 07:25:41 | Air condition 1 failure alarm at RIY0462-P1-HUB_SRAN-FON @ Sceco | 10/20/2025 01:19:53 | Major | 65104 | Air condition 1 failure alarm | 10/20/2025 01:15:18 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0462 | FLM_EM | [8 empty] | API | 10/20/2025 01:25:41 | 10/22/2025 17:49:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000073 | PCM-20251020-00000132 | TT-20251020-00133 | EM | Region_2 | RIY2200 | RIY2200 |  |  |  | Adham Adham Hassan Farghal | 10/20/2025 01:28:46 | 10/20/2025 09:37:27 | 10/20/2025 13:28:46 | Mains Failure at RIY2200-P3_SRAN-PC @ Sceco | 10/20/2025 01:22:29 | Minor | 65109 | Mains Failure | 10/20/2025 01:18:18 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2200 | FLM_EM | [8 empty] | API | 10/20/2025 01:28:46 | 10/20/2025 09:37:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000076 | PCM-20251020-00000136 | TT-20251020-00136 | EM | Region_2 | RIY2617 | RIY2617 | Enviroment | Fire Alarm | Reset Fire Pannel | Tanveer Ahmad Fateh Muhammad | 10/20/2025 01:29:16 | 10/22/2025 14:57:44 | 10/20/2025 13:29:16 | Fire Fighting system alarm at RIY2617-P3_SRAN-PC @ Sceco | 10/20/2025 01:20:44 | Minor | 65111 | Fire Fighting system alarm | 10/20/2025 01:18:44 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2617 | FLM_EM | [8 empty] | API | 10/20/2025 01:29:16 | 10/20/2025 11:17:33 | 10/22/2025 14:41:18 | 10/22/2025 14:41:25 | 10/22/2025 14:41:33 | 10/22/2025 14:57:44 |  | Tanveer Ahmad Fateh Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000113 | PCM-20251020-00000201 | TT-20251020-00212 | EM | Region_1 | HFF0059 | HFF0059 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/20/2025 02:25:01 | 10/20/2025 10:23:39 | 10/20/2025 14:25:01 | Door opening alarm at HFF0059-P2_SRAN @ Sceco | 10/20/2025 02:24:27 | Minor | 65101 | Door opening alarm | 10/20/2025 02:24:22 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0059 | FLM_EM | [8 empty] | API | 10/20/2025 02:25:01 | 10/20/2025 04:22:39 | 10/20/2025 10:23:34 |  |  | 10/20/2025 10:23:39 |  | Shahid Khan Dilawar Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000118 | PCM-20251020-00000208 | TT-20251020-00217 | Reference_EM | Region_1 | QLB0006 | QLB0006 |  |  |  | Elsaid Adel Mohamed Abouhegara | 10/20/2025 02:29:41 | 10/22/2025 21:34:09 | 10/20/2025 14:29:41 | Generator Failure(SH1) at QLB2M7006-P3-PC @ Power Cube | 10/20/2025 02:18:57 | Minor | 65046 | Generator Failure(SH1) | 10/20/2025 02:18:54 | P3 | 4G | quriyat | Power Cube | 2G NSA | QLB2M7006 | FLM_EM | [8 empty] | API | 10/20/2025 02:29:41 | 10/22/2025 21:34:09 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000191 | PCM-20251020-00000371 | TT-20251020-00393 | EM | Region_1 | QLB0006 | QLB0006 |  |  |  | Elsaid Adel Mohamed Abouhegara | 10/20/2025 04:21:51 | 10/22/2025 21:34:10 | 10/20/2025 16:21:51 | Door opening at QLB2M7006-P3-PC @ Power Cube | 10/20/2025 04:21:03 | Minor | 65101 | Door opening | 10/20/2025 04:20:59 | P3 | 4G | quriyat | Power Cube | 2G NSA | QLB2M7006 | FLM_EM | [8 empty] | API | 10/20/2025 04:21:51 | 10/22/2025 21:34:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000201 | PCM-20251020-00000386 | TT-20251020-00417 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/20/2025 04:40:56 | 10/20/2025 13:09:24 | 10/20/2025 16:40:56 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/20/2025 04:34:34 | Minor | 40564 | Genset Fault | 10/20/2025 04:34:34 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/20/2025 04:40:56 | 10/20/2025 07:12:14 | 10/20/2025 13:09:14 |  |  | 10/20/2025 13:09:24 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251020000220 | PCM-20251020-00000415 | TT-20251020-00450 | Reference_EM | Region_1 | ARM0991 | ARM0991 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Montasir Awadalla Abdalla Bala | 10/20/2025 05:18:12 | 10/20/2025 09:57:56 | 10/20/2025 17:18:12 | Generator failure at ARM0991-P2_SRAN-PC @ Power Cube | 10/20/2025 05:07:46 | Minor | 65114 | Generator failure | 10/20/2025 05:07:43 | P2 | SRAN | hafouf | Power Cube | 2G NSA | ARM0991 | FLM_EM | [8 empty] | API | 10/20/2025 05:18:12 | 10/20/2025 06:23:34 | 10/20/2025 06:33:36 | 10/20/2025 06:35:31 | 10/20/2025 06:35:36 | 10/20/2025 09:57:56 |  | Montasir Awadalla Abdalla Bala |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251020000236 | PCM-20251020-00000507 | TT-20251020-00548 | EM | Region_1 | HDT0951 | HDT0951 |  |  |  | Mabrouk Mohamed Mabrouk Kandil | 10/20/2025 06:09:21 | 10/20/2025 06:09:21 | 10/20/2025 12:09:21 | Door opening alarm at HDT0951-P1-DIA_SRAN @ Sceco | 10/20/2025 06:08:35 | Major | 65101 | Door opening alarm | 10/20/2025 06:08:32 | P1 | SRAN | quriyat | Sceco | 2G NSA | HDT0951 | FLM_EM | [8 empty] | API | 10/20/2025 06:09:21 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000241 | PCM-20251020-00000520 | TT-20251020-00558 | EM | Region_2 | RYMK2519 | RYMK2519 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Saleem Khan Amir Dost | 10/20/2025 06:20:41 | 10/20/2025 10:46:24 | 10/20/2025 18:20:41 | Mains Failure at RYMK2519-P2-HUB_SRAN @ Generator_DG | 10/20/2025 06:10:25 | Minor | 65109 | Mains Failure | 10/20/2025 06:10:22 | P2 | SRAN | quweyah | Generator_DG | 2G NSA | RYMK2519 | FLM_EM | [8 empty] | API | 10/20/2025 06:20:41 | 10/20/2025 09:59:57 | 10/20/2025 10:17:02 | 10/20/2025 10:17:06 | 10/20/2025 10:17:10 | 10/20/2025 10:46:24 |  | Saleem Khan Amir Dost |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000262 | PCM-20251020-00000567 | TT-20251020-00611 | Reference_EM | Region_1 | SMN0831 | SMN0831 |  |  |  | Shaker Saied Mohamed ElShafie | 10/20/2025 07:14:26 | 10/20/2025 07:33:15 | 10/20/2025 13:14:26 | Mains Failure at SMN0831-P1-USF-HUB_SRAN @ Sceco | 10/20/2025 07:04:03 | Major | 65109 | Mains Failure | 10/20/2025 07:04:00 | P1 | SRAN | hafr | Sceco | 2G NSA | SMN0831 | FLM_EM | [8 empty] | API | 10/20/2025 07:14:26 | 10/20/2025 07:33:15 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000264 | PCM-20251020-00000577 | TT-20251020-00620 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/20/2025 07:26:16 | 10/22/2025 21:40:43 | 10/20/2025 19:26:16 | Generator failure at SMN0805-P3_SRAN @ Generator_DG | 10/20/2025 07:18:18 | Minor | 65114 | Generator failure | 10/20/2025 07:15:54 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/20/2025 07:26:16 | 10/22/2025 21:40:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000300 | PCM-20251020-00000646 | TT-20251020-00683 | EM | Region_1 | KBR0163 | KBR0163 |  |  |  | Yasser Mohamed Abdelnabi Ibrahim | 10/20/2025 08:04:01 | 10/20/2025 13:04:36 | 10/20/2025 12:04:01 | high temprature 40 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/20/2025 08:01:45 | Critical | 65103 | high temprature 40 | 10/20/2025 08:01:41 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/20/2025 08:04:01 | 10/20/2025 13:04:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000322 | PCM-20251020-00000689 | TT-20251020-00719 | Reference_EM | Region_1 | KFJ2490 | KFJ2490 |  |  |  | Dileesh Muringothil Devarajan | 10/20/2025 08:24:06 | 10/20/2025 09:37:50 | 10/20/2025 20:24:06 | Air condition 1 failure alarm at KFJ2490-P2_SRAN @ Sceco | 10/20/2025 08:13:36 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 08:13:33 | P2 | SRAN | khafji | Sceco | 2G NSA | KFJ2490 | FLM_EM | [8 empty] | API | 10/20/2025 08:24:06 | 10/20/2025 09:37:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000329 | PCM-20251020-00000702 | TT-20251020-00728 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/20/2025 08:32:51 | 10/20/2025 14:14:36 | 10/20/2025 20:32:51 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/20/2025 08:22:21 | Minor | 65102 | high temprature 32 | 10/20/2025 08:22:18 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/20/2025 08:32:51 | 10/20/2025 14:14:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000355 | PCM-20251020-00000758 | TT-20251020-00785 | EM | Region_1 | DAM2072 | DAM2072 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/20/2025 08:55:35 | 10/20/2025 11:08:00 | 10/20/2025 20:55:35 | Door opening alarm at DAM2072-P3-CAP_SRAN @ Generator_SG | 10/20/2025 08:55:04 | Minor | 65101 | Door opening alarm | 10/20/2025 08:54:58 | P3 | SRAN | dammam | Generator_SG | 2G NSA | DAM2072 | FLM_EM | [8 empty] | API | 10/20/2025 08:55:35 | 10/20/2025 11:08:00 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000383 | PCM-20251020-00000834 | TT-20251020-00856 | EM | Region_1 | NRY0541 | NRY0541 | Enviroment | SCECO_Failure | SCECO auto restored | Dileesh Muringothil Devarajan | 10/20/2025 09:39:00 | 10/20/2025 11:53:27 | 10/20/2025 21:39:00 | Main Failure at NRY2M7541-P3-PC @ Sceco | 10/20/2025 09:28:51 | Minor | 65109 | Main Failure | 10/20/2025 09:28:47 | P3 | 4G | jubail | Sceco | LTE NSA | NRY2M7541 | FLM_EM | [8 empty] | API | 10/20/2025 09:39:00 | 10/20/2025 09:41:12 | 10/20/2025 11:20:00 | 10/20/2025 11:20:03 | 10/20/2025 11:20:05 | 10/20/2025 11:53:27 |  | Dileesh Muringothil Devarajan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251020000389 | PCM-20251020-00000851 | TT-20251020-00872 | EM | Region_1 | SAK0583 | SAK0583 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Amjad Muhammad | 10/20/2025 09:43:40 | 10/20/2025 15:26:53 | 10/20/2025 21:43:40 | Mains Failure at SAK0583-P3_SRAN @ Sceco | 10/20/2025 09:41:47 | Minor | 65109 | Mains Failure | 10/20/2025 09:30:49 | P3 | SRAN | sakaka | Sceco | 2G NSA | SAK0583 | FLM_EM | [8 empty] | API | 10/20/2025 09:43:40 | 10/20/2025 12:25:03 | 10/20/2025 15:26:30 |  |  | 10/20/2025 15:26:53 |  | Mohamed Amjad Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000390 | PCM-20251020-00000852 | TT-20251020-00873 | EM | Region_1 | HMBY2123 | HMBY2123 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/20/2025 09:44:11 | 10/20/2025 10:19:24 | 10/20/2025 21:44:11 | Mains Failure at HMBY2123-P3_SRAN @ Generator_SG | 10/20/2025 09:34:04 | Minor | 65109 | Mains Failure | 10/20/2025 09:34:00 | P3 | SRAN | dammam | Generator_SG | 2G NSA | HMBY2123 | FLM_EM | [8 empty] | API | 10/20/2025 09:44:11 | 10/20/2025 10:19:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000391 | PCM-20251020-00000853 | TT-20251020-00875 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/20/2025 09:45:46 | 10/20/2025 19:22:10 | 10/20/2025 15:45:46 | high temprature 40 at RIY0232-P1_SRAN @ Sceco | 10/20/2025 09:34:59 | Major | 65103 | high temprature 40 | 10/20/2025 09:34:56 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/20/2025 09:45:46 | 10/20/2025 19:22:10 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000407 | PCM-20251020-00000887 | TT-20251020-00909 | EM | Region_1 | KBR0987 | KBR0987 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Khaled Mohamed Abdulla Wahba | 10/20/2025 10:11:35 | 10/20/2025 16:33:45 | 10/20/2025 22:11:35 | Door opening alarm at KBR0987-P3_SRAN @ Sceco | 10/20/2025 10:10:44 | Minor | 65101 | Door opening alarm | 10/20/2025 10:10:41 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0987 | FLM_EM | [8 empty] | API | 10/20/2025 10:11:35 | 10/20/2025 11:04:24 | 10/20/2025 16:33:36 |  |  | 10/20/2025 16:33:45 |  | Khaled Mohamed Abdulla Wahba |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251020000425 | PCM-20251020-00000923 | TT-20251020-00939 | Reference_EM | Region_1 | DAM2409 | DAM2409 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/20/2025 10:32:15 | 10/20/2025 11:38:09 | 10/20/2025 22:32:15 | high temprature 32 at DAM2409-P2_SRAN @ Sceco | 10/20/2025 10:17:01 | Minor | 65102 | high temprature 32 | 10/20/2025 10:21:26 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2409 | FLM_EM | [8 empty] | API | 10/20/2025 10:32:15 | 10/20/2025 11:37:53 | 10/20/2025 11:38:00 | 10/20/2025 11:38:06 | 10/20/2025 11:38:09 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000447 | PCM-20251020-00000997 | TT-20251020-01018 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change compressor | Emad Mahmoud Ahmed Mohamed | 10/20/2025 11:06:52 | 10/21/2025 15:08:22 | 10/20/2025 15:06:52 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/20/2025 11:04:44 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/20/2025 11:04:37 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 1-(1-B) |  |  | API | 10/20/2025 11:06:52 | 10/20/2025 12:01:22 | 10/21/2025 15:08:11 |  |  | 10/21/2025 15:08:22 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000474 | PCM-20251020-00001050 | TT-20251020-01065 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/20/2025 11:30:36 | 10/20/2025 13:29:47 | 10/20/2025 17:30:36 | high temprature 32 at DAM2066-P1-HUB_SRAN @ Sceco | 10/20/2025 11:09:57 | Major | 65102 | high temprature 32 | 10/20/2025 11:19:59 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/20/2025 11:30:36 | 10/20/2025 13:29:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000483 | PCM-20251020-00001077 | TT-20251020-01094 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/20/2025 11:46:40 | 10/20/2025 15:43:18 | 10/20/2025 23:46:40 | high temprature 40 at RYHF2036-P2_SRAN @ Generator_SG | 10/20/2025 11:36:13 | Minor | 65103 | high temprature 40 | 10/20/2025 11:36:08 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/20/2025 11:46:40 | 10/20/2025 15:43:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000486 | PCM-20251020-00001082 | TT-20251020-01097 | EM | Region_1 | HFB0003 | HFB0003 |  |  |  | Reda Magdi Elmetwalli Ghazi | 10/20/2025 11:47:40 | 10/20/2025 13:21:49 | 10/20/2025 23:47:40 | Door opening alarm at HFB2M5003-P2 @ Generator_DG | 10/20/2025 11:47:17 | Minor | 65101 | Door opening alarm | 10/20/2025 11:47:13 | P2 | 2G | hafouf | Generator_DG | 2G NSA | HFB2M5003 | FLM_EM | [8 empty] | API | 10/20/2025 11:47:40 | 10/20/2025 13:21:49 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000510 | PCM-20251020-00001126 | TT-20251020-01137 | EM | Region_1 | ARM0991 | ARM0991 |  |  |  | Montasir Awadalla Abdalla Bala | 10/20/2025 12:04:11 | 10/21/2025 00:02:05 | 10/21/2025 00:04:11 | Door opening alarm at ARM0991-P2_SRAN-PC @ Power Cube | 10/20/2025 12:03:46 | Minor | 65101 | Door opening alarm | 10/20/2025 12:03:42 | P2 | SRAN | hafouf | Power Cube | 2G NSA | ARM0991 | FLM_EM | [8 empty] | API | 10/20/2025 12:04:11 | 10/21/2025 00:02:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000522 | PCM-20251020-00001160 | TT-20251020-01171 | EM | Region_1 | SKAR0181 | SKAR0181 | Enviroment | SCECO_Failure | SCECO auto restored | Asmat Anwar Sher Ullah Khan | 10/20/2025 12:21:15 | 10/20/2025 16:05:56 | 10/20/2025 16:21:15 | Genset running at SKAR0181-P2-WDM_SRAN @ Sceco_STB | 10/20/2025 12:19:02 | Critical | 65112 | Genset running | 10/20/2025 12:19:00 | P2 | SRAN | sakaka | Sceco_STB | 2G NSA | SKAR0181 | FLM_EM | [8 empty] | API | 10/20/2025 12:21:15 | 10/20/2025 12:21:24 | 10/20/2025 13:58:16 | 10/20/2025 13:58:19 | 10/20/2025 13:58:23 | 10/20/2025 16:05:56 |  | Asmat Anwar Sher Ullah Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251020000531 | PCM-20251020-00001176 | TT-20251020-01184 | EM | Region_1 | SKA0180 | SKA0180 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Mohammed Kholi | 10/20/2025 12:29:00 | 10/20/2025 16:16:17 | 10/21/2025 00:29:00 | Mains Failure at SKA0180-P3_SRAN @ Sceco | 10/20/2025 12:19:02 | Minor | 65109 | Mains Failure | 10/20/2025 12:18:58 | P3 | SRAN | sakaka | Sceco | 2G NSA | SKA0180 | FLM_EM | [8 empty] | API | 10/20/2025 12:29:00 |  | 10/20/2025 16:16:09 |  |  | 10/20/2025 16:16:17 |  | Mohammed Kholi |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000532 | PCM-20251020-00001178 | TT-20251020-01185 | EM | Region_1 | SKA0178 | SKA0178 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Amjad Muhammad | 10/20/2025 12:29:01 | 10/20/2025 15:27:51 | 10/21/2025 00:29:01 | Mains Failure at SKA0178-P2_SRAN @ Sceco | 10/20/2025 12:19:00 | Minor | 65109 | Mains Failure | 10/20/2025 12:18:56 | P2 | SRAN | sakaka | Sceco | 2G NSA | SKA0178 | FLM_EM | [8 empty] | API | 10/20/2025 12:29:01 | 10/20/2025 12:32:40 | 10/20/2025 15:17:32 | 10/20/2025 15:17:35 |  | 10/20/2025 15:27:51 |  | Mohamed Amjad Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000541 | PCM-20251020-00001198 | TT-20251020-01209 | EM | Region_1 | ARR9807 | ARR9807 | Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator | Ismail Salah Ismail Elbery | 10/20/2025 12:35:41 | 10/22/2025 13:21:35 | 10/21/2025 00:35:41 | NETECO: Genset Work Abnormally at ARR9807 @ Generator_SG | 10/20/2025 12:29:20 | Minor | 40561 | Genset Work Abnormally | 10/20/2025 12:29:20 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/20/2025 12:35:41 | 10/22/2025 13:20:36 | 10/22/2025 13:21:28 |  |  | 10/22/2025 13:21:35 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000547 | PCM-20251020-00001204 | TT-20251020-01215 | EM | Region_1 | DAM2409 | DAM2409 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/20/2025 12:38:51 | 10/20/2025 13:29:47 | 10/21/2025 00:38:51 | Door opening alarm at DAM2409-P2_SRAN @ Sceco | 10/20/2025 12:38:16 | Minor | 65101 | Door opening alarm | 10/20/2025 12:38:13 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2409 | FLM_EM | [8 empty] | API | 10/20/2025 12:38:51 | 10/20/2025 13:29:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000554 | PCM-20251020-00001214 | TT-20251020-01227 | Reference_EM | Region_1 | SMN0851 | SMN0851 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/20/2025 12:44:30 | 10/20/2025 13:09:48 | 10/21/2025 00:44:30 | Air condition 1 failure alarm at SMN0851-P2-USF_SRAN @ Generator_SG | 10/20/2025 12:33:54 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 12:33:52 | P2 | SRAN | hafr | Generator_SG | 2G NSA | SMN0851 | FLM_EM | [8 empty] | API | 10/20/2025 12:44:30 | 10/20/2025 13:07:49 | 10/20/2025 13:09:35 |  |  | 10/20/2025 13:09:48 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000586 | PCM-20251020-00001276 | TT-20251020-01281 | EM | Region_1 | SLW0916 | SLW0916 |  |  |  | Moustafa Mohamed Saleh Saif | 10/20/2025 13:16:31 | 10/20/2025 14:37:41 | 10/21/2025 01:16:31 | Generator failure at SLW0916-P2-USF_SRAN-PC @ Power Cube | 10/20/2025 13:06:20 | Minor | 65114 | Generator failure | 10/20/2025 13:06:13 | P2 | SRAN | hafouf | Power Cube | 2G NSA | SLW0916 | FLM_EM | [8 empty] | API | 10/20/2025 13:16:31 | 10/20/2025 14:37:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000590 | PCM-20251020-00001280 | TT-20251020-01283 | Reference_EM | Region_1 | SLW0912 | SLW0912 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Moustafa Mohamed Saleh Saif | 10/20/2025 13:17:00 | 10/20/2025 17:16:19 | 10/21/2025 01:17:00 | Generator failure at SLW0912-P3-USF_SRAN-PC @ Power Cube | 10/20/2025 13:06:20 | Minor | 65114 | Generator failure | 10/20/2025 13:06:16 | P3 | SRAN | hafouf | Power Cube | 2G NSA | SLW0912 | FLM_EM | [8 empty] | API | 10/20/2025 13:17:00 | 10/20/2025 14:36:49 | 10/20/2025 15:34:48 | 10/20/2025 15:34:59 | 10/20/2025 15:35:03 | 10/20/2025 17:16:19 |  | Moustafa Mohamed Saleh Saif |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251020000593 | PCM-20251020-00001285 | TT-20251020-01297 | EM | Region_1 | HFS2026 | HFS2026 |  |  |  | Ayman Ibrahim Mohamed Elayad | 10/20/2025 13:21:42 | 10/20/2025 13:21:42 | 10/21/2025 01:21:42 | Door opening alarm at HFS2M2026-P3 @ Generator_SG | 10/20/2025 13:21:14 | Minor | 65101 | Door opening alarm | 10/20/2025 13:21:09 | P3 | 2G | hafouf | Generator_SG | 2G NSA | HFS2M2026 | FLM_EM | [8 empty] | API | 10/20/2025 13:21:42 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000598 | PCM-20251020-00001304 | TT-20251020-01314 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/20/2025 13:28:26 | 10/21/2025 09:24:30 | 10/21/2025 01:28:26 | high temprature 40 at KBR0166-P3_SRAN @ Sceco | 10/20/2025 13:17:58 | Minor | 65103 | high temprature 40 | 10/20/2025 13:17:55 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/20/2025 13:28:26 | 10/21/2025 09:24:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000603 | PCM-20251020-00001314 | TT-20251020-01328 | EM | Region_1 | DAM0389 | DAM0389 | Enviroment | Air Condition | Change Fan | Yasser Mohamed Abdelnabi Ibrahim | 10/20/2025 13:36:11 | 10/21/2025 16:20:19 | 10/20/2025 17:36:11 | Air condition 2 failure alarm at DAM0389-FWA-P1-VIP-HUB-WDM_SRAN @ Sceco | 10/20/2025 13:34:08 | Critical | 65105 | Air condition 2 failure alarm | 10/20/2025 13:34:04 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0389 | FLM_EM | [8 empty] | API | 10/20/2025 13:36:11 | 10/21/2025 11:13:33 | 10/21/2025 12:31:01 | 10/21/2025 12:31:08 | 10/21/2025 12:31:11 | 10/21/2025 16:20:19 |  | Yasser Mohamed Abdelnabi Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000610 | PCM-20251020-00001330 | TT-20251020-01342 | Reference_EM | Region_1 | ARM0871 | ARM0871 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/20/2025 13:43:26 | 10/20/2025 14:50:04 | 10/21/2025 01:43:26 | High temperature 32C alarm at ARM2M1871-P3 @ Sceco | 10/20/2025 13:32:51 | Minor | 65102 | High temperature 32C alarm | 10/20/2025 13:32:48 | P3 | 2G | dammam | Sceco | 2G NSA | ARM2M1871 | FLM_EM | [8 empty] | API | 10/20/2025 13:43:26 | 10/20/2025 14:50:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000623 | PCM-20251020-00001358 | TT-20251020-01378 | Reference_EM | Region_1 | NRY0574 | NRY0574 |  |  |  | Dileesh Muringothil Devarajan | 10/20/2025 13:55:21 | 10/20/2025 16:39:56 | 10/21/2025 01:55:21 | Minor Rec alarm at NRY0574-P3-USF_SRAN-PC @ Sceco | 10/20/2025 13:44:51 | Minor | 65108 | Minor Rec alarm | 10/20/2025 13:44:47 | P3 | SRAN | jubail | Sceco | 2G NSA | NRY0574 | FLM_EM | [8 empty] | API | 10/20/2025 13:55:21 | 10/20/2025 16:39:56 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000634 | PCM-20251020-00001378 | TT-20251020-01388 | EM | Region_1 | SAK0583 | SAK0583 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Mohamed Amjad Muhammad | 10/20/2025 14:00:26 | 10/20/2025 16:03:16 | 10/21/2025 02:00:26 | Door opening alarm at SAK0583-P3_SRAN @ Sceco | 10/20/2025 14:00:01 | Minor | 65101 | Door opening alarm | 10/20/2025 13:48:46 | P3 | SRAN | sakaka | Sceco | 2G NSA | SAK0583 | FLM_EM | [8 empty] | API | 10/20/2025 14:00:26 | 10/20/2025 15:53:23 | 10/20/2025 16:02:51 |  |  | 10/20/2025 16:03:16 |  | Mohamed Amjad Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000636 | PCM-20251020-00001382 | TT-20251020-01391 | EM | Region_1 | URY9013 | URY9013 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/20/2025 14:03:00 | 10/22/2025 02:05:04 | 10/21/2025 02:03:00 | NETECO: Speed Sensor Failure at URY9013 @ Power Cube | 10/20/2025 13:56:42 | Minor | 8143 | Speed Sensor Failure | 10/20/2025 13:56:42 | P3 | Repeater | jubail | Power Cube | 2G NSA | URY9013 | FLM_EM | [8 empty] | API | 10/20/2025 14:03:00 | 10/22/2025 02:05:04 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000646 | PCM-20251020-00001414 | TT-20251020-01429 | Reference_EM | Region_1 | DMAP0404 | DMAP0404 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/20/2025 14:12:50 | 10/21/2025 05:58:39 | 10/20/2025 20:12:50 | Air-condition #2 failure alarm at DMAP2M3404-P1-VIP @ Generator_SG | 10/20/2025 14:02:25 | Major | 65105 | Air-condition #2 failure alarm | 10/20/2025 14:02:21 | VIP | 3G | dammam | Generator_SG | 3G NSA | DMAP2M3404 | FLM_EM | [8 empty] | API | 10/20/2025 14:12:50 | 10/21/2025 05:58:22 | 10/21/2025 05:58:31 |  |  | 10/21/2025 05:58:39 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000662 | PCM-20251020-00001446 | TT-20251020-01463 | EM | Region_2 | AFL9003 | AFL9003 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Sher Zamin Nasib Muhammad | 10/20/2025 14:23:11 | 10/21/2025 07:54:19 | 10/20/2025 18:23:11 | RELAY_ALARM_CRITICAL at AFL9003_NE_2 @ Power Cube | 10/20/2025 14:22:16 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/20/2025 14:22:04 | P3 | Repeater | aflaj | Power Cube | TX NSA | AFL9003 | FLM_EM | [8 empty] | API | 10/20/2025 14:23:11 | 10/21/2025 07:53:18 | 10/21/2025 07:54:11 |  |  | 10/21/2025 07:54:19 |  | Sher Zamin Nasib Muhammad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000676 | PCM-20251020-00001476 | TT-20251020-01495 | Reference_EM | Region_2 | KHJ0011 | KHJ0011 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Fritz Ian Generale | 10/20/2025 14:36:36 | 10/20/2025 16:08:05 | 10/21/2025 02:36:36 | Generator failure at KHJ0011-P2-USF_SRAN-PC @ Power Cube | 10/20/2025 14:26:18 | Minor | 65114 | Generator failure | 10/20/2025 14:26:15 | P2 | SRAN | al kharj | Power Cube | 2G NSA | KHJ0011 | FLM_EM | [8 empty] | API | 10/20/2025 14:36:36 | 10/20/2025 15:44:35 | 10/20/2025 15:44:43 | 10/20/2025 15:44:48 | 10/20/2025 15:54:27 | 10/20/2025 16:08:05 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000711 | PCM-20251020-00001568 | TT-20251020-01585 | EM | Region_1 | JBL0531 | JBL0531 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/20/2025 15:17:55 | 10/21/2025 09:08:25 | 10/21/2025 03:17:55 | Door opening alarm at JBL0531-P3_SRAN-PC @ Power Cube | 10/20/2025 15:17:32 | Minor | 65101 | Door opening alarm | 10/20/2025 15:17:29 | P3 | SRAN | jubail | Power Cube | 2G NSA | JBL0531 | FLM_EM | [8 empty] | API | 10/20/2025 15:17:55 | 10/21/2025 09:08:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000769 | PCM-20251020-00001635 | TT-20251020-01648 | EM | Region_1 | SMN0806 | SMN0806 |  |  |  | Rahman Ullah Said Halim | 10/20/2025 15:22:06 | 10/22/2025 21:40:44 | 10/21/2025 03:22:06 | Door opening alarm at SMN0806-P2_SRAN @ Generator_DG | 10/20/2025 15:21:26 | Minor | 65101 | Door opening alarm | 10/20/2025 15:21:23 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/20/2025 15:22:06 | 10/22/2025 21:40:44 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000784 | PCM-20251020-00001669 | TT-20251020-01674 | EM | Region_1 | URY9011 | URY9011 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/20/2025 15:34:31 | 10/20/2025 15:48:45 | 10/20/2025 19:34:31 | RELAY_ALARM_CRITICAL at URY9011_NE_2 @ Sceco | 10/20/2025 15:33:33 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/20/2025 15:33:21 | P3 | Repeater | dammam | Sceco | TX NSA | URY9011 | FLM_EM | [8 empty] | API | 10/20/2025 15:34:31 | 10/20/2025 15:48:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251020000795 | PCM-20251020-00001693 | TT-20251020-01693 | Reference_EM | Region_1 | DMJR2263 | DMJR2263 | Enviroment | Air Condition | Change Fan | Ibrahim Ù Abdulfttah Ibrahim | 10/20/2025 15:41:11 | 10/20/2025 20:57:17 | 10/21/2025 03:41:11 | Air condition 1 failure alarm at DMJR2263-P3-USF_SRAN @ Generator_DG | 10/20/2025 15:30:44 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 15:30:41 | P3 | SRAN | hafr | Generator_DG | 2G NSA | DMJR2263 | FLM_EM | [8 empty] | API | 10/20/2025 15:41:11 | 10/20/2025 20:30:28 | 10/20/2025 20:32:15 | 10/20/2025 20:37:04 | 10/20/2025 20:37:08 | 10/20/2025 20:57:17 |  | Ibrahim Ù Abdulfttah Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000805 | PCM-20251020-00001715 | TT-20251020-01711 | EM | Region_1 | ARR9807 | ARR9807 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ismail Salah Ismail Elbery | 10/20/2025 15:47:55 | 10/22/2025 13:21:24 | 10/21/2025 03:47:55 | NETECO: Door Status Sensor Alarm at ARR9807 @ Generator_SG | 10/20/2025 15:47:18 | Minor | 5152 | Door Status Sensor Alarm | 10/20/2025 15:47:18 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/20/2025 15:47:55 | 10/22/2025 13:20:36 | 10/22/2025 13:21:17 |  |  | 10/22/2025 13:21:24 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000821 | PCM-20251020-00001761 | TT-20251020-01753 | EM | Region_1 | SKAR0181 | SKAR0181 | Enviroment | Air Condition | Change Blower | Asmat Anwar Sher Ullah Khan | 10/20/2025 16:04:56 | 10/20/2025 20:45:39 | 10/20/2025 20:04:56 | AMBIENT_TEMP_FLUCT at SKAR0181_HYB @ Sceco_STB | 10/20/2025 16:03:12 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/20/2025 16:03:07 | P2 | SRAN | sakaka | Sceco_STB | DWDM NSA | SKAR0181 | FLM_EM | [5 empty] | 3-TO ARR0518(1-A) |  |  | API | 10/20/2025 16:04:56 | 10/20/2025 16:06:22 | 10/20/2025 20:44:47 |  |  | 10/20/2025 20:45:39 |  | Asmat Anwar Sher Ullah Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251020000841 | PCM-20251020-00001797 | TT-20251020-01785 | Reference_EM | Region_1 | SMN0806 | SMN0806 |  |  |  | Rahman Ullah Said Halim | 10/20/2025 16:18:21 | 10/22/2025 21:40:45 | 10/21/2025 04:18:21 | Air condition 1 failure alarm at SMN0806-P2_SRAN @ Generator_DG | 10/20/2025 16:07:47 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 16:07:44 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0806 | FLM_EM | [8 empty] | API | 10/20/2025 16:18:21 | 10/22/2025 21:40:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251020000852 | PCM-20251020-00001827 | TT-20251020-01814 | EM | Region_1 | DMAP0404 | DMAP0404 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/20/2025 16:28:16 | 10/21/2025 05:58:51 | 10/20/2025 22:28:16 | Door opening alarm at DMAP2M3404-P1-VIP @ Generator_SG | 10/20/2025 16:27:48 | Major | 65101 | Door opening alarm | 10/20/2025 16:27:45 | VIP | 3G | dammam | Generator_SG | 3G NSA | DMAP2M3404 | FLM_EM | [8 empty] | API | 10/20/2025 16:28:16 | 10/21/2025 05:58:22 | 10/21/2025 05:58:44 |  |  | 10/21/2025 05:58:51 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000862 | PCM-20251020-00001844 | TT-20251020-01835 | EM | Region_1 | HFF2359 | HFF2359 |  |  |  | Moustafa Mohamed Saleh Saif | 10/20/2025 16:34:56 | 10/21/2025 11:34:11 | 10/21/2025 04:34:56 | NETECO: Communication Failure at HFF2359 @ Sceco | 10/20/2025 16:28:07 | Minor | 9354 | Communication Failure | 10/20/2025 16:28:07 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2359 | FLM_EM | [8 empty] | API | 10/20/2025 16:34:56 | 10/21/2025 11:34:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000888 | PCM-20251020-00001894 | TT-20251020-01888 | EM | Region_1 | RAF0511 | RAF0511 |  |  |  | Murtada Awad AbdElwahab Ahmed | 10/20/2025 17:01:16 | 10/20/2025 20:12:18 | 10/21/2025 05:01:16 | Door opening alarm at RAF0511-P2-USF_SRAN @ Sceco | 10/20/2025 17:00:51 | Minor | 65101 | Door opening alarm | 10/20/2025 17:00:48 | P2 | SRAN | rafha | Sceco | 2G NSA | RAF0511 | FLM_EM | [8 empty] | API | 10/20/2025 17:01:16 | 10/20/2025 20:12:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000906 | PCM-20251020-00001931 | TT-20251020-01924 | EM | Region_1 | HFF2359 | HFF2359 |  |  |  | Moustafa Mohamed Saleh Saif | 10/20/2025 17:16:41 | 10/21/2025 11:34:12 | 10/21/2025 05:16:41 | NETECO: Door Status Sensor Alarm at HFF2359 @ Sceco | 10/20/2025 17:16:14 | Minor | 5152 | Door Status Sensor Alarm | 10/20/2025 17:16:14 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2359 | FLM_EM | [8 empty] | API | 10/20/2025 17:16:41 | 10/21/2025 11:34:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000907 | PCM-20251020-00001932 | TT-20251020-01925 | EM | Region_1 | HFF2359 | HFF2359 |  |  |  | Moustafa Mohamed Saleh Saif | 10/20/2025 17:16:45 | 10/21/2025 11:34:13 | 10/21/2025 05:16:45 | Door opening alarm at HFF2359-P2_SRAN @ Sceco | 10/20/2025 17:16:20 | Minor | 65101 | Door opening alarm | 10/20/2025 17:16:16 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2359 | FLM_EM | [8 empty] | API | 10/20/2025 17:16:45 | 10/21/2025 11:34:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251020000915 | PCM-20251020-00001942 | TT-20251020-01932 | EM | Region_1 | DMBQ0073 | DMBQ0073 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/20/2025 17:24:30 | 10/20/2025 17:24:30 | 10/21/2025 05:24:30 | Door opening alarm at DMBQ2M5073-P2 @ Generator_SG | 10/20/2025 17:23:58 | Minor | 65101 | Door opening alarm | 10/20/2025 17:23:56 | P2 | 2G | hafouf | Generator_SG | 2G NSA | DMBQ2M5073 | FLM_EM | [8 empty] | API | 10/20/2025 17:24:30 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000924 | PCM-20251020-00001971 | TT-20251020-01956 | Reference_EM | Region_1 | SMN0795 | SMN0795 |  |  |  | Shaker Saied Mohamed ElShafie | 10/20/2025 17:39:25 | 10/22/2025 09:01:34 | 10/20/2025 23:39:25 | Air condition 1 failure alarm at SMN0795-P1-HUB_SRAN @ Sceco | 10/20/2025 17:28:57 | Major | 65104 | Air condition 1 failure alarm | 10/20/2025 17:28:53 | P1 | SRAN | hafr | Sceco | 2G NSA | SMN0795 | FLM_EM | [8 empty] | API | 10/20/2025 17:39:25 | 10/22/2025 09:01:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020000926 | PCM-20251020-00001974 | TT-20251020-01959 | Reference_EM | Region_1 | HFF2359 | HFF2359 |  |  |  | Moustafa Mohamed Saleh Saif | 10/20/2025 17:40:32 | 10/21/2025 11:34:13 | 10/21/2025 05:40:32 | high temprature 40 at HFF2359-P2_SRAN @ Sceco | 10/20/2025 17:30:00 | Minor | 65103 | high temprature 40 | 10/20/2025 17:29:57 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2359 | FLM_EM | [8 empty] | API | 10/20/2025 17:40:32 | 10/21/2025 11:34:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000935 | PCM-20251020-00001993 | TT-20251020-01972 | EM | Region_1 | KBR0630 | KBR0630 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 10/20/2025 17:45:06 | 10/21/2025 21:15:45 | 10/21/2025 05:45:06 | Door opening alarm at KBR0630-P2_SRAN @ Generator_SG | 10/20/2025 17:44:34 | Minor | 65101 | Door opening alarm | 10/20/2025 17:44:30 | P2 | SRAN | dammam | Generator_SG | 2G NSA | KBR0630 | FLM_EM | [8 empty] | API | 10/20/2025 17:45:06 | 10/20/2025 20:36:20 | 10/21/2025 21:15:31 |  |  | 10/21/2025 21:15:45 |  | Ahmed AbdELmoaz Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000939 | PCM-20251020-00002002 | TT-20251020-01983 | EM | Region_1 | ARR0652 | ARR0652 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Ahmed Goda | 10/20/2025 17:50:46 | 10/20/2025 18:03:05 | 10/20/2025 23:50:46 | Mains Failure at ARR0652-FWA-P1-VIP_SRAN-PC @ Sceco | 10/20/2025 17:40:40 | Major | 65109 | Mains Failure | 10/20/2025 17:40:38 | P3 | SRAN | arar | Sceco | 2G NSA | ARR0652 | FLM_EM | [8 empty] | API | 10/20/2025 17:50:46 | 10/20/2025 18:01:53 | 10/20/2025 18:02:36 | 10/20/2025 18:02:39 | 10/20/2025 18:02:42 | 10/20/2025 18:03:05 |  | Mohamed Ahmed Goda |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000940 | PCM-20251020-00002005 | TT-20251020-01988 | Reference_EM | Region_1 | DMJR0133 | DMJR0133 | Enviroment | Air Condition | Change Fan | Ahmed Bashir Sahib Rahman | 10/20/2025 17:52:50 | 10/22/2025 10:06:34 | 10/21/2025 05:52:50 | Air condition 2 failure alarm at DMJR0133-P3_SRAN @ Sceco | 10/20/2025 17:42:17 | Minor | 65105 | Air condition 2 failure alarm | 10/20/2025 17:42:14 | P3 | SRAN | quriyat | Sceco | 2G NSA | DMJR0133 | FLM_EM | [8 empty] | API | 10/20/2025 17:52:50 | 10/22/2025 10:05:41 | 10/22/2025 10:06:19 |  |  | 10/22/2025 10:06:34 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000944 | PCM-20251020-00002008 | TT-20251020-01991 | Reference_EM | Region_2 | DUB0017 | DUB0017 | Enviroment | Genset failure_Pump | Change Fuel Pump | Fritz Ian Generale | 10/20/2025 17:53:55 | 10/20/2025 19:26:13 | 10/21/2025 05:53:55 | Generator failure at DUB0017-P3-USF_SRAN-PC @ Power Cube | 10/20/2025 17:43:24 | Minor | 65114 | Generator failure | 10/20/2025 17:43:21 | P3 | SRAN | al kharj | Power Cube | 2G NSA | DUB0017 | FLM_EM | [8 empty] | API | 10/20/2025 17:53:55 | 10/20/2025 19:25:38 | 10/20/2025 19:25:49 |  |  | 10/20/2025 19:26:13 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251020000972 | PCM-20251020-00002075 | TT-20251020-02078 | Reference_EM | Region_1 | DAM2487 | DAM2487 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/20/2025 18:43:01 | 10/21/2025 13:03:25 | 10/21/2025 06:43:01 | Air condition 1 failure alarm at DAM2487-P3_SRAN @ Generator_SG | 10/20/2025 18:32:36 | Minor | 65104 | Air condition 1 failure alarm | 10/20/2025 18:32:32 | P3 | SRAN | dammam | Generator_SG | 2G NSA | DAM2487 | FLM_EM | [8 empty] | API | 10/20/2025 18:43:01 | 10/21/2025 13:03:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020000981 | PCM-20251020-00002098 | TT-20251020-02098 | Reference_EM | Region_2 | AFL0018 | AFL0018 | Enviroment | Genset failure_AVR | Change Generator AVR | Fritz Ian Generale | 10/20/2025 18:54:21 | 10/20/2025 20:48:06 | 10/21/2025 06:54:21 | Generator failure at AFL0018-P3-USF_SRAN-PC @ Power Cube | 10/20/2025 18:43:49 | Minor | 65114 | Generator failure | 10/20/2025 18:43:47 | P3 | SRAN | al kharj | Power Cube | 2G NSA | AFL0018 | FLM_EM | [8 empty] | API | 10/20/2025 18:54:21 | 10/20/2025 19:25:39 | 10/20/2025 19:26:24 | 10/20/2025 19:26:26 | 10/20/2025 19:39:08 | 10/20/2025 20:48:06 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020001012 | PCM-20251020-00002147 | TT-20251020-02145 | Reference_EM | Region_1 | NRY0579 | NRY0579 |  |  |  | Muhammed Asif Riaz Riaz Hussain Akhgar | 10/20/2025 19:26:21 | 10/21/2025 14:49:34 | 10/21/2025 07:26:21 | Low battery voltage at NRY0579-P2-USF_SRAN-PC @ Power Cube | 10/20/2025 19:16:01 | Minor | 65110 | Low battery voltage | 10/20/2025 19:15:55 | P2 | SRAN | dammam | Power Cube | 2G NSA | NRY0579 | FLM_EM | [8 empty] | API | 10/20/2025 19:26:21 | 10/21/2025 14:49:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251020001052 | PCM-20251020-00002237 | TT-20251020-02236 | EM | Region_1 | DAM0643 | DAM0643 | Enviroment | Fire Alarm | Reset Fire Pannel | Ibrahim said mohamed Elmarhoumy | 10/20/2025 20:29:56 | 10/20/2025 21:51:16 | 10/21/2025 08:29:56 | Door opening alarm at DAM0643-P2_SRAN @ Sceco | 10/20/2025 20:29:24 | Minor | 65101 | Door opening alarm | 10/20/2025 20:29:21 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0643 | FLM_EM | [8 empty] | API | 10/20/2025 20:29:56 |  | 10/20/2025 21:38:17 | 10/20/2025 21:38:24 | 10/20/2025 21:38:26 | 10/20/2025 21:51:16 |  | Ibrahim said mohamed Elmarhoumy |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020001077 | PCM-20251020-00002307 | TT-20251020-02272 | Telecom | Region_4 | RAB1MN0720 | RAB0720 |  |  |  | Khizer Hayat | 10/20/2025 21:10:36 | 10/20/2025 23:14:04 | 10/21/2025 03:10:36 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB1MN0720-NR2.6-P2 @ Sceco | 10/20/2025 20:57:18 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:57:15 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | RAB1MN0720 | FLM_TE |  |  | PCM-20251020-00002285 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 21:10:36 | 10/20/2025 23:14:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001081 | PCM-20251020-00002313 | TT-20251020-02299 | Telecom | Region_1 | JDNR2M3776 | JDNR0776 |  |  |  | Rafiq Ahmed Elturifi | 10/20/2025 21:16:31 | 10/21/2025 09:35:43 | 10/21/2025 01:16:31 | 1(3G) sites down under JDNR0776-P1-HUB/JB1RNCH01 @ Generator_SG | 10/20/2025 21:08:27 | Critical | 22214 | NodeB Unavailable | 10/20/2025 21:08:23 | P1 | 3G | jubail | Generator_SG | 3G SA | JDNR0776-P1-HUB | FLM_TE | JDNR0776 | Results: DOWN SITE HUB JDNR0776-P1-HUB JDNR0776 Summary: Hub: JDNR0776, Down Count: 1, Down Sites: JDNR0776-P1-HUB Alarm Summary: JDNR0776 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 21:16:31 | 10/21/2025 09:35:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001084 | PCM-20251020-00002320 | TT-20251020-02317 | Telecom | Region_2 | RY1 | RY1 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Junaid Riaz Arbab Khan | 10/20/2025 21:22:47 | 10/21/2025 07:42:20 | 10/21/2025 03:22:47 | Observing Link Down flapped and restored on RYD1_vMSE_RN06_NEW_EOR connected to 100GE2/5/0/0 If Alias=To RYD HDTAPSM1 | 10/20/2025 21:18:51 | Major | 5000003 | Link Down | 10/20/2025 21:18:51 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | RY1 | FLM_TE | [5 empty] | Observing Link Down flapped and restored on RYD1_vMSE_RN06_NEW_EOR connected to 100GE2/5/0/0 If Alias=To RYD HDTAPSM1 |  |  | API | 10/20/2025 21:22:47 |  | 10/21/2025 07:41:38 |  |  | 10/21/2025 07:42:20 |  | Junaid Riaz Arbab Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001085 | PCM-20251020-00002322 | TT-20251020-02315 | EM | Region_4 | JED2301 | JED2301 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/20/2025 21:27:01 | 10/21/2025 13:18:01 | 10/21/2025 03:27:01 | 1(2G/5G) sites down under JED2301-P3/JED2301-P3 @ Sceco | 10/20/2025 21:18:35 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 21:18:29 | P3 | 2G | jeddah | Sceco | 2G SA | JED2301-P3 | FLM_TE | JED2301 | Results: DOWN SITE HUB JED2301-P3 JED2301 Summary: Hub: JED2301, Down Count: 1, Down Sites: JED2301-P3 Alarm Summary: JED2301 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 21:27:01 | 10/21/2025 13:18:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001090 | PCM-20251020-00002334 | TT-20251020-02284 | Telecom | Region_4 | RAB0721 | RAB0721 |  |  |  | Khizer Hayat | 10/20/2025 21:32:38 | 10/20/2025 23:14:10 | 10/21/2025 09:32:38 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB0721-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/20/2025 21:01:27 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 21:01:15 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | RAB0721 | FLM_TE |  |  | PCM-20251020-00002293 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 21:32:38 | 10/20/2025 23:14:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001095 | PCM-20251020-00002340 | TT-20251020-02290 | Telecom | Region_4 | RAB1MN2123 | RAB2123 |  |  |  | Khizer Hayat | 10/20/2025 21:35:20 | 10/20/2025 23:14:12 | 10/21/2025 03:35:20 | BASE STATION SERVICE PROBLEM (Antenna calibration error caused by reception path (Rx) failure) at RAB1MN2123-NR2.6-P3 @ Sceco | 10/20/2025 21:01:41 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 21:01:35 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | RAB1MN2123 | FLM_TE |  |  | PCM-20251020-00002298 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/20/2025 21:35:20 | 10/20/2025 23:14:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001103 | PCM-20251020-00002350 | TT-20251020-02331 | Telecom | Region_6 | NMR0133 | NMR0133 |  |  |  | Manzoor Ahmed | 10/20/2025 21:41:30 | 10/20/2025 23:46:36 | 10/21/2025 01:41:30 | PORT_MODULE_OFFLINE at NMR0133_OCS @ Sceco | 10/20/2025 16:43:03 | Critical | 1-63629 | PORT_MODULE_OFFLINE | 10/20/2025 16:42:50 | P2 | 2G | makhwa | Sceco | DWDM NSA | NMR0133 | FLM_TE | [5 empty] | 0-TO BLJ0046(1-A)-7-T1SCC-2(RM2/TM2)-OCH:1 |  |  | API | 10/20/2025 21:41:30 | 10/20/2025 23:46:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001104 | PCM-20251020-00002351 | TT-20251020-02332 | Telecom | Region_6 | NMR0133 | NMR0133 |  |  |  | Manzoor Ahmed | 10/20/2025 21:41:30 | 10/20/2025 23:46:37 | 10/21/2025 01:41:30 | PORT_MODULE_OFFLINE at NMR0133_ELC @ Sceco | 10/20/2025 16:43:46 | Critical | 1-63629 | PORT_MODULE_OFFLINE | 10/20/2025 16:43:36 | P2 | 2G | makhwa | Sceco | DWDM NSA | NMR0133 | FLM_TE | [5 empty] | 0-ELC(1-B)-8-T1SCC-1(RM1/TM1)-OCH:1 |  |  | API | 10/20/2025 21:41:30 | 10/20/2025 23:46:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001109 | PCM-20251020-00002364 | TT-20251020-02342 | EM | Region_6 | DRB0404 | DRB0404 |  |  |  | Aziz Ul Haq Umar Gul | 10/20/2025 21:57:00 | 10/20/2025 21:59:52 | 10/21/2025 09:57:00 | SHELTER DOOR OPEN at DRB0404-GSM-P2 @ Sceco | 10/20/2025 21:56:21 | Minor | 7103 | SHELTER DOOR OPEN | 10/20/2025 21:56:10 | P2 | 2G | derb | Sceco | 2G NSA | DRB0404 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/20/2025 21:57:00 | 10/20/2025 21:59:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001112 | PCM-20251020-00002367 | TT-20251020-02341 | Telecom | Region_4 | MKSH1M3170 | MKSH0170 |  |  |  | Riasat Ali Allah Baksh | 10/20/2025 22:01:32 | 10/22/2025 13:09:19 | 10/21/2025 04:01:32 | 1(3G) sites down under MKSH0170-P2-USF/MKSH1M3170-P2-USF @ Generator_SG | 10/20/2025 21:53:49 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/20/2025 21:53:09 | P2 | 3G | makkah | Generator_SG | 3G SA | MKSH0170-P2-USF | FLM_TE | MKSH0170 | Results: DOWN SITE HUB MKSH0170-P2-USF MKSH0170 Summary: Hub: MKSH0170, Down Count: 1, Down Sites: MKSH0170-P2-USF Alarm Summary: MKSH0170 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 22:01:32 | 10/22/2025 13:09:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001113 | PCM-20251020-00002368 | TT-20251020-02347 | Reference_telecom | Region_4 | JED6008 | JED6008 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/20/2025 22:03:41 | 10/21/2025 18:09:46 | 10/21/2025 10:03:41 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6008-DCU-P3 @ Sceco | 10/20/2025 19:03:40 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/20/2025 19:03:36 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/20/2025 22:03:41 | 10/21/2025 10:49:23 | 10/21/2025 18:09:37 |  |  | 10/21/2025 18:09:46 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251020001114 | PCM-20251020-00002369 | TT-20251020-02349 | Telecom | [7 empty] | 10/20/2025 22:05:44 | 10/20/2025 22:05:44 | 10/21/2025 04:05:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6006-G9-L18-L21-NR3.5-SBTS-MMM @ Sceco | 10/20/2025 22:04:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 22:04:32 | P3 | 2G |  | Sceco | 5G_Cell SA | JED6006 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 22:05:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001116 | PCM-20251020-00002372 | TT-20251020-02348 | EM | Region_1 | KKM2M2168 | KKM2168 | Enviroment | SCECO_Failure | SCECO auto restored | Reda Mohammed Mohamed Hassanein | 10/20/2025 22:09:34 | 10/22/2025 19:26:59 | 10/21/2025 04:09:34 | 1(2G/3G/LTE) sites down under KKM2168-P3/HB1BSCH01 @ Sceco | 10/20/2025 22:02:39 | Major | 21825 | CSL Fault | 10/20/2025 22:02:37 | P3 | 2G | hafr | Sceco | 2G_3G_LTE SA | KKM2168-P3 | FLM_EM | KKM2168 | Results: DOWN SITE HUB KKM2168-P3 KKM2168 Summary: Hub: KKM2168, Down Count: 1, Down Sites: KKM2168-P3 Alarm Summary: KKM2168 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/20/2025 22:09:34 | 10/21/2025 06:04:42 | 10/22/2025 19:26:50 |  |  | 10/22/2025 19:26:59 |  | Reda Mohammed Mohamed Hassanein |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251020001117 | PCM-20251020-00002373 | TT-20251020-02333 | Telecom | Region_4 | JED1M7129 | JED0129 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/20/2025 22:09:49 | 10/20/2025 22:09:49 | 10/21/2025 04:09:49 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7129-CA-L900-L800-SBTS @ Sceco | 10/20/2025 21:37:33 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 21:37:23 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7129 | FLM_TE |  |  | PCM-20251020-00002353 | Please check RSSI at the site | Please check RSSI at the site |  |  |  | API | 10/20/2025 22:09:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001119 | PCM-20251020-00002377 | TT-20251020-02356 | Reference_telecom | Region_1 | TRF2M8507 | TRF2507 |  |  |  | Muhammad Zubair Guilzar | 10/20/2025 22:14:53 | 10/21/2025 01:15:19 | 10/21/2025 10:14:53 | Cell RX Channel Interference Noise Power Unbalanced at TRF2M8507-P2-L800 @ Generator_SG | 10/20/2025 19:12:21 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/20/2025 19:12:15 | P2 | 4G | arar | Generator_SG | 2G NSA | TRF2M8507 | FLM_TE |  |  | PCM-20251020-00002375 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/20/2025 22:14:53 | 10/21/2025 01:15:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001126 | PCM-20251020-00002391 | TT-20251020-02375 | Reference_telecom | Region_2 | RYAB0605 | RYAB0605 | Transsmission | MW_Waveguide | Replace Waveguide | Hakim Ullah Raif Ullah Jan | 10/20/2025 22:29:00 | 10/23/2025 15:12:20 | 10/21/2025 10:29:00 | MW_LOF at RYAB0605_NE_1 @ Generator_SG | 10/20/2025 18:28:36 | Minor | 1-631 | MW_LOF | 10/20/2025 18:28:25 | P3 | SRAN | al kharj | Generator_SG | TX NSA | RYAB0605 | FLM_TE | [8 empty] | API | 10/20/2025 22:29:00 | 10/21/2025 08:32:43 | 10/23/2025 15:11:23 | 10/23/2025 15:11:25 |  | 10/23/2025 15:12:20 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001125 | PCM-20251020-00002390 | TT-20251020-02374 | Reference_telecom | Region_2 | RYAB0604 | RYAB0604 | Transsmission | MW_Waveguide | Replace Waveguide | Hakim Ullah Raif Ullah Jan | 10/20/2025 22:29:00 | 10/23/2025 15:11:16 | 10/21/2025 10:29:00 | MW_LOF at RYAB0604_NE_1 @ Sceco | 10/20/2025 18:28:36 | Minor | 1-631 | MW_LOF | 10/20/2025 18:28:26 | P3 | SRAN | al kharj | Sceco | TX NSA | RYAB0604 | FLM_TE | [8 empty] | API | 10/20/2025 22:29:00 | 10/23/2025 11:41:16 | 10/23/2025 13:19:06 | 10/23/2025 13:19:22 | 10/23/2025 14:27:17 | 10/23/2025 15:11:16 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001129 | PCM-20251020-00002406 | TT-20251013-02053 | MW_HC | Region_4 | JED0980 | JED0980 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 22:42:47 | 10/20/2025 22:42:47 | 10/21/2025 10:42:47 | Nokia MW HC_P1 Observing Performance Issue at JED0980 _01-JED0198-8 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | jeddah | Sceco | TX NSA | JED0980 _01-JED0198-8 | FLM_TE |  |  | PCM-20251020-00002396 | No attachment found | No attachment found |  |  |  | API | 10/20/2025 22:42:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001135 | PCM-20251020-00002413 | TT-20251020-02394 | Telecom | Region_4 | JED1MN0755 | JED0755 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/20/2025 22:55:52 | 10/20/2025 22:55:52 | 10/21/2025 02:55:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0755-NR2.6-P1-VIP @ Generator_SG | 10/20/2025 22:55:15 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 22:55:10 | VIP | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN0755 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 22:55:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001140 | PCM-20251020-00002424 | TT-20251020-02399 | Telecom | Region_4 | JED0991 | JED0991 |  |  |  | BARKAT ALI MAIN HILAL | 10/20/2025 23:06:01 | 10/21/2025 10:51:38 | 10/21/2025 03:06:01 | 1(2G) sites down under JED0991-FWA-P1-VIP/JED0991-FWA-P1-VIP @ Sceco | 10/20/2025 22:57:30 | Critical | 7706 | BTS O&M LINK FAILURE | 10/20/2025 22:57:26 | P3 | 2G | jeddah | Sceco | 2G SA | JED0991-FWA-P1-VIP | FLM_TE | JED0991 | Results: DOWN SITE HUB JED0991-FWA-P1-VIP JED0991 Summary: Hub: JED0991, Down Count: 1, Down Sites: JED0991-FWA-P1-VIP Alarm Summary: JED0991 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 23:06:01 | 10/21/2025 10:51:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001141 | PCM-20251020-00002426 | TT-20251020-02402 | Reference_telecom | Region_1 | DMJR2266 | DMJR2266 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/20/2025 23:06:11 | 10/20/2025 23:13:44 | 10/21/2025 11:06:11 | RF Unit RX Channel RTWP/RSSI Unbalanced at DMJR2266-P3-USF_SRAN @ Sceco | 10/20/2025 20:05:48 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/20/2025 20:05:42 | P3 | SRAN | hafr | Sceco | 2G NSA | DMJR2266 | FLM_TE | [8 empty] | API | 10/20/2025 23:06:11 | 10/20/2025 23:13:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001142 | PCM-20251020-00002427 | TT-20251020-02405 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/20/2025 23:07:44 | 10/21/2025 09:04:30 | 10/21/2025 05:07:44 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/20/2025 20:06:17 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/20/2025 20:07:24 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/20/2025 23:07:44 | 10/21/2025 09:04:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251020001143 | PCM-20251020-00002434 | TT-20251020-02404 | Telecom | Region_5 | SHD1M3142 | SHD0142 |  |  |  | Hazem Ali Moustafa Ali | 10/20/2025 23:12:31 | 10/20/2025 23:12:31 | 10/21/2025 05:12:31 | 1(3G) sites down under SHD0142-P2-USF/SHD1M3142-P2-USF @ Generator_SG | 10/20/2025 23:04:50 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/20/2025 23:04:10 | P2 | 3G | makkah | Generator_SG | 3G SA | SHD0142-P2-USF | FLM_TE | SHD0142 | Results: DOWN SITE HUB SHD0142-P2-USF SHD0142 Summary: Hub: SHD0142, Down Count: 1, Down Sites: SHD0142-P2-USF Alarm Summary: SHD0142 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 23:12:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001145 | PCM-20251020-00002438 | TT-20251020-02412 | Telecom | Region_4 | JED1M7188 | JED0188 | Equipment | Power Cable_RRU_BTS | Change Port on FPFH | MALIK ATIF ZAMAN | 10/20/2025 23:20:38 | 10/22/2025 15:29:25 | 10/21/2025 05:20:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7188-P3-CA-L900-L800-SBTS @ Sceco | 10/20/2025 23:19:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 23:19:39 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7188 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/20/2025 23:20:38 | 10/21/2025 18:52:48 | 10/21/2025 19:07:45 | 10/21/2025 19:07:55 | 10/21/2025 19:08:04 | 10/22/2025 15:29:25 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001146 | PCM-20251020-00002441 | TT-20251020-02352 | Telecom | Region_4 | JED1M7491 | JED0491 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/20/2025 23:22:58 | 10/21/2025 11:50:38 | 10/21/2025 11:22:58 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7491-G9-L18-SBTS-P2 @ Generator_SG | 10/20/2025 22:02:27 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 22:02:22 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | JED1M7491 | FLM_TE |  |  | PCM-20251020-00002371 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:22:58 | 10/21/2025 11:49:38 | 10/21/2025 11:50:32 |  |  | 10/21/2025 11:50:38 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001147 | PCM-20251020-00002442 | TT-20251020-02362 | Telecom | Region_4 | JDRS1M7760 | JDRS0760 |  |  |  | Khizer Hayat | 10/20/2025 23:23:03 | 10/21/2025 14:05:38 | 10/21/2025 11:23:03 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDRS1M7760-G9-L8-SBTS-P2-USF @ Sceco | 10/20/2025 22:15:55 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 22:15:47 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JDRS1M7760 | FLM_TE |  |  | PCM-20251020-00002382 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:23:03 | 10/21/2025 14:05:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001148 | PCM-20251020-00002443 | TT-20251020-02365 | Telecom | Region_4 | JED1U6052 | JED6152 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/20/2025 23:23:09 | 10/21/2025 18:08:58 | 10/21/2025 05:23:09 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/20/2025 22:15:15 | Major | 7654 | CELL OPERATION DEGRADED | 10/20/2025 22:15:09 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251020-00002384 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:23:09 | 10/21/2025 10:49:24 | 10/21/2025 18:08:52 |  |  | 10/21/2025 18:08:58 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001151 | PCM-20251020-00002446 | TT-20251020-02397 | Telecom | Region_5 | MAK1U6909 | MAK6009 |  |  |  | Mosab Nasr eldeen Mohamed | 10/20/2025 23:23:36 | 10/21/2025 21:37:02 | 10/21/2025 05:23:36 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RRC Connection Setup Attempts) at MAK1U6909-CA-P1-HRM-SBTS @ Sceco | 10/20/2025 22:51:57 | Major | 7654 | CELL OPERATION DEGRADED | 10/20/2025 22:51:50 | P1 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6909 | FLM_TE |  |  | PCM-20251020-00002420 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:23:36 | 10/21/2025 21:37:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001153 | PCM-20251020-00002449 | TT-20251020-02376 | Reference_telecom | Region_4 | TAF1M3139 | TAF0139 | Equipment | BSS_HW_Stuck | Reset System Module | Ahmad Kamal Abdelmawla | 10/20/2025 23:23:50 | 10/21/2025 10:07:29 | 10/21/2025 05:23:50 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TAF1M3139-P2 @ Sceco | 10/20/2025 22:01:33 | Major | 7771 | WCDMA CELL OUT OF USE | 10/20/2025 21:59:24 | P2 | 3G | taif | Sceco | 3G SA | TAF1M3139 | FLM_TE |  |  | PCM-20251020-00002392 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:23:50 | 10/20/2025 23:38:47 | 10/21/2025 10:07:17 |  |  | 10/21/2025 10:07:29 |  | Ahmad Kamal Abdelmawla |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001158 | PCM-20251020-00002459 | TT-20251020-02414 | Telecom | Region_4 | JED0864 | JED0864 |  |  |  | MALIK ATIF ZAMAN | 10/20/2025 23:28:41 | 10/21/2025 18:52:49 | 10/21/2025 11:28:41 | BASE STATION SERVICE PROBLEM (RF Module filter input power missing) at JED0864-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/20/2025 23:17:00 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 23:16:49 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0864 | FLM_TE |  |  | PCM-20251020-00002440 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:28:41 | 10/21/2025 18:52:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001159 | PCM-20251020-00002460 | TT-20251020-02413 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 23:28:50 | 10/21/2025 11:05:56 | 10/21/2025 05:28:50 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at TURY0826-GSM-P2 @ Sceco | 10/20/2025 23:16:06 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 23:15:55 | P2 | 2G | taif | Sceco | 5G_Cell SA | TURY0826 | FLM_TE |  |  | PCM-20251020-00002439 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:28:50 | 10/21/2025 11:05:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001162 | PCM-20251020-00002472 | TT-20251020-02436 | Telecom | Region_2 | RIY0340 | RIY0340 |  |  |  | Farmanullah Akbar Jan | 10/20/2025 23:35:30 | 10/21/2025 07:48:44 | 10/21/2025 11:35:30 | As per visibility report ,NCE MW Observing Visibility Down at 6 NEs under RIY0340 Subnet RIY0340-FON | 10/20/2025 23:33:57 | Minor | 2 | NE_NOT_LOGIN | 10/20/2025 23:33:57 | VIP | SRAN | riyadh | Sceco | TX NSA | RIY0224_NE_1_V RIY0224_NE_2_H RIY0224_NE_3 RIY0340_NE_5_V RIY0340_NE_6_H RIY0363_NE_5_H | FLM_TE | [5 empty] | As per visibility report ,NCE MW Observing Visibility Down at 6 NEs under RIY0340 Subnet RIY0340-FON |  |  | API | 10/20/2025 23:35:30 | 10/21/2025 07:48:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001164 | PCM-20251020-00002474 | TT-20251020-02433 | Reference_telecom | Region_4 | TAF1M3277 | TAF0277 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/20/2025 23:37:46 | 10/21/2025 11:05:56 | 10/21/2025 05:37:46 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at TAF1M3277-P2 @ Sceco | 10/20/2025 23:04:45 | Major | 7771 | WCDMA CELL OUT OF USE | 10/20/2025 23:02:35 | P2 | 3G | taif | Sceco | 3G SA | TAF1M3277 | FLM_TE |  |  | PCM-20251020-00002470 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:37:46 | 10/21/2025 11:05:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001165 | PCM-20251020-00002475 | TT-20251020-02427 | Telecom | Region_4 | JED0310 | JED0310 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 23:37:58 | 10/23/2025 09:13:35 | 10/21/2025 11:37:58 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at JED0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Generator_SG | 10/20/2025 23:25:21 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 23:25:14 | VIP | 2G | jeddah | Generator_SG | LTE NSA | JED0310 | FLM_TE |  |  | PCM-20251020-00002463 | kindly check and confirm no dust or air blockage | kindly check and confirm no dust or air blockage |  |  |  | API | 10/20/2025 23:37:58 | 10/21/2025 05:56:19 | 10/23/2025 09:13:25 |  |  | 10/23/2025 09:13:35 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001169 | PCM-20251020-00002481 | TT-20251020-02440 | Telecom | Region_4 | JED0155 | JED0155 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/20/2025 23:42:52 | 10/23/2025 09:13:57 | 10/21/2025 05:42:52 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED0155-G9-L8-L18-L21-NNR6-NR2.6-NR3.5-SBTS-P1-VVIP-HUB-WDM-FON @ Sceco | 10/20/2025 23:35:47 | Major | 7114 | CELL SERVICE PROBLEM | 10/20/2025 23:35:39 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0155 | FLM_TE |  |  | PCM-20251020-00002478 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/20/2025 23:42:52 | 10/21/2025 05:56:20 | 10/23/2025 09:13:46 |  |  | 10/23/2025 09:13:57 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001170 | PCM-20251020-00002483 | TT-20251020-02441 | Reference_EM | Region_2 | RIYB6108 | RIYB6108 | Transsmission | SFP_Transmission | Replace SFP | Muhammad Waqas Ashraf Muhammad Ashraf | 10/20/2025 23:45:17 | 10/21/2025 18:01:46 | 10/21/2025 05:45:17 | 1(2G/LTE) Site down at RIYB6108-P3 (REF::TT-20251020-02373) | 10/20/2025 22:25:29 | Major | 21825 | CSL Fault | 10/20/2025 22:25:29 | P3 | SRAN | riyadh | Sceco | 2G_LTE SA | RIYB6108 | FLM_EM | RIYB6108 | Results: DOWN SITE HUB RIYB6108 RIYB6108 Summary: Hub: RIYB6108, Down Count: 1, Down Sites: RIYB6108 Alarm Summary: RIYB6108 No Active Alarm on HUB |  |  |  |  | site down |  | API | 10/20/2025 23:45:17 | 10/21/2025 17:26:48 | 10/21/2025 17:27:12 | 10/21/2025 17:27:27 | 10/21/2025 17:35:58 | 10/21/2025 18:01:46 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251020001172 | PCM-20251020-00002485 | TT-20251020-02295 | Telecom | Region_1 | JDNR2704 | JDNR2704 |  |  |  | Tahir Mahmood Hafiz Yar | 10/20/2025 23:48:25 | 10/21/2025 05:13:08 | 10/21/2025 05:48:25 | 1(2G) sites down under JDNR2704-P3/R1_DM_HWBSC01 @ Sceco | 10/20/2025 21:04:11 | Major | 21807 | OML Fault | 10/20/2025 21:04:03 | P3 | SRAN | jubail | Sceco | 2G SA | JDNR2704-P3 | FLM_TE | JDNR2704 | Dear FLM, We are observing Frame ID ,LOF alarms active at hub site JDNR2704 slot 11 , 12 | PCM-20251020-00002421 | Dear FLM, We are observing Frame ID ,LOF alarms active at hub site JDNR2704 slot 11 , 12 | Dear FLM, We are observing Frame ID ,LOF alarms active at hub site JDNR2704 slot 11 , 12 |  | sites down |  | API | 10/20/2025 23:48:25 | 10/21/2025 05:13:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251020001173 | PCM-20251020-00002487 | TT-20251020-02449 | EM | Region_6 | UKHA2360 | UKHA2360 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/20/2025 23:55:04 | 10/23/2025 13:14:39 | 10/21/2025 05:55:04 | 3(2G) 3(LTE) sites down under UKHA2363-P3,UKHA2371-P3,UKHA2360-P3/UKHA2360-P3 @ Generator_DG | 10/20/2025 23:46:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/20/2025 23:46:51 | P3 | 2G | Baha | Generator_DG | 2G_LTE SA | UKHA2360-P3 | FLM_EM | UKHA2360 | Results: DOWN SITE HUB UKHA2360-P3 UKHA2360 Summary: Hub: UKHA2360, Down Count: 1, Down Sites: UKHA2360-P3 Alarm Summary: UKHA2360 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/20/2025 23:55:04 | 10/21/2025 08:19:54 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001174 | PCM-20251020-00002489 | TT-20251020-02454 | Reference_telecom | Region_6 | AQQ2431 | AQQ2431 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Manzoor Ahmed | 10/20/2025 23:57:50 | 10/23/2025 23:05:39 | 10/21/2025 11:57:50 | Degrade observed in AQQ2431_02 towards 10.221.247.71 @ Generator_SG | 10/20/2025 11:57:48 | Minor |  | Degrade | 10/20/2025 11:57:44 | P3 | 2G | Baha | Generator_SG | TX NSA | AQQ2431 | FLM_TE | [8 empty] | API | 10/20/2025 23:57:50 | 10/21/2025 14:54:33 | 10/23/2025 23:05:21 |  |  | 10/23/2025 23:05:39 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000004 | PCM-20251021-00000005 | TT-20251021-00004 | Telecom | Region_1 | HFR2U6102 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/21/2025 00:01:41 | 10/21/2025 01:10:53 | 10/21/2025 06:01:41 | GSM Local Cell Unusable at HFR2U6102-P3 @ Sceco | 10/20/2025 23:54:56 | Major | 28016 | GSM Local Cell Unusable | 10/20/2025 23:53:52 | P3 | 2G | hafr | Sceco | 2G SA | HFR2U6102 | FLM_TE | [8 empty] | API | 10/21/2025 00:01:41 | 10/21/2025 01:10:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000007 | PCM-20251021-00000019 | TT-20251021-00017 | Telecom | Region_4 | JED1M8178 | JED2178 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 00:11:16 | 10/21/2025 00:11:16 | 10/21/2025 06:11:16 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8178-P3-CA-L800 @ Sceco | 10/21/2025 00:10:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 00:10:23 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8178 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 00:11:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000008 | PCM-20251021-00000020 | TT-20251015-00527 | Telecom | Region_4 | JED0151(JD1) | JED0151 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 00:12:07 | 10/21/2025 00:12:07 | 10/21/2025 06:12:07 | REMOTE_FAULT alarm at JED0151 (JD1) NCE | 10/15/2025 06:33:59 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/15/2025 06:33:59 | P1 | DWDM | jeddah | Sceco_STB_Rental | DWDM NSA | JED0151 (JD1 | FLM_TE |  |  | PCM-20251020-00002269 | Follow up with FO to check the cause and fix it | Follow up with FO to check the cause and fix it |  |  |  | API | 10/21/2025 00:12:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000009 | PCM-20251021-00000022 | TT-20251001-01156 | Telecom | Region_6 | MUHAYIL-SEC0048_ELC | SEC0048 |  |  |  | Aftab Ali | 10/21/2025 00:15:45 | 10/21/2025 00:15:45 | 10/21/2025 06:15:45 | IN_PWR_LOW ALARM AT MUHAYIL-SEC0048 | 10/01/2025 12:54:22 | Major | 1.3.6.1.4.1.7483.2.1.2.2.2.2.1.0.51 | LOS | 10/01/2025 12:54:22 | P1 | DWDM | abha | Sceco_STB | DWDM NSA | MUHAYIL-SEC0048 | FLM_TE |  |  | PCM-20251020-00002268 | Check the corresponding port with FO and apply RFC to troubleshoot link after collecting impact | Check the corresponding port with FO and apply RFC to troubleshoot link after collecting impact |  |  |  | API | 10/21/2025 00:15:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000010 | PCM-20251021-00000023 | TT-20251014-00549 | Telecom | Region_5 | MAK0118(MK1) | MAK0118 |  |  |  | Muhammad Zubair | 10/21/2025 00:16:51 | 10/21/2025 00:16:51 | 10/21/2025 06:16:51 | RMON_ALM_INBADOCTS_OVER ALARMS AT MK1,MK4,HM1,HA1 | 10/14/2025 06:16:44 | Major | 1.3.6.1.4.1.1751.1.102.200.11.1004.59 | LOS-P | 10/14/2025 06:16:44 | P1 | DWDM | makkah | Sceco_STB_Rental | DWDM NSA | MAK0118(MK1) | FLM_TE |  |  | PCM-20251020-00002083 | Check the corresponding issue in OSP during timestamp with FO and close TT | Check the corresponding issue in OSP during timestamp with FO and close TT |  |  |  | API | 10/21/2025 00:16:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000011 | PCM-20251021-00000027 | TT-20251021-00027 | EM | Region_3 | HL1 | HL1 |  |  |  | Mohamed Yasser Zakir Mohamed | 10/21/2025 00:19:02 | 10/21/2025 00:19:02 | 10/21/2025 04:19:02 | Door opening alarm BSC New shelter at HL1-Shelter 3-WDM-Core-P1 @ Sceco_STB | 10/21/2025 00:18:48 | Critical | 65134 | Door opening alarm BSC New shelter | 10/21/2025 00:18:43 | P1 | BSC | hail | Sceco_STB | 2G NSA | HL1 | FLM_EM | [8 empty] | API | 10/21/2025 00:19:02 | [10 empty] | EM | Zain |  | Running |  | OWS
Departed | CM20251021000015 | PCM-20251021-00000034 | TT-20251013-02042 | MW_HC | Region_6 | KMS0588 | KMS0588 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/21/2025 00:28:48 | 10/21/2025 15:03:54 | 10/21/2025 12:28:48 | Nokia MW HC_P1 Observing Performance Issue at KMS0588_01-KMS0464-3 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0588_01-KMS0464-3 | FLM_TE |  |  | PCM-20251020-00002435 | Pls share RCA with evidence snap | Pls share RCA with evidence snap |  |  |  | API | 10/21/2025 00:28:48 | 10/21/2025 05:02:06 | 10/21/2025 15:03:51 | 10/21/2025 15:03:54 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000018 | PCM-20251021-00000046 | TT-20251020-01594 | Reference_telecom | Region_6 | ABH0119 | ABH0119 | Transsmission | MW_HW_fault | Replace ODU | Amir Sohail | 10/21/2025 00:39:43 | 10/21/2025 10:35:18 | 10/21/2025 12:39:43 | Nokia Eband Observing DialogFailure-Port 7/3,LossOfSignal-Port 7/3,Bandw at ABH0119-10.10.155.45 | 10/19/2025 16:21:15 | Minor |  | LOF | 10/19/2025 16:21:15 | P2 | 2G | abha | Sceco | TX NSA | ABH0119-10.10.155.45 | FLM_TE |  |  | PCM-20251020-00002428 | Approved | Approved |  |  |  | API | 10/21/2025 00:39:43 | 10/21/2025 01:04:06 | 10/21/2025 10:35:02 |  |  | 10/21/2025 10:35:18 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000021 | PCM-20251021-00000049 | TT-20251021-00065 | Telecom | Region_1 | DAM2178 | DAM2178 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/21/2025 00:43:18 | 10/21/2025 09:07:16 | 10/21/2025 12:43:18 | RF Unit Maintenance Link Failure at DAM2178-P2_SRAN @ Sceco | 10/21/2025 00:39:42 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 00:37:58 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2178 | FLM_TE | [8 empty] | API | 10/21/2025 00:43:18 | 10/21/2025 09:07:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000025 | PCM-20251021-00000062 | TT-20251020-02439 | Telecom | Region_3 | TBK2692 | TBK2692 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Tahir Abbas Fateh Khan | 10/21/2025 00:49:32 | 10/21/2025 01:12:31 | 10/21/2025 06:49:32 | NR Cell Unavailable at TBK2692-P1-HUB_SRAN @ Sceco | 10/20/2025 23:32:00 | Major | 29841 | NR Cell Unavailable | 10/20/2025 23:30:26 | P1 | SRAN | tabouk | Sceco | 5G SA | TBK2692 | FLM_TE |  |  | PCM-20251021-00000060 | check mail | check mail |  |  |  | API | 10/21/2025 00:49:32 | 10/21/2025 00:52:57 | 10/21/2025 00:53:06 | 10/21/2025 00:53:09 | 10/21/2025 00:53:11 | 10/21/2025 01:12:31 |  | Tahir Abbas Fateh Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000027 | PCM-20251021-00000066 | TT-20251021-00079 | Telecom | Region_4 | JED0276 | JED0276 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 00:56:13 | 10/21/2025 00:56:13 | 10/21/2025 06:56:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0276-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB-WDM-FON @ Sceco | 10/21/2025 00:55:36 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 00:55:30 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0276 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 00:56:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000029 | PCM-20251021-00000070 | TT-20251021-00078 | EM | Region_6 | QLW2364 | QLW2364 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 01:00:04 | 10/21/2025 08:19:56 | 10/21/2025 07:00:04 | 1(2G/LTE) sites down under QLW2364-P3/QLW2364-P3 @ Generator_SG | 10/21/2025 00:52:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 00:51:53 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | QLW2364-P3 | FLM_EM | QLW2364 | Results: DOWN SITE HUB QLW2364-P3 QLW2364 Summary: Hub: QLW2364, Down Count: 1, Down Sites: QLW2364-P3 Alarm Summary: QLW2364 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 01:00:04 | 10/21/2025 08:19:56 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000043 | PCM-20251021-00000086 | TT-20251021-00099 | Reference_EM | Region_2 | RIYD6037 | RIYD6037 |  |  |  | Adham Adham Hassan Farghal | 10/21/2025 01:06:33 | 10/21/2025 13:42:33 | 10/21/2025 07:06:33 | Air condition 1 failure alarm at RIYD6037-P1-VIP_SRAN @ Sceco | 10/21/2025 00:56:20 | Major | 65104 | Air condition 1 failure alarm | 10/21/2025 00:56:04 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIYD6037 | FLM_EM | [8 empty] | API | 10/21/2025 01:06:33 | 10/21/2025 13:42:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000050 | PCM-20251021-00000096 | TT-20251021-00103 | Telecom | Region_4 | JED0276 | JED0276 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 01:13:02 | 10/21/2025 06:22:30 | 10/21/2025 05:13:02 | 1(5G) sites down under JED0276-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB-WDM-FON @ Sceco | 10/21/2025 01:04:42 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 01:04:39 | P1 | 2G | jeddah | Sceco | 5G SA | JED0276-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB-WDM-FON | FLM_TE | JED0276 | Results: DOWN SITE HUB JED0276-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB-WDM-FON JED0276 Summary: Hub: JED0276, Down Count: 1, Down Sites: JED0276-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB-WDM-FON Alarm Summary: JED0276 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.16.124:8080] [URL:http://10.96.16.124:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 01:13:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000051 | PCM-20251021-00000097 | TT-20251021-00109 | Reference_telecom | Region_4 | USMD0760 | USMD0760 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 01:14:18 | 10/21/2025 11:05:57 | 10/21/2025 13:14:18 | DemFail observed in USMD0760 towards 10.74.120.114 @ Sceco | 10/20/2025 13:18:02 | Minor |  | DemFail | 10/20/2025 13:13:59 | P2 | 2G | taif | Sceco | TX NSA | USMD0760 | FLM_TE | [8 empty] | API | 10/21/2025 01:14:18 | 10/21/2025 11:05:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000054 | PCM-20251021-00000100 | TT-20251021-00113 | Telecom | Region_4 | JED1MN0957 | JED0957 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 01:16:22 | 10/21/2025 13:18:02 | 10/21/2025 13:16:22 | BASE STATION INFORMATION (No module fan detected) at JED1MN0957-NR2.6-P3 @ Sceco | 10/21/2025 01:07:48 | Minor | 7115 | BASE STATION INFORMATION | 10/21/2025 01:07:59 | P3 | 5G | jeddah | Sceco | 5G NSA | JED1MN0957 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/21/2025 01:16:22 | 10/21/2025 13:18:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000056 | PCM-20251021-00000112 | TT-20251021-00117 | EM | Region_6 | QLW2352 | QLW2352 |  |  |  | Fathy Mohamed | 10/21/2025 01:24:03 | 10/21/2025 20:48:10 | 10/21/2025 07:24:03 | 1(2G/LTE) sites down under QLW2352-P3/QLW2352-P3 @ Generator_SG | 10/21/2025 01:15:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 01:15:53 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | QLW2352-P3 | FLM_EM | QLW2352 | Results: DOWN SITE HUB QLW2352-P3 QLW2352 Summary: Hub: QLW2352, Down Count: 1, Down Sites: QLW2352-P3 Alarm Summary: QLW2352 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 01:24:03 | 10/21/2025 20:48:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000069 | PCM-20251021-00000134 | TT-20251021-00139 | Telecom | Region_2 | SHIR2S5217 | SHIR0217 |  |  |  | Asad Ali Nadiq Khan | 10/21/2025 01:33:01 | 10/21/2025 09:30:21 | 10/21/2025 07:33:01 | 1(3G) sites down under SHIR0217-P3/RY1RNCH05 @ Sceco | 10/21/2025 01:26:58 | Major | 22214 | NodeB Unavailable | 10/21/2025 01:24:33 | P3 | 3G | riyadh | Sceco | 3G SA | SHIR0217-P3 | FLM_TE | SHIR0217 | Results: DOWN SITE HUB SHIR0217-P3 SHIR0217 Summary: Hub: SHIR0217, Down Count: 1, Down Sites: SHIR0217-P3 Alarm Summary: SHIR0217 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 01:33:01 | 10/21/2025 09:30:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000071 | PCM-20251021-00000137 | TT-20251021-00124 | EM | Region_5 | SHD0142 | SHD0142 |  |  |  | Hazem Ali Moustafa Ali | 10/21/2025 01:34:42 | 10/21/2025 01:34:42 | 10/21/2025 13:34:42 | TRX FAULTY (FF FF FF FF FF FF shared:S) at SHD0142-P2-USF @ Generator_SG | 10/21/2025 01:14:12 | Minor | 7606 | TRX FAULTY | 10/21/2025 01:14:09 | P2 | 2G | makkah | Generator_SG | 2G_Cell SA | SHD0142 | FLM_TE |  |  | PCM-20251021-00000106 | No Power Issue | No Power Issue |  |  |  | API | 10/21/2025 01:34:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000074 | PCM-20251021-00000143 | TT-20251021-00016 | Reference_telecom | Region_4 | JED1M7667 | JED0667 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 01:36:29 | 10/21/2025 18:52:49 | 10/21/2025 07:36:29 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1M7667-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/20/2025 20:08:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:08:21 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7667 | FLM_TE |  |  | PCM-20251021-00000016 | Kindly perform HC on site and clean FAN unit and check for any blockage of air | Kindly perform HC on site and clean FAN unit and check for any blockage of air |  |  |  | API | 10/21/2025 01:36:29 | 10/21/2025 18:52:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000075 | PCM-20251021-00000145 | TT-20251021-00060 | Reference_telecom | Region_4 | JED0310 | JED0310 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Ramadan A Abu Abid | 10/21/2025 01:37:09 | 10/23/2025 09:14:14 | 10/21/2025 07:37:09 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP @ Generator_SG | 10/20/2025 20:39:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 20:39:14 | VIP | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0310 | FLM_TE |  |  | PCM-20251021-00000044 | Kindly perform HC on site and clean FAN unit and check for any blockage of air | Kindly perform HC on site and clean FAN unit and check for any blockage of air |  |  |  | API | 10/21/2025 01:37:09 | 10/21/2025 05:56:20 | 10/23/2025 09:14:03 |  |  | 10/23/2025 09:14:14 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000076 | PCM-20251021-00000149 | TT-20251021-00149 | Telecom | Region_2 | RIY0340 | RIY0340 |  |  |  | Farmanullah Akbar Jan | 10/21/2025 01:39:33 | 10/21/2025 07:48:44 | 10/21/2025 13:39:33 | Board Not In Position at RIY0340-P1-SHOP-HUB-VIP_SRAN-FON @ Sceco | 10/21/2025 01:30:24 | Minor | 26204 | Board Not In Position | 10/21/2025 01:28:50 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0340 | FLM_TE |  |  | PCM-20251021-00000142 | Please check | Please check |  |  |  | API | 10/21/2025 01:39:33 | 10/21/2025 07:48:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000077 | PCM-20251021-00000150 | TT-20251021-00154 | EM | Region_1 | Sk1 | SK1 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/21/2025 01:40:08 | 10/21/2025 01:40:08 | 10/21/2025 05:40:08 | Door opening alarm at SK1-Shelter 1-WDM-HUB-Core-P1 @ Sceco_STB | 10/21/2025 01:39:44 | Critical | 65101 | Door opening alarm | 10/21/2025 01:38:48 | P1 | DWDM | sakaka | Sceco_STB | 2G NSA | SK1 | FLM_EM | [8 empty] | API | 10/21/2025 01:40:08 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000078 | PCM-20251021-00000151 | TT-20251021-00150 | EM | Region_6 | RYAB1M3648 | RYAB0648 | Transsmission | MW_HW_stuck | Reset ODU | Umair Abbas Muhammad Abbas | 10/21/2025 01:41:03 | 10/21/2025 19:30:15 | 10/21/2025 05:41:03 | 1(3G/5G) sites down under RYAB0648-P1-HUB-USF/RYAB1M3648-P1-HUB-USF @ Sceco_STB | 10/21/2025 01:33:19 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 01:32:37 | P1 | 3G | turaib | Sceco_STB | 3G_5G SA | RYAB0648-P1-HUB-USF | FLM_EM | RYAB0648 | Results: DOWN SITE HUB RYAB0648-P1-HUB-USF RYAB0648 Summary: Hub: RYAB0648, Down Count: 1, Down Sites: RYAB0648-P1-HUB-USF Alarm Summary: RYAB0648 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 01:41:03 | 10/21/2025 17:18:51 | 10/21/2025 19:29:51 |  |  | 10/21/2025 19:30:15 |  | Umair Abbas Muhammad Abbas |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000091 | PCM-20251021-00000299 | TT-20251021-00319 | Reference_telecom | Region_6 | ABH0289 | ABH0289 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 02:15:29 | 10/21/2025 03:36:47 | 10/21/2025 14:15:29 | FanFailure observed in ABH0289 _02 towards 10.10.154.196 @ Sceco | 10/20/2025 14:15:42 | Minor |  | FanFailure | 10/20/2025 14:14:23 | P3 | 2G | abha | Sceco | TX NSA | ABH0289 | FLM_TE | [8 empty] | API | 10/21/2025 02:15:29 | 10/21/2025 03:36:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000096 | PCM-20251021-00000312 | TT-20251021-00334 | EM | Region_4 | HHR1M7448 | HHR0448 |  |  |  | AbdAllah Mohammad abd Elgawad Fath Elbab | 10/21/2025 02:20:56 | 10/21/2025 11:27:44 | 10/21/2025 08:20:56 | RECTIFIRE MAIN FAILURE at HHR1M7448-P1-VIP-HHR-L800-CA @ Generator_SG | 10/21/2025 02:12:49 | Major | 7103 | RECTIFIRE MAIN FAILURE | 10/21/2025 02:12:39 | VIP | 4G | jeddah | Generator_SG | LTE NSA | HHR1M7448 | FLM_EM | [5 empty] | RECTIFIRE MAIN FAILURE |  |  | API | 10/21/2025 02:20:56 | 10/21/2025 11:27:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000097 | PCM-20251021-00000313 | TT-20251021-00329 | Telecom | Region_5 | MAK1U6934 | MAK6034 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 02:21:42 | 10/21/2025 02:21:42 | 10/21/2025 08:21:42 | CELL OPERATION DEGRADED (VSWR minor alarm) at MAK1U6934-P3-CA @ Sceco | 10/21/2025 02:09:26 | Major | 7654 | CELL OPERATION DEGRADED | 10/21/2025 02:09:16 | P3 | 4G | makkah | Sceco | LTE_Cell SA | MAK1U6934 | FLM_TE |  |  | PCM-20251021-00000308 | Kindly check the VSWR alarm active at site | Kindly check the VSWR alarm active at site |  |  |  | API | 10/21/2025 02:21:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000099 | PCM-20251021-00000316 | TT-20251021-00341 | Reference_telecom | Region_6 | KMS0586 | KMS0586 | Transsmission | MW_HW_stuck | Reset IDU | Ahmed Abdelaziz Hamid Abdelrahman | 10/21/2025 02:24:01 | 10/22/2025 19:36:34 | 10/21/2025 14:24:01 | DialogFailure observed in KMS0586 towards 10.74.123.117 @ Sceco | 10/20/2025 14:25:51 | Minor |  | DialogFailure | 10/20/2025 14:23:49 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0586 | FLM_TE | [8 empty] | API | 10/21/2025 02:24:01 | 10/21/2025 04:31:10 | 10/22/2025 19:36:20 |  |  | 10/22/2025 19:36:34 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000102 | PCM-20251021-00000321 | TT-20251021-00338 | EM | [7 empty] | 10/21/2025 02:27:01 | 10/21/2025 02:27:01 | 10/21/2025 08:27:01 | 1(2G/LTE) sites down under RIYD6026-P3/R2_RY3_HWBSC01 @ Sceco | 10/21/2025 02:18:39 | Major | 21825 | CSL Fault | 10/21/2025 02:18:35 | P3 | 2G |  | Sceco | 2G_LTE SA | RIYD6026-P3 | FLM_EM | RIYD6026 | Results: DOWN SITE HUB RIYD6026-P3 RIYD6026 Summary: Hub: RIYD6026, Down Count: 1, Down Sites: RIYD6026-P3 Alarm Summary: RIYD6026 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 02:27:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000105 | PCM-20251021-00000329 | TT-20251021-00340 | Telecom | Region_3 | YNB0672 | YNB0672 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Muhammad Sajjad R3 | 10/21/2025 02:31:08 | 10/21/2025 12:04:58 | 10/21/2025 06:31:08 | 3(3G) 3(LTE) sites down under YB1MBSCH01 @ Sceco | 10/21/2025 02:21:51 | Critical | 22214 | NodeB Unavailable | 10/21/2025 02:21:44 | P1 | SRAN | yanbu | Sceco | 3G_LTE SA | YNB0664-P2 LTE,YNB2958-P2-L800-CA LTE,YNB0665-P2 LTE,YNB0672-P3 3G,YNB0637-P2 3G | FLM_TE | YNB0672 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00000323 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 02:31:08 | 10/21/2025 07:22:41 | 10/21/2025 12:04:51 |  |  | 10/21/2025 12:04:58 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000107 | PCM-20251021-00000331 | TT-20251021-00355 | EM | Region_4 | JD3_CORE | JD3 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 02:33:21 | 10/22/2025 12:56:01 | 10/21/2025 08:33:21 | DOOR OPEN ALARM EQUIPMENT ROOM at JD3_CORE-P1-VIP @ Sceco_STB | 10/21/2025 02:32:57 | Major | 7103 | DOOR OPEN ALARM EQUIPMENT ROOM | 10/21/2025 02:32:50 | P1 | 4G | jeddah | Sceco_STB | DWDM NSA | JD3_CORE | FLM_EM | [5 empty] | DOOR OPEN ALARM EQUIPMENT ROOM |  |  | API | 10/21/2025 02:33:21 | 10/22/2025 12:56:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000109 | PCM-20251021-00000336 | TT-20251021-00361 | EM | Region_6 | BSH1M7080 | BSH0080 |  |  |  | Fizan Ahmed | 10/21/2025 02:37:28 | 10/21/2025 11:30:04 | 10/21/2025 14:37:28 | AIRCON 2 FAILURE at BSH1M7080-P3-CA-L800 @ Sceco | 10/21/2025 02:29:45 | Minor | 7103 | AIRCON 2 FAILURE | 10/21/2025 02:29:19 | P3 | 4G | baish | Sceco | LTE NSA | BSH1M7080 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/21/2025 02:37:28 | 10/21/2025 11:30:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000111 | PCM-20251021-00000343 | TT-20251021-00368 | Reference_telecom | Region_2 | RIYA6090 | RIYA6090 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/21/2025 02:38:33 | 10/21/2025 11:32:34 | 10/21/2025 08:38:33 | RF Unit VSWR Threshold Crossed at RIYA6090-P2_SRAN @ Sceco | 10/21/2025 00:54:10 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 00:53:20 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYA6090 | FLM_TE | [8 empty] | API | 10/21/2025 02:38:33 | 10/21/2025 11:32:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000112 | PCM-20251021-00000349 | TT-20251021-00374 | Telecom | Region_2 | RIYB6005 | RIYB6005 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/21/2025 02:38:37 | 10/21/2025 11:32:35 | 10/21/2025 08:38:37 | BBU CPRI Interface Error at RIYB6005-P1-SHOP_SRAN @ Sceco | 10/21/2025 00:55:21 | Major | 26234 | BBU CPRI Interface Error | 10/21/2025 00:52:16 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIYB6005 | FLM_TE | [8 empty] | API | 10/21/2025 02:38:37 | 10/21/2025 11:32:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000117 | PCM-20251021-00000364 | TT-20251021-00393 | Reference_telecom | Region_5 | MAK0380 | MAK0380 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 02:48:49 | 10/21/2025 02:48:49 | 10/21/2025 14:48:49 | BatteryFail observed in MAK0380_SH01 towards 10.10.178.243 @ Sceco | 10/20/2025 14:48:38 | Minor |  | BatteryFail | 10/20/2025 14:48:33 | VIP | 2G | makkah | Sceco | TX NSA | MAK0380 | FLM_TE | [8 empty] | API | 10/21/2025 02:48:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000118 | PCM-20251021-00000365 | TT-20251021-00394 | Telecom | Region_1 | DAM2474 | DAM2474 | Equipment | BSS_HW_Stuck | Reset RRU | Shakeel Ahmed Hafeez Ameen | 10/21/2025 02:48:49 | 10/23/2025 17:07:07 | 10/21/2025 14:48:49 | RF Unit Maintenance Link Failure at DAM2474-P1-SHOP_SRAN @ Sceco | 10/21/2025 02:43:49 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 02:43:38 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2474 | FLM_TE | [8 empty] | API | 10/21/2025 02:48:49 | 10/21/2025 09:07:17 | 10/23/2025 17:07:00 |  |  | 10/23/2025 17:07:07 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000120 | PCM-20251021-00000369 | TT-20251021-00061 | Reference_telecom | Region_5 | BIK1M7153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/21/2025 02:53:59 | 10/21/2025 02:53:59 | 10/21/2025 08:53:59 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BIK1M7153-L800-CA-P3 @ Generator_SG | 10/20/2025 22:39:26 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 22:39:20 | P3 | 4G | makkah | Generator_SG | LTE NSA | BIK1M7153 | FLM_TE |  |  | PCM-20251021-00000147 | Dear FLM, Thanks to rectify BIK0153-BIK0788 | Dear FLM, Thanks to rectify BIK0153-BIK0788 |  |  |  | API | 10/21/2025 02:53:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000121 | PCM-20251021-00000378 | TT-20251008-01989 | MW_HC | Region_6 | KMS0586 | KMS0586 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/21/2025 02:57:41 | 10/21/2025 04:31:10 | 10/21/2025 14:57:41 | Nokia MW HC_P0 Observing Performance Issue at KMS0586-KMS0599_01 | 10/08/2025 15:25:25 | Minor |  | LOF | 10/08/2025 15:25:25 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0586-KMS0599_01 | FLM_TE |  | What is type of support needed and support to contact BO by mail or by whats app not by PCM and check old comment check link was flapping and counting error | PCM-20251021-00000220 | PPP Fail on PPP RadioLAG#2 - KMS0586_RL active alarm | PPP Fail on PPP RadioLAG#2 - KMS0586_RL active alarm |  |  |  | API | 10/21/2025 02:57:41 | 10/21/2025 04:31:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000122 | PCM-20251021-00000381 | TT-20251021-00411 | EM | Region_6 | TBL1M7451 | TBL0451 |  |  |  | Asad Saddiq | 10/21/2025 02:59:40 | 10/21/2025 08:55:42 | 10/21/2025 14:59:40 | AC1 FAILURE at TBL1M7451-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/21/2025 02:51:22 | Minor | 7103 | AC1 FAILURE | 10/21/2025 02:51:13 | P3 | 4G | bisha | Sceco | LTE NSA | TBL1M7451 | FLM_EM | [5 empty] | AC1 FAILURE |  |  | API | 10/21/2025 02:59:40 | 10/21/2025 08:55:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000124 | PCM-20251021-00000383 | TT-20251021-00412 | EM | Region_6 | BSA0219 | BSA0219 |  |  |  | Asad Saddiq | 10/21/2025 03:00:42 | 10/21/2025 08:55:44 | 10/21/2025 15:00:42 | AIRCON 1 FAILURE at BSA0219-G9-L8-L18-L21-NNR2.6-SBTS-P2-WBB-G3 @ Sceco | 10/21/2025 02:53:36 | Minor | 7103 | AIRCON 1 FAILURE | 10/21/2025 02:52:18 | P2 | 2G | bisha | Sceco | 2G NSA | BSA0219 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/21/2025 03:00:42 | 10/21/2025 08:55:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000127 | PCM-20251021-00000392 | TT-20251021-00420 | Reference_telecom | Region_4 | BHR0308 | BHR0308 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 03:05:51 | 10/21/2025 13:18:02 | 10/21/2025 15:05:51 | DemXpicLOS observed in BHR0308 towards 10.10.188.82 @ Sceco | 10/20/2025 15:07:11 | Minor |  | DemXpicLOS | 10/20/2025 15:05:43 | P1 | 2G | jeddah | Sceco | TX NSA | BHR0308 | FLM_TE | [8 empty] | API | 10/21/2025 03:05:51 | 10/21/2025 13:18:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000133 | PCM-20251021-00000416 | TT-20251021-00431 | Telecom | Region_3 | YNB2M7427 | YNB0427 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/21/2025 03:17:31 | 10/21/2025 12:04:46 | 10/21/2025 09:17:31 | 1(LTE) sites down under YNB0427-P2-L800 @ Sceco | 10/21/2025 03:11:00 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/21/2025 03:09:25 | P2 | 4G | yanbu | Sceco | LTE SA | YNB0427-P2-L800 | FLM_TE | YNB0427 | Results: DOWN SITE HUB YNB0427-P2-L800 YNB0427 Summary: Hub: YNB0427, Down Count: 1, Down Sites: YNB0427-P2-L800 Alarm Summary: YNB0427 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 03:17:31 | 10/21/2025 07:22:42 | 10/21/2025 12:04:38 |  |  | 10/21/2025 12:04:46 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000136 | PCM-20251021-00000421 | TT-20251021-00454 | Telecom | Region_2 | RY2-ASG-02 | RY2 | Equipment | SFP_BTS | Clean SFP | WAQAR AHMED BASHIR AHMED | 10/21/2025 03:19:49 | 10/21/2025 07:15:35 | 10/21/2025 15:19:49 | Chassis Fail at RY2-ASG-02 @ Sceco_STB | 10/21/2025 03:19:37 | Minor | 101-2505202 | Chassis Fail | 10/21/2025 03:19:33 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | RY2-ASG-02 | FLM_TE | [8 empty] | API | 10/21/2025 03:19:49 | 10/21/2025 04:18:07 | 10/21/2025 04:58:21 | 10/21/2025 04:58:23 | 10/21/2025 05:23:13 | 10/21/2025 07:15:35 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000139 | PCM-20251021-00000435 | TT-20251021-00468 | EM | Region_6 | RYAB0638 | RYAB0638 |  |  |  | Faisal Javed Javed Akhtar | 10/21/2025 03:27:04 | 10/21/2025 07:15:10 | 10/21/2025 15:27:04 | RECTIFIER MAINS POWER FAILURE at RYAB0638-GSM-UMTS-P3 @ Sceco | 10/21/2025 03:20:37 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 03:18:46 | P3 | 2G | tathleeth | Sceco | 2G NSA | RYAB0638 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 03:27:04 | 10/21/2025 07:15:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000142 | PCM-20251021-00000441 | TT-20251021-00477 | Reference_telecom | Region_5 | MKJD1M9651 | MKJD0651 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 03:30:08 | 10/21/2025 19:57:08 | 10/21/2025 09:30:08 | BASE STATION ANTENNA LINE PROBLEM (VSWR upper threshold exceeded) at MKJD1M9651-L800-P1 (Ref:TT-20251001-01862) @ Sceco | 10/01/2025 19:20:34 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/01/2025 19:20:24 | P1 | 4G | makkah | Sceco | LTE NSA | MKJD1M9651 | FLM_TE | [5 empty] | VSWR upper threshold exceeded |  |  | API | 10/21/2025 03:30:08 | 10/21/2025 19:57:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000143 | PCM-20251021-00000450 | TT-20251021-00470 | Telecom | Region_3 | YNB0417 | YNB0417 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/21/2025 03:34:44 | 10/22/2025 01:55:01 | 10/21/2025 09:34:44 | 1(2G) 1(3G) 1(LTE) sites down under YNB0677-P2,YNB0417-P2/YB1MBSCH01 @ Sceco | 10/21/2025 03:26:17 | Major | 21825 | CSL Fault | 10/21/2025 03:26:15 | P3 | SRAN | yanbu | Sceco | 2G_LTE SA | YNB0677-P2-L800 LTE,YNB0417-P2 2G | FLM_TE | YNB0417 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0417 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00000446 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0417 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0417 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 03:34:44 | 10/21/2025 07:22:42 | 10/21/2025 12:04:23 |  |  | 10/21/2025 12:04:30 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000146 | PCM-20251021-00000457 | TT-20251021-00498 | Reference_telecom | Region_1 | JBL2394 | JBL2394 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Rafiq Ahmed Elturifi | 10/21/2025 03:41:00 | 10/21/2025 12:49:28 | 10/21/2025 15:41:00 | RF Unit RX Channel RTWP/RSSI Unbalanced at JBL2394-P2_SRAN @ Sceco | 10/21/2025 00:40:40 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/21/2025 00:40:37 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL2394 | FLM_TE | [8 empty] | API | 10/21/2025 03:41:00 | 10/21/2025 09:35:44 | 10/21/2025 10:59:03 | 10/21/2025 10:59:07 | 10/21/2025 11:43:49 | 10/21/2025 12:49:28 |  | Rafiq Ahmed Elturifi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000149 | PCM-20251021-00000462 | TT-20251021-00491 | Telecom | Region_3 | YNB0672 | YNB0672 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Muhammad Sajjad R3 | 10/21/2025 03:43:09 | 10/22/2025 02:33:02 | 10/21/2025 09:43:09 | 3(2G) 2(3G) 3(LTE) sites down under YNB0413-P2,YNB0436-MMM,YNB0643-P3 @ Sceco | 10/21/2025 03:32:41 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/21/2025 03:31:08 | P1 | SRAN | yanbu | Sceco | 2G_LTE SA | YNB0436-MMM 2G_LTE,YNB0643-P3 LTE,YNB0413-P2-L800 LTE | FLM_TE | YNB0672 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00000455 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 03:43:09 | 10/21/2025 07:22:43 | 10/21/2025 12:04:09 |  |  | 10/21/2025 12:04:18 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000155 | PCM-20251021-00000482 | TT-20251021-00522 | EM | Region_4 | RNRY0663 | RNRY0663 |  |  |  | Mohamed Elsaid Abdou Younes | 10/21/2025 04:02:10 | 10/21/2025 12:28:57 | 10/21/2025 10:02:10 | Generator Running at RNRY0663-GSM-P1-HUB @ Generator_DG | 10/21/2025 03:54:03 | Major | 7103 | Generator Running | 10/21/2025 03:53:57 | P1 | 2G | taif | Generator_DG | 2G NSA | RNRY0663 | FLM_EM | [5 empty] | Generator Running |  |  | API | 10/21/2025 04:02:10 | 10/21/2025 12:28:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000156 | PCM-20251021-00000483 | TT-20251021-00523 | Reference_telecom | Region_6 | BCH2193 | BCH2193 | Transsmission | MW_HW_stuck | Reset ODU | SHAH KHALID | 10/21/2025 04:02:40 | 10/21/2025 07:54:19 | 10/21/2025 16:02:40 | LossOfSignal observed in BCH2193_02 towards 10.221.244.183 @ Generator_SG | 10/20/2025 16:03:48 | Minor |  | LossOfSignal | 10/20/2025 16:02:22 | P3 | 2G | Baha | Generator_SG | TX NSA | BCH2193 | FLM_TE | [8 empty] | API | 10/21/2025 04:02:40 | 10/21/2025 04:05:12 | 10/21/2025 07:53:43 |  |  | 10/21/2025 07:54:19 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000161 | PCM-20251021-00000500 | TT-20251021-00553 | Telecom | Region_1 | DM1 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/21/2025 04:23:24 | 10/21/2025 04:23:24 | 10/21/2025 10:23:24 | Observing Multiple ALU CIDs down B/w DAM - KBR - ARR - JN | 10/21/2025 04:16:30 | Major | 5000003 | Link Down | 10/21/2025 04:16:30 | P1 | DWDM | dammam | Sceco_STB | IPBB NSA | DM1 | FLM_TE | [5 empty] | Observing Multiple ALU CIDs down B/w DAM - KBR - ARR - JN |  |  | API | 10/21/2025 04:23:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000163 | PCM-20251021-00000512 | TT-20251021-00567 | Reference_telecom | Region_1 | HFF2M7052 | HFF0052 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 04:36:27 | 10/21/2025 05:41:59 | 10/21/2025 16:36:27 | Cell RX Channel Interference Noise Power Unbalanced at HFF2M7052-P2-L800 @ Sceco | 10/21/2025 01:34:14 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/21/2025 01:34:11 | P2 | 4G | hafouf | Sceco | 2G NSA | HFF2M7052 | FLM_TE |  |  | PCM-20251021-00000510 | Need FLM to make RF path HC for MRFU 0 4 2 | Need FLM to make RF path HC for MRFU 0 4 2 |  |  |  | API | 10/21/2025 04:36:27 | 10/21/2025 05:41:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000166 | PCM-20251021-00000516 | TT-20251021-00579 | Telecom | Region_4 | JED1M8175 | JED2175 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 04:41:56 | 10/21/2025 18:52:50 | 10/21/2025 10:41:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8175-CA-L800-P3 @ Sceco | 10/21/2025 04:41:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 04:41:07 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8175 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 04:41:56 | 10/21/2025 18:52:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000167 | PCM-20251021-00000517 | TT-20251021-00575 | EM | Region_1 | JBRK2M3924 | JBRK0924 |  |  |  | Hamid Bilal Bashir Ahmed | 10/21/2025 04:42:04 | 10/21/2025 15:31:23 | 10/21/2025 10:42:04 | 1(3G/LTE) sites down under JBRK0924-P2/JB1RNCH01 @ Sceco | 10/21/2025 04:34:17 | Major | 22214 | NodeB Unavailable | 10/21/2025 04:34:14 | P2 | 3G | jubail | Sceco | 3G_LTE SA | JBRK0924-P2 | FLM_EM | JBRK0924 | Results: DOWN SITE HUB JBRK0924-P2 JBRK0924 Summary: Hub: JBRK0924, Down Count: 1, Down Sites: JBRK0924-P2 Alarm Summary: JBRK0924 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 04:42:04 | 10/21/2025 15:31:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000171 | PCM-20251021-00000522 | TT-20251021-00588 | Telecom | Region_5 | MAK1MN0320 | MAK0320 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 04:54:20 | 10/21/2025 04:54:20 | 10/21/2025 08:54:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 10/21/2025 04:53:42 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 04:53:38 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0320 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 04:54:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251021000172 | PCM-20251021-00000524 | TT-20251021-00561 | Telecom | Region_4 | JED1M7006 | JED0006 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 04:55:24 | 10/22/2025 10:57:32 | 10/21/2025 16:55:24 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at JED1M7006-P2-USF--CA-L900-L800-SBTS @ Sceco | 10/21/2025 04:27:52 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 04:27:42 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7006 | FLM_TE |  |  | PCM-20251021-00000508 | Kindly check the Fiber cable and SFP at site | Kindly check the Fiber cable and SFP at site |  |  |  | API | 10/21/2025 04:55:24 | 10/21/2025 13:18:03 | 10/22/2025 10:13:50 | 10/22/2025 10:13:52 | 10/22/2025 10:57:32 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000176 | PCM-20251021-00000528 | TT-20251021-00578 | EM | Region_3 | YBDB0282 | YBDB0282 | Transsmission | MW_SW | We are observing PORT_EXC_TRAFFIC alarms , No action done by FLM under BO domain | Muhammad Sajjad R3 | 10/21/2025 04:58:32 | 10/21/2025 12:04:03 | 10/21/2025 08:58:32 | 1(3G/LTE) sites down under YBDB0282-P1-HUB/YB1MBSCH01 @ Generator_DG | 10/21/2025 04:37:13 | Critical | 22214 | NodeB Unavailable | 10/21/2025 04:37:10 | P1 | SRAN | yanbu | Generator_DG | 3G SA | YBDB0282-P1-HUB | FLM_TE | YBDB0282 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YBDB0282 DIR YBDB0283,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00000523 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YBDB0282 DIR YBDB0283,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YBDB0282 DIR YBDB0283,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 04:58:32 | 10/21/2025 07:22:43 | 10/21/2025 12:03:51 |  |  | 10/21/2025 12:04:03 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000177 | PCM-20251021-00000529 | TT-20251021-00586 | EM | Region_1 | KKM2M4164 | KKM2164 | Enviroment | SCECO_Failure | SCECO auto restored | Reda Mohammed Mohamed Hassanein | 10/21/2025 04:59:03 | 10/22/2025 19:26:40 | 10/21/2025 10:59:03 | 1(3G/LTE) sites down under KKM2164-P3/HB1RNCH01 @ Sceco | 10/21/2025 04:50:43 | Major | 22214 | NodeB Unavailable | 10/21/2025 04:50:37 | P3 | 3G | hafr | Sceco | 3G_LTE SA | KKM2164-P3 | FLM_EM | KKM2164 | Results: DOWN SITE HUB KKM2164-P3 KKM2164 Summary: Hub: KKM2164, Down Count: 1, Down Sites: KKM2164-P3 Alarm Summary: KKM2164 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 04:59:03 | 10/21/2025 06:04:42 | 10/22/2025 19:26:31 |  |  | 10/22/2025 19:26:40 |  | Reda Mohammed Mohamed Hassanein |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000178 | PCM-20251021-00000530 | TT-20251021-00549 | Telecom | Region_3 | YB1MBSCH01 | YB2 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/21/2025 04:59:11 | 10/23/2025 19:28:47 | 10/21/2025 10:59:11 | Transmission Resource Pool Ping Packet Loss YB1MBSCH01 | 10/21/2025 04:12:31 | Major | 21394 | Transmission Resource Pool Ping Packet Loss | 10/21/2025 04:12:31 | P1 | BSC | yanbu | Sceco_STB | 2G NSA | YB1MBSCH01 | FLM_TE |  |  | PCM-20251021-00000503 | PM Errors and RSL degradation observed on YNB0675-YNB0305 FLM Team please perform health check for the mentioned MW link | PM Errors and RSL degradation observed on YNB0675-YNB0305 FLM Team please perform health check for the mentioned MW link |  |  |  | API | 10/21/2025 04:59:11 | 10/21/2025 07:22:44 | 10/23/2025 19:28:39 |  |  | 10/23/2025 19:28:47 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000179 | PCM-20251021-00000532 | TT-20251021-00591 | Telecom | Region_3 | YNA2M3508 | YNA0508 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/21/2025 05:01:54 | 10/21/2025 12:03:41 | 10/21/2025 11:01:54 | UMTS Cell Unavailable at YNA2M3508-P1 @ Sceco | 10/21/2025 04:57:43 | Major | 22202 | UMTS Cell Unavailable | 10/21/2025 04:57:41 | P2 | 3G | yanbu | Sceco | 3G SA | YNA2M3508 | FLM_TE | [8 empty] | API | 10/21/2025 05:01:54 | 10/21/2025 07:22:44 | 10/21/2025 12:03:33 |  |  | 10/21/2025 12:03:41 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000183 | PCM-20251021-00000542 | TT-20251021-00601 | Reference_telecom | Region_6 | TLT0743 | TLT0743 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/21/2025 05:09:49 | 10/21/2025 05:41:34 | 10/21/2025 17:09:49 | LossOfSignal observed in TLT0743_04 towards 10.74.121.81 @ Sceco_STB | 10/20/2025 17:10:33 | Minor |  | LossOfSignal | 10/20/2025 17:09:35 | P1 | 2G | tathleeth | Sceco_STB | TX NSA | TLT0743 | FLM_TE | [8 empty] | API | 10/21/2025 05:09:49 | 10/21/2025 05:40:04 | 10/21/2025 05:41:27 |  |  | 10/21/2025 05:41:34 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000187 | PCM-20251021-00000547 | TT-20251021-00605 | Telecom | [7 empty] | 10/21/2025 05:12:56 | 10/21/2025 05:12:56 | 10/21/2025 17:12:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2608-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Generator_SG | 10/21/2025 05:12:20 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 05:12:12 | P3 | 2G |  | Generator_SG | 5G_Cell SA | JED2608 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 05:12:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000188 | PCM-20251021-00000552 | TT-20251021-00609 | Telecom | Region_5 | MAK1MN0320 | MAK0320 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 05:16:34 | 10/21/2025 05:16:34 | 10/21/2025 17:16:34 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 10/21/2025 05:08:16 | Minor | 7115 | BASE STATION INFORMATION | 10/21/2025 05:08:09 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0320 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/21/2025 05:16:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000189 | PCM-20251021-00000554 | TT-20251021-00584 | Telecom | Region_4 | JED6135 | JED6135 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/21/2025 05:21:09 | 10/21/2025 18:07:58 | 10/21/2025 17:21:09 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED6135-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/21/2025 04:45:08 | Minor | 7114 | CELL SERVICE PROBLEM | 10/21/2025 04:44:57 | P3 | SRAN | jeddah | Sceco | 5G_Cell SA | JED6135 | FLM_TE |  |  | PCM-20251021-00000521 | Kindly check and perform HC at site as sleeping cell alarm active | Kindly check and perform HC at site as sleeping cell alarm active |  |  |  | API | 10/21/2025 05:21:09 | 10/21/2025 10:49:26 | 10/21/2025 18:07:53 |  |  | 10/21/2025 18:07:58 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000190 | PCM-20251021-00000556 | TT-20251021-00600 | Telecom | Region_4 | SQR0055 | SQR0055 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/21/2025 05:22:40 | 10/21/2025 19:30:37 | 10/21/2025 11:22:40 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at SQR0055-GSM-UMTS-P2-USF @ Generator_SG | 10/21/2025 05:04:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 05:04:01 | P2 | 2G | alaith | Generator_SG | 5G_Cell SA | SQR0055 | FLM_TE |  |  | PCM-20251021-00000540 | Kindly check as rx signal level alarm active at site | Kindly check as rx signal level alarm active at site |  |  |  | API | 10/21/2025 05:22:40 | 10/21/2025 08:39:40 | 10/21/2025 19:30:25 |  |  | 10/21/2025 19:30:37 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000192 | PCM-20251021-00000569 | TT-20251021-00631 | Reference_telecom | Region_1 | KBR2U6164 | KBR6064 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Meraj Husain Idd Baksh | 10/21/2025 05:34:09 | 10/21/2025 09:48:45 | 10/21/2025 11:34:09 | GSM Cell out of Service at KBR2U6164-P1-VIP @ Sceco (REF:TT-20250915-01318) | 10/19/2025 03:32:32 | Major | 21801 | GSM Cell out of Service | 10/19/2025 03:32:32 | VIP | 2G | dammam | Sceco | 2G SA | KBR2U6164-P1-VIP | FLM_TE | [8 empty] | API | 10/21/2025 05:34:09 | 10/21/2025 07:04:48 | 10/21/2025 09:48:18 | 10/21/2025 09:48:22 | 10/21/2025 09:48:28 | 10/21/2025 09:48:45 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000193 | PCM-20251021-00000570 | TT-20251021-00616 | EM | Region_3 | YBYN0305 | YBYN0305 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/21/2025 05:34:21 | 10/21/2025 12:03:05 | 10/21/2025 09:34:21 | 1(2G/3G/LTE) sites down under YNA0508-P1/YB1MBSCH01 @ Sceco | 10/21/2025 05:19:06 | Critical | 22214 | NodeB Unavailable | 10/21/2025 05:19:03 | P3 | SRAN | yanbu | Generator_SG | 3G_LTE SA | YNA0508-P1 | FLM_TE | YBYN0305 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0675 DIR YBYN0305,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00000563 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0675 DIR YBYN0305,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0675 DIR YBYN0305,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 05:34:21 | 10/21/2025 07:22:45 | 10/21/2025 12:02:56 |  |  | 10/21/2025 12:03:05 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000196 | PCM-20251021-00000577 | TT-20251021-00610 | EM | Region_4 | JDJZ0764 | JDJZ0764 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 05:40:30 | 10/22/2025 13:09:22 | 10/21/2025 11:40:30 | 1(2G/3G) sites down under JDJZ0764-P2/JDJZ0764-P2 @ Generator_DG | 10/21/2025 05:13:46 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 05:13:43 | P2 | 2G | qunfuddah | Generator_DG | 2G_3G SA | JDJZ0764-P2 | FLM_TE | JDJZ0764 | Results: DOWN SITE HUB JDJZ0764-P2 JDJZ0764 Summary: Hub: JDJZ0764, Down Count: 1, Down Sites: JDJZ0764-P2 Alarm Summary: JDJZ0764 No Active Alarm on HUB | PCM-20251021-00000555 | No Power Issue | No Power Issue |  | sites down |  | API | 10/21/2025 05:40:30 | 10/22/2025 13:09:22 | [6 empty] | NSN_RO |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000199 | PCM-20251021-00000583 | TT-20251021-00626 | Telecom | Region_3 | HLV2198 | HLV2198 | Enviroment | SCECO_Failure | SCECO auto restored | Mazin Meshary AlEnzi | 10/21/2025 05:50:18 | 10/21/2025 16:05:23 | 10/21/2025 09:50:18 | 1(2G) sites down under HLV2198-P1-HUB/R3_HL_HWBSC01 @ Sceco_STB | 10/21/2025 05:29:13 | Critical | 21807 | OML Fault | 10/21/2025 05:29:04 | P1 | SRAN | hail | Sceco_STB | 2G SA | HLV2198-P1-HUB | FLM_TE | HLV2198 | We are not observing any issue at TX end. Kindly visit the site and check issue locally | PCM-20251021-00000579 | We are not observing any issue at TX end. Kindly visit the site and check issue locally | We are not observing any issue at TX end. Kindly visit the site and check issue locally |  | sites down |  | API | 10/21/2025 05:50:18 | 10/21/2025 10:47:35 | 10/21/2025 16:05:14 |  |  | 10/21/2025 16:05:23 |  | Mazin Meshary AlEnzi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000202 | PCM-20251021-00000593 | TT-20251021-00654 | Reference_telecom | Region_4 | JED2596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 06:05:38 | 10/21/2025 18:52:50 | 10/21/2025 18:05:38 | LossOfSignal observed in JED2596 towards 10.1.230.53 @ Sceco | 10/20/2025 18:06:57 | Minor |  | LossOfSignal | 10/20/2025 18:05:32 | P1 | 2G | jeddah | Sceco | TX NSA | JED2596 | FLM_TE | [8 empty] | API | 10/21/2025 06:05:38 | 10/21/2025 18:52:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000203 | PCM-20251021-00000601 | TT-20251021-00656 | Telecom | Region_1 | JBL0477 | JBL0477 | Enviroment | Genset failure_Speed | Change Generator speed sensor | Ahmed Hassan Ahmed Hassanin | 10/21/2025 06:13:59 | 10/21/2025 08:51:34 | 10/21/2025 12:13:59 | 4(2G) 4(3G) 4(LTE) sites down under JBL2399-P2,JBL0477-P2,JBL2938-P3,JBL0894-P2/R1_JB_HWBSC01 @ Generator_SG | 10/21/2025 06:03:30 | Major | 21807 | OML Fault | 10/21/2025 06:03:25 | P2 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBL0894-P2 2G_3G_LTE,JBL2399-P2 2G_3G_LTE,JBL0477-P2 2G_3G_LTE,JBL2938-P3 2G_3G_LTE | FLM_EM | JBL0477 | Dear Team, Hub:- JBL0477 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | PCM-20251021-00000598 | Dear Team, Hub:- JBL0477 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. | Dear Team, Hub:- JBL0477 Observing -90 RSL & RADIO_RSL_LOW alarm at FE ,Kindly send to EM-FLM team as we suspecting power issue at hub site and support to resolve the issue at site. |  | sites down |  | API | 10/21/2025 06:13:59 | 10/21/2025 07:06:10 | 10/21/2025 07:06:33 | 10/21/2025 07:32:33 | 10/21/2025 07:32:37 | 10/21/2025 08:51:34 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000206 | PCM-20251021-00000609 | TT-20251021-00456 | Telecom | Region_4 | JED2038 | JED2038 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 06:19:39 | 10/21/2025 10:51:38 | 10/21/2025 12:19:39 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED2038-P3 @ Sceco | 10/21/2025 03:18:39 | Major | 7602 | BCF NOTIFICATION | 10/21/2025 03:14:57 | P3 | 2G | jeddah | Sceco | 2G NSA | JED2038 | FLM_TE |  |  | PCM-20251021-00000423 | Increased in BER alarm is active at site, kindly check and support to clear | Increased in BER alarm is active at site, kindly check and support to clear |  |  |  | API | 10/21/2025 06:19:39 | 10/21/2025 10:51:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000207 | PCM-20251021-00000614 | TT-20251021-00677 | Telecom | Region_4 | JED0086 | JED0086 | Equipment | BSS_HW_fault | Replace RF Module | Ahmad Mostafa Hamouda Ibrahem | 10/21/2025 06:22:41 | 10/22/2025 19:42:54 | 10/21/2025 12:22:41 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0086-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-SHOP-HUB-WDM-FON @ Sceco | 10/21/2025 06:21:50 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 06:21:45 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0086 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 06:22:41 | 10/21/2025 14:08:13 | 10/21/2025 18:01:12 | 10/21/2025 18:01:15 | 10/21/2025 18:01:16 | 10/22/2025 19:42:54 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000211 | PCM-20251021-00000622 | TT-20251021-00687 | Reference_telecom | Region_4 | JED6010 | JED6010 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 06:28:54 | 10/21/2025 10:49:27 | 10/21/2025 18:28:54 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6010-DCU @ Sceco | 10/21/2025 03:28:25 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/21/2025 03:28:23 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6010 | FLM_TE | [8 empty] | API | 10/21/2025 06:28:54 | 10/21/2025 10:49:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000212 | PCM-20251021-00000623 | TT-20251021-00682 | Reference_telecom | Region_6 | ZHR1M7138 | ZHR0138 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/21/2025 06:29:04 | 10/21/2025 10:13:24 | 10/21/2025 12:29:04 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ZHR1M7138-USF-CA-L800 @ Sceco | 10/21/2025 04:37:08 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 04:23:19 | P2 | 4G | al harja | Sceco | LTE NSA | ZHR1M7138 | FLM_TE |  |  | PCM-20251021-00000618 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/21/2025 06:29:04 | 10/21/2025 08:08:58 | 10/21/2025 10:13:08 |  |  | 10/21/2025 10:13:24 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000215 | PCM-20251021-00000626 | TT-20251021-00680 | Reference_telecom | Region_6 | ZHR1M7278 | ZHR0278 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/21/2025 06:30:24 | 10/21/2025 10:13:43 | 10/21/2025 12:30:24 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ZHR1M7278-P2-CA-L800 @ Sceco | 10/21/2025 04:37:12 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 04:22:55 | P2 | 4G | al harja | Sceco | LTE NSA | ZHR1M7278 | FLM_TE |  |  | PCM-20251021-00000616 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/21/2025 06:30:24 | 10/21/2025 08:08:59 | 10/21/2025 10:13:29 |  |  | 10/21/2025 10:13:43 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000216 | PCM-20251021-00000627 | TT-20251021-00689 | EM | [7 empty] | 10/21/2025 06:30:57 | 10/21/2025 06:30:57 | 10/21/2025 10:30:57 | BATTERY FAILURE ALARM at MUHAYIL-SEC0048_OCS @ Sceco | 10/21/2025 06:29:02 | Critical | 1-12307 | BATTERY FAILURE ALARM | 10/21/2025 06:28:54 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-[BATTERY FAILURE ALARM]:4 |  |  | API | 10/21/2025 06:30:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000225 | PCM-20251021-00000638 | TT-20251021-00699 | Reference_telecom | Region_4 | JED6231 | JED6131 | Equipment | SFP_BTS | Replace SFP | Mohamed Farag Abdelbary | 10/21/2025 06:42:52 | 10/21/2025 18:05:13 | 10/21/2025 12:42:52 | BCCH MISSING at JED6231-P3 (Ref::TT-20251016-00031) @ Sceco | 10/21/2025 02:52:58 | Major | 7767 | BCCH MISSING | 10/21/2025 02:52:53 | P3 | 2G | jeddah | Sceco | 2G_Cell SA | JED6231 | FLM_TE | [5 empty] | 0A |  |  | API | 10/21/2025 06:42:52 | 10/21/2025 10:49:27 | 10/21/2025 18:05:07 |  |  | 10/21/2025 18:05:13 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000227 | PCM-20251021-00000640 | TT-20251020-01701 | Telecom | Region_4 | SIR0050 | SIR0050 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/21/2025 06:44:22 | 10/22/2025 10:50:54 | 10/21/2025 12:44:22 | BCF NOTIFICATION (FF FF FF FF FF FF) at SIR0050-P2-USF @ Sceco | 10/20/2025 15:35:41 | Major | 7602 | BCF NOTIFICATION | 10/20/2025 15:35:27 | P2 | 2G | adam | Sceco | 2G NSA | SIR0050 | FLM_TE |  |  | PCM-20251020-00001702 | Kindly check the LTE site and make HC at site. | Kindly check the LTE site and make HC at site. |  |  |  | API | 10/21/2025 06:44:22 | 10/22/2025 10:50:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000228 | PCM-20251021-00000641 | TT-20251021-00701 | Telecom | [7 empty] | 10/21/2025 06:44:23 | 10/21/2025 06:44:23 | 10/21/2025 12:44:23 | SPAN_LOSS_UPPER_GAIN at USH-SEC0030_HYB @ Sceco | 10/21/2025 06:40:00 | Major | 1-13649 | SPAN_LOSS_UPPER_GAIN | 10/21/2025 06:39:50 | P1 | DWDM |  | Sceco | DWDM NSA | USH | FLM_TE | [5 empty] | 1-TO TAF0136(TF1)(1-B)-3-G6WDAPXF-11(LINEIN/LINEOUT(TO TAF0136(TF1)_OCS-TNG6WDAPXF(1-A03)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/21/2025 06:44:23 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000229 | PCM-20251021-00000642 | TT-20251020-00978 | Reference_telecom | Region_6 | SAB1MT0041 | SAB0041 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/21/2025 06:45:06 | 10/21/2025 21:48:32 | 10/21/2025 12:45:06 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SAB1MT0041-P2 @ Sceco | 10/20/2025 09:42:17 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 08:50:36 | P2 | 4G | baish | Sceco | LTE NSA | SAB1MT0041 | FLM_TE |  |  | PCM-20251020-00001042 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/21/2025 06:45:06 | 10/21/2025 13:22:09 | 10/21/2025 21:48:11 |  |  | 10/21/2025 21:48:32 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000231 | PCM-20251021-00000645 | TT-20251020-00979 | Reference_telecom | Region_6 | SAB1M7052 | SAB0052 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/21/2025 06:48:41 | 10/21/2025 17:54:34 | 10/21/2025 18:48:41 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at SAB1M7052-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/20/2025 09:42:42 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 08:50:49 | P2 | 4G | baish | Sceco | LTE NSA | SAB1M7052 | FLM_TE |  |  | PCM-20251020-00001039 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/21/2025 06:48:41 | 10/21/2025 13:22:09 | 10/21/2025 17:54:21 |  |  | 10/21/2025 17:54:34 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000233 | PCM-20251021-00000650 | TT-20251021-00676 | Reference_telecom | Region_3 | MDN2M8984 | MDN2984 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | TAUSEEF ILYAS | 10/21/2025 06:51:35 | 10/21/2025 19:35:40 | 10/21/2025 18:51:35 | Cell RX Channel Interference Noise Power Unbalanced at MDN2M8984-P2-L800 @ Sceco | 10/21/2025 03:21:43 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/21/2025 03:21:39 | P2 | 4G | madinah | Sceco | 2G NSA | MDN2M8984 | FLM_TE |  |  | PCM-20251021-00000613 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/21/2025 06:51:35 | 10/21/2025 07:13:03 | 10/21/2025 19:35:32 |  |  | 10/21/2025 19:35:40 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000234 | PCM-20251021-00000651 | TT-20251021-00710 | Reference_telecom | Region_3 | YNB0659 | YNB0659 |  |  |  | Muhammad Sajjad R3 | 10/21/2025 06:51:49 | 10/21/2025 07:22:46 | 10/21/2025 18:51:49 | GNSS Locked Satellites Insufficient at YNB0659-P1-SHOP-HUB-WDM_SRAN-FON @ Sceco_STB | 10/21/2025 05:55:58 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/21/2025 05:52:34 | P1 | SRAN | yanbu | Sceco_STB | 2G NSA | YNB0659 | FLM_TE | [8 empty] | API | 10/21/2025 06:51:49 | 10/21/2025 07:22:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000239 | PCM-20251021-00000660 | TT-20251021-00719 | Telecom | Region_4 | JED6071 | JED6071 | Enviroment | Air Condition | Change Fan | Mohamed Farag Abdelbary | 10/21/2025 06:53:43 | 10/21/2025 18:04:40 | 10/21/2025 18:53:43 | PT::FLM need to perform HC for AC issue at JED6071 | 10/21/2025 06:53:25 | Minor | 676767671 | Health Check-WO to TE FME | 10/21/2025 06:53:25 | P1 | 2G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED6071 | FLM_TE | [8 empty] | API | 10/21/2025 06:53:43 | 10/21/2025 10:49:28 | 10/21/2025 18:03:59 |  |  | 10/21/2025 18:04:40 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000240 | PCM-20251021-00000661 | TT-20251021-00707 | Telecom | Region_3 | HLHD2M5709 | HLHD0709 | Equipment | CB_BTS | Switch on CB on Rectifier | Mazin Meshary AlEnzi | 10/21/2025 06:54:02 | 10/21/2025 16:05:41 | 10/21/2025 12:54:02 | 1(2G) sites down under HLHD0709-P3/R3_HL_HWBSC01 @ Generator_SG | 10/21/2025 06:45:55 | Major | 21807 | OML Fault | 10/21/2025 06:45:46 | P3 | 2G | hail | Generator_SG | 2G SA | HLHD0709-P3 | FLM_TE | HLHD0709 | Results: DOWN SITE HUB HLHD0709-P3 HLHD0709 Summary: Hub: HLHD0709, Down Count: 1, Down Sites: HLHD0709-P3 Alarm Summary: HLHD0709 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 06:54:02 | 10/21/2025 10:47:35 | 10/21/2025 16:05:32 |  |  | 10/21/2025 16:05:41 |  | Mazin Meshary AlEnzi |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000243 | PCM-20251021-00000668 | TT-20251021-00698 | Telecom | Region_4 | TAF0292 | TAF0292 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 06:57:56 | 10/21/2025 14:01:01 | 10/21/2025 10:57:56 | 1(2G) 1(LTE) 5(5G) sites down under TAF2130-G9-L8-L18-L21-NR3.5-SBTS-P3 @ Sceco | 10/21/2025 06:39:25 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 06:39:23 | P3 | 2G | taif | Sceco | LTE_5G SA | TAF2130-G9-L8-L18-L21-NR3.5-SBTS-P3 5G,TAF0135-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP 5G,TAF2114-CA-L800-SBTS-P2 LTE,TAF0156-NR2.6-P2 5G,TAF0164-NR2.6-P3 5G,TAF0292-G9-L8-L18-L21-NR2.6-P3-SBTS 5G | FLM_TE | TAF0292 | DOWN SITE HUB TX FB TAF0135-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP 5G TAF0135 Observing no issue at HUB , kindly check locally TAF2114-CA-L800-SBTS-P2 LTE TAF2114 Observing no issue at HUB , kindly check locally TAF0156-NR2.6-P2 5G TAF0156 Link flapping at HUB TAF0164-NR2.6-P3 5G TAF0164 Observing no issue at HUB , kindly check locally TAF0292-G9-L8-L18-L21-NR2.6-P3-SBTS 5G TAF0292 Visibility down at HUB | PCM-20251021-00000643 | DOWN SITE HUB TX FB TAF0135-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP 5G TAF0135 Observing no issue at HUB , kindly check locally TAF2114-CA-L800-SBTS-P2 LTE TAF2114 Observing no issue at HUB , kindly check locally TAF0156-NR2.6-P2 5G TAF0156 Link flapping at HUB TAF0164-NR2.6-P3 5G TAF0164 Observing no issue at HUB , kindly check locally TAF0292-G9-L8-L18-L21-NR2.6-P3-SBTS 5G TAF0292 Visibility down at HUB | DOWN SITE HUB TX FB TAF0135-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP 5G TAF0135 Observing no issue at HUB , kindly check locally TAF2114-CA-L800-SBTS-P2 LTE TAF2114 Observing no issue at HUB , kindly check locally TAF0156-NR2.6-P2 5G TAF0156 Link flapping at HUB TAF0164-NR2.6-P3 5G TAF0164 Observing no issue at HUB , kindly check locally TAF0292-G9-L8-L18-L21-NR2.6-P3-SBTS 5G TAF0292 Visibility down at HUB |  | sites down |  | API | 10/21/2025 06:57:56 | 10/21/2025 10:06:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000245 | PCM-20251021-00000673 | TT-20251021-00692 | Telecom | Region_3 | YBYN0305 | YBYN0305 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/21/2025 06:59:29 | 10/21/2025 12:02:45 | 10/21/2025 12:59:29 | 1(2G) sites down under YNA0524-P3/YB1MBSCH01 @ Generator_SG | 10/21/2025 06:29:39 | Major | 21807 | OML Fault | 10/21/2025 06:29:39 | P3 | SRAN | yanbu | Generator_SG | 2G SA | YNA0524-P3 | FLM_TE | YBYN0305 | Dear FLM, Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0675 DIR YBYN0305,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00000664 | Dear FLM, Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0675 DIR YBYN0305,Kindly visit the link and perform the HC at mentioned link . | Dear FLM, Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0675 DIR YBYN0305,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 06:59:29 | 10/21/2025 07:22:46 | 10/21/2025 12:02:37 |  |  | 10/21/2025 12:02:45 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000248 | PCM-20251021-00000707 | TT-20251021-00765 | Reference_telecom | Region_5 | MAK1M9580 | MAK0580 |  |  |  | Ahmed Mohamed Soliman Mohamed | 10/21/2025 07:05:01 | 10/21/2025 07:05:01 | 10/21/2025 13:05:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9580-P1-VIP-HRM-SBTS (Ref:TT-20251011-00975) @ Sceco | 10/11/2025 13:58:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/11/2025 13:58:29 | VIP | 4G | makkah | Sceco | LTE SA | MAK1M9580 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 07:05:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000250 | PCM-20251021-00000711 | TT-20251021-00769 | Telecom | [7 empty] | 10/21/2025 07:08:41 | 10/21/2025 07:08:41 | 10/21/2025 13:08:41 | LAN_LOC at MUHAYIL-SEC0048_OCS @ Sceco | 10/21/2025 07:03:42 | Major | 1-12926 | LAN_LOC | 10/21/2025 07:03:31 | P1 | DWDM |  | Sceco | DWDM NSA | MUHAYIL | FLM_TE | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-71-E1EFI-12(EFINM)-COM:1 |  |  | API | 10/21/2025 07:08:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000252 | PCM-20251021-00000716 | TT-20251021-00728 | Telecom | Region_6 | BKR1M8283 | BKR2283 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/21/2025 07:09:48 | 10/21/2025 08:26:01 | 10/21/2025 19:09:48 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BKR1M8283-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/21/2025 06:57:39 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 16:03:19 | P3 | 4G | Baha | Sceco | LTE NSA | BKR1M8283 | FLM_TE |  |  | PCM-20251021-00000672 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/21/2025 07:09:48 | 10/21/2025 07:55:21 | 10/21/2025 08:25:40 |  |  | 10/21/2025 08:26:01 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000260 | PCM-20251021-00000731 | TT-20251021-00768 | Reference_telecom | Region_4 | MKYL0914 | MKYL0914 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 07:26:45 | 10/22/2025 13:09:23 | 10/21/2025 13:26:45 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at MKYL0914-GSM-UMTS-P3 (Ref::TT-20251020-02411) @ Sceco | 10/20/2025 23:07:49 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/20/2025 23:07:37 | P3 | 2G | alaith | Sceco | 5G_Cell SA | MKYL0914 | FLM_TE |  |  | PCM-20251021-00000710 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/21/2025 07:26:45 | 10/22/2025 13:09:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000262 | PCM-20251021-00000733 | TT-20251021-00777 | Telecom | Region_4 | JED1M7180 | JED0180 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 07:27:07 | 10/21/2025 18:52:51 | 10/21/2025 13:27:07 | BASE STATION ANTENNA LINE PROBLEM at JED1M7180-CA-L800-P1-VIP-SBTS @ Generator_DG | 10/21/2025 07:08:43 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/21/2025 07:08:35 | VIP | 4G | jeddah | Generator_DG | LTE NSA | JED1M7180 | FLM_TE |  |  | PCM-20251021-00000720 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/21/2025 07:27:07 | 10/21/2025 18:52:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000263 | PCM-20251021-00000734 | TT-20251021-00779 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/21/2025 07:27:27 | 10/21/2025 18:03:45 | 10/21/2025 11:27:27 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/21/2025 07:10:16 | Critical | 7654 | CELL OPERATION DEGRADED | 10/21/2025 07:10:11 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251021-00000723 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/21/2025 07:27:27 | 10/21/2025 10:49:28 | 10/21/2025 18:03:38 |  |  | 10/21/2025 18:03:45 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000264 | PCM-20251021-00000735 | TT-20251021-00724 | Telecom | Region_6 | BKR1M8214 | BKR2214 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/21/2025 07:28:17 | 10/21/2025 16:00:09 | 10/21/2025 19:28:17 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at BKR1M8214-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/21/2025 06:56:07 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 16:03:27 | P3 | 4G | Baha | Generator_SG | LTE NSA | BKR1M8214 | FLM_TE |  |  | PCM-20251021-00000667 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/21/2025 07:28:17 | 10/21/2025 07:55:21 | 10/21/2025 15:59:59 |  |  | 10/21/2025 16:00:09 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000265 | PCM-20251021-00000739 | TT-20251021-00770 | Reference_telecom | Region_3 | MDN2M7815 | MDN0815 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/21/2025 07:28:36 | 10/21/2025 08:54:53 | 10/21/2025 19:28:36 | Cell RX Channel Interference Noise Power Unbalanced at MDN2M7815-CA-L800-P3 @ Sceco | 10/21/2025 00:28:57 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/21/2025 00:28:54 | P3 | 4G | madinah | Sceco | 2G NSA | MDN2M7815 | FLM_TE |  |  | PCM-20251021-00000712 | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/21/2025 07:28:36 | 10/21/2025 08:54:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000268 | PCM-20251021-00000749 | TT-20251021-00797 | Reference_EM | Region_1 | DMJR0161 | DMJR0161 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Ragab Farg Abdel Nabi Bekhatro | 10/21/2025 07:31:25 | 10/21/2025 07:43:25 | 10/21/2025 13:31:25 | Generator failure at DMJR0161-P1-HUB_SRAN @ Sceco_STB | 10/21/2025 07:21:00 | Major | 65114 | Generator failure | 10/21/2025 07:20:56 | P1 | SRAN | arar | Sceco_STB | 2G NSA | DMJR0161 | FLM_EM | [8 empty] | API | 10/21/2025 07:31:25 | 10/21/2025 07:42:58 | 10/21/2025 07:43:13 | 10/21/2025 07:43:16 |  | 10/21/2025 07:43:25 |  | Ragab Farg Abdel Nabi Bekhatro |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000269 | PCM-20251021-00000752 | TT-20251021-00807 | Reference_telecom | Region_1 | JBL2108-ZJu04-CSG-01 | JBL2108 |  |  |  | Tahir Mahmood Hafiz Yar | 10/21/2025 07:35:53 | 10/21/2025 08:38:24 | 10/21/2025 13:35:53 | MW Alarm of failed LAG negotiation at JBL2108-ZJu04-CSG-01 REF: TT-20250915-00318 @ Generator_DG | 10/21/2025 07:00:07 | Major | 101-1102218 | Alarm of failed LAG negotiation | 10/21/2025 07:00:02 | P1 | IPRAN | jubail | Generator_DG | IPRAN SA | JBL2108-ZJu04-CSG-01 | FLM_TE | [8 empty] | API | 10/21/2025 07:35:53 | 10/21/2025 08:38:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000272 | PCM-20251021-00000771 | TT-20251021-00771 | Reference_telecom | Region_4 | TAF1M7277 | TAF0277 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 07:38:53 | 10/21/2025 11:05:59 | 10/21/2025 19:38:53 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at TAF1M7277-G9-L18-L21-SBTS-P2 @ Sceco | 10/21/2025 05:08:42 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 05:08:51 | P2 | 4G | taif | Sceco | LTE NSA | TAF1M7277 | FLM_TE |  |  | PCM-20251021-00000714 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/21/2025 07:38:53 | 10/21/2025 11:05:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000277 | PCM-20251021-00000790 | TT-20251021-00835 | Telecom | [7 empty] | 10/21/2025 07:47:26 | 10/21/2025 07:47:26 | 10/21/2025 13:47:26 | SPAN_LOSS_UPPER_GAIN at MYH-SEC0029_HYB @ Sceco_STB | 10/21/2025 07:43:10 | Major | 1-13649 | SPAN_LOSS_UPPER_GAIN | 10/21/2025 07:43:01 | P1 | DWDM |  | Sceco_STB | DWDM NSA | MYH | FLM_TE | [5 empty] | 0-TO RYMK0671&R2-RYMK-SEC0028(1-A)-5-G6WDAPXF-11(LINEIN/LINEOUT(TO RYMK0671_OCS-TNG6WDAPXF(1-A02)-LINEIN/LINEOUT))-OTS:1 |  |  | API | 10/21/2025 07:47:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000280 | PCM-20251021-00000803 | TT-20251021-00839 | EM | Region_1 | JBL0477 | JBL0477 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Hassan Ahmed Hassanin | 10/21/2025 07:51:33 | 10/21/2025 08:51:49 | 10/21/2025 19:51:33 | Mains Failure at JBL0477-P2_SRAN @ Sceco | 10/21/2025 07:45:58 | Minor | 65109 | Mains Failure | 10/21/2025 07:41:30 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL0477 | FLM_EM | [8 empty] | API | 10/21/2025 07:51:33 | 10/21/2025 08:51:39 | 10/21/2025 08:51:43 |  |  | 10/21/2025 08:51:49 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000287 | PCM-20251021-00000822 | TT-20251021-00858 | EM | Region_6 | MHL1M7180 | MHL0180 |  |  |  | Zia Ur Rahamn | 10/21/2025 08:07:03 | 10/21/2025 19:03:16 | 10/21/2025 20:07:03 | RECTIFIER MODULE FAILURE at MHL1M7180-P2-CA-L800 @ Sceco | 10/21/2025 07:58:53 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/21/2025 07:58:46 | P2 | 4G | mohail | Sceco | LTE NSA | MHL1M7180 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/21/2025 08:07:03 | 10/21/2025 19:03:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000290 | PCM-20251021-00000833 | TT-20251021-00871 | Telecom | Region_1 | HFF2M7050 | HFF0050 | Equipment | Power Cable_RRU_BTS | Replace Indoor Power Connector | Imran Ali Yousaf | 10/21/2025 08:12:37 | 10/21/2025 10:26:12 | 10/21/2025 14:12:37 | Cell Unavailable at HFF2M7050-P1-SHOP-WDM-L800 @ Sceco | 10/21/2025 08:06:13 | Major | 29240 | Cell Unavailable | 10/21/2025 08:05:41 | P1 | 4G | hafouf | Sceco | LTE SA | HFF2M7050 | FLM_TE | [8 empty] | API | 10/21/2025 08:12:37 | 10/21/2025 09:43:44 | 10/21/2025 09:43:55 | 10/21/2025 09:44:03 | 10/21/2025 09:48:34 | 10/21/2025 10:26:12 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000295 | PCM-20251021-00000841 | TT-20251021-00874 | Telecom | Region_4 | JED0044 | JED0044 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 08:20:04 | 10/21/2025 08:20:04 | 10/21/2025 12:20:04 | 1(2G) sites down under JED0044-P1/JED0044-P1 @ Sceco | 10/21/2025 08:11:49 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 08:11:47 | P1 | 2G | jeddah | Sceco | 2G SA | JED0044-P1 | FLM_TE | JED0044 | Results: DOWN SITE HUB JED0044-P1 JED0044 Summary: Hub: JED0044, Down Count: 1, Down Sites: JED0044-P1 Alarm Summary: JED0044 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 08:20:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000302 | PCM-20251021-00000856 | TT-20251021-00890 | EM | Region_6 | BCH1M8203 | BCH2203 |  |  |  | Fathy Mohamed | 10/21/2025 08:26:41 | 10/21/2025 20:48:11 | 10/21/2025 20:26:41 | RECTIFIER MODULE FAILURE at BCH1M8203-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/21/2025 08:18:40 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/21/2025 08:18:31 | P3 | 4G | Baha | Generator_SG | LTE NSA | BCH1M8203 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/21/2025 08:26:41 | 10/21/2025 20:48:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000307 | PCM-20251021-00000867 | TT-20251021-00889 | Telecom | Region_4 | KMMD9075 | KMMD9075 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/21/2025 08:32:17 | 10/21/2025 13:39:32 | 10/21/2025 12:32:17 | 4(2G) 3(3G) 1(LTE) 2(5G) sites down under JED2889-FWA-P1-VIP,KMMD0726-P3,KMMD0754-P3,KMMD0748-P3/KMMD0748-P3 @ Sceco | 10/21/2025 08:23:14 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 08:23:10 | P3 | Repeater | jeddah | Generator_SG | 2G_3G_5G SA | KMMD0726-P3 2G_3G_5G,JED2889-FWA-P1-VIP 2G_5G,KMMD0754-P3 2G_3G,KMMD0748-P3 2G_3G | FLM_TE | KMMD9075 | DOWN SITE HUB TX FB JED2889-FWA-P1-VIP JED2889 suspected Power issue at HUB KMMD0754-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally KMMD0726-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally KMMD0748-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally | PCM-20251021-00000866 | DOWN SITE HUB TX FB JED2889-FWA-P1-VIP JED2889 suspected Power issue at HUB KMMD0754-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally KMMD0726-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally KMMD0748-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally | DOWN SITE HUB TX FB JED2889-FWA-P1-VIP JED2889 suspected Power issue at HUB KMMD0754-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally KMMD0726-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally KMMD0748-P3 KMMD9075 We observing odu cable open at the HUB ,kindly check locally |  | sites down |  | API | 10/21/2025 08:32:17 | 10/21/2025 11:49:40 | 10/21/2025 11:50:49 |  |  | 10/21/2025 11:50:54 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000308 | PCM-20251021-00000869 | TT-20251021-00900 | EM | Region_1 | JBRK0914 | JBRK0914 |  |  |  | Dileesh Muringothil Devarajan | 10/21/2025 08:32:54 | 10/21/2025 17:13:21 | 10/21/2025 20:32:54 | Door opening alarm at JBRK0914-P2_SRAN @ Sceco | 10/21/2025 08:32:31 | Minor | 65101 | Door opening alarm | 10/21/2025 08:29:30 | P2 | SRAN | jubail | Sceco | 2G NSA | JBRK0914 | FLM_EM | [8 empty] | API | 10/21/2025 08:32:54 | 10/21/2025 17:13:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000317 | PCM-20251021-00000898 | TT-20251021-00931 | Reference_telecom | Region_6 | TLT0722 | TLT0722 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/21/2025 08:46:48 | 10/21/2025 10:08:03 | 10/21/2025 20:46:48 | LossOfSignal observed in TLT0722_01 towards 10.74.121.83 @ Sceco | 10/20/2025 20:46:46 | Minor |  | LossOfSignal | 10/20/2025 20:46:42 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0722 | FLM_TE | [8 empty] | API | 10/21/2025 08:46:48 | 10/21/2025 10:04:14 | 10/21/2025 10:07:56 |  |  | 10/21/2025 10:08:03 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000318 | PCM-20251021-00000901 | TT-20251021-00932 | EM | Region_1 | ARM0735 | ARM0735 |  |  |  | Khaled Mohamed Abdulla Wahba | 10/21/2025 08:48:21 | 10/21/2025 09:01:23 | 10/21/2025 20:48:21 | NETECO: AC Overfrequency at ARM0735 @ Generator_SG | 10/21/2025 08:42:00 | Minor | 1589 | AC Overfrequency | 10/21/2025 08:42:00 | VIP | SRAN | dammam | Generator_SG | 2G NSA | ARM0735 | FLM_EM | [8 empty] | API | 10/21/2025 08:48:21 | 10/21/2025 09:01:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000321 | PCM-20251021-00000904 | TT-20251021-00915 | Telecom | Region_4 | HHR0489 | HHR0489 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Anas Mohamedelamin Abbas Mustafa | 10/21/2025 08:50:21 | 10/22/2025 01:08:00 | 10/21/2025 12:50:21 | 4(2G) 2(LTE) 4(5G) sites down under HHR0489-P1-VIP-HHR,JED2107-P3,HHR0484-P1-VIP-HHR,JED0005-P2/JED0005-P2 @ Sceco | 10/21/2025 08:31:10 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 08:31:03 | VIP | 2G | jeddah | Generator_SG | 2G_LTE_5G SA | HHR0489-P1-VIP-HHR 2G_LTE,JED0005-P2 2G_5G,JED2107-P3 2G_5G,HHR0484-P1-VIP-HHR 2G | FLM_EM | HHR0489 | DOWN SITE HUB TX FB JED2107-P3 JED2107 Node Rebooted HHR0489-P1-VIP-HHR HHR0489 suspected Power issue at HUB HHR0484-P1-VIP-HHR HHR0489 suspected Power issue at HUB JED0005-P2 JED0005 suspected Power issue at HUB | PCM-20251021-00000885 | DOWN SITE HUB TX FB JED2107-P3 JED2107 Node Rebooted HHR0489-P1-VIP-HHR HHR0489 suspected Power issue at HUB HHR0484-P1-VIP-HHR HHR0489 suspected Power issue at HUB JED0005-P2 JED0005 suspected Power issue at HUB | DOWN SITE HUB TX FB JED2107-P3 JED2107 Node Rebooted HHR0489-P1-VIP-HHR HHR0489 suspected Power issue at HUB HHR0484-P1-VIP-HHR HHR0489 suspected Power issue at HUB JED0005-P2 JED0005 suspected Power issue at HUB |  | sites down |  | API | 10/21/2025 08:50:21 | 10/21/2025 23:34:31 | 10/21/2025 23:39:25 | 10/21/2025 23:39:27 |  | 10/22/2025 01:08:00 |  | Anas Mohamedelamin Abbas Mustafa |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000323 | PCM-20251021-00000906 | TT-20251021-00913 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 08:50:53 | 10/21/2025 08:50:53 | 10/21/2025 14:50:53 | LOCAL BLOCK at JED0500-P2 @ Sceco | 10/21/2025 08:29:57 | Major | 7208 | LOCAL BLOCK | 10/21/2025 08:29:43 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0500 | FLM_TE |  |  | PCM-20251021-00000879 | Please check the local access at site | Please check the local access at site |  |  |  | API | 10/21/2025 08:50:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000328 | PCM-20251021-00000918 | TT-20251021-00947 | Telecom | Region_3 | MDN2M8907 | MDN2907 | Equipment | BTS_Cable | Replace CPRI Cable | Hussain Ahmad Sultan Muhammad | 10/21/2025 08:57:14 | 10/21/2025 11:21:38 | 10/21/2025 14:57:14 | Cell Unavailable at MDN2M8907-P2-L800 @ Sceco | 10/21/2025 08:56:28 | Major | 29240 | Cell Unavailable | 10/21/2025 08:54:55 | P2 | 4G | madinah | Sceco | LTE SA | MDN2M8907 | FLM_TE | [8 empty] | API | 10/21/2025 08:57:14 | 10/21/2025 09:56:41 | 10/21/2025 10:05:55 | 10/21/2025 10:06:35 | 10/21/2025 10:11:18 | 10/21/2025 11:21:38 |  | Hussain Ahmad Sultan Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000331 | PCM-20251021-00000923 | TT-20251021-00952 | Telecom | Region_3 | MDN2907 | MDN2907 | Equipment | BTS_Cable | Replace CPRI Cable | Hussain Ahmad Sultan Muhammad | 10/21/2025 09:00:16 | 10/21/2025 11:27:55 | 10/21/2025 15:00:16 | BBU CPRI Interface Error at MDN2907-P2_SRAN @ Sceco | 10/21/2025 08:57:27 | Major | 26234 | BBU CPRI Interface Error | 10/21/2025 08:54:52 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2907 | FLM_TE | [8 empty] | API | 10/21/2025 09:00:16 | 10/21/2025 09:56:41 | 10/21/2025 11:22:04 | 10/21/2025 11:22:12 | 10/21/2025 11:22:17 | 10/21/2025 11:27:55 |  | Hussain Ahmad Sultan Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000333 | PCM-20251021-00000926 | TT-20251021-00946 | EM | Region_4 | TFBH0807 | TFBH0807 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 09:02:04 | 10/21/2025 12:14:31 | 10/21/2025 15:02:04 | 1(2G/3G/5G) sites down under TFBH0807-P3 @ Sceco | 10/21/2025 08:53:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 08:53:54 | P3 | 2G | taif | Sceco | 5G SA | TFBH0807-GSM-P3 | FLM_TE | TFBH0807 | Results: DOWN SITE HUB TFBH0807-GSM-P3 TFBH0807 Summary: Hub: TFBH0807, Down Count: 1, Down Sites: TFBH0807-GSM-P3 Alarm Summary: TFBH0807 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.2.12:8080] [URL:http://10.98.2.12:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 09:02:04 | 10/21/2025 10:06:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000336 | PCM-20251021-00000930 | TT-20251021-00960 | EM | Region_1 | DMJR0161 | DMJR0161 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Ragab Farg Abdel Nabi Bekhatro | 10/21/2025 09:05:56 | 10/21/2025 09:08:01 | 10/21/2025 15:05:56 | Door opening alarm at DMJR0161-P1-HUB_SRAN @ Sceco_STB | 10/21/2025 09:05:19 | Major | 65101 | Door opening alarm | 10/21/2025 09:05:15 | P1 | SRAN | arar | Sceco_STB | 2G NSA | DMJR0161 | FLM_EM | [8 empty] | API | 10/21/2025 09:05:56 | 10/21/2025 09:07:39 | 10/21/2025 09:07:55 |  |  | 10/21/2025 09:08:01 |  | Ragab Farg Abdel Nabi Bekhatro |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000338 | PCM-20251021-00000932 | TT-20251021-00955 | EM | Region_1 | UQR2M1681 | UQR0681 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 09:06:07 | 10/21/2025 21:36:23 | 10/21/2025 15:06:07 | 1(2G/3G/LTE) sites down under UQR0681-P3-USF/R1_DM_HWBSC01 @ Power Cube | 10/21/2025 08:57:54 | Major | 21825 | CSL Fault | 10/21/2025 08:57:52 | P3 | 2G | hafouf | Power Cube | 2G SA | UQR0681-P3-USF | FLM_TE | UQR0681 | Results: DOWN SITE HUB UQR0681-P3-USF UQR0681 Summary: Hub: UQR0681, Down Count: 1, Down Sites: UQR0681-P3-USF Alarm Summary: UQR0681 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 09:06:07 | 10/21/2025 21:36:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000342 | PCM-20251021-00000942 | TT-20251021-00968 | Telecom | Region_1 | DAM0257 | DAM0257 | Equipment | BSS_HW_Stuck | Reset RFU | Shakeel Ahmed Hafeez Ameen | 10/21/2025 09:12:09 | 10/21/2025 14:14:22 | 10/21/2025 21:12:09 | ALD Maintenance Link Failure at DAM0257-P2_SRAN @ Sceco | 10/21/2025 09:09:17 | Minor | 26541 | ALD Maintenance Link Failure | 10/21/2025 09:07:42 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0257 | FLM_TE | [8 empty] | API | 10/21/2025 09:12:09 | 10/21/2025 09:23:07 | 10/21/2025 12:32:52 | 10/21/2025 12:54:33 | 10/21/2025 13:34:44 | 10/21/2025 14:14:22 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000349 | PCM-20251021-00000956 | TT-20251021-00982 | EM | Region_1 | KBR2417 | KBR2417 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 09:17:51 | 10/21/2025 16:28:32 | 10/21/2025 21:17:51 | Door opening alarm at KBR2417-P3_SRAN @ Generator_SG | 10/21/2025 09:17:30 | Minor | 65101 | Door opening alarm | 10/21/2025 09:17:25 | P3 | SRAN | dammam | Generator_SG | 2G NSA | KBR2417 | FLM_EM | [8 empty] | API | 10/21/2025 09:17:51 | 10/21/2025 16:28:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000350 | PCM-20251021-00000957 | TT-20251021-00984 | EM | Region_1 | HFB2M5001 | HFB0001 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/21/2025 09:18:51 | 10/21/2025 09:18:51 | 10/21/2025 15:18:51 | Mains Failure at HFB2M5001-P1-DIA @ Generator_SG | 10/21/2025 09:09:08 | Major | 65109 | Mains Failure | 10/21/2025 09:09:06 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5001 | FLM_EM | [8 empty] | API | 10/21/2025 09:18:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000352 | PCM-20251021-00000959 | TT-20251021-00987 | EM | Region_1 | HFSW0901 | HFSW0901 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/21/2025 09:21:58 | 10/23/2025 11:12:25 | 10/21/2025 15:21:58 | Door opening alarm at HFSW0901-P1-HUB-VIP_SRAN @ Generator_SG | 10/21/2025 09:21:47 | Major | 65101 | Door opening alarm | 10/21/2025 09:21:43 | VIP | SRAN | hafouf | Generator_SG | 2G NSA | HFSW0901 | FLM_EM | [8 empty] | API | 10/21/2025 09:21:58 | 10/22/2025 08:41:50 | 10/23/2025 11:12:13 |  |  | 10/23/2025 11:12:25 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000354 | PCM-20251021-00000961 | TT-20251021-00976 | Telecom | Region_4 | JED1U6720 | JED6020 | Equipment | SFP_BTS | Clean SFP | Mohamed Farag Abdelbary | 10/21/2025 09:22:41 | 10/21/2025 18:03:24 | 10/21/2025 15:22:41 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/21/2025 09:09:29 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/21/2025 09:09:19 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251021-00000949 | Please check the SRIO connectivity between LTE to TDD. | Please check the SRIO connectivity between LTE to TDD. |  |  |  | API | 10/21/2025 09:22:41 | 10/21/2025 10:49:29 | 10/21/2025 18:03:17 |  |  | 10/21/2025 18:03:24 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000365 | PCM-20251021-00000981 | TT-20251021-01010 | Telecom | Region_1 | KBR2U6764 | KBR6064 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Meraj Husain Idd Baksh | 10/21/2025 09:34:53 | 10/21/2025 09:49:24 | 10/21/2025 21:34:53 | RF Unit Maintenance Link Failure at KBR2U6764-P1-VIP @ Sceco | 10/21/2025 09:31:28 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 09:29:45 | VIP | 4G | dammam | Sceco | LTE NSA | KBR2U6764 | FLM_TE | [8 empty] | API | 10/21/2025 09:34:53 | 10/21/2025 09:40:29 | 10/21/2025 09:49:01 | 10/21/2025 09:49:03 | 10/21/2025 09:49:08 | 10/21/2025 09:49:24 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000368 | PCM-20251021-00000989 | TT-20251021-01015 | Telecom | Region_6 | SHF0105 | SHF0105 | Transsmission | CB_MW | Switch on CB on Rectifier | Amir Sohail | 10/21/2025 09:40:33 | 10/22/2025 17:07:00 | 10/21/2025 21:40:33 | Power Supply at SHF0105 on 10.1.172.10 @ Sceco | 10/21/2025 09:34:26 | Minor | Power Supply | Power Supply | 10/21/2025 09:39:13 | P3 | 2G | khamis mushyet | Sceco | TX NSA | SHF0105 | FLM_TE | [8 empty] | API | 10/21/2025 09:40:33 | 10/21/2025 10:01:52 | 10/22/2025 17:06:46 |  |  | 10/22/2025 17:07:00 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000378 | PCM-20251021-00001016 | TT-20251021-01032 | EM | Region_4 | TAF2349 | TAF2349 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 09:54:02 | 10/21/2025 13:54:32 | 10/21/2025 15:54:02 | 1(2G/3G/5G) sites down under TAF2349-P2 @ Sceco | 10/21/2025 09:45:46 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 09:45:42 | P2 | 2G | taif | Sceco | 5G SA | TAF2349-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | TAF2349 | Results: DOWN SITE HUB TAF2349-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 TAF2349 Summary: Hub: TAF2349, Down Count: 1, Down Sites: TAF2349-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 Alarm Summary: TAF2349 Alarm Active on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-4376952 [ACTIVE] [URL:http://10.98.72.116:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 09:54:02 | 10/21/2025 11:05:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000380 | PCM-20251021-00001019 | TT-20251021-01045 | Telecom | Region_1 | HFF2M8071 | HFF2071 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 09:54:44 | 10/21/2025 21:36:24 | 10/21/2025 15:54:44 | Cell Unavailable at HFF2M8071-FWA-P1-VIP-L800 @ Sceco | 10/21/2025 09:53:58 | Major | 29240 | Cell Unavailable | 10/21/2025 09:53:24 | P2 | 4G | hafouf | Sceco | LTE SA | HFF2M8071 | FLM_TE | [8 empty] | API | 10/21/2025 09:54:44 | 10/21/2025 21:36:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000383 | PCM-20251021-00001022 | TT-20251021-00895 | Reference_telecom | Region_6 | ABH1M7342 | ABH0342 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 09:55:27 | 10/21/2025 20:35:33 | 10/21/2025 15:55:27 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ABH1M7342-CA-L800-P3 @ Sceco | 10/21/2025 06:54:08 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 06:29:16 | P3 | 4G | abha | Sceco | LTE NSA | ABH1M7342 | FLM_TE |  | Dear team , site was down and restored ,kindly check | PCM-20251021-00001006 | Dear team , site was down and restored ,kindly check | Dear team , site was down and restored ,kindly check |  |  |  | API | 10/21/2025 09:55:27 | 10/21/2025 12:09:19 | 10/21/2025 20:35:23 |  |  | 10/21/2025 20:35:33 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000388 | PCM-20251021-00001043 | TT-20251021-01064 | Telecom | Region_1 | HFF6028 | HFF6028 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 10:03:49 | 10/21/2025 14:23:15 | 10/21/2025 22:03:49 | RF Unit Maintenance Link Failure at HFF6028-DCU1 @ Sceco | 10/21/2025 09:50:42 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 09:58:32 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/21/2025 10:03:49 | 10/21/2025 14:23:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000391 | PCM-20251021-00001048 | TT-20251021-01069 | Telecom | Region_4 | JED6032 | JED6032 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mohamed Farag Abdelbary | 10/21/2025 10:05:47 | 10/22/2025 15:48:22 | 10/21/2025 22:05:47 | PT: Zain Site ID JED6032/4543 No Coverage Issue STC ref # PR00040330968 STC ID IJD076 | 10/21/2025 10:03:59 | Minor | 676767681 | Health Check-WO to TE FME | 10/21/2025 10:05:41 | P3 | 2G | jeddah | Sceco | LTE NSA | PT: Zain Site ID JED6032/4543 No Coverage Issue STC ref # PR00040330968 STC ID IJD076 | FLM_TE | [8 empty] | API | 10/21/2025 10:05:47 | 10/21/2025 10:49:29 | 10/22/2025 11:09:46 | 10/22/2025 11:10:13 | 10/22/2025 11:10:32 | 10/22/2025 15:48:22 |  | Mohamed Farag Abdelbary |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000392 | PCM-20251021-00001050 | TT-20251021-00639 | Telecom | Region_1 | JBKH2M3603 | JBKH0603 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Meraj Husain Idd Baksh | 10/21/2025 10:06:21 | 10/23/2025 17:01:44 | 10/21/2025 22:06:21 | RF Unit Maintenance Link Failure at JBKH2M3603-P2 @ Sceco | 10/21/2025 05:39:47 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 05:38:05 | P2 | 3G | dammam | Sceco | 2G NSA | JBKH2M3603 | FLM_TE |  |  | PCM-20251021-00000998 | 3G cells deactivated , pls check with NOC | 3G cells deactivated , pls check with NOC |  |  |  | API | 10/21/2025 10:06:21 | 10/21/2025 10:07:57 | 10/23/2025 15:04:24 | 10/23/2025 15:05:06 | 10/23/2025 15:45:18 | 10/23/2025 17:01:44 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000395 | PCM-20251021-00001060 | TT-20251021-01080 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/21/2025 10:11:02 | 10/22/2025 08:43:23 | 10/21/2025 22:11:02 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/21/2025 10:02:35 | Minor | 7103 | HIGH TEMP | 10/21/2025 10:02:31 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/21/2025 10:11:02 | 10/22/2025 08:43:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000398 | PCM-20251021-00001063 | TT-20251021-01083 | Telecom | Region_1 | HFF6028 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 10:12:05 | 10/21/2025 14:55:36 | 10/21/2025 22:12:05 | RF Unit CPRI Interface Error at HFF6028-DCU1 @ Sceco | 10/21/2025 09:57:19 | Minor | 26504 | RF Unit CPRI Interface Error | 10/21/2025 10:04:54 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/21/2025 10:12:05 | 10/21/2025 14:23:17 | 10/21/2025 14:55:23 |  |  | 10/21/2025 14:55:36 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000399 | PCM-20251021-00001064 | TT-20251021-01073 | Telecom | Region_4 | SJED1S7666 | SJED0666 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 10:12:31 | 10/21/2025 10:51:41 | 10/21/2025 16:12:31 | 1(LTE) sites down under SJED0666-CA-P3 @ Sceco | 10/21/2025 10:04:26 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 10:04:24 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0666-CA-P3 | FLM_TE | SJED0666 | Results: DOWN SITE HUB SJED0666-CA-P3 SJED0666 Summary: Hub: SJED0666, Down Count: 1, Down Sites: SJED0666-CA-P3 Alarm Summary: SJED0666 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.99.235.228:8080] [URL:http://10.99.235.228:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 10:12:31 | 10/21/2025 10:51:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000402 | PCM-20251021-00001074 | TT-20251021-01095 | Telecom | Region_4 | THO0371 | THO0371 |  |  |  | Khizer Hayat | 10/21/2025 10:16:11 | 10/21/2025 14:05:39 | 10/21/2025 22:16:11 | BASE STATION SERVICE PROBLEM (No connection to unit) at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/21/2025 10:15:31 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 10:15:20 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | THO0371 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 10:16:11 | 10/21/2025 14:05:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000403 | PCM-20251021-00001075 | TT-20251021-01097 | Telecom | Region_1 | HFF6028 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 10:17:45 | 10/21/2025 14:56:00 | 10/21/2025 22:17:45 | RF Unit Clock Problem at HFF6028-DCU1 @ Sceco | 10/21/2025 10:01:56 | Minor | 26538 | RF Unit Clock Problem | 10/21/2025 10:09:27 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/21/2025 10:17:45 | 10/21/2025 14:23:18 | 10/21/2025 14:55:47 |  |  | 10/21/2025 14:56:00 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000404 | PCM-20251021-00001076 | TT-20251021-01099 | Telecom | Region_3 | HLV0081 | HLV0081 | Equipment | BTS_Cable | Replace Indoor Feeder Cable Connector | Atif Shahzad Muhammad Ajaib | 10/21/2025 10:18:46 | 10/21/2025 17:57:15 | 10/21/2025 22:18:46 | ALD Maintenance Link Failure at HLV0081-P2_SRAN @ Sceco | 10/21/2025 10:16:52 | Minor | 26541 | ALD Maintenance Link Failure | 10/21/2025 10:05:43 | P2 | SRAN | hail | Sceco | 2G NSA | HLV0081 | FLM_TE | [8 empty] | API | 10/21/2025 10:18:46 | 10/21/2025 10:25:06 | 10/21/2025 17:41:07 | 10/21/2025 17:41:12 | 10/21/2025 17:41:20 | 10/21/2025 17:57:15 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251021000406 | PCM-20251021-00001078 | TT-20251021-01100 | Telecom | Region_4 | JED1MN0007 | JED0007 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 10:20:35 | 10/21/2025 15:08:50 | 10/21/2025 16:20:35 | PT:: FLM Need to perform HC at JED1MN0007 under R4 (BO Request) | 10/21/2025 10:20:17 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 10:20:17 | P2 | 5G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED1MN0007 | FLM_TE | [8 empty] | API | 10/21/2025 10:20:35 | 10/21/2025 13:18:04 | 10/21/2025 14:49:49 | 10/21/2025 15:07:45 | 10/21/2025 15:08:50 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000408 | PCM-20251021-00001081 | TT-20251021-01102 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 10:21:22 | 10/21/2025 22:26:23 | 10/21/2025 22:21:22 | FIRE ALARM+FIRE ALARM FAILURE at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/21/2025 10:13:01 | Minor | 7103 | FIRE ALARM+FIRE ALARM FAILURE | 10/21/2025 10:12:50 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | FIRE ALARM+FIRE ALARM FAILURE |  |  | Manual | 10/21/2025 10:21:22 | 10/21/2025 22:26:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000409 | PCM-20251021-00001085 | TT-20251021-00713 | Telecom | Region_3 | MDTB-0339-NE40E-X1-P&PE-01 | MDTB0339 | Transsmission | IPRAN_Fluctuation | Reset port | Ibrahim Mohammad AbdulMalik alraee | 10/21/2025 10:23:44 | 10/22/2025 21:15:06 | 10/21/2025 22:23:44 | Overlow Input Power of Optical Module at MDTB-0339-NE40E-X1-P&PE-01 @ Sceco_STB | 10/21/2025 06:52:20 | Minor | 101-3067697 | Overlow Input Power of Optical Module | 10/21/2025 06:51:32 | P1 | IPRAN | madinah | Sceco_STB | IPRAN NSA | MDTB-0339-NE40E-X1-P&PE-01 | FLM_TE |  |  | PCM-20251021-00000921 | please check this port in MW as we are receiving Low power <MDTB-0339-NE40E-X1-P&PE-01>dis int GigabitEthernet1-4-0 Rx Power: -19.10dBm, Warning range: [-16.99, 0.00]dBm Tx Power: -5.49dBm, Warning range: [-9.50, 0.00]dBm | please check this port in MW as we are receiving Low power <MDTB-0339-NE40E-X1-P&PE-01>dis int GigabitEthernet1-4-0 Rx Power: -19.10dBm, Warning range: [-16.99, 0.00]dBm Tx Power: -5.49dBm, Warning range: [-9.50, 0.00]dBm |  |  |  | API | 10/21/2025 10:23:44 | 10/21/2025 12:20:29 | 10/22/2025 21:14:02 |  |  | 10/22/2025 21:15:06 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000410 | PCM-20251021-00001089 | TT-20251021-01107 | Telecom | [7 empty] | 10/21/2025 10:24:27 | 10/21/2025 10:24:27 | 10/21/2025 16:24:27 | BBU CPRI Interface Error at HFF6003-P3_SRAN @ Sceco | 10/21/2025 10:19:01 | Major | 26234 | BBU CPRI Interface Error | 10/21/2025 10:17:28 | P3 | SRAN |  | Sceco | 2G NSA | HFF6003 | FLM_TE | [8 empty] | API | 10/21/2025 10:24:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000412 | PCM-20251021-00001091 | TT-20251021-01101 | Telecom | Region_4 | JED2279 | JED2279 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 10:25:24 | 10/21/2025 10:51:41 | 10/21/2025 22:25:24 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at JED2279-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/21/2025 10:16:07 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 10:15:56 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2279 | FLM_TE |  |  | PCM-20251021-00001080 | FLM need to check RFM and perform HC at site. | FLM need to check RFM and perform HC at site. |  |  |  | API | 10/21/2025 10:25:24 | 10/21/2025 10:51:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000415 | PCM-20251021-00001097 | TT-20251021-01114 | Telecom | Region_3 | HAL2U6706C | HAL6006 |  |  |  | Atif Shahzad Muhammad Ajaib | 10/21/2025 10:28:05 | 10/21/2025 10:29:31 | 10/21/2025 22:28:05 | RF Unit Maintenance Link Failure at HAL2U6706C-P3 @ Sceco | 10/21/2025 10:24:21 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 10:22:39 | P3 | 4G | hail | Sceco | 2G NSA | HAL2U6706C | FLM_TE | [8 empty] | API | 10/21/2025 10:28:05 | 10/21/2025 10:29:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000416 | PCM-20251021-00001098 | TT-20251021-01093 | Telecom | Region_4 | SJED0664 | SJED0664 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 10:29:03 | 10/21/2025 10:29:03 | 10/21/2025 22:29:03 | SJED1W0665, SJED1W0666 Complete down | 10/21/2025 10:10:44 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/21/2025 10:10:44 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0665, SJED1W0666 | FLM_EM | SJED0664 | Hub: SJED0664 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00001072 | Hub: SJED0664 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: SJED0664 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/21/2025 10:29:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000417 | PCM-20251021-00001099 | TT-20251021-01116 | EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/21/2025 10:29:06 | 10/22/2025 11:21:13 | 10/21/2025 16:29:06 | Board Temperature Unacceptable at RIY2866-P3_SRAN-PC @ Sceco | 10/21/2025 10:20:17 | Major | 26104 | Board Temperature Unacceptable | 10/21/2025 10:18:44 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/21/2025 10:29:06 | 10/22/2025 11:21:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000418 | PCM-20251021-00001100 | TT-20251021-01117 | Telecom | Region_3 | HAL2U6706C | HAL6006 |  |  |  | Atif Shahzad Muhammad Ajaib | 10/21/2025 10:29:07 | 10/21/2025 10:29:32 | 10/21/2025 16:29:07 | RF Out of Service at HAL2U6706C-P3 @ Sceco | 10/21/2025 10:24:15 | Major | 29248 | RF Out of Service | 10/21/2025 10:22:43 | P3 | 4G | hail | Sceco | 2G SA | HAL2U6706C | FLM_TE | [8 empty] | API | 10/21/2025 10:29:07 | 10/21/2025 10:29:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000424 | PCM-20251021-00001111 | TT-20251021-01130 | EM | Region_1 | SKJF0198 | SKJF0198 | Equipment | PMR_Power_Cable_RRU | Change Port on FPFH | Mahmoud Abdelwanis Massoud Elrashidy | 10/21/2025 10:33:16 | 10/22/2025 11:29:55 | 10/21/2025 16:33:16 | Door opening alarm at SKJF0198-P1-HUB_SRAN @ Generator_DG | 10/21/2025 10:32:47 | Major | 65101 | Door opening alarm | 10/21/2025 10:32:44 | P1 | SRAN | sakaka | Generator_DG | 2G NSA | SKJF0198 | FLM_EM | [8 empty] | API | 10/21/2025 10:33:16 | 10/22/2025 11:29:37 | 10/22/2025 11:29:47 |  |  | 10/22/2025 11:29:55 |  | Mahmoud Abdelwanis Massoud Elrashidy |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000427 | PCM-20251021-00001114 | TT-20251021-01115 | Telecom | Region_6 | BHAB2063 | BHAB2063 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 10:34:23 | 10/21/2025 11:10:40 | 10/21/2025 16:34:23 | 2(2G) 2(LTE) sites down under BHAB2063-P3,BHAB2069-P3/BHAB2069-P3 @ Generator_SG | 10/21/2025 10:24:58 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 10:24:54 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2069-P3 2G_LTE,BHAB2063-P3 2G_LTE | FLM_EM | BHAB2063 | Hub: BHAB2063 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00001110 | Hub: BHAB2063 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: BHAB2063 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/21/2025 10:34:23 | 10/21/2025 11:10:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000428 | PCM-20251021-00001118 | TT-20251021-01136 | Telecom | Region_4 | TAF1M4383 | TAF2383 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 10:36:37 | 10/21/2025 11:06:00 | 10/21/2025 16:36:37 | CELL OPERATION DEGRADED (Failure in optical RP3 interface) at TAF1M4383-P2 @ Sceco | 10/21/2025 10:34:10 | Major | 7654 | CELL OPERATION DEGRADED | 09/05/2025 14:28:21 | P2 | 3G | taif | Sceco | LTE_Cell SA | TAF1M4383 | FLM_TE |  |  | PCM-20251021-00001116 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/21/2025 10:36:37 | 10/21/2025 11:06:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000431 | PCM-20251021-00001123 | TT-20251021-01051 | Telecom | Region_4 | JED0284 | JED0284 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 10:40:24 | 10/21/2025 10:50:35 | 10/21/2025 22:40:24 | CELL SERVICE PROBLEM (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED0284-G9-L8-L18-L21-NNR6-NR2.6-SBTS-P2 @ Sceco | 10/21/2025 09:54:18 | Minor | 7114 | CELL SERVICE PROBLEM | 10/21/2025 09:54:07 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0284 | FLM_TE |  |  | PCM-20251021-00001027 | FLM need to check and clear the below degraded SFP BBMOD-2(ABIO) RF1 | FLM need to check and clear the below degraded SFP BBMOD-2(ABIO) RF1 |  |  |  | API | 10/21/2025 10:40:24 | 10/21/2025 10:50:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000433 | PCM-20251021-00001125 | TT-20251021-01139 | EM | Region_4 | RYMK1M7535 | RYMK0535 | Enviroment | Genset failure_Speed | Change Generator speed sensor | Mohamed Elsaid Abdou Younes | 10/21/2025 10:40:29 | 10/21/2025 14:56:00 | 10/21/2025 16:40:29 | COMMERCIAL POWER FAILURE at RYMK1M7535-L800-P1-SBTS @ Generator_DG | 10/21/2025 10:32:26 | Major | 7103 | COMMERCIAL POWER FAILURE | 10/21/2025 10:32:18 | P1 | 4G | taif | Generator_DG | LTE NSA | RYMK1M7535 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/21/2025 10:40:29 | 10/21/2025 12:28:58 | 10/21/2025 12:29:03 | 10/21/2025 12:29:06 | 10/21/2025 12:30:58 | 10/21/2025 14:56:00 |  | Mohamed Elsaid Abdou Younes |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000435 | PCM-20251021-00001127 | TT-20251021-01143 | Telecom | Region_4 | JED2555 | JED2555 | Equipment | SFP_BTS | Clean SFP | MALIK ATIF ZAMAN | 10/21/2025 10:41:01 | 10/22/2025 15:28:55 | 10/21/2025 14:41:01 | BCCH MISSING at JED2555-P1-VVIP @ Generator_SG | 10/21/2025 10:38:47 | Critical | 7767 | BCCH MISSING | 10/21/2025 10:38:41 | VIP | 2G | jeddah | Generator_SG | 2G_Cell SA | JED2555 | FLM_TE | [5 empty] | 03 |  |  | API | 10/21/2025 10:41:01 | 10/21/2025 18:52:51 | 10/22/2025 12:30:36 | 10/22/2025 12:30:38 | 10/22/2025 12:46:13 | 10/22/2025 15:28:55 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000436 | PCM-20251021-00001130 | TT-20251021-01141 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 10:45:33 | 10/21/2025 21:36:25 | 10/21/2025 16:45:33 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/21/2025 10:37:26 | Major | 22214 | NodeB Unavailable | 10/21/2025 10:37:24 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 10:45:33 | 10/21/2025 21:36:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000437 | PCM-20251021-00001135 | TT-20251021-01155 | Telecom | Region_4 | JED1MN2823 | JED2823 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 10:48:14 | 10/21/2025 10:51:41 | 10/21/2025 16:48:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2823-NR2.6-P3 @ Generator_SG | 10/21/2025 10:47:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 10:47:01 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2823 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 10:48:14 | 10/21/2025 10:51:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000440 | PCM-20251021-00001139 | TT-20251021-01151 | Telecom | Region_4 | SIR1M3050 | SIR0050 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/21/2025 10:50:12 | 10/22/2025 10:50:55 | 10/21/2025 16:50:12 | 1(3G) sites down under SIR0050-P2-USF/SIR1M3050-P2-USF @ Sceco | 10/21/2025 10:42:33 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 10:41:52 | P2 | 3G | adam | Sceco | 3G SA | SIR0050-P2-USF | FLM_TE | SIR0050 | Results: DOWN SITE HUB SIR0050-P2-USF SIR0050 Summary: Hub: SIR0050, Down Count: 1, Down Sites: SIR0050-P2-USF Alarm Summary: SIR0050 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 10:50:12 | 10/22/2025 10:50:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000441 | PCM-20251021-00001144 | TT-20251021-01166 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/21/2025 10:53:10 | 10/21/2025 10:53:10 | 10/21/2025 16:53:10 | Observing Multiple Links Down at RYD-SAIXR0001-NE40E-X8 Connected to Eth-Trunk65(Tencent_CDN) & Eth-Trunk75(Tencent_CDN) | 10/21/2025 10:48:25 | Major | 5000003 | Link Down | 10/21/2025 10:48:25 | P1 | BSC | riyadh | Sceco_STB | TTImpacISPNSA | Observing Multiple Links Down at RYD-SAIXR0001-NE40E-X8 Connected to Eth-Trunk65(Tencent_CDN) & Eth-Trunk75(Tencent_CDN) | FLM_TE | [5 empty] | Observing Multiple Links Down at RYD-SAIXR0001-NE40E-X8 Connected to Eth-Trunk65(Tencent_CDN) & Eth-Trunk75(Tencent_CDN) |  |  | API | 10/21/2025 10:53:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000447 | PCM-20251021-00001153 | TT-20251021-01164 | EM | Region_1 | HFF2M2365 | HFF2365 |  |  |  | Moustafa Mohamed Saleh Saif | 10/21/2025 10:56:33 | 10/21/2025 11:34:15 | 10/21/2025 16:56:33 | 1(2G/3G/LTE) sites down under HFF2365-P2/R1_HF_HWBSC01 @ Sceco | 10/21/2025 10:49:39 | Major | 21825 | CSL Fault | 10/21/2025 10:49:39 | P2 | 2G | hafouf | Sceco | 2G_3G_LTE SA | HFF2365-P2 | FLM_EM | HFF2365 | Results: DOWN SITE HUB HFF2365-P2 HFF2365 Summary: Hub: HFF2365, Down Count: 1, Down Sites: HFF2365-P2 Alarm Summary: HFF2365 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 10:56:33 | 10/21/2025 11:34:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000448 | PCM-20251021-00001158 | TT-20251021-01178 | EM | Region_4 | JZMA1M8413 | JZMA2413 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/21/2025 11:02:10 | 10/22/2025 08:43:24 | 10/21/2025 23:02:10 | RECTIFIER MAJOR ALARM at JZMA1M8413-G9-L8-L18-SBTS-P3-CAP @ Generator_SG | 10/21/2025 10:54:05 | Minor | 7103 | RECTIFIER MAJOR ALARM | 10/21/2025 10:53:56 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8413 | FLM_EM | [5 empty] | RECTIFIER MAJOR ALARM |  |  | API | 10/21/2025 11:02:10 | 10/22/2025 08:43:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251021000449 | PCM-20251021-00001160 | TT-20251021-01180 | EM | [7 empty] | 10/21/2025 11:02:40 | 10/21/2025 11:02:40 | 10/21/2025 23:02:40 | NETECO: Door Status Sensor Alarm at BDR2111 @ Generator_SG | 10/21/2025 11:02:04 | Minor | 5152 | Door Status Sensor Alarm | 10/21/2025 11:02:04 | P3 | SRAN |  | Generator_SG | 2G NSA | BDR2111 | FLM_EM | [8 empty] | API | 10/21/2025 11:02:40 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000450 | PCM-20251021-00001164 | TT-20251021-01183 | Telecom | Region_4 | JED1MN2417 | JED2417 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 11:03:15 | 10/21/2025 12:15:55 | 10/21/2025 17:03:15 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2417-NR2.6-P3 @ Sceco | 10/21/2025 11:02:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 11:02:08 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2417 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 11:03:15 | 10/21/2025 12:15:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000452 | PCM-20251021-00001169 | TT-20251021-01187 | Telecom | Region_4 | JED0739 | JED0739 | Equipment | BSS_HW_fault | Replace Interface Card | Ahmad Mostafa Hamouda Ibrahem | 10/21/2025 11:06:19 | 10/21/2025 17:01:16 | 10/21/2025 23:06:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0739-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 11:05:14 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 11:05:04 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0739 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 11:06:19 | 10/21/2025 16:39:48 | 10/21/2025 16:40:02 | 10/21/2025 16:40:05 | 10/21/2025 16:40:08 | 10/21/2025 17:01:16 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000455 | PCM-20251021-00001176 | TT-20251021-01193 | EM | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Gamal Mohamed Farag | 10/21/2025 11:07:20 | 10/21/2025 11:07:20 | 10/21/2025 23:07:20 | HIGH TEMPERATURE 32 DEGREE C at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/21/2025 10:58:53 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/21/2025 10:58:46 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7558 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/21/2025 11:07:20 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000462 | PCM-20251021-00001188 | TT-20251021-01203 | Reference_telecom | Region_2 | RAS0044 | RAS0044 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/21/2025 11:11:59 | 10/21/2025 12:51:09 | 10/21/2025 23:11:59 | MW_LOF at RAS0044_NE_3 @ Sceco | 10/21/2025 07:11:42 | Minor | 1-631 | MW_LOF | 10/21/2025 07:11:33 | P2 | SRAN | al rass | Sceco | TX NSA | RAS0044 | FLM_TE | [8 empty] | API | 10/21/2025 11:11:59 | 10/21/2025 12:51:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000463 | PCM-20251021-00001187 | TT-20251021-01204 | Telecom | Region_4 | TFBH0807 | TFBH0807 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 11:11:59 | 10/22/2025 17:29:57 | 10/21/2025 17:11:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at TFBH0807-GSM-P3 @ Sceco | 10/21/2025 11:11:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 11:11:11 | P3 | 2G | taif | Sceco | 5G_Cell SA | TFBH0807 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 11:11:59 | 10/22/2025 17:29:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000464 | PCM-20251021-00001189 | TT-20251021-01196 | EM | Region_4 | JED2635 | JED2635 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 11:14:02 | 10/21/2025 18:52:52 | 10/21/2025 17:14:02 | 1(2G/5G) sites down under JED2635-P3/JED2635-P3 @ Sceco | 10/21/2025 11:05:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 11:05:44 | P3 | 2G | jeddah | Sceco | 2G SA | JED2635-P3 | FLM_TE | JED2635 | Results: DOWN SITE HUB JED2635-P3 JED2635 Summary: Hub: JED2635, Down Count: 1, Down Sites: JED2635-P3 Alarm Summary: JED2635 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 11:14:02 | 10/21/2025 18:52:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000465 | PCM-20251021-00001190 | TT-20251021-01206 | EM | Region_6 | ABBS1M8174 | ABBS2174 |  |  |  | Muhammad Naeem Taj Din | 10/21/2025 11:14:04 | 10/21/2025 15:32:33 | 10/21/2025 23:14:04 | SHELTER DOOR OPEN at ABBS1M8174-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 11:13:36 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 11:13:31 | P3 | 4G | namas | Generator_SG | LTE NSA | ABBS1M8174 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 11:14:04 | 10/21/2025 15:32:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251021000467 | PCM-20251021-00001192 | TT-20251021-01211 | Telecom | Region_4 | JED1M7498 | JED0498 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 11:16:03 | 10/21/2025 17:56:47 | 10/21/2025 17:16:03 | PT:: FLM Need to perform HC at JED1M7498 under R4 (BO Request) | 10/21/2025 11:15:38 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 11:15:38 | P1 | 4G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED1M7498 | FLM_TE | [8 empty] | API | 10/21/2025 11:16:03 | 10/21/2025 12:28:25 | 10/21/2025 17:36:54 | 10/21/2025 17:45:27 | 10/21/2025 17:56:47 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000469 | PCM-20251021-00001198 | TT-20251021-01216 | Reference_telecom | Region_4 | SJED1S7018 | SJED0018 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 11:18:36 | 10/21/2025 18:52:52 | 10/21/2025 15:18:36 | BASE STATION OPERATION DEGRADED (BTS reference clock missing: GPS receiver alarm: not tracking satellites) at SJED1S7018-CA-P1-ARP-HAJJ-VIP @ Sceco | 10/21/2025 11:14:33 | Critical | 7651 | BASE STATION OPERATION DEGRADED | 10/21/2025 11:04:29 | VIP | 4G | jeddah | Sceco | LTE NSA | SJED1S7018 | FLM_TE |  |  | PCM-20251021-00001196 | TOP IP 10.88.254.4 NOT WORKING | TOP IP 10.88.254.4 NOT WORKING |  |  |  | API | 10/21/2025 11:18:36 | 10/21/2025 18:52:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000470 | PCM-20251021-00001206 | TT-20251021-01210 | Telecom | Region_4 | JED1M8108 | JED2108 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 11:19:32 | 10/21/2025 12:28:25 | 10/21/2025 17:19:32 | 1(LTE) sites down under JED2108-P3-L800-CA @ Sceco | 10/21/2025 11:11:27 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 11:11:24 | P3 | 4G | jeddah | Sceco | LTE SA | JED2108-P3-L800-CA | FLM_TE | JED2108 | Results: DOWN SITE HUB JED2108-P3-L800-CA JED2108 Summary: Hub: JED2108, Down Count: 1, Down Sites: JED2108-P3-L800-CA Alarm Summary: JED2108 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.112.252:8080] [URL:http://10.96.112.252:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 11:19:32 | 10/21/2025 12:28:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000472 | PCM-20251021-00001208 | TT-20251021-01224 | Telecom | Region_5 | HAJ0092 | HAJ0092 |  |  |  | HUSSEIN MOHAMED ABDELRAHMAN ELAZZAB | 10/21/2025 11:20:46 | 10/24/2025 01:40:12 | 10/21/2025 23:20:46 | ALD Maintenance Link Failure at HAJ0092-P1_SRAN @ Sceco | 10/21/2025 11:17:47 | Minor | 26541 | ALD Maintenance Link Failure | 10/21/2025 11:16:11 | P1 | SRAN | makkah | Sceco | 2G NSA | HAJ0092 | FLM_TE | [8 empty] | API | 10/21/2025 11:20:46 | 10/24/2025 01:40:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000473 | PCM-20251021-00001209 | TT-20251021-01212 | EM | Region_6 | NJR1U6318 | NJR6018 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/21/2025 11:21:06 | 10/22/2025 01:25:25 | 10/21/2025 17:21:06 | 1(3G/LTE/5G) sites down under NJR6018-P3/NJR1U6318-P3 @ Sceco | 10/21/2025 11:13:12 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 11:12:31 | P3 | 3G | najran | Sceco | 3G_LTE_5G SA | NJR6018-P3 | FLM_EM | NJR6018 | Results: DOWN SITE HUB NJR6018-P3 NJR6018 Summary: Hub: NJR6018, Down Count: 1, Down Sites: NJR6018-P3 Alarm Summary: NJR6018 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 11:21:06 | 10/21/2025 12:40:17 | 10/22/2025 01:25:15 |  |  | 10/22/2025 01:25:25 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000474 | PCM-20251021-00001211 | TT-20251021-01226 | EM | Region_4 | RYMK1M7544 | RYMK0544 |  |  |  | Farghal Ashour Hassan Farghal | 10/21/2025 11:21:17 | 10/21/2025 12:33:10 | 10/21/2025 23:21:17 | HIGH TEMPERATURE 32 DEGREE C at RYMK1M7544-L800-P2-USF @ Sceco | 10/21/2025 11:13:10 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/21/2025 11:13:01 | P2 | 4G | taif | Sceco | LTE NSA | RYMK1M7544 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/21/2025 11:21:17 | 10/21/2025 12:33:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000477 | PCM-20251021-00001218 | TT-20251021-01235 | MW_HC | Region_6 | DRB0910 | DRB0910 | Transsmission | MW_Connectors | Replace Outdoor MW Connector | Muhammad Usman Muhammad Zia ul haq | 10/21/2025 11:26:09 | 10/21/2025 18:50:55 | 10/21/2025 23:26:09 | As BO Requested MW Nokia Observing Still counting errors For MW Link DRB0910-JDJZ0785 | 10/21/2025 11:24:39 | Minor | 113388 | LOF | 10/21/2025 11:24:41 | P1 | 2G | derb | Sceco_STB | TX NSA | DRB0910-JDJZ0785 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing Still counting errors For MW Link DRB0910-JDJZ0785 |  |  | API | 10/21/2025 11:26:09 | 10/21/2025 15:08:09 | 10/21/2025 15:19:27 | 10/21/2025 15:19:30 | 10/21/2025 15:19:32 | 10/21/2025 18:50:55 |  | Muhammad Usman Muhammad Zia ul haq |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000479 | PCM-20251021-00001222 | TT-20251021-01239 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/21/2025 11:28:32 | 10/21/2025 11:28:32 | 10/21/2025 15:28:32 | Generator Failure(SH1) at R2_RY2_HWBSC01 @ Sceco_STB | 10/21/2025 11:28:13 | Critical | 65346 | Generator Failure(SH1) | 10/21/2025 11:28:09 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/21/2025 11:28:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000480 | PCM-20251021-00001223 | TT-20251021-01240 | EM | Region_4 | JED1M7335 | JED0335 |  |  |  | Ramadan Mohamed Sabri Mohamed | 10/21/2025 11:30:05 | 10/21/2025 11:30:05 | 10/21/2025 23:30:05 | HIGH TEMPERATURE 32 DEGREE C at JED1M7335-CA-L900-L800-SBTS @ Sceco | 10/21/2025 11:22:03 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/21/2025 11:21:54 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7335 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/21/2025 11:30:05 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251021000481 | PCM-20251021-00001225 | TT-20251021-01242 | EM | [7 empty] | 10/21/2025 11:30:36 | 10/21/2025 11:30:36 | 10/21/2025 15:30:36 | DOOR OPEN at SABYA-SEC0014_HYB @ Sceco | 10/21/2025 11:30:08 | Critical | 1-12307 | DOOR OPEN | 10/21/2025 11:29:59 | P1 | DWDM |  | Sceco | DWDM NSA | SABYA | FLM_EM | [5 empty] | 0-TO SHUQAIQ-SEC0019(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/21/2025 11:30:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000487 | PCM-20251021-00001235 | TT-20251021-01254 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/21/2025 11:36:16 | 10/21/2025 12:01:18 | 10/21/2025 17:36:16 | high temprature 32 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/21/2025 11:25:50 | Major | 65102 | high temprature 32 | 10/21/2025 11:25:46 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/21/2025 11:36:16 | 10/21/2025 12:01:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000488 | PCM-20251021-00001236 | TT-20251021-01096 | EM | Region_4 | SQR0055 | SQR0055 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/21/2025 11:36:48 | 10/21/2025 19:30:17 | 10/21/2025 17:36:48 | 1(2G/3G/5G) sites down under SQR0055-P2-USF/SQR0055-P2-USF @ Generator_SG | 10/21/2025 10:13:29 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 10:13:25 | P2 | 2G | alaith | Generator_SG | 2G_3G_5G SA | SQR0055-P2-USF | FLM_TE | SQR0055 | Results: DOWN SITE HUB SQR0055-P2-USF SQR0055 Summary: Hub: SQR0055, Down Count: 1, Down Sites: SQR0055-P2-USF Alarm Summary: SQR0055 No Active Alarm on HUB | PCM-20251021-00001082 | No Power Issue | No Power Issue |  | sites down |  | API | 10/21/2025 11:36:48 | 10/21/2025 19:28:15 | 10/21/2025 19:30:00 |  |  | 10/21/2025 19:30:17 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000489 | PCM-20251021-00001237 | TT-20251021-01256 | EM | Region_6 | BHAB1M8055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 11:37:18 | 10/21/2025 15:46:57 | 10/21/2025 23:37:18 | SHELTER DOOR OPEN at BHAB1M8055-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/21/2025 11:36:49 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 11:36:44 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAB1M8055 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 11:37:18 | 10/21/2025 15:46:57 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000490 | PCM-20251021-00001241 | TT-20251021-01260 | EM | Region_2 | R2_RY2_HWBSC01 | RY2 |  |  |  | Farhat Saeed Pirzada | 10/21/2025 11:38:19 | 10/21/2025 11:38:19 | 10/21/2025 15:38:19 | Gen set running(SH1) at R2_RY2_HWBSC01 @ Sceco_STB | 10/21/2025 11:38:11 | Critical | 65344 | Gen set running(SH1) | 10/21/2025 11:38:06 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY2_HWBSC01 | FLM_EM | [8 empty] | API | 10/21/2025 11:38:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000494 | PCM-20251021-00001245 | TT-20251021-01263 | EM | Region_6 | RYAB0622 | RYAB0622 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Muhammad Bilal Niamat Ali | 10/21/2025 11:39:22 | 10/21/2025 14:06:49 | 10/21/2025 17:39:22 | RECTIFIER MAINS POWER FAILURE at RYAB0622-GSM-UMTS-P1-HUB @ Sceco_STB | 10/21/2025 11:31:10 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 11:31:04 | P1 | 2G | sulail | Sceco_STB | 2G NSA | RYAB0622 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 11:39:22 | 10/21/2025 12:34:07 | 10/21/2025 12:51:25 | 10/21/2025 12:51:31 | 10/21/2025 12:51:35 | 10/21/2025 14:06:49 |  | Muhammad Bilal Niamat Ali |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000495 | PCM-20251021-00001249 | TT-20251021-01251 | Telecom | Region_5 | MKMD1M7551 | MKMD0551 |  |  |  | Amr Abdulla Ali Othman | 10/21/2025 11:40:32 | 10/21/2025 11:40:32 | 10/21/2025 17:40:32 | 1(LTE) sites down under MKMD0551-L800-SBTS @ Generator_DG | 10/21/2025 11:32:06 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 11:32:03 | P2 | 4G | makkah | Generator_DG | LTE SA | MKMD0551-L800-SBTS | FLM_TE | MKMD0551 | Results: DOWN SITE HUB MKMD0551-L800-SBTS MKMD0551 Summary: Hub: MKMD0551, Down Count: 1, Down Sites: MKMD0551-L800-SBTS Alarm Summary: MKMD0551 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.160.196:8080] [URL:http://10.98.160.196:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 11:40:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000497 | PCM-20251021-00001254 | TT-20251021-01272 | Telecom | Region_4 | JED0930 | JED0930 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/21/2025 11:42:29 | 10/21/2025 13:57:08 | 10/21/2025 17:42:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0930-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/21/2025 11:41:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 11:41:26 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0930 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 11:42:29 | 10/21/2025 11:49:43 | 10/21/2025 13:57:02 |  |  | 10/21/2025 13:57:08 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000499 | PCM-20251021-00001256 | TT-20251021-01275 | Telecom | Region_4 | GMK2154 | GMK2154 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 11:44:01 | 10/22/2025 13:09:26 | 10/21/2025 23:44:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at GMK2154-G9-L8-L18-L21-NNR2.6-SBTS-P3 @ Generator_SG | 10/21/2025 11:43:21 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 11:43:12 | P3 | 2G | jeddah | Generator_SG | 5G_Cell SA | GMK2154 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 11:44:01 | 10/22/2025 13:09:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000501 | PCM-20251021-00001258 | TT-20251021-01264 | EM | Region_4 | SHB1M3670 | SHB0670 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 11:45:04 | 10/22/2025 13:09:27 | 10/21/2025 17:45:04 | 1(2G/3G/LTE) sites down under SHB0670-P3/SHB1M3670-P3 @ Sceco | 10/21/2025 11:37:30 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 11:36:49 | P3 | 3G | qunfuddah | Sceco | 3G SA | SHB0670-P3 | FLM_TE | SHB0670 | Results: DOWN SITE HUB SHB0670-P3 SHB0670 Summary: Hub: SHB0670, Down Count: 1, Down Sites: SHB0670-P3 Alarm Summary: SHB0670 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 11:45:04 | 10/22/2025 13:09:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000504 | PCM-20251021-00001268 | TT-20251021-01287 | EM | Region_6 | KMBS1M8304 | KMBS2304 |  |  |  | Asad Saddiq | 10/21/2025 11:48:09 | 10/21/2025 15:19:50 | 10/21/2025 23:48:09 | SHELTER DOOR OPEN at KMBS1M8304-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/21/2025 11:47:59 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 11:47:49 | P3 | 4G | bisha | Generator_SG | LTE NSA | KMBS1M8304 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 11:48:09 | 10/21/2025 15:19:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000511 | PCM-20251021-00001284 | TT-20251021-01302 | Telecom | Region_4 | SHB1M7670 | SHB0670 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 11:59:00 | 10/22/2025 13:09:28 | 10/21/2025 23:59:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at SHB1M7670-G9-L18-SBTS-P3 @ Sceco | 10/21/2025 11:58:24 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 11:58:13 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | SHB1M7670 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 11:59:00 | 10/22/2025 13:09:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000513 | PCM-20251021-00001287 | TT-20251021-01103 | Telecom | Region_3 | HAL2029 | HAL2029 | Transsmission | CB_MW | Replace DCDU Fuse | Atif Shahzad Muhammad Ajaib | 10/21/2025 12:01:51 | 10/21/2025 12:42:30 | 10/21/2025 18:01:51 | 3(2G) 2(3G) 2(LTE) sites down under HAL0905-P2,HAL2946-P3,HAL2029-P3/R3_HL_HWBSC01 @ Sceco | 10/21/2025 10:20:26 | Major | 21825 | CSL Fault | 10/21/2025 10:20:21 | P3 | SRAN | hail | Sceco | 2G_3G_LTE SA | HAL0905-P2 2G_3G_LTE,HAL2946-P3 2G_LTE,HAL2029-P3 2G_3G | FLM_TE | HAL2029 | Hub:- HAL2029 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251021-00001101 | No Power Issue | No Power Issue |  | sites down |  | API | 10/21/2025 12:01:51 | 10/21/2025 12:19:02 | 10/21/2025 12:26:54 | 10/21/2025 12:26:57 | 10/21/2025 12:26:59 | 10/21/2025 12:42:30 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000517 | PCM-20251021-00001294 | TT-20251021-01311 | EM | Region_6 | BHAB1M8055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 12:08:49 | 10/21/2025 15:46:58 | 10/22/2025 00:08:49 | RECTIFIER MAINS POWER FAILURE at BHAB1M8055-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/21/2025 12:00:26 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 12:00:14 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAB1M8055 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 12:08:49 | 10/21/2025 15:46:58 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000519 | PCM-20251021-00001298 | TT-20251021-01318 | Telecom | Region_5 | MAK1M9992 | MAK0992 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 12:13:59 | 10/21/2025 12:13:59 | 10/21/2025 18:13:59 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9992-P1-VIP-HRM-CA-L800-SBTS @ Sceco | 10/21/2025 12:13:05 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 12:12:56 | VIP | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9992 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 12:13:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000522 | PCM-20251021-00001315 | TT-20251021-01334 | EM | Region_1 | SMRY0816 | SMRY0816 |  |  |  | Samir Elzain Abdu Gumaa | 10/21/2025 12:17:37 | 10/21/2025 12:17:37 | 10/22/2025 00:17:37 | Door opening alarm at SMRY0816-P2_SRAN @ Generator_SG | 10/21/2025 12:17:23 | Minor | 65101 | Door opening alarm | 10/21/2025 12:17:19 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0816 | FLM_EM | [8 empty] | API | 10/21/2025 12:17:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000523 | PCM-20251021-00001317 | TT-20251016-02518 | Reference_telecom | Region_4 | JED2138 | JED2138 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:18:41 | 10/21/2025 18:52:53 | 10/22/2025 00:18:41 | FanFailure observed in JED2138 towards 10.3.225.37 @ Sceco | 10/16/2025 11:17:44 | Minor |  | FanFailure | 10/16/2025 11:17:40 | P3 | 2G | jeddah | Sceco | TX NSA | JED2138 | FLM_TE |  |  | PCM-20251021-00001267 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/21/2025 12:18:41 | 10/21/2025 18:52:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000526 | PCM-20251021-00001324 | TT-20251021-01344 | Telecom | Region_4 | JED1M7692 | JED0692 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:24:19 | 10/21/2025 18:52:53 | 10/21/2025 18:24:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7692-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/21/2025 12:23:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 12:23:33 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7692 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 12:24:19 | 10/21/2025 18:52:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000528 | PCM-20251021-00001327 | TT-20251021-01340 | EM | Region_4 | JED1M8178 | JED2178 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:25:02 | 10/22/2025 11:26:31 | 10/21/2025 18:25:02 | 1(2G/LTE) sites down under JED2178-P3 @ Sceco | 10/21/2025 12:16:32 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 12:16:29 | P3 | 4G | jeddah | Sceco | LTE SA | JED2178-P3-CA-L800 | FLM_TE | JED2178 | Results: DOWN SITE HUB JED2178-P3-CA-L800 JED2178 Summary: Hub: JED2178, Down Count: 1, Down Sites: JED2178-P3-CA-L800 Alarm Summary: JED2178 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.96.16.44:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 12:25:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000532 | PCM-20251021-00001334 | TT-20251021-01357 | Telecom | Region_5 | MAK2129 | MAK2129 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:28:58 | 10/21/2025 19:57:10 | 10/22/2025 00:28:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2129-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/21/2025 12:28:20 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 12:28:09 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2129 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 12:28:58 | 10/21/2025 19:57:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000533 | PCM-20251021-00001336 | TT-20251021-01358 | EM | Region_1 | JBL2937 | JBL2937 |  |  |  | Hamid Bilal Bashir Ahmed | 10/21/2025 12:30:00 | 10/21/2025 15:31:24 | 10/22/2025 00:30:00 | Door opening alarm at JBL2937-P3_SRAN @ Sceco | 10/21/2025 12:29:31 | Minor | 65101 | Door opening alarm | 10/21/2025 12:29:27 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL2937 | FLM_EM | [8 empty] | API | 10/21/2025 12:30:00 | 10/21/2025 15:31:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000537 | PCM-20251021-00001345 | TT-20251021-01369 | Telecom | Region_2 | RY3 | RY3 |  |  |  | Saddam hussain muhammad khan | 10/21/2025 12:33:07 | 10/22/2025 12:18:51 | 10/21/2025 16:33:07 | STC : LINK DOWN B/W RY3-RIY0283 & RIY0462 -- RIY0788 | 10/21/2025 12:32:37 | Critical | 1-12843 | OSC_LOS | 10/21/2025 12:32:25 | P1 | BSC | riyadh | Sceco_STB | DWDM NSA | RY3 | FLM_TE | [5 empty] | 0-1-C-2-F1AST4-1(RM1/TM1(FROM RIY0283))-OSC:1 |  |  | API | 10/21/2025 12:33:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000539 | PCM-20251021-00001347 | TT-20251021-01372 | Telecom | Region_2 | RIY0459-ZRi02-3-CSG-03 | RIY0459 |  |  |  | Farmanullah Akbar Jan | 10/21/2025 12:33:29 | 10/21/2025 12:46:52 | 10/21/2025 18:33:29 | DWDM_Alarm of failed LAG negotiation at RIY0459-ZRi02-3-CSG-03 @ Sceco | 10/21/2025 12:32:55 | Major | 101-1102218 | Alarm of failed LAG negotiation | 10/21/2025 12:32:26 | P1 | IPRAN | riyadh | Sceco | IPRAN SA | RIY0459-ZRi02-3-CSG-03 | FLM_TE | [8 empty] | API | 10/21/2025 12:33:29 | 10/21/2025 12:46:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000541 | PCM-20251021-00001350 | TT-20251021-01376 | Reference_telecom | Region_1 | KBR2U6764 | KBR6064 |  |  |  | Meraj Husain Idd Baksh | 10/21/2025 12:35:10 | 10/21/2025 14:26:20 | 10/21/2025 18:35:10 | RF Unit VSWR Threshold Crossed at KBR2U6764-P1-VIP @ Sceco | 10/21/2025 09:35:10 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 09:34:59 | VIP | 4G | dammam | Sceco | LTE NSA | KBR2U6764 | FLM_TE | [8 empty] | API | 10/21/2025 12:35:10 | 10/21/2025 14:26:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000542 | PCM-20251021-00001351 | TT-20251021-01366 | Reference_telecom | Region_1 | HFF2U6728 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 12:35:14 | 10/21/2025 14:55:15 | 10/22/2025 00:35:14 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6728-P3 @ Sceco | 10/21/2025 09:32:26 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/21/2025 09:32:21 | P3 | 4G | hafouf | Sceco | 2G NSA | HFF2U6728 | FLM_TE |  | Dears Kindly check HW | PCM-20251021-00001343 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/21/2025 12:35:14 | 10/21/2025 14:23:18 | 10/21/2025 14:55:02 |  |  | 10/21/2025 14:55:15 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000547 | PCM-20251021-00001359 | TT-20251021-01383 | Reference_telecom | Region_1 | KBR2U6763 | KBR6063 |  |  |  | Meraj Husain Idd Baksh | 10/21/2025 12:37:16 | 10/21/2025 14:26:21 | 10/21/2025 18:37:16 | RF Unit VSWR Threshold Crossed at KBR2U6763-P3 @ Sceco | 10/21/2025 09:37:00 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 09:36:47 | P3 | 4G | dammam | Sceco | LTE NSA | KBR2U6763 | FLM_TE | [8 empty] | API | 10/21/2025 12:37:16 | 10/21/2025 14:26:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000548 | PCM-20251021-00001360 | TT-20251021-01384 | Telecom | Region_1 | JBL2M4394 | JBL2394 | Equipment | BSS_HW_Stuck | Reset RRU | Rafiq Ahmed Elturifi | 10/21/2025 12:37:29 | 10/21/2025 12:50:09 | 10/21/2025 18:37:29 | UMTS Cell Unavailable at JBL2M4394-P2 @ Sceco | 10/21/2025 12:36:07 | Major | 22202 | UMTS Cell Unavailable | 10/21/2025 12:36:01 | P2 | 3G | jubail | Sceco | 3G SA | JBL2M4394 | FLM_TE | [8 empty] | API | 10/21/2025 12:37:29 | 10/21/2025 12:49:34 | 10/21/2025 12:50:00 |  |  | 10/21/2025 12:50:09 |  | Rafiq Ahmed Elturifi |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000549 | PCM-20251021-00001362 | TT-20251021-01386 | EM | Region_4 | HHR0614 | HHR0614 |  |  |  | Aly Ahmed Aly Sawy | 10/21/2025 12:38:16 | 10/21/2025 12:38:16 | 10/21/2025 18:38:16 | RECTIFIER MAINS POWER FAILURE at HHR0614-GSM-UMTS-P1-VIP-HHR @ Sceco | 10/21/2025 12:29:52 | Major | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 12:29:41 | VIP | 2G | jeddah | Sceco | 2G NSA | HHR0614 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 12:38:16 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000551 | PCM-20251021-00001365 | TT-20251021-01389 | MW_HC | Region_4 | RAB2123 | RAB2123 |  |  |  | Khizer Hayat | 10/21/2025 12:38:32 | 10/21/2025 14:05:40 | 10/22/2025 00:38:32 | Nokia MW HC_P2 Observing Performance Issue at RAB2123_03-RAB2154 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | RAB2123_03-RAB2154 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:32 | 10/21/2025 14:05:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000552 | PCM-20251021-00001366 | TT-20251021-01390 | MW_HC | Region_4 | JED2985 | JED2985 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 12:38:33 | 10/21/2025 19:40:39 | 10/22/2025 00:38:33 | Nokia MW HC_P2 Observing Modem Down at JED2985 -JED0411 _6 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2985 -JED0411 _6 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:33 | 10/21/2025 19:40:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000553 | PCM-20251021-00001367 | TT-20251021-01391 | MW_HC | Region_4 | BHR2551 | BHR2551 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:38:34 | 10/21/2025 13:18:04 | 10/22/2025 00:38:34 | Nokia MW HC_P1 Observing Performance Issue at BHR2551-JED0001 _12 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Generator_SG | TX NSA | BHR2551-JED0001 _12 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:34 | 10/21/2025 13:18:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000554 | PCM-20251021-00001368 | TT-20251021-01392 | MW_HC | Region_6 | BAH0832 | BAH0832 |  |  |  | SHAH KHALID | 10/21/2025 12:38:36 | 10/21/2025 14:15:38 | 10/22/2025 00:38:36 | Nokia MW HC_P1 Observing Performance Issue at BAH0832-BAH0831_2 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | Albaha | Sceco | TX NSA | BAH0832-BAH0831_2 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:36 | 10/21/2025 14:15:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000556 | PCM-20251021-00001370 | TT-20251021-01394 | MW_HC | Region_6 | BHAB0816 | BHAB0816 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 12:38:38 | 10/21/2025 14:01:19 | 10/22/2025 00:38:38 | Nokia MW HC_P0 Observing Performance Issue at BHAB0816_01-BHAB0817_01 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | abha | Sceco_STB | TX NSA | BHAB0816_01-BHAB0817_01 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:38 | 10/21/2025 14:01:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000557 | PCM-20251021-00001371 | TT-20251021-01395 | MW_HC | Region_4 | JED2601 | JED2601 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:38:39 | 10/21/2025 18:52:54 | 10/22/2025 00:38:39 | Nokia MW HC_P0 Observing Performance Issue at JED2601-JED2602_02 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2601-JED2602_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:39 | 10/21/2025 18:52:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000559 | PCM-20251021-00001373 | TT-20251021-01397 | MW_HC | Region_4 | JED2183 | JED2183 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:38:41 | 10/21/2025 18:52:54 | 10/22/2025 00:38:41 | Nokia MW HC_P2 Observing Performance Issue at JED2183-JED0564 _03 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2183-JED0564 _03 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:41 | 10/21/2025 18:52:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000560 | PCM-20251021-00001374 | TT-20251021-01398 | MW_HC | Region_4 | JED2140 | JED2140 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:38:42 | 10/21/2025 18:52:55 | 10/22/2025 00:38:42 | Nokia MW HC_P2 Observing Performance Issue at JED2140_01-JED2034_03 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P2 | 2G | jeddah | Sceco | TX NSA | JED2140_01-JED2034_03 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:42 | 10/21/2025 18:52:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251021000561 | PCM-20251021-00001375 | TT-20251021-01399 | MW_HC | Region_6 | BNT0082 | BNT0082 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/21/2025 12:38:44 | 10/21/2025 15:04:14 | 10/22/2025 00:38:44 | Nokia MW HC_P1 Observing Performance Issue at BNT0082-TND0130 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P1 | 2G | khamis mushyet | Sceco_STB | TX NSA | BNT0082-TND0130 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:44 | 10/21/2025 12:45:44 | 10/21/2025 15:04:07 | 10/21/2025 15:04:14 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000562 | PCM-20251021-00001376 | TT-20251021-01400 | MW_HC | Region_4 | JED2158 | JED2158 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:38:45 | 10/21/2025 13:12:18 | 10/22/2025 00:38:45 | Nokia MW HC_P1 Observing Performance Issue at JED2158-JED2126 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2158-JED2126 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:45 | 10/21/2025 13:12:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000563 | PCM-20251021-00001377 | TT-20251021-01401 | MW_HC | Region_4 | JED0194 | JED0194 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:38:46 | 10/21/2025 12:38:46 | 10/22/2025 00:38:46 | Nokia MW HC_P0 Observing Performance Issue at JED0194-JED0116-6 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P2 | 2G | jeddah | Sceco | TX NSA | JED0194-JED0116-6 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000564 | PCM-20251021-00001379 | TT-20251021-01403 | MW_HC | Region_4 | RNY0658 | RNY0658 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 12:38:47 | 10/22/2025 17:29:58 | 10/22/2025 00:38:47 | Nokia MW HC_P2 Observing Performance Issue at RNY0658_1-RNRY0339_02 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | VIP | 2G | taif | Sceco | TX NSA | RNY0658_1-RNRY0339_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:47 | 10/22/2025 17:29:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000566 | PCM-20251021-00001381 | TT-20251021-01404 | MW_HC | Region_4 | JED2903 | JED2903 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:38:50 | 10/21/2025 18:52:55 | 10/22/2025 00:38:50 | Nokia MW HC_P0 Observing Performance Issue at JED2903-JED0862_02 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2903-JED0862_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:50 | 10/21/2025 18:52:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000567 | PCM-20251021-00001382 | TT-20251021-01405 | MW_HC | Region_4 | JED2168 | JED2168 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:38:51 | 10/21/2025 12:38:51 | 10/22/2025 00:38:51 | Nokia MW HC_P2 Observing Performance Issue at JED2168-JED0341 _ 16 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2168-JED0341 _ 16 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000568 | PCM-20251021-00001383 | TT-20251021-01406 | MW_HC | Region_4 | JED2126 | JED2126 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:38:52 | 10/21/2025 13:12:20 | 10/22/2025 00:38:52 | Nokia MW HC_P2 Observing Performance Issue at JED2126-JED0285-5 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2126-JED0285-5 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:52 | 10/21/2025 13:12:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000569 | PCM-20251021-00001384 | TT-20251021-01407 | MW_HC | Region_4 | JED2823 | JED2823 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 12:38:53 | 10/21/2025 19:40:39 | 10/22/2025 00:38:53 | Nokia MW HC_P0 Observing Performance Issue at JED2823-JED0416 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2823-JED0416 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:53 | 10/21/2025 19:40:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000570 | PCM-20251021-00001385 | TT-20251021-01408 | MW_HC | Region_4 | JDMD0862 | JDMD0862 |  |  |  | Nazeer Mohammed | 10/21/2025 12:38:54 | 10/22/2025 10:26:31 | 10/22/2025 00:38:54 | Nokia MW HC_P0 Observing Performance Issue at JDMD0862_01-JDMD0859-2 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P2 | 2G | jeddah | Generator_DG | TX NSA | JDMD0862_01-JDMD0859-2 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:54 | 10/22/2025 10:26:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000571 | PCM-20251021-00001386 | TT-20251021-01409 | MW_HC | Region_4 | JED0375 | JED0375 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:38:55 | 10/21/2025 18:52:56 | 10/22/2025 00:38:55 | Nokia MW HC_P0 Observing Performance Issue at JED0375-JED0449 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0375-JED0449 | FLM_TE | [8 empty] | API | 10/21/2025 12:38:55 | 10/21/2025 18:52:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000575 | PCM-20251021-00001390 | TT-20251021-01413 | MW_HC | Region_4 | JED2249 | JED2249 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:39:00 | 10/21/2025 12:39:00 | 10/22/2025 00:39:00 | Nokia MW HC_P0 Observing Performance Issue at JED2249-JED0095-10 | 10/21/2025 12:34:22 | Minor |  | LOF | 10/21/2025 12:34:22 | P3 | 2G | jeddah | Sceco | TX NSA | JED2249-JED0095-10 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000577 | PCM-20251021-00001391 | TT-20251021-01414 | MW_HC | Region_4 | JED2215 | JED2215 |  |  |  | Nazeer Mohammed | 10/21/2025 12:39:02 | 10/22/2025 10:26:32 | 10/22/2025 00:39:02 | Nokia MW HC_P0 Observing Performance Issue at JED2215-JED2288 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2215-JED2288 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:02 | 10/22/2025 10:26:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251021000578 | PCM-20251021-00001392 | TT-20251021-01415 | MW_HC | Region_4 | JED0170 | JED0170 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/21/2025 12:39:03 | 10/23/2025 11:42:00 | 10/22/2025 00:39:03 | Nokia MW HC_P1 Observing Performance Issue at JED0170-JED2012 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0170-JED2012 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:03 | 10/23/2025 11:27:04 | 10/23/2025 11:41:50 | 10/23/2025 11:41:53 | 10/23/2025 11:42:00 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000579 | PCM-20251021-00001393 | TT-20251021-01416 | MW_HC | Region_4 | JED2106 | JED2106 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 12:39:04 | 10/21/2025 19:40:40 | 10/22/2025 00:39:04 | Nokia MW HC_P2 Observing Performance Issue at JED2106-JED0307 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2106-JED0307 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:04 | 10/21/2025 19:40:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000580 | PCM-20251021-00001394 | TT-20251021-01417 | MW_HC | Region_4 | TAF0285 | TAF0285 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 12:39:05 | 10/22/2025 17:29:58 | 10/22/2025 00:39:05 | Nokia MW HC_P1 Observing Performance Issue at TAF0285-TAF0144 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | taif | Sceco | TX NSA | TAF0285-TAF0144 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:05 | 10/22/2025 17:29:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000581 | PCM-20251021-00001395 | TT-20251021-01418 | MW_HC | Region_4 | JED0560 | JED0560 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:39:07 | 10/21/2025 18:52:56 | 10/22/2025 00:39:07 | Nokia MW HC_P2 Observing Performance Issue at JED0560-JED0778 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | VIP | 2G | jeddah | Sceco | TX NSA | JED0560-JED0778 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:07 | 10/21/2025 18:52:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000582 | PCM-20251021-00001396 | TT-20251021-01419 | MW_HC | Region_4 | JED0236 | JED0236 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:39:08 | 10/21/2025 12:39:08 | 10/22/2025 00:39:08 | Nokia MW HC_P0 Observing Performance Issue at JED0236-JED0898 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0236-JED0898 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000583 | PCM-20251021-00001397 | TT-20251021-01420 | MW_HC | Region_4 | JED0086 | JED0086 | Equipment | BSS_HW_fault | Replace RF Module | Ahmad Mostafa Hamouda Ibrahem | 10/21/2025 12:39:10 | 10/22/2025 19:45:30 | 10/22/2025 00:39:10 | Nokia MW HC_P1 Observing Performance Issue at JED0086_15-JED0254 _02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | VIP | 2G | jeddah | Sceco | TX NSA | JED0086_15-JED0254 _02 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:10 | 10/22/2025 10:45:36 | 10/22/2025 11:15:20 | 10/22/2025 11:15:22 | 10/22/2025 11:15:33 | 10/22/2025 19:45:30 |  | Ahmad Mostafa Hamouda Ibrahem |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000584 | PCM-20251021-00001398 | TT-20251021-01421 | MW_HC | Region_6 | RTH0954 | RTH0954 |  |  |  | Muhammad Ali | 10/21/2025 12:39:11 | 10/21/2025 14:39:35 | 10/22/2025 00:39:11 | Nokia MW HC_P0 Observing Performance Issue at RTH0954_01-RTH9801_03 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | raith | Sceco | TX NSA | RTH0954_01-RTH9801_03 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:11 | 10/21/2025 14:39:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000586 | PCM-20251021-00001400 | TT-20251021-01423 | MW_HC | Region_4 | JED0599 | JED0599 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:39:15 | 10/21/2025 18:52:57 | 10/22/2025 00:39:15 | Nokia MW HC_P0 Observing Performance Issue at JED0599-JED0604_10 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0599-JED0604_10 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:15 | 10/21/2025 18:52:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251021000587 | PCM-20251021-00001401 | TT-20251021-01424 | MW_HC | Region_4 | JED2273 | JED2273 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/21/2025 12:39:16 | 10/23/2025 16:22:57 | 10/22/2025 00:39:16 | Nokia MW HC_P1 Observing Performance Issue at JED2273_FTK-JED0978 FTK | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2273_FTK-JED0978 FTK | FLM_TE | [8 empty] | API | 10/21/2025 12:39:16 | 10/23/2025 16:18:09 | 10/23/2025 16:22:49 | 10/23/2025 16:22:54 | 10/23/2025 16:22:57 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000588 | PCM-20251021-00001402 | TT-20251021-01425 | MW_HC | Region_6 | AHM0097 | AHM0097 |  |  |  | Zeshan Ali Adnan | 10/21/2025 12:39:17 | 10/21/2025 12:44:48 | 10/22/2025 00:39:17 | Nokia MW HC_P0 Observing Performance Issue at AHM0097-AHM0036_02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jizan | Sceco | TX NSA | AHM0097-AHM0036_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:17 | 10/21/2025 12:44:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000590 | PCM-20251021-00001404 | TT-20251021-01427 | MW_HC | Region_4 | JED0793 | JED0793 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:39:21 | 10/21/2025 12:39:21 | 10/22/2025 00:39:21 | Nokia MW HC_P1 Observing Performance Issue at JED0793_1-JED0347-NE6 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0793_1-JED0347-NE6 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:21 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000592 | PCM-20251021-00001406 | TT-20251021-01429 | MW_HC | Region_4 | TAF0342 | TAF0342 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 12:39:23 | 10/22/2025 07:52:53 | 10/22/2025 00:39:23 | Nokia MW HC_P1 Observing Performance Issue at TAF0342_01-TAF0340_03 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | taif | Sceco | TX NSA | TAF0342_01-TAF0340_03 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:23 | 10/22/2025 07:52:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000593 | PCM-20251021-00001407 | TT-20251021-01430 | MW_HC | Region_4 | JED0848 | JED0848 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:39:24 | 10/21/2025 13:18:05 | 10/22/2025 00:39:24 | Nokia MW HC_P0 Observing Performance Issue at JED0848-JED2573_03 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0848-JED2573_03 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:24 | 10/21/2025 13:18:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000594 | PCM-20251021-00001408 | TT-20251021-01431 | MW_HC | Region_5 | MAK0073 | MAK0073 |  |  |  | Mosab Nasr eldeen Mohamed | 10/21/2025 12:39:26 | 10/21/2025 21:37:03 | 10/22/2025 00:39:26 | Nokia MW HC_P0 Observing Performance Issue at MAK0073-01-MAK0195-02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | makkah | Sceco | TX NSA | MAK0073-01-MAK0195-02 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:26 | 10/21/2025 21:37:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000596 | PCM-20251021-00001410 | TT-20251021-01433 | MW_HC | Region_5 | MAK0532 | MAK0532 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:39:29 | 10/21/2025 19:57:11 | 10/22/2025 00:39:29 | Nokia MW HC_P2 Observing Performance Issue at MAK0532-MAK0014_18 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0532-MAK0014_18 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:29 | 10/21/2025 19:57:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000597 | PCM-20251021-00001411 | TT-20251021-01434 | MW_HC | Region_4 | JED2704 | JED2704 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:39:29 | 10/21/2025 12:39:29 | 10/22/2025 00:39:29 | Nokia MW HC_P2 Observing Performance Issue at JED2704_01-JED0980_02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2704_01-JED0980_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000598 | PCM-20251021-00001412 | TT-20251021-01435 | MW_HC | Region_4 | JED0241 | JED0241 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:39:31 | 10/21/2025 12:39:31 | 10/22/2025 00:39:31 | Nokia MW HC_P2 Observing Modem Down at JED0241-JED0854 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0241-JED0854 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000599 | PCM-20251021-00001413 | TT-20251021-01436 | MW_HC | Region_4 | JED2171 | JED2171 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:39:32 | 10/21/2025 13:18:06 | 10/22/2025 00:39:32 | Nokia MW HC_P1 Observing Performance Issue at JED2171-JED2039_03 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2171-JED2039_03 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:32 | 10/21/2025 13:18:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000601 | PCM-20251021-00001415 | TT-20251021-01438 | MW_HC | Region_5 | ABU0315 | ABU0315 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:39:34 | 10/21/2025 19:57:12 | 10/22/2025 00:39:34 | Nokia MW HC_P1 Observing Performance Issue at ABU0315_01-JUM0323_02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | ABU0315_01-JUM0323_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:34 | 10/21/2025 19:57:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000604 | PCM-20251021-00001418 | TT-20251021-01441 | MW_HC | Region_4 | JED0797 | JED0797 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:39:38 | 10/21/2025 13:18:06 | 10/22/2025 00:39:38 | Nokia MW HC_P0 Observing Performance Issue at JED0797-01-BHR0318 -11 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0797-01-BHR0318 -11 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:38 | 10/21/2025 13:18:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000605 | PCM-20251021-00001419 | TT-20251021-01442 | MW_HC | Region_4 | TAF0271 | TAF0271 |  |  |  | Rashid Shafique | 10/21/2025 12:39:39 | 10/21/2025 16:17:01 | 10/22/2025 00:39:39 | Nokia MW HC_P2 Observing Performance Issue at TAF0271-TAF0283-7 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | taif | Sceco | TX NSA | TAF0271-TAF0283-7 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:39 | 10/21/2025 16:17:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000607 | PCM-20251021-00001421 | TT-20251021-01444 | MW_HC | Region_6 | NJR0264 | NJR0264 |  |  |  | TALEH MUHAMMAD | 10/21/2025 12:39:41 | 10/21/2025 17:41:37 | 10/22/2025 00:39:41 | Nokia MW HC_P0 Observing Performance Issue at NJR0264-2-NJR0234 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | najran | Sceco | TX NSA | NJR0264-2-NJR0234 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:41 | 10/21/2025 17:41:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000608 | PCM-20251021-00001422 | TT-20251021-01445 | MW_HC | Region_6 | NJR0037 | NJR0037 |  |  |  | TALEH MUHAMMAD | 10/21/2025 12:39:42 | 10/21/2025 17:41:38 | 10/22/2025 00:39:42 | Nokia MW HC_P1 Observing Performance Issue at NJR0037-NJR0026 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | najran | Sceco | TX NSA | NJR0037-NJR0026 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:42 | 10/21/2025 17:41:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000609 | PCM-20251021-00001423 | TT-20251021-01446 | MW_HC | Region_4 | MKJD0571 | MKJD0571 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:39:43 | 10/21/2025 13:18:07 | 10/22/2025 00:39:43 | Nokia MW HC_P2 Observing Performance Issue at MKJD0571-JED0001 -15 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco_STB | TX NSA | MKJD0571-JED0001 -15 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:43 | 10/21/2025 13:18:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000610 | PCM-20251021-00001424 | TT-20251021-01447 | MW_HC | Region_5 | MK3 | MAK3 |  |  |  | Muhammad Zubair | 10/21/2025 12:39:44 | 10/21/2025 12:39:44 | 10/22/2025 00:39:44 | Nokia MW HC_P1 Observing Performance Issue at MK3-35-MAK0265-2 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | DWDM | makkah | Sceco_STB | TX NSA | MK3-35-MAK0265-2 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000613 | PCM-20251021-00001427 | TT-20251021-01450 | MW_HC | Region_5 | MAK0936 | MAK0936 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 12:39:48 | 10/21/2025 12:39:48 | 10/22/2025 00:39:48 | Nokia MW HC_P1 Observing Performance Issue at MAK0936-FTK-MAK0536 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | makkah | Sceco | TX NSA | MAK0936-FTK-MAK0536 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:48 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000614 | PCM-20251021-00001428 | TT-20251021-01452 | MW_HC | Region_5 | MAK0856 | MAK0856 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:39:49 | 10/21/2025 19:57:13 | 10/22/2025 00:39:49 | Nokia MW HC_P0 Observing Performance Issue at MAK0856-MAK0058 - 5 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | makkah | Sceco | TX NSA | MAK0856-MAK0058 - 5 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:49 | 10/21/2025 19:57:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000615 | PCM-20251021-00001429 | TT-20251021-01451 | EM | Region_4 | HHR0489 | HHR0489 |  |  |  | Anas Mohamedelamin Abbas Mustafa | 10/21/2025 12:39:50 | 10/21/2025 23:34:31 | 10/21/2025 18:39:50 | SHELTER DOOR OPEN at HHR0489-P1-VIP-HHR @ Generator_SG | 10/21/2025 12:39:40 | Major | 7103 | SHELTER DOOR OPEN | 10/21/2025 12:39:33 | VIP | 2G | jeddah | Generator_SG | 2G NSA | HHR0489 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 12:39:50 | 10/21/2025 23:34:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000616 | PCM-20251021-00001430 | TT-20251021-01453 | MW_HC | Region_5 | MAK0737 | MAK0737 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 12:39:50 | 10/21/2025 12:39:50 | 10/22/2025 00:39:50 | Nokia MW HC_P2 Observing Performance Issue at MAK0737-MAK0765 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | VIP | 2G | makkah | Sceco | TX NSA | MAK0737-MAK0765 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000617 | PCM-20251021-00001431 | TT-20251021-01454 | MW_HC | Region_5 | MAK0692 | MAK0692 |  |  |  | Mosab Nasr eldeen Mohamed | 10/21/2025 12:39:51 | 10/21/2025 21:37:03 | 10/22/2025 00:39:51 | Nokia MW HC_P1 Observing Performance Issue at MAK0692-MAK0065_03 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0692-MAK0065_03 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:51 | 10/21/2025 21:37:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000618 | PCM-20251021-00001432 | TT-20251021-01455 | MW_HC | Region_5 | MAK0660 | MAK0660 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:39:53 | 10/21/2025 19:57:13 | 10/22/2025 00:39:53 | Nokia MW HC_P0 Observing Performance Issue at MAK0660-MAK0615_04 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | makkah | Sceco | TX NSA | MAK0660-MAK0615_04 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:53 | 10/21/2025 19:57:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000619 | PCM-20251021-00001433 | TT-20251021-01456 | MW_HC | Region_5 | MAK0643 | MAK0643 |  |  |  | Amjad Ali Muhammad Parves | 10/21/2025 12:39:54 | 10/22/2025 09:40:28 | 10/22/2025 00:39:54 | Nokia MW HC_P0 Observing Performance Issue at MAK0643_01-MAK0251_11 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0643_01-MAK0251_11 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:54 | 10/22/2025 09:40:28 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000620 | PCM-20251021-00001434 | TT-20251021-01457 | MW_HC | Region_5 | MAK0620 | MAK0620 |  |  |  | Mosab Nasr eldeen Mohamed | 10/21/2025 12:39:55 | 10/21/2025 21:37:04 | 10/22/2025 00:39:55 | Nokia MW HC_P1 Observing Performance Issue at MAK0620-MAK0082 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0620-MAK0082 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:55 | 10/21/2025 21:37:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000621 | PCM-20251021-00001435 | TT-20251021-01458 | MW_HC | Region_5 | MAK0598 | MAK0598 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 12:39:56 | 10/21/2025 12:39:56 | 10/22/2025 00:39:56 | Nokia MW HC_P0 Observing Performance Issue at MAK0598-MAK0001-8 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0598-MAK0001-8 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000622 | PCM-20251021-00001436 | TT-20251021-01459 | MW_HC | Region_5 | MAK0542 | MAK0542 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:39:57 | 10/21/2025 19:57:14 | 10/22/2025 00:39:57 | Nokia MW HC_P2 Observing Performance Issue at MAK0542-MAK0538-11 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0542-MAK0538-11 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:57 | 10/21/2025 19:57:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000623 | PCM-20251021-00001437 | TT-20251021-01460 | MW_HC | Region_5 | MAK0540 | MAK0540 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 12:39:58 | 10/21/2025 12:39:58 | 10/22/2025 00:39:58 | Nokia MW HC_P2 Observing Modem Down at MAK0540-MAK0010-3 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | VIP | 2G | makkah | Sceco | TX NSA | MAK0540-MAK0010-3 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000624 | PCM-20251021-00001438 | TT-20251021-01461 | MW_HC | Region_5 | MAK0531 | MAK0531 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 12:39:59 | 10/21/2025 12:39:59 | 10/22/2025 00:39:59 | Nokia MW HC_P1 Observing Performance Issue at MAK0531-MAK2087-4 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0531-MAK2087-4 | FLM_TE | [8 empty] | API | 10/21/2025 12:39:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000625 | PCM-20251021-00001439 | TT-20251021-01462 | MW_HC | Region_5 | MAK0473 | MAK0473 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 12:40:00 | 10/21/2025 12:40:00 | 10/22/2025 00:40:00 | Nokia MW HC_P2 Observing Performance Issue at MAK0473-MAK0011-10 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | makkah | Sceco | TX NSA | MAK0473-MAK0011-10 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000626 | PCM-20251021-00001440 | TT-20251021-01463 | MW_HC | Region_5 | MAK0452 | MAK0452 |  |  |  | Muhammad Shabbir Muhammad | 10/21/2025 12:40:02 | 10/21/2025 12:40:02 | 10/22/2025 00:40:02 | Nokia MW HC_P2 Observing Performance Issue at MAK0452-MAK0038-8 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | makkah | Generator_SG | TX NSA | MAK0452-MAK0038-8 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000628 | PCM-20251021-00001443 | TT-20251021-01465 | MW_HC | Region_5 | MAK0261 | MAK0261 |  |  |  | Husain Hassan Ishag Omer | 10/21/2025 12:40:05 | 10/22/2025 01:12:57 | 10/22/2025 00:40:05 | Nokia MW HC_P1 Observing Performance Issue at MAK0261-MAK0030-4 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0261-MAK0030-4 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:05 | 10/22/2025 01:12:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000631 | PCM-20251021-00001446 | TT-20251021-01468 | MW_HC | Region_5 | MAK0119 | MAK0119 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 12:40:08 | 10/21/2025 12:40:08 | 10/22/2025 00:40:08 | Nokia MW HC_P1 Observing Performance Issue at MAK0119-01-MAK0610-7 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | makkah | Sceco | TX NSA | MAK0119-01-MAK0610-7 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000632 | PCM-20251021-00001447 | TT-20251021-01469 | MW_HC | Region_5 | MAK0117 | MAK0117 |  |  |  | Husain Hassan Ishag Omer | 10/21/2025 12:40:10 | 10/22/2025 01:12:57 | 10/22/2025 00:40:10 | Nokia MW HC_P1 Observing Performance Issue at MAK0117-1-MAK0005-9 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | makkah | Sceco | TX NSA | MAK0117-1-MAK0005-9 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:10 | 10/22/2025 01:12:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000633 | PCM-20251021-00001448 | TT-20251021-01470 | MW_HC | Region_5 | MAK0075 | MAK0075 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 12:40:10 | 10/21/2025 12:40:10 | 10/22/2025 00:40:10 | Nokia MW HC_P1 Observing Performance Issue at MAK0075-MAK0076 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0075-MAK0076 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:10 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000634 | PCM-20251021-00001449 | TT-20251021-01471 | MW_HC | Region_5 | MAK0069 | MAK0069 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/21/2025 12:40:13 | 10/21/2025 12:40:13 | 10/22/2025 00:40:13 | Nokia MW HC_P0 Observing Performance Issue at MAK0069-1-MAK0033 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0069-1-MAK0033 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000635 | PCM-20251021-00001450 | TT-20251021-01472 | MW_HC | Region_5 | MAK0065 | MAK0065 |  |  |  | Khamis Mosaad Moursy Shaboun | 10/21/2025 12:40:14 | 10/21/2025 12:40:14 | 10/22/2025 00:40:14 | Nokia MW HC_P0 Observing Performance Issue at MAK0065_1-MK2_41 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0065_1-MK2_41 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000637 | PCM-20251021-00001452 | TT-20251021-01474 | MW_HC | Region_5 | MAK0027 | MAK0027 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 12:40:17 | 10/21/2025 12:40:17 | 10/22/2025 00:40:17 | Nokia MW HC_P0 Observing Performance Issue at MAK0027-1-MAK0060 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | makkah | Sceco | TX NSA | MAK0027-1-MAK0060 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000638 | PCM-20251021-00001453 | TT-20251021-01475 | MW_HC | Region_5 | MAK0013 | MAK0013 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 12:40:18 | 10/21/2025 19:57:15 | 10/22/2025 00:40:18 | Nokia MW HC_P2 Observing Performance Issue at MAK0013-MAK0741_02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0013-MAK0741_02 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:18 | 10/21/2025 19:57:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251021000639 | PCM-20251021-00001454 | TT-20251021-01476 | MW_HC | Region_6 | KMS2147 | KMS2147 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/21/2025 12:40:20 | 10/21/2025 15:04:23 | 10/22/2025 00:40:20 | Nokia MW HC_P2 Observing Performance Issue at KMS2147_2-KMS0046 _1 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KMS2147_2-KMS0046 _1 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:20 | 10/21/2025 12:45:44 | 10/21/2025 15:04:19 | 10/21/2025 15:04:23 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Departed | CM20251021000640 | PCM-20251021-00001455 | TT-20251021-01477 | MW_HC | Region_6 | KMS0033 | KMS0033 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/21/2025 12:40:21 | 10/21/2025 21:40:15 | 10/22/2025 00:40:21 | Nokia MW HC_P0 Observing Performance Issue at KMS0033-KMS0508 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS0033-KMS0508 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:21 | 10/21/2025 12:45:45 | 10/21/2025 21:40:12 | 10/21/2025 21:40:15 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000642 | PCM-20251021-00001457 | TT-20251021-01479 | MW_HC | Region_4 | JED2191 | JED2191 |  |  |  | Nazeer Mohammed | 10/21/2025 12:40:23 | 10/22/2025 10:26:33 | 10/22/2025 00:40:23 | Nokia MW HC_P0 Observing Performance Issue at JED2191_01-JED0723 -6 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | VIP | 2G | jeddah | Sceco | TX NSA | JED2191_01-JED0723 -6 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:23 | 10/22/2025 10:26:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000644 | PCM-20251021-00001458 | TT-20251021-01480 | MW_HC | Region_4 | JED2170 | JED2170 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:40:24 | 10/21/2025 13:18:07 | 10/22/2025 00:40:24 | Nokia MW HC_P1 Observing Performance Issue at JED2170-JED0909 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2170-JED0909 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:24 | 10/21/2025 13:18:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000645 | PCM-20251021-00001459 | TT-20251021-01481 | MW_HC | Region_4 | JED2061 | JED2061 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:25 | 10/21/2025 18:52:57 | 10/22/2025 00:40:25 | Nokia MW HC_P0 Observing Performance Issue at JED2061-JED0604-4 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2061-JED0604-4 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:25 | 10/21/2025 18:52:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000646 | PCM-20251021-00001460 | TT-20251021-01482 | MW_HC | Region_4 | JED2058 | JED2058 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:40:27 | 10/21/2025 13:12:21 | 10/22/2025 00:40:27 | Nokia MW HC_P2 Observing Performance Issue at JED2058-JED0567 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED2058-JED0567 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:27 | 10/21/2025 13:12:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000647 | PCM-20251021-00001461 | TT-20251021-01483 | MW_HC | Region_4 | JED2049 | JED2049 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:40:29 | 10/21/2025 13:12:21 | 10/22/2025 00:40:29 | Nokia MW HC_P2 Observing Performance Issue at JED2049-FTK-JED0997 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED2049-FTK-JED0997 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:29 | 10/21/2025 13:12:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000648 | PCM-20251021-00001462 | TT-20251021-01484 | MW_HC | Region_4 | JED2016 | JED2016 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:40:30 | 10/21/2025 12:40:30 | 10/22/2025 00:40:30 | Nokia MW HC_P0 Observing Performance Issue at JED2016-JED0365 - 9 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2016-JED0365 - 9 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:30 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000649 | PCM-20251021-00001463 | TT-20251021-01485 | MW_HC | Region_4 | JED2006 | JED2006 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:40:32 | 10/21/2025 12:40:32 | 10/22/2025 00:40:32 | Nokia MW HC_P1 Observing Performance Issue at JED2006-FTK-JED0276-6 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED2006-FTK-JED0276-6 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000651 | PCM-20251021-00001465 | TT-20251021-01487 | MW_HC | Region_4 | JED0943 | JED0943 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:35 | 10/21/2025 18:52:58 | 10/22/2025 00:40:35 | Nokia MW HC_P0 Observing Performance Issue at JED0943-JED0604-5 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0943-JED0604-5 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:35 | 10/21/2025 18:52:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000652 | PCM-20251021-00001466 | TT-20251021-01488 | MW_HC | Region_4 | JED0887 | JED0887 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:40:37 | 10/21/2025 12:40:37 | 10/22/2025 00:40:37 | Nokia MW HC_P1 Observing Performance Issue at JED0887-JED0092 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0887-JED0092 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:37 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000653 | PCM-20251021-00001467 | TT-20251021-01489 | MW_HC | Region_4 | JED0886 | JED0886 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:40:38 | 10/21/2025 12:40:38 | 10/22/2025 00:40:38 | Nokia MW HC_P2 Observing Performance Issue at JED0886-JED0103 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0886-JED0103 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000654 | PCM-20251021-00001468 | TT-20251021-01490 | MW_HC | Region_4 | JED0844 | JED0844 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:39 | 10/21/2025 18:52:58 | 10/22/2025 00:40:39 | Nokia MW HC_P1 Observing Performance Issue at JED0844_1-JED0676 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0844_1-JED0676 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:39 | 10/21/2025 18:52:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000655 | PCM-20251021-00001469 | TT-20251021-01491 | MW_HC | Region_4 | JED0782 | JED0782 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 12:40:40 | 10/21/2025 13:18:08 | 10/22/2025 00:40:40 | Nokia MW HC_P2 Observing Performance Issue at JED0782-JED0134-10 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0782-JED0134-10 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:40 | 10/21/2025 13:18:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000656 | PCM-20251021-00001470 | TT-20251021-01492 | MW_HC | Region_4 | JED0777 | JED0777 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 12:40:42 | 10/21/2025 19:40:41 | 10/22/2025 00:40:42 | Nokia MW HC_P0 Observing Performance Issue at JED0777-JED0038-NE8 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0777-JED0038-NE8 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:42 | 10/21/2025 19:40:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000657 | PCM-20251021-00001471 | TT-20251021-01493 | MW_HC | Region_4 | JED0734 | JED0734 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:43 | 10/21/2025 18:52:58 | 10/22/2025 00:40:43 | Nokia MW HC_P0 Observing Performance Issue at JED0734-JED0604-7 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0734-JED0604-7 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:43 | 10/21/2025 18:52:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000659 | PCM-20251021-00001473 | TT-20251021-01495 | MW_HC | Region_4 | JED0603 | JED0603 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:45 | 10/21/2025 18:52:59 | 10/22/2025 00:40:45 | Nokia MW HC_P0 Observing Performance Issue at JED0603-JED0435-10 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0603-JED0435-10 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:45 | 10/21/2025 18:52:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000660 | PCM-20251021-00001474 | TT-20251021-01496 | MW_HC | Region_4 | JED0559 | JED0559 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:47 | 10/21/2025 18:52:59 | 10/22/2025 00:40:47 | Nokia MW HC_P1 Observing Performance Issue at JED0559-JED0435-8 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED0559-JED0435-8 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:47 | 10/21/2025 18:52:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000661 | PCM-20251021-00001475 | TT-20251021-01497 | MW_HC | Region_4 | JED0495 | JED0495 |  |  |  | Nazeer Mohammed | 10/21/2025 12:40:48 | 10/22/2025 10:26:33 | 10/22/2025 00:40:48 | Nokia MW HC_P1 Observing Performance Issue at JED0495-JED2191_04 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0495-JED2191_04 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:48 | 10/22/2025 10:26:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000662 | PCM-20251021-00001476 | TT-20251021-01498 | MW_HC | Region_4 | JED0431 | JED0431 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:40:49 | 10/21/2025 12:40:49 | 10/22/2025 00:40:49 | Nokia MW HC_P1 Observing Performance Issue at JED0431_09-JED0063 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | jeddah | Sceco | TX NSA | JED0431_09-JED0063 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000663 | PCM-20251021-00001477 | TT-20251021-01499 | MW_HC | Region_4 | JED0430 | JED0430 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:50 | 10/21/2025 18:53:00 | 10/22/2025 00:40:50 | Nokia MW HC_P1 Observing Performance Issue at JED0430-01-JED0127-10 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0430-01-JED0127-10 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:50 | 10/21/2025 18:53:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000665 | PCM-20251021-00001480 | TT-20251021-01502 | MW_HC | Region_4 | JED0363 | JED0363 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:40:52 | 10/21/2025 12:40:52 | 10/22/2025 00:40:52 | Nokia MW HC_P0 Observing Performance Issue at JED0363-JED0017 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0363-JED0017 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:52 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000666 | PCM-20251021-00001481 | TT-20251021-01503 | MW_HC | Region_4 | JED0349 | JED0349 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:40:53 | 10/21/2025 12:40:53 | 10/22/2025 00:40:53 | Nokia MW HC_P1 Observing Performance Issue at JED0349-JED0347-9 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0349-JED0347-9 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000667 | PCM-20251021-00001482 | TT-20251021-01504 | MW_HC | Region_4 | JED0337 | JED0337 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:40:55 | 10/21/2025 18:53:00 | 10/22/2025 00:40:55 | Nokia MW HC_P0 Observing Performance Issue at JED0337-JED0604-8 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0337-JED0604-8 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:55 | 10/21/2025 18:53:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000668 | PCM-20251021-00001483 | TT-20251021-01505 | MW_HC | Region_4 | JED0153 | JED0153 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:40:56 | 10/21/2025 12:40:56 | 10/22/2025 00:40:56 | Nokia MW HC_P0 Observing Performance Issue at JED0153-JED0065-NE5 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0153-JED0065-NE5 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000669 | PCM-20251021-00001484 | TT-20251021-01506 | MW_HC | Region_6 | ARS0125 | ARS0125 |  |  |  | Zeshan Ali Adnan | 10/21/2025 12:40:57 | 10/21/2025 12:44:49 | 10/22/2025 00:40:57 | Nokia MW HC_P1 Observing Performance Issue at ARS0125-ARS0017_07 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jizan | Sceco | TX NSA | ARS0125-ARS0017_07 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:57 | 10/21/2025 12:44:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000670 | PCM-20251021-00001485 | TT-20251021-01507 | MW_HC | Region_4 | JED0223 | JED0223 |  |  |  | Nazeer Mohammed | 10/21/2025 12:40:58 | 10/22/2025 10:26:34 | 10/22/2025 00:40:58 | Nokia MW HC_P0 Observing Performance Issue at JED0223 -1-JED0723-9 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | jeddah | Sceco_STB | TX NSA | JED0223 -1-JED0723-9 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:58 | 10/22/2025 10:26:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000671 | PCM-20251021-00001486 | TT-20251021-01508 | MW_HC | Region_4 | JED0181 | JED0181 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:40:59 | 10/21/2025 12:40:59 | 10/22/2025 00:40:59 | Nokia MW HC_P2 Observing Performance Issue at JED0181-14-JD1_34 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | jeddah | Sceco | TX NSA | JED0181-14-JD1_34 | FLM_TE | [8 empty] | API | 10/21/2025 12:40:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000673 | PCM-20251021-00001488 | TT-20251021-01510 | MW_HC | Region_6 | ABH0527 | ABH0527 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 12:41:02 | 10/21/2025 14:01:21 | 10/22/2025 00:41:02 | Nokia MW HC_P2 Observing Performance Issue at ABH0527-ABH0525 _02 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | abha | Sceco | TX NSA | ABH0527-ABH0525 _02 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:02 | 10/21/2025 14:01:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000674 | PCM-20251021-00001489 | TT-20251021-01511 | MW_HC | Region_4 | JED0167 | JED0167 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 12:41:04 | 10/21/2025 18:53:01 | 10/22/2025 00:41:04 | Nokia MW HC_P0 Observing Performance Issue at JED0167-JED0559 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0167-JED0559 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:04 | 10/21/2025 18:53:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000675 | PCM-20251021-00001490 | TT-20251021-01512 | MW_HC | Region_4 | JED0171 | JED0171 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:41:05 | 10/21/2025 13:12:24 | 10/22/2025 00:41:05 | Nokia MW HC_P0 Observing Performance Issue at JED0171-1-JED0121-8 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | jeddah | Sceco | TX NSA | JED0171-1-JED0121-8 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:05 | 10/21/2025 13:12:24 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000679 | PCM-20251021-00001494 | TT-20251021-01516 | MW_HC | Region_4 | JED0088 | JED0088 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:41:10 | 10/21/2025 13:12:25 | 10/22/2025 00:41:10 | Nokia MW HC_P1 Observing Performance Issue at JED0088-JED0129-4 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | jeddah | Sceco | TX NSA | JED0088-JED0129-4 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:10 | 10/21/2025 13:12:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000680 | PCM-20251021-00001495 | TT-20251021-01517 | MW_HC | Region_5 | HAS0678 | HAS0678 |  |  |  | Amjad Ali Muhammad Parves | 10/21/2025 12:41:11 | 10/22/2025 09:40:29 | 10/22/2025 00:41:11 | Nokia MW HC_P1 Observing Performance Issue at HAS0678_01-MAK0643_01 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | HAS0678_01-MAK0643_01 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:11 | 10/22/2025 09:40:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000681 | PCM-20251021-00001496 | TT-20251021-01518 | MW_HC | Region_4 | JED0327 | JED0327 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 12:41:12 | 10/21/2025 12:41:12 | 10/22/2025 00:41:12 | Nokia MW HC_P1 Observing Performance Issue at JED0327-JED0765 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0327-JED0765 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:12 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000682 | PCM-20251021-00001497 | TT-20251021-01519 | MW_HC | Region_4 | JED0313 | JED0313 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 12:41:14 | 10/21/2025 12:41:14 | 10/22/2025 00:41:14 | Nokia MW HC_P2 Observing Modem Down at JED0313-JED0114 -4 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0313-JED0114 -4 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:14 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000683 | PCM-20251021-00001498 | TT-20251021-01520 | MW_HC | Region_4 | JED0047 | JED0047 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:41:15 | 10/21/2025 13:12:25 | 10/22/2025 00:41:15 | Nokia MW HC_P1 Observing Performance Issue at JED0047-JED0332-9 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0047-JED0332-9 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:15 | 10/21/2025 13:12:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000684 | PCM-20251021-00001499 | TT-20251021-01521 | MW_HC | Region_4 | JED0283 | JED0283 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 12:41:16 | 10/21/2025 13:12:26 | 10/22/2025 00:41:16 | Nokia MW HC_P1 Observing Performance Issue at JED0283-JED0155-14 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P1 | 2G | jeddah | Sceco | TX NSA | JED0283-JED0155-14 | FLM_TE | [8 empty] | API | 10/21/2025 12:41:16 | 10/21/2025 13:12:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000690 | PCM-20251021-00001511 | TT-20251021-01534 | Telecom | Region_4 | JED1M8037 | JED2037 | Equipment | SFP_BTS | Replace SFP | Khaled Mohammad Abdallah | 10/21/2025 12:48:06 | 10/22/2025 02:31:24 | 10/22/2025 00:48:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8037-CA-L800-P2-SBTS @ Sceco | 10/21/2025 12:47:08 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 12:46:59 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8037 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 12:48:06 | 10/21/2025 21:58:02 | 10/21/2025 23:56:19 | 10/21/2025 23:56:22 | 10/21/2025 23:56:24 | 10/22/2025 02:31:24 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000695 | PCM-20251021-00001522 | TT-20251021-01546 | Telecom | Region_1 | HFB0031 | HFB0031 | Equipment | BSS_HW_fault | Replace UPEU Card | Imran Ali Yousaf | 10/21/2025 12:53:29 | 10/21/2025 17:51:46 | 10/22/2025 00:53:29 | HC for HFB0031 | 10/21/2025 12:52:35 | Minor | 676767672 | Health Check-WO to TE FME | 10/21/2025 12:52:37 | P1 | SRAN | hafouf | Generator_SG | 2G NSA | HFB0031 | FLM_TE | [8 empty] | API | 10/21/2025 12:53:29 | 10/21/2025 16:45:52 | 10/21/2025 16:46:06 | 10/21/2025 16:46:11 | 10/21/2025 16:46:18 | 10/21/2025 17:51:46 |  | Imran Ali Yousaf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000698 | PCM-20251021-00001533 | TT-20251021-01556 | Reference_telecom | Region_1 | ARM9885 | ARM9885 |  |  |  | Mahmoud Abdulaziz Mahmoud Khalaf Allah | 10/21/2025 12:56:53 | 10/21/2025 14:50:38 | 10/22/2025 00:56:53 | ETH_LOS at ARM9885_NE_1_VRRP @ Sceco | 10/21/2025 08:56:55 | Minor | 1-235 | ETH_LOS | 10/21/2025 08:56:45 |  | Repeater | jubail | Sceco | TX NSA | ARM9885 | FLM_TE | [8 empty] | API | 10/21/2025 12:56:53 | 10/21/2025 14:50:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000699 | PCM-20251021-00001537 | TT-20251021-01561 | Telecom | Region_4 | TAF1MC2418 | TAF2418 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 12:58:25 | 10/22/2025 17:29:59 | 10/21/2025 18:58:25 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connector) at TAF1MC2418-NR3.5-VIP @ Sceco | 10/21/2025 12:53:46 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 12:53:42 | VIP | 5G | taif | Sceco | 5G_Cell SA | TAF1MC2418 | FLM_TE | [5 empty] | Increased BER detected on the optical connector |  |  | API | 10/21/2025 12:58:25 | 10/22/2025 17:29:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000700 | PCM-20251021-00001538 | TT-20251021-01562 | Reference_telecom | Region_2 | RIY0747 | RIY0747 |  |  |  | Farmanullah Akbar Jan | 10/21/2025 12:58:56 | 10/21/2025 13:20:37 | 10/22/2025 00:58:56 | MW_LOF at RIY0747_NE_7_V @ Sceco | 10/21/2025 08:58:56 | Minor | 1-631 | MW_LOF | 10/21/2025 08:58:42 | P2 | SRAN | riyadh | Sceco | TX NSA | RIY0747 | FLM_TE | [8 empty] | API | 10/21/2025 12:58:56 | 10/21/2025 13:20:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000704 | PCM-20251021-00001544 | TT-20251021-01565 | Telecom | Region_5 | MAK2709 | MAK2709 |  |  |  | Husain Hassan Ishag Omer | 10/21/2025 13:01:00 | 10/22/2025 01:12:57 | 10/21/2025 19:01:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2709-G9-L8-L18-L21-NR2.6-SBTS @ Sceco | 10/21/2025 13:00:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 13:00:02 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2709 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 13:01:00 | 10/22/2025 01:12:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000707 | PCM-20251021-00001552 | TT-20251021-01317 | Telecom | Region_4 | JED2569 | JED2569 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 13:05:45 | 10/21/2025 18:53:02 | 10/21/2025 19:05:45 | 3(2G) 3(LTE) 3(5G) sites down under JED2569-P3,JED2322-P3,JED2296-P3/JED2296-P3 @ Sceco | 10/21/2025 12:07:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 12:07:52 | P3 | 2G | jeddah | Sceco | 2G_LTE SA | JED2322-P3 2G_LTE_5G,JED2569-P3 2G_LTE,JED2296-P3 2G_LTE | FLM_TE | JED2569 | Hub: JED2569 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00001323 | No Power Issue | No Power Issue |  | sites down |  | API | 10/21/2025 13:05:45 | 10/21/2025 18:53:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000708 | PCM-20251021-00001558 | TT-20251021-01583 | Telecom | Region_4 | JED0822 | JED0822 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/21/2025 13:10:49 | 10/22/2025 10:29:22 | 10/22/2025 01:10:49 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0822-G9-L8-L18-L21-NR2.6-SBTS-P2-USF @ Sceco | 10/21/2025 13:10:06 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 13:10:00 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0822 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 13:10:49 | 10/22/2025 10:26:34 | 10/22/2025 10:29:17 |  |  | 10/22/2025 10:29:22 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000714 | PCM-20251021-00001566 | TT-20251021-01591 | Telecom | Region_1 | DAM2178 | DAM2178 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/21/2025 13:17:12 | 10/21/2025 14:29:44 | 10/21/2025 19:17:12 | BBU CPRI Optical Module or Electrical Port Not Ready at DAM2178-P2_SRAN @ Sceco | 10/21/2025 00:49:03 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 10/21/2025 00:47:30 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2178 | FLM_TE | [8 empty] | API | 10/21/2025 13:17:12 | 10/21/2025 14:29:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000716 | PCM-20251021-00001569 | TT-20251021-01594 | Telecom | Region_5 | MAK1M9646 | MAK0646 |  |  |  | Amjad Ali Muhammad Parves | 10/21/2025 13:18:34 | 10/22/2025 09:40:30 | 10/21/2025 19:18:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9646-CA-L800-P2 @ Sceco | 10/21/2025 13:17:38 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 13:17:33 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9646 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 13:18:34 | 10/22/2025 09:40:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000719 | PCM-20251021-00001574 | TT-20251021-01599 | EM | Region_4 | JZMA1M8414 | JZMA2414 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/21/2025 13:21:10 | 10/22/2025 08:43:24 | 10/22/2025 01:21:10 | RECTIFIER MAJOR ALARM at JZMA1M8414-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/21/2025 13:13:08 | Minor | 7103 | RECTIFIER MAJOR ALARM | 10/21/2025 13:12:59 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8414 | FLM_EM | [5 empty] | RECTIFIER MAJOR ALARM |  |  | API | 10/21/2025 13:21:10 | 10/22/2025 08:43:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000720 | PCM-20251021-00001576 | TT-20251021-01601 | EM | Region_1 | R1_DM_HWBSC01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/21/2025 13:22:43 | 10/22/2025 10:22:20 | 10/21/2025 17:22:43 | High Room Temp-BATT Room at R1_DM_HWBSC01 @ Sceco_STB | 10/21/2025 13:22:15 | Critical | 65351 | High Room Temp-BATT Room | 10/21/2025 13:22:09 | P1 | BSC | dammam | Sceco_STB | 2G NSA | R1_DM_HWBSC01 | FLM_EM | [8 empty] | API | 10/21/2025 13:22:43 | 10/22/2025 10:22:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000721 | PCM-20251021-00001578 | TT-20251021-01604 | EM | Region_6 | KHS0218 | KHS0218 |  |  |  | Amir Abbas Arif Raza | 10/21/2025 13:24:15 | 10/21/2025 14:35:27 | 10/22/2025 01:24:15 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at KHS0218-GSM-P2-USF @ Sceco | 10/21/2025 13:16:15 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/21/2025 13:16:03 | P2 | 2G | khamis mushyet | Sceco | 2G NSA | KHS0218 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/21/2025 13:24:15 | 10/21/2025 14:35:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000724 | PCM-20251021-00001583 | TT-20251021-01610 | Reference_EM | Region_1 | SMRY0808 | SMRY0808 |  |  |  | Samir Elzain Abdu Gumaa | 10/21/2025 13:26:51 | 10/21/2025 13:26:51 | 10/21/2025 19:26:51 | Minor Rec alarm at SMRY0808-P1-HUB_SRAN @ Generator_SG | 10/21/2025 13:16:31 | Major | 65108 | Minor Rec alarm | 10/21/2025 13:16:26 | P1 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0808 | FLM_EM | [8 empty] | API | 10/21/2025 13:26:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251021000732 | PCM-20251021-00001595 | TT-20251021-01598 | Telecom | [7 empty] | 10/21/2025 13:32:57 | 10/21/2025 13:32:57 | 10/22/2025 01:32:57 | WMKJD0001 Complete down | 10/21/2025 13:17:50 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/21/2025 13:17:50 | P3 | WIFI |  | Sceco | Wifi SA | WMKJD0001 | FLM_EM | WMKJD0001 | Hub: WMKJD0001 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00001573 | Hub: WMKJD0001 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: WMKJD0001 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  |  |  | API | 10/21/2025 13:32:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000733 | PCM-20251021-00001596 | TT-20251019-02671 | Reference_telecom | Region_4 | JED2506 | JED2506 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 13:33:11 | 10/21/2025 18:53:02 | 10/22/2025 01:33:11 | LossOfSignal observed in JED2506 towards 10.3.225.35 @ Sceco | 10/19/2025 11:24:12 | Minor |  | LossOfSignal | 10/19/2025 11:24:07 | P3 | 2G | jeddah | Sceco | TX NSA | JED2506 | FLM_TE |  | Approved | PCM-20251021-00001266 | Approved | Approved |  |  |  | API | 10/21/2025 13:33:11 | 10/21/2025 18:53:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000738 | PCM-20251021-00001608 | TT-20251021-01623 | Telecom | Region_1 | HFF6029 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 13:39:45 | 10/21/2025 14:53:28 | 10/21/2025 19:39:45 | DCU CPRI Interface Error at HFF6029-DCU1 @ Sceco | 10/21/2025 13:33:35 | Major | 26234 | DCU CPRI Interface Error | 10/21/2025 13:32:37 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/21/2025 13:39:45 | 10/21/2025 14:23:20 | 10/21/2025 14:53:02 |  |  | 10/21/2025 14:53:28 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000741 | PCM-20251021-00001614 | TT-20251006-02408 | Reference_telecom | Region_4 | JED0185 | JED0185 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 13:43:40 | 10/21/2025 18:53:03 | 10/22/2025 01:43:40 | DemXpicLOS observed in JED0185_01 towards 10.1.224.210 @ Sceco | 10/06/2025 11:53:07 | Minor |  | DemXpicLOS | 10/06/2025 11:51:45 | P3 | 2G | jeddah | Sceco | TX NSA | JED0185 | FLM_TE |  |  | PCM-20251021-00001263 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/21/2025 13:43:40 | 10/21/2025 18:53:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000743 | PCM-20251021-00001622 | TT-20251021-01627 | Reference_telecom | Region_3 | WFR2275 | WFR2275 | Enviroment | SCECO_Failure | SCECO auto restored | TAUSEEF ILYAS | 10/21/2025 13:48:05 | 10/21/2025 23:15:20 | 10/21/2025 19:48:05 | 2(2G) 2(LTE) sites down under WFR2275-P3,WFR2277-P3/R3_MD_HWBSC01 @ Generator_DG | 10/21/2025 13:22:18 | Major | 21825 | CSL Fault | 10/21/2025 13:22:18 | P3 | SRAN | madinah | Generator_SG | 2G_3G_LTE SA | WFR2275-P3,WFR2277-P3/ | FLM_TE | WFR2275 | Results: DOWN SITE HUB WFR2275-P3 WFR2275 WFR2277-P3/ WFR2277 Summary: Hub: WFR2275, Down Count: 1, Down Sites: WFR2275-P3 Hub: WFR2277, Down Count: 1, Down Sites: WFR2277-P3/ Alarm Summary: WFR2275 Alarm Active on HUB WFR2277 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 13:48:05 | 10/21/2025 13:51:14 | 10/21/2025 23:15:13 |  |  | 10/21/2025 23:15:20 |  | TAUSEEF ILYAS |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000745 | PCM-20251021-00001628 | TT-20251021-01630 | Telecom | Region_1 | DAM0332 | DAM0332 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 13:50:24 | 10/21/2025 16:28:37 | 10/21/2025 17:50:24 | 2(2G) 2(3G) sites down under DAM0332-P1-VIP,DAM2180-P1-VIP/R1_DM_HWBSC01 @ Sceco | 10/21/2025 13:40:34 | Critical | 21825 | CSL Fault | 10/21/2025 13:40:33 | VIP | SRAN | dammam | Sceco | 2G_3G SA | DAM2180-P1-VIP 2G_3G,DAM0332-P1-VIP 2G_3G | FLM_EM | DAM0332 | Hub:- DAM0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251021-00001623 | Hub:- DAM0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- DAM0332 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/21/2025 13:50:24 | 10/21/2025 16:28:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000746 | PCM-20251021-00001629 | TT-20251021-01582 | Telecom | Region_6 | BHAB1M8069 | BHAB2069 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/21/2025 13:50:24 | 10/21/2025 14:16:19 | 10/22/2025 01:50:24 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHAB1M8069-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 13:08:51 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 10:25:25 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8069 | FLM_TE |  | Thanks to check | PCM-20251021-00001598 | Thanks to check | Thanks to check |  |  |  | API | 10/21/2025 13:50:24 | 10/21/2025 14:15:39 | 10/21/2025 14:16:06 |  |  | 10/21/2025 14:16:19 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000747 | PCM-20251021-00001630 | TT-20251021-01644 | Telecom | Region_1 | DAM2M7257 | DAM0257 | Equipment | BSS_HW_Stuck | Reset RFU | Shakeel Ahmed Hafeez Ameen | 10/21/2025 13:50:27 | 10/21/2025 15:49:54 | 10/21/2025 19:50:27 | Cell Unavailable at DAM2M7257-P2-CA-L800 @ Sceco | 10/21/2025 13:49:02 | Major | 29240 | Cell Unavailable | 10/21/2025 13:47:29 | P2 | 4G | dammam | Sceco | LTE SA | DAM2M7257 | FLM_TE | [8 empty] | API | 10/21/2025 13:50:27 | 10/21/2025 14:29:44 | 10/21/2025 15:49:43 |  |  | 10/21/2025 15:49:54 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000750 | PCM-20251021-00001633 | TT-20251021-01621 | Reference_telecom | Region_1 | HFF2U6729 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 13:52:30 | 10/21/2025 14:54:24 | 10/22/2025 01:52:30 | Cell RX Channel Interference Noise Power Unbalanced at HFF2U6729-P3 @ Sceco | 10/21/2025 10:38:52 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/21/2025 10:38:48 | P3 | 4G | hafouf | Sceco | 2G NSA | HFF2U6729 | FLM_TE |  |  | PCM-20251021-00001605 | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. | Dear FLM, Need to check 1. RRU has single jumper or double jumper and related RRU antenna port checked for any possible fault. If single jumper then diversity connection are thoroughly verified. 2. Jumper connection at all end RRU, TMA, duplexer, combiner & antenna end they are tighten with proper weather proofing or not. 3. Site has any TMA available or not & if TMA present related TMA & its port are checked for any possible fault. (You can verify with BO for TMA attenuation setting if available) 4. Antenna & their port are thoroughly checked for any possible fault. 5. This alarm to be solved with hit & trial method by swapping hardware one by one with any other normal sector and keeping under observation some hours for every single change (Not to perform all hardware swap on single day). If alarm swapping with any of the hardware swap then particular hardware to be replaced. 6. As well FLM to take board RTWP trend for 20-300 min while doing troubleshooting to check signal strength on both ports & difference should be below 12 db. |  |  |  | API | 10/21/2025 13:52:30 | 10/21/2025 14:23:20 | 10/21/2025 14:54:11 |  |  | 10/21/2025 14:54:24 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000754 | PCM-20251021-00001644 | TT-20251021-01658 | EM | [7 empty] | 10/21/2025 13:58:51 | 10/21/2025 13:58:51 | 10/22/2025 01:58:51 | SHELTER DOOR OPEN at KMBS1M8327-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/21/2025 13:58:18 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 13:58:14 | P3 | 4G |  | Sceco | LTE NSA | KMBS1M8327 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 13:58:51 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000755 | PCM-20251021-00001646 | TT-20251021-01661 | EM | Region_1 | SMRY0809 | SMRY0809 |  |  |  | Samir Elzain Abdu Gumaa | 10/21/2025 14:01:57 | 10/21/2025 14:01:57 | 10/22/2025 02:01:57 | Mains Failure at SMRY0809-P3_SRAN @ Generator_SG | 10/21/2025 13:52:07 | Minor | 65109 | Mains Failure | 10/21/2025 13:52:04 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0809 | FLM_EM | [8 empty] | API | 10/21/2025 14:01:57 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000763 | PCM-20251021-00001667 | TT-20251021-01666 | Telecom | Region_4 | SJED1S7705 | SJED0705 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 14:09:02 | 10/21/2025 14:09:02 | 10/21/2025 20:09:02 | 1(LTE) sites down under SJED0705-P3-CA @ Sceco | 10/21/2025 14:00:42 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 14:00:39 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0705-P3-CA | FLM_TE | SJED0705 | Results: DOWN SITE HUB SJED0705-P3-CA SJED0705 Summary: Hub: SJED0705, Down Count: 1, Down Sites: SJED0705-P3-CA Alarm Summary: SJED0705 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.168.108:8080] [URL:http://10.96.168.108:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 14:09:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000765 | PCM-20251021-00001673 | TT-20251021-01684 | Telecom | Region_5 | MAK2967 | MAK2967 |  |  |  | SAID AHMED HASSAN ABDALLA | 10/21/2025 14:10:44 | 10/21/2025 14:10:44 | 10/22/2025 02:10:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2967-G9-L8-L18-L21-NR2.6-P3-SBTS @ Generator_SG | 10/21/2025 14:10:01 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 14:09:52 | P3 | 2G | makkah | Generator_SG | 5G_Cell SA | MAK2967 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 14:10:44 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000768 | PCM-20251021-00001679 | TT-20251021-01690 | Telecom | Region_5 | MAK1M9630 | MAK0630 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/21/2025 14:13:20 | 10/21/2025 19:57:16 | 10/22/2025 02:13:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1M9630-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/21/2025 14:12:20 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 14:12:12 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9630 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 14:13:20 | 10/21/2025 19:57:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000772 | PCM-20251021-00001689 | TT-20251021-01700 | EM | Region_4 | JED0252 | JED0252 |  |  |  | Muhammad Arqam Muhammad Dawood | 10/21/2025 14:15:54 | 10/21/2025 14:15:54 | 10/22/2025 02:15:54 | AIRCON 1 FAILURE at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/21/2025 14:07:31 | Minor | 7103 | AIRCON 1 FAILURE | 10/21/2025 14:07:22 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0252 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/21/2025 14:15:54 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000776 | PCM-20251021-00001694 | TT-20251021-01705 | Telecom | Region_4 | JED2635 | JED2635 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 14:18:29 | 10/21/2025 18:53:03 | 10/22/2025 02:18:29 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2635-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/21/2025 14:17:39 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 14:17:28 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2635 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 14:18:29 | 10/21/2025 18:53:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000777 | PCM-20251021-00001695 | TT-20251021-01707 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 14:19:00 | 10/21/2025 14:19:00 | 10/21/2025 18:19:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/21/2025 14:18:24 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 14:18:14 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 14:19:00 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000778 | PCM-20251021-00001696 | TT-20251021-01708 | EM | Region_3 | WFR2277 | WFR2277 |  |  |  | Muhammad arshad Anwar | 10/21/2025 14:19:31 | 10/21/2025 14:19:31 | 10/22/2025 02:19:31 | NETECO: Maintenance Reminder at WFR2277 @ Generator_DG | 10/21/2025 14:13:09 | Minor | 40563 | Maintenance Reminder | 10/21/2025 14:13:09 | P3 | SRAN | madinah | Generator_DG | 2G NSA | WFR2277 | FLM_EM | [8 empty] | API | 10/21/2025 14:19:31 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000783 | PCM-20251021-00001708 | TT-20251021-01720 | Reference_telecom | Region_4 | JED0848 | JED0848 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 14:26:13 | 10/21/2025 17:28:53 | 10/22/2025 02:26:13 | DemFail observed in JED0848 towards 10.21.76.150 @ Generator_SG | 10/21/2025 02:26:12 | Minor |  | DemFail | 10/21/2025 02:26:07 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0848 | FLM_TE | [8 empty] | API | 10/21/2025 14:26:13 | 10/21/2025 17:28:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000785 | PCM-20251021-00001712 | TT-20251021-01723 | Telecom | Region_2 | QSDH0704 | QSDH0704 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/21/2025 14:27:16 | 10/21/2025 17:39:17 | 10/22/2025 02:27:16 | ETH_LINK_DOWN at QSDH0704_NE_3_DIA @ Sceco_STB | 10/21/2025 14:25:19 | Minor | 1-12793 | ETH_LINK_DOWN | 10/20/2025 14:09:09 | P2 | SRAN | buraidah | Sceco_STB | TX NSA | QSDH0704 | FLM_TE | [8 empty] | API | 10/21/2025 14:27:16 | 10/21/2025 17:39:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000786 | PCM-20251021-00001713 | TT-20251021-01726 | Telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 14:28:49 | 10/21/2025 14:28:49 | 10/22/2025 02:28:49 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/21/2025 14:20:31 | Minor | 7115 | BASE STATION INFORMATION | 10/21/2025 14:20:22 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0601 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/21/2025 14:28:49 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000790 | PCM-20251021-00001725 | TT-20251021-00005 | Telecom | Region_4 | TAF1M4349 | TAF2349 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 14:33:50 | 10/22/2025 07:52:54 | 10/21/2025 20:33:50 | WCDMA CELL OUT OF USE at TAF1M4349-P2 @ Sceco | 10/20/2025 23:56:58 | Major | 7771 | WCDMA CELL OUT OF USE | 10/20/2025 23:54:43 | P3 | 3G | taif | Sceco | 3G SA | TAF1M4349 | FLM_TE |  |  | PCM-20251021-00001650 | check local with spare ( UBT-EAC) | check local with spare ( UBT-EAC) |  |  |  | API | 10/21/2025 14:33:50 | 10/22/2025 07:52:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000792 | PCM-20251021-00001727 | TT-20251021-01709 | Telecom | [7 empty] | 10/21/2025 14:34:03 | 10/21/2025 14:34:03 | 10/22/2025 02:34:03 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at BAH1M8152-G9-L8-L18-SBTS-P3-CAP @ Generator_SG | 10/21/2025 14:17:35 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 11:26:57 | P3 | 4G |  | Generator_SG | LTE NSA | BAH1M8152 | FLM_TE |  |  | PCM-20251021-00001697 | Alarm Cleared. FLM need to check and close with RCA. | Alarm Cleared. FLM need to check and close with RCA. |  |  |  | API | 10/21/2025 14:34:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000799 | PCM-20251021-00001742 | TT-20251021-01747 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 14:44:19 | 10/21/2025 14:44:19 | 10/22/2025 02:44:19 | BASE STATION ANTENNA LINE PROBLEM at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/21/2025 14:34:52 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/21/2025 14:34:41 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0539 | FLM_TE |  |  | PCM-20251021-00001741 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/21/2025 14:44:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000801 | PCM-20251021-00001752 | TT-20251021-01758 | Telecom | Region_6 | MKW1M8140 | MKW2140 |  |  |  | Manzoor Ahmed | 10/21/2025 14:47:33 | 10/21/2025 14:54:38 | 10/21/2025 20:47:33 | PT::: site Flapped ,FLM need to Check at MKW1M8140-L800-SBTS-P3 | 10/21/2025 14:47:13 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 14:47:15 | P3 | 4G | Baha | Sceco | 2G_3G_LTE_5G NSA | MKW1M8140-L800-SBTS-P3 | FLM_TE | [8 empty] | API | 10/21/2025 14:47:33 | 10/21/2025 14:54:38 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000803 | PCM-20251021-00001753 | TT-20251021-01750 | EM | Region_6 | ABH0086 | ABH0086 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/21/2025 14:48:05 | 10/22/2025 03:27:44 | 10/21/2025 20:48:05 | 1(2G/3G/5G) sites down under ABH0086-P2/ABH0086-P2 @ Sceco | 10/21/2025 14:40:20 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 14:40:16 | P2 | 2G | abha | Sceco | 2G_3G_5G SA | ABH0086-P2 | FLM_EM | ABH0086 | Results: DOWN SITE HUB ABH0086-P2 ABH0086 Summary: Hub: ABH0086, Down Count: 1, Down Sites: ABH0086-P2 Alarm Summary: ABH0086 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 14:48:05 | 10/22/2025 03:27:44 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000804 | PCM-20251021-00001754 | TT-20251021-01759 | Reference_telecom | Region_6 | AQQ2427 | AQQ2427 |  |  |  | Manzoor Ahmed | 10/21/2025 14:48:58 | 10/21/2025 14:54:39 | 10/22/2025 02:48:58 | ReplaceableUnitMissing observed in AQQ2427_01 towards 10.221.247.72 @ Generator_SG | 10/21/2025 02:50:53 | Minor |  | ReplaceableUnitMissing | 10/21/2025 02:48:35 | P3 | 2G | Baha | Generator_SG | TX NSA | AQQ2427 | FLM_TE | [8 empty] | API | 10/21/2025 14:48:58 | 10/21/2025 14:54:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000805 | PCM-20251021-00001759 | TT-20251021-00721 | Reference_telecom | Region_5 | MAK0211 | MAK0211 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 14:52:09 | 10/21/2025 14:52:09 | 10/22/2025 02:52:09 | LossOfSignal observed in MAK0211 - 07 towards 10.21.67.194 @ Sceco | 10/20/2025 18:58:09 | Minor |  | LossOfSignal | 10/20/2025 18:55:58 | P1 | 2G | makkah | Sceco | TX NSA | MAK0211 | FLM_TE |  | Approved | PCM-20251021-00001634 | Approved | Approved |  |  |  | API | 10/21/2025 14:52:09 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000806 | PCM-20251021-00001761 | TT-20251021-01765 | Telecom | Region_4 | JED1MN0007 | JED0007 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 14:53:06 | 10/21/2025 17:28:53 | 10/21/2025 20:53:06 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0007-NR2.6-P2 @ Sceco | 10/21/2025 14:52:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 14:52:15 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0007 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 14:53:06 | 10/21/2025 17:28:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000807 | PCM-20251021-00001763 | TT-20251021-01766 | MW_HC | Region_5 | MAK0211 | MAK0211 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 14:53:26 | 10/21/2025 14:53:26 | 10/22/2025 02:53:26 | As BO Requested MW Nokia Observing Performance issue For MW Link MK4-MAK0211 | 10/21/2025 14:52:37 | Minor | 113388 | LOF | 10/21/2025 14:52:39 | P1 | 2G | makkah | Sceco | TX NSA | MK4-MAK0211 | FLM_TE | [5 empty] | As BO Requested MW Nokia Observing Performance issue For MW Link MK4-MAK0211 |  |  | API | 10/21/2025 14:53:26 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021000810 | PCM-20251021-00001771 | TT-20251021-01776 | Reference_telecom | [7 empty] | 10/21/2025 14:58:17 | 10/21/2025 14:58:17 | 10/22/2025 02:58:17 | BASE STATION INFORMATION (Unit temperature is high) at JDRS1M7759-L800-CA-P3 @ Generator_DG | 10/21/2025 14:18:21 | Minor | 7115 | BASE STATION INFORMATION | 10/21/2025 14:18:11 | P3 | 4G |  | Generator_DG | LTE NSA | JDRS1M7759 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/21/2025 14:58:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000811 | PCM-20251021-00001773 | TT-20251021-01780 | EM | Region_1 | SMRY0808 | SMRY0808 |  |  |  | Samir Elzain Abdu Gumaa | 10/21/2025 15:01:22 | 10/21/2025 15:01:22 | 10/21/2025 21:01:22 | Door opening alarm at SMRY0808-P1-HUB_SRAN @ Generator_SG | 10/21/2025 15:00:57 | Major | 65101 | Door opening alarm | 10/21/2025 15:00:54 | P1 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0808 | FLM_EM | [8 empty] | API | 10/21/2025 15:01:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000813 | PCM-20251021-00001776 | TT-20251021-01782 | Telecom | Region_4 | JED1M8602 | JED2602 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 15:02:24 | 10/21/2025 18:53:04 | 10/21/2025 21:02:24 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8602-CA-L800-P3 @ Sceco | 10/21/2025 15:01:20 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 15:01:13 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8602 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 15:02:24 | 10/21/2025 18:53:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000814 | PCM-20251021-00001777 | TT-20251021-01673 | Reference_telecom | Region_6 | NMS0097 | NMS0097 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Fawad Khan | 10/21/2025 15:02:31 | 10/21/2025 18:32:00 | 10/22/2025 03:02:31 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at NMS0097-G9-L18-NNR2.6-SBTS-P3 @ Sceco | 10/21/2025 12:15:10 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 12:06:28 | P3 | 2G | namas | Sceco | 2G NSA | NMS0097 | FLM_TE |  |  | PCM-20251021-00001659 | Alarm cleared. FLM need to check and close with RCA. | Alarm cleared. FLM need to check and close with RCA. |  |  |  | API | 10/21/2025 15:02:31 | 10/21/2025 17:44:56 | 10/21/2025 18:31:31 |  |  | 10/21/2025 18:32:00 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000815 | PCM-20251021-00001779 | TT-20251021-01762 | Reference_telecom | Region_6 | WDS0499 | WDS0499 |  |  |  | Ahmed Mamdouh Helal Helal | 10/21/2025 15:03:12 | 10/21/2025 22:56:52 | 10/21/2025 21:03:12 | MW Link down at WDS0499-LL-CSG-01 // TT-20250721-02113 // TT-20250817-00807 | 10/21/2025 14:51:00 | Major | 15269 | LOS | 10/21/2025 14:51:02 | P1 | 2G | wadi dawasar | Sceco | IPRAN NSA | MW Link down at WDS0499-LL-CSG-01 // TT-20250721-02113 // TT-20250817-00807 | FLM_TE |  |  | PCM-20251021-00001757 | thanks to update for re-rerouting g Link WDS0503-WDS0499 and new connection from both Router WDS0499-WDS0277 and visibility for WDS0503-WDS0499 | thanks to update for re-rerouting g Link WDS0503-WDS0499 and new connection from both Router WDS0499-WDS0277 and visibility for WDS0503-WDS0499 |  |  |  | API | 10/21/2025 15:03:12 | 10/21/2025 22:56:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000821 | PCM-20251021-00001789 | TT-20251021-01777 | Telecom | Region_4 | GMK0442 | GMK0442 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 15:06:49 | 10/22/2025 13:09:29 | 10/21/2025 21:06:49 | 4(2G) 3(3G) sites down under GMK0442-P2-USF,GMK0349-P2-USF,GMK2154-P3,NSH0168-P3/NSH0168-P3 @ Generator_SG | 10/21/2025 14:55:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 14:55:53 | P2 | 2G | qunfuddah | Sceco | 2G_3G SA | NSH0168-P3 2G_3G,GMK0442-P2-USF 2G_3G,GMK0349-P2-USF 2G_3G,GMK2154-P3 2G | FLM_TE | GMK0442 | Results: DOWN SITE HUB NSH0168-P3 GMK0442 GMK0442-P2-USF GMK0442 GMK0349-P2-USF GMK0442 GMK2154-P3 GMK0442 Summary: Hub: GMK0442, Down Count: 4, Down Sites: NSH0168-P3, GMK0442-P2-USF, GMK0349-P2-USF, GMK2154-P3 Alarm Summary: GMK0442 Alarm Active on HUB | PCM-20251021-00001783 | GMK0442 | GMK0442 |  | sites down |  | API | 10/21/2025 15:06:49 | 10/22/2025 13:09:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000822 | PCM-20251021-00001790 | TT-20251021-01711 | Reference_telecom | Region_6 | BHMF1M7856 | BHMF0856 | Equipment | BSS_HW_Stuck | Reset Air Scale | SHAH KHALID | 10/21/2025 15:07:20 | 10/21/2025 16:48:56 | 10/22/2025 03:07:20 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BHMF1M7856-G9-L8-L18-SBTS-P3 @ Sceco | 10/21/2025 12:23:53 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 12:20:11 | P3 | 4G | makhwa | Sceco | LTE NSA | BHMF1M7856 | FLM_TE |  | Thanks to check | PCM-20251021-00001781 | Thanks to check | Thanks to check |  |  |  | API | 10/21/2025 15:07:20 | 10/21/2025 16:33:24 | 10/21/2025 16:48:34 |  |  | 10/21/2025 16:48:56 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000824 | PCM-20251021-00001794 | TT-20251021-01799 | Telecom | Region_4 | JED2629 | JED2629 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/21/2025 15:11:42 | 10/22/2025 10:28:55 | 10/22/2025 03:11:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2629-G9-L8-L18-L21-NR2.6-P3-SBTS-CAP @ Sceco | 10/21/2025 15:10:38 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 15:10:28 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2629 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 15:11:42 | 10/22/2025 10:26:36 | 10/22/2025 10:28:49 |  |  | 10/22/2025 10:28:55 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000825 | PCM-20251021-00001795 | TT-20251021-01801 | Telecom | Region_4 | JED1M7244 | JED0244 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 15:11:43 | 10/21/2025 18:53:04 | 10/21/2025 21:11:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7244-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/21/2025 15:10:56 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 15:10:43 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7244 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 15:11:43 | 10/21/2025 18:53:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000826 | PCM-20251021-00001798 | TT-20251021-01803 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/21/2025 15:12:43 | 10/22/2025 20:21:06 | 10/22/2025 03:12:43 | AIRCON 1 FAILURE at JED6020-GSM-P3 @ Sceco | 10/21/2025 15:04:47 | Minor | 7103 | AIRCON 1 FAILURE | 10/21/2025 15:04:35 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/21/2025 15:12:43 | 10/22/2025 20:21:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000827 | PCM-20251021-00001800 | TT-20251021-01804 | Telecom | Region_4 | BHR1M7332 | BHR0332 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 15:13:59 | 10/21/2025 17:28:54 | 10/21/2025 21:13:59 | PT:: FLM Need to check minor flapping of Base station service problem (FSP overheating) at BHR1M7332 under R4. | 10/21/2025 15:13:44 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 15:13:44 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G SA | BHR1M7332 | FLM_TE | [8 empty] | API | 10/21/2025 15:13:59 | 10/21/2025 17:28:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000830 | PCM-20251021-00001804 | TT-20251021-01795 | EM | Region_5 | MAK2967 | MAK2967 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Muhammad Saleem Iqbal | 10/21/2025 15:15:03 | 10/22/2025 01:55:07 | 10/21/2025 21:15:03 | 1(2G/5G) sites down under MAK2967-P3/MAK2967-P3 @ Generator_SG | 10/21/2025 15:06:58 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 15:06:55 | P3 | 2G | makkah | Generator_SG | 2G SA | MAK2967-P3 | FLM_TE | MAK2967 | Results: DOWN SITE HUB MAK2967-P3 MAK2967 Summary: Hub: MAK2967, Down Count: 1, Down Sites: MAK2967-P3 Alarm Summary: MAK2967 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 15:15:03 | 10/21/2025 22:36:57 | 10/21/2025 23:01:56 | 10/21/2025 23:02:25 | 10/21/2025 23:29:09 | 10/22/2025 01:55:07 |  | Muhammad Saleem Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000833 | PCM-20251021-00001808 | TT-20251021-01812 | Reference_telecom | Region_6 | KHNJ0850 | KHNJ0850 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Bilal Anwar Khurshid Anwar | 10/21/2025 15:19:26 | 10/22/2025 02:51:45 | 10/22/2025 03:19:26 | LagPortDown observed in KHNJ0850_01 towards 10.74.121.226 @ Sceco | 10/21/2025 03:19:20 | Minor |  | LagPortDown | 10/21/2025 03:18:54 | P1 | 2G | al harja | Sceco | TX NSA | KHNJ0850 | FLM_TE | [8 empty] | API | 10/21/2025 15:19:26 | 10/21/2025 15:34:20 | 10/21/2025 23:41:12 | 10/21/2025 23:41:15 | 10/21/2025 23:46:43 | 10/22/2025 02:51:45 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000835 | PCM-20251021-00001811 | TT-20251021-01806 | EM | Region_4 | JZMA2413 | JZMA2413 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/21/2025 15:21:02 | 10/22/2025 08:43:25 | 10/21/2025 21:21:02 | 1(2G/LTE) sites down under JZMA2413-P3-CAP/JZMA2413-P3-CAP @ Generator_SG | 10/21/2025 15:12:59 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 15:12:51 | P3 | 2G | jeddah | Generator_SG | 2G_LTE SA | JZMA2413-P3-CAP | FLM_EM | JZMA2413 | Results: DOWN SITE HUB JZMA2413-P3-CAP JZMA2413 Summary: Hub: JZMA2413, Down Count: 1, Down Sites: JZMA2413-P3-CAP Alarm Summary: JZMA2413 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 15:21:02 | 10/22/2025 08:43:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251021000836 | PCM-20251021-00001812 | TT-20251021-01807 | Telecom | [7 empty] | 10/21/2025 15:22:01 | 10/21/2025 15:22:01 | 10/21/2025 21:22:01 | 1(2G) sites down under BDR2111-900/R3_MD_HWBSC01 @ Generator_SG | 10/21/2025 15:13:39 | Major | 21825 | CSL Fault | 10/21/2025 15:13:33 | P3 | 2G |  | Generator_SG | 2G SA | BDR2111-900 | FLM_TE | BDR2111 | Results: DOWN SITE HUB BDR2111-900 BDR2111 Summary: Hub: BDR2111, Down Count: 1, Down Sites: BDR2111-900 Alarm Summary: BDR2111 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 15:22:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000837 | PCM-20251021-00001814 | TT-20251021-01816 | Reference_telecom | Region_6 | AQQ2434 | AQQ2434 |  |  |  | Manzoor Ahmed | 10/21/2025 15:23:34 | 10/21/2025 15:49:53 | 10/22/2025 03:23:34 | LossOfSignal observed in AQQ2434_03 towards 10.221.247.65 @ Generator_SG | 10/21/2025 03:23:23 | Minor |  | LossOfSignal | 10/21/2025 03:23:19 | P3 | 2G | Baha | Generator_SG | TX NSA | AQQ2434 | FLM_TE | [8 empty] | API | 10/21/2025 15:23:34 | 10/21/2025 15:49:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000838 | PCM-20251021-00001818 | TT-20251021-01755 | Telecom | Region_4 | HAW2088 | HAW2088 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 15:25:17 | 10/22/2025 07:52:54 | 10/21/2025 21:25:17 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at HAW2088-P3 @ Sceco | 10/21/2025 14:41:49 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 14:41:46 | P3 | 2G | taif | Sceco | 2G_TRX NSA | HAW2088 | FLM_TE |  |  | PCM-20251021-00001747 | Please check the ALD issue | Please check the ALD issue |  |  |  | API | 10/21/2025 15:25:17 | 10/22/2025 07:52:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000840 | PCM-20251021-00001821 | TT-20251021-01825 | Telecom | Region_4 | JZMA1M7824 | JZMA0824 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/21/2025 15:27:43 | 10/22/2025 10:50:55 | 10/22/2025 03:27:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at JZMA1M7824-G9-L8-SBTS-P3 @ Sceco | 10/21/2025 15:27:06 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 15:25:41 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JZMA1M7824 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 15:27:43 | 10/22/2025 10:50:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000842 | PCM-20251021-00001823 | TT-20251021-01817 | EM | Region_6 | ULY2209 | ULY2209 |  |  |  | Asad Saddiq | 10/21/2025 15:28:36 | 10/21/2025 15:31:13 | 10/21/2025 21:28:36 | 1(2G/LTE) sites down under ULY2209-P3/ULY2209-P3 @ Sceco | 10/21/2025 15:20:26 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 15:20:21 | P3 | 2G | bisha | Sceco | 2G_LTE SA | ULY2209-P3 | FLM_EM | ULY2209 | Results: DOWN SITE HUB ULY2209-P3 ULY2209 Summary: Hub: ULY2209, Down Count: 1, Down Sites: ULY2209-P3 Alarm Summary: ULY2209 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 15:28:36 | 10/21/2025 15:31:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000845 | PCM-20251021-00001827 | TT-20251021-01829 | Telecom | Region_4 | HBI1M7353 | HBI0353 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/21/2025 15:35:03 | 10/22/2025 10:50:56 | 10/21/2025 21:35:03 | 1(LTE) sites down under HBI0353-G9-L8-L18-SBTS-P3 @ Sceco | 10/21/2025 15:26:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 15:26:54 | P3 | 4G | qunfuddah | Sceco | LTE SA | HBI0353-G9-L8-L18-SBTS-P3 | FLM_TE | HBI0353 | Results: DOWN SITE HUB HBI0353-G9-L8-L18-SBTS-P3 HBI0353 Summary: Hub: HBI0353, Down Count: 1, Down Sites: HBI0353-G9-L8-L18-SBTS-P3 Alarm Summary: HBI0353 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.98.0.180:8080] [URL:http://10.98.0.180:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 15:35:03 | 10/22/2025 10:50:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000846 | PCM-20251021-00001830 | TT-20251021-01831 | EM | Region_6 | NMS0175 | NMS0175 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/21/2025 15:37:36 | 10/22/2025 23:42:22 | 10/21/2025 21:37:36 | 1(2G/3G/LTE) sites down under NMS0175-P2-WBB-G3/NMS0175-P2-WBB-G3 @ Sceco | 10/21/2025 15:29:26 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 15:29:21 | P2 | 2G | namas | Sceco | 2G_3G_LTE SA | NMS0175-P2-WBB-G3 | FLM_EM | NMS0175 | Results: DOWN SITE HUB NMS0175-P2-WBB-G3 NMS0175 Summary: Hub: NMS0175, Down Count: 1, Down Sites: NMS0175-P2-WBB-G3 Alarm Summary: NMS0175 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 15:37:36 | 10/22/2025 23:42:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000847 | PCM-20251021-00001834 | TT-20251021-01838 | Telecom | Region_4 | JED1MN2149 | JED2149 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 15:41:35 | 10/21/2025 15:41:35 | 10/21/2025 21:41:35 | PT:: FLM Need to check minor flapping of Base station service problem (Unit synchronization failed) at JED1MN2149-NR2.6-P3,JED1MN2230-NR2.6-P1 under R4. | 10/21/2025 15:41:11 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 15:41:11 | P3 | 5G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED1MN2149-NR2.6-P3,JED1MN2230-NR2.6-P1 | FLM_TE | [8 empty] | API | 10/21/2025 15:41:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000848 | PCM-20251021-00001835 | TT-20251021-01839 | EM | Region_6 | NMS1M7175 | NMS0175 |  |  |  | Fiaz Ahmad Abdul Ghani | 10/21/2025 15:42:42 | 10/22/2025 23:42:24 | 10/22/2025 03:42:42 | RECTIFIER MAINS POWER FAILURE at NMS1M7175-G9-L8-L18-NL21-SBTS-P2-WBB-G3 @ Sceco | 10/21/2025 15:36:08 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 15:34:32 | P2 | 4G | namas | Sceco | LTE NSA | NMS1M7175 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 15:42:42 | 10/22/2025 23:42:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000849 | PCM-20251021-00001836 | TT-20251021-01840 | Telecom | Region_6 | FUR0050 | FUR0050 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Mohammed Sideag Mohammed Ali | 10/21/2025 15:43:07 | 10/22/2025 22:37:40 | 10/21/2025 21:43:07 | PT::: as per BO request FLM need to check CHANNEL FAILURE RATE ABOVE DEFINED THRESHOLD at 10 sites | 10/21/2025 15:42:09 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 15:42:17 | P3 | 2G | jizan | Sceco_STB | 2G_3G_LTE_5G NSA | FUR0050-P3,BSH0081-P2,JDS0796-P3,FUR0050-P3,JDSM0794-P3,JDSM0794-P3,JDS0797-P2,NJR0676-NNN,DAR0950-P1,DRB0902-P3 | FLM_TE | [8 empty] | API | 10/21/2025 15:43:07 | 10/21/2025 16:34:08 | 10/22/2025 22:37:17 |  |  | 10/22/2025 22:37:40 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000850 | PCM-20251021-00001838 | TT-20251021-01846 | Telecom | Region_4 | JED2823 | JED2823 | Equipment | SFP_BTS | Replace SFP | BARKAT ALI MAIN HILAL | 10/21/2025 15:44:28 | 10/22/2025 12:55:47 | 10/21/2025 21:44:28 | PT:: FLM Need to check CHANNEL FAILURE RATE ABOVE DEFINED THRESHOLD at JED2823-P3,JED2297-P3,HLA2439-P3,JED0608-P3,JED0717-P1-VIP under R4 (BO Request) | 10/21/2025 15:44:11 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 15:44:11 | P3 | 2G | jeddah | Generator_SG | 2G_3G_LTE_5G SA | JED2823-P3,JED2297-P3,HLA2439-P3,JED0608-P3,JED0717-P1-VIP | FLM_TE | [8 empty] | API | 10/21/2025 15:44:28 | 10/21/2025 19:40:42 | 10/22/2025 10:03:50 | 10/22/2025 10:23:31 | 10/22/2025 10:28:40 | 10/22/2025 12:55:47 |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000853 | PCM-20251021-00001844 | TT-20251021-01860 | Telecom | Region_5 | MAK0002 | MAK0002 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | KAMRAN AAMIR | 10/21/2025 15:51:02 | 10/21/2025 19:01:22 | 10/22/2025 03:51:02 | PT::FLM need to perform HC at MAK0002-P1-DIA,TAF2349-P2,HAW0309-P2 and MKTF0801-P2-USF (BO request) | 10/21/2025 15:50:53 | Minor | 676767671 | Health Check-WO to TE FME | 10/21/2025 15:50:53 | P1 | 2G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK0002-P1-DIA,TAF2349-P2,HAW0309-P2 and MKTF0801-P2-USF | FLM_TE | [8 empty] | API | 10/21/2025 15:51:02 |  | 10/21/2025 16:29:30 | 10/21/2025 16:29:34 | 10/21/2025 17:12:55 | 10/21/2025 19:01:22 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000855 | PCM-20251021-00001848 | TT-20251021-01856 | Telecom | Region_5 | MAK6182 | MAK6082 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 15:54:13 | 10/21/2025 15:54:13 | 10/21/2025 19:54:13 | 1(2G) sites down under MAK6082-P1-HRM/MAK6182-P1-HRM @ Sceco | 10/21/2025 15:46:06 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 15:45:59 | P1 | 2G | makkah | Sceco | 2G SA | MAK6082-P1-HRM | FLM_TE | MAK6082 | Results: DOWN SITE HUB MAK6082-P1-HRM MAK6082 Summary: Hub: MAK6082, Down Count: 1, Down Sites: MAK6082-P1-HRM Alarm Summary: MAK6082 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 15:54:13 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000856 | PCM-20251021-00001850 | TT-20251021-01857 | Telecom | Region_3 | DBQL2M5264 | DBQL0264 |  |  |  | Moustafa Samir Omar | 10/21/2025 15:54:31 | 10/21/2025 16:27:23 | 10/21/2025 21:54:31 | 1(2G) sites down under DBQL0264-P3/R3_TB_HWBSC01 @ Generator_SG | 10/21/2025 15:46:30 | Major | 21807 | OML Fault | 10/21/2025 15:46:24 | P3 | 2G | tabouk | Generator_SG | 2G SA | DBQL0264-P3 | FLM_TE |  | Results: DOWN SITE HUB DBQL0264-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/21/2025 15:54:31 | 10/21/2025 16:27:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000859 | PCM-20251021-00001855 | TT-20251021-01871 | EM | Region_6 | BHAB1M8258 | BHAB2258 |  |  |  | Zia Ur Rahamn | 10/21/2025 15:56:08 | 10/21/2025 19:03:16 | 10/22/2025 03:56:08 | SHELTER DOOR OPEN at BHAB1M8258-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 15:55:54 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 15:55:50 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8258 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 15:56:08 | 10/21/2025 19:03:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000863 | PCM-20251021-00001862 | TT-20251021-01873 | EM | Region_6 | BHAB2090 | BHAB2090 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 15:58:10 | 10/21/2025 22:26:24 | 10/22/2025 03:58:10 | AIRCON 2 FAILURE at BHAB2090-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/21/2025 15:49:55 | Minor | 7103 | AIRCON 2 FAILURE | 10/21/2025 15:49:37 | P3 | 2G | mohail | Generator_SG | 2G NSA | BHAB2090 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/21/2025 15:58:10 | 10/21/2025 22:26:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000864 | PCM-20251021-00001863 | TT-20251021-01874 | EM | Region_4 | JED1M7620 | JED0620 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/21/2025 15:59:12 | 10/22/2025 20:21:07 | 10/22/2025 03:59:12 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JED1M7620-CA-L900-L800-SBTS @ Sceco | 10/21/2025 15:51:18 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/21/2025 15:51:08 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7620 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/21/2025 15:59:12 | 10/22/2025 20:21:07 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000865 | PCM-20251021-00001868 | TT-20251021-01879 | Reference_telecom | Region_5 | MAK0190 | MAK0190 |  |  |  | Amr Abdulla Ali Othman | 10/21/2025 16:01:17 | 10/21/2025 16:01:17 | 10/22/2025 04:01:17 | Degrade observed in MAK0190 SH03 towards 10.3.229.228 @ Sceco | 10/21/2025 04:02:49 | Minor |  | Degrade | 10/21/2025 04:00:48 | P2 | 2G | makkah | Sceco | TX NSA | MAK0190 | FLM_TE | [8 empty] | API | 10/21/2025 16:01:17 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000866 | PCM-20251021-00001871 | TT-20251021-00794 | Reference_telecom | Region_2 | UNZ0069 | UNZ0069 | Transsmission | MW_Connectors | Remade Outdoor MW Connector | Muhammad Naeem Muhammad Gulzar | 10/21/2025 16:02:28 | 10/21/2025 16:51:28 | 10/21/2025 22:02:28 | MW Alarm of failed LAG negotiation at UNZ0069-ZQa02-1-CSG-03 REF:QR20251016001562 @ Sceco_STB | 10/21/2025 01:24:51 | Major | 101-1102218 | Alarm of failed LAG negotiation | 10/21/2025 01:24:45 | P1 | SRAN | buraidah | Sceco_STB | IPRAN SA | UNZ0069-ZQa02-1-CSG-03 | FLM_TE |  | Dear FLM, We are observing visibility issue at both ends ,Kindly check issue locally. | PCM-20251021-00001660 | UNZ0069 port is 0-9-7 | UNZ0069 port is 0-9-7 |  |  |  | API | 10/21/2025 16:02:28 | 10/21/2025 16:03:05 | 10/21/2025 16:51:14 |  |  | 10/21/2025 16:51:28 |  | Muhammad Naeem Muhammad Gulzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000867 | PCM-20251021-00001872 | TT-20251021-01880 | Reference_telecom | Region_4 | JDRS1M3759 | JDRS0759 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Khizer Hayat | 10/21/2025 16:02:59 | 10/21/2025 21:37:16 | 10/21/2025 22:02:59 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at JDRS1M3759-P3 @ Generator_DG | 10/21/2025 15:33:26 | Major | 7771 | WCDMA CELL OUT OF USE | 10/21/2025 15:31:15 | P3 | 3G | jeddah | Generator_DG | 3G SA | JDRS1M3759 | FLM_TE |  |  | PCM-20251021-00001869 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/21/2025 16:02:59 | 10/21/2025 17:20:07 | 10/21/2025 21:37:10 |  |  | 10/21/2025 21:37:16 |  | Khizer Hayat |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000868 | PCM-20251021-00001873 | TT-20251021-01886 | EM | Region_6 | BHAB1M8258 | BHAB2258 |  |  |  | Zia Ur Rahamn | 10/21/2025 16:04:23 | 10/21/2025 19:03:17 | 10/22/2025 04:04:23 | RECTIFIER MAINS POWER FAILURE at BHAB1M8258-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 15:56:17 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 15:56:14 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8258 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 16:04:23 | 10/21/2025 19:03:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000869 | PCM-20251021-00001874 | TT-20251021-01888 | EM | Region_4 | JZMA1M8414 | JZMA2414 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/21/2025 16:06:27 | 10/22/2025 08:43:25 | 10/22/2025 04:06:27 | SHELTER DOOR OPEN at JZMA1M8414-G9-L8-L18-L21-SBTS-P3-CAP @ Generator_SG | 10/21/2025 16:06:05 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 16:05:53 | P3 | 4G | jeddah | Generator_SG | LTE NSA | JZMA1M8414 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 16:06:27 | 10/22/2025 08:43:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000872 | PCM-20251021-00001879 | TT-20251021-01899 | EM | Region_4 | JED1M7620 | JED0620 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/21/2025 16:09:34 | 10/22/2025 20:21:08 | 10/22/2025 04:09:34 | SHELTER DOOR OPEN at JED1M7620-CA-L900-L800-SBTS @ Sceco | 10/21/2025 16:09:00 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 16:08:51 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7620 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 16:09:34 | 10/22/2025 20:21:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000873 | PCM-20251021-00001880 | TT-20251021-01901 | EM | Region_6 | BKR1M8214 | BKR2214 |  |  |  | Fathy Mohamed | 10/21/2025 16:10:05 | 10/21/2025 20:48:13 | 10/22/2025 04:10:05 | AIRCON 1 FAILURE at BKR1M8214-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/21/2025 16:02:50 | Minor | 7103 | AIRCON 1 FAILURE | 10/21/2025 16:01:34 | P3 | 4G | Baha | Generator_SG | LTE NSA | BKR1M8214 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/21/2025 16:10:05 | 10/21/2025 20:48:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000874 | PCM-20251021-00001883 | TT-20251021-01904 | Reference_telecom | Region_2 | ARS0174 | ARS0174 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/21/2025 16:11:06 | 10/21/2025 16:22:51 | 10/22/2025 04:11:06 | RF Unit RX Channel RTWP/RSSI Unbalanced at ARS0174-P3_SRAN @ Sceco | 10/21/2025 13:10:56 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/21/2025 13:10:52 | P3 | SRAN | al rass | Sceco | 2G NSA | ARS0174 | FLM_TE | [8 empty] | API | 10/21/2025 16:11:06 | 10/21/2025 16:22:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000875 | PCM-20251021-00001889 | TT-20251021-01905 | EM | Region_1 | HFF2747 | HFF2747 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/21/2025 16:12:09 | 10/21/2025 20:43:57 | 10/21/2025 22:12:09 | Door opening alarm at HFF2747-P1-SHOP_SRAN @ Sceco | 10/21/2025 16:11:56 | Major | 65101 | Door opening alarm | 10/21/2025 16:11:53 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFF2747 | FLM_EM | [8 empty] | API | 10/21/2025 16:12:09 | 10/21/2025 20:37:59 | 10/21/2025 20:43:50 |  |  | 10/21/2025 20:43:57 |  | Shahid Khan Dilawar Khan |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000876 | PCM-20251021-00001890 | TT-20251021-01754 | Telecom | Region_4 | TAF2278 | TAF2278 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 16:13:19 | 10/22/2025 17:30:00 | 10/21/2025 22:13:19 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TAF2278-P3 @ Sceco | 10/21/2025 14:41:49 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 14:41:46 | P3 | 2G | taif | Sceco | 2G_TRX NSA | TAF2278 | FLM_TE |  |  | PCM-20251021-00001746 | Dear FLM Team, Please support to check Antenna line device HW failure | Dear FLM Team, Please support to check Antenna line device HW failure |  |  |  | API | 10/21/2025 16:13:19 | 10/22/2025 17:30:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000877 | PCM-20251021-00001893 | TT-20251021-01892 | Telecom | Region_6 | KMS0168 | KMS0168 |  |  |  | Amir Abbas Arif Raza | 10/21/2025 16:14:38 | 10/21/2025 18:30:08 | 10/21/2025 22:14:38 | 2(2G) 1(3G) 2(5G) sites down under KMS0352-P3,KMS0168-P3/KMS0168-P3 @ Sceco | 10/21/2025 16:03:50 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 16:03:46 | P3 | 2G | khamis mushyet | Sceco | 2G_3G_5G SA | KMS0168-P3 2G_3G_5G,KMS0352-P3 2G_5G | FLM_EM | KMS0168 | Hub: KMS0168 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00001887 | Hub: KMS0168 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Hub: KMS0168 We are observing RSL-99.00 at far end, kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/21/2025 16:14:38 | 10/21/2025 18:30:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000879 | PCM-20251021-00001896 | TT-20251021-01756 | Telecom | Region_4 | TAF2277 | TAF2277 |  |  |  | Rashid Shafique | 10/21/2025 16:15:10 | 10/21/2025 16:17:01 | 10/21/2025 22:15:10 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TAF2277-P3 @ Sceco | 10/21/2025 14:41:53 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 14:41:48 | P3 | 2G | taif | Sceco | 2G_TRX NSA | TAF2277 | FLM_TE |  |  | PCM-20251021-00001748 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/21/2025 16:15:10 | 10/21/2025 16:17:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000880 | PCM-20251021-00001897 | TT-20251021-01902 | Telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 16:15:26 | 10/21/2025 17:28:54 | 10/22/2025 04:15:26 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/21/2025 16:05:47 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 16:05:38 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251021-00001881 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/21/2025 16:15:26 | 10/21/2025 17:28:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000881 | PCM-20251021-00001899 | TT-20251021-01736 | Reference_telecom | Region_1 | RST0352 | RST0352 |  |  |  | Rafiq Ahmed Elturifi | 10/21/2025 16:16:51 | 10/21/2025 20:54:29 | 10/21/2025 22:16:51 | MW:Link down at RST0352-ZDa03-CSG-01 to DAM0353 // TT-20250918-02333 | 10/21/2025 14:34:51 | Major | 15269 | LOS | 10/21/2025 14:34:53 | P1 | SRAN | jubail | Sceco | IPRAN NSA | MW:Link down at RST0352-ZDa03-CSG-01 to DAM0353 // TT-20250918-02333 | FLM_TE |  |  | PCM-20251021-00001867 | Below card has Hard Bad, need to change after TS [NE:HLQS0396_NE_1] [Board:ISM6 Slot:5] Item=03022VHK | Below card has Hard Bad, need to change after TS [NE:HLQS0396_NE_1] [Board:ISM6 Slot:5] Item=03022VHK |  |  |  | API | 10/21/2025 16:16:51 | 10/21/2025 20:54:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000882 | PCM-20251021-00001901 | TT-20251021-01910 | Telecom | Region_4 | JDJZ1M7870 | JDJZ0870 |  |  |  | Mudassar Bashir Bashir Ahmad | 10/21/2025 16:18:06 | 10/22/2025 10:50:57 | 10/22/2025 04:18:06 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JDJZ1M7870-G9-NL8-L18-SBTS-P3 @ Sceco | 10/21/2025 16:11:24 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 16:11:18 | P3 | 4G | qunfuddah | Sceco | 5G_Cell SA | JDJZ1M7870 | FLM_TE |  |  | PCM-20251021-00001898 | FLM need to check connecting ports and verify the antenna line | FLM need to check connecting ports and verify the antenna line |  |  |  | API | 10/21/2025 16:18:06 | 10/22/2025 10:50:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000884 | PCM-20251021-00001903 | TT-20251021-00989 | Telecom | Region_2 | RY4-ASG-02 | RY4 |  |  |  | Saddam hussain muhammad khan | 10/21/2025 16:18:31 | 10/21/2025 16:18:31 | 10/22/2025 04:18:31 | Bad Package Error Rising at RY4-ASG-02 @ Sceco_STB | 10/21/2025 09:23:03 | Minor | 101-2501403 | Bad Package Error Rising | 10/21/2025 09:24:01 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | RY4-ASG-02 | FLM_TE |  |  | PCM-20251021-00001778 | you should secure DIA approval for all DIA in Ry4 as Hazard impact | you should secure DIA approval for all DIA in Ry4 as Hazard impact |  |  |  | API | 10/21/2025 16:18:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000885 | PCM-20251021-00001904 | TT-20251021-00780 | Reference_telecom | Region_3 | HLQS0396 | HLQS0396 | Transsmission | MW_HW_stuck | Reset IF Board/Modem card | Atif Shahzad Muhammad Ajaib | 10/21/2025 16:18:43 | 10/21/2025 19:55:14 | 10/22/2025 04:18:43 | SLAVE_BAD at HLQS0396_NE_1 @ Generator_DG | 10/21/2025 06:18:53 | Minor | 1-423 | SLAVE_BAD | 10/21/2025 06:18:44 | P1 | SRAN | hail | Generator_DG | TX NSA | HLQS0396 | FLM_TE |  |  | PCM-20251021-00001849 | Below card need to be change after checking [NE:HLQS0396_NE_1] [Board:ISM6 Slot:5] [Board Properties] BoardType=SL91ISM6 BarCode=022VHKCNFB001782 Item=03022VHK | Below card need to be change after checking [NE:HLQS0396_NE_1] [Board:ISM6 Slot:5] [Board Properties] BoardType=SL91ISM6 BarCode=022VHKCNFB001782 Item=03022VHK |  |  |  | API | 10/21/2025 16:18:43 | 10/21/2025 16:32:59 | 10/21/2025 19:36:29 | 10/21/2025 19:36:31 | 10/21/2025 19:36:33 | 10/21/2025 19:55:14 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000886 | PCM-20251021-00001909 | TT-20251021-01922 | EM | Region_6 | BHAB1M7817 | BHAB0817 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/21/2025 16:23:30 | 10/22/2025 03:27:45 | 10/22/2025 04:23:30 | SHELTER DOOR OPEN at BHAB1M7817-G9-L8-SBTS-P2 @ Sceco | 10/21/2025 16:23:16 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 16:23:11 | P1 | 4G | abha | Sceco | LTE NSA | BHAB1M7817 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 16:23:30 | 10/22/2025 03:27:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000889 | PCM-20251021-00001915 | TT-20251021-01929 | EM | Region_6 | ABBS0155 | ABBS0155 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/21/2025 16:32:05 | 10/22/2025 03:27:47 | 10/21/2025 22:32:05 | 1(2G/3G/LTE) sites down under ABBS0155-P2-USF/ABBS0155-P2-USF @ Sceco | 10/21/2025 16:24:10 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 16:24:03 | P2 | 2G | bisha | Sceco | 2G_3G_LTE SA | ABBS0155-P2-USF | FLM_EM | ABBS0155 | Results: DOWN SITE HUB ABBS0155-P2-USF ABBS0155 Summary: Hub: ABBS0155, Down Count: 1, Down Sites: ABBS0155-P2-USF Alarm Summary: ABBS0155 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 16:32:05 | 10/22/2025 03:27:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000893 | PCM-20251021-00001931 | TT-20251021-01938 | EM | Region_6 | BSH0197 | BSH0197 |  |  |  | Fizan Ahmed | 10/21/2025 16:35:37 | 10/21/2025 16:35:37 | 10/21/2025 22:35:37 | 1(2G/3G/LTE/5G) sites down under BSH0197-P2/BSH0197-P2 @ Sceco | 10/21/2025 16:27:32 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 16:27:29 | P2 | 2G | baish | Sceco | 2G_3G_LTE_5G SA | BSH0197-P2 | FLM_EM | BSH0197 | Results: DOWN SITE HUB BSH0197-P2 BSH0197 Summary: Hub: BSH0197, Down Count: 1, Down Sites: BSH0197-P2 Alarm Summary: BSH0197 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 16:35:37 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000894 | PCM-20251021-00001932 | TT-20251021-01953 | Reference_EM | Region_1 | KFKM0793 | KFKM0793 | Enviroment | Fire Alarm | Change fire sensor | Reda Mohammed Mohamed Hassanein | 10/21/2025 16:35:54 | 10/21/2025 21:05:45 | 10/22/2025 04:35:54 | Fire Fighting system alarm at KFKM0793-P3_SRAN @ Generator_SG | 10/21/2025 16:25:47 | Minor | 65111 | Fire Fighting system alarm | 10/21/2025 16:25:39 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0793 | FLM_EM | [8 empty] | API | 10/21/2025 16:35:54 | 10/21/2025 18:16:32 | 10/21/2025 18:17:13 | 10/21/2025 18:17:16 | 10/21/2025 18:24:28 | 10/21/2025 21:05:45 |  | Reda Mohammed Mohamed Hassanein |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000897 | PCM-20251021-00001937 | TT-20251021-01865 | Telecom | Region_1 | ABQ2889 | ABQ2889 |  |  |  | Imran Ali Yousaf | 10/21/2025 16:39:32 | 10/21/2025 16:40:35 | 10/21/2025 22:39:32 | 1(LTE) sites down under ABQ2889-P2-L800 @ Sceco | 10/21/2025 15:50:41 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/21/2025 15:49:34 | P2 | SRAN | dammam | Sceco | LTE SA | ABQ2889-P2-L800 | FLM_TE | ABQ2889 | SINGLE SITE CHECK LOCALLY | PCM-20251021-00001908 | SINGLE SITE CHECK LOCALLY | SINGLE SITE CHECK LOCALLY |  | sites down |  | API | 10/21/2025 16:39:32 | 10/21/2025 16:40:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000900 | PCM-20251021-00001948 | TT-20251021-01970 | Reference_EM | Region_1 | DMJB0086 | DMJB0086 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Samir Farahat Allam | 10/21/2025 16:46:14 | 10/22/2025 18:01:28 | 10/21/2025 22:46:14 | DC power fail at DMJB0086-P1-HUB_SRAN @ Generator_SG | 10/21/2025 16:36:05 | Major | 65106 | DC power fail | 10/21/2025 16:36:01 | P1 | SRAN | dammam | Generator_SG | 2G NSA | DMJB0086 | FLM_EM | [8 empty] | API | 10/21/2025 16:46:14 | 10/22/2025 17:38:30 | 10/22/2025 17:39:43 | 10/22/2025 17:39:50 | 10/22/2025 17:40:04 | 10/22/2025 18:01:28 |  | Mohamed Samir Farahat Allam |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000901 | PCM-20251021-00001959 | TT-20251021-01981 | EM | Region_4 | JED6025 | JED6025 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/21/2025 16:50:23 | 10/22/2025 20:21:08 | 10/22/2025 04:50:23 | SHELTER DOOR OPEN at JED6025-GSM-P3 @ Sceco | 10/21/2025 16:49:54 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 16:49:44 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6025 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 16:50:23 | 10/22/2025 20:21:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000902 | PCM-20251021-00001963 | TT-20251021-01975 | EM | Region_1 | RSK2M2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/21/2025 16:51:50 | 10/21/2025 17:13:22 | 10/21/2025 22:51:50 | 1(2G/3G/LTE) sites down under RSK2086-P2/R1_JB_HWBSC01 @ Sceco | 10/21/2025 16:44:59 | Major | 21825 | CSL Fault | 10/21/2025 16:44:56 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | RSK2086-P2 | FLM_EM | RSK2086 | Results: DOWN SITE HUB RSK2086-P2 RSK2086 Summary: Hub: RSK2086, Down Count: 1, Down Sites: RSK2086-P2 Alarm Summary: RSK2086 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 16:51:50 | 10/21/2025 17:13:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000904 | PCM-20251021-00001965 | TT-20251021-01985 | EM | Region_6 | BHAB1M8023 | BHAB2023 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 16:52:26 | 10/21/2025 22:26:25 | 10/22/2025 04:52:26 | SHELTER DOOR OPEN at BHAB1M8023-G9-L8-L18-L21-SBTS-P3 @ Generator_DG | 10/21/2025 16:51:52 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 16:51:42 | P3 | 4G | Baha | Generator_DG | LTE NSA | BHAB1M8023 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 16:52:26 | 10/21/2025 22:26:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000905 | PCM-20251021-00001966 | TT-20251021-01989 | EM | Region_6 | UKHA1M8371 | UKHA2371 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 16:56:04 | 10/21/2025 22:26:28 | 10/22/2025 04:56:04 | SHELTER DOOR OPEN at UKHA1M8371-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/21/2025 16:55:51 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 16:55:38 | P3 | 4G | Baha | Generator_DG | LTE NSA | UKHA1M8371 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 16:56:04 | 10/21/2025 22:26:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000906 | PCM-20251021-00001968 | TT-20251021-01991 | Reference_EM | Region_3 | DBQL2M5264 | DBQL0264 |  |  |  | Moustafa Samir Omar | 10/21/2025 16:57:36 | 10/22/2025 21:57:17 | 10/22/2025 04:57:36 | Mains Failure at DBQL2M5264-P3 @ Generator_SG | 10/21/2025 16:47:26 | Minor | 65109 | Mains Failure | 10/21/2025 16:47:23 | P3 | 2G | tabouk | Generator_SG | 2G NSA | DBQL2M5264 | FLM_EM | [8 empty] | API | 10/21/2025 16:57:36 | 10/22/2025 21:57:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000909 | PCM-20251021-00001975 | TT-20251021-01995 | Telecom | Region_4 | JED6099 | JED6099 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 16:58:38 | 10/21/2025 17:58:17 | 10/21/2025 22:58:38 | PT:: FLM Need to perform HC at JED6099 under R4 | 10/21/2025 16:58:27 | Major | 676767671 | Health Check-WO to TE FME | 10/21/2025 16:58:27 | P3 | 2G | jeddah | Sceco | 2G_3G_LTE_5G SA | JED6099 | FLM_TE | [8 empty] | API | 10/21/2025 16:58:38 | 10/21/2025 17:58:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000910 | PCM-20251021-00001978 | TT-20251021-02014 | Reference_EM | Region_1 | HFB2M5031 | HFB0031 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/21/2025 16:59:39 | 10/21/2025 16:59:39 | 10/21/2025 22:59:39 | Air-condition #2 failure alarm at HFB2M5031-P1-HUB @ Generator_SG | 10/21/2025 16:49:31 | Major | 65105 | Air-condition #2 failure alarm | 10/21/2025 16:49:28 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5031 | FLM_EM | [8 empty] | API | 10/21/2025 16:59:39 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000912 | PCM-20251021-00001984 | TT-20251021-02021 | EM | Region_1 | RSK2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/21/2025 17:02:46 | 10/21/2025 17:13:23 | 10/22/2025 05:02:46 | Door opening alarm at RSK2086-P2_SRAN @ Sceco | 10/21/2025 17:02:15 | Minor | 65101 | Door opening alarm | 10/21/2025 16:59:53 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2086 | FLM_EM | [8 empty] | API | 10/21/2025 17:02:46 | 10/21/2025 17:13:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000914 | PCM-20251021-00001993 | TT-20251021-02030 | Reference_telecom | Region_2 | RIY0573 | RIY0573 |  |  |  | Khan zeb Shah nawaz | 10/21/2025 17:09:29 | 10/21/2025 18:58:47 | 10/22/2025 05:09:29 | RF Unit RX Channel RTWP/RSSI Unbalanced at RIY0573-P2_SRAN-FON @ Sceco | 10/21/2025 14:09:26 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/21/2025 14:09:23 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RIY0573 | FLM_TE | [8 empty] | API | 10/21/2025 17:09:29 | 10/21/2025 18:58:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000916 | PCM-20251021-00001995 | TT-20251021-02031 | EM | Region_1 | RSK2086 | RSK2086 |  |  |  | Dileesh Muringothil Devarajan | 10/21/2025 17:10:00 | 10/21/2025 17:13:24 | 10/22/2025 05:10:00 | Mains Failure at RSK2086-P2_SRAN @ Sceco | 10/21/2025 17:02:15 | Minor | 65109 | Mains Failure | 10/21/2025 16:59:53 | P2 | SRAN | jubail | Sceco | 2G NSA | RSK2086 | FLM_EM | [8 empty] | API | 10/21/2025 17:10:00 | 10/21/2025 17:13:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021000917 | PCM-20251021-00001997 | TT-20251021-02025 | EM | Region_6 | AQQ2423 | AQQ2423 |  |  |  | Abdul Shakor Abassi | 10/21/2025 17:10:33 | 10/21/2025 17:10:33 | 10/21/2025 23:10:33 | 1(2G/LTE) sites down under AQQ2423-P3/AQQ2423-P3 @ Generator_DG | 10/21/2025 17:02:03 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 17:01:56 | P3 | 2G | Baha | Generator_DG | 2G_LTE SA | AQQ2423-P3 | FLM_EM | AQQ2423 | Results: DOWN SITE HUB AQQ2423-P3 AQQ2423 Summary: Hub: AQQ2423, Down Count: 1, Down Sites: AQQ2423-P3 Alarm Summary: AQQ2423 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 17:10:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000919 | PCM-20251021-00002002 | TT-20251021-02035 | EM | Region_6 | BSA1M8292 | BSA2292 |  |  |  | Asad Saddiq | 10/21/2025 17:12:05 | 10/22/2025 01:37:00 | 10/22/2025 05:12:05 | SHELTER DOOR OPEN at BSA1M8292-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 17:11:38 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 17:11:29 | P3 | 4G | bisha | Generator_SG | LTE NSA | BSA1M8292 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 17:12:05 | 10/22/2025 01:37:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021000922 | PCM-20251021-00002008 | TT-20251021-02047 | Reference_telecom | Region_6 | ABDB9019 | ABDB9019 |  |  |  | Amir Sohail | 10/21/2025 17:16:18 | 10/21/2025 18:42:53 | 10/22/2025 05:16:18 | NEC MW Observing Frame ID,Frame ID,High BER,High BER at ABDB9019-2(10.154.175.117) | 09/25/2025 19:00:19 | Minor |  | LOF | 09/25/2025 19:00:19 | P1 | Repeater | abha | Sceco_STB | TX NSA | ABDB9019-2(10.154.175.117) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:18 | 10/21/2025 18:42:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000923 | PCM-20251021-00002009 | TT-20251021-02048 | Reference_telecom | Region_6 | ABH0135 | ABH0135 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 17:16:19 | 10/21/2025 17:20:20 | 10/22/2025 05:16:19 | NEC MW Observing High BER at ABH0135-1(10.154.161.148) | 10/07/2025 15:20:28 | Minor |  | LOF | 10/07/2025 15:20:28 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0135-1(10.154.161.148) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:19 | 10/21/2025 17:20:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000924 | PCM-20251021-00002010 | TT-20251021-02049 | Reference_telecom | Region_1 | ARM0705 | ARM0705 |  |  |  | Imran Ali Yousaf | 10/21/2025 17:16:21 | 10/21/2025 18:10:43 | 10/22/2025 05:16:21 | NEC MW Observing MODEM Power Supply Alarm,XIF,XIF,MODEM Power Supply Alarm at ARM0705(10.74.77.22) | 10/19/2025 15:15:38 | Minor |  | LOF | 10/19/2025 15:15:38 | P3 | SRAN | dammam | Sceco | TX NSA | ARM0705(10.74.77.22) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:21 | 10/21/2025 18:10:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000925 | PCM-20251021-00002011 | TT-20251021-02050 | Reference_telecom | Region_1 | ARM0734 | ARM0734 |  |  |  | Imran Ali Yousaf | 10/21/2025 17:16:22 | 10/21/2025 18:10:44 | 10/22/2025 05:16:22 | NEC MW Observing XIF,LOF,LOF,MODEM Power Supply Alarm,ODU CPU / Cable Open,Frame ID at ARM0734(10.154.6.164) | 10/19/2025 22:00:06 | Minor |  | LOF | 10/19/2025 22:00:06 | P3 | SRAN | dammam | Generator_SG | TX NSA | ARM0734(10.154.6.164) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:22 | 10/21/2025 18:10:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000926 | PCM-20251021-00002012 | TT-20251021-02051 | Reference_telecom | Region_1 | ARM2759 | ARM2759 |  |  |  | Tahir Mahmood Hafiz Yar | 10/21/2025 17:16:23 | 10/21/2025 20:47:40 | 10/22/2025 05:16:23 | NEC MW Observing MODEM Power Supply Alarm,MODEM Power Supply Alarm at ARM2759(10.76.111.229) | 09/09/2025 20:20:28 | Minor |  | LOF | 09/09/2025 20:20:28 | P1 | SRAN | jubail | Power Cube | TX NSA | ARM2759(10.76.111.229) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:23 | 10/21/2025 20:47:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000929 | PCM-20251021-00002015 | TT-20251021-02054 | Reference_telecom | Region_6 | BAH0004 | BAH0004 |  |  |  | SHAH KHALID | 10/21/2025 17:16:26 | 10/21/2025 17:50:02 | 10/22/2025 05:16:26 | NEC MW Observing RX Level,LOF,RX Level,LOF at BAH0004-2(10.1.174.1) | 10/15/2025 16:39:05 | Minor |  | LOF | 10/15/2025 16:39:05 | P1 | 2G | Albaha | Sceco | TX NSA | BAH0004-2(10.1.174.1) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:26 | 10/21/2025 17:50:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000930 | PCM-20251021-00002016 | TT-20251021-02055 | Reference_telecom | Region_6 | BHAB9035 | BHAB9035 |  |  |  | Fawad Khan | 10/21/2025 17:16:28 | 10/21/2025 17:44:57 | 10/22/2025 05:16:28 | NEC MW Observing ETH LOS,LAN Link at BHAB9035-2(10.154.171.219) | 10/16/2025 13:40:03 | Minor |  | LOF | 10/16/2025 13:40:03 | P1 | Repeater | namas | Sceco_STB | TX NSA | BHAB9035-2(10.154.171.219) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:28 | 10/21/2025 17:44:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000931 | PCM-20251021-00002017 | TT-20251021-02056 | Reference_telecom | Region_5 | BIK0153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/21/2025 17:16:29 | 10/21/2025 17:16:29 | 10/22/2025 05:16:29 | NEC MW Observing RX Level,LOF at BIK0153(10.154.126.198) | 10/20/2025 17:21:04 | Minor |  | LOF | 10/20/2025 17:21:04 | P3 | 2G | makkah | Generator_SG | TX NSA | BIK0153(10.154.126.198) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000932 | PCM-20251021-00002018 | TT-20251021-02057 | Reference_telecom | Region_6 | BLC9224 | BLC9224 |  |  |  | Manzoor Ahmed | 10/21/2025 17:16:30 | 10/22/2025 14:04:22 | 10/22/2025 05:16:30 | NEC MW Observing LAG Link at BLC9224_3(10.154.161.6) | 03/20/2025 13:45:40 | Minor |  | LOF | 03/20/2025 13:45:40 | P1 | Repeater | Albaha | Sceco | TX NSA | BLC9224_3(10.154.161.6) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:30 | 10/22/2025 14:04:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000933 | PCM-20251021-00002019 | TT-20251021-02058 | Reference_telecom | Region_1 | DAM0295 | DAM0295 | Transsmission | MW_HW_fault | Replace FAN | Shakeel Ahmed Hafeez Ameen | 10/21/2025 17:16:31 | 10/22/2025 14:05:12 | 10/22/2025 05:16:31 | NEC MW Observing FAN FAIL at DAM0295(10.1.218.58) | 10/19/2025 15:12:47 | Minor |  | LOF | 10/19/2025 15:12:47 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0295(10.1.218.58) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:31 | 10/21/2025 17:16:57 | 10/22/2025 11:09:46 | 10/22/2025 11:42:25 | 10/22/2025 12:09:38 | 10/22/2025 14:05:12 |  | Shakeel Ahmed Hafeez Ameen |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000934 | PCM-20251021-00002020 | TT-20251021-02059 | Reference_telecom | Region_3 | DBQL0253 | DBQL0253 |  |  |  | Hossam Ali Ahmed Ali | 10/21/2025 17:16:32 | 10/21/2025 17:48:20 | 10/22/2025 05:16:32 | NEC MW Observing LOF,LOF,ODU CPU / Cable Open,ODU CPU / Cable Open,Radio Traffic Aggregation Link at DBQL0253 Dir SHR0006(10.159.105.202) | 10/17/2025 09:02:11 | Minor |  | LOF | 10/17/2025 09:02:11 | VIP | SRAN | tabouk | Generator_DG | TX NSA | DBQL0253 Dir SHR0006(10.159.105.202) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:32 | 10/21/2025 17:48:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000935 | PCM-20251021-00002021 | TT-20251021-02060 | Reference_telecom | Region_3 | DBTB0636 | DBTB0636 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Hossam Ali Ahmed Ali | 10/21/2025 17:16:33 | 10/22/2025 18:42:40 | 10/22/2025 05:16:33 | NEC MW Observing RX Level,LOF,Radio Traffic Aggregation Link,LOF,RX Level at DBTB0636(10.154.73.101) | 10/17/2025 09:06:28 | Minor |  | LOF | 10/17/2025 09:06:28 | P3 | SRAN | tabouk | Generator_DG | TX NSA | DBTB0636(10.154.73.101) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:33 | 10/21/2025 17:48:21 | 10/22/2025 18:42:28 |  |  | 10/22/2025 18:42:40 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000936 | PCM-20251021-00002022 | TT-20251021-02061 | Reference_telecom | Region_6 | DMD0042 | DMD0042 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/21/2025 17:16:34 | 10/22/2025 14:25:56 | 10/22/2025 05:16:34 | NEC MW Observing TX Bus Error,RX Level,LOF at DMD0042-2(10.154.172.126) | 10/12/2025 18:53:10 | Minor |  | LOF | 10/12/2025 18:53:10 | P1 | 2G | jizan | Sceco_STB | TX NSA | DMD0042-2(10.154.172.126) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:34 | 10/21/2025 22:29:54 | 10/21/2025 22:30:38 |  |  | 10/22/2025 14:25:56 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000937 | PCM-20251021-00002023 | TT-20251021-02062 | Reference_telecom | Region_1 | DMH0106 | DMH0106 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/21/2025 17:16:35 | 10/21/2025 20:47:29 | 10/22/2025 05:16:35 | NEC MW Observing High BER,High BER at DMH0106-4(10.248.39.42) | 10/09/2025 00:41:36 | Minor |  | LOF | 10/09/2025 00:41:36 | P1 | SRAN | hafr | Sceco_STB | TX NSA | DMH0106-4(10.248.39.42) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:35 | 10/21/2025 20:47:29 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000938 | PCM-20251021-00002024 | TT-20251021-02063 | Reference_telecom | Region_1 | DMH0107 | DMH0107 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/21/2025 17:16:37 | 10/21/2025 20:47:30 | 10/22/2025 05:16:37 | NEC MW Observing High BER,High BER at DMH0107-DMH0106(10.248.39.40) | 10/11/2025 12:10:37 | Minor |  | LOF | 10/11/2025 12:10:37 | P1 | SRAN | hafr | Generator_DG | TX NSA | DMH0107-DMH0106(10.248.39.40) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:37 | 10/21/2025 20:47:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000939 | PCM-20251021-00002025 | TT-20251021-02064 | Reference_telecom | Region_1 | DMJ9917 | DMJ9917 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/21/2025 17:16:37 | 10/21/2025 20:47:31 | 10/22/2025 05:16:37 | NEC MW Observing LOF,High BER,LOF,Frame ID,Frame ID at DMJ9917(10.76.109.211) | 10/11/2025 12:03:24 | Minor |  | LOF | 10/11/2025 12:03:24 | P3 | Repeater | hafr | Generator_SG | TX NSA | DMJ9917(10.76.109.211) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:37 | 10/21/2025 20:47:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000940 | PCM-20251021-00002026 | TT-20251021-02065 | Reference_telecom | Region_1 | DMJB0086 | DMJB0086 |  |  |  | Meraj Husain Idd Baksh | 10/21/2025 17:16:39 | 10/21/2025 19:38:52 | 10/22/2025 05:16:39 | NEC MW Observing High BER at DMJB0086-1(10.248.32.40) | 10/19/2025 21:59:55 | Minor |  | LOF | 10/19/2025 21:59:55 | P1 | SRAN | dammam | Generator_SG | TX NSA | DMJB0086-1(10.248.32.40) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:39 | 10/21/2025 19:38:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000941 | PCM-20251021-00002027 | TT-20251021-02066 | Reference_telecom | Region_1 | DMJB0975 | DMJB0975 | Transsmission | MW_HW_fault | Replace Service Interface Board | Meraj Husain Idd Baksh | 10/21/2025 17:16:40 | 10/22/2025 22:33:22 | 10/22/2025 05:16:40 | NEC MW Observing Communication FAIL,High BER at DMJB0975-2(10.248.32.42) | 10/19/2025 21:56:01 | Minor |  | LOF | 10/19/2025 21:56:01 | P1 | SRAN | dammam | Generator_SG | TX NSA | DMJB0975-2(10.248.32.42) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:40 | 10/21/2025 19:38:53 | 10/22/2025 18:16:00 | 10/22/2025 18:16:03 | 10/22/2025 18:41:09 | 10/22/2025 22:33:22 |  | Meraj Husain Idd Baksh |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000942 | PCM-20251021-00002028 | TT-20251021-02067 | Reference_telecom | Region_1 | DMJR0157 | DMJR0157 |  |  |  | Muhammad Zubair Guilzar | 10/21/2025 17:16:41 | 10/21/2025 18:10:07 | 10/22/2025 05:16:41 | NEC MW Observing LOF,LOF,Frame ID,Frame ID at DMJR0157-4(10.76.111.72) | 10/19/2025 20:09:57 | Minor |  | LOF | 10/19/2025 20:09:57 | P1 | SRAN | arar | Generator_DG | TX NSA | DMJR0157-4(10.76.111.72) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:41 | 10/21/2025 18:10:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000943 | PCM-20251021-00002029 | TT-20251021-02068 | Reference_telecom | Region_1 | HFB0029 | HFB0029 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 17:16:42 | 10/21/2025 21:36:25 | 10/22/2025 05:16:42 | NEC MW Observing LOF,High BER,Frame ID,Low BER,LOF,LOF,Frame ID,LOF,Frame ID,LOF,Frame ID,Frame ID at HFB0029(10.74.86.106) | 10/19/2025 21:58:26 | Minor |  | LOF | 10/19/2025 21:58:26 | P3 | SRAN | hafouf | Generator_SG | TX NSA | HFB0029(10.74.86.106) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:42 | 10/21/2025 21:36:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000944 | PCM-20251021-00002030 | TT-20251021-02069 | Reference_telecom | Region_1 | HFB0030 | HFB0030 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 17:16:43 | 10/21/2025 21:36:26 | 10/22/2025 05:16:43 | NEC MW Observing LOF,Frame ID,LOF,Frame ID at HFB0030-2(10.74.86.109) | 10/19/2025 21:58:10 | Minor |  | LOF | 10/19/2025 21:58:10 | P3 | SRAN | hafouf | Generator_SG | TX NSA | HFB0030-2(10.74.86.109) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:43 | 10/21/2025 21:36:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000945 | PCM-20251021-00002031 | TT-20251021-02070 | Reference_telecom | Region_1 | HFB2004 | HFB2004 |  |  |  | Mohamed Magdy Fouad Zayed | 10/21/2025 17:16:44 | 10/21/2025 21:36:27 | 10/22/2025 05:16:44 | NEC MW Observing Low BER,Low BER at HFB2004 #2(10.74.86.71) | 10/19/2025 21:59:23 | Minor |  | LOF | 10/19/2025 21:59:23 | P1 | SRAN | hafouf | Sceco | TX NSA | HFB2004 #2(10.74.86.71) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:44 | 10/21/2025 21:36:27 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000946 | PCM-20251021-00002032 | TT-20251021-02071 | Reference_telecom | Region_1 | HFF0937 | HFF0937 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 17:16:45 | 10/22/2025 17:27:02 | 10/22/2025 05:16:45 | NEC MW Observing LOF,Frame ID at HFF0937(10.158.221.106) | 10/19/2025 21:22:13 | Minor |  | LOF | 10/19/2025 21:22:13 | P3 | SRAN | hafouf | Sceco | TX NSA | HFF0937(10.158.221.106) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:45 | 10/21/2025 18:10:53 | 10/22/2025 16:58:01 | 10/22/2025 16:58:05 | 10/22/2025 16:58:24 | 10/22/2025 17:27:02 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000947 | PCM-20251021-00002033 | TT-20251021-02072 | Reference_telecom | Region_1 | HFF6030 | HFF6030 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 17:16:46 | 10/21/2025 18:10:53 | 10/22/2025 05:16:46 | NEC MW Observing TX Power,ODU Alarm at HFF6030(10.158.221.107) | 10/19/2025 15:15:47 | Minor |  | LOF | 10/19/2025 15:15:47 | P3 | SRAN | hafouf | Sceco | TX NSA | HFF6030(10.158.221.107) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:46 | 10/21/2025 18:10:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000948 | PCM-20251021-00002034 | TT-20251021-01967 | Telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 17:16:46 | 10/21/2025 17:16:46 | 10/21/2025 23:16:46 | CELL SERVICE PROBLEM (Cell problem due to associated X2 links and/or NG links and/or E1 link unavailability) at JED1MN0035-NR2.6-P2 @ Sceco | 10/21/2025 16:38:22 | Major | 7114 | CELL SERVICE PROBLEM | 10/21/2025 16:38:14 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0035 | FLM_TE |  |  | PCM-20251021-00001945 | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site |  |  |  | API | 10/21/2025 17:16:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000949 | PCM-20251021-00002035 | TT-20251021-02073 | Reference_telecom | Region_1 | HFS0067 | HFS0067 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 17:16:47 | 10/21/2025 18:10:53 | 10/22/2025 05:16:47 | NEC MW Observing Low BER,Low BER at HFS0067(10.154.27.83) | 10/19/2025 19:56:02 | Minor |  | LOF | 10/19/2025 19:56:02 | P3 | SRAN | hafouf | Generator_SG | TX NSA | HFS0067(10.154.27.83) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:47 | 10/21/2025 18:10:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000950 | PCM-20251021-00002036 | TT-20251021-02074 | Reference_telecom | Region_1 | HFSW2019 | HFSW2019 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 17:16:48 | 10/21/2025 18:10:54 | 10/22/2025 05:16:48 | NEC MW Observing LOF,Frame ID,LOF,Frame ID,High BER,High BER,LOF,LOF at HFSW2019-2(10.248.32.137) | 10/19/2025 22:04:59 | Minor |  | LOF | 10/19/2025 22:04:59 | P1 | SRAN | hafouf | Generator_SG | TX NSA | HFSW2019-2(10.248.32.137) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:48 | 10/21/2025 18:10:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000952 | PCM-20251021-00002038 | TT-20251021-02076 | Reference_telecom | Region_1 | JBL2108 | JBL2108 |  |  |  | Tahir Mahmood Hafiz Yar | 10/21/2025 17:16:51 | 10/21/2025 20:47:40 | 10/22/2025 05:16:51 | NEC MW Observing LOF at JBL2108-Access 4(10.154.13.225) | 10/19/2025 21:58:49 | Minor |  | LOF | 10/19/2025 21:58:49 | P1 | SRAN | jubail | Generator_DG | TX NSA | JBL2108-Access 4(10.154.13.225) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:51 | 10/21/2025 20:47:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000953 | PCM-20251021-00002039 | TT-20251021-02077 | Reference_telecom | Region_1 | JBL2139 | JBL2139 |  |  |  | Rafiq Ahmed Elturifi | 10/21/2025 17:16:51 | 10/21/2025 20:54:30 | 10/22/2025 05:16:51 | NEC MW Observing LOF,RX Level at JBL2139(10.76.111.198) | 10/19/2025 15:35:35 | Minor |  | LOF | 10/19/2025 15:35:35 | P2 | SRAN | jubail | Generator_SG | TX NSA | JBL2139(10.76.111.198) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:51 | 10/21/2025 20:54:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000954 | PCM-20251021-00002040 | TT-20251021-02078 | Reference_telecom | Region_4 | JDJZ0768 | JDJZ0768 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 17:16:53 | 10/22/2025 13:09:31 | 10/22/2025 05:16:53 | NEC MW Observing SBY TX Bus Error at JDJZ0768_2(10.154.111.195) | 10/19/2025 18:46:43 | Minor |  | LOF | 10/19/2025 18:46:43 | P1 | 2G | qunfuddah | Generator_DG | TX NSA | JDJZ0768_2(10.154.111.195) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:53 | 10/22/2025 13:09:31 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000955 | PCM-20251021-00002041 | TT-20251021-02079 | Reference_telecom | Region_4 | JDJZ0769 | JDJZ0769 |  |  |  | Riasat Ali Allah Baksh | 10/21/2025 17:16:54 | 10/22/2025 13:09:32 | 10/22/2025 05:16:54 | NEC MW Observing LOF,LOF,LOF,LOF,Radio Traffic Aggregation Link,Radio Traffic Aggregation Link at JDJZ0769 TO NNL0168 PLL2(10.88.224.51) | 10/19/2025 16:35:17 | Minor |  | LOF | 10/19/2025 16:35:17 | P1 | 2G | qunfuddah | Sceco_STB | TX NSA | JDJZ0769 TO NNL0168 PLL2(10.88.224.51) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:54 | 10/22/2025 13:09:32 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000956 | PCM-20251021-00002042 | TT-20251021-02080 | Reference_telecom | Region_4 | JED0017 | JED0017 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 17:16:55 | 10/21/2025 17:16:55 | 10/22/2025 05:16:55 | NEC MW Observing LOF,Frame ID,High BER at JED0017_A3(10.154.153.17) | 10/13/2025 00:46:02 | Minor |  | LOF | 10/13/2025 00:46:02 | P1 | 2G | jeddah | Sceco | TX NSA | JED0017_A3(10.154.153.17) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:55 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000957 | PCM-20251021-00002043 | TT-20251021-02081 | Reference_telecom | Region_4 | JED0110 | JED0110 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 17:16:56 | 10/21/2025 17:23:36 | 10/22/2025 05:16:56 | NEC MW Observing TX Power,ODU Alarm at JED0110_2(10.1.165.90) | 10/19/2025 11:10:15 | Minor |  | LOF | 10/19/2025 11:10:15 | VIP | 2G | jeddah | Sceco | TX NSA | JED0110_2(10.1.165.90) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:56 | 10/21/2025 17:23:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000958 | PCM-20251021-00002044 | TT-20251021-02082 | Reference_telecom | Region_4 | JED0400 | JED0400 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 17:16:57 | 10/21/2025 17:23:37 | 10/22/2025 05:16:57 | NEC MW Observing Frame ID at JED0400(10.1.165.169) | 10/19/2025 18:40:21 | Minor |  | LOF | 10/19/2025 18:40:21 | P2 | 2G | jeddah | Sceco | TX NSA | JED0400(10.1.165.169) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:57 | 10/21/2025 17:23:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000959 | PCM-20251021-00002045 | TT-20251021-02083 | Reference_telecom | Region_4 | JED0686 | JED0686 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 17:16:58 | 10/21/2025 17:23:39 | 10/22/2025 05:16:58 | NEC MW Observing Frame ID,LOF at JED0686_JED6025(10.154.146.12) | 10/19/2025 17:45:33 | Minor |  | LOF | 10/19/2025 17:45:33 | P2 | 2G | jeddah | Sceco | TX NSA | JED0686_JED6025(10.154.146.12) | FLM_TE | [8 empty] | API | 10/21/2025 17:16:58 | 10/21/2025 17:23:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000960 | PCM-20251021-00002046 | TT-20251021-02084 | Reference_telecom | Region_4 | JED6101 | JED6101 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 17:17:00 | 10/21/2025 17:58:18 | 10/22/2025 05:17:00 | NEC MW Observing LOF,Frame ID at JED6101(10.1.165.89) | 10/19/2025 18:35:24 | Minor |  | LOF | 10/19/2025 18:35:24 | P3 | 2G | jeddah | Sceco | TX NSA | JED6101(10.1.165.89) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:00 | 10/21/2025 17:58:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000961 | PCM-20251021-00002047 | TT-20251021-02085 | Reference_telecom | Region_1 | KBR0202 | KBR0202 |  |  |  | Imran Ali Yousaf | 10/21/2025 17:17:00 | 10/21/2025 18:10:46 | 10/22/2025 05:17:00 | NEC MW Observing LOF,Frame ID at KBR0202-1(10.1.218.170) | 10/19/2025 22:01:23 | Minor |  | LOF | 10/19/2025 22:01:23 | P1 | SRAN | dammam | Sceco | TX NSA | KBR0202-1(10.1.218.170) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:00 | 10/21/2025 18:10:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000962 | PCM-20251021-00002048 | TT-20251021-02086 | Reference_telecom | Region_1 | KFKM0790 | KFKM0790 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/21/2025 17:17:02 | 10/21/2025 20:47:34 | 10/22/2025 05:17:02 | NEC MW Observing Low BER at KFKM0790(10.147.11.230) | 10/09/2025 01:55:50 | Minor |  | LOF | 10/09/2025 01:55:50 | P3 | SRAN | hafr | Generator_SG | TX NSA | KFKM0790(10.147.11.230) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:02 | 10/21/2025 20:47:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000963 | PCM-20251021-00002049 | TT-20251021-02087 | Reference_telecom | Region_6 | KHS0563 | KHS0563 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/21/2025 17:17:03 | 10/21/2025 18:29:08 | 10/22/2025 05:17:03 | NEC MW Observing ODU CPU / Cable Open,LOF at KHS0563-1(10.89.220.84) | 10/07/2025 12:06:08 | Minor |  | LOF | 10/07/2025 12:06:08 | P2 | 2G | khamis mushyet | Sceco | TX NSA | KHS0563-1(10.89.220.84) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:03 | 10/21/2025 18:29:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000964 | PCM-20251021-00002050 | TT-20251021-02088 | Reference_telecom | Region_3 | MDHL0380 | MDHL0380 |  |  |  | Mohamed Naveed | 10/21/2025 17:17:04 | 10/21/2025 20:41:00 | 10/22/2025 05:17:04 | NEC MW Observing LOF,RX Level,LOF,Frame ID,Frame ID,RX Level,Frame ID,RX Level,RX Level,Frame ID,LOF,LOF at MDHL0380-MDHL0379(10.253.0.134) | 09/14/2025 12:34:48 | Minor |  | LOF | 09/14/2025 12:34:48 | P1 | SRAN | hail | Sceco_STB | TX NSA | MDHL0380-MDHL0379(10.253.0.134) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:04 | 10/21/2025 20:41:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000965 | PCM-20251021-00002051 | TT-20251021-02089 | Reference_telecom | Region_3 | MDTB0342 | MDTB0342 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/21/2025 17:17:05 | 10/21/2025 23:34:59 | 10/22/2025 05:17:05 | NEC MW Observing Frame ID,LOF at MDTB0342-MDTB0341(10.154.66.69) | 10/17/2025 09:18:53 | Minor |  | LOF | 10/17/2025 09:18:53 | P1 | SRAN | tabouk | Sceco | TX NSA | MDTB0342-MDTB0341(10.154.66.69) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:05 | 10/21/2025 23:34:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000967 | PCM-20251021-00002053 | TT-20251021-02091 | Reference_telecom | Region_3 | MDTB9339 | MDTB9339 |  |  |  | Ibrahim Mohammad AbdulMalik alraee | 10/21/2025 17:17:07 | 10/21/2025 23:35:00 | 10/22/2025 05:17:07 | NEC MW Observing High BER at MDTB9339-MDTB0340(10.154.66.72) | 10/18/2025 07:56:53 | Minor |  | LOF | 10/18/2025 07:56:53 | P3 | Repeater | madinah | Sceco | TX NSA | MDTB9339-MDTB0340(10.154.66.72) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:07 | 10/21/2025 23:35:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000968 | PCM-20251021-00002054 | TT-20251021-02092 | Reference_telecom | Region_4 | MKMD0561 | MKMD0561 |  |  |  | Khizer Hayat | 10/21/2025 17:17:09 | 10/21/2025 17:20:08 | 10/22/2025 05:17:09 | NEC MW Observing LAN Link,LAN Link,LAG Link at MKMD0561_1(10.154.119.210) | 09/30/2025 14:03:33 | Minor |  | LOF | 09/30/2025 14:03:33 | P2 | 2G | jeddah | Sceco | TX NSA | MKMD0561_1(10.154.119.210) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:09 | 10/21/2025 17:20:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000970 | PCM-20251021-00002056 | TT-20251021-02094 | Reference_telecom | Region_1 | RSK2234 | RSK2234 |  |  |  | Mohamed Abdelaziz | 10/21/2025 17:17:11 | 10/21/2025 19:01:30 | 10/22/2025 05:17:11 | NEC MW Observing LOF,ODU CPU / Cable Open at RSK2234(10.76.116.227) | 10/19/2025 18:21:26 | Minor |  | LOF | 10/19/2025 18:21:26 | P3 | SRAN | jubail | Generator_SG | TX NSA | RSK2234(10.76.116.227) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:11 | 10/21/2025 19:01:30 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000972 | PCM-20251021-00002058 | TT-20251021-02096 | Reference_telecom | Region_6 | SBAR0706 | SBAR0706 | Transsmission | SFP_Transmission | Reset SFP | Zeshan Ali Adnan | 10/21/2025 17:17:13 | 10/22/2025 00:55:00 | 10/22/2025 05:17:13 | NEC MW Observing LOF,TX Bus Error,RX Level at SBAR0706-2(10.154.172.125) | 10/12/2025 18:59:56 | Minor |  | LOF | 10/12/2025 18:59:56 | P3 | 2G | jizan | Sceco | TX NSA | SBAR0706-2(10.154.172.125) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:13 | 10/21/2025 22:29:54 | 10/22/2025 00:54:27 |  |  | 10/22/2025 00:55:00 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000973 | PCM-20251021-00002059 | TT-20251021-02097 | Reference_telecom | Region_6 | SDA0425 | SDA0425 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 17:17:14 | 10/21/2025 17:20:20 | 10/22/2025 05:17:14 | NEC MW Observing MODEM Power Supply Alarm at SDA0425(10.154.163.186) | 08/10/2025 17:31:34 | Minor |  | LOF | 08/10/2025 17:31:34 | P3 | 2G | abha | Sceco | TX NSA | SDA0425(10.154.163.186) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:14 | 10/21/2025 17:20:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000974 | PCM-20251021-00002060 | TT-20251021-02098 | Reference_telecom | Region_6 | SDA0425 | SDA0425 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 17:17:16 | 10/21/2025 17:20:21 | 10/22/2025 05:17:16 | NEC MW Observing XIF,MODEM Power Supply Alarm,MODEM Power Supply Alarm,MODEM Power Supply Alarm at SDA0425(10.154.163.202) | 10/07/2025 20:07:01 | Minor |  | LOF | 10/07/2025 20:07:01 | P3 | 2G | abha | Sceco | TX NSA | SDA0425(10.154.163.202) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:16 | 10/21/2025 17:20:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000975 | PCM-20251021-00002061 | TT-20251021-02099 | Reference_telecom | Region_4 | SQR9442 | SQR9442 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/21/2025 17:17:17 | 10/21/2025 19:28:22 | 10/22/2025 05:17:17 | NEC MW Observing LOF,RX Level at SQR9442(10.88.220.200) | 10/07/2025 10:52:03 | Minor |  | LOF | 10/07/2025 10:52:03 | P3 | Repeater | alaith | Generator_SG | TX NSA | SQR9442(10.88.220.200) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:17 | 10/21/2025 19:28:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000976 | PCM-20251021-00002062 | TT-20251021-02100 | Reference_telecom | Region_4 | TFBH0893 | TFBH0893 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 17:17:19 | 10/22/2025 17:30:00 | 10/22/2025 05:17:19 | NEC MW Observing RX Level,LOF at TFBH0893(10.154.143.66) | 10/19/2025 17:06:22 | Minor |  | LOF | 10/19/2025 17:06:22 | P1 | 2G | taif | Sceco_STB | TX NSA | TFBH0893(10.154.143.66) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:19 | 10/22/2025 17:30:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000977 | PCM-20251021-00002063 | TT-20251021-02101 | Reference_telecom | Region_4 | TFBH9443 | TFBH9443 |  |  |  | Asad Ur Rehman | 10/21/2025 17:17:20 | 10/23/2025 00:11:58 | 10/22/2025 05:17:20 | NEC MW Observing Communication FAIL at TFBH9443(10.88.221.215) | 09/26/2025 15:27:46 | Minor |  | LOF | 09/26/2025 15:27:46 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9443(10.88.221.215) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000978 | PCM-20251021-00002064 | TT-20251021-02102 | Reference_telecom | Region_4 | TFBH9451 | TFBH9451 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 17:17:21 | 10/22/2025 17:30:01 | 10/22/2025 05:17:21 | NEC MW Observing LAG Link,LAN Link,LAN Link at TFBH9451-4(10.88.224.22) | 10/15/2025 17:10:24 | Minor |  | LOF | 10/15/2025 17:10:24 | P1 | Repeater | taif | Generator_DG | TX NSA | TFBH9451-4(10.88.224.22) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:21 | 10/22/2025 17:30:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000979 | PCM-20251021-00002065 | TT-20251021-02103 | Reference_telecom | Region_6 | TLT0376 | TLT0376 |  |  |  | Umair Abbas Muhammad Abbas | 10/21/2025 17:17:22 | 10/21/2025 19:28:41 | 10/22/2025 05:17:22 | NEC MW Observing LOF,RX Level at TLT0376-2(10.89.221.136) | 10/20/2025 11:14:35 | Minor |  | LOF | 10/20/2025 11:14:35 | P3 | 2G | turaib | Generator_SG | TX NSA | TLT0376-2(10.89.221.136) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:22 | 10/21/2025 19:28:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000980 | PCM-20251021-00002066 | TT-20251021-02104 | Reference_telecom | Region_6 | ARS0017 | ARS0017 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/21/2025 17:17:23 | 10/22/2025 16:37:29 | 10/22/2025 05:17:23 | Nokia Eband Observing LagPortDown-Port 3/5,Degrade-LAG 1 at ARS0017_07-10.21.71.113 | 09/10/2025 15:29:43 | Minor |  | LOF | 09/10/2025 15:29:43 | P1 | 2G | jizan | Sceco | TX NSA | ARS0017_07-10.21.71.113 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:23 | 10/21/2025 22:29:55 | 10/22/2025 16:36:17 | 10/22/2025 16:37:13 |  | 10/22/2025 16:37:29 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000981 | PCM-20251021-00002067 | TT-20251021-02105 | Reference_telecom | Region_6 | ABH0289 | ABH0289 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 17:17:24 | 10/21/2025 17:20:21 | 10/22/2025 05:17:24 | Nokia Eband Observing ReplaceableUnitProblem-fanTray-1,FanFailure-fanTra at ABH0289 _02-10.10.154.196 | 10/20/2025 14:14:23 | Minor |  | LOF | 10/20/2025 14:14:23 | P3 | 2G | abha | Sceco | TX NSA | ABH0289 _02-10.10.154.196 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:24 | 10/21/2025 17:20:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000982 | PCM-20251021-00002068 | TT-20251021-02106 | Reference_telecom | Region_6 | TLT0743 | TLT0743 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/21/2025 17:17:25 | 10/21/2025 19:24:46 | 10/22/2025 05:17:25 | Nokia Eband Observing ReplaceableUnitMissing-Port 1/5,ReplaceableUnitMis at TLT0743-2-10.221.245.161 | 10/20/2025 13:26:32 | Minor |  | LOF | 10/20/2025 13:26:32 | P1 | 2G | tathleeth | Sceco_STB | TX NSA | TLT0743-2-10.221.245.161 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:25 | 10/21/2025 19:06:24 | 10/21/2025 19:24:38 |  |  | 10/21/2025 19:24:46 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000983 | PCM-20251021-00002069 | TT-20251021-02107 | Reference_telecom | Region_6 | ABH0086 | ABH0086 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 17:17:27 | 10/21/2025 17:20:22 | 10/22/2025 05:17:27 | Nokia Eband Observing ReplaceableUnitMissing-Card - 5 at ABH0086-2-10.10.152.219 | 10/20/2025 12:41:10 | Minor |  | LOF | 10/20/2025 12:41:10 | P2 | 2G | abha | Sceco | TX NSA | ABH0086-2-10.10.152.219 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:27 | 10/21/2025 17:20:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000984 | PCM-20251021-00002070 | TT-20251021-02108 | Reference_telecom | Region_6 | ARS0017 | ARS0017 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/21/2025 17:17:28 | 10/22/2025 16:36:08 | 10/22/2025 05:17:28 | Nokia Eband Observing Degrade-LAG 1 at ARS0017-10-10.10.150.241 | 09/04/2025 06:20:40 | Minor |  | LOF | 09/04/2025 06:20:40 | P1 | 2G | jizan | Sceco | TX NSA | ARS0017-10-10.10.150.241 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:28 | 10/21/2025 22:29:56 | 10/22/2025 16:35:50 |  |  | 10/22/2025 16:36:08 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021000985 | PCM-20251021-00002071 | TT-20251021-02109 | Reference_telecom | Region_5 | MAK0231 | MAK0231 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 17:17:29 | 10/21/2025 17:17:29 | 10/22/2025 05:17:29 | Nokia Eband Observing ReplaceableUnitMissing-Port 1/8 at MAK0231-1-10.10.178.242 | 10/20/2025 17:47:43 | Minor |  | LOF | 10/20/2025 17:47:43 | VIP | 2G | makkah | Sceco | TX NSA | MAK0231-1-10.10.178.242 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:29 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000986 | PCM-20251021-00002072 | TT-20251021-02110 | Reference_telecom | Region_6 | TLT0722 | TLT0722 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/21/2025 17:17:30 | 10/21/2025 19:25:12 | 10/22/2025 05:17:30 | Nokia Eband Observing LossOfSignal-Port 1/7 at TLT0722_01-10.74.121.83 | 10/20/2025 20:46:42 | Minor |  | LOF | 10/20/2025 20:46:42 | P3 | 2G | tathleeth | Sceco | TX NSA | TLT0722_01-10.74.121.83 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:30 | 10/21/2025 19:06:25 | 10/21/2025 19:25:05 |  |  | 10/21/2025 19:25:12 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000987 | PCM-20251021-00002073 | TT-20251021-02111 | Reference_telecom | Region_6 | TLT0743 | TLT0743 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/21/2025 17:17:31 | 10/21/2025 19:24:13 | 10/22/2025 05:17:31 | Nokia Eband Observing Degrade-LAG 2,LossOfSignal-Port 6/5 at TLT0743_04-10.74.121.81 | 10/20/2025 17:09:35 | Minor |  | LOF | 10/20/2025 17:09:35 | P1 | 2G | tathleeth | Sceco_STB | TX NSA | TLT0743_04-10.74.121.81 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:31 | 10/21/2025 19:06:26 | 10/21/2025 19:24:06 |  |  | 10/21/2025 19:24:13 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000988 | PCM-20251021-00002074 | TT-20251021-02112 | Reference_telecom | Region_4 | JED2596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 17:17:32 | 10/21/2025 18:53:05 | 10/22/2025 05:17:32 | Nokia Eband Observing InternalCommunicationProblem-Port 4/5,ReplaceableU at JED2596-10.1.230.53 | 10/20/2025 18:05:32 | Minor |  | LOF | 10/20/2025 18:05:32 | P1 | 2G | jeddah | Sceco | TX NSA | JED2596-10.1.230.53 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:32 | 10/21/2025 18:53:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251020001082 | PCM-20251020-00002314 | TT-20251020-02311 | EM | Region_1 | RYDM0061 | RYDM0061 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 10/20/2025 21:16:56 | 10/20/2025 23:16:16 | 10/21/2025 03:16:56 | Mains Failure at RYDM0061-P1-HUB_SRAN @ Sceco_STB | 10/20/2025 21:06:46 | Major | 65109 | Mains Failure | 10/20/2025 21:06:42 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | RYDM0061 | FLM_EM | [8 empty] | API | 10/20/2025 21:16:56 | 10/20/2025 22:59:54 | 10/20/2025 23:16:07 |  |  | 10/20/2025 23:16:16 |  | Ahmed AbdELmoaz Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251020001154 | PCM-20251020-00002448 | TT-20251020-02418 | EM | Region_2 | RIY2917 | RIY2917 |  |  |  | Zeeshan Haider Iftikhar Ahmad Faridi | 10/20/2025 23:23:55 | 10/21/2025 09:34:35 | 10/21/2025 05:23:55 | Mains Failure at RIY2917-P1-VIP_SRAN @ Generator_SG | 10/20/2025 23:13:46 | Major | 65109 | Mains Failure | 10/20/2025 23:13:44 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2917 | FLM_EM | [8 empty] | API | 10/20/2025 23:23:55 | 10/21/2025 09:34:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000019 | PCM-20251021-00000047 | TT-20251021-00062 | Reference_EM | Region_2 | DUB0015 | DUB0015 | Enviroment | Genset failure_Fan Belt | Change Fan Belt | Fritz Ian Generale | 10/21/2025 00:42:31 | 10/21/2025 02:03:07 | 10/21/2025 12:42:31 | Generator failure at DUB0015-P3-USF_SRAN-PC @ Power Cube | 10/21/2025 00:32:04 | Minor | 65114 | Generator failure | 10/21/2025 00:32:01 | P3 | SRAN | al kharj | Power Cube | 2G NSA | DUB0015 | FLM_EM | [8 empty] | API | 10/21/2025 00:42:31 | 10/21/2025 02:00:17 | 10/21/2025 02:00:23 | 10/21/2025 02:00:29 | 10/21/2025 02:00:32 | 10/21/2025 02:03:07 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021000024 | PCM-20251021-00000061 | TT-20251021-00072 | Reference_EM | Region_2 | RIY0446 | RIY0446 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 00:48:41 | 10/22/2025 17:49:45 | 10/21/2025 12:48:41 | Minor Rec alarm at RIY0446-P2_SRAN @ Sceco | 10/21/2025 00:38:22 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:38:19 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0446 | FLM_EM | [8 empty] | API | 10/21/2025 00:48:41 | 10/22/2025 17:49:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000030 | PCM-20251021-00000071 | TT-20251021-00082 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 01:01:36 | 10/22/2025 17:49:45 | 10/21/2025 13:01:36 | Minor Rec alarm at RIY0349-P2_SRAN @ Sceco | 10/21/2025 00:50:55 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:50:49 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/21/2025 01:01:36 | 10/22/2025 17:49:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000031 | PCM-20251021-00000072 | TT-20251021-00083 | EM | Region_2 | RIY0261 | RIY0261 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 01:02:10 | 10/22/2025 17:49:46 | 10/21/2025 13:02:10 | Minor Rec alarm at RIY0261-P2_SRAN @ Sceco | 10/21/2025 00:53:05 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:51:40 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0261 | FLM_EM | [8 empty] | API | 10/21/2025 01:02:10 | 10/22/2025 17:49:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000032 | PCM-20251021-00000074 | TT-20251021-00085 | EM | Region_2 | RIY0251 | RIY0251 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/21/2025 01:02:12 | 10/22/2025 11:21:12 | 10/21/2025 07:02:12 | Air condition 1 failure alarm at RIY0251-P1-VIP_SRAN @ Sceco | 10/21/2025 00:53:25 | Major | 65104 | Air condition 1 failure alarm | 10/21/2025 00:51:42 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0251 | FLM_EM | [8 empty] | API | 10/21/2025 01:02:12 | 10/22/2025 11:21:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000033 | PCM-20251021-00000077 | TT-20251021-00088 | EM | Region_2 | RIY2059 | RIY2059 |  |  |  | Kadri Jalal Mohammed Asmail | 10/21/2025 01:02:40 | 10/22/2025 11:33:25 | 10/21/2025 13:02:40 | Minor Rec alarm at RIY2059-P3_SRAN @ Sceco | 10/21/2025 00:53:47 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:52:00 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2059 | FLM_EM | [8 empty] | API | 10/21/2025 01:02:40 | 10/21/2025 09:21:42 | [6 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000034 | PCM-20251021-00000079 | TT-20251021-00090 | EM | Region_2 | RIY0366 | RIY0366 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/21/2025 01:02:41 | 10/22/2025 11:21:13 | 10/21/2025 13:02:41 | Minor Rec alarm at RIY0366-P2_SRAN @ Sceco | 10/21/2025 00:53:33 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:51:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0366 | FLM_EM | [8 empty] | API | 10/21/2025 01:02:41 | 10/22/2025 11:21:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000035 | PCM-20251021-00000075 | TT-20251021-00086 | EM | Region_2 | RIY0219 | RIY0219 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 01:02:43 | 10/22/2025 17:49:46 | 10/21/2025 13:02:43 | Air condition 2 failure alarm at RIY0219-P2_SRAN @ Sceco | 10/21/2025 00:53:16 | Minor | 65105 | Air condition 2 failure alarm | 10/21/2025 00:51:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0219 | FLM_EM | [8 empty] | API | 10/21/2025 01:02:43 | 10/22/2025 17:49:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000036 | PCM-20251021-00000076 | TT-20251021-00087 | EM | Region_2 | RIY0246 | RIY0246 | Enviroment | Rectifier Module | Change rectifer module | Ajmal Hafeez Hafeez Ahmed Awan | 10/21/2025 01:02:44 | 10/23/2025 11:58:42 | 10/21/2025 13:02:44 | Minor Rec alarm at RIY0246-P2_SRAN @ Sceco | 10/21/2025 00:53:22 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:52:09 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0246 | FLM_EM | [8 empty] | API | 10/21/2025 01:02:44 | 10/23/2025 11:23:10 | 10/23/2025 11:23:15 | 10/23/2025 11:23:18 | 10/23/2025 11:23:22 | 10/23/2025 11:58:42 |  | Ajmal Hafeez Hafeez Ahmed Awan | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000039 | PCM-20251021-00000082 | TT-20251021-00094 | EM | Region_2 | RIY0220 | RIY0220 |  |  |  | Adham Adham Hassan Farghal | 10/21/2025 01:04:11 | 10/21/2025 13:42:33 | 10/21/2025 13:04:11 | Minor Rec alarm at RIY0220-P2_SRAN @ Sceco | 10/21/2025 00:54:34 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:53:28 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0220 | FLM_EM | [8 empty] | API | 10/21/2025 01:04:11 | 10/21/2025 13:42:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000041 | PCM-20251021-00000083 | TT-20251021-00096 | Reference_EM | Region_2 | RIY2340 | RIY2340 | Enviroment | Rectifier Module | Change rectifer module | Vignesh Sivakumar Sivakumar | 10/21/2025 01:05:46 | 10/22/2025 15:58:25 | 10/21/2025 13:05:46 | Minor Rec alarm at RIY2340-P3_SRAN @ Sceco | 10/21/2025 00:55:27 | Minor | 65108 | Minor Rec alarm | 10/21/2025 00:55:23 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2340 | FLM_EM | [8 empty] | API | 10/21/2025 01:05:46 | 10/22/2025 14:40:23 | 10/22/2025 15:23:00 | 10/22/2025 15:23:03 | 10/22/2025 15:23:12 | 10/22/2025 15:58:25 |  | Vignesh Sivakumar Sivakumar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251021000044 | PCM-20251021-00000087 | TT-20251021-00100 | Reference_EM | Region_2 | RIY2107 | RIY2107 |  |  |  | Pawan Virdi Santokh Singh | 10/21/2025 01:06:46 | 10/22/2025 13:48:57 | 10/21/2025 13:06:46 | Mains Failure at RIY2107-P3_SRAN-PC @ Sceco | 10/21/2025 00:56:25 | Minor | 65109 | Mains Failure | 10/21/2025 00:56:21 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2107 | FLM_EM | [8 empty] | API | 10/21/2025 01:06:46 | 10/21/2025 01:06:53 | 10/22/2025 13:31:38 | 10/22/2025 13:31:42 | 10/22/2025 13:48:57 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000045 | PCM-20251021-00000088 | TT-20251021-00101 | EM | Region_2 | RIY2237 | RIY2237 | Enviroment | Fire Alarm | Reset Fire Pannel | Ahmed Mohamed Ibrahim Elnagar | 10/21/2025 01:06:47 | 10/22/2025 11:14:55 | 10/21/2025 13:06:47 | Mains Failure at RIY2237-P3_SRAN-PC @ Sceco | 10/21/2025 00:56:33 | Minor | 65109 | Mains Failure | 10/21/2025 00:56:29 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2237 | FLM_EM | [8 empty] | API | 10/21/2025 01:06:47 | 10/21/2025 01:44:12 | 10/22/2025 11:10:40 | 10/22/2025 11:10:49 | 10/22/2025 11:10:53 | 10/22/2025 11:14:55 |  | Ahmed Mohamed Ibrahim Elnagar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000046 | PCM-20251021-00000089 | TT-20251021-00102 | EM | Region_2 | RIY2563 | RIY2563 | Enviroment | SCECO_Failure | SCECO auto restored | Moin Uddin | 10/21/2025 01:06:48 | 10/22/2025 16:34:12 | 10/21/2025 13:06:48 | Mains Failure at RIY2563-P3_SRAN-PC @ Sceco | 10/21/2025 00:56:37 | Minor | 65109 | Mains Failure | 10/21/2025 00:56:33 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2563 | FLM_EM | [8 empty] | API | 10/21/2025 01:06:48 | 10/22/2025 10:30:57 | 10/22/2025 16:23:50 | 10/22/2025 16:23:53 | 10/22/2025 16:23:57 | 10/22/2025 16:34:12 |  | Moin Uddin |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000048 | PCM-20251021-00000093 | TT-20251021-00106 | Reference_EM | Region_1 | DAM0362 | DAM0362 |  |  |  | Ibrahim said mohamed Elmarhoumy | 10/21/2025 01:12:30 | 10/21/2025 02:06:55 | 10/21/2025 07:12:30 | high temprature 40 at DAM0362-P1-HUB_SRAN @ Sceco | 10/21/2025 01:02:12 | Major | 65103 | high temprature 40 | 10/21/2025 01:02:07 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0362 | FLM_EM | [8 empty] | API | 10/21/2025 01:12:30 | 10/21/2025 02:06:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000110 | PCM-20251021-00000338 | TT-20251021-00363 | EM | Region_1 | DMJR0166 | DMJR0166 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Ragab Farg Abdel Nabi Bekhatro | 10/21/2025 02:38:16 | 10/21/2025 04:11:53 | 10/21/2025 08:38:16 | Mains Failure at DMJR0166-P1-HUB_SRAN @ Generator_SG | 10/21/2025 02:28:11 | Major | 65109 | Mains Failure | 10/21/2025 02:28:08 | P1 | SRAN | arar | Generator_SG | 2G NSA | DMJR0166 | FLM_EM | [8 empty] | API | 10/21/2025 02:38:16 | 10/21/2025 03:04:11 | 10/21/2025 03:04:16 | 10/21/2025 03:04:18 | 10/21/2025 04:10:58 | 10/21/2025 04:11:53 |  | Ragab Farg Abdel Nabi Bekhatro |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000129 | PCM-20251021-00000399 | TT-20251021-00427 | Reference_EM | Region_2 | RIY2230 | RIY2230 | Enviroment | Fire Alarm | Change smoke sensor | Adham Adham Hassan Farghal | 10/21/2025 03:10:18 | 10/22/2025 20:17:48 | 10/21/2025 09:10:18 | Low battery voltage at RIY2230-P1-DIA_SRAN-PC @ Sceco | 10/21/2025 02:59:52 | Major | 65110 | Low battery voltage | 10/21/2025 02:59:49 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY2230 | FLM_EM | [8 empty] | API | 10/21/2025 03:10:18 | 10/21/2025 13:42:34 | 10/22/2025 19:48:19 | 10/22/2025 19:48:22 | 10/22/2025 19:48:29 | 10/22/2025 20:17:48 |  | Adham Adham Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021000131 | PCM-20251021-00000408 | TT-20251021-00443 | EM | Region_1 | DAM0033 | DAM0033 |  |  |  | Ibrahim said mohamed Elmarhoumy | 10/21/2025 03:15:26 | 10/21/2025 04:25:19 | 10/21/2025 15:15:26 | Door opening alarm at DAM0033-P2_SRAN @ Sceco | 10/21/2025 03:14:44 | Minor | 65101 | Door opening alarm | 10/21/2025 03:14:41 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0033 | FLM_EM | [8 empty] | API | 10/21/2025 03:15:26 | 10/21/2025 04:25:19 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000198 | PCM-20251021-00000582 | TT-20251021-00643 | EM | Region_1 | HFR2488 | HFR2488 | Enviroment | SCECO_Failure | SCECO auto restored | Reda Mohammed Mohamed Hassanein | 10/21/2025 05:49:20 | 10/22/2025 19:27:23 | 10/21/2025 17:49:20 | Mains Failure at HFR2488-P3_SRAN-PC @ Sceco | 10/21/2025 05:39:23 | Minor | 65109 | Mains Failure | 10/21/2025 05:39:20 | P3 | SRAN | hafr | Sceco | 2G NSA | HFR2488 | FLM_EM | [8 empty] | API | 10/21/2025 05:49:20 | 10/21/2025 06:04:43 | 10/22/2025 19:27:16 |  |  | 10/22/2025 19:27:23 |  | Reda Mohammed Mohamed Hassanein |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251021000288 | PCM-20251021-00000824 | TT-20251021-00860 | EM | Region_1 | HMBY2123 | HMBY2123 |  |  |  | Isslam Abdelrahman Abdelkader Aziz | 10/21/2025 08:07:51 | 10/21/2025 20:18:57 | 10/21/2025 20:07:51 | Mains Failure at HMBY2123-P3_SRAN @ Generator_SG | 10/21/2025 07:57:36 | Minor | 65109 | Mains Failure | 10/21/2025 07:57:32 | P3 | SRAN | dammam | Generator_SG | 2G NSA | HMBY2123 | FLM_EM | [8 empty] | API | 10/21/2025 08:07:51 | 10/21/2025 08:11:47 | 10/21/2025 20:18:42 | 10/21/2025 20:18:46 | 10/21/2025 20:18:57 | [6 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000291 | PCM-20251021-00000835 | TT-20251021-00872 | Reference_EM | Region_2 | RIY0612 | RIY0612 | Enviroment | Rectifier Module | Change rectifer module | Ahmed Mohamed Ibrahim Elnagar | 10/21/2025 08:14:01 | 10/22/2025 14:06:20 | 10/21/2025 20:14:01 | Minor Rec alarm at RIY0612-P2_SRAN @ Sceco | 10/21/2025 08:03:16 | Minor | 65108 | Minor Rec alarm | 10/21/2025 08:03:13 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0612 | FLM_EM | [8 empty] | API | 10/21/2025 08:14:01 | 10/22/2025 11:15:02 | 10/22/2025 13:47:35 | 10/22/2025 13:47:44 | 10/22/2025 13:48:43 | 10/22/2025 14:06:20 |  | Ahmed Mohamed Ibrahim Elnagar | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021000303 | PCM-20251021-00000855 | TT-20251021-00891 | EM | Region_1 | JBKH0069 | JBKH0069 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/21/2025 08:26:56 | 10/21/2025 09:08:26 | 10/21/2025 14:26:56 | Mains Failure at JBKH0069-P1-HUB_SRAN @ Generator_DG | 10/21/2025 08:16:58 | Major | 65109 | Mains Failure | 10/21/2025 08:16:55 | P1 | SRAN | jubail | Generator_DG | 2G NSA | JBKH0069 | FLM_EM | [8 empty] | API | 10/21/2025 08:26:56 | 10/21/2025 09:08:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021000306 | PCM-20251021-00000864 | TT-20251021-00896 | Reference_EM | Region_1 | KFJ2490 | KFJ2490 |  |  |  | Dileesh Muringothil Devarajan | 10/21/2025 08:31:01 | 10/21/2025 17:13:21 | 10/21/2025 20:31:01 | Air condition 1 failure alarm at KFJ2490-P2_SRAN @ Sceco | 10/21/2025 08:20:46 | Minor | 65104 | Air condition 1 failure alarm | 10/21/2025 08:20:42 | P2 | SRAN | khafji | Sceco | 2G NSA | KFJ2490 | FLM_EM | [8 empty] | API | 10/21/2025 08:31:01 | 10/21/2025 17:13:21 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000310 | PCM-20251021-00000883 | TT-20251021-00920 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 08:38:16 | 10/22/2025 17:49:47 | 10/21/2025 20:38:16 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/21/2025 08:27:54 | Minor | 65107 | Major Rec alarm | 10/21/2025 08:27:51 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/21/2025 08:38:16 | 10/22/2025 17:49:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000314 | PCM-20251021-00000892 | TT-20251021-00928 | EM | Region_1 | DAM0313 | DAM0313 | Enviroment | Fire Alarm | Reset Fire Pannel | Abdul Malik Shaik | 10/21/2025 08:43:25 | 10/21/2025 11:51:50 | 10/21/2025 12:43:25 | Door opening alarm at DAM0313-P1-DIA-WDM_SRAN @ Sceco | 10/21/2025 08:42:52 | Critical | 65101 | Door opening alarm | 10/21/2025 08:42:49 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0313 | FLM_EM | [8 empty] | API | 10/21/2025 08:43:25 | 10/21/2025 11:16:16 | 10/21/2025 11:25:20 | 10/21/2025 11:25:26 | 10/21/2025 11:49:31 | 10/21/2025 11:51:50 |  | Abdul Malik Shaik |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251021000326 | PCM-20251021-00000911 | TT-20251021-00937 | Reference_EM | Region_1 | JBL0598 | JBL0598 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/21/2025 08:52:46 | 10/21/2025 09:08:27 | 10/21/2025 20:52:46 | Mains Failure at JBL0598-P2_SRAN @ Generator_SG | 10/21/2025 08:42:28 | Minor | 65109 | Mains Failure | 10/21/2025 08:42:25 | P2 | SRAN | jubail | Generator_SG | 2G NSA | JBL0598 | FLM_EM | [8 empty] | API | 10/21/2025 08:52:46 | 10/21/2025 09:08:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000359 | PCM-20251021-00000970 | TT-20251021-00996 | EM | Region_2 | KHJ9021 | KHJ9021 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Fritz Ian Generale | 10/21/2025 09:28:56 | 10/22/2025 09:41:26 | 10/21/2025 13:28:56 | RELAY_ALARM_CRITICAL at KHJ9021_NE_1 @ Power Cube | 10/21/2025 09:27:59 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/21/2025 09:27:48 | P1 | Repeater | al kharj | Power Cube | TX NSA | KHJ9021 | FLM_EM | [8 empty] | API | 10/21/2025 09:28:56 | 10/21/2025 23:56:21 | 10/22/2025 09:41:08 |  |  | 10/22/2025 09:41:26 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021000361 | PCM-20251021-00000972 | TT-20251021-00998 | Reference_EM | Region_1 | HMBY2007 | HMBY2007 |  |  |  | Yasser Mohamed Abdelnabi Ibrahim | 10/21/2025 09:29:56 | 10/22/2025 03:52:05 | 10/21/2025 21:29:56 | Mains Failure at HMBY2007-P3_SRAN @ Generator_SG | 10/21/2025 09:19:33 | Minor | 65109 | Mains Failure | 10/21/2025 09:19:29 | P3 | SRAN | dammam | Generator_SG | 2G NSA | HMBY2007 | FLM_EM | [8 empty] | API | 10/21/2025 09:29:56 | 10/22/2025 03:52:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251021000384 | PCM-20251021-00001025 | TT-20251021-01049 | Reference_EM | Region_2 | DLM0485 | DLM0485 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/21/2025 09:57:50 | 10/21/2025 09:57:50 | 10/21/2025 21:57:50 | high temprature 32 at DLM0485-P2_SRAN @ Sceco | 10/21/2025 09:47:22 | Minor | 65102 | high temprature 32 | 10/21/2025 09:47:18 | P2 | SRAN | al kharj | Sceco | 2G NSA | DLM0485 | FLM_EM | [8 empty] | API | 10/21/2025 09:57:50 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000396 | PCM-20251021-00001061 | TT-20251021-01081 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/21/2025 10:11:15 | 10/21/2025 13:42:34 | 10/21/2025 16:11:15 | high temprature 40 at RIY0232-P1_SRAN @ Sceco | 10/21/2025 10:00:56 | Major | 65103 | high temprature 40 | 10/21/2025 10:00:52 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/21/2025 10:11:15 | 10/21/2025 13:42:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000400 | PCM-20251021-00001066 | TT-20251021-01086 | EM | Region_1 | DBS0014 | DBS0014 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Bashir Sahib Rahman | 10/21/2025 10:12:52 | 10/22/2025 10:07:01 | 10/21/2025 22:12:52 | Door opening at DBS2M7014-P3-PC @ Power Cube | 10/21/2025 10:12:03 | Minor | 65101 | Door opening | 10/21/2025 10:05:44 | P3 | 4G | quriyat | Power Cube | 2G NSA | DBS2M7014 | FLM_EM | [8 empty] | API | 10/21/2025 10:12:52 | 10/22/2025 10:05:43 | 10/22/2025 10:06:49 |  |  | 10/22/2025 10:07:01 |  | Ahmed Bashir Sahib Rahman |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000411 | PCM-20251021-00001090 | TT-20251021-01108 | Reference_EM | Region_1 | HFF0821 | HFF0821 |  |  |  | Moustafa Mohamed Saleh Saif | 10/21/2025 10:24:43 | 10/21/2025 11:34:14 | 10/21/2025 22:24:43 | high temprature 40 at HFF0821-P2-USF_SRAN-PC @ Power Cube | 10/21/2025 10:13:58 | Minor | 65103 | high temprature 40 | 10/21/2025 10:13:55 | P2 | SRAN | hafouf | Power Cube | 2G NSA | HFF0821 | FLM_EM | [8 empty] | API | 10/21/2025 10:24:43 | 10/21/2025 11:34:14 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000423 | PCM-20251021-00001109 | TT-20251021-01127 | EM | Region_1 | JBKH0069 | JBKH0069 |  |  |  | Nabawy Salah Ibrahim Loulah | 10/21/2025 10:31:56 | 10/21/2025 10:33:17 | 10/21/2025 16:31:56 | Door opening alarm at JBKH0069-P1-HUB_SRAN @ Generator_DG | 10/21/2025 10:31:16 | Major | 65101 | Door opening alarm | 10/21/2025 10:31:14 | P1 | SRAN | jubail | Generator_DG | 2G NSA | JBKH0069 | FLM_EM | [8 empty] | API | 10/21/2025 10:31:56 | 10/21/2025 10:33:17 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251021000426 | PCM-20251021-00001113 | TT-20251021-01132 | Reference_EM | Region_1 | DMAP0750 | DMAP0750 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/21/2025 10:34:01 | 10/21/2025 22:03:13 | 10/21/2025 16:34:01 | Mains Failure at DMAP0750-P1-VIP-HUB_SRAN @ Generator_SG | 10/21/2025 10:23:38 | Major | 65109 | Mains Failure | 10/21/2025 10:23:34 | VIP | SRAN | dammam | Generator_SG | 2G NSA | DMAP0750 | FLM_EM | [8 empty] | API | 10/21/2025 10:34:01 | 10/21/2025 22:00:49 | 10/21/2025 22:03:06 |  |  | 10/21/2025 22:03:13 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251021000454 | PCM-20251021-00001174 | TT-20251021-01191 | EM | Region_1 | SMRY0817 | SMRY0817 |  |  |  | Samir Elzain Abdu Gumaa | 10/21/2025 11:07:01 | 10/21/2025 11:07:01 | 10/21/2025 23:07:01 | Door opening alarm at SMRY0817-P3-USF_SRAN @ Generator_SG | 10/21/2025 11:06:37 | Minor | 65101 | Door opening alarm | 10/21/2025 11:06:34 | P3 | SRAN | hafr | Generator_SG | 2G NSA | SMRY0817 | FLM_EM | [8 empty] | API | 10/21/2025 11:07:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000484 | PCM-20251021-00001231 | TT-20251021-01247 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/21/2025 11:35:28 | 10/21/2025 13:03:27 | 10/21/2025 17:35:28 | high temprature 32 at DAM2066-P1-HUB_SRAN @ Sceco | 10/21/2025 11:00:43 | Major | 65102 | high temprature 32 | 10/21/2025 11:24:53 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/21/2025 11:35:28 | 10/21/2025 13:03:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000498 | PCM-20251021-00001255 | TT-20251021-01274 | Reference_EM | Region_2 | RIY0518 | RIY0518 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 11:43:46 | 10/22/2025 17:49:47 | 10/21/2025 23:43:46 | Minor Rec alarm at RIY0518-P2_SRAN @ Sceco | 10/21/2025 11:33:00 | Minor | 65108 | Minor Rec alarm | 10/21/2025 11:32:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0518 | FLM_EM | [8 empty] | API | 10/21/2025 11:43:46 | 10/22/2025 17:49:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000502 | PCM-20251021-00001260 | TT-20251021-01281 | Reference_EM | Region_2 | HIR0543 | HIR0543 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/21/2025 11:45:50 | 10/22/2025 17:49:48 | 10/21/2025 23:45:50 | high temprature 32 at HIR0543-P2_SRAN @ Sceco | 10/21/2025 11:35:24 | Minor | 65102 | high temprature 32 | 10/21/2025 11:35:20 | P2 | SRAN | riyadh | Sceco | 2G NSA | HIR0543 | FLM_EM | [8 empty] | API | 10/21/2025 11:45:50 | 10/22/2025 17:49:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000510 | PCM-20251021-00001281 | TT-20251021-01300 | Reference_EM | Region_1 | SAR0067 | SAR0067 | Equipment | FAN Cleaning | Clean FAN | Abdelrahim Ateem Ali Adam | 10/21/2025 11:58:11 | 10/22/2025 13:27:04 | 10/21/2025 17:58:11 | Low battery voltage at SAR0067-P1-USF-HUB_SRAN @ Generator_SG | 10/21/2025 11:47:53 | Major | 65110 | Low battery voltage | 10/21/2025 11:47:49 | P1 | SRAN | sakaka | Generator_SG | 2G NSA | SAR0067 | FLM_EM | [8 empty] | API | 10/21/2025 11:58:11 | 10/21/2025 13:46:52 | 10/21/2025 13:47:04 | 10/21/2025 13:47:10 | 10/21/2025 13:47:23 | 10/22/2025 13:27:04 |  | Abdelrahim Ateem Ali Adam |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000515 | PCM-20251021-00001291 | TT-20251021-01306 | EM | Region_1 | DAM0321 | DAM0321 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 12:06:25 | 10/21/2025 16:28:33 | 10/22/2025 00:06:25 | Door opening alarm at DAM0321-P2_SRAN @ Sceco | 10/21/2025 12:05:59 | Minor | 65101 | Door opening alarm | 10/21/2025 12:05:55 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0321 | FLM_EM | [8 empty] | API | 10/21/2025 12:06:25 | 10/21/2025 16:28:33 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000520 | PCM-20251021-00001300 | TT-20251021-01320 | EM | Region_1 | ABQ2508 | ABQ2508 |  |  |  | Abdul Malik Shaik | 10/21/2025 12:14:46 | 10/22/2025 11:57:12 | 10/22/2025 00:14:46 | Air condition 1 failure alarm at ABQ2508-P2-USF_SRAN-PC @ Power Cube | 10/21/2025 12:04:29 | Minor | 65104 | Air condition 1 failure alarm | 10/21/2025 12:04:24 | P2 | SRAN | dammam | Power Cube | 2G NSA | ABQ2508 | FLM_EM | [8 empty] | API | 10/21/2025 12:14:46 | 10/22/2025 11:57:12 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000524 | PCM-20251021-00001318 | TT-20251021-01338 | EM | Region_1 | DMJR0137 | DMJR0137 | Enviroment | Air Condition | Change Fan | Emad Mahmoud Ahmed Mohamed | 10/21/2025 12:19:20 | 10/23/2025 10:52:39 | 10/21/2025 16:19:20 | AMBIENT_TEMP_FLUCT at DMJR0137_HYB @ Sceco_STB | 10/21/2025 12:17:29 | Critical | 1-13987 | AMBIENT_TEMP_FLUCT | 10/21/2025 12:17:22 | P2 | SRAN | hafr | Sceco_STB | DWDM NSA | DMJR0137 | FLM_EM | [5 empty] | 1-(1-B) |  |  | API | 10/21/2025 12:19:20 | 10/21/2025 15:06:10 | 10/23/2025 10:52:27 |  |  | 10/23/2025 10:52:39 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251021000531 | PCM-20251021-00001331 | TT-20251021-01353 | EM | Region_1 | NRY0582 | NRY0582 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/21/2025 12:28:11 | 10/22/2025 02:05:05 | 10/22/2025 00:28:11 | Door opening alarm at NRY0582-P3-USF_SRAN-PC @ Power Cube | 10/21/2025 12:27:32 | Minor | 65101 | Door opening alarm | 10/21/2025 12:27:28 | P3 | SRAN | jubail | Power Cube | 2G NSA | NRY0582 | FLM_EM | [8 empty] | API | 10/21/2025 12:28:11 | 10/22/2025 02:05:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000535 | PCM-20251021-00001338 | TT-20251021-01364 | EM | Region_1 | DAM0319 | DAM0319 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 12:31:46 | 10/21/2025 16:28:34 | 10/22/2025 00:31:46 | Door opening alarm at DAM0319-P2_SRAN @ Sceco | 10/21/2025 12:31:26 | Minor | 65101 | Door opening alarm | 10/21/2025 12:31:23 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0319 | FLM_EM | [8 empty] | API | 10/21/2025 12:31:46 | 10/21/2025 16:28:34 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251021000544 | PCM-20251021-00001355 | TT-20251021-01378 | Reference_EM | Region_2 | HRHT0132 | HRHT0132 |  |  |  | ABUZAR Ahmed Humida Mustafa | 10/21/2025 12:36:27 | 10/21/2025 12:36:27 | 10/22/2025 00:36:27 | Generator failure at HRHT0132-P3_SRAN-PC @ Power Cube | 10/21/2025 12:25:45 | Minor | 65114 | Generator failure | 10/21/2025 12:25:40 | P3 | SRAN | al kharj | Power Cube | 2G NSA | HRHT0132 | FLM_EM | [8 empty] | API | 10/21/2025 12:36:27 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000693 | PCM-20251021-00001515 | TT-20251021-01538 | EM | Region_1 | HFF2162 | HFF2162 |  |  |  | Moustafa Mohamed Saleh Saif | 10/21/2025 12:49:21 | 10/23/2025 01:46:23 | 10/21/2025 18:49:21 | Door opening alarm at HFF2162-P1-HUB_SRAN @ Sceco | 10/21/2025 12:49:01 | Major | 65101 | Door opening alarm | 10/21/2025 12:48:57 | P1 | SRAN | hafouf | Sceco | 2G NSA | HFF2162 | FLM_EM | [8 empty] | API | 10/21/2025 12:49:21 | 10/23/2025 01:46:23 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000711 | PCM-20251021-00001562 | TT-20251021-01588 | EM | Region_1 | HMBY2420 | HMBY2420 |  |  |  | Abdul Malik Shaik | 10/21/2025 13:15:40 | 10/22/2025 11:57:13 | 10/22/2025 01:15:40 | NETECO: AC Failure at HMBY2420 @ Sceco | 10/21/2025 13:09:15 | Minor | 10202 | AC Failure | 10/21/2025 13:09:15 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2420 | FLM_EM | [8 empty] | API | 10/21/2025 13:15:40 | 10/22/2025 11:57:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251021000717 | PCM-20251021-00001570 | TT-20251021-01595 | EM | Region_1 | HMBY2420 | HMBY2420 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Samir Farahat Allam | 10/21/2025 13:19:21 | 10/22/2025 03:48:45 | 10/22/2025 01:19:21 | Mains Failure at HMBY2420-P3_SRAN @ Sceco | 10/21/2025 13:09:20 | Minor | 65109 | Mains Failure | 10/21/2025 13:09:16 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2420 | FLM_EM | [8 empty] | API | 10/21/2025 13:19:21 | 10/21/2025 15:40:58 | 10/21/2025 15:41:05 | 10/21/2025 15:41:07 | 10/21/2025 15:41:10 | 10/22/2025 03:48:45 |  | Mohamed Samir Farahat Allam |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021000722 | PCM-20251021-00001580 | TT-20251021-01606 | EM | Region_1 | JBL0966 | JBL0966 |  |  |  | Hamid Bilal Bashir Ahmed | 10/21/2025 13:25:01 | 10/21/2025 15:31:24 | 10/22/2025 01:25:01 | Mains Failure at JBL2M1966-P2 @ Sceco | 10/21/2025 13:15:03 | Minor | 65109 | Mains Failure | 10/21/2025 13:14:58 | P2 | 2G | jubail | Sceco | 2G NSA | JBL2M1966 | FLM_EM | [8 empty] | API | 10/21/2025 13:25:01 | 10/21/2025 15:31:24 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000725 | PCM-20251021-00001582 | TT-20251021-01609 | EM | Region_1 | SLW9002 | SLW9002 |  |  |  | Nazar Mohammed Siddig Abdalla | 10/21/2025 13:27:06 | 10/23/2025 08:25:53 | 10/21/2025 17:27:06 | RELAY_ALARM_CRITICAL at SLW9002_NE_2 @ Power Cube | 10/21/2025 13:26:12 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/21/2025 13:26:01 | P3 | Repeater | hafouf | Power Cube | TX NSA | SLW9002 | FLM_EM | [8 empty] | API | 10/21/2025 13:27:06 | 10/23/2025 08:25:53 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000730 | PCM-20251021-00001591 | TT-20251021-01614 | EM | Region_1 | DAM0384 | DAM0384 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 13:31:41 | 10/21/2025 16:28:35 | 10/22/2025 01:31:41 | Door opening alarm at DAM0384-P2_SRAN @ Sceco | 10/21/2025 13:31:06 | Minor | 65101 | Door opening alarm | 10/21/2025 13:31:01 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0384 | FLM_EM | [8 empty] | API | 10/21/2025 13:31:41 | 10/21/2025 16:28:35 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000731 | PCM-20251021-00001594 | TT-20251021-01616 | EM | Region_1 | SLW9002 | SLW9002 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazar Mohammed Siddig Abdalla | 10/21/2025 13:32:46 | 10/23/2025 08:47:16 | 10/22/2025 01:32:46 | NETECO: Smart D.G. Start Failure at SLW9002 @ Power Cube | 10/21/2025 13:25:56 | Minor | 8101 | Smart D.G. Start Failure | 10/21/2025 13:25:56 | P3 | Repeater | hafouf | Power Cube | 2G NSA | SLW9002 | FLM_EM | [8 empty] | API | 10/21/2025 13:32:46 | 10/23/2025 08:25:54 | 10/23/2025 08:47:09 |  |  | 10/23/2025 08:47:16 |  | Nazar Mohammed Siddig Abdalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000739 | PCM-20251021-00001610 | TT-20251021-01624 | EM | Region_1 | DAM0389 | DAM0389 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 13:42:35 | 10/21/2025 16:28:36 | 10/21/2025 17:42:35 | Door opening alarm at DAM0389-FWA-P1-VIP-HUB-WDM_SRAN @ Sceco | 10/21/2025 13:41:51 | Critical | 65101 | Door opening alarm | 10/21/2025 13:41:47 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0389 | FLM_EM | [8 empty] | API | 10/21/2025 13:42:35 | 10/21/2025 16:28:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251021000742 | PCM-20251021-00001619 | TT-20251021-01634 | EM | Region_1 | DMJR2263 | DMJR2263 | Equipment | PMR_Power_Cable_RRU | Change Port on DCDU | Mahmoud Youssef Mohamed Ahmed | 10/21/2025 13:46:11 | 10/22/2025 06:04:47 | 10/22/2025 01:46:11 | Door opening alarm at DMJR2263-P3-USF_SRAN @ Generator_DG | 10/21/2025 13:45:46 | Minor | 65101 | Door opening alarm | 10/21/2025 13:45:43 | P3 | SRAN | hafr | Generator_DG | 2G NSA | DMJR2263 | FLM_EM | [8 empty] | API | 10/21/2025 13:46:11 | 10/22/2025 06:02:24 | 10/22/2025 06:04:33 |  |  | 10/22/2025 06:04:47 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000760 | PCM-20251021-00001656 | TT-20251021-01670 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/21/2025 14:05:46 | 10/22/2025 21:40:47 | 10/22/2025 02:05:46 | Door opening alarm at SMN0805-P3_SRAN @ Generator_DG | 10/21/2025 14:05:00 | Minor | 65101 | Door opening alarm | 10/21/2025 14:04:57 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/21/2025 14:05:46 | 10/22/2025 21:40:47 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021000852 | PCM-20251021-00001841 | TT-20251021-01851 | EM | Region_1 | ARR9807 | ARR9807 | Transsmission | MW_loop | Remote action done by BO by removing VLAN loop | Ismail Salah Ismail Elbery | 10/21/2025 15:48:06 | 10/22/2025 13:21:02 | 10/22/2025 03:48:06 | NETECO: Genset Fault at ARR9807 @ Generator_SG | 10/21/2025 15:41:31 | Minor | 40564 | Genset Fault | 10/21/2025 15:41:31 | P3 | Repeater | rafha | Generator_SG | 2G NSA | ARR9807 | FLM_EM | [8 empty] | API | 10/21/2025 15:48:06 | 10/22/2025 13:20:38 | 10/22/2025 13:20:57 |  |  | 10/22/2025 13:21:02 |  | Ismail Salah Ismail Elbery |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021000989 | PCM-20251021-00002075 | TT-20251021-02113 | Reference_telecom | Region_4 | JED0001 | JED0001 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 17:17:33 | 10/21/2025 17:28:55 | 10/22/2025 05:17:33 | Nokia Eband Observing DemFail-Port 4/5 at JED0001-19-10.10.188.81 | 10/20/2025 14:22:25 | Minor |  | LOF | 10/20/2025 14:22:25 | P1 | 2G | jeddah | Sceco | TX NSA | JED0001-19-10.10.188.81 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:33 | 10/21/2025 17:28:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000990 | PCM-20251021-00002076 | TT-20251021-02114 | Reference_telecom | Region_6 | ARS0017 | ARS0017 | Equipment | SFP_BTS | Clean SFP | Zeshan Ali Adnan | 10/21/2025 17:17:34 | 10/22/2025 15:08:28 | 10/22/2025 05:17:34 | Nokia Eband Observing BandwidthDegradeForProtectionSwitch-ethRing-10.21. at ARS0017_03-10.21.77.49 | 09/07/2025 11:58:51 | Minor |  | LOF | 09/07/2025 11:58:51 | P1 | 2G | jizan | Sceco | TX NSA | ARS0017_03-10.21.77.49 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:34 | 10/21/2025 22:29:56 | 10/22/2025 15:07:33 |  |  | 10/22/2025 15:08:28 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000991 | PCM-20251021-00002077 | TT-20251021-02115 | Reference_telecom | Region_6 | TNM0728 | TNM0728 |  |  |  | Muhammad Jamal Khan Abbas Ali | 10/21/2025 17:17:35 | 10/22/2025 00:11:16 | 10/22/2025 05:17:35 | NEC MW Observing Radio Traffic Aggregation Link at TNM0728(10.154.162.241) | 09/19/2025 22:03:52 | Minor |  | LOF | 09/19/2025 22:03:52 | P3 | 2G | mohail | Sceco | TX NSA | TNM0728(10.154.162.241) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:35 | 10/22/2025 00:11:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000992 | PCM-20251021-00002078 | TT-20251021-02116 | Reference_telecom | Region_4 | BHR0308 | BHR0308 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 17:17:37 | 10/21/2025 17:28:55 | 10/22/2025 05:17:37 | Nokia Eband Observing LossOfSignal-Port 4/5,InternalCommunicationProblem at BHR0308-10.10.188.82 | 10/20/2025 15:05:43 | Minor |  | LOF | 10/20/2025 15:05:43 | P1 | 2G | jeddah | Sceco | TX NSA | BHR0308-10.10.188.82 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:37 | 10/21/2025 17:28:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000993 | PCM-20251021-00002079 | TT-20251021-02117 | Reference_telecom | Region_3 | YBDB0293 | YBDB0293 |  |  |  | Hossam Ali Ahmed Ali | 10/21/2025 17:17:38 | 10/21/2025 17:48:22 | 10/22/2025 05:17:38 | NEC MW Observing High BER,LOF,Frame ID at YBDB0293(10.159.108.230) | 10/18/2025 11:51:09 | Minor |  | LOF | 10/18/2025 11:51:09 | P1 | SRAN | tabouk | Generator_DG | TX NSA | YBDB0293(10.159.108.230) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:38 | 10/21/2025 17:48:22 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000994 | PCM-20251021-00002080 | TT-20251021-02118 | Reference_telecom | Region_6 | KMS0586 | KMS0586 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/21/2025 17:17:38 | 10/21/2025 18:29:09 | 10/22/2025 05:17:38 | Nokia Eband Observing DialogFailure-Port 1/3 at KMS0586-10.74.123.117 | 10/20/2025 14:23:49 | Minor |  | LOF | 10/20/2025 14:23:49 | P3 | 2G | Khamis Mushait | Sceco | TX NSA | KMS0586-10.74.123.117 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:38 | 10/21/2025 18:29:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000995 | PCM-20251021-00002081 | TT-20251021-02119 | Reference_telecom | Region_4 | JED0942 | JED0942 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 17:17:40 | 10/21/2025 17:28:56 | 10/22/2025 05:17:40 | Nokia Eband Observing HouseKeeping-auxIn-14,HouseKeeping-auxIn-13,HouseK at JED0942-10.10.184.227 | 10/20/2025 08:05:52 | Minor |  | LOF | 10/20/2025 08:05:52 | P2 | 2G | jeddah | Sceco | TX NSA | JED0942-10.10.184.227 | FLM_TE | [8 empty] | API | 10/21/2025 17:17:40 | 10/21/2025 17:28:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021000996 | PCM-20251021-00002082 | TT-20251021-02120 | Reference_telecom | Region_3 | YBDB0290 | YBDB0290 |  |  |  | Muhammad Sajjad R3 | 10/21/2025 17:17:41 | 10/22/2025 17:26:58 | 10/22/2025 05:17:41 | NEC MW Observing ETH LOS at YBDB0290-YBDB0291(10.159.108.211) | 10/14/2025 05:29:21 | Minor |  | LOF | 10/14/2025 05:29:21 | P1 | SRAN | yanbu | Generator_DG | TX NSA | YBDB0290-YBDB0291(10.159.108.211) | FLM_TE | [8 empty] | API | 10/21/2025 17:17:41 | 10/22/2025 17:26:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021000998 | PCM-20251021-00002088 | TT-20251021-02044 | Telecom | Region_4 | MLJI1M3187 | MLJI0187 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TOSIF AHMED - MUHAMMAD SHARIF | 10/21/2025 17:19:10 | 10/21/2025 19:28:58 | 10/21/2025 23:19:10 | 1(3G) sites down under MLJI0187-P2-USF/MLJI1M3187-P2-USF @ Sceco | 10/21/2025 17:11:35 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 17:10:56 | P2 | 3G | alaith | Sceco | 3G SA | MLJI0187-P2-USF | FLM_TE | MLJI0187 | Results: DOWN SITE HUB MLJI0187-P2-USF MLJI0187 Summary: Hub: MLJI0187, Down Count: 1, Down Sites: MLJI0187-P2-USF Alarm Summary: MLJI0187 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 17:19:10 | 10/21/2025 19:28:26 | 10/21/2025 19:28:43 |  |  | 10/21/2025 19:28:58 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001004 | PCM-20251021-00002101 | TT-20251021-00681 | Reference_telecom | Region_6 | KHNJ1M8241 | KHNJ2241 | Transsmission | MW_Problematic | Interference Issue | Bilal Anwar Khurshid Anwar | 10/21/2025 17:24:51 | 10/22/2025 01:12:34 | 10/22/2025 05:24:51 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHNJ1M8241-CA-L800-P3-SBTS @ Sceco | 10/21/2025 04:37:08 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 04:22:51 | P3 | 4G | al harja | Sceco | LTE NSA | KHNJ1M8241 | FLM_TE |  |  | PCM-20251021-00002096 | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site |  |  |  | API | 10/21/2025 17:24:51 | 10/21/2025 17:26:03 | 10/22/2025 01:12:17 |  |  | 10/22/2025 01:12:34 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001005 | PCM-20251021-00002102 | TT-20251021-02141 | Reference_telecom | Region_6 | KHNJ0849 | KHNJ0849 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Bilal Anwar Khurshid Anwar | 10/21/2025 17:24:58 | 10/22/2025 04:32:47 | 10/22/2025 05:24:58 | LossOfSignal observed in KHNJ0849_02 towards 10.74.121.225 @ Sceco_STB | 10/21/2025 05:25:23 | Minor |  | LossOfSignal | 10/21/2025 05:24:28 | P1 | 2G | al harja | Sceco_STB | TX NSA | KHNJ0849 | FLM_TE | [8 empty] | API | 10/21/2025 17:24:58 | 10/21/2025 17:26:07 | 10/22/2025 04:32:30 |  |  | 10/22/2025 04:32:47 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001006 | PCM-20251021-00002103 | TT-20251021-00730 | Reference_telecom | Region_6 | KHNJ1M8242 | KHNJ2242 | Transsmission | MW_Problematic | Interference Issue | Bilal Anwar Khurshid Anwar | 10/21/2025 17:25:02 | 10/22/2025 01:12:09 | 10/22/2025 05:25:02 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHNJ1M8242-CA-L800-P3-SBTS @ Generator_SG | 10/21/2025 05:25:46 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 05:01:02 | P3 | 4G | al harja | Generator_SG | LTE NSA | KHNJ1M8242 | FLM_TE |  |  | PCM-20251021-00002095 | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site | FLM need to check HW Module ,SFP and Optical Cable on the site also check power input at site |  |  |  | API | 10/21/2025 17:25:02 | 10/21/2025 17:26:09 | 10/22/2025 01:11:45 |  |  | 10/22/2025 01:12:09 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001007 | PCM-20251021-00002106 | TT-20251021-02146 | Telecom | Region_4 | RYMK0528-LL-CSG | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 17:26:33 | 10/22/2025 07:52:55 | 10/21/2025 21:26:33 | The Device is offline at RYMK0528-LL-CSG @ Generator_SG | 10/21/2025 17:25:57 | Critical | 101-7 | The Device is offline | 10/21/2025 17:25:56 | P1 | IPRAN | taif | Generator_SG | IPRAN SA | RYMK0528-LL-CSG | FLM_TE | [8 empty] | API | 10/21/2025 17:26:33 | 10/22/2025 07:52:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001009 | PCM-20251021-00002108 | TT-20251021-02150 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/21/2025 17:28:06 | 10/21/2025 22:26:30 | 10/22/2025 05:28:06 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 17:19:52 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/21/2025 17:19:42 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/21/2025 17:28:06 | 10/21/2025 22:26:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021001010 | PCM-20251021-00002109 | TT-20251021-02151 | Reference_telecom | Region_5 | MAK6018 | MAK6018 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/21/2025 17:28:36 | 10/21/2025 17:28:36 | 10/22/2025 05:28:36 | RF Unit RX Channel RTWP/RSSI Unbalanced at MAK6018-DCU-P3 @ Sceco | 10/21/2025 14:28:30 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/21/2025 14:28:27 | P3 | SRAN | makkah | Sceco | 2G NSA | MAK6018 | FLM_TE | [8 empty] | API | 10/21/2025 17:28:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001014 | PCM-20251021-00002113 | TT-20251021-01587 | Telecom | Region_2 | RYD-SR-01 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/21/2025 17:30:22 | 10/21/2025 17:30:22 | 10/22/2025 05:30:22 | Bad Package Error Rising at RYD-SR-01 @ Sceco_STB | 10/21/2025 13:14:38 | Minor | 101-2501403 | Bad Package Error Rising | 10/21/2025 13:14:32 | P1 | IPBB | riyadh | Sceco_STB | IPRAN NSA | RYD-SR-01 | FLM_TE |  |  | PCM-20251021-00001784 | dears , do physical troubleshoot | dears , do physical troubleshoot |  |  |  | API | 10/21/2025 17:30:22 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001019 | PCM-20251021-00002130 | TT-20251021-02153 | Telecom | Region_4 | RYMK0528 | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 17:46:04 | 10/22/2025 07:52:55 | 10/21/2025 21:46:04 | 2(2G) 2(3G) 2(LTE) sites down under RYMK0528-P1,RYMK0665-P3/RYMK0665-P3 @ Generator_DG | 10/21/2025 17:26:18 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 17:26:13 | P1 | 2G | taif | Generator_SG | 2G_3G_LTE SA | RYMK0528-P1 2G_3G_LTE,RYMK0665-P3 2G_3G | FLM_TE | RYMK0528 | Results: DOWN SITE HUB RYMK0528-P1 RYMK0528 RYMK0665-P3 RYMK0665 Summary: Hub: RYMK0528, Down Count: 1, Down Sites: RYMK0528-P1 Hub: RYMK0665, Down Count: 1, Down Sites: RYMK0665-P3 Alarm Summary: RYMK0528 Alarm Active on HUB RYMK0665 Alarm Active on HUB | PCM-20251021-00002121 | HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . | HUB: RYMK0528 Kindly check with IPRAN as HUB is P2 . |  | sites down |  | API | 10/21/2025 17:46:04 | 10/22/2025 07:52:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001020 | PCM-20251021-00002131 | TT-20250922-01783 | MW_HC | Region_6 | ABH0162 | ABH0162 |  |  |  | Muhammad Jamshaid Muhammad Ashraf | 10/21/2025 17:46:37 | 10/21/2025 18:26:51 | 10/22/2025 05:46:37 | Nokia MW HC_P1 Observing Performance Issue at ABH0119-ABH0162_03 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0119-ABH0162_03 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251021-00002126 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/21/2025 17:46:37 | 10/21/2025 18:26:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001022 | PCM-20251021-00002134 | TT-20251021-02183 | EM | Region_4 | JDJZ2000 | JDJZ2000 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/21/2025 17:48:44 | 10/22/2025 08:43:26 | 10/22/2025 05:48:44 | SHELTER DOOR OPEN at JDJZ2000-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/21/2025 17:48:30 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 17:48:23 | P3 | 2G | qunfuddah | Generator_SG | 2G NSA | JDJZ2000 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 17:48:44 | 10/22/2025 08:43:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001025 | PCM-20251021-00002137 | TT-20251021-02184 | Telecom | Region_3 | HLV0081 | HLV0081 | Equipment | PMR_Power_Cable_RRU | Replace Indoor Power Connector | Atif Shahzad Muhammad Ajaib | 10/21/2025 17:51:33 | 10/21/2025 17:57:47 | 10/21/2025 23:51:33 | Local Cell Unusable at HLV0081-P2_SRAN @ Sceco | 10/21/2025 17:50:15 | Major | 28203 | Local Cell Unusable | 10/21/2025 17:48:39 | P2 | SRAN | hail | Sceco | 3G SA | HLV0081 | FLM_TE | [8 empty] | API | 10/21/2025 17:51:33 | 10/21/2025 17:57:30 | 10/21/2025 17:57:36 |  |  | 10/21/2025 17:57:47 |  | Atif Shahzad Muhammad Ajaib |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001029 | PCM-20251021-00002143 | TT-20251021-02190 | Telecom | Region_2 | RIY2042 | RIY2042 | Equipment | SFP_BTS | Re-Plug SFP | Waseem Shahzad Ghulam Rasool | 10/21/2025 17:55:59 | 10/21/2025 19:45:37 | 10/21/2025 23:55:59 | BBU CPRI Interface Error at RIY2042-P2_SRAN @ Sceco | 10/21/2025 17:53:15 | Major | 26234 | BBU CPRI Interface Error | 10/21/2025 17:50:43 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2042 | FLM_TE | [8 empty] | API | 10/21/2025 17:55:59 | 10/21/2025 18:14:14 | 10/21/2025 18:57:25 | 10/21/2025 18:57:27 | 10/21/2025 18:57:29 | 10/21/2025 19:45:37 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001030 | PCM-20251021-00002144 | TT-20251021-02193 | EM | Region_4 | JED1U6729 | JED6029 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/21/2025 17:59:36 | 10/22/2025 20:21:08 | 10/22/2025 05:59:36 | Rectifier Low battery voltage at JED1U6729-G9-L18-L21-SBTS-P3 @ Sceco | 10/21/2025 17:51:17 | Minor | 7103 | Rectifier Low battery voltage | 10/21/2025 17:51:09 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6729 | FLM_EM | [5 empty] | Rectifier Low battery voltage |  |  | API | 10/21/2025 17:59:36 | 10/22/2025 20:21:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001040 | PCM-20251021-00002175 | TT-20251021-02222 | Telecom | Region_4 | JED1M7498 | JED0498 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 18:17:10 | 10/21/2025 19:40:42 | 10/21/2025 22:17:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7498-CA-L800-L900-P1-HUB-WDM @ Sceco | 10/21/2025 18:16:34 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 18:16:24 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7498 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 18:17:10 | 10/21/2025 19:40:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001042 | PCM-20251021-00002179 | TT-20251021-02230 | Reference_EM | Region_3 | MDV0071 | MDV0071 | Enviroment | SCECO_Failure | SCECO auto restored | Ayman Mohamed Sayed Ahmed | 10/21/2025 18:19:45 | 10/23/2025 09:16:43 | 10/22/2025 06:19:45 | DC power fail at MDV0071-P2_SRAN @ Sceco | 10/21/2025 18:09:35 | Minor | 65106 | DC power fail | 10/21/2025 18:09:31 | P3 | SRAN | madinah | Sceco | 2G NSA | MDV0071 | FLM_EM | [8 empty] | API | 10/21/2025 18:19:45 | 10/22/2025 14:05:06 | 10/22/2025 14:05:19 | 10/22/2025 14:05:29 | 10/22/2025 14:30:56 | 10/23/2025 09:16:43 |  | Ayman Mohamed Sayed Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001043 | PCM-20251021-00002181 | TT-20251021-02237 | Reference_telecom | Region_2 | ARS0171 | ARS0171 |  |  |  | Syed Sibtain Naqvi SyedManzoor | 10/21/2025 18:21:18 | 10/21/2025 18:25:18 | 10/22/2025 06:21:18 | COMMUN_FAIL at ARS0171_NE_8 @ Sceco | 10/21/2025 17:21:37 | Minor | 1-199 | COMMUN_FAIL | 10/21/2025 17:21:01 | P3 | SRAN | al rass | Sceco | TX NSA | ARS0171 | FLM_TE | [8 empty] | API | 10/21/2025 18:21:18 | 10/21/2025 18:25:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001047 | PCM-20251021-00002189 | TT-20251021-02235 | EM | Region_6 | SMT0174 | SMT0174 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Touseef Ahmed | 10/21/2025 18:25:35 | 10/21/2025 21:35:15 | 10/22/2025 00:25:35 | 1(2G/3G/LTE) sites down under SMT0174-P2/SMT0174-P2 @ Sceco | 10/21/2025 18:17:48 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 18:17:44 | P2 | 2G | jizan | Sceco | 2G_3G_LTE SA | SMT0174-P2 | FLM_EM | SMT0174 | Results: DOWN SITE HUB SMT0174-P2 SMT0174 Summary: Hub: SMT0174, Down Count: 1, Down Sites: SMT0174-P2 Alarm Summary: SMT0174 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 18:25:35 | 10/21/2025 19:25:36 | 10/21/2025 21:34:54 | 10/21/2025 21:34:57 | 10/21/2025 21:34:59 | 10/21/2025 21:35:15 |  | Touseef Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001048 | PCM-20251021-00002190 | TT-20251021-02243 | Telecom | Region_2 | KHJ0302 | KHJ0302 | Transsmission | SFP_Transmission | Replace SFP | Hakim Ullah Raif Ullah Jan | 10/21/2025 18:26:02 | 10/22/2025 10:09:53 | 10/22/2025 06:26:02 | As BO Requested MW HW HC port KHJ0302_NE_31_V/1-MXXI4B-5 which heavily flapping IN_PWR_LOW alarm | 10/21/2025 18:24:36 | Minor | 1-631 | MW_LOF | 10/21/2025 18:24:40 | P1 | SRAN | al kharj | Sceco | TX NSA | KHJ0302_NE_31_V | FLM_TE | [8 empty] | API | 10/21/2025 18:26:02 | 10/21/2025 21:53:00 | 10/22/2025 09:37:36 | 10/22/2025 09:37:42 | 10/22/2025 09:52:22 | 10/22/2025 10:09:53 |  | Hakim Ullah Raif Ullah Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001049 | PCM-20251021-00002192 | TT-20251021-02248 | EM | Region_6 | BHAB1M7819 | BHAB0819 |  |  |  | Arif Ullah Shah | 10/21/2025 18:29:03 | 10/22/2025 15:24:46 | 10/22/2025 06:29:03 | COMMERCIAL POWER FAILURE at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/21/2025 18:21:00 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/21/2025 18:20:48 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7819 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/21/2025 18:29:03 | 10/22/2025 15:24:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001050 | PCM-20251021-00002195 | TT-20251021-02250 | Reference_telecom | Region_6 | JEC0090 | JEC0090 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/21/2025 18:33:00 | 10/21/2025 23:41:51 | 10/22/2025 00:33:00 | TRX OPERATION DEGRADED at JEC0090-P1-VIP-HUB (Ref:TT-20251016-02169) @ Sceco_STB | 10/21/2025 07:23:11 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 07:23:07 | VIP | 2G | baish | Sceco_STB | 2G_TRX NSA | JEC0090 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/21/2025 18:33:00 | 10/21/2025 23:38:37 | 10/21/2025 23:41:37 |  |  | 10/21/2025 23:41:51 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001052 | PCM-20251021-00002197 | TT-20251021-02252 | Telecom | Region_4 | JED1M8596 | JED2596 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 18:33:42 | 10/21/2025 18:53:05 | 10/21/2025 22:33:42 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8596-P1-CA-L800 @ Sceco | 10/21/2025 18:32:58 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 18:32:46 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8596 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 18:33:42 | 10/21/2025 18:53:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001053 | PCM-20251021-00002198 | TT-20251021-02253 | Reference_telecom | Region_6 | BSH0082 | BSH0082 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/21/2025 18:35:19 | 10/21/2025 23:41:26 | 10/22/2025 00:35:19 | TRX OPERATION DEGRADED at BSH0082-P2 (Ref:TT-20251020-01546) @ Sceco | 10/21/2025 02:35:13 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 02:34:46 | P2 | 2G | baish | Sceco | 2G_TRX NSA | BSH0082 | FLM_TE | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/21/2025 18:35:19 | 10/21/2025 23:38:38 | 10/21/2025 23:41:16 |  |  | 10/21/2025 23:41:26 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001059 | PCM-20251021-00002210 | TT-20251021-02266 | Telecom | Region_1 | QTF0491 | QTF0491 |  |  |  | Meraj Husain Idd Baksh | 10/21/2025 18:45:18 | 10/21/2025 19:38:53 | 10/22/2025 00:45:18 | Inter-BBU Port Failure at QTF0491-P2_SRAN @ Generator_SG | 10/21/2025 17:26:34 | Major | 26314 | Inter-BBU Port Failure | 10/21/2025 17:23:53 | P2 | SRAN | dammam | Generator_SG | 2G NSA | QTF0491 | FLM_TE | [8 empty] | API | 10/21/2025 18:45:18 | 10/21/2025 19:38:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001061 | PCM-20251021-00002212 | TT-20251021-02268 | Reference_telecom | Region_2 | BUR6002 | BUR6002 |  |  |  | Raise Ahmed Nisar Ahmed | 10/21/2025 18:46:32 | 10/22/2025 12:06:59 | 10/22/2025 00:46:32 | RFC Port Underpower at BUR6002-DCU1 @ Sceco | 10/21/2025 15:21:20 | Major | 29803 | RFC Port Underpower | 10/21/2025 15:21:07 | VIP | SRAN | buraidah | Sceco | 2G SA | BUR6002 | FLM_TE | [8 empty] | API | 10/21/2025 18:46:32 | 10/22/2025 12:06:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001062 | PCM-20251021-00002213 | TT-20251021-02269 | Telecom | Region_4 | JED2480 | JED2480 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/21/2025 18:47:08 | 10/23/2025 12:46:47 | 10/22/2025 06:47:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2480-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/21/2025 18:46:28 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 18:46:23 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2480 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 18:47:08 | 10/22/2025 10:26:37 | 10/23/2025 12:46:41 |  |  | 10/23/2025 12:46:47 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001064 | PCM-20251021-00002215 | TT-20251021-02271 | Reference_telecom | Region_2 | RIYB2U6778 | RIYB6078 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/21/2025 18:48:42 | 10/22/2025 08:23:03 | 10/22/2025 00:48:42 | RF Unit VSWR Threshold Crossed at RIYB2U6778-P3 @ Sceco | 10/21/2025 15:48:47 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 15:48:35 | P3 | 4G | riyadh | Sceco | LTE NSA | RIYB2U6778 | FLM_TE | [8 empty] | API | 10/21/2025 18:48:42 | 10/22/2025 08:23:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001066 | PCM-20251021-00002220 | TT-20251021-02277 | EM | Region_1 | HMBY2877 | HMBY2877 | Enviroment | Fire Alarm | Reset Fire Pannel | Ibrahim said mohamed Elmarhoumy | 10/21/2025 18:52:49 | 10/22/2025 07:00:11 | 10/22/2025 06:52:49 | Mains Failure at HMBY2877-P3_SRAN-PC @ Sceco | 10/21/2025 18:43:00 | Minor | 65109 | Mains Failure | 10/21/2025 18:42:57 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2877 | FLM_EM | [8 empty] | API | 10/21/2025 18:52:49 | 10/21/2025 20:49:35 | 10/21/2025 21:33:27 | 10/21/2025 21:33:29 | 10/21/2025 21:33:32 | 10/22/2025 07:00:11 |  | Ibrahim said mohamed Elmarhoumy |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001068 | PCM-20251021-00002224 | TT-20251021-02282 | Reference_telecom | Region_6 | RTH0607 | RTH0607 |  |  |  | Muhammad Ali | 10/21/2025 18:57:30 | 10/21/2025 21:21:10 | 10/22/2025 00:57:30 | BASE STATION ANTENNA LINE PROBLEM (VSWR lower threshold exceeded) at RTH0607-GSM-UMTS-P2 (Ref:TT-20251019-02308) @ Generator_DG | 10/20/2025 03:19:50 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/20/2025 03:19:42 | P2 | 2G | raith | Generator_DG | LTE NSA | RTH0607 | FLM_TE | [5 empty] | VSWR lower threshold exceeded |  |  | API | 10/21/2025 18:57:30 | 10/21/2025 21:21:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021001069 | PCM-20251021-00002225 | TT-20251021-02283 | Reference_telecom | [7 empty] | 10/21/2025 18:57:59 | 10/21/2025 18:57:59 | 10/22/2025 00:57:59 | RF Unit VSWR Threshold Crossed at HFF6003-P3_SRAN @ Sceco | 10/21/2025 15:57:49 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 16:53:36 | P3 | SRAN |  | Sceco | 2G NSA | HFF6003 | FLM_TE | [8 empty] | API | 10/21/2025 18:57:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001071 | PCM-20251021-00002231 | TT-20251021-02289 | EM | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/21/2025 19:02:37 | 10/22/2025 21:40:59 | 10/22/2025 07:02:37 | NETECO: L3-L1 Overvoltage at KFKM0784 @ Generator_SG | 10/21/2025 18:56:09 | Minor | 10259 | L3-L1 Overvoltage | 10/21/2025 18:56:09 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0784 | FLM_EM | [8 empty] | API | 10/21/2025 19:02:37 | 10/22/2025 21:40:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251021001073 | PCM-20251021-00002236 | TT-20251021-02294 | Telecom | Region_5 | MAK1M9803 | MAK0803 | Equipment | BSS_HW_fault | Replace RF Module | Muhammad Saleem Iqbal | 10/21/2025 19:04:43 | 10/22/2025 06:34:57 | 10/22/2025 07:04:43 | BASE STATION SERVICE PROBLEM (TX out of order) at MAK1M9803-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/21/2025 18:59:50 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 18:59:42 | P3 | 4G | makkah | Generator_SG | LTE_Cell SA | MAK1M9803 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/21/2025 19:04:43 | 10/22/2025 04:41:32 | 10/22/2025 04:43:09 | 10/22/2025 04:43:13 | 10/22/2025 06:34:57 |  |  | Sher Ali Munir |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001075 | PCM-20251021-00002240 | TT-20251021-02287 | EM | Region_6 | KMS1M4147 | KMS2147 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ezat Mohammed | 10/21/2025 19:06:03 | 10/23/2025 09:21:20 | 10/21/2025 23:06:03 | 1(3G/5G) sites down under KMS2147-FWA-P1-VIP/KMS1M4147-FWA-P1-VIP @ Sceco | 10/21/2025 18:58:16 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 18:57:34 | P3 | 3G | khamis mushyet | Sceco | 3G_5G SA | KMS2147-FWA-P1-VIP | FLM_EM | KMS2147 | Results: DOWN SITE HUB KMS2147-FWA-P1-VIP KMS2147 Summary: Hub: KMS2147, Down Count: 1, Down Sites: KMS2147-FWA-P1-VIP Alarm Summary: KMS2147 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 19:06:03 | 10/21/2025 23:20:44 | 10/23/2025 09:21:12 |  |  | 10/23/2025 09:21:20 |  | Ezat Mohammed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001076 | PCM-20251021-00002242 | TT-20251021-02298 | Reference_telecom | Region_4 | JED2886 | JED2886 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 19:07:47 | 10/21/2025 19:40:43 | 10/22/2025 07:07:47 | DemFail observed in JED2886 towards 10.10.154.142 @ Generator_SG | 10/21/2025 07:07:51 | Minor |  | DemFail | 10/21/2025 07:07:12 | P3 | 2G | jeddah | Generator_SG | TX NSA | JED2886 | FLM_TE | [8 empty] | API | 10/21/2025 19:07:47 | 10/21/2025 19:40:43 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001078 | PCM-20251021-00002248 | TT-20251021-02297 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/21/2025 19:12:35 | 10/22/2025 20:21:09 | 10/22/2025 01:12:35 | 1(2G/LTE/5G) sites down under JED6020-GSM-P3/JED6020-GSM-P3 @ Sceco | 10/21/2025 19:04:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 19:04:09 | P3 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED6020-GSM-P3 | FLM_EM | JED6020 | Results: DOWN SITE HUB JED6020-GSM-P3 JED6020 Summary: Hub: JED6020, Down Count: 1, Down Sites: JED6020-GSM-P3 Alarm Summary: JED6020 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 19:12:35 | 10/22/2025 20:21:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001079 | PCM-20251021-00002249 | TT-20251021-01449 | MW_HC | Region_5 | MAK2306 | MAK2306 |  |  |  | Mosab Nasr eldeen Mohamed | 10/21/2025 19:14:13 | 10/21/2025 21:37:05 | 10/22/2025 07:14:13 | Nokia MW HC_P1 Observing Performance Issue at MAK2306-MAK0982-SH04 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P3 | 2G | makkah | Sceco | TX NSA | MAK2306-MAK0982-SH04 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251021-00002241 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/21/2025 19:14:13 | 10/21/2025 21:37:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001080 | PCM-20251021-00002251 | TT-20251021-01437 | MW_HC | Region_5 | MAK0617 | MAK0617 |  |  |  | Mosab Nasr eldeen Mohamed | 10/21/2025 19:17:58 | 10/21/2025 21:37:05 | 10/22/2025 07:17:58 | Nokia MW HC_P1 Observing Performance Issue at MAK0617 _03-MAK0937 | 10/21/2025 12:34:21 | Minor |  | LOF | 10/21/2025 12:34:21 | P2 | 2G | makkah | Sceco | TX NSA | MAK0617 _03-MAK0937 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251021-00002238 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/21/2025 19:17:58 | 10/21/2025 21:37:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001083 | PCM-20251021-00002254 | TT-20251021-02284 | Telecom | Region_4 | RYMK1M3528 | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/21/2025 19:20:27 | 10/22/2025 07:52:56 | 10/22/2025 01:20:27 | BASE STATION CONNECTIVITY PROBLEM (BTS RNC interface signalling link failure) at RYMK1M3528-P3 @ Generator_SG | 10/21/2025 18:56:49 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 17:31:46 | P3 | 3G | taif | Generator_SG | 3G NSA | RYMK1M3528 | FLM_TE |  |  | PCM-20251021-00002226 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/21/2025 19:20:27 | 10/22/2025 07:52:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001085 | PCM-20251021-00002256 | TT-20251021-02242 | Telecom | Region_5 | MAK0002 | MAK0002 |  |  |  | Husain Hassan Ishag Omer | 10/21/2025 19:20:53 | 10/22/2025 01:12:58 | 10/22/2025 01:20:53 | BASE STATION ANTENNA LINE PROBLEM at MAK0002-G9-L8-L18-L21-NNR2.6-SBTS-P1-DIA @ Sceco | 10/21/2025 18:18:05 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/21/2025 18:17:56 | P1 | 2G | makkah | Sceco | 2G NSA | MAK0002 | FLM_TE |  |  | PCM-20251021-00002188 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/21/2025 19:20:53 | 10/22/2025 01:12:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001086 | PCM-20251021-00002257 | TT-20251021-02221 | Telecom | Region_4 | JED1U6739 | JED6039 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 19:21:02 | 10/22/2025 15:47:56 | 10/22/2025 01:21:02 | BASE STATION ANTENNA LINE PROBLEM at JED1U6739-G9-L18-SBTS-P1-VIP @ Sceco | 10/21/2025 18:09:23 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/21/2025 18:09:18 | VIP | 4G | jeddah | Sceco | LTE NSA | JED1U6739 | FLM_TE |  |  | PCM-20251021-00002174 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/21/2025 19:21:02 | 10/22/2025 15:47:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001087 | PCM-20251021-00002258 | TT-20251021-02245 | Telecom | Region_5 | USMD0771 | USMD0771 |  |  |  | Amr Abdulla Ali Othman | 10/21/2025 19:21:11 | 10/21/2025 19:21:11 | 10/22/2025 01:21:11 | BASE STATION ANTENNA LINE PROBLEM at USMD0771-G9-NL8-L18-L21-NNR2.6-SBTS-P1-HUB-USF @ Sceco | 10/21/2025 18:20:20 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/21/2025 18:20:09 | P1 | 2G | makkah | Sceco | 2G NSA | USMD0771 | FLM_TE |  |  | PCM-20251021-00002191 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/21/2025 19:21:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251021001089 | PCM-20251021-00002260 | TT-20251021-02185 | Telecom | Region_4 | JED2032 | JED2032 | Equipment | SFP_BTS | Clean SFP | BARKAT ALI MAIN HILAL | 10/21/2025 19:21:37 | 10/22/2025 13:09:35 | 10/22/2025 07:21:37 | BASE STATION SERVICE PROBLEM (FSP Reset Needed) at JED2032-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/21/2025 17:49:37 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 17:49:25 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2032 | FLM_TE |  |  | PCM-20251021-00002139 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/21/2025 19:21:37 | 10/22/2025 13:06:30 | 10/22/2025 13:06:44 | 10/22/2025 13:06:46 | 10/22/2025 13:09:35 |  |  | BARKAT ALI MAIN HILAL |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001090 | PCM-20251021-00002265 | TT-20251021-02309 | Telecom | Region_4 | JED1M7732 | JED0732 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 19:26:23 | 10/21/2025 22:51:04 | 10/22/2025 07:26:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7732-P3-CA-L900-L800-SBTS @ Sceco | 10/21/2025 19:25:42 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 19:25:34 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7732 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 19:26:23 | 10/21/2025 22:51:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001097 | PCM-20251021-00002279 | TT-20251021-02308 | Telecom | Region_6 | DMD0042 | DMD0042 | Transsmission | MW_Connectors | Remade Indoor MW Connector | Zeshan Ali Adnan | 10/21/2025 19:35:05 | 10/22/2025 00:59:50 | 10/22/2025 07:35:05 | Firmware Version Mismatch at DMD0042-2 on 10.154.172.126 @ Sceco_STB | 10/21/2025 19:17:16 | Minor | Firmware Version Mismatch | Firmware Version Mismatch | 10/21/2025 19:21:02 | P1 | 2G | jizan | Sceco_STB | TX NSA | DMD0042 | FLM_TE |  |  | PCM-20251021-00002262 | FW Ongoing , requested FLM | FW Ongoing , requested FLM |  |  |  | API | 10/21/2025 19:35:05 | 10/21/2025 22:29:57 | 10/22/2025 00:55:31 |  |  | 10/22/2025 00:59:50 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001098 | PCM-20251021-00002283 | TT-20251021-02316 | EM | Region_4 | JED0188 | JED0188 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 19:37:01 | 10/21/2025 22:51:05 | 10/22/2025 01:37:01 | 1(2G/LTE/5G) sites down under JED0188-P3/JED0188-P3 @ Sceco | 10/21/2025 19:28:45 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 19:28:41 | P3 | 2G | jeddah | Sceco | 2G SA | JED0188-P3 | FLM_TE | JED0188 | Results: DOWN SITE HUB JED0188-P3 JED0188 Summary: Hub: JED0188, Down Count: 1, Down Sites: JED0188-P3 Alarm Summary: JED0188 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 19:37:01 | 10/21/2025 22:51:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001101 | PCM-20251021-00002288 | TT-20251021-02325 | Reference_telecom | Region_6 | KMS2503 | KMS2503 | Transsmission | MW_HW_stuck | Reset FAN | Ahmed Abdelaziz Hamid Abdelrahman | 10/21/2025 19:42:54 | 10/22/2025 13:41:47 | 10/22/2025 07:42:54 | FanFailure observed in KMS2503_02 towards 10.10.156.3 @ Sceco | 10/21/2025 07:43:46 | Minor |  | FanFailure | 10/21/2025 07:42:20 | P3 | 2G | khamis mushyet | Sceco | TX NSA | KMS2503 | FLM_TE | [8 empty] | API | 10/21/2025 19:42:54 | 10/21/2025 20:40:26 | 10/22/2025 13:41:30 |  |  | 10/22/2025 13:41:47 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001102 | PCM-20251021-00002289 | TT-20251021-02275 | Reference_telecom | Region_6 | WJZ1M7065 | WJZ0065 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Ali | 10/21/2025 19:43:31 | 10/21/2025 23:15:02 | 10/22/2025 01:43:31 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at WJZ1M7065-P3-L800-CA @ Sceco | 10/21/2025 16:50:49 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:50:25 | P3 | 4G | jizan | Sceco | LTE NSA | WJZ1M7065 | FLM_TE |  |  | PCM-20251021-00002261 | need check QIS0267-QIS0031 | need check QIS0267-QIS0031 |  |  |  | API | 10/21/2025 19:43:31 | 10/21/2025 21:21:11 | 10/21/2025 23:14:53 |  |  | 10/21/2025 23:15:02 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001103 | PCM-20251021-00002294 | TT-20251021-02274 | Reference_telecom | Region_6 | FIF1M7150 | FIF0150 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Ali | 10/21/2025 19:49:21 | 10/21/2025 23:35:04 | 10/22/2025 01:49:21 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at FIF1M7150-P2-L2100-L800 @ Sceco | 10/21/2025 16:50:55 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:50:20 | P2 | 4G | dair | Sceco | LTE NSA | FIF1M7150 | FLM_TE |  |  | PCM-20251021-00002263 | need check QIS0267-QIS0031 | need check QIS0267-QIS0031 |  |  |  | API | 10/21/2025 19:49:21 | 10/21/2025 21:21:12 | 10/21/2025 23:34:35 |  |  | 10/21/2025 23:35:04 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001104 | PCM-20251021-00002295 | TT-20251021-02273 | Reference_telecom | Region_6 | FIF1M7045 | FIF0045 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Ali | 10/21/2025 19:51:34 | 10/21/2025 23:35:23 | 10/22/2025 01:51:34 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at FIF1M7045-P2-CA-L800 @ Sceco | 10/21/2025 16:50:51 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:50:00 | P2 | 4G | dair | Sceco | LTE NSA | FIF1M7045 | FLM_TE |  |  | PCM-20251021-00002271 | need check QIS0267-QIS0031 | need check QIS0267-QIS0031 |  |  |  | API | 10/21/2025 19:51:34 | 10/21/2025 21:21:13 | 10/21/2025 23:35:11 |  |  | 10/21/2025 23:35:23 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251021001105 | PCM-20251021-00002296 | TT-20251021-02332 | Telecom | Region_4 | JED0229 | JED0229 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 19:52:13 | 10/22/2025 12:18:14 | 10/22/2025 07:52:13 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0229-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/21/2025 19:51:30 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 19:51:19 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0229 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 19:52:13 | 10/22/2025 10:09:08 | 10/22/2025 11:20:50 | 10/22/2025 11:20:53 | 10/22/2025 12:18:14 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001106 | PCM-20251021-00002297 | TT-20251021-02333 | Reference_telecom | Region_1 | SMN0850 | SMN0850 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/21/2025 19:52:13 | 10/21/2025 20:47:37 | 10/22/2025 01:52:13 | RF Unit VSWR Threshold Crossed at SMN0850-P2-USF_SRAN @ Generator_DG | 10/21/2025 16:51:57 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 16:51:45 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0850 | FLM_TE | [8 empty] | API | 10/21/2025 19:52:13 | 10/21/2025 20:47:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001111 | PCM-20251021-00002307 | TT-20251021-02337 | EM | Region_4 | JED6029 | JED6029 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 20:00:31 | 10/22/2025 15:47:57 | 10/22/2025 02:00:31 | 1(2G/LTE) sites down under JED6029-P3/JED6029-P3 @ Sceco | 10/21/2025 19:52:16 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 19:52:11 | P3 | 2G | jeddah | Sceco | 2G SA | JED6029-P3 | FLM_TE | JED6029 | Results: DOWN SITE HUB JED6029-P3 JED6029 Summary: Hub: JED6029, Down Count: 1, Down Sites: JED6029-P3 Alarm Summary: JED6029 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 20:00:31 | 10/22/2025 15:47:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001112 | PCM-20251021-00002314 | TT-20251021-02354 | Telecom | Region_4 | BHR0310 | BHR0310 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/21/2025 20:11:19 | 10/22/2025 10:09:09 | 10/22/2025 08:11:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR0310-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 20:10:30 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 20:10:23 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | BHR0310 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 20:11:19 | 10/22/2025 10:09:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001114 | PCM-20251021-00002318 | TT-20251021-02364 | Telecom | Region_4 | JED1M7241 | JED0241 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 20:19:04 | 10/21/2025 20:19:04 | 10/22/2025 08:19:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7241-CA-L900-L800-P2-SBTS @ Sceco | 10/21/2025 20:18:26 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 20:18:19 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7241 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 20:19:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001119 | PCM-20251021-00002326 | TT-20251021-02370 | Telecom | Region_3 | AHT2M8160 | AHT2160 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohamed Naveed | 10/21/2025 20:27:32 | 10/22/2025 01:23:18 | 10/22/2025 02:27:32 | 1(LTE) sites down under AHT2160-P3-L800 @ Sceco | 10/21/2025 20:20:30 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/21/2025 20:18:56 | P3 | 4G | hail | Sceco | LTE SA | AHT2160-P3-L800 | FLM_TE | AHT2160 | Results: DOWN SITE HUB AHT2160-P3-L800 AHT2160 Summary: Hub: AHT2160, Down Count: 1, Down Sites: AHT2160-P3-L800 Alarm Summary: AHT2160 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 20:27:32 | 10/21/2025 20:41:01 | 10/22/2025 01:23:10 |  |  | 10/22/2025 01:23:18 |  | Mohamed Naveed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001122 | PCM-20251021-00002331 | TT-20251021-02379 | EM | Region_1 | JBL0475 | JBL0475 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Hamid Bilal Bashir Ahmed | 10/21/2025 20:33:02 | 10/21/2025 21:54:12 | 10/22/2025 08:33:02 | Door opening alarm at JBL0475-P3_SRAN @ Sceco | 10/21/2025 20:32:42 | Minor | 65101 | Door opening alarm | 10/21/2025 20:32:37 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL0475 | FLM_EM | [8 empty] | API | 10/21/2025 20:33:02 | 10/21/2025 21:24:46 | 10/21/2025 21:48:32 | 10/21/2025 21:48:35 | 10/21/2025 21:48:37 | 10/21/2025 21:54:12 |  | Hamid Bilal Bashir Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021001124 | PCM-20251021-00002334 | TT-20251021-02381 | Telecom | Region_4 | JED2179 | JED2179 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 20:35:36 | 10/21/2025 20:35:36 | 10/22/2025 08:35:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2179-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/21/2025 20:34:58 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 20:34:53 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2179 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 20:35:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001125 | PCM-20251021-00002333 | TT-20251021-02380 | Telecom | Region_4 | JED1M8609 | JED2609 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 20:35:37 | 10/22/2025 12:55:57 | 10/22/2025 02:35:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8609-P3-L800-CA @ Sceco | 10/21/2025 20:34:55 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 20:34:48 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8609 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 20:35:37 | 10/22/2025 12:55:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001128 | PCM-20251021-00002339 | TT-20251021-02385 | Telecom | Region_4 | FAT0348 | FAT0348 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 20:40:45 | 10/22/2025 17:30:02 | 10/22/2025 08:40:45 | Temperature at FAT0348-IDU#5 on 10.1.175.181 @ Generator_DG | 10/21/2025 20:40:00 | Minor | Temperature | Temperature | 10/21/2025 20:30:58 | P1 | 2G | taif | Generator_DG | TX NSA | FAT0348 | FLM_TE | [8 empty] | API | 10/21/2025 20:40:45 | 10/22/2025 17:30:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001131 | PCM-20251021-00002352 | TT-20251021-02200 | Reference_telecom | Region_6 | JIZ0243 | JIZ0243 | Equipment | SFP_BTS | Clean SFP | Zeshan Ali Adnan | 10/21/2025 20:50:58 | 10/22/2025 13:42:53 | 10/22/2025 08:50:58 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ0243-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/21/2025 16:54:32 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:02:37 | P3 | 2G | jizan | Sceco | 2G NSA | JIZ0243 | FLM_TE |  |  | PCM-20251021-00002277 | Dear FLM team, kindly check MW JIZ0243-JIZ0169 flapping | Dear FLM team, kindly check MW JIZ0243-JIZ0169 flapping |  |  |  | API | 10/21/2025 20:50:58 | 10/21/2025 22:29:57 | 10/22/2025 13:42:25 |  |  | 10/22/2025 13:42:53 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001132 | PCM-20251021-00002353 | TT-20251021-02201 | Reference_telecom | Region_6 | JIZ1MT0168 | JIZ0168 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/21/2025 20:51:12 | 10/21/2025 23:48:06 | 10/22/2025 02:51:12 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1MT0168-P3 @ Sceco | 10/21/2025 16:54:30 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:02:43 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1MT0168 | FLM_TE |  |  | PCM-20251021-00002274 | Dear FLM team, kindly check MW JIZ0243-JIZ0169 flapping | Dear FLM team, kindly check MW JIZ0243-JIZ0169 flapping |  |  |  | API | 10/21/2025 20:51:12 | 10/21/2025 23:21:43 | 10/21/2025 23:47:55 |  |  | 10/21/2025 23:48:06 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001133 | PCM-20251021-00002354 | TT-20251021-02202 | Reference_telecom | Region_6 | JIZ1M7258 | JIZ0258 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Zeshan Ali Adnan | 10/21/2025 20:51:36 | 10/22/2025 13:41:23 | 10/22/2025 08:51:36 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JIZ1M7258-P3-NCA-L800-SBTS @ Sceco | 10/21/2025 16:54:26 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:02:48 | P3 | 4G | jizan | Sceco | LTE NSA | JIZ1M7258 | FLM_TE |  |  | PCM-20251021-00002273 | Dear FLM team, kindly check MW JIZ0243-JIZ0169 flapping | Dear FLM team, kindly check MW JIZ0243-JIZ0169 flapping |  |  |  | API | 10/21/2025 20:51:36 | 10/21/2025 22:29:58 | 10/22/2025 13:40:54 |  |  | 10/22/2025 13:41:23 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001137 | PCM-20251021-00002360 | TT-20251021-02362 | Telecom | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/21/2025 20:55:58 | 10/23/2025 17:06:30 | 10/22/2025 02:55:58 | 4(2G) 2(3G) sites down under KFKM0784,KFKM0783-P3,KFKM0782-P3,JBKH0143-P3-USF/HB1BSCH01 @ Generator_SG | 10/21/2025 20:15:46 | Major | 21825 | CSL Fault | 10/21/2025 20:15:42 | P3 | SRAN | hafr | Generator_SG | 2G_3G SA | JBKH0143-P3-USF 2G_3G,KFKM0783-P3 2G,KFKM0782-P3 2G | FLM_EM | KFKM0784 | Dear Team, Hub:- KFKM0784 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251021-00002341 | Dear Team, Hub:- KFKM0784 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Dear Team, Hub:- KFKM0784 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/21/2025 20:55:58 | 10/22/2025 21:41:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001138 | PCM-20251021-00002361 | TT-20251021-02398 | EM | Region_1 | HMBY2M2877 | HMBY2877 |  |  |  | Abdul Malik Shaik | 10/21/2025 20:58:32 | 10/22/2025 11:57:14 | 10/22/2025 02:58:32 | 1(2G/LTE) sites down under HMBY2877-P3/DM1MBSCH01 @ Sceco | 10/21/2025 20:50:13 | Major | 21825 | CSL Fault | 10/21/2025 20:50:10 | P3 | 2G | dammam | Sceco | 2G_LTE SA | HMBY2877-P3 | FLM_EM | HMBY2877 | Results: DOWN SITE HUB HMBY2877-P3 HMBY2877 Summary: Hub: HMBY2877, Down Count: 1, Down Sites: HMBY2877-P3 Alarm Summary: HMBY2877 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/21/2025 20:58:32 | 10/22/2025 11:57:14 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251021001139 | PCM-20251021-00002362 | TT-20251021-02400 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/21/2025 20:59:01 | 10/21/2025 21:22:41 | 10/22/2025 02:59:01 | 1(5G) sites down under JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 20:50:42 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 20:50:39 | P2 | 2G | jeddah | Sceco | 5G SA | JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | JED0500 | Results: DOWN SITE HUB JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 JED0500 Summary: Hub: JED0500, Down Count: 1, Down Sites: JED0500-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 Alarm Summary: JED0500 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.104.124:8080] [URL:http://10.96.104.124:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 20:59:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001140 | PCM-20251021-00002365 | TT-20251021-02394 | Telecom | Region_6 | ARS1M7122 | ARS0122 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Zeshan Ali Adnan | 10/21/2025 21:02:20 | 10/22/2025 14:17:33 | 10/22/2025 09:02:20 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at ARS1M7122-CA-L800-SBTS-P3 @ Sceco | 10/21/2025 20:45:35 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 20:45:24 | P3 | 4G | jizan | Sceco | 5G_Cell SA | ARS1M7122 | FLM_TE |  |  | PCM-20251021-00002350 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/21/2025 21:02:20 | 10/21/2025 22:30:00 | 10/22/2025 14:16:45 | 10/22/2025 14:16:48 | 10/22/2025 14:16:52 | 10/22/2025 14:17:33 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001142 | PCM-20251021-00002367 | TT-20251021-02411 | Telecom | Region_4 | JED0714 | JED0714 | Equipment | SFP_BTS | Replace SFP | Mohammed Ramadan A Abu Abid | 10/21/2025 21:04:01 | 10/22/2025 11:52:42 | 10/22/2025 03:04:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0714-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/21/2025 21:03:07 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 21:03:01 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0714 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 21:04:01 | 10/21/2025 22:11:29 | 10/22/2025 09:54:06 | 10/22/2025 09:54:10 | 10/22/2025 09:55:55 | 10/22/2025 11:52:42 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001143 | PCM-20251021-00002370 | TT-20251021-02415 | Telecom | Region_5 | MAK1MN0808 | MAK0808 | Equipment | BSS_HW_fault | Replace FAN | Sher Ali Munir | 10/21/2025 21:06:36 | 10/21/2025 23:37:01 | 10/22/2025 09:06:36 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0808-NR2.6-P2 @ Sceco | 10/21/2025 20:59:05 | Minor | 7115 | BASE STATION INFORMATION | 10/21/2025 20:58:28 | P2 | 5G | makkah | Sceco | 5G NSA | MAK1MN0808 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/21/2025 21:06:36 | 10/21/2025 22:33:00 | 10/21/2025 22:33:17 | 10/21/2025 22:33:34 | 10/21/2025 22:33:41 | 10/21/2025 23:37:01 |  | Sher Ali Munir |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001144 | PCM-20251021-00002371 | TT-20251021-02417 | Reference_telecom | Region_4 | JED2175 | JED2175 |  |  |  | MALIK ATIF ZAMAN | 10/21/2025 21:07:06 | 10/21/2025 22:51:05 | 10/22/2025 09:07:06 | LagPortDown observed in JED2175 towards 10.10.180.215 @ Sceco | 10/21/2025 09:07:13 | Minor |  | LagPortDown | 10/21/2025 09:06:36 | P3 | 2G | jeddah | Sceco | TX NSA | JED2175 | FLM_TE | [8 empty] | API | 10/21/2025 21:07:06 | 10/21/2025 22:51:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001145 | PCM-20251021-00002372 | TT-20251021-02418 | Telecom | Region_4 | JED2063 | JED2063 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 21:07:38 | 10/21/2025 21:07:38 | 10/22/2025 09:07:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2063-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 21:06:35 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 21:06:30 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED2063 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 21:07:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001146 | PCM-20251021-00002374 | TT-20251021-02407 | Telecom | Region_1 | HFF0819 | HFF0819 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/21/2025 21:08:34 | 10/22/2025 16:03:20 | 10/22/2025 03:08:34 | 2(2G) 2(3G) sites down under HRD0859-P3-USF,HFF0819-P3-USF/R1_HF_HWBSC01 @ Power Cube | 10/21/2025 20:58:59 | Major | 21825 | CSL Fault | 10/21/2025 20:58:54 | P3 | SRAN | hafouf | Power Cube | 2G_3G SA | HRD0859-P3-USF 2G_3G,HFF0819-P3-USF 2G_3G | FLM_TE | HFF0819 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : HFF0819 DIR HFF0821,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00002369 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : HFF0819 DIR HFF0821,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : HFF0819 DIR HFF0821,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 21:08:34 | 10/22/2025 08:41:26 | 10/22/2025 16:03:04 |  |  | 10/22/2025 16:03:20 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001147 | PCM-20251021-00002377 | TT-20251021-02423 | Telecom | Region_4 | TAF1M8114 | TAF2114 |  |  |  | Ahmad Kamal Abdelmawla | 10/21/2025 21:18:04 | 10/22/2025 17:30:03 | 10/22/2025 03:18:04 | 1(LTE) sites down under TAF2114-CA-L800-SBTS-P2 @ Sceco | 10/21/2025 21:09:56 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 21:09:54 | P2 | 4G | taif | Sceco | LTE SA | TAF2114-CA-L800-SBTS-P2 | FLM_TE | TAF2114 | Results: DOWN SITE HUB TAF2114-CA-L800-SBTS-P2 TAF2114 Summary: Hub: TAF2114, Down Count: 1, Down Sites: TAF2114-CA-L800-SBTS-P2 Alarm Summary: TAF2114 No Active Alarm on HUB |  |  |  | 30,000 milliseconds timeout on connection http-outgoing-4420572 [ACTIVE] [URL:http://10.98.72.212:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 21:18:04 | 10/22/2025 17:30:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001149 | PCM-20251021-00002380 | TT-20251021-02437 | Reference_telecom | Region_6 | ABBS0152 | ABBS0152 |  |  |  | Manzoor Ahmed | 10/21/2025 21:19:35 | 10/22/2025 14:04:23 | 10/22/2025 09:19:35 | ReplaceableUnitMissing observed in ABBS0152 towards 10.74.122.12 @ Sceco | 10/21/2025 09:21:28 | Minor |  | ReplaceableUnitMissing | 10/21/2025 09:19:23 | P3 | 2G | Albaha | Sceco | TX NSA | ABBS0152 | FLM_TE | [8 empty] | API | 10/21/2025 21:19:35 | 10/22/2025 14:04:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001151 | PCM-20251021-00002382 | TT-20251021-02419 | Telecom | Region_4 | JED1U6831 | JED6131 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 21:19:45 | 10/22/2025 15:47:57 | 10/22/2025 03:19:45 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6831-P3 @ Sceco | 10/21/2025 20:59:18 | Major | 7654 | CELL OPERATION DEGRADED | 10/21/2025 20:59:12 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6831 | FLM_TE |  |  | PCM-20251021-00002373 | Please check VSWR at the site | Please check VSWR at the site |  |  |  | API | 10/21/2025 21:19:45 | 10/22/2025 15:47:57 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001152 | PCM-20251021-00002383 | TT-20251021-02455 | EM | Region_4 | TAF2349 | TAF2349 |  |  |  | Walid Magdy Tawfik Elbana | 10/21/2025 21:21:34 | 10/21/2025 21:21:34 | 10/22/2025 09:21:34 | SHELTER DOOR OPEN at TAF2349-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 21:21:14 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 21:21:04 | P2 | 2G | taif | Sceco | 2G NSA | TAF2349 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 21:21:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251021001153 | PCM-20251021-00002385 | TT-20251021-02457 | EM | [7 empty] | 10/21/2025 21:30:52 | 10/21/2025 21:30:52 | 10/22/2025 01:30:52 | MAJOR + MINOR RECTIFIER ALARM at ABHA-E-SEC0022_OCS @ Sceco_STB | 10/21/2025 21:29:27 | Critical | 1-12307 | MAJOR + MINOR RECTIFIER ALARM | 10/21/2025 21:29:17 | P1 | DWDM |  | Sceco_STB | DWDM NSA | ABHA | FLM_EM | [5 empty] | 0-TO ABH0027 (AB1)&SHUQAIQ-SEC0019(1-A)-71-E1EFI-[MAJOR + MINOR RECTIFIER ALARM]:2 |  |  | API | 10/21/2025 21:30:52 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001155 | PCM-20251021-00002389 | TT-20251021-02459 | Telecom | Region_6 | KMS0250 | KMS0250 |  |  |  | Amir Abbas Arif Raza | 10/21/2025 21:38:50 | 10/21/2025 21:50:42 | 10/22/2025 01:38:50 | 2(2G) 2(3G) 1(LTE) 1(5G) sites down under KMS0471-P3,KMS0250-P2/KMS0250-P2 @ Sceco | 10/21/2025 21:29:29 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 21:29:24 | P2 | 2G | khamis mushyet | Sceco | 2G_3G_LTE_5G SA | KMS0471-P3 2G_3G_LTE,KMS0250-P2 2G_3G_5G | FLM_EM | KMS0250 | Dear team , Hub: KMS0250 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00002388 | Dear team , Hub: KMS0250 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: KMS0250 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/21/2025 21:38:50 | 10/21/2025 21:50:42 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001159 | PCM-20251021-00002396 | TT-20251021-01738 | Reference_telecom | Region_1 | RYDM2058 | RYDM2058 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/21/2025 21:45:21 | 10/21/2025 22:34:50 | 10/22/2025 03:45:21 | MW_IS-IS Adjacency Changed at RYDM2058-LL-CSG to RYDM2050 REF: TT-20250430-00810 | 10/21/2025 14:36:33 | Major | 15269 | LOS | 10/21/2025 14:36:35 | P1 | SRAN | dammam | Sceco_STB | IPRAN_NSA | MW_IS-IS Adjacency Changed at RYDM2058-LL-CSG to RYDM2050 REF: TT-20250430-00810 | FLM_TE |  |  | PCM-20251021-00002316 | Dear FLM, Please do the required HC for mentioned link , Details already shared by email | Dear FLM, Please do the required HC for mentioned link , Details already shared by email |  |  |  | API | 10/21/2025 21:45:21 | 10/21/2025 22:34:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001161 | PCM-20251021-00002397 | TT-20251021-02466 | EM | Region_6 | SDA0322 | SDA0322 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/21/2025 21:47:33 | 10/22/2025 03:27:47 | 10/22/2025 03:47:33 | 1(2G/LTE) sites down under SDA0322-P3/SDA0322-P3 @ Sceco | 10/21/2025 21:39:28 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 21:39:23 | P3 | 2G | abha | Sceco | 2G_LTE SA | SDA0322-P3 | FLM_EM | SDA0322 | Results: DOWN SITE HUB SDA0322-P3 SDA0322 Summary: Hub: SDA0322, Down Count: 1, Down Sites: SDA0322-P3 Alarm Summary: SDA0322 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 21:47:33 | 10/22/2025 03:27:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251021001162 | PCM-20251021-00002399 | TT-20251021-02465 | Telecom | Region_4 | JED0391 | JED0391 |  |  |  | BARKAT ALI MAIN HILAL | 10/21/2025 21:48:51 | 10/22/2025 16:17:15 | 10/22/2025 09:48:51 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at JED0391-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 21:35:17 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 21:35:05 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0391 | FLM_TE |  |  | PCM-20251021-00002392 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/21/2025 21:48:51 | 10/22/2025 12:55:57 | 10/22/2025 15:53:25 | 10/22/2025 15:53:27 | 10/22/2025 16:17:15 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001164 | PCM-20251021-00002402 | TT-20251021-02474 | Telecom | Region_5 | MAK1U6943 | MAK6043 |  |  |  | Atif Javed Javed Hussain | 10/21/2025 21:50:53 | 10/21/2025 21:50:53 | 10/22/2025 03:50:53 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at MAK1U6943-G18-L21-SBTS-P1-HRM @ Sceco | 10/21/2025 21:45:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 21:45:20 | P1 | 4G | makkah | Sceco | 5G_Cell SA | MAK1U6943 | FLM_TE |  |  | PCM-20251021-00002400 | Please check RSSI at the site | Please check RSSI at the site |  |  |  | API | 10/21/2025 21:50:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001167 | PCM-20251021-00002422 | TT-20251021-02490 | EM | Region_4 | JED1M7241 | JED0241 | Equipment | BSS_HW_Stuck | Reset System Module | Khaled Mohammad Abdallah | 10/21/2025 22:14:32 | 10/24/2025 06:50:02 | 10/22/2025 04:14:32 | 1(2G/LTE) sites down under JED0241-P2 @ Sceco | 10/21/2025 22:06:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/21/2025 22:06:09 | P2 | 4G | jeddah | Sceco | LTE SA | JED0241-CA-L900-L800-P2-SBTS | FLM_TE | JED0241 | Results: DOWN SITE HUB JED0241-CA-L900-L800-P2-SBTS JED0241 Summary: Hub: JED0241, Down Count: 1, Down Sites: JED0241-CA-L900-L800-P2-SBTS Alarm Summary: JED0241 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.32.196:8080] [URL:http://10.96.32.196:8080/NE3S/1.0/] | sites down |  | API | 10/21/2025 22:14:32 |  | 10/22/2025 02:47:01 | 10/22/2025 02:47:03 | 10/22/2025 02:47:08 | 10/24/2025 06:50:02 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001168 | PCM-20251021-00002423 | TT-20251021-02503 | EM | Region_6 | SBA2020 | SBA2020 |  |  |  | Khurram Nawaz Muhammad Akram | 10/21/2025 22:14:46 | 10/23/2025 08:59:41 | 10/22/2025 10:14:46 | TRX FAULTY (FF FF FF FF FF FF shared:S) at SBA2020-P2 @ Sceco | 10/21/2025 22:07:21 | Minor | 7606 | TRX FAULTY | 10/21/2025 22:07:18 | P2 | 2G | baish | Sceco | 2G_Cell SA | SBA2020 | FLM_EM | [5 empty] | FF FF FF FF FF FF shared:S |  |  | API | 10/21/2025 22:14:46 | 10/23/2025 08:59:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251021001169 | PCM-20251021-00002429 | TT-20251021-02509 | EM | [7 empty] | 10/21/2025 22:20:58 | 10/21/2025 22:20:58 | 10/22/2025 02:20:58 | DOOR OPEN at ABHA-E-SEC0022_OCS @ Sceco_STB | 10/21/2025 22:20:48 | Critical | 1-12307 | DOOR OPEN | 10/21/2025 22:20:37 | P1 | DWDM |  | Sceco_STB | DWDM NSA | ABHA | FLM_EM | [5 empty] | 0-TO ABH0027 (AB1)&SHUQAIQ-SEC0019(1-A)-71-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/21/2025 22:20:58 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001172 | PCM-20251021-00002436 | TT-20251021-02504 | Telecom | Region_4 | JED1M7164 | JED0164 |  |  |  | Mohammed Ramadan A Abu Abid | 10/21/2025 22:23:53 | 10/23/2025 17:17:26 | 10/22/2025 04:23:53 | BASE STATION ANTENNA LINE PROBLEM at JED1M7164-CA-L900-L800-P1-WDM-SBTS @ Sceco | 10/21/2025 22:07:19 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/21/2025 22:07:11 | P1 | 4G | jeddah | Sceco | LTE NSA | JED1M7164 | FLM_TE |  |  | PCM-20251021-00002424 | Please check HW at the site | Please check HW at the site |  |  |  | API | 10/21/2025 22:23:53 | 10/23/2025 17:17:26 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001174 | PCM-20251021-00002438 | TT-20251021-02479 | Telecom | Region_5 | MAK2964 | MAK2964 |  |  |  | Sarwar Saheb Kolkar Muhammad | 10/21/2025 22:24:58 | 10/21/2025 22:24:58 | 10/22/2025 04:24:58 | BASE STATION SERVICE PROBLEM (RF module gain adjusting failure) at MAK2964-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/21/2025 21:53:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 21:52:52 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2964 | FLM_TE |  |  | PCM-20251021-00002405 | Alarm is cleared, please close | Alarm is cleared, please close |  |  |  | API | 10/21/2025 22:24:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001175 | PCM-20251021-00002441 | TT-20251021-02522 | Telecom | Region_4 | JED1MN0196 | JED0196 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 22:31:50 | 10/21/2025 22:31:50 | 10/22/2025 04:31:50 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0196-NR2.6 @ Sceco | 10/21/2025 22:30:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 22:30:34 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0196 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 22:31:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251021001177 | PCM-20251021-00002443 | TT-20251021-02524 | Telecom | [7 empty] | 10/21/2025 22:32:20 | 10/21/2025 22:32:20 | 10/22/2025 04:32:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6006-G9-L18-L21-NR3.5-SBTS-MMM @ Sceco | 10/21/2025 22:31:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 22:31:35 | P3 | 2G |  | Sceco | 5G_Cell SA | JED6006 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 22:32:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001179 | PCM-20251021-00002446 | TT-20251021-02529 | Telecom | Region_3 | RSP0001-MDC-NE8K-M14-02 | RSP0001 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Hossam Ali Ahmed Ali | 10/21/2025 22:43:12 | 10/22/2025 18:45:31 | 10/22/2025 10:43:12 | Bad Package Error Rising at RSP0001-MDC-NE8K-M14-02 @ Sceco | 10/21/2025 22:42:37 | Minor | 101-2501403 | Bad Package Error Rising | 10/21/2025 22:42:29 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | RSP0001-MDC-NE8K-M14-02 | FLM_TE | [8 empty] | API | 10/21/2025 22:43:12 | 10/21/2025 23:07:35 | 10/22/2025 18:45:10 |  |  | 10/22/2025 18:45:31 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001181 | PCM-20251021-00002448 | TT-20251021-02531 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/21/2025 22:46:48 | 10/21/2025 22:56:55 | 10/22/2025 10:46:48 | RF Unit Maintenance Link Failure at DAM6027-DCU1 @ Sceco | 10/21/2025 22:41:47 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/21/2025 22:41:33 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/21/2025 22:46:48 | 10/21/2025 22:56:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001184 | PCM-20251021-00002450 | TT-20251021-02533 | Telecom | Region_5 | MAK1MN0808 | MAK0808 |  |  |  | Mosab Nasr eldeen Mohamed | 10/21/2025 22:49:54 | 10/21/2025 22:49:54 | 10/22/2025 04:49:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0808-NR2.6-P2 @ Sceco | 10/21/2025 22:49:10 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 22:49:02 | P2 | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0808 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/21/2025 22:49:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001186 | PCM-20251021-00002455 | TT-20251021-02539 | Reference_telecom | Region_3 | YNA0508 | YNA0508 |  |  |  | Muhammad Sajjad R3 | 10/21/2025 23:00:46 | 10/22/2025 17:26:58 | 10/22/2025 05:00:46 | RF Unit VSWR Threshold Crossed at YNA0508-P1_SRAN @ Sceco | 10/21/2025 22:37:23 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/21/2025 22:37:11 | P1 | SRAN | yanbu | Sceco | 2G NSA | YNA0508 | FLM_TE | [8 empty] | API | 10/21/2025 23:00:46 | 10/22/2025 17:26:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001187 | PCM-20251021-00002456 | TT-20251021-02540 | EM | Region_4 | SAD1M7340 | SAD0340 |  |  |  | Walid Magdy Tawfik Elbana | 10/21/2025 23:01:47 | 10/21/2025 23:01:47 | 10/22/2025 11:01:47 | SHELTER DOOR OPEN at SAD1M7340-G9-L18-SBTS-P2 @ Sceco | 10/21/2025 23:01:24 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 23:01:13 | P3 | 4G | taif | Sceco | LTE NSA | SAD1M7340 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 23:01:47 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001189 | PCM-20251021-00002459 | TT-20251021-02517 | Telecom | Region_4 | JED1U6052 | JED6152 |  |  |  | Mohamed Farag Abdelbary | 10/21/2025 23:04:50 | 10/22/2025 15:47:59 | 10/22/2025 05:04:50 | CELL OPERATION DEGRADED (Sleeping Cell Detection Due To Degraded RACH Setup Attempts) at JED1U6052-P3-CA @ Sceco | 10/21/2025 22:15:17 | Major | 7654 | CELL OPERATION DEGRADED | 10/21/2025 22:15:10 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6052 | FLM_TE |  |  | PCM-20251021-00002435 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/21/2025 23:04:50 | 10/22/2025 15:47:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001194 | PCM-20251021-00002466 | TT-20251021-02350 | Telecom | Region_5 | MAK1M9223 | MAK0223 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/21/2025 23:08:34 | 10/21/2025 23:08:34 | 10/22/2025 11:08:34 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface;Default System Time) at MAK1M9223-P3-CA-L800-SBTS @ Sceco | 10/21/2025 20:06:27 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 17:18:08 | P3 | 4G | makkah | Sceco | LTE NSA | MAK1M9223 | FLM_TE |  |  | PCM-20251021-00002311 | site was down please handle with same RCA | site was down please handle with same RCA |  |  |  | API | 10/21/2025 23:08:34 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001195 | PCM-20251021-00002467 | TT-20251021-02543 | Reference_telecom | Region_4 | JED2074 | JED2074 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/21/2025 23:11:35 | 10/21/2025 23:11:35 | 10/22/2025 11:11:35 | ReplaceableUnitProblem observed in JED2074 FTK towards 10.10.185.131 @ Sceco | 10/21/2025 11:11:24 | Minor |  | ReplaceableUnitProblem | 10/21/2025 11:11:20 | P3 | 2G | jeddah | Sceco | TX NSA | JED2074 | FLM_TE | [8 empty] | API | 10/21/2025 23:11:35 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001205 | PCM-20251021-00002478 | TT-20251021-02561 | Reference_telecom | Region_6 | ABH0161 | ABH0161 | Transsmission | MW_HW_stuck | Reset ODU | Amir Sohail | 10/21/2025 23:23:27 | 10/23/2025 01:09:45 | 10/22/2025 11:23:27 | Degrade observed in ABH0161_02 towards 10.10.144.113 @ Sceco_STB | 10/21/2025 20:24:26 | Minor |  | Degrade | 10/21/2025 20:23:29 | P1 | 2G | abha | Sceco_STB | TX NSA | ABH0161 | FLM_TE | [8 empty] | API | 10/21/2025 23:23:27 | 10/21/2025 23:26:38 | 10/22/2025 16:32:49 | 10/22/2025 16:32:52 | 10/22/2025 16:45:04 | 10/23/2025 01:09:45 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251021001206 | PCM-20251021-00002483 | TT-20251021-02556 | Telecom | Region_5 | BIK1M3153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/21/2025 23:25:32 | 10/21/2025 23:25:32 | 10/22/2025 05:25:32 | 1(3G) sites down under BIK0153-P3/BIK1M3153-P3 @ Generator_SG | 10/21/2025 23:18:04 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/21/2025 23:17:25 | P3 | 3G | makkah | Generator_SG | 3G SA | BIK0153-P3 | FLM_TE | BIK0153 | Results: DOWN SITE HUB BIK0153-P3 BIK0153 Summary: Hub: BIK0153, Down Count: 1, Down Sites: BIK0153-P3 Alarm Summary: BIK0153 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/21/2025 23:25:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001207 | PCM-20251021-00002485 | TT-20251021-02189 | Telecom | Region_2 | RIY2M8042 | RIY2042 | Equipment | BTS_Cable | Replace Fiber Cable | WAQAR AHMED BASHIR AHMED | 10/21/2025 23:27:10 | 10/21/2025 23:38:01 | 10/22/2025 05:27:10 | Cell Unavailable at RIY2M8042-P2-L800-L900 @ Sceco | 10/21/2025 17:52:28 | Major | 29240 | Cell Unavailable | 10/21/2025 17:50:55 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M8042 | FLM_TE |  |  | PCM-20251021-00002477 | Approved as per FLM TS Item # 14130621 | Approved as per FLM TS Item # 14130621 |  |  |  | API | 10/21/2025 23:27:10 | 10/21/2025 23:37:22 | 10/21/2025 23:37:32 | 10/21/2025 23:37:34 | 10/21/2025 23:37:36 | 10/21/2025 23:38:01 |  | WAQAR AHMED BASHIR AHMED |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001217 | PCM-20251021-00002496 | TT-20251021-02580 | EM | Region_4 | JED1M7309 | JED0309 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/21/2025 23:46:43 | 10/23/2025 11:51:20 | 10/22/2025 11:46:43 | SHELTER DOOR OPEN at JED1M7309-CA-L900-L800-SBTS @ Sceco | 10/21/2025 23:46:24 | Minor | 7103 | SHELTER DOOR OPEN | 10/21/2025 23:46:18 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7309 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/21/2025 23:46:43 | 10/23/2025 11:51:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001220 | PCM-20251021-00002503 | TT-20251021-02565 | Telecom | Region_4 | HHR0489 | HHR0489 |  |  |  | Anas Mohamedelamin Abbas Mustafa | 10/21/2025 23:52:20 | 10/22/2025 09:54:01 | 10/22/2025 03:52:20 | 2(2G) 2(LTE) 2(5G) sites down under HHR0484-P1-VIP-HHR,HHR0489-P1-VIP-HHR/HHR0489-P1-VIP-HHR @ Generator_SG | 10/21/2025 23:20:33 | Critical | 7706 | BTS O&M LINK FAILURE | 10/21/2025 23:20:30 | VIP | 2G | jeddah | Generator_SG | 2G SA | HHR0489-P1-VIP-HHR 2G,HHR0484-P1-VIP-HHR 2G | FLM_EM | HHR0489 | Dear team , Hub: HHR0489 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | PCM-20251021-00002488 | Dear team , Hub: HHR0489 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM | Dear team , Hub: HHR0489 We are observing RSL -99.00 at far end, Kindly visit the site and check the issue as we are suspecting power issue at site. Kindly update TT under EM, FLM |  | sites down |  | API | 10/21/2025 23:52:20 | 10/22/2025 09:54:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251021001223 | PCM-20251021-00002511 | TT-20251021-02591 | EM | Region_6 | BHAB0836 | BHAB0836 |  |  |  | Zia Ur Rahamn | 10/21/2025 23:56:33 | 10/22/2025 05:56:25 | 10/22/2025 11:56:33 | AIRCON 1 FAILURE at BHAB0836-GSM-UMTS-P3 @ Sceco | 10/21/2025 23:48:33 | Minor | 7103 | AIRCON 1 FAILURE | 10/21/2025 23:48:23 | P3 | 2G | mohail | Sceco | 2G NSA | BHAB0836 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/21/2025 23:56:33 | 10/22/2025 05:56:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251021001224 | PCM-20251021-00002512 | TT-20251021-02583 | Telecom | Region_3 | YNB0672 | YNB0672 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Muhammad Sajjad R3 | 10/21/2025 23:56:41 | 10/22/2025 17:30:33 | 10/22/2025 05:56:41 | 2(2G) 1(3G) 2(LTE) sites down under YNB0665-P2,YNB0645-P2 @ Sceco | 10/21/2025 23:48:52 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/21/2025 23:47:19 | P1 | SRAN | yanbu | Sceco | LTE SA | YNB0645-P2-L800 LTE,YNB0665-P2 LTE | FLM_TE | YNB0672 | Dear FLM, We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | PCM-20251021-00002509 | Dear FLM, We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | Dear FLM, We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/21/2025 23:56:41 | 10/22/2025 17:26:59 | 10/22/2025 17:30:22 |  |  | 10/22/2025 17:30:33 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000003 | PCM-20251022-00000003 | TT-20251021-02592 | EM | Region_6 | BHAB2055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 00:04:03 | 10/22/2025 03:10:19 | 10/22/2025 06:04:03 | 1(2G/LTE) sites down under BHAB2055-P3-WBB-G3/BHAB2055-P3-WBB-G3 @ Sceco | 10/21/2025 23:56:13 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 23:56:10 | P3 | 2G | Albaha | Sceco | 2G_LTE SA | BHAB2055-P3-WBB-G3 | FLM_EM | BHAB2055 | Results: DOWN SITE HUB BHAB2055-P3-WBB-G3 BHAB2055 Summary: Hub: BHAB2055, Down Count: 1, Down Sites: BHAB2055-P3-WBB-G3 Alarm Summary: BHAB2055 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 00:04:03 | 10/22/2025 03:10:19 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000008 | PCM-20251022-00000011 | TT-20251021-02296 | Reference_telecom | Region_6 | KHS0562 | KHS0562 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/22/2025 00:14:23 | 10/22/2025 02:26:34 | 10/22/2025 06:14:23 | CELL OPERATION DEGRADED (VSWR minor alarm) at KHS1M75622 (Ref:TT-20251006-01416) @ Sceco | 10/09/2025 16:44:49 | Major | 7654 | CELL OPERATION DEGRADED | 10/09/2025 16:44:44 | P2 | 2G | khamis mushyet | Sceco | LTE_Cell SA | KHS0562 | FLM_TE |  |  | PCM-20251021-00002489 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/22/2025 00:14:23 | 10/22/2025 00:14:39 | 10/22/2025 02:26:25 |  |  | 10/22/2025 02:26:34 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000010 | PCM-20251022-00000013 | TT-20251021-02566 | Telecom | Region_4 | TURY0826 | TURY0826 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 00:14:52 | 10/23/2025 07:25:58 | 10/22/2025 06:14:52 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at TURY0826-P2 @ Sceco | 10/21/2025 23:19:48 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 23:19:45 | P2 | 2G | taif | Sceco | 2G_TRX NSA | TURY0826 | FLM_TE |  |  | PCM-20251021-00002482 | kindly check RF path from TOP to bottom with cable connections | kindly check RF path from TOP to bottom with cable connections |  |  |  | API | 10/22/2025 00:14:52 | 10/23/2025 07:25:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000011 | PCM-20251022-00000014 | TT-20251021-02567 | Reference_telecom | Region_5 | MAK1MN0601 | MAK0601 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 00:15:07 | 10/22/2025 00:15:07 | 10/22/2025 04:15:07 | BASE STATION SERVICE PROBLEM (RF Power decreased) at MAK1MN0601-NR2.6-P1-VIP-HRM @ Sceco | 10/21/2025 19:26:14 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 19:26:06 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0601 | FLM_TE |  |  | PCM-20251021-00002484 | kindly check and confirm no dust or air blockage | kindly check and confirm no dust or air blockage |  |  |  | API | 10/22/2025 00:15:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000012 | PCM-20251022-00000016 | TT-20251022-00005 | Telecom | Region_1 | ARM2759 | ARM2759 |  |  |  | Tahir Mahmood Hafiz Yar | 10/22/2025 00:15:33 | 10/22/2025 05:08:48 | 10/22/2025 04:15:33 | 1(LTE) sites down under ARM2759-P1_SRAN-PC @ Power Cube | 10/22/2025 00:07:18 | Critical | 301 | NE Is Disconnected | 10/22/2025 00:07:14 | P1 | SRAN | jubail | Power Cube | LTE SA | ARM2759-P1_SRAN-PC | FLM_TE | ARM2759 | Results: DOWN SITE HUB ARM2759-P1_SRAN-PC ARM2759 Summary: Hub: ARM2759, Down Count: 1, Down Sites: ARM2759-P1_SRAN-PC Alarm Summary: ARM2759 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 00:15:33 | 10/22/2025 05:08:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000013 | PCM-20251022-00000017 | TT-20251022-00009 | EM | Region_1 | Sk1 | SK1 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/22/2025 00:16:11 | 10/22/2025 00:16:11 | 10/22/2025 04:16:11 | Door opening alarm BSC New shelter at SK1-Shelter 4-WDM-HUB-Core-P1 @ Sceco_STB | 10/22/2025 00:15:39 | Critical | 65134 | Door opening alarm BSC New shelter | 10/22/2025 00:15:36 | P1 | DWDM | sakaka | Sceco_STB | 2G NSA | SK1 | FLM_EM | [8 empty] | API | 10/22/2025 00:16:11 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251022000015 | PCM-20251022-00000019 | TT-20251022-00011 | EM | [7 empty] | 10/22/2025 00:16:41 | 10/22/2025 00:16:41 | 10/22/2025 04:16:41 | DOOR OPEN at 8760-SEC0042_OCS @ Sceco | 10/22/2025 00:16:24 | Critical | 1-12307 | DOOR OPEN | 10/22/2025 00:16:12 | P1 | DWDM |  | Sceco | DWDM NSA | 8760 | FLM_EM | [5 empty] | 0-TO 8708-SEC0041(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/22/2025 00:16:41 | [10 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251022000017 | PCM-20251022-00000022 | TT-20251022-00017 | Telecom | [7 empty] | 10/22/2025 00:18:53 | 10/22/2025 00:18:53 | 10/22/2025 04:18:53 | Optical Remove at JED6006-KASC-Room2-CSG-01 @ Sceco | 10/21/2025 23:10:05 | Critical | 101-2505222 | Optical Remove | 10/21/2025 23:09:58 | P3 | 2G |  | Sceco | IPRAN NSA | JED6006-KASC-Room2-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 00:18:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000020 | PCM-20251022-00000046 | TT-20251022-00044 | EM | Region_3 | R3_MD_HWBSC02 | MD2 |  |  |  | Essam Aboulfadil | 10/22/2025 00:28:03 | 10/22/2025 11:18:12 | 10/22/2025 04:28:03 | Intruder Alarm BATT Room at R3_MD_HWBSC02 @ Sceco_STB | 10/22/2025 00:27:34 | Critical | 65374 | Intruder Alarm BATT Room | 10/22/2025 00:27:31 | P1 | BSC | madinah | Sceco_STB | 2G NSA | R3_MD_HWBSC02 | FLM_EM | [8 empty] | API | 10/22/2025 00:28:03 | 10/22/2025 11:18:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000027 | PCM-20251022-00000062 | TT-20251022-00051 | Telecom | Region_4 | JDJZ0772 | JDJZ0772 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mudassar Bashir Bashir Ahmad | 10/22/2025 00:35:31 | 10/23/2025 12:42:31 | 10/22/2025 06:35:31 | 1(5G) sites down under JDJZ0772-GSM-P3-USF @ Generator_DG | 10/22/2025 00:27:12 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 00:27:09 | P3 | 2G | qunfuddah | Generator_DG | 5G SA | JDJZ0772-GSM-P3-USF | FLM_TE | JDJZ0772 | Results: DOWN SITE HUB JDJZ0772-GSM-P3-USF JDJZ0772 Summary: Hub: JDJZ0772, Down Count: 1, Down Sites: JDJZ0772-GSM-P3-USF Alarm Summary: JDJZ0772 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.162.250.108:8080] [URL:http://10.162.250.108:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 00:35:31 | 10/22/2025 10:50:57 | 10/23/2025 12:42:17 |  |  | 10/23/2025 12:42:31 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000029 | PCM-20251022-00000079 | TT-20251022-00070 | EM | Region_6 | TNM2093 | TNM2093 |  |  |  | ISHFAQ HUSSAIN MUSHTAQ HUSSAIN | 10/22/2025 00:44:51 | 10/22/2025 23:55:43 | 10/22/2025 06:44:51 | 1(2G/LTE) sites down under TNM2093-P3/TNM2093-P3 @ Sceco_STB | 10/22/2025 00:36:24 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 00:36:20 | P3 | 2G | mohail | Sceco_STB | 2G_LTE SA | TNM2093-P3 | FLM_EM | TNM2093 | Results: DOWN SITE HUB TNM2093-P3 TNM2093 Summary: Hub: TNM2093, Down Count: 1, Down Sites: TNM2093-P3 Alarm Summary: TNM2093 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 00:44:51 | 10/22/2025 23:55:43 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000030 | PCM-20251022-00000081 | TT-20251022-00087 | Telecom | Region_4 | JED1M8139 | JED2139 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 00:47:41 | 10/22/2025 15:45:12 | 10/22/2025 04:47:41 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8139-CA-L1800-L800-FWA-P1-VIP @ Sceco | 10/22/2025 00:47:04 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 00:46:53 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8139 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 00:47:41 | 10/22/2025 15:45:12 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000034 | PCM-20251022-00000098 | TT-20251022-00099 | Telecom | Region_1 | YBR2M7617 | YBR0617 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 01:01:01 | 10/22/2025 16:06:49 | 10/22/2025 07:01:01 | 1(LTE) sites down under YBR0617-L800-P3-USF @ Power Cube | 10/22/2025 00:54:13 | Major | 29213 | eNodeB S1 Control Plane Transmission Interruption | 10/22/2025 00:52:37 | P3 | 4G | hafouf | Power Cube | LTE SA | YBR0617-L800-P3-USF | FLM_TE | YBR0617 | Results: DOWN SITE HUB YBR0617-L800-P3-USF YBR0617 Summary: Hub: YBR0617, Down Count: 1, Down Sites: YBR0617-L800-P3-USF Alarm Summary: YBR0617 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 01:01:01 | 10/22/2025 08:41:26 | 10/22/2025 16:06:38 |  |  | 10/22/2025 16:06:49 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000035 | PCM-20251022-00000100 | TT-20251022-00102 | Telecom | Region_3 | MDN2M1815 | MDN0815 | Equipment | BTS_Cable | Reconnect BTS/BBU Power Cable | Ibrahim Mohammad AbdulMalik alraee | 10/22/2025 01:02:49 | 10/22/2025 21:13:28 | 10/22/2025 07:02:49 | 1(2G) sites down under MDN0815-P3/R3_MD_HWBSC01 @ Sceco | 10/22/2025 00:54:44 | Major | 21825 | CSL Fault | 10/22/2025 00:54:42 | P3 | 2G | madinah | Sceco | 2G SA | MDN0815-P3 | FLM_TE | MDN0815 | Results: DOWN SITE HUB MDN0815-P3 MDN0815 Summary: Hub: MDN0815, Down Count: 1, Down Sites: MDN0815-P3 Alarm Summary: MDN0815 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 01:02:49 | 10/22/2025 11:12:32 | 10/22/2025 21:13:17 |  |  | 10/22/2025 21:13:28 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000038 | PCM-20251022-00000104 | TT-20251022-00109 | EM | Region_4 | JED1M8619 | JED2619 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 01:07:36 | 10/22/2025 21:59:31 | 10/22/2025 07:07:36 | 1(2G/LTE/5G) sites down under JED2619-P3 @ Sceco | 10/22/2025 00:59:28 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 00:59:24 | P3 | 4G | jeddah | Sceco | LTE SA | JED2619-P3-CA-L800 | FLM_TE | JED2619 | Results: DOWN SITE HUB JED2619-P3-CA-L800 JED2619 Summary: Hub: JED2619, Down Count: 1, Down Sites: JED2619-P3-CA-L800 Alarm Summary: JED2619 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.48.100:8080] [URL:http://10.97.48.100:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 01:07:36 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000040 | PCM-20251022-00000108 | TT-20251022-00116 | EM | Region_1 | SAK0585 | SAK0585 |  |  |  | Ahmed Mahmoud Muhammed Saleh | 10/22/2025 01:10:56 | 10/22/2025 01:10:56 | 10/22/2025 05:10:56 | Door opening alarm at SAK0585-P1-Core-SHOP-HUB-WDM_SRAN-FON @ Sceco | 10/22/2025 01:10:20 | Critical | 65101 | Door opening alarm | 10/22/2025 01:10:15 | P1 | SRAN | sakaka | Sceco | 2G NSA | SAK0585 | FLM_EM | [8 empty] | API | 10/22/2025 01:10:56 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000043 | PCM-20251022-00000110 | TT-20251022-00118 | Telecom | Region_1 | JBL2139 | JBL2139 | Equipment | BSS_HW_Stuck | Reset RRU | Rafiq Ahmed Elturifi | 10/22/2025 01:11:58 | 10/22/2025 15:59:25 | 10/22/2025 13:11:58 | RF Unit ALD Current Out of Range at JBL2139-P2_SRAN @ Generator_SG | 10/22/2025 01:09:25 | Minor | 26530 | RF Unit ALD Current Out of Range | 10/22/2025 01:07:51 | P2 | SRAN | jubail | Generator_SG | 2G NSA | JBL2139 | FLM_TE | [8 empty] | API | 10/22/2025 01:11:58 | 10/22/2025 09:28:03 | 10/22/2025 10:28:19 | 10/22/2025 10:28:24 | 10/22/2025 12:32:23 | 10/22/2025 15:59:25 |  | Rafiq Ahmed Elturifi |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000044 | PCM-20251022-00000117 | TT-20251021-02390 | Reference_telecom | Region_6 | DMD1M7043 | DMD0043 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Zeshan Ali Adnan | 10/22/2025 01:15:26 | 10/22/2025 15:07:05 | 10/22/2025 13:15:26 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at DMD1M7043-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/21/2025 18:55:12 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 18:46:23 | P2 | 4G | jizan | Sceco | LTE NSA | DMD1M7043 | FLM_TE |  |  | PCM-20251021-00002463 | Dear FLM team, kindly check it related to SBAR0706-SBAR0706 activity | Dear FLM team, kindly check it related to SBAR0706-SBAR0706 activity |  |  |  | API | 10/22/2025 01:15:26 | 10/22/2025 11:03:51 | 10/22/2025 15:06:36 |  |  | 10/22/2025 15:07:05 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000045 | PCM-20251022-00000124 | TT-20251022-00132 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/22/2025 01:21:47 | 10/22/2025 08:23:04 | 10/22/2025 05:21:47 | The Device is offline at RIYB6066-CSG-01 @ Sceco | 10/22/2025 01:21:22 | Critical | 101-7 | The Device is offline | 10/22/2025 01:21:20 | P3 | IPRAN | riyadh | Sceco | IPRAN SA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 01:21:47 | 10/22/2025 08:23:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000047 | PCM-20251022-00000127 | TT-20251022-00139 | Telecom | Region_4 | JED1M7980 | JED0980 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 01:25:24 | 10/22/2025 01:25:24 | 10/22/2025 07:25:24 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1M7980-CA-L800-SBTS @ Sceco | 10/22/2025 01:20:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 01:20:25 | P3 | 4G | jeddah | Sceco | LTE_Cell SA | JED1M7980 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/22/2025 01:25:24 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000048 | PCM-20251022-00000128 | TT-20251021-02526 | Reference_telecom | Region_6 | ARS1M7166 | ARS0166 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Zeshan Ali Adnan | 10/22/2025 01:25:38 | 10/22/2025 15:05:54 | 10/22/2025 13:25:38 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ARS1M7166-P2-NCA-L800-SBTS @ Sceco | 10/21/2025 20:38:48 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 20:34:38 | P2 | 4G | jizan | Sceco | LTE NSA | ARS1M7166 | FLM_TE |  |  | PCM-20251021-00002470 | Dear FLM team, kindly check as it related to SBAR0706-DMD0042 activity | Dear FLM team, kindly check as it related to SBAR0706-DMD0042 activity |  |  |  | API | 10/22/2025 01:25:38 | 10/22/2025 11:03:51 | 10/22/2025 15:05:29 |  |  | 10/22/2025 15:05:54 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000049 | PCM-20251022-00000132 | TT-20251022-00054 | Telecom | Region_2 | BURA0050-ZQa02-1-CSG-05 | BUR0005 | Equipment | SFP_BTS | Clean SFP | Muhammad Naeem Muhammad Gulzar | 10/22/2025 01:26:33 | 10/22/2025 05:08:41 | 10/22/2025 13:26:33 | Bad Package Error Rising at BURA0050-ZQa02-1-CSG-05 @ Sceco | 10/22/2025 00:31:57 | Minor | 101-2501403 | Bad Package Error Rising | 10/22/2025 00:31:49 | P2 | IPRAN | buraidah | Sceco | IPRAN NSA | BURA0050-ZQa02-1-CSG-05 | FLM_TE |  |  | PCM-20251022-00000101 | GE0-13-3 connected with MW,Please check patch cord and sfp Item=34060742 | GE0-13-3 connected with MW,Please check patch cord and sfp Item=34060742 |  |  |  | API | 10/22/2025 01:26:33 | 10/22/2025 04:03:21 | 10/22/2025 04:03:28 | 10/22/2025 04:03:39 |  | 10/22/2025 05:08:41 |  | Muhammad Naeem Muhammad Gulzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000050 | PCM-20251022-00000133 | TT-20251021-01969 | Telecom | Region_4 | MLJI0204 | MLJI0204 |  |  |  | TOSIF AHMED - MUHAMMAD SHARIF | 10/22/2025 01:26:53 | 10/22/2025 06:58:01 | 10/22/2025 07:26:53 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at MLJI0204-P3 @ Generator_SG | 10/21/2025 16:41:26 | Major | 7607 | TRX OPERATION DEGRADED | 10/21/2025 16:41:23 | P3 | 2G | alaith | Generator_SG | 2G_TRX NSA | MLJI0204 | FLM_TE |  |  | PCM-20251021-00002473 | Dear FLM team, kindly perform HC for MW SQR0184-TFBH9443 | Dear FLM team, kindly perform HC for MW SQR0184-TFBH9443 |  |  |  | API | 10/22/2025 01:26:53 | 10/22/2025 06:58:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000051 | PCM-20251022-00000135 | TT-20251022-00147 | EM | Region_6 | NMR1M8000 | NMR2000 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 01:27:59 | 10/22/2025 03:10:20 | 10/22/2025 13:27:59 | LOW BATTERY VOLTAGE 46.3V at NMR1M8000-G9-L8-L18-SBTS-WBB-G3 @ Generator_SG | 10/22/2025 01:20:05 | Minor | 7103 | LOW BATTERY VOLTAGE 46.3V | 10/22/2025 01:19:54 | P3 | 4G | Albaha | Generator_SG | LTE NSA | NMR1M8000 | FLM_EM | [5 empty] | LOW BATTERY VOLTAGE 46.3V |  |  | API | 10/22/2025 01:27:59 | 10/22/2025 03:10:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251022000052 | PCM-20251022-00000138 | TT-20251022-00138 | EM | [7 empty] | 10/22/2025 01:29:31 | 10/22/2025 01:29:31 | 10/22/2025 07:29:31 | 1(2G/LTE) sites down under RIYB6066-P3/R2_RY4_HWBSC01 @ Sceco | 10/22/2025 01:21:06 | Major | 21825 | CSL Fault | 10/22/2025 01:21:05 | P3 | 2G |  | Sceco | 2G_LTE SA | RIYB6066-P3 | FLM_EM | RIYB6066 | Results: DOWN SITE HUB RIYB6066-P3 RIYB6066 Summary: Hub: RIYB6066, Down Count: 1, Down Sites: RIYB6066-P3 Alarm Summary: RIYB6066 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 01:29:31 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000053 | PCM-20251022-00000139 | TT-20251022-00133 | Telecom | Region_4 | JED2025 | JED2025 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/22/2025 01:30:23 | 10/22/2025 10:27:55 | 10/22/2025 07:30:23 | 1(2G) 1(LTE) 2(5G) sites down under JED0349-NR2.6-P2,JED2025-P3/JED2025-P3 @ Sceco | 10/22/2025 01:20:28 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 01:20:24 | P3 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED0349-NR2.6-P2 5G,JED2025-P3 2G_LTE | FLM_TE | JED2025 | DOWN SITE HUB TX FB JED0349 JED0349 LOS to Air Scale JED2025 JED2025 LOS to Air Scale | PCM-20251022-00000134 | DOWN SITE HUB TX FB JED0349 JED0349 LOS to Air Scale JED2025 JED2025 LOS to Air Scale | DOWN SITE HUB TX FB JED0349 JED0349 LOS to Air Scale JED2025 JED2025 LOS to Air Scale |  | sites down |  | API | 10/22/2025 01:30:23 | 10/22/2025 10:26:38 | 10/22/2025 10:27:49 |  |  | 10/22/2025 10:27:55 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000055 | PCM-20251022-00000147 | TT-20250922-02139 | MW_HC | Region_6 | AQQ0036 | AQQ0036 | Transsmission | SFP_Transmission | Reset SFP | Manzoor Ahmed | 10/22/2025 01:33:19 | 10/22/2025 19:25:00 | 10/22/2025 13:33:19 | As per BO request NOKIA MW link AQQ0036-AQQ0038 as H ODU down AQQ0038 | 09/22/2025 20:00:44 | Minor | 113388 | LOF | 09/22/2025 20:00:46 | P2 | 2G | Albaha | Sceco_STB | TX NSA | AQQ0036-AQQ0038 | FLM_TE |  |  | PCM-20251022-00000065 | kindly check again as XPD NOK and V UBT SFP NOK at AQQ0036 | kindly check again as XPD NOK and V UBT SFP NOK at AQQ0036 |  |  |  | API | 10/22/2025 01:33:19 | 10/22/2025 14:04:37 | 10/22/2025 18:17:07 | 10/22/2025 18:17:12 | 10/22/2025 18:17:15 | 10/22/2025 19:25:00 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000056 | PCM-20251022-00000149 | TT-20251022-00172 | Telecom | Region_2 | RIYB6066-CSG-01 | RIYB6066 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/22/2025 01:33:40 | 10/22/2025 08:23:04 | 10/22/2025 13:33:40 | Chassis Fail at RIYB6066-CSG-01 @ Sceco | 10/22/2025 01:33:11 | Minor | 101-2505202 | Chassis Fail | 10/22/2025 01:26:58 | P3 | IPRAN | riyadh | Sceco | IPRAN NSA | RIYB6066-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 01:33:40 | 10/22/2025 08:23:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000060 | PCM-20251022-00000166 | TT-20251022-00194 | EM | Region_6 | NJR0163 | NJR0163 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/22/2025 01:47:38 | 10/22/2025 03:38:28 | 10/22/2025 13:47:38 | RECTIFIER MAINS POWER FAILURE FO at NJR0163-G9-L8-L18-L21-NNR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/22/2025 01:39:43 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE FO | 10/22/2025 01:39:17 | P2 | 2G | najran | Sceco | 2G NSA | NJR0163 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE FO |  |  | API | 10/22/2025 01:47:38 | 10/22/2025 02:11:57 | 10/22/2025 02:36:09 | 10/22/2025 02:36:14 | 10/22/2025 02:54:19 | 10/22/2025 03:38:28 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000064 | PCM-20251022-00000175 | TT-20251022-00197 | Telecom | Region_3 | YNB0672 | YNB0672 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Muhammad Sajjad R3 | 10/22/2025 01:56:33 | 10/22/2025 17:30:16 | 10/22/2025 05:56:33 | 5(2G) 5(3G) 4(LTE) sites down under YB1MBSCH01 @ Sceco | 10/22/2025 01:48:51 | Critical | 21825 | CSL Fault | 10/22/2025 01:48:51 | P1 | SRAN | yanbu | Sceco | 2G_3G_LTE SA | YNB0416-P2-L800-CA LTE,YNB0664-P2 LTE,YNB0652-P1-L800-SHOP LTE,YNB0672-P3 2G_3G_LTE,YNB0308-P2 2G,YNB0642-P2 2G | FLM_TE | YNB0672 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | PCM-20251022-00000172 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YNB0672 DIR YNB0541,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/22/2025 01:56:33 | 10/22/2025 17:26:59 | 10/22/2025 17:30:09 |  |  | 10/22/2025 17:30:16 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000086 | PCM-20251022-00000214 | TT-20251022-00241 | Telecom | Region_2 | RIY0462 | RIY0462 | Transsmission | Fiber CUT | STC LL cut | Muhammad Naseer Muhammad Nazir | 10/22/2025 02:12:24 | 10/22/2025 03:56:17 | 10/22/2025 06:12:24 | OSC_LOS at RIY0462-OCS1 @ Sceco | 10/22/2025 02:11:47 | Critical | 1-12843 | OSC_LOS | 10/22/2025 02:11:36 | P1 | SRAN | riyadh | Sceco | DWDM NSA | RIY0462 | FLM_TE | [5 empty] | 0-1-C-9-F1AST4-2(RM2/TM2(FROM RIY0788))-OSC:1 |  |  | API | 10/22/2025 02:12:24 | 10/22/2025 03:07:22 | 10/22/2025 03:07:51 | 10/22/2025 03:07:56 | 10/22/2025 03:16:14 | 10/22/2025 03:56:17 |  | Muhammad Naseer Muhammad Nazir |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000087 | PCM-20251022-00000216 | TT-20251022-00207 | EM | Region_3 | YNB0678 | YNB0678 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 02:13:41 | 10/22/2025 17:30:00 | 10/22/2025 08:13:41 | 1(2G/3G/LTE) sites down under YNB0678-P2/YB1MBSCH01 @ Sceco | 10/22/2025 01:56:11 | Major | 21825 | CSL Fault | 10/22/2025 01:56:06 | P3 | SRAN | yanbu | Sceco | 2G_3G SA | YNB0678-P2 | FLM_TE | YNB0678 | Results: DOWN SITE HUB YNB0678-P2 YNB0678 Summary: Hub: YNB0678, Down Count: 1, Down Sites: YNB0678-P2 Alarm Summary: YNB0678 No Active Alarm on HUB | PCM-20251022-00000188 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 02:13:41 | 10/22/2025 17:27:00 | 10/22/2025 17:29:47 |  |  | 10/22/2025 17:30:00 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000089 | PCM-20251022-00000221 | TT-20251022-00249 | EM | Region_4 | QIA1M7361 | QIA0361 |  |  |  | Walid Magdy Tawfik Elbana | 10/22/2025 02:16:33 | 10/22/2025 02:16:33 | 10/22/2025 14:16:33 | RECTIFIER MAINS POWER FAILURE at QIA1M7361-L900-L800-P3 @ Sceco | 10/22/2025 02:08:32 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 02:08:23 | P3 | 4G | taif | Sceco | LTE NSA | QIA1M7361 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 02:16:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000090 | PCM-20251022-00000224 | TT-20251022-00203 | Telecom | Region_4 | JED2038 | JED2038 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 02:21:52 | 10/22/2025 12:55:58 | 10/22/2025 08:21:52 | 1(2G) 1(LTE) 2(5G) sites down under JED0294-P3,JED2038-CA-L800-SBTS-P3 @ Sceco | 10/22/2025 01:53:42 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 01:53:39 | P3 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED0294-GSM-P3 5G,JED2038-CA-L800-SBTS-P3 LTE_5G | FLM_TE | JED2038 | DOWN SITE HUB TX FB JED0294 JED0294 Observing no issue at HUB , kindly check locally JED2038 JED2038 LOS to Air Scale | PCM-20251022-00000183 | DOWN SITE HUB TX FB JED0294 JED0294 Observing no issue at HUB , kindly check locally JED2038 JED2038 LOS to Air Scale | DOWN SITE HUB TX FB JED0294 JED0294 Observing no issue at HUB , kindly check locally JED2038 JED2038 LOS to Air Scale |  | sites down |  | API | 10/22/2025 02:21:52 | 10/22/2025 12:55:58 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000092 | PCM-20251022-00000229 | TT-20251022-00243 | Telecom | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 02:23:40 | 10/22/2025 02:23:40 | 10/22/2025 08:23:40 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/22/2025 02:08:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 02:08:43 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7558 | FLM_TE |  |  | PCM-20251022-00000215 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/22/2025 02:23:40 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000093 | PCM-20251022-00000231 | TT-20251022-00225 | Telecom | Region_6 | KMS0045 | KMS0045 | Equipment | Jumper_Cable | Re-Tightened Indoor Jumper cable Connector | Muhammad shafiq Muhammad Rasheed | 10/22/2025 02:23:53 | 10/22/2025 12:09:43 | 10/22/2025 08:23:53 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at KMS0045-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB @ Sceco_STB | 10/22/2025 02:01:17 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 02:01:06 | P1 | 2G | khamis mushyet | Sceco_STB | 5G_Cell SA | KMS0045 | FLM_TE |  |  | PCM-20251022-00000198 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/22/2025 02:23:53 | 10/22/2025 10:43:42 | 10/22/2025 10:45:29 | 10/22/2025 10:45:32 |  | 10/22/2025 12:09:43 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000094 | PCM-20251022-00000239 | TT-20251022-00199 | Reference_telecom | Region_5 | BIK1M7153 | BIK0153 |  |  |  | Hazem Ali Moustafa Ali | 10/22/2025 02:29:11 | 10/22/2025 02:29:11 | 10/22/2025 08:29:11 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BIK1M7153-L800-CA-P3 @ Generator_SG | 10/21/2025 23:52:55 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 23:52:47 | P3 | 4G | makkah | Generator_SG | LTE NSA | BIK1M7153 | FLM_TE |  |  | PCM-20251022-00000169 | PLR alarm active at site, kindly check | PLR alarm active at site, kindly check |  |  |  | API | 10/22/2025 02:29:11 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000095 | PCM-20251022-00000245 | TT-20251022-00278 | EM | Region_6 | BHAQ1M8435 | BHAQ2435 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/22/2025 02:32:03 | 10/22/2025 23:41:48 | 10/22/2025 14:32:03 | Genset Running at BHAQ1M8435-P3 -G900-L800-SBTS @ Generator_DG | 10/22/2025 02:24:09 | Minor | 7103 | Genset Running | 10/22/2025 02:23:58 | P3 | 4G | Albaha | Generator_DG | LTE NSA | BHAQ1M8435 | FLM_EM | [5 empty] | Genset Running |  |  | API | 10/22/2025 02:32:03 | 10/22/2025 10:17:54 | 10/22/2025 23:41:34 |  |  | 10/22/2025 23:41:48 |  | SHAH KHALID |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000096 | PCM-20251022-00000251 | TT-20251022-00127 | Telecom | Region_4 | JDJZ0764 | JDJZ0764 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 02:39:39 | 10/22/2025 13:09:33 | 10/22/2025 08:39:39 | BCF NOTIFICATION (FF FF FF FF FF FF) at JDJZ0764-P2 @ Generator_DG | 10/22/2025 01:10:03 | Major | 7602 | BCF NOTIFICATION | 10/22/2025 01:09:48 | P2 | 2G | qunfuddah | Generator_DG | 2G NSA | JDJZ0764 | FLM_TE |  |  | PCM-20251022-00000119 | Kindly check GPS alarm active on 4G | Kindly check GPS alarm active on 4G |  |  |  | API | 10/22/2025 02:39:39 | 10/22/2025 13:09:33 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000102 | PCM-20251022-00000268 | TT-20251022-00296 | Telecom | Region_5 | MAK1MC2077 | MAK2077 | Equipment | SFP_BTS | Clean SFP | KAMRAN AAMIR | 10/22/2025 02:51:10 | 10/22/2025 12:22:58 | 10/22/2025 08:51:10 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MC2077-NR3.5-P3 @ Sceco | 10/22/2025 02:50:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 02:50:15 | P3 | 5G | makkah | Sceco | 5G_Cell SA | MAK1MC2077 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 02:51:10 |  | 10/22/2025 10:53:32 | 10/22/2025 10:53:39 | 10/22/2025 11:18:52 | 10/22/2025 12:22:58 |  | KAMRAN AAMIR |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000103 | PCM-20251022-00000271 | TT-20251022-00211 | Telecom | Region_4 | QIA0361 | QIA0361 |  |  |  | Walid Magdy Tawfik Elbana | 10/22/2025 02:52:32 | 10/22/2025 04:29:35 | 10/22/2025 06:52:32 | 9(2G) 4(3G) 3(LTE) 2(5G) sites down under TURY0338-P2 @ Sceco | 10/22/2025 01:56:41 | Critical | 7706 | BTS O&M LINK FAILURE | 10/22/2025 01:56:39 | P2 | 2G | taif | Sceco | 2G_3G_5G SA | TUR0693-P2 2G_3G_5G,TURY0338-P2 2G_3G_5G,QIA0361-P2 2G_3G,TUR0691-P3 2G_3G,TFBH0804-P3 2G,TFBH0805-P3 2G,TFBH0766-P3 2G,TURY0692-P3 2G,TFBH0803-P2 2G | FLM_EM | QIA0361 | QIA0361 | PCM-20251022-00000269 | QIA0361 | QIA0361 |  | sites down |  | API | 10/22/2025 02:52:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000105 | PCM-20251022-00000277 | TT-20251022-00290 | Telecom | Region_4 | JED2417 | JED2417 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 02:57:08 | 10/22/2025 17:00:33 | 10/22/2025 08:57:08 | 1(2G) 2(LTE) 2(5G) sites down under JED2417-P3-CA-L800,JED2592-P3/JED2592-P3 @ Sceco | 10/22/2025 02:41:14 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 02:41:09 | P3 | 2G | jeddah | Sceco | 2G_LTE_5G SA | JED2417-P3-CA-L800 LTE,JED2592-P3 2G_LTE_5G | FLM_TE | JED2417 | DOWN SITE HUB TX FB JED2417 JED2417 LOS to Air Scale JED2592 JED2592 LOS to Air Scale | PCM-20251022-00000266 | DOWN SITE HUB TX FB JED2417 JED2417 LOS to Air Scale JED2592 JED2592 LOS to Air Scale | DOWN SITE HUB TX FB JED2417 JED2417 LOS to Air Scale JED2592 JED2592 LOS to Air Scale |  | sites down |  | API | 10/22/2025 02:57:08 | 10/22/2025 05:49:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000113 | PCM-20251022-00000294 | TT-20251022-00214 | EM | Region_2 | RYDM0656 | RYDM0656 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/22/2025 03:02:17 | 10/22/2025 04:44:50 | 10/22/2025 09:02:17 | 1(2G/LTE) sites down under RIY2951-P3 @ Sceco | 10/22/2025 01:58:01 | Major | 301 | NE Is Disconnected | 10/22/2025 01:57:15 | P2 | SRAN | riyadh | Generator_DG | LTE SA | RIY2951-P3_SRAN | FLM_EM | RYDM0656 | Hub:- RYDM0656 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00000275 | Hub:- RYDM0656 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RYDM0656 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 03:02:17 | 10/22/2025 04:44:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000114 | PCM-20251022-00000295 | TT-20251022-00228 | EM | Region_2 | RYDM0656 | RYDM0656 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/22/2025 03:02:56 | 10/22/2025 04:44:51 | 10/22/2025 09:02:56 | 1(2G/LTE) sites down under RIY2989-P3 @ Generator_SG | 10/22/2025 02:03:09 | Major | 301 | NE Is Disconnected | 10/22/2025 02:03:06 | P2 | SRAN | riyadh | Generator_DG | LTE SA | RIY2989-P3_SRAN | FLM_EM | RYDM0656 | Hub:- RYDM0656 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00000276 | Hub:- RYDM0656 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RYDM0656 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 03:02:56 | 10/22/2025 04:44:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000116 | PCM-20251022-00000302 | TT-20251022-00327 | Telecom | Region_1 | HFR2U6102 | HFR6002 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/22/2025 03:13:36 | 10/22/2025 04:23:20 | 10/22/2025 09:13:36 | GSM Local Cell Unusable at HFR2U6102-P3 @ Sceco | 10/22/2025 03:12:15 | Major | 28016 | GSM Local Cell Unusable | 10/22/2025 03:10:53 | P3 | 2G | hafr | Sceco | 2G SA | HFR2U6102 | FLM_TE | [8 empty] | API | 10/22/2025 03:13:36 | 10/22/2025 04:23:20 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000118 | PCM-20251022-00000310 | TT-20251022-00337 | Reference_telecom | Region_4 | JZMA2413 | JZMA2413 |  |  |  | Khizer Hayat | 10/22/2025 03:20:06 | 10/22/2025 05:49:37 | 10/22/2025 15:20:06 | LossOfSignal observed in JZMA2413_01 towards 10.21.73.53 @ Generator_SG | 10/21/2025 15:21:16 | Minor |  | LossOfSignal | 10/21/2025 15:19:56 | P3 | 2G | jeddah | Generator_SG | TX NSA | JZMA2413 | FLM_TE | [8 empty] | API | 10/22/2025 03:20:06 | 10/22/2025 05:49:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000120 | PCM-20251022-00000327 | TT-20251022-00366 | Reference_telecom | Region_4 | JZMA2414 | JZMA2414 |  |  |  | Khizer Hayat | 10/22/2025 03:33:36 | 10/22/2025 05:49:37 | 10/22/2025 15:33:36 | LossOfSignal observed in JZMA2414_02 towards 10.21.73.51 @ Generator_SG | 10/21/2025 15:33:18 | Minor |  | LossOfSignal | 10/21/2025 15:33:14 | P3 | 2G | jeddah | Generator_SG | TX NSA | JZMA2414 | FLM_TE | [8 empty] | API | 10/22/2025 03:33:36 | 10/22/2025 05:49:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000122 | PCM-20251022-00000330 | TT-20251022-00347 | Reference_telecom | Region_6 | KHNJ1M7852 | KHNJ0852 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/22/2025 03:35:23 | 10/22/2025 04:12:27 | 10/22/2025 15:35:23 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHNJ1M7852-L800-P3-SBTS @ Sceco | 10/22/2025 01:26:45 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 01:25:20 | P3 | 4G | najran | Sceco | LTE NSA | KHNJ1M7852 | FLM_TE |  |  | PCM-20251022-00000316 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 03:35:23 | 10/22/2025 04:02:21 | 10/22/2025 04:12:11 |  |  | 10/22/2025 04:12:27 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000124 | PCM-20251022-00000332 | TT-20251022-00345 | Reference_telecom | Region_6 | KHNJ1M7896 | KHNJ0896 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/22/2025 03:35:42 | 10/22/2025 04:12:45 | 10/22/2025 15:35:42 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHNJ1M7896-L800-P3-SBTS @ Sceco | 10/22/2025 01:26:31 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 01:25:36 | P3 | 4G | najran | Sceco | LTE NSA | KHNJ1M7896 | FLM_TE |  |  | PCM-20251022-00000314 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 03:35:42 | 10/22/2025 04:02:22 | 10/22/2025 04:12:33 |  |  | 10/22/2025 04:12:45 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000125 | PCM-20251022-00000333 | TT-20251022-00308 | Telecom | Region_4 | JED1M8176 | JED2176 | Equipment | BSS_HW_Stuck | Reset Interface Card | MALIK ATIF ZAMAN | 10/22/2025 03:36:00 | 10/22/2025 16:58:10 | 10/22/2025 09:36:00 | BASE STATION SERVICE PROBLEM (FSP Reset Needed) at JED1M8176-CA-L1800-L800-P3 @ Sceco | 10/22/2025 02:54:54 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 02:54:50 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8176 | FLM_TE |  |  | PCM-20251022-00000284 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/22/2025 03:36:00 | 10/22/2025 15:45:13 | 10/22/2025 15:46:03 | 10/22/2025 15:49:27 | 10/22/2025 16:42:13 | 10/22/2025 16:58:10 |  | MALIK ATIF ZAMAN |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000126 | PCM-20251022-00000335 | TT-20251022-00367 | Telecom | Region_6 | AQQ1M7039 | AQQ0039 |  |  |  | Manzoor Ahmed | 10/22/2025 03:36:33 | 10/22/2025 14:04:41 | 10/22/2025 15:36:33 | BASE STATION SOFTWARE MANAGEMENT PROBLEM at AQQ1M7039-G9-NL8-L18-NL21-SBTS-P3 @ Sceco | 10/22/2025 03:31:13 | Minor | 7111 | BASE STATION SOFTWARE MANAGEMENT PROBLEM | 10/22/2025 03:28:58 | P3 | 4G | Albaha | Sceco | LTE NSA | AQQ1M7039 | FLM_TE |  |  | PCM-20251022-00000328 | Kindly check the alarm locally at site | Kindly check the alarm locally at site |  |  |  | API | 10/22/2025 03:36:33 | 10/22/2025 14:04:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000127 | PCM-20251022-00000336 | TT-20251022-00371 | Telecom | Region_4 | TAF0287 | TAF0287 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 03:37:09 | 10/22/2025 17:30:03 | 10/22/2025 09:37:09 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF0287-GSM-P3 @ Sceco | 10/22/2025 03:36:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 03:36:23 | P3 | 2G | taif | Sceco | 5G_Cell SA | TAF0287 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 03:37:09 | 10/22/2025 17:30:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000128 | PCM-20251022-00000341 | TT-20251022-00375 | EM | Region_5 | MK5 | MAK5 |  |  |  | Mohamed Aly Abdelkarim Abdel Rahman | 10/22/2025 03:40:14 | 10/22/2025 10:50:52 | 10/22/2025 07:40:14 | door open(Input) (Input-2) at MK5-4 on 10.154.129.209 @ Sceco | 10/22/2025 03:38:14 | Critical | door open(Input) (Input-2) | door open(Input) (Input-2) | 10/22/2025 03:24:50 | P1 | BSC | makkah | Sceco | TX NSA | MK5 | FLM_EM | [8 empty] | API | 10/22/2025 03:40:14 | 10/22/2025 10:50:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000130 | PCM-20251022-00000349 | TT-20251022-00382 | Telecom | Region_1 | SRA2M7012 | SRA0012 |  |  |  | Muhammad Anwar Hussain Akhtar Hussain | 10/22/2025 03:54:01 | 10/22/2025 04:23:21 | 10/22/2025 09:54:01 | 1(LTE) sites down under SRA0012-P3-PC @ Power Cube | 10/22/2025 03:45:40 | Major | 301 | NE Is Disconnected | 10/22/2025 03:45:38 | P3 | 4G | hafr | Power Cube | LTE SA | SRA0012-P3-PC | FLM_TE | SRA0012 | Results: DOWN SITE HUB SRA0012-P3-PC SRA0012 Summary: Hub: SRA0012, Down Count: 1, Down Sites: SRA0012-P3-PC Alarm Summary: SRA0012 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 03:54:01 | 10/22/2025 04:23:21 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251022000131 | PCM-20251022-00000350 | TT-20251022-00389 | EM | Region_4 | JED1M7335 | JED0335 |  |  |  | Amer Attallah Awadallah | 10/22/2025 03:56:17 | 10/22/2025 05:42:36 | 10/22/2025 15:56:17 | HIGH TEMPERATURE 32 DEGREE C at JED1M7335-CA-L900-L800-SBTS @ Sceco | 10/22/2025 03:48:19 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/22/2025 03:48:10 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7335 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/22/2025 03:56:17 | 10/22/2025 04:08:33 | 10/22/2025 04:11:40 | 10/22/2025 04:11:57 | 10/22/2025 05:42:36 | [6 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000134 | PCM-20251022-00000353 | TT-20251022-00391 | EM | Region_1 | DM1MBSCH01 | DM1 |  |  |  | Tasawar Hussain Mohamed Shafqat | 10/22/2025 03:58:22 | 10/22/2025 10:22:22 | 10/22/2025 07:58:22 | Door open Alarm Equipment room at DM1MBSCH01 @ Generator_DG | 10/22/2025 03:58:05 | Critical | 65334 | Door open Alarm Equipment room | 10/22/2025 03:58:01 |  | BSC | dammam | Generator_DG | 2G NSA | DM1MBSCH01 | FLM_EM | [8 empty] | API | 10/22/2025 03:58:22 | 10/22/2025 10:22:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251022000135 | PCM-20251022-00000356 | TT-20251022-00393 | Reference_telecom | Region_4 | JED0947 | JED0947 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 03:59:21 | 10/22/2025 18:41:33 | 10/22/2025 15:59:21 | DialogFailure observed in JED0947_2 towards 10.10.154.135 @ Sceco | 10/21/2025 15:58:54 | Minor |  | DialogFailure | 10/21/2025 15:58:50 | P2 | 2G | jeddah | Sceco | TX NSA | JED0947 | FLM_TE | [8 empty] | API | 10/22/2025 03:59:21 | 10/22/2025 12:55:58 | 10/22/2025 18:37:18 | 10/22/2025 18:37:21 | 10/22/2025 18:41:33 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000140 | PCM-20251022-00000368 | TT-20251022-00404 | EM | Region_4 | JED1M8641 | JED2641 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 04:09:01 | 10/22/2025 14:14:42 | 10/22/2025 10:09:01 | 1(2G/LTE) sites down under JED2641-P3 @ Sceco | 10/22/2025 04:00:49 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 04:00:46 | P3 | 4G | jeddah | Sceco | LTE SA | JED2641-P3-CA-L800-SBTS | FLM_TE | JED2641 | Results: DOWN SITE HUB JED2641-P3-CA-L800-SBTS JED2641 Summary: Hub: JED2641, Down Count: 1, Down Sites: JED2641-P3-CA-L800-SBTS Alarm Summary: JED2641 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.97.168.124:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 04:09:01 | 10/22/2025 12:55:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000141 | PCM-20251022-00000369 | TT-20251022-00407 | EM | Region_3 | YNA2M3508 | YNA0508 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 04:11:01 | 10/22/2025 17:29:40 | 10/22/2025 08:11:01 | 1(2G/3G/LTE) sites down under YNA0508-P1/YB1MBSCH01 @ Sceco | 10/22/2025 04:02:41 | Critical | 22214 | NodeB Unavailable | 10/22/2025 04:02:38 | P2 | 3G | yanbu | Sceco | 3G SA | YNA0508-P1 | FLM_TE | YNA0508 | Results: DOWN SITE HUB YNA0508-P1 YNA0508 Summary: Hub: YNA0508, Down Count: 1, Down Sites: YNA0508-P1 Alarm Summary: YNA0508 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 04:11:01 | 10/22/2025 17:27:00 | 10/22/2025 17:29:32 |  |  | 10/22/2025 17:29:40 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000142 | PCM-20251022-00000370 | TT-20251022-00416 | Telecom | Region_1 | ARM2M3992 | ARM0992 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 04:14:04 | 10/22/2025 16:07:37 | 10/22/2025 10:14:04 | UMTS Cell Unavailable at ARM2M3992-P2 @ Power Cube | 10/22/2025 04:09:12 | Major | 22202 | UMTS Cell Unavailable | 10/22/2025 04:09:10 | P2 | 3G | hafouf | Power Cube | 3G SA | ARM2M3992 | FLM_TE | [8 empty] | API | 10/22/2025 04:14:04 | 10/22/2025 08:41:27 | 10/22/2025 16:07:26 |  |  | 10/22/2025 16:07:37 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000144 | PCM-20251022-00000379 | TT-20251022-00434 | Telecom | Region_4 | JED1MN0905 | JED0905 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 04:24:41 | 10/22/2025 04:24:41 | 10/22/2025 10:24:41 | BASE STATION SERVICE PROBLEM (TX out of order) at JED1MN0905-NR2.6-P3 @ Sceco | 10/22/2025 04:20:00 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 04:19:55 | P2 | 5G | jeddah | Sceco | LTE_Cell SA | JED1MN0905 | FLM_TE | [5 empty] | TX out of order |  |  | API | 10/22/2025 04:24:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000146 | PCM-20251022-00000383 | TT-20251022-00436 | Reference_telecom | Region_6 | NJR2046 | NJR2046 | Transsmission | MW_HW_fault | Replace Fiber Cable | TALEH MUHAMMAD | 10/22/2025 04:26:44 | 10/22/2025 21:16:27 | 10/22/2025 16:26:44 | Degrade observed in NJR2046_04 towards 10.1.230.200 @ Sceco | 10/21/2025 16:27:55 | Minor |  | Degrade | 10/21/2025 16:26:30 | P3 | 2G | najran | Sceco | TX NSA | NJR2046 | FLM_TE | [8 empty] | API | 10/22/2025 04:26:44 | 10/22/2025 04:48:25 | 10/22/2025 20:52:59 | 10/22/2025 20:53:07 | 10/22/2025 20:53:51 | 10/22/2025 21:16:27 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000147 | PCM-20251022-00000384 | TT-20251022-00437 | Reference_telecom | Region_6 | NJR2452 | NJR2452 | Transsmission | MW_HW_fault | Replace Fiber Cable | TALEH MUHAMMAD | 10/22/2025 04:26:45 | 10/23/2025 18:32:58 | 10/22/2025 16:26:45 | LossOfSignal observed in NJR2452 towards 10.1.230.201 @ Sceco | 10/21/2025 16:27:55 | Minor |  | LossOfSignal | 10/21/2025 16:26:30 | P3 | 2G | najran | Sceco | TX NSA | NJR2452 | FLM_TE | [8 empty] | API | 10/22/2025 04:26:45 | 10/22/2025 04:48:26 | 10/22/2025 18:36:39 | 10/22/2025 18:36:43 | 10/22/2025 18:39:00 | 10/23/2025 18:32:58 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251022000148 | PCM-20251022-00000385 | TT-20251022-00438 | Telecom | Region_1 | JBKH0603 | JBKH0603 |  |  |  | Meraj Husain Idd Baksh | 10/22/2025 04:27:16 | 10/22/2025 10:42:19 | 10/22/2025 16:27:16 | BD_STATUS at JBKH0603_NE_1 @ Sceco | 10/22/2025 01:12:41 | Minor | 1-119 | BD_STATUS | 10/22/2025 01:10:56 | P2 | SRAN | dammam | Sceco | TX NSA | JBKH0603 | FLM_TE | [8 empty] | API | 10/22/2025 04:27:16 | 10/22/2025 08:20:46 | 10/22/2025 10:42:05 | 10/22/2025 10:42:14 | 10/22/2025 10:42:19 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000151 | PCM-20251022-00000388 | TT-20251022-00444 | Telecom | Region_3 | YBDB0291 | YBDB0291 |  |  |  | Waqas Shah | 10/22/2025 04:31:56 | 10/22/2025 12:06:23 | 10/22/2025 10:31:56 | COMMUN_FAIL at YBDB0291_OCS @ Generator_DG | 10/22/2025 04:28:28 | Major | 1-199 | COMMUN_FAIL | 10/22/2025 04:28:16 | P1 | DWDM | yanbu | Generator_DG | DWDM NSA | YBDB0291 | FLM_TE | [5 empty] | 2-LOCAL-1(1-C)-6-G6WDAPE-OTHER |  |  | API | 10/22/2025 04:31:56 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000152 | PCM-20251022-00000389 | TT-20251022-00439 | Telecom | Region_3 | YBDB2M4677 | YBDB2677 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Muhammad Sajjad R3 | 10/22/2025 04:33:03 | 10/22/2025 17:29:27 | 10/22/2025 10:33:03 | 1(3G) sites down under YBDB2677-P3/YB1MBSCH01 @ Sceco_STB | 10/22/2025 04:24:45 | Major | 22214 | NodeB Unavailable | 10/22/2025 04:24:42 | P3 | 3G | yanbu | Sceco_STB | 3G SA | YBDB2677-P3 | FLM_TE | YBDB2677 | Results: DOWN SITE HUB YBDB2677-P3 YBDB2677 Summary: Hub: YBDB2677, Down Count: 1, Down Sites: YBDB2677-P3 Alarm Summary: YBDB2677 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 04:33:03 | 10/22/2025 17:27:01 | 10/22/2025 17:29:20 |  |  | 10/22/2025 17:29:27 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000154 | PCM-20251022-00000397 | TT-20251022-00453 | Telecom | Region_3 | YBDB2M2292 | YBDB2292 | Equipment | BTS_Cable | Reconnect Ethernet Cable | Hossam Ali Ahmed Ali | 10/22/2025 04:38:32 | 10/22/2025 18:43:21 | 10/22/2025 08:38:32 | 1(2G) sites down under YBDB2292-P1-HUB/YB1MBSCH01 @ Generator_DG | 10/22/2025 04:30:07 | Critical | 21825 | CSL Fault | 10/22/2025 04:30:03 | P1 | 2G | tabouk | Generator_DG | 2G SA | YBDB2292-P1-HUB | FLM_TE | YBDB2292 | Results: DOWN SITE HUB YBDB2292-P1-HUB YBDB2292 Summary: Hub: YBDB2292, Down Count: 1, Down Sites: YBDB2292-P1-HUB Alarm Summary: YBDB2292 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 04:38:32 | 10/22/2025 07:52:27 | 10/22/2025 18:43:09 |  |  | 10/22/2025 18:43:21 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000155 | PCM-20251022-00000398 | TT-20251022-00460 | Telecom | Region_1 | DAM6027 | DAM6027 |  |  |  | Meraj Husain Idd Baksh | 10/22/2025 04:38:38 | 10/22/2025 08:20:46 | 10/22/2025 16:38:38 | RF Unit CPRI Interface Error at DAM6027-DCU1 @ Sceco | 10/22/2025 04:32:00 | Minor | 26504 | RF Unit CPRI Interface Error | 10/22/2025 04:31:30 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM6027 | FLM_TE | [8 empty] | API | 10/22/2025 04:38:38 | 10/22/2025 08:20:46 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000156 | PCM-20251022-00000400 | TT-20251022-00463 | Reference_telecom | Region_4 | JED2176 | JED2176 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 04:39:39 | 10/22/2025 15:45:13 | 10/22/2025 16:39:39 | Degrade observed in JED2176 towards 10.10.183.66 @ Sceco | 10/21/2025 16:39:16 | Minor |  | Degrade | 10/21/2025 16:39:11 | P3 | 2G | jeddah | Sceco | TX NSA | JED2176 | FLM_TE | [8 empty] | API | 10/22/2025 04:39:39 | 10/22/2025 15:45:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000158 | PCM-20251022-00000403 | TT-20251022-00468 | Telecom | Region_4 | JED-SR-01 | JD1 |  |  |  | Muhammad Mustaqeem Irshad Ali | 10/22/2025 04:40:43 | 10/22/2025 04:40:43 | 10/22/2025 16:40:43 | Chassis Fail at JED-SR-01 @ Sceco_STB | 10/22/2025 04:40:17 | Minor | 101-2505202 | Chassis Fail | 10/22/2025 04:40:13 | P1 | IPBB | jeddah | Sceco_STB | IPRAN NSA | JED-SR-01 | FLM_TE | [8 empty] | API | 10/22/2025 04:40:43 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000159 | PCM-20251022-00000406 | TT-20251022-00470 | EM | Region_3 | YBDB2292 | YBDB2292 | Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue | Eid Fawzi Sayed Ali | 10/22/2025 04:41:15 | 10/22/2025 12:34:53 | 10/22/2025 10:41:15 | Generator failure at YBDB2292-P1-HUB_SRAN @ Generator_DG | 10/22/2025 04:36:29 | Major | 65114 | Generator failure | 10/22/2025 04:30:46 | P1 | SRAN | tabouk | Generator_DG | 2G NSA | YBDB2292 | FLM_EM | [8 empty] | API | 10/22/2025 04:41:15 | 10/22/2025 04:56:50 | 10/22/2025 10:53:57 | 10/22/2025 11:37:28 | 10/22/2025 11:39:24 | 10/22/2025 12:34:53 |  | Eid Fawzi Sayed Ali |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000161 | PCM-20251022-00000411 | TT-20251022-00474 | Reference_telecom | Region_4 | JED0245 | JED0245 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 04:47:23 | 10/22/2025 15:45:14 | 10/22/2025 16:47:23 | LagPortDown observed in JED0245_13 towards 10.10.183.65 @ Sceco | 10/21/2025 16:48:35 | Minor |  | LagPortDown | 10/21/2025 16:47:17 | P1 | 2G | jeddah | Sceco | TX NSA | JED0245 | FLM_TE | [8 empty] | API | 10/22/2025 04:47:23 | 10/22/2025 15:45:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000164 | PCM-20251022-00000418 | TT-20251022-00486 | Reference_telecom | Region_6 | ARF0315 | ARF0315 |  |  |  | Muhammad shafiq Muhammad Rasheed | 10/22/2025 04:54:06 | 10/22/2025 10:43:42 | 10/22/2025 16:54:06 | ReplaceableUnitProblem observed in ARF0315 towards 10.1.232.166 @ Sceco | 10/21/2025 16:53:56 | Minor |  | ReplaceableUnitProblem | 10/21/2025 16:53:34 | P3 | 2G | khamis mushyet | Sceco | TX NSA | ARF0315 | FLM_TE | [8 empty] | API | 10/22/2025 04:54:06 | 10/22/2025 10:43:42 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000168 | PCM-20251022-00000426 | TT-20251022-00475 | Telecom | Region_3 | YBDB0979 | YBDB0979 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Hossam Ali Ahmed Ali | 10/22/2025 04:59:18 | 10/22/2025 18:44:47 | 10/22/2025 08:59:18 | 3(3G) 2(LTE) sites down under YBDB0978-P1-SHOP-HUB,AWJ0064-P2,AWJ0138-P2/YB1MBSCH01 @ Sceco | 10/22/2025 04:44:19 | Critical | 22214 | NodeB Unavailable | 10/22/2025 04:44:13 | P3 | SRAN | tabouk | Sceco | 3G SA | AWJ0138-P2 3G,YBDB0978-P1-SHOP-HUB 3G,AWJ0064-P2 3G | FLM_TE | YBDB0979 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YBDB0297 DIR YBDB0979,Kindly visit the link and perform the HC at mentioned link . | PCM-20251022-00000417 | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YBDB0297 DIR YBDB0979,Kindly visit the link and perform the HC at mentioned link . | Dear FLM TE Team , We are observing PM Error and RSL degradation at link : YBDB0297 DIR YBDB0979,Kindly visit the link and perform the HC at mentioned link . |  | sites down |  | API | 10/22/2025 04:59:18 | 10/22/2025 07:52:27 | 10/22/2025 18:44:28 |  |  | 10/22/2025 18:44:47 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000171 | PCM-20251022-00000431 | TT-20251022-00499 | Telecom | Region_5 | MAK1MN0320 | MAK0320 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 05:04:58 | 10/22/2025 05:04:58 | 10/22/2025 09:04:58 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 10/22/2025 05:04:16 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 05:04:05 | VIP | 5G | makkah | Sceco | 5G_Cell SA | MAK1MN0320 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 05:04:58 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000179 | PCM-20251022-00000464 | TT-20251022-00538 | Telecom | Region_5 | MAK1MN0320 | MAK0320 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 05:17:53 | 10/22/2025 05:17:53 | 10/22/2025 17:17:53 | BASE STATION INFORMATION (No module fan detected) at MAK1MN0320-NR2.6-P1-VIP-HAJJ @ Sceco | 10/22/2025 05:09:36 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 05:09:26 | VIP | 5G | makkah | Sceco | 5G NSA | MAK1MN0320 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/22/2025 05:17:53 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000181 | PCM-20251022-00000467 | TT-20251022-00539 | Telecom | Region_1 | DAM6012 | DAM6012 |  |  |  | Meraj Husain Idd Baksh | 10/22/2025 05:18:55 | 10/22/2025 08:20:47 | 10/22/2025 17:18:55 | DCU Optical Module Transmit/Receive Fault at DAM6012-DCU3 @ Sceco | 10/22/2025 05:06:17 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/22/2025 05:11:50 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM6012 | FLM_TE | [8 empty] | API | 10/22/2025 05:18:55 | 10/22/2025 08:20:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000182 | PCM-20251022-00000470 | TT-20251022-00544 | Reference_EM | Region_1 | RAF2581 | RAF2581 | Enviroment | Rectifier Module | Adding module due to load issue | Emad Mahmoud Ahmed Mohamed | 10/22/2025 05:23:04 | 10/22/2025 18:03:44 | 10/22/2025 11:23:04 | low fuel alarm at RAF2581-P1-USF-HUB_SRAN @ Generator_DG | 10/22/2025 05:12:47 | Major | 65115 | low fuel alarm | 10/22/2025 05:12:45 | P1 | SRAN | hafr | Generator_DG | 2G NSA | RAF2581 | FLM_EM | [8 empty] | API | 10/22/2025 05:23:04 | 10/22/2025 05:37:01 | 10/22/2025 18:03:30 |  |  | 10/22/2025 18:03:44 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000183 | PCM-20251022-00000484 | TT-20251022-00565 | Telecom | Region_4 | JED0935 | JED0935 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 05:38:03 | 10/22/2025 05:49:19 | 10/22/2025 17:38:03 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0935-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Generator_SG | 10/22/2025 05:37:03 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 05:36:56 | P2 | 2G | jeddah | Generator_SG | 5G_Cell SA | JED0935 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 05:38:03 | 10/22/2025 05:49:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000184 | PCM-20251022-00000485 | TT-20251022-00567 | Reference_telecom | Region_2 | RIYA6056 | RIYA6056 |  |  |  | Ali Raza Abdi Syed Muhammad Taqi Abdi | 10/22/2025 05:39:04 | 10/22/2025 08:23:04 | 10/22/2025 11:39:04 | RF Unit VSWR Threshold Crossed at RIYA6056-DCU1 @ Sceco | 10/22/2025 02:37:32 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/22/2025 02:38:39 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6056 | FLM_TE | [8 empty] | API | 10/22/2025 05:39:04 | 10/22/2025 08:23:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000185 | PCM-20251022-00000486 | TT-20251022-00568 | EM | Region_3 | MDN2564 | MDN2564 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/22/2025 05:41:07 | 10/22/2025 05:41:07 | 10/22/2025 17:41:07 | NETECO: Insufficient Redundant Rectifiers at MDN2564 @ Generator_DG | 10/22/2025 05:34:54 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/22/2025 05:34:54 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDN2564 | FLM_EM | [8 empty] | API | 10/22/2025 05:41:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000190 | PCM-20251022-00000495 | TT-20251022-00574 | EM | Region_3 | RUSF9024 | RUSF9024 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/22/2025 05:46:19 | 10/22/2025 23:38:27 | 10/22/2025 09:46:19 | RELAY_ALARM_MAJOR at RUSF9024_NE_1 @ Generator_DG | 10/22/2025 05:44:34 | Critical | 1-12306 | RELAY_ALARM_MAJOR | 10/22/2025 05:44:23 | P3 | Repeater | madinah | Generator_DG | TX NSA | RUSF9024 | FLM_EM | [8 empty] | API | 10/22/2025 05:46:19 | 10/22/2025 23:38:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251022000191 | PCM-20251022-00000496 | TT-20251022-00575 | Telecom | Region_1 | JBKH2M3603 | JBKH0603 |  |  |  | Meraj Husain Idd Baksh | 10/22/2025 05:46:19 | 10/22/2025 18:43:35 | 10/22/2025 17:46:19 | RF Unit Maintenance Link Failure at JBKH2M3603-P2 @ Sceco | 10/22/2025 05:42:40 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 05:40:57 | P2 | 3G | dammam | Sceco | 2G NSA | JBKH2M3603 | FLM_TE | [8 empty] | API | 10/22/2025 05:46:19 | 10/22/2025 08:20:47 | 10/22/2025 18:43:35 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000192 | PCM-20251022-00000497 | TT-20251022-00576 | Telecom | Region_2 | RIY0406 | RIY0406 | Equipment | BSS_HW_fault | Replace RFU | Farmanullah Akbar Jan | 10/22/2025 05:46:19 | 10/22/2025 09:45:52 | 10/22/2025 17:46:19 | RF Unit Maintenance Link Failure at RIY0406-P2_SRAN @ Sceco | 10/22/2025 05:41:04 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 05:40:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0406 | FLM_TE | [8 empty] | API | 10/22/2025 05:46:19 | 10/22/2025 09:04:45 | 10/22/2025 09:44:47 | 10/22/2025 09:44:51 | 10/22/2025 09:44:54 | 10/22/2025 09:45:52 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000194 | PCM-20251022-00000500 | TT-20251022-00580 | Reference_EM | Region_2 | RIYB2U6173a | RIYB6073 |  |  |  | Kadri Jalal Mohammed Asmail | 10/22/2025 05:50:57 | 10/23/2025 03:06:47 | 10/22/2025 11:50:57 | Major Rec. alarm at RIYB2U6173A-P1-DIA-SHOP @ Sceco | 10/22/2025 05:40:35 | Major | 65107 | Major Rec. alarm | 10/22/2025 05:40:31 | P1 | 2G | riyadh | Sceco | 2G NSA | RIYB2U6173A | FLM_EM | [8 empty] | API | 10/22/2025 05:50:57 | 10/23/2025 03:06:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000195 | PCM-20251022-00000501 | TT-20251022-00581 | EM | Region_4 | JED2050 | JED2050 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/22/2025 05:51:29 | 10/22/2025 20:21:09 | 10/22/2025 17:51:29 | AIRCON 1 FAILURE at JED2050-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/22/2025 05:43:22 | Minor | 7103 | AIRCON 1 FAILURE | 10/22/2025 05:43:13 | P2 | 2G | jeddah | Sceco | 2G NSA | JED2050 | FLM_EM | [5 empty] | AIRCON 1 FAILURE |  |  | API | 10/22/2025 05:51:29 | 10/22/2025 20:21:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000196 | PCM-20251022-00000503 | TT-20251022-00584 | EM | Region_1 | KFKM0784 | KFKM0784 |  |  |  | Rahman Ullah Said Halim | 10/22/2025 05:55:04 | 10/23/2025 15:22:17 | 10/22/2025 17:55:04 | NETECO: Door Status Sensor Alarm at KFKM0784 @ Generator_SG | 10/22/2025 05:54:39 | Minor | 5152 | Door Status Sensor Alarm | 10/22/2025 05:54:39 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0784 | FLM_EM | [8 empty] | API | 10/22/2025 05:55:04 | 10/23/2025 15:22:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000197 | PCM-20251022-00000507 | TT-20251022-00578 | Telecom | Region_5 | MAK1M9254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 05:59:50 | 10/22/2025 05:59:50 | 10/22/2025 11:59:50 | BASE STATION ANTENNA LINE PROBLEM at MAK1M9254-P1-SHOP-CA-L800-SBTS @ Sceco | 10/22/2025 05:41:18 | Major | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/22/2025 05:41:09 | P1 | 4G | makkah | Sceco | LTE NSA | MAK1M9254 | FLM_TE |  |  | PCM-20251022-00000499 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/22/2025 05:59:50 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000198 | PCM-20251022-00000508 | TT-20251022-00557 | Reference_telecom | Region_4 | JED1M7667 | JED0667 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 06:00:14 | 10/22/2025 15:45:14 | 10/22/2025 12:00:14 | BASE STATION SERVICE PROBLEM (RF Power decreased) at JED1M7667-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/22/2025 01:33:29 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 01:33:24 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7667 | FLM_TE |  |  | PCM-20251022-00000479 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/22/2025 06:00:14 | 10/22/2025 15:45:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000199 | PCM-20251022-00000509 | TT-20251022-00036 | Telecom | Region_6 | BSH1M7085 | BSH0085 | Equipment | Jumper_Cable | Re-Tightened Outdoor Jumper cable Connector | Ansir Iqbal Muhammad Iqbal | 10/22/2025 06:00:43 | 10/22/2025 22:23:16 | 10/22/2025 12:00:43 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at BSH1M7085-G9-L8-L18-L21-SBTS-P1-HUB @ Sceco_STB | 10/22/2025 00:19:35 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 00:19:30 | P1 | 4G | baish | Sceco_STB | 5G_Cell SA | BSH1M7085 | FLM_TE |  |  | PCM-20251022-00000433 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/22/2025 06:00:43 | 10/22/2025 13:52:58 | 10/22/2025 15:02:29 | 10/22/2025 15:03:26 | 10/22/2025 17:57:19 | 10/22/2025 22:23:16 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000200 | PCM-20251022-00000511 | TT-20251022-00593 | Telecom | Region_1 | KBR0308 | KBR0308 |  |  |  | Imran Ali Yousaf | 10/22/2025 06:00:46 | 10/22/2025 12:30:19 | 10/22/2025 18:00:46 | RF Unit Maintenance Link Failure at KBR0308-P1-SHOP_SRAN @ Sceco | 10/22/2025 01:22:37 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 01:20:53 | P1 | SRAN | dammam | Sceco | 2G NSA | KBR0308 | FLM_TE | [8 empty] | API | 10/22/2025 06:00:46 | 10/22/2025 12:30:19 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000201 | PCM-20251022-00000510 | TT-20251022-00592 | Telecom | Region_2 | RIY0624 | RIY0624 |  |  |  | Farmanullah Akbar Jan | 10/22/2025 06:00:46 | 10/22/2025 07:47:52 | 10/22/2025 18:00:46 | RF Unit Maintenance Link Failure at RIY0624-P2_SRAN @ Sceco | 10/22/2025 01:22:37 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 01:20:53 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0624 | FLM_TE | [8 empty] | API | 10/22/2025 06:00:46 | 10/22/2025 07:47:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000204 | PCM-20251022-00000515 | TT-20251022-00597 | EM | Region_3 | AHT2211 | AHT2211 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/22/2025 06:02:19 | 10/22/2025 08:34:26 | 10/22/2025 18:02:19 | Mains Failure at AHT2211-P3_SRAN @ Sceco | 10/22/2025 05:52:21 | Minor | 65109 | Mains Failure | 10/22/2025 05:52:17 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2211 | FLM_EM | [8 empty] | API | 10/22/2025 06:02:19 | 10/22/2025 08:34:26 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000205 | PCM-20251022-00000516 | TT-20251022-00435 | Reference_telecom | Region_4 | TAF1M3287 | TAF0287 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 06:02:45 | 10/22/2025 17:30:04 | 10/22/2025 12:02:45 | RNW O&M SCENARIO FAILURE at TAF1M3287-P3 @ Sceco | 10/22/2025 03:55:56 | Major | 7761 | RNW O&M SCENARIO FAILURE | 10/22/2025 03:55:02 | P3 | 3G | taif | Sceco | 3G NSA | TAF1M3287 | FLM_TE |  |  | PCM-20251022-00000381 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/22/2025 06:02:45 | 10/22/2025 17:30:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000206 | PCM-20251022-00000517 | TT-20251022-00587 | Telecom | Region_5 | HRT1M7139 | HRT0139 |  |  |  | Muhammad Shabbir Muhammad | 10/22/2025 06:03:33 | 10/22/2025 06:03:33 | 10/22/2025 12:03:33 | 1(LTE) sites down under HRT0139-G9-NL8-L9-SBTS-P2-USF @ Generator_SG | 10/22/2025 05:55:20 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 05:55:18 | P2 | 4G | makkah | Generator_SG | LTE SA | HRT0139-G9-NL8-L9-SBTS-P2-USF | FLM_TE | HRT0139 | Results: DOWN SITE HUB HRT0139-G9-NL8-L9-SBTS-P2-USF HRT0139 Summary: Hub: HRT0139, Down Count: 1, Down Sites: HRT0139-G9-NL8-L9-SBTS-P2-USF Alarm Summary: HRT0139 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.63.196:8080] [URL:http://10.88.63.196:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 06:03:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000211 | PCM-20251022-00000530 | TT-20251022-00606 | EM | Region_6 | QLW1M8370 | QLW2370 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 06:11:06 | 10/22/2025 08:52:00 | 10/22/2025 18:11:06 | SHELTER DOOR OPEN at QLW1M8370-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/22/2025 06:10:30 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 06:10:20 | P3 | 4G | Baha | Generator_SG | LTE NSA | QLW1M8370 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 06:11:06 | 10/22/2025 08:52:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000215 | PCM-20251022-00000538 | TT-20251022-00610 | Telecom | Region_4 | SJED1S7018 | SJED0018 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 06:18:02 | 10/22/2025 15:45:14 | 10/22/2025 10:18:02 | 1(LTE) sites down under SJED0018-CA-P1-ARP-HAJJ-VIP @ Sceco | 10/22/2025 06:09:47 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 06:09:44 | VIP | 4G | jeddah | Sceco | LTE SA | SJED0018-CA-P1-ARP-HAJJ-VIP | FLM_TE | SJED0018 | Results: DOWN SITE HUB SJED0018-CA-P1-ARP-HAJJ-VIP SJED0018 Summary: Hub: SJED0018, Down Count: 1, Down Sites: SJED0018-CA-P1-ARP-HAJJ-VIP Alarm Summary: SJED0018 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.96.184.60:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 06:18:02 | 10/22/2025 15:45:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000216 | PCM-20251022-00000540 | TT-20251022-00573 | Telecom | Region_2 | RIY2M7406 | RIY0406 | Equipment | BSS_HW_fault | Replace RFU | Farmanullah Akbar Jan | 10/22/2025 06:18:25 | 10/22/2025 09:43:06 | 10/22/2025 12:18:25 | Cell Unavailable at RIY2M7406-P2-L800 @ Sceco | 10/22/2025 05:42:52 | Major | 29240 | Cell Unavailable | 10/22/2025 05:42:19 | P2 | 4G | riyadh | Sceco | LTE SA | RIY2M7406 | FLM_TE |  |  | PCM-20251022-00000520 | Approved as per FLM TS. HW:- MRFU Item # 02310CEU | Approved as per FLM TS. HW:- MRFU Item # 02310CEU |  |  |  | API | 10/22/2025 06:18:25 | 10/22/2025 08:33:47 | 10/22/2025 09:04:49 | 10/22/2025 09:04:54 | 10/22/2025 09:10:04 | 10/22/2025 09:43:06 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000217 | PCM-20251022-00000542 | TT-20251022-00397 | Telecom | Region_4 | JED1M7056 | JED0056 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 06:21:12 | 10/22/2025 12:55:59 | 10/22/2025 12:21:12 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at JED1M7056-P3-CA-L800 @ Sceco | 10/22/2025 03:58:33 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 04:20:47 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M7056 | FLM_TE |  |  | PCM-20251022-00000357 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/22/2025 06:21:12 | 10/22/2025 12:55:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000218 | PCM-20251022-00000543 | TT-20251022-00534 | EM | Region_3 | YNA0509 | YNA0509 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 06:22:30 | 10/22/2025 17:29:15 | 10/22/2025 12:22:30 | 1(2G/3G/LTE) sites down under YNA0509-P3/YB1MBSCH01 @ Sceco | 10/22/2025 05:14:15 | Major | 21825 | CSL Fault | 10/22/2025 05:14:13 | P3 | SRAN | yanbu | Sceco | 2G_3G SA | YNA0509-P3 | FLM_TE | YNA0509 | Results: DOWN SITE HUB YNA0509-P3 YNA0509 Summary: Hub: YNA0509, Down Count: 1, Down Sites: YNA0509-P3 Alarm Summary: YNA0509 Alarm Active on HUB | PCM-20251022-00000469 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 06:22:30 | 10/22/2025 17:27:01 | 10/22/2025 17:29:07 |  |  | 10/22/2025 17:29:15 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000221 | PCM-20251022-00000546 | TT-20251022-00617 | EM | Region_4 | KAC1M7461 | KAC0461 |  |  |  | Rami Mohamed Abubakr Ibrahim | 10/22/2025 06:24:34 | 10/23/2025 12:26:37 | 10/22/2025 12:24:34 | 1(LTE/5G) sites down under KAC0461-GSM-P2 @ Generator_SG | 10/22/2025 06:16:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 06:16:09 | P2 | 4G | jeddah | Generator_SG | LTE_5G SA | KAC0461-GSM-P2 | FLM_EM | KAC0461 | Results: DOWN SITE HUB KAC0461-GSM-P2 KAC0461 Summary: Hub: KAC0461, Down Count: 1, Down Sites: KAC0461-GSM-P2 Alarm Summary: KAC0461 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.96.144.164:8080] [URL:http://10.96.144.164:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 06:24:34 | 10/23/2025 12:26:37 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000223 | PCM-20251022-00000550 | TT-20251022-00622 | Telecom | Region_1 | JBL2131 | JBL2131 | Equipment | BSS_HW_fault | Replace System Module | Tahir Mahmood Hafiz Yar | 10/22/2025 06:25:57 | 10/22/2025 13:27:26 | 10/22/2025 18:25:57 | RF Unit CPRI Interface Error at JBL2131-P1_SRAN @ Generator_SG | 10/22/2025 04:47:04 | Minor | 26504 | RF Unit CPRI Interface Error | 10/22/2025 04:45:30 | P1 | SRAN | jubail | Generator_SG | 2G NSA | JBL2131 | FLM_TE | [8 empty] | API | 10/22/2025 06:25:57 | 10/22/2025 09:14:51 | 10/22/2025 12:45:26 | 10/22/2025 12:45:29 | 10/22/2025 12:58:54 | 10/22/2025 13:27:26 |  | Tahir Mahmood Hafiz Yar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000224 | PCM-20251022-00000551 | TT-20251022-00623 | Telecom | Region_2 | RYDM0655 | RYDM0655 | Equipment | BSS_HW_Stuck | Reset ALD | Waseem Shahzad Ghulam Rasool | 10/22/2025 06:26:21 | 10/22/2025 15:58:31 | 10/22/2025 18:26:21 | ALD Maintenance Link Failure at RYDM0655-P2_SRAN @ Generator_SG | 10/22/2025 04:36:41 | Minor | 26541 | ALD Maintenance Link Failure | 10/22/2025 04:28:25 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RYDM0655 | FLM_TE | [8 empty] | API | 10/22/2025 06:26:21 | 10/22/2025 11:54:55 | 10/22/2025 12:36:24 | 10/22/2025 12:36:26 | 10/22/2025 14:20:37 | 10/22/2025 15:58:31 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000225 | PCM-20251022-00000552 | TT-20251022-00406 | Reference_telecom | Region_6 | BLC2171 | BLC2171 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/22/2025 06:26:41 | 10/23/2025 16:22:50 | 10/22/2025 18:26:41 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at BLC2171-G9-L18-NNR2.6-SBTS-P3 @ Sceco | 10/22/2025 02:06:45 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 02:05:29 | P3 | 2G | Albaha | Sceco | 2G NSA | BLC2171 | FLM_TE |  |  | PCM-20251022-00000365 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/22/2025 06:26:41 | 10/22/2025 14:04:44 | 10/23/2025 16:22:35 |  |  | 10/23/2025 16:22:50 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000226 | PCM-20251022-00000553 | TT-20251022-00624 | Telecom | Region_2 | RIY0624 | RIY0624 |  |  |  | Farmanullah Akbar Jan | 10/22/2025 06:26:46 | 10/22/2025 07:47:52 | 10/22/2025 12:26:46 | BBU CPRI Optical Module or Electrical Port Not Ready at RIY0624-P2_SRAN @ Sceco | 10/22/2025 01:42:02 | Major | 26231 | BBU CPRI Optical Module or Electrical Port Not Ready | 10/22/2025 01:40:30 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0624 | FLM_TE | [8 empty] | API | 10/22/2025 06:26:46 | 10/22/2025 07:47:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000228 | PCM-20251022-00000556 | TT-20251022-00627 | Telecom | Region_4 | JED6008 | JED6008 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 06:27:07 | 10/22/2025 15:48:00 | 10/22/2025 18:27:07 | Cell Capability Degraded at JED6008-DCU-P3 @ Sceco | 10/21/2025 19:58:41 | Minor | 28751 | Cell Capability Degraded | 10/21/2025 19:57:08 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6008 | FLM_TE | [8 empty] | API | 10/22/2025 06:27:07 | 10/22/2025 15:48:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000230 | PCM-20251022-00000559 | TT-20251021-02528 | Telecom | Region_4 | JED1M8139 | JED2139 | Equipment | BSS_HW_fault | Replace System Module | Khaled Mohammad Abdallah | 10/22/2025 06:28:56 | 10/24/2025 06:49:16 | 10/22/2025 18:28:56 | PT::FLM need to check BASE STATION INFORMATION (Increased BER detected on the optical connector) at JED1M8139-CA-L1800-L800-FWA-P1-VIP | 10/21/2025 22:39:29 | Minor | 7115 | BASE STATION INFORMATION | 10/21/2025 22:39:29 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | JED1M8139-CA-L1800-L800-FWA-P1-VIP | FLM_TE |  |  | PCM-20251022-00000541 | Please close TT with rectification RC. | Please close TT with rectification RC. |  |  |  | API | 10/22/2025 06:28:56 |  | 10/22/2025 07:54:58 | 10/22/2025 07:55:00 | 10/22/2025 07:55:02 | 10/24/2025 06:49:16 |  | Khaled Mohammad Abdallah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000231 | PCM-20251022-00000560 | TT-20251022-00594 | Telecom | Region_2 | RIY0340 | RIY0340 |  |  |  | Farmanullah Akbar Jan | 10/22/2025 06:29:14 | 10/22/2025 07:47:53 | 10/22/2025 18:29:14 | Board Not In Position at RIY0340-P1-SHOP-HUB-VIP_SRAN-FON @ Sceco | 10/22/2025 01:58:38 | Minor | 26204 | Board Not In Position | 10/22/2025 01:57:04 | VIP | SRAN | riyadh | Sceco | 2G NSA | RIY0340 | FLM_TE |  |  | PCM-20251022-00000512 | Dear FLM, Kindly check locally | Dear FLM, Kindly check locally |  |  |  | API | 10/22/2025 06:29:14 | 10/22/2025 07:47:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000233 | PCM-20251022-00000564 | TT-20251022-00620 | EM | Region_4 | JED1M8131 | JED2131 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 06:30:31 | 10/22/2025 23:16:33 | 10/22/2025 12:30:31 | 1(LTE/5G) sites down under JED2131-NR2.6-P2 @ Sceco | 10/22/2025 06:22:16 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 06:22:14 | P2 | 4G | jeddah | Sceco | LTE SA | JED2131-L800-CA-SBTS-P2 | FLM_TE | JED2131 | Results: DOWN SITE HUB JED2131-L800-CA-SBTS-P2 JED2131 Summary: Hub: JED2131, Down Count: 1, Down Sites: JED2131-L800-CA-SBTS-P2 Alarm Summary: JED2131 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.88.249.92:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 06:30:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000234 | PCM-20251022-00000565 | TT-20251022-00628 | Telecom | Region_3 | YBYN0305 | YBYN0305 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 06:32:33 | 10/22/2025 17:28:58 | 10/22/2025 12:32:33 | 1(LTE) sites down under YBYN0305-P3_SRAN @ Generator_SG | 10/22/2025 06:24:23 | Major | 301 | NE Is Disconnected | 10/22/2025 06:24:21 | P3 | SRAN | yanbu | Generator_SG | LTE SA | YBYN0305-P3_SRAN | FLM_TE | YBYN0305 | Results: DOWN SITE HUB YBYN0305-P3_SRAN YBYN0305 Summary: Hub: YBYN0305, Down Count: 1, Down Sites: YBYN0305-P3_SRAN Alarm Summary: YBYN0305 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 06:32:33 | 10/22/2025 17:27:01 | 10/22/2025 17:28:51 |  |  | 10/22/2025 17:28:58 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000236 | PCM-20251022-00000570 | TT-20251022-00075 | Telecom | Region_4 | JED1MN0135 | JED0135 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 06:39:02 | 10/22/2025 10:09:09 | 10/22/2025 12:39:02 | BASE STATION CONNECTIVITY PROBLEM (NG SCTP endpoint broken) at JED1MN0135-NR2.6-P3 @ Sceco | 10/22/2025 00:34:38 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 00:34:32 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0135 | FLM_TE |  |  | PCM-20251022-00000070 | LMP access on found during alarm time, Please close TT with rectification RC. | LMP access on found during alarm time, Please close TT with rectification RC. |  |  |  | API | 10/22/2025 06:39:02 | 10/22/2025 10:09:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000238 | PCM-20251022-00000576 | TT-20251022-00652 | Reference_telecom | Region_4 | TAF2349 | TAF2349 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 06:42:36 | 10/23/2025 07:25:59 | 10/22/2025 18:42:36 | ReplaceableUnitMissing observed in TAF2349 towards 10.10.190.163 @ Sceco | 10/21/2025 18:42:15 | Minor |  | ReplaceableUnitMissing | 10/21/2025 18:42:09 | P2 | 2G | taif | Sceco | TX NSA | TAF2349 | FLM_TE | [8 empty] | API | 10/22/2025 06:42:36 | 10/23/2025 07:25:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000239 | PCM-20251022-00000579 | TT-20251022-00346 | Reference_telecom | Region_6 | ZHR1M7136 | ZHR0136 | Transsmission | MW_Problematic | Interference Issue | Bilal Anwar Khurshid Anwar | 10/22/2025 06:43:29 | 10/22/2025 16:42:13 | 10/22/2025 18:43:29 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at ZHR1M7136-G9-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 01:26:50 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 01:25:42 | P3 | 4G | al harja | Sceco | LTE NSA | ZHR1M7136 | FLM_TE |  |  | PCM-20251022-00000410 | Please close TT with restoration RC. | Please close TT with restoration RC. |  |  |  | API | 10/22/2025 06:43:29 | 10/22/2025 11:31:31 | 10/22/2025 16:41:48 |  |  | 10/22/2025 16:42:13 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000240 | PCM-20251022-00000580 | TT-20251022-00625 | Telecom | Region_2 | RIY2543 | RIY2543 | Equipment | BSS_HW_Stuck | Reset Controller Card | Khan zeb Shah nawaz | 10/22/2025 06:43:44 | 10/22/2025 11:02:41 | 10/22/2025 12:43:44 | Board Software Auto-Supply Failure at RIY2543-P2_SRAN-PC @ Sceco | 10/21/2025 22:52:53 | Major | 26253 | Board Software Auto-Supply Failure | 10/21/2025 22:52:48 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2543 | FLM_TE |  |  | PCM-20251022-00000566 | Dear FLM, Kindly support to check locally and try to reset UMPT | Dear FLM, Kindly support to check locally and try to reset UMPT |  |  |  | API | 10/22/2025 06:43:44 | 10/22/2025 09:07:00 | 10/22/2025 09:19:59 | 10/22/2025 09:20:05 | 10/22/2025 10:25:51 | 10/22/2025 11:02:41 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000241 | PCM-20251022-00000587 | TT-20251022-00648 | Reference_telecom | Region_4 | HHR1M7448 | HHR0448 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 06:54:15 | 10/22/2025 10:09:10 | 10/22/2025 12:54:15 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at HHR1M7448-P1-VIP-HHR-L800-CA (Ref::TT-20251021-00334) @ Generator_SG | 10/22/2025 01:08:11 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 01:07:59 | VIP | 4G | jeddah | Generator_SG | 5G_Cell SA | HHR1M7448 | FLM_TE |  |  | PCM-20251022-00000572 | Please check ALD HW & all the connectivity from ALD To RMOD. | Please check ALD HW & all the connectivity from ALD To RMOD. |  |  |  | API | 10/22/2025 06:54:15 | 10/22/2025 10:09:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000242 | PCM-20251022-00000588 | TT-20251022-00645 | Telecom | Region_4 | JED0024 | JED0024 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 06:54:51 | 10/22/2025 12:56:00 | 10/22/2025 12:54:51 | BASE STATION HARDWARE PROBLEM (RX Power too low) at JED0024-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA @ Sceco | 10/22/2025 06:31:58 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/22/2025 06:31:48 | P1 | 2G | jeddah | Sceco | 2G NSA | JED0024 | FLM_TE |  |  | PCM-20251022-00000569 | Please perform HC on SFP, Cable connectivity & HW. | Please perform HC on SFP, Cable connectivity & HW. |  |  |  | API | 10/22/2025 06:54:51 | 10/22/2025 12:56:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000243 | PCM-20251022-00000589 | TT-20251022-00659 | EM | Region_4 | JED0935 | JED0935 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 06:55:04 | 10/22/2025 16:43:31 | 10/22/2025 12:55:04 | 1(2G/5G) sites down under JED0935-P2 @ Generator_SG | 10/22/2025 06:46:41 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 06:46:39 | P2 | 2G | jeddah | Generator_SG | 5G SA | JED0935-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | JED0935 | Results: DOWN SITE HUB JED0935-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 JED0935 Summary: Hub: JED0935, Down Count: 1, Down Sites: JED0935-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 Alarm Summary: JED0935 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.96.244:8080] [URL:http://10.97.96.244:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 06:55:04 | 10/22/2025 08:16:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000244 | PCM-20251022-00000591 | TT-20251022-00671 | Telecom | Region_3 | YNB2953 | YNB2953 |  |  |  | Muhammad Sajjad R3 | 10/22/2025 06:57:40 | 10/22/2025 17:27:02 | 10/22/2025 18:57:40 | GNSS Clock Output Unavailable at YNB2953-P2_SRAN @ Sceco | 10/21/2025 23:52:17 | Minor | 26124 | GNSS Clock Output Unavailable | 10/21/2025 23:50:43 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB2953 | FLM_TE | [8 empty] | API | 10/22/2025 06:57:40 | 10/22/2025 17:27:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000246 | PCM-20251022-00000594 | TT-20251022-00673 | Reference_telecom | Region_3 | MDYB0641 | MDYB0641 |  |  |  | Muhammad Sajjad R3 | 10/22/2025 06:58:29 | 10/22/2025 17:27:02 | 10/22/2025 18:58:29 | GNSS Locked Satellites Insufficient at MDYB0641-P1-HUB_SRAN @ Generator_DG | 10/21/2025 22:53:16 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/21/2025 22:49:52 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB0641 | FLM_TE | [8 empty] | API | 10/22/2025 06:58:29 | 10/22/2025 17:27:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000248 | PCM-20251022-00000596 | TT-20251022-00675 | Reference_telecom | Region_3 | YNB0167 | YNB0167 |  |  |  | Muhammad Sajjad R3 | 10/22/2025 06:58:41 | 10/22/2025 17:27:03 | 10/22/2025 18:58:41 | GNSS Locked Satellites Insufficient at YNB0167-P2_SRAN @ Sceco | 10/21/2025 23:12:23 | Minor | 26126 | GNSS Locked Satellites Insufficient | 10/21/2025 23:10:09 | P2 | SRAN | yanbu | Sceco | 2G NSA | YNB0167 | FLM_TE | [8 empty] | API | 10/22/2025 06:58:41 | 10/22/2025 17:27:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000251 | PCM-20251022-00000603 | TT-20251022-00680 | Reference_telecom | Region_2 | BUR0050 | BUR0050 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Muhammad Naeem Muhammad Gulzar | 10/22/2025 07:00:11 | 10/24/2025 00:05:42 | 10/22/2025 19:00:11 | POWER_ABNORMAL at BUR0050_NE_7_FON @ Sceco | 10/22/2025 05:30:12 | Minor | 1-412 | POWER_ABNORMAL | 10/22/2025 05:30:05 | P2 | SRAN | buraidah | Sceco | TX NSA | BUR0050 | FLM_TE | [8 empty] | API | 10/22/2025 07:00:11 | 10/22/2025 13:37:51 | 10/23/2025 23:24:23 | 10/23/2025 23:24:26 | 10/23/2025 23:40:09 | 10/24/2025 00:05:42 |  | Muhammad Naeem Muhammad Gulzar |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000259 | PCM-20251022-00000648 | TT-20251022-00723 | EM | Region_5 | MAK1M9992 | MAK0992 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 07:15:03 | 10/22/2025 13:28:31 | 10/22/2025 11:15:03 | 1(LTE/5G) sites down under MAK0992-NR2.6-VIP @ Sceco | 10/22/2025 07:06:35 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 07:06:32 | VIP | 4G | makkah | Sceco | LTE SA | MAK0992-P1-VIP-HRM-CA-L800-SBTS | FLM_TE | MAK0992 | Results: DOWN SITE HUB MAK0992-P1-VIP-HRM-CA-L800-SBTS MAK0992 Summary: Hub: MAK0992, Down Count: 1, Down Sites: MAK0992-P1-VIP-HRM-CA-L800-SBTS Alarm Summary: MAK0992 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.99.40.148:8080] [URL:http://10.99.40.148:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 07:15:03 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000260 | PCM-20251022-00000650 | TT-20251022-00730 | Reference_EM | Region_1 | SMN0802 | SMN0802 | Enviroment | SCECO_Failure | SCECO auto restored | Shaker Saied Mohamed ElShafie | 10/22/2025 07:16:43 | 10/22/2025 09:27:16 | 10/22/2025 19:16:43 | Minor Rec alarm at SMN0802-P2_SRAN @ Generator_SG | 10/22/2025 07:06:32 | Minor | 65108 | Minor Rec alarm | 10/22/2025 07:06:29 | P2 | SRAN | hafr | Generator_SG | 2G NSA | SMN0802 | FLM_EM | [8 empty] | API | 10/22/2025 07:16:43 | 10/22/2025 09:01:35 | 10/22/2025 09:25:23 | 10/22/2025 09:26:50 | 10/22/2025 09:26:53 | 10/22/2025 09:27:16 |  | Shaker Saied Mohamed ElShafie |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000261 | PCM-20251022-00000652 | TT-20251022-00717 | EM | Region_3 | YBDB0282 | YBDB0282 | Transsmission | MW_SW | Remote action done by BO for MW configuration | Muhammad Sajjad R3 | 10/22/2025 07:19:40 | 10/22/2025 17:28:28 | 10/22/2025 11:19:40 | 1(3G/LTE) sites down under YBDB0282-P1-HUB/YB1MBSCH01 @ Generator_DG | 10/22/2025 07:04:13 | Critical | 22214 | NodeB Unavailable | 10/22/2025 07:04:10 | P1 | SRAN | yanbu | Generator_DG | 3G_LTE SA | YBDB0282-P1-HUB | FLM_TE | YBDB0282 | Results: DOWN SITE HUB YBDB0282-P1-HUB YBDB0282 Summary: Hub: YBDB0282, Down Count: 1, Down Sites: YBDB0282-P1-HUB Alarm Summary: YBDB0282 No Active Alarm on HUB | PCM-20251022-00000645 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 07:19:40 | 10/22/2025 17:27:03 | 10/22/2025 17:28:17 |  |  | 10/22/2025 17:28:28 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000262 | PCM-20251022-00000654 | TT-20251022-00677 | Reference_telecom | Region_3 | MDYB0410 | MDYB0410 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 07:23:56 | 10/23/2025 19:27:56 | 10/22/2025 19:23:56 | IP Link Performance Measurement Fault at MDYB0410-P1-HUB_SRAN @ Generator_DG | 10/22/2025 02:21:05 | Minor | 25904 | IP Link Performance Measurement Fault | 10/22/2025 02:20:32 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB0410 | FLM_TE |  |  | PCM-20251022-00000599 | PM Errors and RSL degradation observed on MW link YNB0292 <> YNB0659 | PM Errors and RSL degradation observed on MW link YNB0292 <> YNB0659 |  |  |  | API | 10/22/2025 07:23:56 | 10/22/2025 17:27:04 | 10/23/2025 19:27:49 |  |  | 10/23/2025 19:27:56 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000263 | PCM-20251022-00000655 | TT-20251022-00679 | Reference_telecom | Region_3 | MDYB0409 | MDYB0409 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 07:24:09 | 10/23/2025 19:27:43 | 10/22/2025 19:24:09 | IP Link Performance Measurement Fault at MDYB0409-P1-HUB_SRAN @ Generator_DG | 10/22/2025 02:51:25 | Minor | 25904 | IP Link Performance Measurement Fault | 10/22/2025 02:50:50 | P1 | SRAN | yanbu | Generator_DG | 2G NSA | MDYB0409 | FLM_TE |  |  | PCM-20251022-00000602 | PM Errors and RSL degradation observed on MW link YNB0292 <> YNB0659 | PM Errors and RSL degradation observed on MW link YNB0292 <> YNB0659 |  |  |  | API | 10/22/2025 07:24:09 | 10/22/2025 17:27:04 | 10/23/2025 19:27:36 |  |  | 10/23/2025 19:27:43 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000264 | PCM-20251022-00000657 | TT-20251022-00682 | Reference_telecom | Region_3 | BDJD0666 | BDJD0666 | Transsmission | MW_Problematic | Fading Issue | Muhammad Sajjad R3 | 10/22/2025 07:24:23 | 10/23/2025 19:27:30 | 10/22/2025 19:24:23 | IP Link Performance Measurement Fault at BDJD0666-P2_SRAN @ Generator_SG | 10/22/2025 02:51:33 | Minor | 25904 | IP Link Performance Measurement Fault | 10/22/2025 02:50:59 | P2 | SRAN | yanbu | Generator_SG | 2G NSA | BDJD0666 | FLM_TE |  |  | PCM-20251022-00000606 | PM Errors and RSL degradation observed on MW link YNB0292 <> YNB0659 | PM Errors and RSL degradation observed on MW link YNB0292 <> YNB0659 |  |  |  | API | 10/22/2025 07:24:23 | 10/22/2025 17:27:05 | 10/23/2025 19:27:18 |  |  | 10/23/2025 19:27:30 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000265 | PCM-20251022-00000658 | TT-20251022-00738 | EM | Region_1 | HFF2365 | HFF2365 |  |  |  | Moustafa Mohamed Saleh Saif | 10/22/2025 07:26:32 | 10/23/2025 01:46:24 | 10/22/2025 19:26:32 | Door opening alarm at HFF2365-P2_SRAN @ Sceco | 10/22/2025 07:26:03 | Minor | 65101 | Door opening alarm | 10/22/2025 07:18:19 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2365 | FLM_EM | [8 empty] | API | 10/22/2025 07:26:32 | 10/23/2025 01:46:24 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000266 | PCM-20251022-00000660 | TT-20251022-00741 | Telecom | Region_4 | JED1M7029 | JED0029 | Equipment | SFP_BTS | Replace SFP | Mohammed Ramadan A Abu Abid | 10/22/2025 07:28:05 | 10/23/2025 08:54:20 | 10/22/2025 13:28:05 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7029-CA-L900-L800-SBTS @ Sceco | 10/22/2025 07:27:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 07:27:12 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7029 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 07:28:05 |  | 10/22/2025 12:13:16 | 10/22/2025 12:13:48 | 10/22/2025 12:49:05 | 10/23/2025 08:54:20 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000267 | PCM-20251022-00000661 | TT-20251022-00742 | EM | Region_1 | HFF2365 | HFF2365 |  |  |  | Moustafa Mohamed Saleh Saif | 10/22/2025 07:28:35 | 10/23/2025 01:46:25 | 10/22/2025 19:28:35 | Air condition 1 failure alarm at HFF2365-P2_SRAN @ Sceco | 10/22/2025 07:26:03 | Minor | 65104 | Air condition 1 failure alarm | 10/22/2025 07:18:19 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF2365 | FLM_EM | [8 empty] | API | 10/22/2025 07:28:35 | 10/23/2025 01:46:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000268 | PCM-20251022-00000663 | TT-20251022-00734 | EM | Region_3 | MDN2U6113 | MDN6013 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Tasbeeh Ullah Muhammad Yousaf | 10/22/2025 07:29:04 | 10/22/2025 08:04:01 | 10/22/2025 11:29:04 | 1(2G/3G/LTE) sites down under MDN6013-P1-HRMCST/R3_MD_HWBSC02 @ Sceco | 10/22/2025 07:21:30 | Critical | 21825 | CSL Fault | 10/22/2025 07:21:27 | P1 | 2G | madinah | Sceco | 2G_3G_LTE SA | MDN6013-P1-HRMCST | FLM_EM | MDN6013 | Results: DOWN SITE HUB MDN6013-P1-HRMCST MDN6013 Summary: Hub: MDN6013, Down Count: 1, Down Sites: MDN6013-P1-HRMCST Alarm Summary: MDN6013 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 07:29:04 | 10/22/2025 08:03:38 | 10/22/2025 08:03:49 |  |  | 10/22/2025 08:04:01 |  | Tasbeeh Ullah Muhammad Yousaf |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000273 | PCM-20251022-00000668 | TT-20251022-00681 | Reference_telecom | Region_6 | JEC1M7088 | JEC0088 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/22/2025 07:30:28 | 10/22/2025 15:55:35 | 10/22/2025 19:30:28 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JEC1M7088-G9-L18-L21-SBTS-P2 @ Sceco_STB | 10/22/2025 05:00:45 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 04:59:52 | VIP | 4G | baish | Sceco_STB | LTE NSA | JEC1M7088 | FLM_TE |  |  | PCM-20251022-00000604 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 07:30:28 | 10/22/2025 13:52:59 | 10/22/2025 15:55:22 |  |  | 10/22/2025 15:55:35 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000275 | PCM-20251022-00000670 | TT-20251022-00737 | Telecom | Region_4 | SJED1S7741 | SJED0741 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 07:30:37 | 10/22/2025 08:16:17 | 10/22/2025 13:30:37 | 1(LTE) sites down under SJED0741-CA-P3 @ Sceco | 10/22/2025 07:22:13 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 07:22:09 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0741-CA-P3 | FLM_TE | SJED0741 | Results: DOWN SITE HUB SJED0741-CA-P3 SJED0741 Summary: Hub: SJED0741, Down Count: 1, Down Sites: SJED0741-CA-P3 Alarm Summary: SJED0741 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.99.221.84:8080] [URL:http://10.99.221.84:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 07:30:37 | 10/22/2025 08:16:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000276 | PCM-20251022-00000671 | TT-20251022-00678 | Reference_telecom | Region_6 | JEC1M7313 | JEC0313 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/22/2025 07:30:37 | 10/22/2025 15:55:13 | 10/22/2025 11:30:37 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JEC1M7313-P1-VIP-CA-L800 @ Generator_SG | 10/22/2025 04:59:30 | Critical | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 04:59:17 | VIP | 4G | baish | Generator_SG | LTE NSA | JEC1M7313 | FLM_TE |  |  | PCM-20251022-00000601 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 07:30:37 | 10/22/2025 13:52:59 | 10/22/2025 15:55:03 |  |  | 10/22/2025 15:55:13 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000277 | PCM-20251022-00000672 | TT-20251022-00663 | Reference_telecom | Region_6 | JEC1M7287 | JEC0287 | Equipment | SW | Issue was solved after softaware configuration | Ansir Iqbal Muhammad Iqbal | 10/22/2025 07:30:47 | 10/22/2025 15:54:57 | 10/22/2025 13:30:47 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JEC1M7287-G9-L18-L21-SBTS-P1-VIP @ Generator_SG | 10/22/2025 04:53:59 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 04:52:26 | VIP | 4G | baish | Generator_SG | LTE NSA | JEC1M7287 | FLM_TE |  |  | PCM-20251022-00000584 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 07:30:47 | 10/22/2025 13:53:00 | 10/22/2025 15:54:44 |  |  | 10/22/2025 15:54:57 |  | Ansir Iqbal Muhammad Iqbal |  |  |  | Telecom | Zain |  | Running |  | OWS
Departed | CM20251022000278 | PCM-20251022-00000673 | TT-20251022-00749 | Telecom | Region_2 | WQSRY0001 | WQSRY0001 |  |  |  | Touseef Iqbal Mazhar Iqbal | 10/22/2025 07:31:02 | 10/22/2025 15:14:28 | 10/22/2025 19:31:02 | WQSRY0001 Partial down | 10/22/2025 07:24:34 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 07:24:34 | P3 | WIFI | Mrat | Sceco | Wifi SA | WQSRY0001_1-GF-AP06 | FLM_TE | [8 empty] | API | 10/22/2025 07:31:02 | 10/22/2025 10:17:34 | 10/22/2025 15:14:22 | 10/22/2025 15:14:28 | [7 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000279 | PCM-20251022-00000674 | TT-20251022-00750 | Reference_telecom | Region_6 | NMR0133-CSG-01 | NMR0133 |  |  |  | Manzoor Ahmed | 10/22/2025 07:31:39 | 10/22/2025 14:04:45 | 10/22/2025 19:31:39 | Optical Invalid at NMR0133-CSG-01 ¦¦ ref TT-20250923-00476 @ Sceco_STB | 10/22/2025 04:50:06 | Minor | 101-2505224 | Optical Invalid | 10/22/2025 04:49:47 | P2 | IPRAN | makhwa | Sceco_STB | IPRAN NSA | NMR0133-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 07:31:39 | 10/22/2025 14:04:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000281 | PCM-20251022-00000676 | TT-20251022-00751 | EM | Region_6 | BHAB2090 | BHAB2090 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 07:32:13 | 10/22/2025 08:52:01 | 10/22/2025 19:32:13 | AIRCON 2 FAILURE at BHAB2090-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/22/2025 07:24:17 | Minor | 7103 | AIRCON 2 FAILURE | 10/22/2025 07:23:48 | P3 | 2G | mohail | Generator_SG | 2G NSA | BHAB2090 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/22/2025 07:32:13 | 10/22/2025 08:52:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000282 | PCM-20251022-00000685 | TT-20251022-00729 | Telecom | Region_5 | MAK1M9681 | MAK0681 | Equipment | SFP_BTS | Replace SFP | Israr Ahmed Muhammad Ghauri | 10/22/2025 07:36:47 | 10/22/2025 16:09:13 | 10/22/2025 19:36:47 | BASE STATION SERVICE PROBLEM (Increased BER detected on the optical connection to Radio Module) at MAK1M9681-P2-NCA-L800-SBTS @ Sceco | 10/22/2025 07:11:34 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 07:11:23 | P2 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9681 | FLM_TE |  |  | PCM-20251022-00000649 | Kindly check the Fiber and SFP at site | Kindly check the Fiber and SFP at site |  |  |  | API | 10/22/2025 07:36:47 | 10/22/2025 14:28:06 | 10/22/2025 14:28:19 | 10/22/2025 14:28:22 | 10/22/2025 15:46:15 | 10/22/2025 16:09:13 |  | Israr Ahmed Muhammad Ghauri |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000285 | PCM-20251022-00000692 | TT-20251022-00771 | EM | [7 empty] | 10/22/2025 07:44:36 | 10/22/2025 07:44:36 | 10/22/2025 19:44:36 | SHELTER DOOR OPEN at BAH1M8152-G9-L8-L18-SBTS-P3-CAP @ Generator_SG | 10/22/2025 07:44:03 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 07:43:56 | P3 | 4G |  | Generator_SG | LTE NSA | BAH1M8152 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 07:44:36 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000286 | PCM-20251022-00000693 | TT-20251022-00746 | Telecom | Region_6 | BHAB0835 | BHAB0835 |  |  |  | Zia Ur Rahamn | 10/22/2025 07:45:22 | 10/22/2025 07:50:04 | 10/22/2025 13:45:22 | 2(2G) 2(3G) 2(5G) sites down under BHAB0835-P3,BHAB0834-P3/BHAB0834-P3 @ Sceco | 10/22/2025 07:26:37 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 07:26:32 | P3 | 2G | mohail | Sceco | 2G_3G_5G SA | BHAB0835-P3 2G_3G_5G,BHAB0834-P3 2G_3G_5G | FLM_EM | BHAB0835 | DOWN SITE HUB TX FB BHAB0835 BHAB0835 Suspected Power issue at HUB BHAB0834 BHAB0834 Suspected Power issue at HUB | PCM-20251022-00000681 | DOWN SITE HUB TX FB BHAB0835 BHAB0835 Suspected Power issue at HUB BHAB0834 BHAB0834 Suspected Power issue at HUB | DOWN SITE HUB TX FB BHAB0835 BHAB0835 Suspected Power issue at HUB BHAB0834 BHAB0834 Suspected Power issue at HUB |  | sites down |  | API | 10/22/2025 07:45:22 | 10/22/2025 07:50:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000287 | PCM-20251022-00000694 | TT-20251021-02562 | Reference_telecom | Region_6 | KHNJ1M7851 | KHNJ0851 | AutoRecovery | Clear_Before_Investigation | Auto Clear | TALEH MUHAMMAD | 10/22/2025 07:46:15 | 10/22/2025 12:04:01 | 10/22/2025 13:46:15 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KHNJ1M7851-L800-P2 @ Sceco | 10/21/2025 21:23:26 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 21:23:20 | P2 | 4G | najran | Sceco | LTE NSA | KHNJ1M7851 | FLM_TE |  |  | PCM-20251022-00000121 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 07:46:15 | 10/22/2025 12:00:50 | 10/22/2025 12:03:45 |  |  | 10/22/2025 12:04:01 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000289 | PCM-20251022-00000703 | TT-20251022-00773 | EM | Region_1 | HFHD2M5436 | HFHD0436 | Enviroment | SCECO_Failure | SCECO auto restored | Emad Mahmoud Ahmed Mohamed | 10/22/2025 07:51:32 | 10/22/2025 11:20:21 | 10/22/2025 13:51:32 | 1(2G/LTE) sites down under HFHD0436-P3/HB1BSCH01 @ Sceco | 10/22/2025 07:43:19 | Major | 21825 | CSL Fault | 10/22/2025 07:43:17 | P3 | 2G | hafr | Sceco | 2G_LTE SA | HFHD0436-P3 | FLM_EM | HFHD0436 | Results: DOWN SITE HUB HFHD0436-P3 HFHD0436 Summary: Hub: HFHD0436, Down Count: 1, Down Sites: HFHD0436-P3 Alarm Summary: HFHD0436 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 07:51:32 | 10/22/2025 10:12:31 | 10/22/2025 11:06:33 | 10/22/2025 11:06:36 | 10/22/2025 11:06:39 | 10/22/2025 11:20:21 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000290 | PCM-20251022-00000704 | TT-20251022-00775 | Reference_telecom | Region_4 | YLM1M7391 | YLM0391 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 07:51:39 | 10/22/2025 13:09:34 | 10/22/2025 13:51:39 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at YLM1M7391-L800-P1-SBTS @ Generator_SG | 10/22/2025 05:47:08 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 05:46:57 | P1 | 4G | alaith | Generator_SG | LTE NSA | YLM1M7391 | FLM_TE |  |  | PCM-20251022-00000695 | Thanks to share RCA for the outage | Thanks to share RCA for the outage |  |  |  | API | 10/22/2025 07:51:39 | 10/22/2025 13:09:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000291 | PCM-20251022-00000708 | TT-20251022-00786 | Telecom | Region_3 | BDR0065-LL-CSG-01 | BDR0065 |  |  |  | Muhammad Sajjad R3 | 10/22/2025 07:52:16 | 10/22/2025 17:27:05 | 10/22/2025 19:52:16 | Optical Invalid at BDR0065-LL-CSG-01 @ Sceco | 10/22/2025 00:46:06 | Minor | 101-2505224 | Optical Invalid | 10/22/2025 00:44:32 | P1 | IPRAN | yanbu | Sceco | IPRAN NSA | BDR0065-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 07:52:16 | 10/22/2025 17:27:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000293 | PCM-20251022-00000709 | TT-20251022-00787 | EM | [7 empty] | 10/22/2025 07:52:21 | 10/22/2025 07:52:21 | 10/22/2025 19:52:21 | RECTIFIER MAINS POWER FAILURE at BAH1M8152-G9-L8-L18-SBTS-P3-CAP @ Generator_SG | 10/22/2025 07:44:03 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 07:43:57 | P3 | 4G |  | Generator_SG | LTE NSA | BAH1M8152 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 07:52:21 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000296 | PCM-20251022-00000712 | TT-20251022-00778 | EM | Region_4 | BHR2323 | BHR2323 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 07:53:01 | 10/22/2025 10:09:10 | 10/22/2025 13:53:01 | 1(2G/5G) sites down under BHR2323-P3/BHR2323-P3 @ Sceco | 10/22/2025 07:44:45 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 07:44:42 | P3 | 2G | jeddah | Sceco | 2G SA | BHR2323-P3 | FLM_TE | BHR2323 | Results: DOWN SITE HUB BHR2323-P3 BHR2323 Summary: Hub: BHR2323, Down Count: 1, Down Sites: BHR2323-P3 Alarm Summary: BHR2323 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 07:53:01 | 10/22/2025 10:09:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000301 | PCM-20251022-00000720 | TT-20251022-00294 | Telecom | Region_1 | KB2 | KB2 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/22/2025 07:58:15 | 10/22/2025 07:58:15 | 10/22/2025 13:58:15 | LOCAL_FAULT at KB2_ELC @ Sceco_STB | 10/22/2025 02:44:29 | Major | 1-12545 | LOCAL_FAULT | 10/22/2025 02:44:19 | P1 | DWDM | dammam | Sceco_STB | DWDM NSA | KB2 | FLM_TE |  |  | PCM-20251022-00000274 | Kindly mention CID name to check the status | Kindly mention CID name to check the status |  |  |  | API | 10/22/2025 07:58:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000303 | PCM-20251022-00000724 | TT-20251022-00801 | Reference_telecom | Region_1 | DAM0374 | DAM0374 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/22/2025 08:00:09 | 10/22/2025 08:46:39 | 10/22/2025 20:00:09 | ETH_LOS at DAM0374_NE_3_SDB @ Sceco | 10/22/2025 04:00:38 | Minor | 1-235 | ETH_LOS | 10/22/2025 03:59:46 | P2 | SRAN | dammam | Sceco | TX NSA | DAM0374 | FLM_TE | [8 empty] | API | 10/22/2025 08:00:09 | 10/22/2025 08:46:39 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000304 | PCM-20251022-00000726 | TT-20251022-00795 | EM | Region_4 | HHR0874 | HHR0874 |  |  |  | Aly Ahmed Aly Sawy | 10/22/2025 08:00:35 | 10/22/2025 08:04:31 | 10/22/2025 12:00:35 | 1(2G/3G/LTE/5G) sites down under HHR0874-P1-VIP-HHR-WBB-G3/HHR0874-P1-VIP-HHR-WBB-G3 @ Generator_SG | 10/22/2025 07:52:38 | Critical | 7706 | BTS O&M LINK FAILURE | 10/22/2025 07:52:34 | VIP | 2G | jeddah | Generator_SG | 2G_3G SA | HHR0874-P1-VIP-HHR-WBB-G3 | FLM_EM | HHR0874 | Results: DOWN SITE HUB HHR0874-P1-VIP-HHR-WBB-G3 HHR0874 Summary: Hub: HHR0874, Down Count: 1, Down Sites: HHR0874-P1-VIP-HHR-WBB-G3 Alarm Summary: HHR0874 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 08:00:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251022000305 | PCM-20251022-00000727 | TT-20251022-00803 | Telecom | Region_5 | MAK2215 | MAK2215 |  |  |  | MOHAMMED JASEEL ARAYIL | 10/22/2025 08:00:37 | 10/23/2025 15:44:25 | 10/22/2025 20:00:37 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK2215-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/22/2025 07:59:54 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 07:59:49 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK2215 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 08:00:37 | 10/22/2025 12:43:33 | 10/23/2025 15:44:25 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000306 | PCM-20251022-00000732 | TT-20251022-00808 | Telecom | Region_4 | JED1MN2910 | JED2910 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 08:01:39 | 10/22/2025 12:56:00 | 10/22/2025 14:01:39 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2910-NR2.6-P3 @ Generator_SG | 10/22/2025 08:00:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 08:00:50 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | JED1MN2910 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 08:01:39 | 10/22/2025 12:56:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000310 | PCM-20251022-00000744 | TT-20251022-00814 | EM | Region_3 | WFR2M2137 | WFR2137 |  |  |  | Muhammad arshad Anwar | 10/22/2025 08:12:32 | 10/22/2025 08:12:32 | 10/22/2025 14:12:32 | 1(2G/LTE) sites down under WFR2137-P3/R3_MD_HWBSC01 @ Sceco | 10/22/2025 08:04:22 | Major | 21825 | CSL Fault | 10/22/2025 08:04:19 | P3 | 2G | madinah | Sceco | 2G_LTE SA | WFR2137-P3 | FLM_EM | WFR2137 | Results: DOWN SITE HUB WFR2137-P3 WFR2137 Summary: Hub: WFR2137, Down Count: 1, Down Sites: WFR2137-P3 Alarm Summary: WFR2137 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 08:12:32 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000314 | PCM-20251022-00000756 | TT-20251022-00829 | Reference_EM | Region_2 | RYMK0502 | RYMK0502 |  |  |  | Moin Uddin | 10/22/2025 08:22:20 | 10/22/2025 10:31:11 | 10/22/2025 20:22:20 | Mains Failure at RYMK0502-P2_SRAN @ Sceco | 10/22/2025 08:12:18 | Minor | 65109 | Mains Failure | 10/22/2025 08:12:14 | P2 | SRAN | muzamiah | Sceco | 2G NSA | RYMK0502 | FLM_EM | [8 empty] | API | 10/22/2025 08:22:20 | 10/22/2025 10:31:11 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000315 | PCM-20251022-00000757 | TT-20251022-00830 | Reference_telecom | Region_6 | ABH0405 | ABH0405 | Transsmission | MW_HW_stuck | Reset ODU | Amir Sohail | 10/22/2025 08:23:21 | 10/23/2025 01:10:19 | 10/22/2025 20:23:21 | Degrade observed in ABH0405_ towards 10.10.144.114 @ Sceco | 10/21/2025 20:24:24 | Minor |  | Degrade | 10/21/2025 20:23:15 | P3 | 2G | abha | Sceco | TX NSA | ABH0405 | FLM_TE | [8 empty] | API | 10/22/2025 08:23:21 | 10/22/2025 11:36:10 | 10/22/2025 17:11:45 | 10/22/2025 17:11:55 | 10/22/2025 17:19:31 | 10/23/2025 01:10:19 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000317 | PCM-20251022-00000763 | TT-20251022-00833 | EM | Region_3 | MDN2U6111 | MDN6011 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Tasbeeh Ullah Muhammad Yousaf | 10/22/2025 08:32:35 | 10/22/2025 15:38:54 | 10/22/2025 12:32:35 | 1(2G/3G/LTE) sites down under MDN6011-P1-HRMCST/R3_MD_HWBSC02 @ Sceco | 10/22/2025 08:24:29 | Critical | 21825 | CSL Fault | 10/22/2025 08:24:27 | P1 | 2G | madinah | Sceco | 2G_3G_LTE SA | MDN6011-P1-HRMCST | FLM_EM | MDN6011 | Results: DOWN SITE HUB MDN6011-P1-HRMCST MDN6011 Summary: Hub: MDN6011, Down Count: 1, Down Sites: MDN6011-P1-HRMCST Alarm Summary: MDN6011 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 08:32:35 | 10/22/2025 14:41:52 | 10/22/2025 15:38:47 |  |  | 10/22/2025 15:38:54 |  | Tasbeeh Ullah Muhammad Yousaf |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000319 | PCM-20251022-00000768 | TT-20251022-00851 | EM | Region_6 | KHS1M7564 | KHS0564 |  |  |  | Ezat Mohammed | 10/22/2025 08:34:43 | 10/23/2025 09:22:08 | 10/22/2025 20:34:43 | RECTIFIER MAINS POWER FAILURE at KHS1M7564-P2-USF-L900 @ Sceco | 10/22/2025 08:26:42 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 08:26:31 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KHS1M7564 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 08:34:43 | 10/23/2025 09:22:08 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000325 | PCM-20251022-00000777 | TT-20251022-00860 | EM | Region_6 | BHAB1M8047 | BHAB2047 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 08:44:32 | 10/22/2025 08:52:02 | 10/22/2025 20:44:32 | RECTIFIER MAINS POWER FAILURE at BHAB1M8047-G9-L8-L18-L21-SBTS-P3 @ Generator_SG | 10/22/2025 08:36:23 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 08:36:14 | P3 | 4G | Baha | Generator_SG | LTE NSA | BHAB1M8047 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 08:44:32 | 10/22/2025 08:52:02 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000330 | PCM-20251022-00000790 | TT-20251022-00864 | EM | Region_1 | SAK2M2953 | SAK2953 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Amjad Muhammad | 10/22/2025 08:57:04 | 10/22/2025 10:40:06 | 10/22/2025 14:57:04 | 1(2G/3G/LTE) sites down under SAK2953-P3-USF/SK1BSCH01 @ Sceco | 10/22/2025 08:50:03 | Major | 21825 | CSL Fault | 10/22/2025 08:49:59 | P3 | 2G | sakaka | Sceco | 2G_3G_LTE SA | SAK2953-P3-USF | FLM_EM | SAK2953 | Results: DOWN SITE HUB SAK2953-P3-USF SAK2953 Summary: Hub: SAK2953, Down Count: 1, Down Sites: SAK2953-P3-USF Alarm Summary: SAK2953 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 08:57:04 | 10/22/2025 09:24:15 | 10/22/2025 10:39:55 |  |  | 10/22/2025 10:40:06 |  | Mohamed Amjad Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000331 | PCM-20251022-00000791 | TT-20251022-00865 | EM | Region_6 | BHAB1M3836 | BHAB0836 |  |  |  | Zia Ur Rahamn | 10/22/2025 08:57:11 | 10/22/2025 08:58:38 | 10/22/2025 14:57:11 | 1(3G/5G) sites down under BHAB0836-P3/BHAB1M3836-P3 @ Sceco | 10/22/2025 08:49:17 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 08:48:38 | P3 | 3G | mohail | Sceco | 3G_5G SA | BHAB0836-P3 | FLM_EM | BHAB0836 | Results: DOWN SITE HUB BHAB0836-P3 BHAB0836 Summary: Hub: BHAB0836, Down Count: 1, Down Sites: BHAB0836-P3 Alarm Summary: BHAB0836 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 08:57:11 | 10/22/2025 08:58:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000332 | PCM-20251022-00000794 | TT-20251022-00878 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 08:58:59 | 10/22/2025 18:29:45 | 10/22/2025 20:58:59 | SHELTER DOOR OPEN at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/22/2025 08:58:45 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 08:56:15 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 08:58:59 | 10/22/2025 18:29:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000333 | PCM-20251022-00000798 | TT-20251022-00876 | EM | Region_6 | SRA2355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 09:00:06 | 10/22/2025 18:29:46 | 10/22/2025 15:00:06 | 1(2G/LTE) sites down under SRA2355-P3/SRA2355-P3 @ Generator_SG | 10/22/2025 08:51:53 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 08:51:45 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | SRA2355-P3 | FLM_EM | SRA2355 | Results: DOWN SITE HUB SRA2355-P3 SRA2355 Summary: Hub: SRA2355, Down Count: 1, Down Sites: SRA2355-P3 Alarm Summary: SRA2355 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 09:00:06 | 10/22/2025 18:29:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000337 | PCM-20251022-00000806 | TT-20251022-00889 | EM | Region_6 | SRA1M8355 | SRA2355 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 09:04:40 | 10/22/2025 18:29:46 | 10/22/2025 21:04:40 | RECTIFIRE MAIN FAIL at SRA1M8355-G9-L8-SBTS-P3 @ Generator_SG | 10/22/2025 08:58:45 | Minor | 7103 | RECTIFIRE MAIN FAIL | 10/22/2025 08:56:15 | P3 | 4G | Baha | Generator_SG | LTE NSA | SRA1M8355 | FLM_EM | [5 empty] | RECTIFIRE MAIN FAIL |  |  | API | 10/22/2025 09:04:40 | 10/22/2025 18:29:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000341 | PCM-20251022-00000816 | TT-20251022-00887 | Telecom | Region_3 | YBDB2M5302 | YBDB0302 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Hossam Ali Ahmed Ali | 10/22/2025 09:09:07 | 10/22/2025 18:44:15 | 10/22/2025 15:09:07 | 1(2G) sites down under YBDB0302-P3/R3_TB_HWBSC01 @ Generator_SG | 10/22/2025 09:00:47 | Major | 21807 | OML Fault | 10/22/2025 09:00:40 | P3 | 2G | tabouk | Generator_SG | 2G SA | YBDB0302-P3 | FLM_TE | YBDB0302 | Results: DOWN SITE HUB YBDB0302-P3 YBDB0302 Summary: Hub: YBDB0302, Down Count: 1, Down Sites: YBDB0302-P3 Alarm Summary: YBDB0302 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 09:09:07 | 10/22/2025 10:39:17 | 10/22/2025 18:44:04 |  |  | 10/22/2025 18:44:15 |  | Hossam Ali Ahmed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000342 | PCM-20251022-00000820 | TT-20251022-00898 | Telecom | Region_4 | MKJD1M7923 | MKJD0923 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 09:09:48 | 10/22/2025 10:09:11 | 10/22/2025 21:09:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKJD1M7923-G9-L8-L18-SBTS-P2 @ Generator_SG | 10/22/2025 09:08:58 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 09:08:50 | P2 | 4G | jeddah | Generator_SG | 5G_Cell SA | MKJD1M7923 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 09:09:48 | 10/22/2025 10:09:11 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000345 | PCM-20251022-00000833 | TT-20251022-00911 | Telecom | Region_6 | WDS0094 | WDS0094 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Mamdouh Helal Helal | 10/22/2025 09:17:33 | 10/22/2025 14:32:11 | 10/22/2025 21:17:33 | BASE STATION SERVICE PROBLEM (No connection to unit) at WDS0094-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/22/2025 09:16:57 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 09:16:49 | P2 | 2G | wadi dawasar | Sceco | 5G_Cell SA | WDS0094 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 09:17:33 | 10/22/2025 13:32:19 | 10/22/2025 14:32:02 |  |  | 10/22/2025 14:32:11 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000346 | PCM-20251022-00000834 | TT-20251022-00912 | EM | [7 empty] | 10/22/2025 09:17:33 | 10/22/2025 09:17:33 | 10/22/2025 21:17:33 | SHELTER DOOR OPEN at TFBH1M8218-G9-L8-L18-L21-SBTS-P3-CAP @ Sceco | 10/22/2025 09:17:25 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 09:17:16 | P2 | 4G |  | Sceco | LTE NSA | TFBH1M8218 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 09:17:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000347 | PCM-20251022-00000837 | TT-20251022-00916 | Telecom | Region_4 | TAF2393 | TAF2393 | Equipment | BSS_HW_fault | Replace GPS Antenna | Asad Ullah Rahim Said | 10/22/2025 09:18:13 | 10/22/2025 12:21:19 | 10/22/2025 21:18:13 | PT:: FLM need to do HC at TAF2393/R4 (BO Request) | 10/22/2025 09:18:04 | Minor | 676767671 | Health Check-WO to TE FME | 10/22/2025 09:18:06 | P3 | 2G | taif | Sceco | 2G_3G_LTE_5G NSA | TAF2393 | FLM_TE | [8 empty] | API | 10/22/2025 09:18:13 | 10/22/2025 11:02:26 | 10/22/2025 11:06:16 | 10/22/2025 11:06:18 | 10/22/2025 11:06:22 | 10/22/2025 12:21:19 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000348 | PCM-20251022-00000838 | TT-20251022-00917 | Reference_telecom | Region_4 | TAF2114 | TAF2114 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 09:18:35 | 10/22/2025 17:30:04 | 10/22/2025 21:18:35 | Degrade observed in TAF2114 towards 10.10.190.167 @ Sceco | 10/21/2025 21:20:32 | Minor |  | Degrade | 10/21/2025 21:18:27 | P2 | 2G | taif | Sceco | TX NSA | TAF2114 | FLM_TE | [8 empty] | API | 10/22/2025 09:18:35 | 10/22/2025 17:30:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000349 | PCM-20251022-00000840 | TT-20251013-02109 | MW_HC | Region_6 | KMS0471 | KMS0471 |  |  |  | Ahmed Abdelaziz Hamid Abdelrahman | 10/22/2025 09:19:49 | 10/22/2025 13:38:35 | 10/22/2025 21:19:49 | Nokia MW HC_P1 Observing Performance Issue at KMS0471-KMS0250_02 | 10/13/2025 15:39:34 | Minor |  | LOF | 10/13/2025 15:39:34 | P3 | 2G | khamis mushyet | Generator_SG | TX NSA | KMS0471-KMS0250_02 | FLM_TE |  | Thanks to check as MW not stable and confirm power | PCM-20251021-00000386 | Thanks to check as MW not stable and confirm power | Thanks to check as MW not stable and confirm power |  |  |  | API | 10/22/2025 09:19:49 | 10/22/2025 13:38:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000351 | PCM-20251022-00000845 | TT-20251022-00920 | Telecom | Region_2 | RIY0406 | RIY0406 | Equipment | BSS_HW_fault | Replace RFU | Farmanullah Akbar Jan | 10/22/2025 09:22:12 | 10/22/2025 09:44:38 | 10/22/2025 15:22:12 | BBU CPRI Interface Error at RIY0406-P2_SRAN @ Sceco | 10/22/2025 09:17:44 | Major | 26234 | BBU CPRI Interface Error | 10/22/2025 09:15:10 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0406 | FLM_TE | [8 empty] | API | 10/22/2025 09:22:12 | 10/22/2025 09:43:12 | 10/22/2025 09:43:16 | 10/22/2025 09:43:22 | 10/22/2025 09:43:26 | 10/22/2025 09:44:38 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000352 | PCM-20251022-00000853 | TT-20251022-00910 | Telecom | Region_4 | JED1U6720 | JED6020 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 09:28:56 | 10/22/2025 15:48:00 | 10/22/2025 15:28:56 | BASE STATION OPERATION DEGRADED (Inter eNB synchronization loss) at JED1U6720-P3 @ Sceco | 10/22/2025 09:09:58 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/22/2025 09:09:50 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6720 | FLM_TE |  |  | PCM-20251022-00000832 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/22/2025 09:28:56 | 10/22/2025 15:48:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000357 | PCM-20251022-00000862 | TT-20251022-00941 | EM | Region_4 | HBI1M8412 | HBI2412 |  |  |  | Hany Mohamed Mahmoud Eldamarany | 10/22/2025 09:33:35 | 10/23/2025 12:57:13 | 10/22/2025 21:33:35 | RECTIFIER MODULE FAILURE at HBI1M8412-G9-L8-L18-SBTS-P3 @ Generator_DG | 10/22/2025 09:25:20 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/22/2025 09:25:10 | P3 | 4G | jeddah | Generator_DG | LTE NSA | HBI1M8412 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/22/2025 09:33:35 | 10/23/2025 12:57:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000361 | PCM-20251022-00000869 | TT-20251022-00946 | Telecom | Region_5 | MAK0015 | MAK0015 | Equipment | SFP_BTS | Replace SFP | Israr Ahmed Muhammad Ghauri | 10/22/2025 09:35:07 | 10/22/2025 14:19:57 | 10/22/2025 21:35:07 | PT:: FLM need to perform HC at MAK0015 /R5 (BO request) | 10/22/2025 09:34:38 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 09:34:38 | P2 | 2G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK0015 | FLM_TE | [8 empty] | API | 10/22/2025 09:35:07 | 10/22/2025 09:56:38 | 10/22/2025 10:44:58 | 10/22/2025 10:45:00 | 10/22/2025 11:13:56 | 10/22/2025 14:19:57 |  | Israr Ahmed Muhammad Ghauri |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000363 | PCM-20251022-00000876 | TT-20251022-00953 | Telecom | Region_5 | MAK0575 | MAK0575 | Equipment | SFP_BTS | Clean SFP | IJAZ ALI | 10/22/2025 09:37:12 | 10/22/2025 15:20:00 | 10/22/2025 21:37:12 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0575-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/22/2025 09:36:13 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 09:36:03 | P2 | 2G | makkah | Sceco | 5G_Cell SA | MAK0575 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 09:37:12 | 10/22/2025 09:49:13 | 10/22/2025 09:49:23 | 10/22/2025 09:49:25 |  | 10/22/2025 15:20:00 |  | IJAZ ALI |  |  |  | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251022000364 | PCM-20251022-00000878 | TT-20251022-00955 | Reference_telecom | Region_4 | TAF2361 | TAF2361 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 09:37:41 | 10/22/2025 21:54:59 | 10/22/2025 21:37:41 | LossOfSignal observed in TAF2361_4 towards 10.10.190.166 @ Sceco | 10/21/2025 21:37:18 | Minor |  | LossOfSignal | 10/21/2025 21:37:14 | P2 | 2G | taif | Sceco | TX NSA | TAF2361 | FLM_TE | [8 empty] | API | 10/22/2025 09:37:41 | 10/22/2025 20:45:21 | 10/22/2025 20:47:25 | 10/22/2025 21:51:04 | 10/22/2025 21:54:59 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000366 | PCM-20251022-00000881 | TT-20251022-00950 | Telecom | Region_6 | BHAB0834 | BHAB0834 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/22/2025 09:43:26 | 10/22/2025 10:40:00 | 10/22/2025 15:43:26 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at BHAB0834-P3 @ Sceco | 10/22/2025 09:31:26 | Major | 7607 | TRX OPERATION DEGRADED | 10/22/2025 09:31:20 | P3 | 2G | mohail | Sceco | 2G_TRX NSA | BHAB0834 | FLM_TE |  |  | PCM-20251022-00000873 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/22/2025 09:43:26 | 10/22/2025 10:13:42 | 10/22/2025 10:39:49 |  |  | 10/22/2025 10:40:00 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000370 | PCM-20251022-00000885 | TT-20251022-00962 | Telecom | Region_1 | JBKH0680 | JBKH0680 |  |  |  | Mohamed Abdelaziz | 10/22/2025 09:45:58 | 10/22/2025 11:26:35 | 10/22/2025 21:45:58 | BBU DC Output Out of Range at JBKH0680-P2-USF_SRAN-PC @ Sceco | 10/22/2025 09:42:59 | Minor | 26112 | BBU DC Output Out of Range | 10/22/2025 09:41:26 | P2 | SRAN | khafji | Sceco | 2G NSA | JBKH0680 | FLM_TE | [8 empty] | API | 10/22/2025 09:45:58 | 10/22/2025 11:26:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000371 | PCM-20251022-00000886 | TT-20251022-00963 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/22/2025 09:46:29 | 10/23/2025 00:46:50 | 10/22/2025 15:46:29 | high temprature 32 at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/22/2025 09:35:59 | Major | 65102 | high temprature 32 | 10/22/2025 09:35:56 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/22/2025 09:46:29 | 10/23/2025 00:46:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000372 | PCM-20251022-00000887 | TT-20251022-00964 | Telecom | Region_1 | JBKH0680 | JBKH0680 |  |  |  | Mohamed Abdelaziz | 10/22/2025 09:47:00 | 10/22/2025 11:26:36 | 10/22/2025 21:47:00 | RF Unit Maintenance Link Failure at JBKH0680-P2-USF_SRAN-PC @ Sceco | 10/22/2025 09:43:13 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 09:41:31 | P2 | SRAN | khafji | Sceco | 2G NSA | JBKH0680 | FLM_TE | [8 empty] | API | 10/22/2025 09:47:00 | 10/22/2025 11:26:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000374 | PCM-20251022-00000891 | TT-20251022-00968 | Reference_EM | Region_1 | SAK2953 | SAK2953 | Enviroment | Rectifier Module | Change rectifer module | Mohamed Amjad Muhammad | 10/22/2025 09:49:36 | 10/22/2025 11:34:01 | 10/22/2025 21:49:36 | Minor Rec alarm at SAK2953-P3-USF_SRAN @ Sceco | 10/22/2025 09:41:47 | Minor | 65108 | Minor Rec alarm | 10/22/2025 09:39:27 | P3 | SRAN | sakaka | Sceco | 2G NSA | SAK2953 | FLM_EM | [8 empty] | API | 10/22/2025 09:49:36 | 10/22/2025 10:40:11 | 10/22/2025 11:33:23 |  |  | 10/22/2025 11:34:01 |  | Mohamed Amjad Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000379 | PCM-20251022-00000903 | TT-20251022-00976 | EM | Region_4 | HLA1M8419 | HLA2419 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/22/2025 09:55:17 | 10/22/2025 15:22:23 | 10/22/2025 21:55:17 | HIGH TEMP at HLA1M8419-G9-L8-L18-SBTS-P3-CAP @ Sceco | 10/22/2025 09:46:50 | Minor | 7103 | HIGH TEMP | 10/22/2025 09:46:42 | P2 | 4G | jeddah | Sceco | LTE NSA | HLA1M8419 | FLM_EM | [5 empty] | HIGH TEMP |  |  | API | 10/22/2025 09:55:17 | 10/22/2025 15:22:23 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000380 | PCM-20251022-00000908 | TT-20251022-00980 | Reference_telecom | Region_2 | BUR0038 | BUR0038 |  |  |  | Raise Ahmed Nisar Ahmed | 10/22/2025 09:57:22 | 10/22/2025 12:07:00 | 10/22/2025 21:57:22 | As BO Requested MW HW HC Observing RSL degradation and alarms flapping for MW link BUR0038 <> BUR0023 | 10/22/2025 09:56:44 | Minor | 1-631 | MW_LOF | 10/22/2025 09:56:48 | P2 | SRAN | buraidah | Sceco | TX NSA | BUR0038 <> BUR0023 | FLM_TE | [8 empty] | API | 10/22/2025 09:57:22 | 10/22/2025 12:07:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000382 | PCM-20251022-00000911 | TT-20251022-00984 | Reference_EM | Region_3 | HLMD2499 | HLMD2499 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/22/2025 09:59:26 | 10/24/2025 00:31:17 | 10/22/2025 21:59:26 | Generator failure at HLMD2499-P3-USF_SRAN @ Generator_SG | 10/22/2025 09:48:58 | Minor | 65114 | Generator failure | 10/22/2025 09:48:52 | P3 | SRAN | hail | Generator_SG | 2G NSA | HLMD2499 | FLM_EM | [8 empty] | API | 10/22/2025 09:59:26 | 10/24/2025 00:31:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000383 | PCM-20251022-00000913 | TT-20251021-02532 | Telecom | Region_6 | BLQ0113 | BLQ0113 | Equipment | BTS_Cable | Replace CPRI Cable | Fawad Khan | 10/22/2025 10:00:07 | 10/22/2025 20:36:35 | 10/22/2025 22:00:07 | BASE STATION SERVICE PROBLEM (No connection to unit) at BLQ0113-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/21/2025 22:47:12 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/21/2025 22:47:01 | P3 | 2G | namas | Sceco | 5G_Cell SA | BLQ0113 | FLM_TE |  |  | PCM-20251022-00000900 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/22/2025 10:00:07 | 10/22/2025 11:25:50 | 10/22/2025 14:03:28 | 10/22/2025 14:03:31 |  | 10/22/2025 20:36:35 |  | Fawad Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000387 | PCM-20251022-00000921 | TT-20251020-01773 | MW_HC | Region_4 | TAF2349 | TAF2349 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 10:04:27 | 10/23/2025 07:26:00 | 10/22/2025 22:04:27 | As BO Requested MW Nokia Observing H UBT continuous flapping TAF2349-TAF2361 | 10/20/2025 16:12:39 | Minor | 113388 | LOF | 10/20/2025 16:12:40 | P2 | 2G | taif | Sceco | TX NSA | TAF2349-TAF2361 | FLM_TE |  |  | PCM-20251022-00000718 | Link still not clear & flapping | Link still not clear & flapping |  |  |  | API | 10/22/2025 10:04:27 | 10/23/2025 07:26:00 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000388 | PCM-20251022-00000922 | TT-20251022-00989 | Reference_telecom | Region_4 | JED1M8555 | JED2555 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 10:04:34 | 10/22/2025 15:45:15 | 10/22/2025 16:04:34 | BASE STATION SERVICE PROBLEM (RX out of order) at JED1M8555-L800-CA-P1-VVIP-SBTS @ Generator_SG | 10/22/2025 09:59:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 09:59:51 | VIP | 4G | jeddah | Generator_SG | LTE_Cell SA | JED1M8555 | FLM_TE | [5 empty] | RX out of order |  |  | API | 10/22/2025 10:04:34 | 10/22/2025 15:45:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000389 | PCM-20251022-00000931 | TT-20251022-01000 | Telecom | Region_4 | JED1W6081 | JED6081 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 10:09:27 | 10/22/2025 15:48:01 | 10/22/2025 22:09:27 | JED1W6081 is partial down | 10/22/2025 10:05:30 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 10:05:30 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_2-6F-AP06 | FLM_TE | [8 empty] | API | 10/22/2025 10:09:27 | 10/22/2025 15:48:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000396 | PCM-20251022-00000947 | TT-20251022-00995 | Reference_telecom | Region_4 | JED1U6070_1 | JED6070 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 10:14:19 | 10/22/2025 15:48:01 | 10/22/2025 14:14:19 | CELL OPERATION DEGRADED (VSWR minor alarm) at JED1U6070_1-P1-VIP-SHOP @ Sceco | 10/22/2025 10:00:18 | Critical | 7654 | CELL OPERATION DEGRADED | 10/22/2025 10:00:07 | VIP | 4G | jeddah | Sceco | LTE_Cell SA | JED1U6070_1 | FLM_TE |  |  | PCM-20251022-00000927 | Please check VSWR locally | Please check VSWR locally |  |  |  | API | 10/22/2025 10:14:19 | 10/22/2025 15:48:01 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000397 | PCM-20251022-00000950 | TT-20251022-01018 | Telecom | Region_5 | MAK0515 | MAK0515 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 10:14:54 | 10/22/2025 10:14:54 | 10/22/2025 22:14:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at MAK0515-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/22/2025 10:13:55 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 10:13:50 | P3 | 2G | makkah | Sceco | 5G_Cell SA | MAK0515 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 10:14:54 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000401 | PCM-20251022-00000957 | TT-20251022-01022 | Reference_EM | Region_2 | QUW0914 | QUW0914 | Enviroment | SCECO_Failure | SCECO auto restored | Saleem Khan Amir Dost | 10/22/2025 10:18:00 | 10/23/2025 04:53:45 | 10/22/2025 22:18:00 | Mains Failure at QUW0914-P2_SRAN @ Sceco | 10/22/2025 10:08:00 | Minor | 65109 | Mains Failure | 10/22/2025 10:07:56 | P2 | SRAN | quweyah | Sceco | 2G NSA | QUW0914 | FLM_EM | [8 empty] | API | 10/22/2025 10:18:00 | 10/22/2025 10:35:34 | 10/23/2025 04:53:38 |  |  | 10/23/2025 04:53:45 |  | Saleem Khan Amir Dost |  |  |  | EM | Zain |  | Running |  | OWS
Preparation | CM20251022000402 | PCM-20251022-00000960 | TT-20251022-01009 | Telecom | Region_4 | JED0500 | JED0500 |  |  |  | Fawzi Muneer Fawzi Mahmoud | 10/22/2025 10:20:02 | 10/23/2025 06:40:54 | 10/22/2025 16:20:02 | LOCAL BLOCK at JED0500-P2 @ Sceco | 10/22/2025 10:08:20 | Major | 7208 | LOCAL BLOCK | 10/22/2025 10:08:07 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0500 | FLM_TE |  |  | PCM-20251022-00000938 | FLM need to check as site fluctuating on regular interval | FLM need to check as site fluctuating on regular interval |  |  |  | API | 10/22/2025 10:20:02 | 10/23/2025 06:39:57 | 10/23/2025 06:40:48 | 10/23/2025 06:40:51 | 10/23/2025 06:40:54 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000404 | PCM-20251022-00000962 | TT-20251022-01010 | Telecom | Region_2 | RYMK0502 | RYMK0502 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Moin Uddin | 10/22/2025 10:20:43 | 10/22/2025 15:26:59 | 10/22/2025 14:20:43 | 5(2G) 5(3G) 5(LTE) sites down under R2_RY1_HWBSC01 @ Sceco | 10/22/2025 10:10:42 | Critical | 21825 | CSL Fault | 10/22/2025 10:10:37 | P2 | SRAN | muzamiah | Sceco | 2G_3G_LTE SA | RIY2138-P2 2G_3G_LTE,RYMK0501-P2 2G_3G_LTE,RIY2273-P2 2G_3G_LTE,RIY2140-P2 2G_3G_LTE,RYMK0502-P2 2G_3G_LTE | FLM_EM | RYMK0502 | Hub:- RYMK0502 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00000956 | Hub:- RYMK0502 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RYMK0502 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 10:20:43 | 10/22/2025 10:31:19 | 10/22/2025 10:31:20 | 10/22/2025 10:31:25 | 10/22/2025 10:31:43 | 10/22/2025 15:26:59 |  | Moin Uddin |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000406 | PCM-20251022-00000965 | TT-20251022-01031 | Reference_EM | Region_3 | RSP0036 | RSP0036 |  |  |  | Sayed Satoor | 10/22/2025 10:24:11 | 10/22/2025 19:35:31 | 10/22/2025 16:24:11 | high temprature 40 at RSP0036-P1-VIP_SRAN @ Generator_SG | 10/22/2025 10:14:04 | Major | 65103 | high temprature 40 | 10/22/2025 10:13:59 | VIP | SRAN | yanbu | Generator_SG | 2G NSA | RSP0036 | FLM_EM | [8 empty] | API | 10/22/2025 10:24:11 | 10/22/2025 19:35:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000408 | PCM-20251022-00000968 | TT-20251022-01034 | EM | Region_3 | HLUL2425 | HLUL2425 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/22/2025 10:24:41 | 10/24/2025 00:31:17 | 10/22/2025 22:24:41 | NETECO: Door Status Sensor Alarm at HLUL2425 @ Generator_SG | 10/22/2025 10:24:30 | Minor | 5152 | Door Status Sensor Alarm | 10/22/2025 10:24:30 | P3 | SRAN | hail | Generator_SG | 2G NSA | HLUL2425 | FLM_EM | [8 empty] | API | 10/22/2025 10:24:41 | 10/24/2025 00:31:17 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000409 | PCM-20251022-00000969 | TT-20251022-01035 | Reference_EM | Region_3 | HLUL2425 | HLUL2425 |  |  |  | Adel Mohamed Mahmoud Kandil | 10/22/2025 10:25:14 | 10/24/2025 00:31:18 | 10/22/2025 22:25:14 | Door opening alarm at HLUL2425-P3_SRAN @ Generator_SG | 10/22/2025 10:24:36 | Minor | 65101 | Door opening alarm | 10/22/2025 10:24:33 | P3 | SRAN | hail | Generator_SG | 2G NSA | HLUL2425 | FLM_EM | [8 empty] | API | 10/22/2025 10:25:14 | 10/24/2025 00:31:18 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000411 | PCM-20251022-00000975 | TT-20251022-01033 | Telecom | Region_5 | MAK0515 | MAK0515 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 10:29:32 | 10/22/2025 10:29:32 | 10/22/2025 16:29:32 | 1(5G) sites down under MAK0515-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/22/2025 10:21:26 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 10:21:23 | P3 | 2G | makkah | Sceco | 5G SA | MAK0515-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 | FLM_TE | MAK0515 | Results: DOWN SITE HUB MAK0515-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 MAK0515 Summary: Hub: MAK0515, Down Count: 1, Down Sites: MAK0515-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 Alarm Summary: MAK0515 No Active Alarm on HUB |  |  |  | Connection refused [URL:http://10.98.176.20:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 10:29:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000412 | PCM-20251022-00000976 | TT-20251022-01042 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/22/2025 10:29:53 | 10/22/2025 11:21:15 | 10/22/2025 16:29:53 | Board Temperature Unacceptable at RIY2866-P3_SRAN-PC @ Sceco | 10/22/2025 10:21:18 | Major | 26104 | Board Temperature Unacceptable | 10/22/2025 10:19:45 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/22/2025 10:29:53 | 10/22/2025 11:21:15 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000413 | PCM-20251022-00000977 | TT-20251022-01039 | Telecom | Region_4 | RAB0483 | RAB0483 |  |  |  | Khizer Hayat | 10/22/2025 10:30:09 | 10/22/2025 11:31:49 | 10/22/2025 22:30:09 | BASE STATION ANTENNA LINE PROBLEM at RAB0483-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/22/2025 10:20:41 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/22/2025 10:20:35 | P2 | 2G | jeddah | Sceco | 2G NSA | RAB0483 | FLM_TE |  |  | PCM-20251022-00000974 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/22/2025 10:30:09 | 10/22/2025 11:31:49 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000414 | PCM-20251022-00000978 | TT-20251022-00937 | Telecom | Region_2 | RY4-ASG-02 | RY4 |  |  |  | Saddam hussain muhammad khan | 10/22/2025 10:30:16 | 10/22/2025 10:30:16 | 10/22/2025 22:30:16 | Bad Package Error Rising at RY4-ASG-02 @ Sceco_STB | 10/22/2025 09:29:16 | Minor | 101-2501403 | Bad Package Error Rising | 10/22/2025 09:30:12 | P1 | IPRAN | riyadh | Sceco_STB | IPRAN NSA | RY4-ASG-02 | FLM_TE |  |  | PCM-20251022-00000861 | email shared with all details | email shared with all details |  |  |  | API | 10/22/2025 10:30:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000415 | PCM-20251022-00000980 | TT-20251021-02203 | Telecom | Region_4 | JED0341 | JED0341 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/22/2025 10:30:41 | 10/22/2025 10:30:41 | 10/22/2025 16:30:41 | 3(2G) 1(LTE) 2(5G) sites down under JED6079-P3,JED0883-P2,JED0113-P2/JED0113-P2 @ Sceco | 10/21/2025 18:00:01 | Major | 7706 | BTS O&M LINK FAILURE | 10/21/2025 17:59:57 | P1 | 2G | jeddah | Sceco | 2G SA | JED0113-P2 2G,JED0883-P2 2G,JED6079-P3 2G | FLM_TE | JED0341 | Approved Results: DOWN SITE HUB JED0113-P2 JED0113 JED0883-P2 JED0113 JED6079-P3 JED6079 Summary: Hub: JED0113, Down Count: 2, Down Sites: JED0113-P2, JED0883-P2 Hub: JED6079, Down Count: 1, Down Sites: JED6079-P3 Alarm Summary: JED0113 No Active Alarm on HUB JED6079 No Active Alarm on HUB | PCM-20251022-00000759 | Approved | Approved |  | sites down |  | API | 10/22/2025 10:30:41 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000416 | PCM-20251022-00000981 | TT-20251022-01011 | Reference_telecom | Region_4 | HHR1M7459 | HHR0459 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 10:30:49 | 10/22/2025 15:45:16 | 10/22/2025 14:30:49 | CELL NOTIFICATION (Temperature alarm) at HHR1M7459-L800-P1-VIP @ Sceco | 10/22/2025 10:04:48 | Critical | 7655 | CELL NOTIFICATION | 10/22/2025 10:04:38 | VIP | 4G | jeddah | Sceco | LTE NSA | HHR1M7459 | FLM_TE |  |  | PCM-20251022-00000940 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/22/2025 10:30:49 | 10/22/2025 15:45:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000417 | PCM-20251022-00000983 | TT-20251022-01047 | Reference_EM | Region_1 | RYDM0060 | RYDM0060 | Transsmission | IPRAN_Fluctuation | Replace Fiber Cable | Ahmed AbdELmoaz Ibrahim | 10/22/2025 10:32:58 | 10/22/2025 13:37:45 | 10/22/2025 22:32:58 | Genset not in auto mode at RYDM0060-P2_SRAN @ Sceco_STB | 10/22/2025 10:22:27 | Minor | 65113 | Genset not in auto mode | 10/22/2025 10:22:24 | P2 | SRAN | dammam | Sceco_STB | 2G NSA | RYDM0060 | FLM_EM | [8 empty] | API | 10/22/2025 10:32:58 | 10/22/2025 10:59:08 | 10/22/2025 13:37:11 |  |  | 10/22/2025 13:37:45 |  | Ahmed AbdELmoaz Ibrahim |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000418 | PCM-20251022-00000985 | TT-20251022-01055 | Reference_EM | Region_1 | TBJF2019 | TBJF2019 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Amjad Muhammad | 10/22/2025 10:35:34 | 10/22/2025 11:33:12 | 10/22/2025 22:35:34 | Mains Failure at TBJF2019-P3_SRAN @ Sceco | 10/22/2025 10:25:39 | Minor | 65109 | Mains Failure | 10/22/2025 10:25:35 | P3 | SRAN | sakaka | Sceco | 2G NSA | TBJF2019 | FLM_EM | [8 empty] | API | 10/22/2025 10:35:34 | 10/22/2025 10:40:12 | 10/22/2025 11:33:02 |  |  | 10/22/2025 11:33:12 |  | Mohamed Amjad Muhammad |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000419 | PCM-20251022-00000992 | TT-20251022-01007 | Reference_telecom | Region_6 | SHF1M7275 | SHF0275 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Amir Sohail | 10/22/2025 10:39:22 | 10/22/2025 11:37:51 | 10/22/2025 22:39:22 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at SHF1M7275-G9-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 10:11:07 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 07:50:43 | P3 | 4G | al harja | Sceco | LTE NSA | SHF1M7275 | FLM_TE |  |  | PCM-20251022-00000937 | Alarm Cleared . FLM need to Check and close with RCA. | Alarm Cleared . FLM need to Check and close with RCA. |  |  |  | API | 10/22/2025 10:39:22 | 10/22/2025 11:36:12 | 10/22/2025 11:37:34 |  |  | 10/22/2025 11:37:51 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000420 | PCM-20251022-00000994 | TT-20251022-01012 | Reference_telecom | Region_6 | SHF1M7272 | SHF0272 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Jamshaid Muhammad Ashraf | 10/22/2025 10:39:58 | 10/22/2025 16:47:42 | 10/22/2025 22:39:58 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at SHF1M7272-G9-L8-SBTS-P3 @ Generator_SG | 10/22/2025 10:10:51 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 07:50:43 | P3 | 4G | al harja | Generator_SG | LTE NSA | SHF1M7272 | FLM_TE |  |  | PCM-20251022-00000941 | Alarm cleared. FLM need to check and close with RCA. | Alarm cleared. FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 10:39:58 | 10/22/2025 10:42:39 | 10/22/2025 16:47:33 |  |  | 10/22/2025 16:47:42 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000423 | PCM-20251022-00001006 | TT-20251022-01071 | Reference_telecom | Region_4 | JED6010 | JED6010 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 10:47:27 | 10/22/2025 15:48:02 | 10/22/2025 22:47:27 | RF Unit RX Channel RTWP/RSSI Unbalanced at JED6010-DCU @ Sceco | 10/22/2025 07:47:19 | Minor | 26522 | RF Unit RX Channel RTWP/RSSI Unbalanced | 10/22/2025 07:47:15 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6010 | FLM_TE | [8 empty] | API | 10/22/2025 10:47:27 | 10/22/2025 15:48:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000426 | PCM-20251022-00001008 | TT-20251020-01101 | MW_HC | Region_5 | MAK0761 | MAK0761 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/22/2025 10:48:02 | 10/22/2025 10:48:02 | 10/22/2025 22:48:02 | As BO Requested MW Nokia Observing Performance issue For MW Link MAK0761-MAK0468 | 10/20/2025 11:47:39 | Minor | 113388 | LOF | 10/20/2025 11:47:41 | P2 | 2G | makkah | Sceco | TX NSA | MAK0761-MAK0468 | FLM_TE |  | Approved | PCM-20251022-00000984 | Approved | Approved |  |  |  | API | 10/22/2025 10:48:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000427 | PCM-20251022-00001009 | TT-20251022-01075 | Telecom | Region_2 | RIYB6158 | RIYB6158 | Equipment | BSS_HW_fault | Replace DRH | Muhammad Waqas Ashraf Muhammad Ashraf | 10/22/2025 10:48:59 | 10/22/2025 11:34:16 | 10/22/2025 16:48:59 | RF Unit Optical Module Transmit/Receive Fault at RIYB6158-DCU3 @ Sceco | 10/22/2025 10:42:30 | Major | 26503 | RF Unit Optical Module Transmit/Receive Fault | 10/22/2025 10:42:14 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYB6158 | FLM_TE | [8 empty] | API | 10/22/2025 10:48:59 | 10/22/2025 11:33:40 | 10/22/2025 11:33:44 | 10/22/2025 11:33:46 | 10/22/2025 11:33:48 | 10/22/2025 11:34:16 |  | Muhammad Waqas Ashraf Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000428 | PCM-20251022-00001011 | TT-20251022-01078 | Telecom | Region_4 | JED1U6771 | JED6071 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 10:50:02 | 10/22/2025 15:48:02 | 10/22/2025 16:50:02 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1U6771-G9-L18-SBTS-P1-SHOP @ Sceco | 10/22/2025 10:49:22 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 10:49:11 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1U6771 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 10:50:02 | 10/22/2025 15:48:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000429 | PCM-20251022-00001012 | TT-20251022-01069 | Telecom | Region_2 | RIY2M2543 | RIY2543 | Equipment | BSS_HW_Stuck | Reset Controller Card | Khan zeb Shah nawaz | 10/22/2025 10:51:03 | 10/22/2025 11:04:23 | 10/22/2025 16:51:03 | 1(2G) sites down under RIY2543-P2/R2_RY2_HWBSC01 @ Sceco | 10/22/2025 10:42:55 | Major | 21825 | CSL Fault | 10/22/2025 10:42:50 | P2 | 2G | riyadh | Sceco | 2G SA | RIY2543-P2 | FLM_TE | RIY2543 | Results: DOWN SITE HUB RIY2543-P2 RIY2543 Summary: Hub: RIY2543, Down Count: 1, Down Sites: RIY2543-P2 Alarm Summary: RIY2543 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 10:51:03 | 10/22/2025 10:54:21 | 10/22/2025 11:03:52 |  |  | 10/22/2025 11:04:23 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000431 | PCM-20251022-00001022 | TT-20251022-01082 | EM | Region_2 | RIY2M2678 | RIY2678 |  |  |  | Asim Mushtaq Mushtaq Ahmad | 10/22/2025 11:02:03 | 10/22/2025 19:42:13 | 10/22/2025 17:02:03 | 1(2G/LTE) sites down under RIY2678-P2/R2_RY4_HWBSC01 @ Generator_SG | 10/22/2025 10:53:42 | Major | 21825 | CSL Fault | 10/22/2025 10:53:40 | P2 | 2G | riyadh | Generator_SG | 2G_LTE SA | RIY2678-P2 | FLM_EM | RIY2678 | Results: DOWN SITE HUB RIY2678-P2 RIY2678 Summary: Hub: RIY2678, Down Count: 1, Down Sites: RIY2678-P2 Alarm Summary: RIY2678 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 11:02:03 | 10/22/2025 19:42:13 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000432 | PCM-20251022-00001026 | TT-20251022-01094 | Telecom | Region_1 | HFF6028 | HFF6028 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 11:02:25 | 10/22/2025 15:59:03 | 10/22/2025 23:02:25 | RF Unit Maintenance Link Failure at HFF6028-DCU1 @ Sceco | 10/22/2025 10:49:26 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 10:57:16 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6028 | FLM_TE | [8 empty] | API | 10/22/2025 11:02:25 | 10/22/2025 11:10:03 | 10/22/2025 15:58:48 |  |  | 10/22/2025 15:59:03 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000435 | PCM-20251022-00001027 | TT-20251022-01095 | Telecom | Region_6 | KMS0250 | KMS0250 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/22/2025 11:02:56 | 10/22/2025 20:41:41 | 10/22/2025 23:02:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS0250-G9-L8-L18-L21-NNR2.6-SBTS-P2 @ Sceco | 10/22/2025 11:02:11 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:02:00 | P2 | 2G | khamis mushyet | Sceco | 5G_Cell SA | KMS0250 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 11:02:56 | 10/22/2025 12:10:24 | 10/22/2025 12:10:50 | 10/22/2025 12:10:53 | 10/22/2025 14:20:30 | 10/22/2025 20:41:41 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000436 | PCM-20251022-00001028 | TT-20251022-01096 | EM | Region_3 | RUSF9040 | RUSF9040 |  |  |  | Mohamed Babeker Abdulrahim Babeker | 10/22/2025 11:03:57 | 10/22/2025 23:38:28 | 10/22/2025 23:03:57 | NETECO: Insufficient Redundant Rectifiers at RUSF9040 @ Sceco_STB | 10/22/2025 10:57:40 | Minor | 16386 | Insufficient Redundant Rectifiers | 10/22/2025 10:57:40 | P3 | Repeater | madinah | Sceco_STB | 2G NSA | RUSF9040 | FLM_EM | [8 empty] | API | 10/22/2025 11:03:57 | 10/22/2025 23:38:28 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000437 | PCM-20251022-00001030 | TT-20251022-01097 | Telecom | Region_3 | MDN2903 | MDN2903 | Equipment | SW | Issue was solved after softaware configuration | Ibrahim Mohammad AbdulMalik alraee | 10/22/2025 11:05:01 | 10/22/2025 21:13:46 | 10/22/2025 23:05:01 | ALD Maintenance Link Failure at MDN2903-P2_SRAN @ Sceco | 10/22/2025 11:02:09 | Minor | 26541 | ALD Maintenance Link Failure | 10/22/2025 11:00:29 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2903 | FLM_TE | [8 empty] | API | 10/22/2025 11:05:01 | 10/22/2025 11:12:33 | 10/22/2025 21:13:39 |  |  | 10/22/2025 21:13:46 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000438 | PCM-20251022-00001031 | TT-20251022-01092 | EM | Region_1 | JBRK2M3924 | JBRK0924 |  |  |  | Rafiq Ahmed Elturifi | 10/22/2025 11:05:34 | 10/22/2025 15:13:02 | 10/22/2025 17:05:34 | 1(3G/LTE) sites down under JBRK0924-P2/JB1RNCH01 @ Sceco | 10/22/2025 10:57:12 | Major | 22214 | NodeB Unavailable | 10/22/2025 10:57:09 | P2 | 3G | jubail | Sceco | 3G SA | JBRK0924-P2 | FLM_TE | JBRK0924 | Results: DOWN SITE HUB JBRK0924-P2 JBRK0924 Summary: Hub: JBRK0924, Down Count: 1, Down Sites: JBRK0924-P2 Alarm Summary: JBRK0924 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 11:05:34 | 10/22/2025 15:13:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000439 | PCM-20251022-00001033 | TT-20251022-01101 | EM | Region_4 | JED1M7558 | JED0558 |  |  |  | Ahmed Gamal Mohamed Farag | 10/22/2025 11:08:06 | 10/22/2025 11:08:06 | 10/22/2025 23:08:06 | HIGH TEMPERATURE 32 DEGREE C at JED1M7558-CA-L900-L800-SBTS @ Sceco | 10/22/2025 10:59:44 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/22/2025 10:59:31 | P2 | 4G | jeddah | Sceco | LTE NSA | JED1M7558 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/22/2025 11:08:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000441 | PCM-20251022-00001035 | TT-20251022-01098 | Telecom | Region_5 | MAK0096 | MAK0096 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 11:10:02 | 10/22/2025 11:10:02 | 10/22/2025 17:10:02 | 1(5G) sites down under MAK0096-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/22/2025 11:01:50 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 11:01:48 | P2 | 2G | makkah | Sceco | 5G SA | MAK0096-G9-L8-L18-L21-NR2.6-SBTS-P2 | FLM_TE | MAK0096 | Results: DOWN SITE HUB MAK0096-G9-L8-L18-L21-NR2.6-SBTS-P2 MAK0096 Summary: Hub: MAK0096, Down Count: 1, Down Sites: MAK0096-G9-L8-L18-L21-NR2.6-SBTS-P2 Alarm Summary: MAK0096 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.98.168.228:8080] [URL:http://10.98.168.228:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 11:10:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000442 | PCM-20251022-00001038 | TT-20251022-01108 | EM | Region_6 | SBA1M8020 | SBA2020 |  |  |  | Khurram Nawaz Muhammad Akram | 10/22/2025 11:11:11 | 10/23/2025 08:59:43 | 10/22/2025 23:11:11 | SHELTER DOOR OPEN at SBA1M8020-P2-NCA-L800-L2100-SBTS @ Sceco | 10/22/2025 11:10:37 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 11:10:26 | P2 | 4G | baish | Sceco | LTE NSA | SBA1M8020 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 11:11:11 | 10/23/2025 08:59:43 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000443 | PCM-20251022-00001039 | TT-20251022-01109 | Reference_telecom | Region_1 | JBKH0680 | JBKH0680 |  |  |  | Mohamed Abdelaziz | 10/22/2025 11:11:42 | 10/22/2025 11:26:37 | 10/22/2025 23:11:42 | POWER_ABNORMAL at JBKH0680_NE_2_VRRP @ Sceco | 10/22/2025 09:41:34 | Minor | 1-412 | POWER_ABNORMAL | 10/22/2025 09:41:23 | P2 | SRAN | khafji | Sceco | TX NSA | JBKH0680 | FLM_TE | [8 empty] | API | 10/22/2025 11:11:42 | 10/22/2025 11:26:37 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000445 | PCM-20251022-00001041 | TT-20251022-01114 | Reference_EM | Region_1 | HFBD2M2007 | HFBD2007 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/22/2025 11:14:50 | 10/23/2025 11:08:06 | 10/22/2025 17:14:50 | Mains Failure at HFBD2M2007-P1-HUB @ Generator_SG | 10/22/2025 11:04:55 | Major | 65109 | Mains Failure | 10/22/2025 11:04:54 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M2007 | FLM_EM | [8 empty] | API | 10/22/2025 11:14:50 | 10/22/2025 17:47:12 | 10/23/2025 07:45:06 | 10/23/2025 07:45:11 |  | 10/23/2025 11:08:06 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000446 | PCM-20251022-00001043 | TT-20251022-01103 | EM | Region_1 | JBL2M1913 | JBL0913 |  |  |  | Hamid Bilal Bashir Ahmed | 10/22/2025 11:15:12 | 10/23/2025 03:56:12 | 10/22/2025 17:15:12 | 1(2G/3G/LTE) sites down under JBL0913-P2/R1_JB_HWBSC01 @ Sceco | 10/22/2025 11:07:59 | Major | 21825 | CSL Fault | 10/22/2025 11:07:56 | P2 | 2G | jubail | Sceco | 2G_3G_LTE SA | JBL0913-P2 | FLM_EM | JBL0913 | Results: DOWN SITE HUB JBL0913-P2 JBL0913 Summary: Hub: JBL0913, Down Count: 1, Down Sites: JBL0913-P2 Alarm Summary: JBL0913 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 11:15:12 | 10/23/2025 03:56:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000449 | PCM-20251022-00001047 | TT-20251022-01115 | Telecom | Region_4 | BHR1MN2551 | BHR2551 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 11:15:51 | 10/22/2025 11:20:45 | 10/22/2025 17:15:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR1MN2551-NR2.6-P3 @ Generator_SG | 10/22/2025 11:14:59 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:14:47 | P3 | 5G | jeddah | Generator_SG | 5G_Cell SA | BHR1MN2551 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 11:15:51 | 10/22/2025 11:20:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000450 | PCM-20251022-00001052 | TT-20251022-01118 | Telecom | Region_4 | JED0086 | JED0086 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/22/2025 11:18:27 | 10/22/2025 11:18:27 | 10/22/2025 17:18:27 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0086-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-SHOP-HUB-WDM-FON @ Sceco | 10/22/2025 11:17:34 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:17:23 | VIP | 2G | jeddah | Sceco | 5G_Cell SA | JED0086 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 11:18:27 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000452 | PCM-20251022-00001054 | TT-20251022-01008 | Telecom | Region_6 | SMT1MT0300 | SMT0300 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/22/2025 11:19:21 | 10/22/2025 12:19:43 | 10/22/2025 17:19:21 | CELL SERVICE PROBLEM (TD-LTE radio disabled) at SMT1MT0300-P3 @ Sceco | 10/22/2025 10:08:19 | Major | 7114 | CELL SERVICE PROBLEM | 10/22/2025 10:08:09 | P2 | 4G | jizan | Sceco | 5G_Cell SA | SMT1MT0300 | FLM_TE |  |  | PCM-20251022-00000939 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/22/2025 11:19:21 | 10/22/2025 12:18:56 | 10/22/2025 12:19:22 |  |  | 10/22/2025 12:19:43 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000453 | PCM-20251022-00001056 | TT-20251022-01122 | EM | Region_3 | MDQS2430 | MDQS2430 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/22/2025 11:24:06 | 10/22/2025 11:51:16 | 10/22/2025 23:24:06 | NETECO: Genset Generator Fault at MDQS2430 @ Generator_DG | 10/22/2025 11:17:48 | Minor | 40564 | Genset Generator Fault | 10/22/2025 11:17:48 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2430 | FLM_EM | [8 empty] | API | 10/22/2025 11:24:06 | 10/22/2025 11:51:16 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000454 | PCM-20251022-00001061 | TT-20251022-01128 | Telecom | Region_1 | DM1 | DM1 |  |  |  | MUHAMMAD UMAR MEHMOOD KHAN | 10/22/2025 11:27:51 | 10/22/2025 11:27:51 | 10/22/2025 17:27:51 | Observed Link Down flapped and restored On DMM1_vMSE_RN03_NEW_EOR Connected to DMM-RC-BLF-04_Eth1/1_for_vDPI | 10/22/2025 11:21:44 | Major | 5000003 | Link Down | 10/22/2025 11:21:44 | P1 | DWDM | dammam | Sceco_STB | IPBB NSA | Observed Link Down flapped and restored On DMM1_vMSE_RN03_NEW_EOR Connected to DMM-RC-BLF-04_Eth1/1_for_vDPI | FLM_TE | [5 empty] | Observed Link Down flapped and restored On DMM1_vMSE_RN03_NEW_EOR Connected to DMM-RC-BLF-04_Eth1/1_for_vDPI |  |  | API | 10/22/2025 11:27:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000455 | PCM-20251022-00001063 | TT-20251022-01130 | Reference_EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/22/2025 11:28:46 | 10/23/2025 00:46:50 | 10/22/2025 17:28:46 | Door opening alarm at RYDM0657-P1-HUB_SRAN @ Generator_DG | 10/22/2025 11:28:09 | Major | 65101 | Door opening alarm | 10/22/2025 11:24:01 | P1 | SRAN | riyadh | Generator_DG | 2G NSA | RYDM0657 | FLM_EM | [8 empty] | API | 10/22/2025 11:28:46 | 10/23/2025 00:46:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000456 | PCM-20251022-00001068 | TT-20251022-01124 | EM | Region_2 | RYDM2M1657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/22/2025 11:30:35 | 10/23/2025 00:46:51 | 10/22/2025 15:30:35 | 1(2G/3G) sites down under RYDM0657-P1-HUB/R2_RY4_HWBSC01 @ Generator_DG | 10/22/2025 11:23:37 | Critical | 21825 | CSL Fault | 10/22/2025 11:23:35 | P1 | 2G | riyadh | Generator_DG | 2G_3G SA | RYDM0657-P1-HUB | FLM_EM | RYDM0657 | Results: DOWN SITE HUB RYDM0657-P1-HUB RYDM0657 Summary: Hub: RYDM0657, Down Count: 1, Down Sites: RYDM0657-P1-HUB Alarm Summary: RYDM0657 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 11:30:35 | 10/23/2025 00:46:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000458 | PCM-20251022-00001078 | TT-20251022-01142 | Telecom | Region_4 | JED2127 | JED2127 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/22/2025 11:37:01 | 10/22/2025 11:37:01 | 10/22/2025 23:37:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2127-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P3 @ Sceco | 10/22/2025 11:36:17 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:36:08 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2127 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 11:37:01 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000461 | PCM-20251022-00001095 | TT-20251022-01158 | Telecom | Region_4 | TAF1M8393 | TAF2393 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 11:40:08 | 10/22/2025 17:30:05 | 10/22/2025 17:40:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF1M8393-L800-P3 @ Sceco | 10/22/2025 11:39:21 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:39:12 | P3 | 4G | taif | Sceco | 5G_Cell SA | TAF1M8393 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 11:40:08 | 10/22/2025 17:30:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000463 | PCM-20251022-00001101 | TT-20251022-01141 | EM | Region_4 | JED2823 | JED2823 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 11:42:52 | 10/22/2025 12:56:02 | 10/22/2025 17:42:52 | 1(2G/LTE) sites down under JED2823-P3/JED2823-P3 @ Generator_SG | 10/22/2025 11:31:58 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 11:31:54 | P3 | 2G | jeddah | Generator_SG | 2G_LTE SA | JED2823-P3 | FLM_TE | JED2823 | Results: DOWN SITE HUB JED2823-P3 JED2823 Summary: Hub: JED2823, Down Count: 1, Down Sites: JED2823-P3 Alarm Summary: JED2823 No Active Alarm on HUB | PCM-20251022-00001094 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 11:42:52 | 10/22/2025 12:56:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000464 | PCM-20251022-00001104 | TT-20251022-01165 | Telecom | Region_4 | JED2721 | JED2721 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 11:43:44 | 10/22/2025 12:56:02 | 10/22/2025 17:43:44 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2721-G9-L8-L18-L21-NR2.6-P3 @ Sceco | 10/22/2025 11:43:03 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:42:58 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED2721 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 11:43:44 | 10/22/2025 12:56:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000465 | PCM-20251022-00001106 | TT-20251022-01102 | EM | Region_1 | JBL0913 | JBL0913 |  |  |  | Hamid Bilal Bashir Ahmed | 10/22/2025 11:44:04 | 10/23/2025 03:56:12 | 10/22/2025 15:44:04 | 1(2G/3G/LTE) sites down under JBAP0137-P1/R1_JB_HWBSC01 @ Sceco | 10/22/2025 11:07:59 | Critical | 21825 | CSL Fault | 10/22/2025 11:07:56 | P2 | SRAN | jubail | Sceco | 2G_3G_LTE SA | JBAP0137-P1 | FLM_EM | JBL0913 | Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001051 | Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- JBL0913 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 11:44:04 | 10/23/2025 03:56:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000469 | PCM-20251022-00001111 | TT-20251022-01090 | EM | Region_4 | SQR0875 | SQR0875 | Equipment | BSS_HW_fault | Replace System Module | TOSIF AHMED - MUHAMMAD SHARIF | 10/22/2025 11:48:08 | 10/22/2025 12:25:26 | 10/22/2025 17:48:08 | 1(2G/LTE/5G) sites down under SQR0875-P3/SQR0875-P3 @ Generator_SG | 10/22/2025 10:56:12 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 10:56:09 | P3 | 2G | adam | Generator_SG | 2G_LTE SA | SQR0875-P3 | FLM_TE |  | Results: DOWN SITE HUB SQR0875-P3 Need to check Summary: Alarm Summary: HUB site not found | PCM-20251022-00001093 | Please share approval mail with all required details | Please share approval mail with all required details |  | sites down |  | API | 10/22/2025 11:48:08 | 10/22/2025 12:10:11 | 10/22/2025 12:25:13 |  |  | 10/22/2025 12:25:26 |  | TOSIF AHMED - MUHAMMAD SHARIF |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000470 | PCM-20251022-00001113 | TT-20251022-01133 | Reference_telecom | Region_6 | KHS0559 | KHS0559 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/22/2025 11:48:57 | 10/22/2025 15:19:24 | 10/22/2025 17:48:57 | BASE STATION SERVICE PROBLEM (Rx signal level failure) at KHS0559-GSM-UMTS-P2-USF @ Sceco | 10/22/2025 11:24:30 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:24:22 | P2 | 2G | khamis mushyet | Sceco | 5G_Cell SA | KHS0559 | FLM_TE |  |  | PCM-20251022-00001066 | FLM need to check RFM & connected SFP at site | FLM need to check RFM & connected SFP at site |  |  |  | API | 10/22/2025 11:48:57 | 10/22/2025 13:38:35 | 10/22/2025 15:19:16 |  |  | 10/22/2025 15:19:24 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000471 | PCM-20251022-00001117 | TT-20251022-01125 | Telecom | Region_5 | MAK1MN0032 | MAK0032 | Equipment | BSS_HW_fault | Replace System Module | Inam ullah | 10/22/2025 11:52:28 | 10/22/2025 19:31:45 | 10/22/2025 17:52:28 | BASE STATION HARDWARE PROBLEM (Oven oscillator clock missing;Default System Time) at MAK1MN0032-NR2.6-P2 @ Sceco | 10/22/2025 11:23:57 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/22/2025 03:03:22 | P3 | 5G | makkah | Sceco | 5G NSA | MAK1MN0032 | FLM_TE |  |  | PCM-20251022-00001058 | FLM need to check HW at site and perform HC. | FLM need to check HW at site and perform HC. |  |  |  | API | 10/22/2025 11:52:28 | 10/22/2025 17:56:37 | 10/22/2025 17:57:02 | 10/22/2025 17:57:09 | 10/22/2025 18:29:00 | 10/22/2025 19:31:45 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000472 | PCM-20251022-00001120 | TT-20251022-01176 | EM | Region_4 | RYMK1M7536 | RYMK0536 |  |  |  | Mohamed Elsaid Abdou Younes | 10/22/2025 11:55:07 | 10/22/2025 11:55:07 | 10/22/2025 23:55:07 | COMMERCIAL POWER FAILURE at RYMK1M7536-L800-P2-SBTS @ Generator_DG | 10/22/2025 11:46:38 | Minor | 7103 | COMMERCIAL POWER FAILURE | 10/22/2025 11:46:33 | P2 | 4G | taif | Generator_DG | LTE NSA | RYMK1M7536 | FLM_EM | [5 empty] | COMMERCIAL POWER FAILURE |  |  | API | 10/22/2025 11:55:07 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000473 | PCM-20251022-00001121 | TT-20251022-01131 | Reference_telecom | Region_4 | JED1M8417 | JED2417 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 11:55:44 | 10/22/2025 12:13:17 | 10/22/2025 17:55:44 | BASE STATION CONNECTIVITY PROBLEM (Transport layer connection failure in S1 interface) at JED1M8417-P3-CA-L800 @ Sceco | 10/22/2025 11:26:56 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/20/2025 20:18:50 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1M8417 | FLM_TE |  |  | PCM-20251022-00001062 | Alarm cleared. FLM need to check and close with RCA. | Alarm cleared. FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 11:55:44 | 10/22/2025 12:13:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000474 | PCM-20251022-00001122 | TT-20251022-01126 | EM | Region_2 | RYDM0657 | RYDM0657 |  |  |  | ELMORSY MOHAMED ELMORSY RAGAB | 10/22/2025 11:56:00 | 10/23/2025 00:46:52 | 10/22/2025 17:56:00 | 1(2G/LTE) sites down under RUM0531-P3/RY1BSCH02 @ Generator_SG | 10/22/2025 11:23:37 | Major | 21825 | CSL Fault | 10/22/2025 11:23:36 | P1 | SRAN | riyadh | Generator_DG | 2G_LTE SA | RUM0531-P3 | FLM_EM | RYDM0657 | Hub:- RYDM0657 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001114 | Hub:- RYDM0657 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RYDM0657 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 11:56:00 | 10/23/2025 00:46:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000475 | PCM-20251022-00001123 | TT-20251022-01179 | Reference_telecom | Region_4 | JED2127 | JED2127 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/22/2025 11:56:07 | 10/22/2025 11:56:07 | 10/22/2025 23:56:07 | ReplaceableUnitProblem observed in JED2127 towards 10.21.69.82 @ Sceco | 10/21/2025 23:55:59 | Minor |  | ReplaceableUnitProblem | 10/21/2025 23:55:55 | P3 | 2G | jeddah | Sceco | TX NSA | JED2127 | FLM_TE | [8 empty] | API | 10/22/2025 11:56:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000476 | PCM-20251022-00001131 | TT-20251022-01177 | Telecom | Region_1 | SHB2M3689 | SHB0689 |  |  |  | Mohamed Magdy Fouad Zayed | 10/22/2025 12:00:32 | 10/22/2025 18:15:54 | 10/22/2025 18:00:32 | 1(3G) sites down under SHB0689-P3/RY1RNCH05 @ Power Cube | 10/22/2025 11:52:20 | Major | 22214 | NodeB Unavailable | 10/22/2025 11:52:16 | P3 | 3G | hafouf | Power Cube | 3G SA | SHB0689-P3 | FLM_TE | SHB0689 | Results: DOWN SITE HUB SHB0689-P3 SHB0689 Summary: Hub: SHB0689, Down Count: 1, Down Sites: SHB0689-P3 Alarm Summary: SHB0689 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 12:00:32 | 10/22/2025 18:15:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000478 | PCM-20251022-00001133 | TT-20251022-01178 | Telecom | Region_4 | JED1M7545 | JED0545 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 12:01:02 | 10/22/2025 12:01:02 | 10/22/2025 18:01:02 | 1(LTE) sites down under JED0545-CA-L900-L800-SBTS @ Sceco | 10/22/2025 11:52:57 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 11:52:54 | P2 | 4G | jeddah | Sceco | LTE SA | JED0545-CA-L900-L800-SBTS | FLM_TE | JED0545 | Results: DOWN SITE HUB JED0545-CA-L900-L800-SBTS JED0545 Summary: Hub: JED0545, Down Count: 1, Down Sites: JED0545-CA-L900-L800-SBTS Alarm Summary: JED0545 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.160.92:8080] [URL:http://10.97.160.92:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 12:01:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000482 | PCM-20251022-00001140 | TT-20251022-01199 | Reference_EM | Region_3 | MDQS2430 | MDQS2430 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/22/2025 12:05:26 | 10/23/2025 11:30:00 | 10/23/2025 00:05:26 | Low battery voltage at MDQS2430-P3_SRAN @ Generator_DG | 10/22/2025 11:55:14 | Minor | 65110 | Low battery voltage | 10/22/2025 11:55:09 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2430 | FLM_EM | [8 empty] | API | 10/22/2025 12:05:26 | 10/23/2025 11:30:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000483 | PCM-20251022-00001141 | TT-20251022-01200 | Reference_telecom | Region_1 | HFF0052 | HFF0052 |  |  |  | Mohamed Magdy Fouad Zayed | 10/22/2025 12:05:27 | 10/22/2025 18:15:55 | 10/22/2025 18:05:27 | RF Unit VSWR Threshold Crossed at HFF0052-P2_SRAN @ Sceco | 10/22/2025 09:05:32 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/22/2025 09:05:19 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0052 | FLM_TE | [8 empty] | API | 10/22/2025 12:05:27 | 10/22/2025 18:15:55 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000484 | PCM-20251022-00001142 | TT-20251022-01174 | Telecom | Region_6 | KHS0558 | KHS0558 |  |  |  | Amir Abbas Arif Raza | 10/22/2025 12:05:48 | 10/22/2025 12:31:41 | 10/22/2025 18:05:48 | 2(2G) 2(LTE) 1(5G) sites down under KHS0558-P2-USF,KHS0332-P3/KHS0332-P3 @ Sceco | 10/22/2025 11:49:18 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 11:49:14 | P2 | 2G | khamis mushyet | Sceco | 2G_LTE_5G SA | KHS0332-P3 2G_LTE_5G,KHS0558-P2-USF 2G_LTE | FLM_EM | KHS0558 | Results: DOWN SITE HUB KHS0332-P3 KHS0332 KHS0558-P2-USF KHS0558 Summary: Hub: KHS0332, Down Count: 1, Down Sites: KHS0332-P3 Hub: KHS0558, Down Count: 1, Down Sites: KHS0558-P2-USF Alarm Summary: KHS0332 Alarm Active on HUB KHS0558 Alarm Active on HUB | PCM-20251022-00001125 | KHS0558 | KHS0558 |  | sites down |  | API | 10/22/2025 12:05:48 | 10/22/2025 12:31:41 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000485 | PCM-20251022-00001143 | TT-20251022-01201 | Reference_telecom | Region_3 | BDR2M3065 | BDR0065 |  |  |  | Muhammad Sajjad R3 | 10/22/2025 12:05:49 | 10/22/2025 17:27:05 | 10/23/2025 00:05:49 | GNSS Antenna Fault at BDR2M3065-P1-DIA(Ref::TT-20251020-02106) @ Sceco | 10/20/2025 07:02:17 | Minor | 26125 | GNSS Antenna Fault | 10/20/2025 07:00:43 | P1 | 3G | yanbu | Sceco | 2G NSA | BDR2M3065 | FLM_TE | [8 empty] | API | 10/22/2025 12:05:49 | 10/22/2025 17:27:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000487 | PCM-20251022-00001147 | TT-20251022-01204 | Telecom | Region_3 | MDTB0343 | MDTB0343 |  |  |  | Qaiser Abbas | 10/22/2025 12:06:29 | 10/22/2025 14:32:07 | 10/22/2025 18:06:29 | HARD_ERR at MDTB0343_ELC @ Sceco_STB | 10/22/2025 12:02:43 | Major | 1-12580 | HARD_ERR | 10/22/2025 12:02:29 | P1 | SRAN | tabouk | Sceco_STB | DWDM NSA | MDTB0343 | FLM_TE | [5 empty] | 1-ELC(3-C)-17-G1M520S-OTHER |  |  | API | 10/22/2025 12:06:29 | 10/22/2025 14:32:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000488 | PCM-20251022-00001149 | TT-20251022-01193 | Telecom | Region_4 | TAF2393 | TAF2393 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 12:07:35 | 10/22/2025 17:30:06 | 10/22/2025 18:07:35 | 1(2G) sites down under TAF2393-P3/TAF2393-P3 @ Sceco | 10/22/2025 11:59:22 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 11:59:16 | P3 | 2G | taif | Sceco | 2G SA | TAF2393-P3 | FLM_TE | TAF2393 | Results: DOWN SITE HUB TAF2393-P3 TAF2393 Summary: Hub: TAF2393, Down Count: 1, Down Sites: TAF2393-P3 Alarm Summary: TAF2393 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 12:07:35 | 10/22/2025 17:30:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000489 | PCM-20251022-00001151 | TT-20251022-01208 | Reference_telecom | Region_6 | KMS1M8060 | KMS2060 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/22/2025 12:08:33 | 10/22/2025 19:36:10 | 10/23/2025 00:08:33 | BASE STATION INFORMATION (Unit temperature is high) at KMS1M8060-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/22/2025 11:28:27 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 11:28:17 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M8060 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/22/2025 12:08:33 | 10/22/2025 13:38:36 | 10/22/2025 19:36:03 |  |  | 10/22/2025 19:36:10 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000490 | PCM-20251022-00001152 | TT-20251022-01210 | Reference_EM | Region_1 | DAM2802 | DAM2802 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/22/2025 12:09:13 | 10/22/2025 13:24:31 | 10/22/2025 18:09:13 | Door opening alarm at DAM2802-FWA-P1-VIP_SRAN @ Sceco | 10/22/2025 12:08:55 | Major | 65101 | Door opening alarm | 10/22/2025 12:08:52 | P3 | SRAN | dammam | Sceco | 2G NSA | DAM2802 | FLM_EM | [8 empty] | API | 10/22/2025 12:09:13 | 10/22/2025 13:24:31 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000491 | PCM-20251022-00001155 | TT-20251022-01214 | Telecom | Region_4 | JDJZ0762 | JDJZ0762 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 12:11:38 | 10/22/2025 13:09:35 | 10/23/2025 00:11:38 | ODU CPU / Cable Open at JDJZ0762 on 10.154.140.73 @ Sceco | 10/22/2025 12:05:26 | Minor | ODU CPU / Cable Open | ODU CPU / Cable Open | 10/22/2025 12:10:10 | P1 | 2G | jeddah | Sceco | TX NSA | JDJZ0762 | FLM_TE | [8 empty] | API | 10/22/2025 12:11:38 | 10/22/2025 13:09:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000493 | PCM-20251022-00001159 | TT-20251022-01219 | Telecom | Region_6 | BHAB1M7828 | BHAB0828 | Equipment | BTS_Cable | Replace Fiber Cable | Muhammad Jamal Khan Abbas Ali | 10/22/2025 12:13:43 | 10/22/2025 17:35:48 | 10/23/2025 00:13:43 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHAB1M7828-P2-L800-CA-SBTS @ Sceco | 10/22/2025 12:13:04 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 12:12:54 | P3 | 4G | makhwa | Sceco | 5G_Cell SA | BHAB1M7828 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 12:13:43 | 10/22/2025 12:32:56 | 10/22/2025 17:35:30 |  |  | 10/22/2025 17:35:48 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000495 | PCM-20251022-00001166 | TT-20251022-01217 | EM | Region_4 | DGB2169 | DGB2169 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 12:17:34 | 10/22/2025 13:09:36 | 10/22/2025 18:17:34 | 1(2G/LTE/5G) sites down under DGB2169-P3/DGB2169-P3 @ Sceco | 10/22/2025 12:09:27 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 12:09:22 | P3 | 2G | alaith | Sceco | 2G SA | DGB2169-P3 | FLM_TE | DGB2169 | Results: DOWN SITE HUB DGB2169-P3 DGB2169 Summary: Hub: DGB2169, Down Count: 1, Down Sites: DGB2169-P3 Alarm Summary: DGB2169 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 12:17:34 | 10/22/2025 13:09:36 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000497 | PCM-20251022-00001169 | TT-20251022-01227 | Reference_EM | Region_3 | SML2332 | SML2332 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/22/2025 12:18:53 | 10/22/2025 16:40:45 | 10/23/2025 00:18:53 | Mains Failure at SML2332-P3-USF_SRAN @ Generator_SG | 10/22/2025 12:08:46 | Minor | 65109 | Mains Failure | 10/22/2025 12:08:43 | P3 | SRAN | hail | Generator_SG | 2G NSA | SML2332 | FLM_EM | [8 empty] | API | 10/22/2025 12:18:53 | 10/22/2025 16:40:45 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251022000500 | PCM-20251022-00001174 | TT-20251022-01231 | Telecom | Region_6 | WDMD0001 | WDMD0001 |  |  |  | Ansir Iqbal Muhammad Iqbal | 10/22/2025 12:22:21 | 10/22/2025 15:53:58 | 10/23/2025 00:22:21 | WDMD0001 is partial down | 10/22/2025 12:12:26 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 12:12:26 | P2 | WIFI | jizan | Sceco | Wifi SA | WDMD0001_1F-AP01 | FLM_TE | [8 empty] | API | 10/22/2025 12:22:21 | 10/22/2025 13:53:00 | 10/22/2025 15:02:16 | 10/22/2025 15:02:20 | 10/22/2025 15:53:58 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000501 | PCM-20251022-00001175 | TT-20251022-01232 | Telecom | Region_4 | JED0914 | JED0914 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 12:23:31 | 10/22/2025 15:45:16 | 10/23/2025 00:23:31 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0914-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/22/2025 12:22:51 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 12:22:41 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0914 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 12:23:31 | 10/22/2025 15:45:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000502 | PCM-20251022-00001177 | TT-20251022-01236 | Reference_EM | Region_3 | HHR2068 | HHR2068 |  |  |  | Shafique Ahmad Sardar Ali | 10/22/2025 12:25:35 | 10/22/2025 12:31:52 | 10/23/2025 00:25:35 | Low battery voltage at HHR2068-P3_SRAN-PC @ Sceco | 10/22/2025 12:15:10 | Minor | 65110 | Low battery voltage | 10/22/2025 12:15:05 | P1 | SRAN | madinah | Sceco | 2G NSA | HHR2068 | FLM_EM | [8 empty] | API | 10/22/2025 12:25:35 | 10/22/2025 12:31:52 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251022000503 | PCM-20251022-00001180 | TT-20251022-00978 | Telecom | [7 empty] | 10/22/2025 12:27:44 | 10/22/2025 12:27:44 | 10/22/2025 18:27:44 | RAS3W6010 complete site down | 10/22/2025 09:53:32 | Major | 676767675 | Health Check-WO to TE FME | 10/22/2025 09:53:32 | P3 | WIFI |  | Sceco | Wifi SA | RAS3W6010 complete site down | FLM_EM |  |  | PCM-20251022-00001173 | Site down due to power issue | Site down due to power issue |  | site down |  | API | 10/22/2025 12:27:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000504 | PCM-20251022-00001181 | TT-20251022-01238 | EM | Region_6 | BHAB1M8055 | BHAB2055 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 12:28:10 | 10/22/2025 18:29:47 | 10/23/2025 00:28:10 | RECTIFIER MODULE FAILURE at BHAB1M8055-G9-L8-L18-L21-SBTS-P3-WBB-G3 @ Sceco | 10/22/2025 12:19:57 | Minor | 7103 | RECTIFIER MODULE FAILURE | 10/22/2025 12:19:53 | P3 | 4G | Albaha | Sceco | LTE NSA | BHAB1M8055 | FLM_EM | [5 empty] | RECTIFIER MODULE FAILURE |  |  | API | 10/22/2025 12:28:10 | 10/22/2025 18:29:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000505 | PCM-20251022-00001186 | TT-20251022-01244 | Telecom | Region_4 | JED1M7692 | JED0692 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 12:30:14 | 10/22/2025 15:45:16 | 10/22/2025 18:30:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M7692-P1-HUB-CA-L900-L800-SBTS @ Sceco | 10/22/2025 12:29:12 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 12:29:00 | P1 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M7692 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 12:30:14 | 10/22/2025 15:45:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000506 | PCM-20251022-00001187 | TT-20251022-00443 | Telecom | Region_6 | MHL1M7122 | MHL0122 | Equipment | BSS_HW_fault | Replace RF Module | Muhammad Jamal Khan Abbas Ali | 10/22/2025 12:31:20 | 10/22/2025 13:03:17 | 10/22/2025 16:31:20 | BASE STATION SERVICE PROBLEM (No connection to unit) at MHL1M7122-CA-L800-P1-SHOP @ Sceco | 10/22/2025 04:29:51 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 04:29:42 | P1 | 4G | mohail | Sceco | 5G_Cell SA | MHL1M7122 | FLM_TE |  |  | PCM-20251022-00001154 | Please share approval mail with all required details | Please share approval mail with all required details |  |  |  | API | 10/22/2025 12:31:20 | 10/22/2025 12:32:57 | 10/22/2025 13:03:01 |  |  | 10/22/2025 13:03:17 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000508 | PCM-20251022-00001189 | TT-20251022-01246 | Telecom | Region_4 | JED6024 | JED6024 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 12:32:19 | 10/22/2025 15:48:03 | 10/22/2025 18:32:19 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED6024-GSM-P3 @ Sceco | 10/22/2025 12:31:39 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 12:31:35 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED6024 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 12:32:19 | 10/22/2025 15:48:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000509 | PCM-20251022-00001190 | TT-20251022-01247 | EM | Region_3 | RUSF9013 | RUSF9013 |  |  |  | Yasser Mohamed Mohamed Yousef | 10/22/2025 12:32:19 | 10/22/2025 12:32:19 | 10/22/2025 16:32:19 | RELAY_ALARM_CRITICAL at RUSF9013_NE_1 @ Generator_SG | 10/22/2025 12:31:22 | Critical | 1-12305 | RELAY_ALARM_CRITICAL | 10/22/2025 12:31:04 | P3 | Repeater | yanbu | Generator_SG | TX NSA | RUSF9013 | FLM_EM | [8 empty] | API | 10/22/2025 12:32:19 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000510 | PCM-20251022-00001192 | TT-20251022-01251 | Reference_telecom | Region_6 | ABH0120 | ABH0120 | Transsmission | MW_HW_fault | Replace Fiber Cable | Amir Sohail | 10/22/2025 12:34:21 | 10/22/2025 13:13:04 | 10/23/2025 00:34:21 | LagPortDown observed in ABH0120 towards 10.10.152.35 @ Sceco | 10/22/2025 00:35:50 | Minor |  | LagPortDown | 10/22/2025 00:34:09 | VIP | 2G | abha | Sceco | TX NSA | ABH0120 | FLM_TE | [8 empty] | API | 10/22/2025 12:34:21 | 10/22/2025 13:12:10 | 10/22/2025 13:12:32 |  |  | 10/22/2025 13:13:04 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000512 | PCM-20251022-00001197 | TT-20251022-01256 | EM | Region_4 | JDRS1M8225 | JDRS2225 |  |  |  | Farag Ahmed Taha Mohamed | 10/22/2025 12:35:56 | 10/23/2025 13:45:36 | 10/23/2025 00:35:56 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V at JDRS1M8225-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 12:27:38 | Minor | 7103 | RECTIFIER LOW BATTERY VOLTAGE 46.3 V | 10/22/2025 12:27:32 | P3 | 4G | jeddah | Sceco | LTE NSA | JDRS1M8225 | FLM_EM | [5 empty] | RECTIFIER LOW BATTERY VOLTAGE 46.3 V |  |  | API | 10/22/2025 12:35:56 | 10/23/2025 13:45:36 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000513 | PCM-20251022-00001198 | TT-20251022-01257 | Reference_EM | Region_1 | HFBD2M2007 | HFBD2007 | Equipment | SW | Issue was solved after softaware configuration | Mohamed Ramadan Mohamed Gomaa | 10/22/2025 12:36:26 | 10/23/2025 11:13:00 | 10/22/2025 18:36:26 | Door opening alarm at HFBD2M2007-P1-HUB @ Generator_SG | 10/22/2025 12:35:58 | Major | 65101 | Door opening alarm | 10/22/2025 12:35:57 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFBD2M2007 | FLM_EM | [8 empty] | API | 10/22/2025 12:36:26 | 10/22/2025 17:47:12 | 10/23/2025 11:12:53 |  |  | 10/23/2025 11:13:00 |  | Mohamed Ramadan Mohamed Gomaa |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000515 | PCM-20251022-00001202 | TT-20251022-01260 | Reference_EM | Region_3 | RSP0039 | RSP0039 |  |  |  | Sayed Satoor | 10/22/2025 12:38:30 | 10/22/2025 19:35:32 | 10/22/2025 18:38:30 | Door opening alarm at RSP0039-P1-ARP-VVIP_SRAN @ Sceco | 10/22/2025 12:38:12 | Major | 65101 | Door opening alarm | 10/22/2025 12:38:07 | VIP | SRAN | yanbu | Sceco | 2G NSA | RSP0039 | FLM_EM | [8 empty] | API | 10/22/2025 12:38:30 | 10/22/2025 19:35:32 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000516 | PCM-20251022-00001206 | TT-20251022-01267 | EM | Region_6 | AQQ1M8431 | AQQ2431 |  |  |  | Sohail Nasir Mir Afzal | 10/22/2025 12:41:37 | 10/23/2025 08:05:06 | 10/23/2025 00:41:37 | SHELTER DOOR OPEN at AQQ1M8431-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/22/2025 12:41:06 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 12:40:59 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8431 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 12:41:37 | 10/23/2025 08:05:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000521 | PCM-20251022-00001223 | TT-20251022-01289 | Reference_telecom | Region_6 | BHAB1M7819 | BHAB0819 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/22/2025 12:51:26 | 10/22/2025 16:51:14 | 10/23/2025 00:51:26 | BASE STATION INFORMATION (Unit temperature is high) at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/22/2025 12:11:07 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 12:11:01 | P3 | 4G | makhwa | Sceco | LTE NSA | BHAB1M7819 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/22/2025 12:51:26 | 10/22/2025 14:32:06 | 10/22/2025 16:50:52 |  |  | 10/22/2025 16:51:14 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000525 | PCM-20251022-00001229 | TT-20251022-01295 | Telecom | Region_6 | ABH1M7361 | ABH0361 | Equipment | BSS_HW_Stuck | Reset RRU | Amir Sohail | 10/22/2025 12:54:31 | 10/22/2025 17:00:35 | 10/23/2025 00:54:31 | BASE STATION INFORMATION (No module fan detected) at ABH1M7361-CA-L800-SBTS-P3 @ Sceco | 10/22/2025 12:46:29 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 12:46:25 | P3 | 4G | abha | Sceco | LTE NSA | ABH1M7361 | FLM_TE | [5 empty] | No module fan detected |  |  | API | 10/22/2025 12:54:31 | 10/22/2025 13:12:11 | 10/22/2025 17:00:23 |  |  | 10/22/2025 17:00:35 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000526 | PCM-20251022-00001231 | TT-20251022-01297 | EM | Region_3 | MDQS2430 | MDQS2430 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/22/2025 12:56:04 | 10/23/2025 11:30:00 | 10/23/2025 00:56:04 | NETECO: Door Open Alarm at MDQS2430 @ Generator_DG | 10/22/2025 12:55:52 | Minor | 5152 | Door Open Alarm | 10/22/2025 12:55:52 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2430 | FLM_EM | [8 empty] | API | 10/22/2025 12:56:04 | 10/23/2025 11:30:00 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000527 | PCM-20251022-00001232 | TT-20251022-01298 | EM | Region_4 | RYMK1M7544 | RYMK0544 |  |  |  | Farghal Ashour Hassan Farghal | 10/22/2025 12:56:05 | 10/22/2025 19:30:56 | 10/23/2025 00:56:05 | HIGH TEMPERATURE 32 DEGREE C at RYMK1M7544-L800-P2-USF @ Sceco | 10/22/2025 12:47:42 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/22/2025 12:47:32 | P2 | 4G | taif | Sceco | LTE NSA | RYMK1M7544 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/22/2025 12:56:05 | 10/22/2025 19:30:56 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000528 | PCM-20251022-00001233 | TT-20251022-01299 | Reference_EM | Region_3 | MDQS2430 | MDQS2430 |  |  |  | Magid Mohamed Ahmed Mohamed Musa | 10/22/2025 12:56:35 | 10/23/2025 11:30:01 | 10/23/2025 00:56:35 | Door opening alarm at MDQS2430-P3_SRAN @ Generator_DG | 10/22/2025 12:55:57 | Minor | 65101 | Door opening alarm | 10/22/2025 12:55:54 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2430 | FLM_EM | [8 empty] | API | 10/22/2025 12:56:35 | 10/23/2025 11:30:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Reject_FME | CM20251022000530 | PCM-20251022-00001237 | TT-20251022-01304 | EM | Region_5 | USMD0771 | USMD0771 |  |  |  | Mohammad Naseer Raja Mohammed | 10/22/2025 13:00:44 | 10/23/2025 06:08:33 | 10/22/2025 19:00:44 | DOOR ALARM at USMD0771-G9-NL8-L18-L21-NNR2.6-SBTS-P1-HUB-USF @ Sceco | 10/22/2025 13:00:19 | Major | 7103 | DOOR ALARM | 10/22/2025 13:00:10 | P1 | 2G | makkah | Sceco | 2G NSA | USMD0771 | FLM_EM | [5 empty] | DOOR ALARM |  |  | API | 10/22/2025 13:00:44 | 10/22/2025 19:38:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000532 | PCM-20251022-00001238 | TT-20251022-01262 | Telecom | Region_2 | RIY2629 | RIY2629 | Transsmission | MW_HW_fault | Replace ODU | Farmanullah Akbar Jan | 10/22/2025 13:02:07 | 10/22/2025 13:07:31 | 10/22/2025 19:02:07 | 1(2G) sites down under RIY2332-P3/R2_RY3_HWBSC01 @ Generator_SG | 10/22/2025 12:35:14 | Major | 21825 | CSL Fault | 10/22/2025 12:35:11 | P2 | SRAN | riyadh | Sceco | 2G SA | RIY2332-P3 | FLM_EM | RIY2629 | Hub:- RIY2629 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001214 | Hub:- RIY2629 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RIY2629 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 13:02:07 | 10/22/2025 13:05:59 | 10/22/2025 13:06:31 | 10/22/2025 13:06:36 | 10/22/2025 13:06:38 | 10/22/2025 13:07:31 |  | Farmanullah Akbar Jan |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000534 | PCM-20251022-00001247 | TT-20251022-01323 | Telecom | Region_2 | RY1 | RY1 |  |  |  | Saddam hussain muhammad khan | 10/22/2025 13:11:07 | 10/22/2025 13:11:07 | 10/22/2025 19:11:07 | support with laptop/console/console pwd to do this change in case connection lost | 10/22/2025 13:10:56 | Major | 5000003 | Link Down | 10/22/2025 13:10:56 | P1 | BSC | riyadh | Sceco_STB | IPBB NSA | support with laptop/console/console pwd to do this change in case connection lost | FLM_TE | [5 empty] | support with laptop/console/console pwd to do this change in case connection lost |  |  | API | 10/22/2025 13:11:07 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000535 | PCM-20251022-00001254 | TT-20251022-01261 | Reference_telecom | Region_5 | MAK1M9629 | MAK0629 |  |  |  | Sohail Ashraf Muhammad Ashraf | 10/22/2025 13:13:28 | 10/22/2025 13:13:28 | 10/23/2025 01:13:28 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at MAK1M9629-P3-NCA-L800-SBTS @ Sceco | 10/22/2025 12:33:40 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 12:33:35 | P3 | 4G | makkah | Sceco | 5G_Cell SA | MAK1M9629 | FLM_TE |  |  | PCM-20251022-00001203 | FLM need to check HW and perform HC at site | FLM need to check HW and perform HC at site |  |  |  | API | 10/22/2025 13:13:28 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000536 | PCM-20251022-00001260 | TT-20251022-01319 | EM | Region_4 | JED0086 | JED0086 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/22/2025 13:15:02 | 10/22/2025 14:31:07 | 10/22/2025 17:15:02 | 1(2G/5G) sites down under JED0086-P1-VIP-SHOP-HUB-WDM-FON/JED0086-P1-VIP-SHOP-HUB-WDM-FON @ Sceco | 10/22/2025 13:06:39 | Critical | 7706 | BTS O&M LINK FAILURE | 10/22/2025 13:06:36 | VIP | 2G | jeddah | Sceco | 2G SA | JED0086-P1-VIP-SHOP-HUB-WDM-FON | FLM_TE | JED0086 | Results: DOWN SITE HUB JED0086-P1-VIP-SHOP-HUB-WDM-FON JED0086 Summary: Hub: JED0086, Down Count: 1, Down Sites: JED0086-P1-VIP-SHOP-HUB-WDM-FON Alarm Summary: JED0086 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:15:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000537 | PCM-20251022-00001261 | TT-20251022-01328 | Reference_telecom | Region_4 | JED0487 | JED0487 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 13:15:26 | 10/22/2025 13:34:10 | 10/23/2025 01:15:26 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0487-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/22/2025 13:08:09 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:08:05 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0487 | FLM_TE |  |  | PCM-20251022-00001253 | RSSI TS Steps: • Clean or Remake Jumper connectors • Check any bending in the Jumper cable. • Confirm MHA HW is OK and Configuration is as per physical connectivity.(If available at site). • RET HW and Values as per design (If available at site). • Hard reset to equipment if values are stuck and not changing at all with above actions. • Sector Swap to check if value swapping to other sector or port. • External interference test as per Care recommendation. • Finally HW replacement. | RSSI TS Steps: • Clean or Remake Jumper connectors • Check any bending in the Jumper cable. • Confirm MHA HW is OK and Configuration is as per physical connectivity.(If available at site). • RET HW and Values as per design (If available at site). • Hard reset to equipment if values are stuck and not changing at all with above actions. • Sector Swap to check if value swapping to other sector or port. • External interference test as per Care recommendation. • Finally HW replacement. |  |  |  | API | 10/22/2025 13:15:26 | 10/22/2025 13:34:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000542 | PCM-20251022-00001268 | TT-20251022-01343 | EM | Region_6 | BAH1M7012 | BAH0012 |  |  |  | Arif Ullah Shah | 10/22/2025 13:16:44 | 10/22/2025 15:24:46 | 10/23/2025 01:16:44 | SHELTER DOOR OPEN at BAH1M7012-G9-L8-SBTS-P3 @ Sceco | 10/22/2025 13:16:22 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 13:16:16 | P3 | 4G | Albaha | Sceco | LTE NSA | BAH1M7012 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 13:16:44 | 10/22/2025 15:24:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000543 | PCM-20251022-00001272 | TT-20251022-01348 | EM | Region_6 | BHAB1M7817 | BHAB0817 |  |  |  | Muhammad Waqas Javed Tariq Javed | 10/22/2025 13:19:50 | 10/22/2025 15:00:48 | 10/23/2025 01:19:50 | AIRCON 2 FAILURE at BHAB1M7817-G9-L8-SBTS-P2 @ Sceco | 10/22/2025 13:11:32 | Minor | 7103 | AIRCON 2 FAILURE | 10/22/2025 13:11:25 | P1 | 4G | abha | Sceco | LTE NSA | BHAB1M7817 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/22/2025 13:19:50 | 10/22/2025 15:00:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000545 | PCM-20251022-00001275 | TT-20251022-01336 | EM | Region_5 | MAK0681 | MAK0681 |  |  |  | Husain Hassan Ishag Omer | 10/22/2025 13:20:05 | 10/23/2025 10:21:10 | 10/22/2025 19:20:05 | 1(2G/LTE/5G) sites down under MAK0681-P2/MAK0681-P2 @ Sceco | 10/22/2025 13:11:44 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 13:11:41 | P2 | 2G | makkah | Sceco | 2G SA | MAK0681-P2 | FLM_TE | MAK0681 | Results: DOWN SITE HUB MAK0681-P2 MAK0681 Summary: Hub: MAK0681, Down Count: 1, Down Sites: MAK0681-P2 Alarm Summary: MAK0681 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:20:05 | 10/23/2025 10:21:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000548 | PCM-20251022-00001281 | TT-20251022-01349 | Reference_telecom | Region_5 | MAK0203 | MAK0203 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 13:22:42 | 10/22/2025 13:22:42 | 10/22/2025 19:22:42 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at MAK0203-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HRM @ Sceco | 10/22/2025 13:15:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:14:58 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0203 | FLM_TE |  |  | PCM-20251022-00001273 | 1. Check if the ambient temperature or environmental conditions are within the designed limits of the radio module. When the ambient temperature or environmental conditions are out of limits, the alarm is expected and no further actions are needed. 2. Check if the airflow is not blocked by some objects. Make sure that the minimum thermal clearances are followed. Remove any objects that might be blocking the airflow, and mount the module according to instructions and recommendations. 3. Check if excessive sunlight might be causing overheating. Install the sun shield and follow the mounting instructions and recommendations. | 1. Check if the ambient temperature or environmental conditions are within the designed limits of the radio module. When the ambient temperature or environmental conditions are out of limits, the alarm is expected and no further actions are needed. 2. Check if the airflow is not blocked by some objects. Make sure that the minimum thermal clearances are followed. Remove any objects that might be blocking the airflow, and mount the module according to instructions and recommendations. 3. Check if excessive sunlight might be causing overheating. Install the sun shield and follow the mounting instructions and recommendations. |  |  |  | API | 10/22/2025 13:22:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000549 | PCM-20251022-00001285 | TT-20251022-01160 | Reference_telecom | Region_5 | MAK0391 | MAK0391 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 13:25:20 | 10/22/2025 13:25:20 | 10/22/2025 19:25:20 | BASE STATION SERVICE PROBLEM (Delay adjustment needed) at MAK0391-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP-HRM @ Sceco | 10/22/2025 11:36:40 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 11:36:31 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0391 | FLM_TE |  |  | PCM-20251022-00001099 | 1. Check if the ambient temperature or environmental conditions are within the designed limits of the radio module. When the ambient temperature or environmental conditions are out of limits, the alarm is expected and no further actions are needed. 2. Check if the airflow is not blocked by some objects. Make sure that the minimum thermal clearances are followed. Remove any objects that might be blocking the airflow, and mount the module according to instructions and recommendations. 3. Check if excessive sunlight might be causing overheating. Install the sun shield and follow the mounting instructions and recommendations. | 1. Check if the ambient temperature or environmental conditions are within the designed limits of the radio module. When the ambient temperature or environmental conditions are out of limits, the alarm is expected and no further actions are needed. 2. Check if the airflow is not blocked by some objects. Make sure that the minimum thermal clearances are followed. Remove any objects that might be blocking the airflow, and mount the module according to instructions and recommendations. 3. Check if excessive sunlight might be causing overheating. Install the sun shield and follow the mounting instructions and recommendations. |  |  |  | API | 10/22/2025 13:25:20 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000550 | PCM-20251022-00001293 | TT-20251022-01340 | Telecom | Region_2 | SRIY0230 | SRIY0230 |  |  |  | Majid Khan Arsalan Khan | 10/22/2025 13:26:56 | 10/23/2025 08:19:01 | 10/22/2025 17:26:56 | 2(3G) sites down under SRIY0230-P3,SRIY0231-P1-DIA/RY1RNCH05 @ Sceco | 10/22/2025 13:12:41 | Critical | 22214 | NodeB Unavailable | 10/22/2025 13:12:36 | P3 | SRAN | riyadh | Sceco | 3G SA | SRIY0231-P1-DIA 3G,SRIY0230-P3 3G | FLM_EM | SRIY0230 | Sites collocated Hub:- SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001277 | Sites collocated Hub:- SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Sites collocated Hub:- SRIY0230 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 13:26:56 | 10/23/2025 08:19:01 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000551 | PCM-20251022-00001295 | TT-20251022-01352 | Telecom | Region_4 | DOM1M3441 | DOM0441 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 13:27:31 | 10/23/2025 07:26:02 | 10/22/2025 19:27:31 | 1(3G) sites down under DOM0441-P2/DOM1M3441-P2 @ Sceco | 10/22/2025 13:19:41 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 13:19:02 | P2 | 3G | taif | Sceco | 3G SA | DOM0441-P2 | FLM_TE | DOM0441 | Results: DOWN SITE HUB DOM0441-P2 DOM0441 Summary: Hub: DOM0441, Down Count: 1, Down Sites: DOM0441-P2 Alarm Summary: DOM0441 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:27:31 | 10/23/2025 07:26:02 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000552 | PCM-20251022-00001297 | TT-20251022-01363 | EM | Region_4 | USF1M7694 | USF0694 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/22/2025 13:27:35 | 10/23/2025 22:25:39 | 10/23/2025 01:27:35 | HIGH TEMPERATURE 32 DEGREE C at USF1M7694-G9-L8-SBTS-P2-USF @ Sceco | 10/22/2025 13:19:18 | Minor | 7103 | HIGH TEMPERATURE 32 DEGREE C | 10/22/2025 13:19:06 | P3 | 4G | jeddah | Sceco | LTE NSA | USF1M7694 | FLM_EM | [5 empty] | HIGH TEMPERATURE 32 DEGREE C |  |  | API | 10/22/2025 13:27:35 | 10/23/2025 22:25:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000553 | PCM-20251022-00001300 | TT-20251022-01368 | Telecom | Region_1 | HFF6031 | HFF6031 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 13:28:38 | 10/22/2025 15:52:04 | 10/23/2025 01:28:38 | RF Unit Maintenance Link Failure at HFF6031-DCU2 @ Sceco | 10/22/2025 13:25:48 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 13:23:25 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6031 | FLM_TE | [8 empty] | API | 10/22/2025 13:28:38 | 10/22/2025 15:52:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000558 | PCM-20251022-00001313 | TT-20251022-01362 | Telecom | Region_5 | MAK0766 | MAK0766 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 13:32:32 | 10/22/2025 13:32:32 | 10/22/2025 17:32:32 | 1(5G) sites down under MAK0766-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM @ Sceco | 10/22/2025 13:24:06 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 13:24:03 | VIP | 2G | makkah | Sceco | 5G SA | MAK0766-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM | FLM_TE | MAK0766 | Results: DOWN SITE HUB MAK0766-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM MAK0766 Summary: Hub: MAK0766, Down Count: 1, Down Sites: MAK0766-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P1-VIP-HRM Alarm Summary: MAK0766 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.99.48.196:8080] [URL:http://10.99.48.196:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 13:32:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000559 | PCM-20251022-00001314 | TT-20251022-01365 | Telecom | Region_4 | TAF1M3160 | TAF0160 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 13:32:37 | 10/23/2025 07:26:03 | 10/22/2025 19:32:37 | 1(3G) sites down under TAF0160-P2/TAF1M3160-P2 @ Sceco | 10/22/2025 13:24:45 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 13:24:04 | P2 | 3G | taif | Sceco | 3G SA | TAF0160-P2 | FLM_TE | TAF0160 | Results: DOWN SITE HUB TAF0160-P2 TAF0160 Summary: Hub: TAF0160, Down Count: 1, Down Sites: TAF0160-P2 Alarm Summary: TAF0160 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:32:37 | 10/23/2025 07:26:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000561 | PCM-20251022-00001319 | TT-20251022-01383 | Telecom | Region_4 | TAF1M8453 | TAF2453 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 13:33:57 | 10/22/2025 17:30:06 | 10/23/2025 01:33:57 | PT:: FLM need to perform HC at 10 sites at TAIF region/R4 (BO request) | 10/22/2025 13:33:19 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 13:33:19 | P3 | 4G | jeddah | Sceco | 2G_3G_LTE_5G NSA | TAF1M8453-P3-CA-L800-P3 HAW1M7308-CA-L800-P3 HAW0300-G9-L8-L18-L21-NR2.6-SBTS-P2 HAW0293-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 TAF1M7168-NCA-L800-SBTS TAF1M8418-G9-L8-L18-L21-SBTS-P2 HAW1M8353-CA-L800-P1-VIP-ARP TAF0266-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB TAF1M7279-G9-L18-L21-SBTS-P2 TAF2388-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 | FLM_TE | [8 empty] | API | 10/22/2025 13:33:57 | 10/22/2025 17:30:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000562 | PCM-20251022-00001320 | TT-20251022-01360 | Reference_telecom | Region_5 | HDSH1M7366 | HDSH0366 | Equipment | SFP_BTS | Replace SFP | Inam ullah | 10/22/2025 13:34:54 | 10/23/2025 12:11:24 | 10/23/2025 01:34:54 | BASE STATION SERVICE PROBLEM (10b8b coding error in optical interface device) at HDSH1M7366-G9-NL8-L18-SBTS-P2-USF @ Sceco | 10/22/2025 13:21:57 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:21:51 | P2 | 4G | makkah | Sceco | 5G_Cell SA | HDSH1M7366 | FLM_TE |  |  | PCM-20251022-00001289 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/22/2025 13:34:54 | 10/23/2025 09:47:06 | 10/23/2025 09:48:03 | 10/23/2025 09:48:19 | 10/23/2025 11:20:57 | 10/23/2025 12:11:24 |  | Inam ullah |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000564 | PCM-20251022-00001326 | TT-20251022-01378 | EM | Region_1 | HFF2M2365 | HFF2365 |  |  |  | Moustafa Mohamed Saleh Saif | 10/22/2025 13:37:33 | 10/23/2025 01:46:25 | 10/22/2025 19:37:33 | 1(2G/3G/LTE) sites down under HFF2365-P2/R1_HF_HWBSC01 @ Sceco | 10/22/2025 13:30:34 | Major | 21825 | CSL Fault | 10/22/2025 13:30:34 | P2 | 2G | hafouf | Sceco | 2G_3G_LTE SA | HFF2365-P2 | FLM_EM | HFF2365 | Results: DOWN SITE HUB HFF2365-P2 HFF2365 Summary: Hub: HFF2365, Down Count: 1, Down Sites: HFF2365-P2 Alarm Summary: HFF2365 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:37:33 | 10/23/2025 01:46:25 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000566 | PCM-20251022-00001329 | TT-20251022-01399 | Telecom | Region_2 | RAS2248 | RAS2248 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Syed Sibtain Naqvi SyedManzoor | 10/22/2025 13:38:26 | 10/22/2025 20:01:21 | 10/23/2025 01:38:26 | ALD Maintenance Link Failure at RAS2248-FWA-P1-VIP_SRAN @ Sceco | 10/22/2025 13:35:44 | Minor | 26541 | ALD Maintenance Link Failure | 10/22/2025 13:34:09 | P2 | SRAN | al rass | Sceco | 2G NSA | RAS2248 | FLM_TE | [8 empty] | API | 10/22/2025 13:38:26 | 10/22/2025 14:54:10 | 10/22/2025 18:40:32 | 10/22/2025 18:40:35 | 10/22/2025 19:23:16 | 10/22/2025 20:01:21 |  | Syed Sibtain Naqvi SyedManzoor |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000567 | PCM-20251022-00001331 | TT-20251022-01388 | Telecom | Region_3 | YNB2M3667 | YNB0667 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Sajjad R3 | 10/22/2025 13:39:11 | 10/23/2025 19:27:08 | 10/23/2025 01:39:11 | Inter-System Communication Failure at YNB2M3667-P2 @ Sceco | 10/22/2025 13:30:33 | Minor | 26270 | Inter-System Communication Failure | 10/22/2025 13:28:55 | P2 | 3G | yanbu | Sceco | 3G NSA | YNB2M3667 | FLM_TE |  | Dears Kindly check locally as NE down | PCM-20251022-00001323 | Dears Kindly check locally as NE down | Dears Kindly check locally as NE down |  |  |  | API | 10/22/2025 13:39:11 | 10/22/2025 17:27:06 | 10/23/2025 19:27:01 |  |  | 10/23/2025 19:27:08 |  | Muhammad Sajjad R3 |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000568 | PCM-20251022-00001332 | TT-20251022-01403 | Telecom | Region_6 | KMS0351 | KMS0351 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/22/2025 13:39:28 | 10/22/2025 19:49:09 | 10/22/2025 19:39:28 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS0351-CA-L800-NR2.6-P3 @ Generator_SG | 10/22/2025 13:38:23 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:38:17 | P3 | 2G | khamis mushyet | Generator_SG | 5G_Cell SA | KMS0351 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 13:39:28 | 10/22/2025 14:52:27 | 10/22/2025 14:52:36 | 10/22/2025 14:52:40 |  | 10/22/2025 19:49:09 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000570 | PCM-20251022-00001342 | TT-20251022-01391 | EM | Region_6 | TNM2221 | TNM2221 |  |  |  | Zia Ur Rahamn | 10/22/2025 13:42:03 | 10/22/2025 17:31:21 | 10/22/2025 19:42:03 | 1(2G/LTE) sites down under TNM2221-P3/TNM2221-P3 @ Generator_SG | 10/22/2025 13:33:38 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 13:33:35 | P3 | 2G | mohail | Generator_SG | 2G_LTE SA | TNM2221-P3 | FLM_EM | TNM2221 | Results: DOWN SITE HUB TNM2221-P3 TNM2221 Summary: Hub: TNM2221, Down Count: 1, Down Sites: TNM2221-P3 Alarm Summary: TNM2221 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:42:03 | 10/22/2025 17:31:21 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000571 | PCM-20251022-00001344 | TT-20251022-01393 | EM | Region_6 | BHAB0832 | BHAB0832 |  |  |  | Zia Ur Rahamn | 10/22/2025 13:42:21 | 10/22/2025 17:31:22 | 10/22/2025 19:42:21 | 1(2G/3G/5G) sites down under BHAB0832-P3/BHAB0832-P3 @ Sceco | 10/22/2025 13:34:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 13:34:24 | P3 | 2G | mohail | Sceco | 2G_3G_5G SA | BHAB0832-P3 | FLM_EM | BHAB0832 | Results: DOWN SITE HUB BHAB0832-P3 BHAB0832 Summary: Hub: BHAB0832, Down Count: 1, Down Sites: BHAB0832-P3 Alarm Summary: BHAB0832 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 13:42:21 | 10/22/2025 17:31:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251022000572 | PCM-20251022-00001345 | TT-20251022-01394 | Telecom | Region_4 | JED1MN2666 | JED2666 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 13:42:32 | 10/22/2025 20:45:24 | 10/22/2025 19:42:32 | 1(5G) sites down under JED2666-NR2.6-P3 @ Sceco | 10/22/2025 13:34:27 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 13:34:24 | P3 | 5G | jeddah | Sceco | 5G SA | JED2666-NR2.6-P3 | FLM_TE | JED2666 | Results: DOWN SITE HUB JED2666-NR2.6-P3 JED2666 Summary: Hub: JED2666, Down Count: 1, Down Sites: JED2666-NR2.6-P3 Alarm Summary: JED2666 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.97.35.236:8080] [URL:http://10.97.35.236:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 13:42:32 | 10/22/2025 14:59:40 | 10/22/2025 20:09:11 | 10/22/2025 20:44:49 | 10/22/2025 20:45:24 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000573 | PCM-20251022-00001346 | TT-20251022-01412 | Telecom | Region_5 | OMQ0633 | OMQ0633 |  |  |  | Amjad Ali Muhammad Parves | 10/22/2025 13:43:36 | 10/22/2025 14:25:06 | 10/22/2025 19:43:36 | BASE STATION SERVICE PROBLEM (No connection to unit) at OMQ0633-GSM-P2-USF @ Generator_SG | 10/22/2025 13:42:43 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:42:33 | P2 | 2G | makkah | Generator_SG | 5G_Cell SA | OMQ0633 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 13:43:36 | 10/22/2025 14:25:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000574 | PCM-20251022-00001348 | TT-20251022-01414 | Telecom | Region_6 | TLM1M8248 | TLM2248 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamal Khan Abbas Ali | 10/22/2025 13:44:44 | 10/22/2025 19:45:43 | 10/22/2025 19:44:44 | PT::: As Per BO request need FLM to do HC in TLM1M8248/R6 | 10/22/2025 13:44:24 | Major | 7100 | BASE STATION HARDWARE PROBLEM | 10/22/2025 13:44:24 | P3 | 4G | mohail | Sceco | 2G_3G_LTE_5G NSA | TLM1M8248 | FLM_TE | [8 empty] | API | 10/22/2025 13:44:44 | 10/22/2025 16:48:45 | 10/22/2025 18:10:43 | 10/22/2025 18:11:16 | 10/22/2025 18:36:19 | 10/22/2025 19:45:43 |  | Muhammad Jamal Khan Abbas Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000575 | PCM-20251022-00001354 | TT-20251022-01417 | Telecom | Region_1 | HFF6029 | HFF6029 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 13:45:40 | 10/22/2025 15:58:38 | 10/22/2025 19:45:40 | DCU CPRI Interface Error at HFF6029-DCU1 @ Sceco | 10/22/2025 13:39:41 | Major | 26234 | DCU CPRI Interface Error | 10/22/2025 13:38:43 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6029 | FLM_TE | [8 empty] | API | 10/22/2025 13:45:40 | 10/22/2025 15:52:05 | 10/22/2025 15:58:22 |  |  | 10/22/2025 15:58:38 |  | Shakeel Ahmad Ghulam Murtaza |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000577 | PCM-20251022-00001357 | TT-20251022-01410 | EM | Region_3 | RUSF9013 | RUSF9013 |  |  |  | Yasser Mohamed Mohamed Yousef | 10/22/2025 13:47:03 | 10/22/2025 13:47:03 | 10/23/2025 01:47:03 | NETECO: Under Fuel Level at RUSF9013 @ Generator_SG | 10/22/2025 13:35:53 | Minor | 301 | Under Fuel Level | 10/22/2025 13:35:53 | P3 | Repeater | yanbu | Generator_SG | 2G NSA | RUSF9013 | FLM_EM | RUSF9013 | Results: DOWN SITE HUB RUSF9013 RUSF9013 Summary: Hub: RUSF9013, Down Count: 1, Down Sites: RUSF9013 Alarm Summary: RUSF9013 No Active Alarm on HUB | [6 empty] | API | 10/22/2025 13:47:03 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000578 | PCM-20251022-00001358 | TT-20251022-01419 | EM | Region_3 | WFR2277 | WFR2277 |  |  |  | Muhammad arshad Anwar | 10/22/2025 13:47:13 | 10/22/2025 13:47:13 | 10/23/2025 01:47:13 | NETECO: Door Status Sensor Alarm at WFR2277 @ Generator_DG | 10/22/2025 13:46:34 | Minor | 5152 | Door Status Sensor Alarm | 10/22/2025 13:46:34 | P3 | SRAN | madinah | Generator_DG | 2G NSA | WFR2277 | FLM_EM | [8 empty] | API | 10/22/2025 13:47:13 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000579 | PCM-20251022-00001360 | TT-20251022-01421 | Reference_EM | Region_3 | WFR2277 | WFR2277 |  |  |  | Muhammad arshad Anwar | 10/22/2025 13:47:14 | 10/22/2025 13:47:14 | 10/23/2025 01:47:14 | Door opening alarm at WFR2277-P3_SRAN @ Generator_DG | 10/22/2025 13:46:41 | Minor | 65101 | Door opening alarm | 10/22/2025 13:46:38 | P3 | SRAN | madinah | Generator_DG | 2G NSA | WFR2277 | FLM_EM | [8 empty] | API | 10/22/2025 13:47:14 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000580 | PCM-20251022-00001361 | TT-20251022-01411 | Telecom | Region_5 | MAK0763 | MAK0763 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 13:47:31 | 10/22/2025 13:47:31 | 10/22/2025 17:47:31 | 1(5G) sites down under MAK0763-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HRM @ Sceco | 10/22/2025 13:39:21 | Critical | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 13:39:17 | VIP | 2G | makkah | Sceco | 5G SA | MAK0763-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HRM | FLM_TE | MAK0763 | Results: DOWN SITE HUB MAK0763-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HRM MAK0763 Summary: Hub: MAK0763, Down Count: 1, Down Sites: MAK0763-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HRM Alarm Summary: MAK0763 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.99.56.28:8080] [URL:http://10.99.56.28:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 13:47:31 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000583 | PCM-20251022-00001365 | TT-20251022-01425 | Reference_telecom | Region_4 | JED0404 | JED0404 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 13:48:16 | 10/22/2025 14:59:40 | 10/23/2025 01:48:16 | Degrade observed in JED0404 towards 10.10.185.251 @ Generator_SG | 10/22/2025 01:48:35 | Minor |  | Degrade | 10/22/2025 01:48:02 | P2 | 2G | jeddah | Generator_SG | TX NSA | JED0404 | FLM_TE | [8 empty] | API | 10/22/2025 13:48:16 | 10/22/2025 14:59:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251022000584 | PCM-20251022-00001367 | TT-20251022-01428 | Reference_telecom | Region_5 | MAK2246 | MAK2246 |  |  |  | Husain Hassan Ishag Omer | 10/22/2025 13:48:45 | 10/23/2025 13:28:38 | 10/23/2025 01:48:45 | Degrade observed in MAK2246 towards 10.10.139.242 @ Sceco | 10/22/2025 01:48:42 | Minor |  | Degrade | 10/22/2025 01:48:23 | P3 | 2G | makkah | Sceco | TX NSA | MAK2246 | FLM_TE | [8 empty] | API | 10/22/2025 13:48:45 | 10/23/2025 13:28:17 | 10/23/2025 13:28:26 | 10/23/2025 13:28:34 | 10/23/2025 13:28:38 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000585 | PCM-20251022-00001368 | TT-20251022-01430 | Telecom | Region_4 | JED2350 | JED2350 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 13:48:46 | 10/22/2025 13:48:46 | 10/23/2025 01:48:46 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED2350-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3-FON @ Sceco | 10/22/2025 13:47:59 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:47:54 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED2350 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 13:48:46 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000586 | PCM-20251022-00001373 | TT-20251022-01374 | Reference_telecom | Region_5 | MAK0319 | MAK0319 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 13:52:04 | 10/22/2025 13:52:04 | 10/22/2025 19:52:04 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at MAK0319-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HAJJ-HRM @ Sceco | 10/22/2025 13:26:37 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:26:30 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0319 | FLM_TE |  |  | PCM-20251022-00001308 | FLM need to check HW and perform HC at site. | FLM need to check HW and perform HC at site. |  |  |  | API | 10/22/2025 13:52:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000588 | PCM-20251022-00001375 | TT-20251022-01439 | Telecom | Region_6 | ABH1M7188 | ABH0188 | Equipment | SFP_BTS | Replace SFP | Muhammad Jamshaid Muhammad Ashraf | 10/22/2025 13:52:54 | 10/22/2025 16:48:05 | 10/22/2025 19:52:54 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH1M7188-P3-L800 @ Sceco | 10/22/2025 13:52:02 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 13:51:52 | P3 | 4G | abha | Sceco | 5G_Cell SA | ABH1M7188 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 13:52:54 | 10/22/2025 14:33:05 | 10/22/2025 16:47:53 |  |  | 10/22/2025 16:48:05 |  | Muhammad Jamshaid Muhammad Ashraf |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000601 | PCM-20251022-00001411 | TT-20251022-01152 | EM | Region_2 | RIY2503 | RIY2503 | Equipment | PMR_Power_Cable_RRU | Replace Outdoor Power Connector | Farmanullah Akbar Jan | 10/22/2025 14:03:05 | 10/22/2025 14:11:24 | 10/22/2025 20:03:05 | 1(2G/LTE) sites down under RIY2503-P3/R2_RY3_HWBSC01 @ Sceco | 10/22/2025 11:35:45 | Major | 21825 | CSL Fault | 10/22/2025 11:35:43 | P3 | SRAN | riyadh | Sceco | 2G_LTE SA | RIY2503-P3 | FLM_TE | RIY2503 | Hub : RIY2503 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. | PCM-20251022-00001383 | Hub : RIY2503 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. | Hub : RIY2503 We are observing ETH_LOS alarm active , kindly visit the site and check the issue. |  | sites down |  | API | 10/22/2025 14:03:05 | 10/22/2025 14:10:04 | 10/22/2025 14:10:38 |  |  | 10/22/2025 14:11:24 |  | Farmanullah Akbar Jan |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000602 | PCM-20251022-00001415 | TT-20251022-01369 | Telecom | [7 empty] | 10/22/2025 14:05:49 | 10/22/2025 14:05:49 | 10/23/2025 02:05:49 | WHRJ0001 is complete down | 10/22/2025 13:20:20 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 13:20:20 | P3 | WIFI |  | Sceco | Wifi SA | WHRJ0001 | FLM_EM |  |  | PCM-20251022-00001302 | HRJ0089 | HRJ0089 |  |  |  | API | 10/22/2025 14:05:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000604 | PCM-20251022-00001418 | TT-20251022-01473 | Telecom | Region_2 | RIY2328 | RIY2328 | Equipment | SFP_BTS | Clean SFP | Khan zeb Shah nawaz | 10/22/2025 14:06:20 | 10/22/2025 14:43:35 | 10/22/2025 20:06:20 | BBU CPRI Interface Error at RIY2328-P2_SRAN @ Generator_SG | 10/22/2025 14:01:58 | Major | 26234 | BBU CPRI Interface Error | 10/22/2025 13:59:25 | P2 | SRAN | riyadh | Generator_SG | 2G NSA | RIY2328 | FLM_TE | [8 empty] | API | 10/22/2025 14:06:20 | 10/22/2025 14:41:52 | 10/22/2025 14:42:58 |  |  | 10/22/2025 14:43:35 |  | Khan zeb Shah nawaz |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000605 | PCM-20251022-00001420 | TT-20251022-01379 | Telecom | [7 empty] | 10/22/2025 14:07:10 | 10/22/2025 14:07:10 | 10/23/2025 02:07:10 | WJIZ0008 is complete down | 10/22/2025 13:27:20 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 13:27:20 | P3 | WIFI |  | Sceco | Wifi SA | WJIZ0008 | FLM_EM |  |  | PCM-20251022-00001316 | JIZ0091 | JIZ0091 |  |  |  | API | 10/22/2025 14:07:10 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000606 | PCM-20251022-00001422 | TT-20251022-01468 | EM | Region_4 | MKYL1M3916 | MKYL0916 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 14:08:01 | 10/23/2025 09:20:51 | 10/22/2025 20:08:01 | 1(2G/3G) sites down under MKYL0916-P3/MKYL1M3916-P3 @ Generator_SG | 10/22/2025 14:00:15 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 13:59:36 | P3 | 3G | alaith | Generator_SG | 3G SA | MKYL0916-P3 | FLM_TE | MKYL0916 | Results: DOWN SITE HUB MKYL0916-P3 MKYL0916 Summary: Hub: MKYL0916, Down Count: 1, Down Sites: MKYL0916-P3 Alarm Summary: MKYL0916 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 14:08:01 | 10/23/2025 09:20:51 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000609 | PCM-20251022-00001425 | TT-20251022-01435 | Telecom | Region_5 | MAK0235 | MAK0235 |  |  |  | Husain Hassan Ishag Omer | 10/22/2025 14:08:47 | 10/23/2025 10:21:10 | 10/22/2025 18:08:47 | 3(2G) 3(5G) sites down under MAK0235-P1-HUB-WDM-USF-FON,MAK0677-P3,MAK2136-P3/MAK2136-P3 @ Sceco | 10/22/2025 13:48:19 | Critical | 7706 | BTS O&M LINK FAILURE | 10/22/2025 13:48:17 | P1 | 2G | makkah | Sceco | 2G_5G SA | MAK0235-P1-HUB-WDM-USF-FON 2G_5G,MAK0677-P3 2G_5G,MAK2136-P3 2G_5G | FLM_TE | MAK0235 | Results: DOWN SITE HUB MAK0235-P1-HUB-WDM-USF-FON MAK0235 MAK0677-P3 MAK0235 MAK2136-P3 MAK0235 Summary: Hub: MAK0235, Down Count: 3, Down Sites: MAK0235-P1-HUB-WDM-USF-FON, MAK0677-P3, MAK2136-P3 Alarm Summary: MAK0235 Alarm Active on HUB | PCM-20251022-00001409 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 14:08:47 | 10/23/2025 10:21:10 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000610 | PCM-20251022-00001426 | TT-20251022-01481 | Telecom | Region_6 | TFBH0887-LL-CSG-01 | TFBH0887 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/22/2025 14:08:55 | 10/22/2025 18:02:22 | 10/23/2025 02:08:55 | Bad Package Error Rising at TFBH0887-LL-CSG-01 @ Sceco_STB | 10/22/2025 14:08:41 | Minor | 101-2501403 | Bad Package Error Rising | 10/22/2025 14:08:34 | P3 | IPRAN | makhwa | Sceco_STB | IPRAN NSA | TFBH0887-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 14:08:55 | 10/22/2025 14:32:07 | 10/22/2025 18:01:54 |  |  | 10/22/2025 18:02:22 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000612 | PCM-20251022-00001428 | TT-20251022-01482 | EM | Region_1 | HLHD0705 | HLHD0705 |  |  |  | Ibrahim Khaled Shendy Khaled | 10/22/2025 14:09:57 | 10/22/2025 20:15:29 | 10/23/2025 02:09:57 | NETECO: Door Open Alarm at HLHD0705 @ Generator_SG | 10/22/2025 14:09:22 | Minor | 5152 | Door Open Alarm | 10/22/2025 14:09:22 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0705 | FLM_EM | [8 empty] | API | 10/22/2025 14:09:57 | 10/22/2025 20:15:29 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000613 | PCM-20251022-00001429 | TT-20251022-01483 | EM | Region_6 | TNM1M8221 | TNM2221 |  |  |  | Zia Ur Rahamn | 10/22/2025 14:09:57 | 10/22/2025 17:31:22 | 10/23/2025 02:09:57 | SHELTER DOOR OPEN at TNM1M8221-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/22/2025 14:09:40 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 14:09:27 | P3 | 4G | mohail | Generator_SG | LTE NSA | TNM1M8221 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 14:09:57 | 10/22/2025 17:31:22 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000616 | PCM-20251022-00001432 | TT-20251022-01484 | Reference_EM | Region_3 | SML2332 | SML2332 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/22/2025 14:10:28 | 10/22/2025 16:40:46 | 10/23/2025 02:10:28 | Door opening alarm at SML2332-P3-USF_SRAN @ Generator_SG | 10/22/2025 14:10:20 | Minor | 65101 | Door opening alarm | 10/22/2025 14:10:15 | P3 | SRAN | hail | Generator_SG | 2G NSA | SML2332 | FLM_EM | [8 empty] | API | 10/22/2025 14:10:28 | 10/22/2025 16:40:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000617 | PCM-20251022-00001433 | TT-20251022-01471 | EM | Region_4 | JED0320 | JED0320 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 14:11:03 | 10/22/2025 21:33:37 | 10/22/2025 20:11:03 | 1(2G/5G) sites down under JED0320-P2/JED0320-P2 @ Sceco | 10/22/2025 14:03:00 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 14:02:53 | P2 | 2G | jeddah | Sceco | 2G SA | JED0320-P2 | FLM_TE | JED0320 | Results: DOWN SITE HUB JED0320-P2 JED0320 Summary: Hub: JED0320, Down Count: 1, Down Sites: JED0320-P2 Alarm Summary: JED0320 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 14:11:03 | 10/22/2025 14:59:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000620 | PCM-20251022-00001436 | TT-20251022-01476 | Telecom | Region_1 | DAM2M4178 | DAM2178 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/22/2025 14:12:02 | 10/22/2025 15:33:59 | 10/22/2025 20:12:02 | Violation of Degradation Mentioned in RFC 1(3G) sites down under DAM2178-P2/DM1RNC01 @ Sceco (ref:CRQ000000536765) | 10/22/2025 14:03:50 | Major | 22214 | NodeB Unavailable | 10/22/2025 14:03:39 | P2 | 3G | dammam | Sceco | 3G SA | DAM2178-P2 | FLM_TE | DAM2178 | Results: DOWN SITE HUB DAM2178-P2 DAM2178 Summary: Hub: DAM2178, Down Count: 1, Down Sites: DAM2178-P2 Alarm Summary: DAM2178 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 14:12:02 | 10/22/2025 14:17:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000621 | PCM-20251022-00001437 | TT-20251022-01487 | Telecom | Region_4 | JED1MN0650 | JED0650 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 14:13:04 | 10/22/2025 14:13:04 | 10/22/2025 20:13:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0650-NR2.6-P2 @ Sceco | 10/22/2025 14:12:14 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:12:03 | P2 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0650 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 14:13:04 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000622 | PCM-20251022-00001438 | TT-20251022-01489 | EM | Region_4 | USF1M7694 | USF0694 |  |  |  | Muhammad Masoof Zafar Mehmood | 10/22/2025 14:13:34 | 10/23/2025 22:25:39 | 10/23/2025 02:13:34 | SHELTER DOOR OPEN at USF1M7694-G9-L8-SBTS-P2-USF @ Sceco | 10/22/2025 14:13:08 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 14:12:59 | P3 | 4G | jeddah | Sceco | LTE NSA | USF1M7694 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 14:13:34 | 10/23/2025 22:25:39 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000624 | PCM-20251022-00001441 | TT-20251022-01492 | EM | Region_1 | KFKM0788 | KFKM0788 | Equipment | Jumper_Cable | Reconnect Indoor Jumper Cable | Mahmoud Youssef Mohamed Ahmed | 10/22/2025 14:15:37 | 10/23/2025 20:02:39 | 10/23/2025 02:15:37 | NETECO: Door Open Alarm at KFKM0788 @ Generator_SG | 10/22/2025 14:15:03 | Minor | 5152 | Door Open Alarm | 10/22/2025 14:15:03 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0788 | FLM_EM | [8 empty] | API | 10/22/2025 14:15:37 | 10/22/2025 20:56:26 | 10/23/2025 20:02:21 |  |  | 10/23/2025 20:02:39 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000625 | PCM-20251022-00001443 | TT-20251022-01495 | Reference_EM | Region_2 | RIY2866 | RIY2866 |  |  |  | Tanveer Ahmad Fateh Muhammad | 10/22/2025 14:17:42 | 10/22/2025 14:41:09 | 10/23/2025 02:17:42 | Door opening alarm at RIY2866-P3_SRAN-PC @ Sceco | 10/22/2025 14:17:17 | Minor | 65101 | Door opening alarm | 10/22/2025 14:17:12 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2866 | FLM_EM | [8 empty] | API | 10/22/2025 14:17:42 | 10/22/2025 14:41:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000626 | PCM-20251022-00001445 | TT-20251022-01497 | Telecom | Region_1 | HFF0052 | HFF0052 |  |  |  | Mohamed Magdy Fouad Zayed | 10/22/2025 14:17:43 | 10/22/2025 18:15:56 | 10/22/2025 20:17:43 | BBU CPRI Interface Error at HFF0052-P2_SRAN @ Sceco | 10/22/2025 14:13:04 | Major | 26234 | BBU CPRI Interface Error | 10/22/2025 14:10:32 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0052 | FLM_TE | [8 empty] | API | 10/22/2025 14:17:43 | 10/22/2025 18:15:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000628 | PCM-20251022-00001447 | TT-20251022-01500 | Telecom | Region_1 | HFF2M7052 | HFF0052 |  |  |  | Mohamed Magdy Fouad Zayed | 10/22/2025 14:18:17 | 10/22/2025 18:15:56 | 10/22/2025 20:18:17 | Cell Unavailable at HFF2M7052-P2-L800 @ Sceco | 10/22/2025 14:11:37 | Major | 29240 | Cell Unavailable | 10/22/2025 14:10:44 | P2 | 4G | hafouf | Sceco | LTE SA | HFF2M7052 | FLM_TE | [8 empty] | API | 10/22/2025 14:18:17 | 10/22/2025 18:15:56 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000629 | PCM-20251022-00001451 | TT-20251022-01503 | EM | Region_1 | HLHD0707 | HLHD0707 |  |  |  | Ibrahim Khaled Shendy Khaled | 10/22/2025 14:20:47 | 10/22/2025 20:15:30 | 10/23/2025 02:20:47 | NETECO: Door Open Alarm at HLHD0707 @ Generator_SG | 10/22/2025 14:20:29 | Minor | 5152 | Door Open Alarm | 10/22/2025 14:20:29 | P3 | SRAN | rafha | Generator_SG | 2G NSA | HLHD0707 | FLM_EM | [8 empty] | API | 10/22/2025 14:20:47 | 10/22/2025 20:15:30 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000630 | PCM-20251022-00001452 | TT-20251022-01504 | Telecom | Region_4 | DAF1M7470 | DAF0470 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Nazeer Mohammed | 10/22/2025 14:20:48 | 10/22/2025 16:25:51 | 10/23/2025 02:20:48 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAF1M7470-P2-CA-L800-SBTS @ Sceco | 10/22/2025 14:20:09 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:20:02 | P2 | 4G | jeddah | Sceco | 5G_Cell SA | DAF1M7470 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 14:20:48 | 10/22/2025 16:25:26 | 10/22/2025 16:25:46 |  |  | 10/22/2025 16:25:51 |  | Nazeer Mohammed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000631 | PCM-20251022-00001453 | TT-20251022-01314 | EM | Region_6 | NJR0777 | NJR0777 | Transsmission | SFP_Transmission | Replace SFP | TALEH MUHAMMAD | 10/22/2025 14:22:04 | 10/22/2025 15:46:08 | 10/22/2025 20:22:04 | 1(2G/LTE) sites down under NJR0777-P3/NJR0777-P3 @ Sceco | 10/22/2025 13:03:04 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 13:03:01 | P3 | 2G | najran | Sceco | 2G_LTE SA | NJR0777-P3 | FLM_TE | NJR0777 | Results: DOWN SITE HUB NJR0777-P3 NJR0777 Summary: Hub: NJR0777, Down Count: 1, Down Sites: NJR0777-P3 Alarm Summary: NJR0777 Alarm Active on HUB | PCM-20251022-00001248 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 14:22:04 | 10/22/2025 15:26:04 | 10/22/2025 15:45:31 |  |  | 10/22/2025 15:46:08 |  | TALEH MUHAMMAD |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000632 | PCM-20251022-00001455 | TT-20251022-01499 | Reference_telecom | Region_2 | RIYB2U6786 | RIYB6086 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/22/2025 14:22:47 | 10/22/2025 14:22:47 | 10/23/2025 02:22:47 | Cell RX Channel Interference Noise Power Unbalanced at RIYB2U6786-L1800-CA-P3 @ Sceco | 10/22/2025 11:17:44 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/22/2025 11:17:41 | P3 | 4G | riyadh | Sceco | 2G NSA | RIYB2U6786 | FLM_TE |  | Dears kindly check HW | PCM-20251022-00001446 | Dears kindly check HW | Dears kindly check HW |  |  |  | API | 10/22/2025 14:22:47 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000635 | PCM-20251022-00001462 | TT-20251022-01512 | Telecom | Region_5 | MAK0991 | MAK0991 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 14:26:51 | 10/22/2025 14:26:51 | 10/22/2025 20:26:51 | BCCH missing under MAK0991-P1-VIP-HRM | 10/22/2025 14:23:22 | Major | 7767 | BCCH MISSING | 10/22/2025 14:23:22 | VIP | 2G | makkah | Sceco | 2G SA | MAK0991-P1-VIP-HRM | FLM_TE | [8 empty] | API | 10/22/2025 14:26:51 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000636 | PCM-20251022-00001466 | TT-20251022-01516 | Reference_EM | Region_1 | HMBY2984 | HMBY2984 |  |  |  | Abdul Malik Shaik | 10/22/2025 14:28:33 | 10/22/2025 21:43:59 | 10/23/2025 02:28:33 | Door opening alarm at HMBY2984-P3_SRAN @ Sceco | 10/22/2025 14:28:17 | Minor | 65101 | Door opening alarm | 10/22/2025 14:28:14 | P3 | SRAN | dammam | Sceco | 2G NSA | HMBY2984 | FLM_EM | [8 empty] | API | 10/22/2025 14:28:33 | 10/22/2025 21:43:59 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000637 | PCM-20251022-00001467 | TT-20251022-01491 | Telecom | Region_5 | WMKJD0001 | WMKJD0001 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 14:29:18 | 10/22/2025 15:48:03 | 10/23/2025 02:29:18 | WMKJD0001 is complete down | 10/22/2025 14:03:34 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 14:03:34 | P3 | WIFI | makkah | Sceco | Wifi SA | WMKJD0001 | FLM_TE | WMKJD0001 |  | PCM-20251022-00001440 | WMKJD0001 | WMKJD0001 |  |  |  | API | 10/22/2025 14:29:18 | 10/22/2025 15:48:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000640 | PCM-20251022-00001471 | TT-20251022-01490 | Telecom | Region_6 | BHAB2091 | BHAB2091 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 14:32:17 | 10/22/2025 18:29:48 | 10/22/2025 20:32:17 | 2(2G) 2(LTE) sites down under BHAB2103-P3,BHAB2091-P3/BHAB2091-P3 @ Generator_SG | 10/22/2025 14:11:25 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 14:11:20 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | BHAB2103-P3 2G_LTE,BHAB2091-P3 2G_LTE | FLM_EM | BHAB2091 | Results: DOWN SITE HUB BHAB2103-P3 BHAB2103 BHAB2091-P3 BHAB2091 Summary: Hub: BHAB2103, Down Count: 1, Down Sites: BHAB2103-P3 Hub: BHAB2091, Down Count: 1, Down Sites: BHAB2091-P3 Alarm Summary: BHAB2103 Alarm Active on HUB BHAB2091 Alarm Active on HUB | PCM-20251022-00001449 | BHAB2091 | BHAB2091 |  | sites down |  | API | 10/22/2025 14:32:17 | 10/22/2025 18:29:48 | [9 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251022000641 | PCM-20251022-00001472 | TT-20251022-01521 | Telecom | Region_6 | ABH0161 | ABH0161 |  |  |  | Amir Sohail | 10/22/2025 14:33:13 | 10/22/2025 18:17:56 | 10/22/2025 20:33:13 | BD_NOT_INSTALLED at ABH0161-OCS1 @ Sceco_STB | 10/22/2025 14:29:27 | Major | 1-625 | BD_NOT_INSTALLED | 10/22/2025 14:29:22 | P1 | 2G | abha | Sceco_STB | DWDM NSA | ABH0161 | FLM_TE | [5 empty] | - |  |  | API | 10/22/2025 14:33:13 | 10/22/2025 14:50:01 | 10/22/2025 18:17:56 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000643 | PCM-20251022-00001478 | TT-20251022-01525 | Telecom | Region_6 | JIZ0090 | JIZ0090 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/22/2025 14:36:49 | 10/22/2025 17:35:08 | 10/23/2025 02:36:49 | BASE STATION SERVICE PROBLEM (No connection to unit) at JIZ0090-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/22/2025 14:35:54 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:35:43 | P3 | 2G | jizan | Sceco | 5G_Cell SA | JIZ0090 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 14:36:49 | 10/22/2025 17:34:42 | 10/22/2025 17:34:55 |  |  | 10/22/2025 17:35:08 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000644 | PCM-20251022-00001480 | TT-20251022-01527 | Telecom | Region_6 | ABBS1M7150 | ABBS0150 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/22/2025 14:42:30 | 10/23/2025 16:22:06 | 10/23/2025 02:42:30 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABBS1M7150-P3-NCA-L800-SBTS-WBB-G3 @ Sceco | 10/22/2025 14:41:24 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:41:14 | P3 | 4G | Albaha | Sceco | 5G_Cell SA | ABBS1M7150 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 14:42:30 | 10/22/2025 14:44:24 | 10/23/2025 16:21:57 |  |  | 10/23/2025 16:22:06 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000645 | PCM-20251022-00001483 | TT-20251021-02569 | Telecom | Region_6 | KMS1M7056 | KMS0056 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/22/2025 14:43:44 | 10/22/2025 19:35:42 | 10/23/2025 02:43:44 | BASE STATION CONNECTIVITY PROBLEM (Inter-Site CA link establishment failure) at KMS1M7056-G9-L18-L21-SBTS-P2 @ Sceco | 10/21/2025 23:28:07 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 23:21:03 | P2 | 4G | khamis mushyet | Sceco | LTE NSA | KMS1M7056 | FLM_TE |  |  | PCM-20251022-00001352 | FLM need to check HW Module ,SFP and Optical Cable on the site | FLM need to check HW Module ,SFP and Optical Cable on the site |  |  |  | API | 10/22/2025 14:43:44 | 10/22/2025 15:18:37 | 10/22/2025 19:35:29 |  |  | 10/22/2025 19:35:42 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000646 | PCM-20251022-00001484 | TT-20251022-01530 | Telecom | Region_1 | HFF6031 | HFF6031 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 14:44:04 | 10/22/2025 15:52:05 | 10/22/2025 20:44:04 | DCU CPRI Interface Error at HFF6031-DCU2 @ Sceco | 10/22/2025 14:39:49 | Major | 26234 | DCU CPRI Interface Error | 10/22/2025 14:36:57 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6031 | FLM_TE | [8 empty] | API | 10/22/2025 14:44:04 | 10/22/2025 15:52:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000647 | PCM-20251022-00001486 | TT-20251022-01531 | Telecom | Region_1 | HFF6031 | HFF6031 |  |  |  | Shakeel Ahmad Ghulam Murtaza | 10/22/2025 14:44:35 | 10/22/2025 15:52:06 | 10/23/2025 02:44:35 | RF Unit Clock Problem at HFF6031-DCU2 @ Sceco | 10/22/2025 14:39:04 | Minor | 26538 | RF Unit Clock Problem | 10/22/2025 14:36:13 | P3 | SRAN | hafouf | Sceco | 2G NSA | HFF6031 | FLM_TE | [8 empty] | API | 10/22/2025 14:44:35 | 10/22/2025 15:52:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000648 | PCM-20251022-00001488 | TT-20251022-01533 | EM | Region_6 | MUMA1M8349 | MUMA2349 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 14:45:36 | 10/22/2025 18:29:49 | 10/23/2025 02:45:36 | SHELTER DOOR OPEN at MUMA1M8349-G9-L8-SBTS-P3 @ Generator_SG | 10/22/2025 14:45:26 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 14:45:15 | P3 | 4G | Baha | Generator_SG | LTE NSA | MUMA1M8349 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 14:45:36 | 10/22/2025 18:29:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000649 | PCM-20251022-00001495 | TT-20251022-01541 | Telecom | Region_3 | YBDB2655 | YBDB2655 |  |  |  | Muhammad Sajjad R3 | 10/22/2025 14:48:45 | 10/22/2025 17:27:06 | 10/22/2025 20:48:45 | LOCAL_FAULT at YBDB2655_ELC @ Sceco_STB | 10/22/2025 14:45:19 | Major | 1-12545 | LOCAL_FAULT | 10/22/2025 14:45:06 | P1 | SRAN | yanbu | Sceco_STB | DWDM NSA | YBDB2655 | FLM_TE | [5 empty] | 0-ELC(1-C)-4-G1M520S-3(RX1/TX1)-CLIENT:1 |  |  | API | 10/22/2025 14:48:45 | 10/22/2025 17:27:06 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000651 | PCM-20251022-00001496 | TT-20251021-02218 | Reference_telecom | Region_6 | KMS0303 | KMS0303 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Abdelaziz Hamid Abdelrahman | 10/22/2025 14:49:17 | 10/22/2025 19:35:58 | 10/23/2025 02:49:17 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at KMS0303-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/21/2025 16:21:30 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/21/2025 16:12:12 | P2 | 2G | abha | Sceco | 2G NSA | KMS0303 | FLM_TE |  | KMS0303 site was down and restored kindly check | PCM-20251022-00001481 | KMS0303 site was down and restored kindly check | KMS0303 site was down and restored kindly check |  |  |  | API | 10/22/2025 14:49:17 | 10/22/2025 15:18:38 | 10/22/2025 19:35:47 |  |  | 10/22/2025 19:35:58 |  | Ahmed Abdelaziz Hamid Abdelrahman |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000652 | PCM-20251022-00001497 | TT-20251022-01543 | EM | Region_5 | QUR1M9338 | QUR0338 |  |  |  | Ezz Ismaeal Mahmoud Sayed | 10/22/2025 14:49:44 | 10/22/2025 14:49:44 | 10/23/2025 02:49:44 | RECTIFIER MAINS POWER FAILURE at QUR1M9338-CA-L800-P2-USF-SBTS @ Sceco | 10/22/2025 14:41:28 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 14:41:19 | P2 | 4G | makkah | Sceco | LTE NSA | QUR1M9338 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 14:49:44 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000654 | PCM-20251022-00001503 | TT-20251022-01549 | EM | Region_2 | R2_RY3_HWBSC01 | RY3 |  |  |  | Farhat Saeed Pirzada | 10/22/2025 14:51:17 | 10/22/2025 14:51:17 | 10/22/2025 18:51:17 | Fire Alarm (SH2) at R2_RY3_HWBSC01 @ Sceco_STB | 10/22/2025 14:51:03 | Critical | 65359 | Fire Alarm (SH2) | 10/22/2025 14:50:58 | P1 | BSC | riyadh | Sceco_STB | 2G NSA | R2_RY3_HWBSC01 | FLM_EM | [8 empty] | API | 10/22/2025 14:51:17 | [10 empty] | EM | Zain |  | Running |  | OWS
Accept | CM20251022000655 | PCM-20251022-00001504 | TT-20251022-01550 | Telecom | Region_6 | ABH0161 | ABH0161 |  |  |  | Amir Sohail | 10/22/2025 14:52:19 | 10/22/2025 21:17:42 | 10/22/2025 18:52:19 | OSC_LOS at ABH0161-OCS1 @ Sceco_STB | 10/22/2025 14:51:40 | Critical | 1-12843 | OSC_LOS | 10/22/2025 14:51:29 | P1 | 2G | abha | Sceco_STB | DWDM NSA | ABH0161 | FLM_TE | [5 empty] | 0-1-C-14-F1AST4-1(RM1/TM1)-OSC:1 |  |  | API | 10/22/2025 14:52:19 | 10/22/2025 15:28:08 | 10/22/2025 21:17:42 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Accept | CM20251022000656 | PCM-20251022-00001505 | TT-20251022-01551 | Telecom | Region_6 | ABH0161 | ABH0161 |  |  |  | Amir Sohail | 10/22/2025 14:52:19 | 10/22/2025 21:44:05 | 10/22/2025 18:52:19 | PORT_MODULE_OFFLINE at ABH0161-OCS1 @ Sceco_STB | 10/22/2025 14:51:38 | Critical | 1-63629 | PORT_MODULE_OFFLINE | 10/22/2025 14:51:27 | P1 | 2G | abha | Sceco_STB | DWDM NSA | ABH0161 | FLM_TE | [5 empty] | 0-1-C-14-F1AST4-2(RM2/TM2)-OSC:1 |  |  | API | 10/22/2025 14:52:19 | 10/22/2025 15:28:08 | 10/22/2025 21:44:05 | [8 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251021001008 | PCM-20251021-00002107 | TT-20251021-02145 | Reference_EM | Region_1 | NRY0594 | NRY0594 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/21/2025 17:26:47 | 10/22/2025 02:05:05 | 10/22/2025 05:26:47 | Generator failure at NRY0594-P2-USF_SRAN-PC @ Power Cube | 10/21/2025 17:16:27 | Minor | 65114 | Generator failure | 10/21/2025 17:16:21 | P2 | SRAN | jubail | Power Cube | 2G NSA | NRY0594 | FLM_EM | [8 empty] | API | 10/21/2025 17:26:47 | 10/22/2025 02:05:05 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251021001021 | PCM-20251021-00002132 | TT-20251021-02180 | EM | Region_1 | ARM0663 | ARM0663 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Ahmed Hassan Ahmed Hassanin | 10/21/2025 17:47:55 | 10/23/2025 03:09:31 | 10/22/2025 05:47:55 | Fire Fighting system alarm at ARM2M1663-P3 @ Generator_SG | 10/21/2025 17:37:43 | Minor | 65111 | Fire Fighting system alarm | 10/21/2025 17:37:37 | P3 | 2G | jubail | Generator_SG | 2G NSA | ARM2M1663 | FLM_EM | [8 empty] | API | 10/21/2025 17:47:55 | 10/23/2025 01:51:00 | 10/23/2025 03:09:25 |  |  | 10/23/2025 03:09:31 |  | Ahmed Hassan Ahmed Hassanin |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021001032 | PCM-20251021-00002148 | TT-20251021-02198 | EM | Region_1 | DAM0313 | DAM0313 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/21/2025 18:02:26 | 10/22/2025 18:50:55 | 10/21/2025 22:02:26 | Door opening alarm at DAM0313-P1-DIA-WDM_SRAN @ Sceco | 10/21/2025 18:01:56 | Critical | 65101 | Door opening alarm | 10/21/2025 18:01:11 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0313 | FLM_EM | [8 empty] | API | 10/21/2025 18:02:26 | 10/22/2025 18:50:55 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251021001077 | PCM-20251021-00002246 | TT-20251021-02301 | Reference_EM | Region_1 | JFQS2017 | JFQS2017 | Enviroment | Genset failure_MCU | Change Generator controller | Asmat Anwar Sher Ullah Khan | 10/21/2025 19:10:06 | 10/21/2025 20:51:48 | 10/22/2025 07:10:06 | Generator failure at JFQS2017-P3_SRAN @ Power Cube | 10/21/2025 18:59:45 | Minor | 65114 | Generator failure | 10/21/2025 18:59:41 | P3 | SRAN | sakaka | Power Cube | 2G NSA | JFQS2017 | FLM_EM | [8 empty] | API | 10/21/2025 19:10:06 | 10/21/2025 20:05:24 | 10/21/2025 20:05:44 | 10/21/2025 20:05:48 | 10/21/2025 20:29:10 | 10/21/2025 20:51:48 |  | Asmat Anwar Sher Ullah Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021001081 | PCM-20251021-00002252 | TT-20251021-02306 | EM | Region_1 | SMN0805 | SMN0805 |  |  |  | Rahman Ullah Said Halim | 10/21/2025 19:18:21 | 10/22/2025 21:41:13 | 10/22/2025 07:18:21 | Mains Failure at SMN0805-P3_SRAN @ Generator_DG | 10/21/2025 19:08:08 | Minor | 65109 | Mains Failure | 10/21/2025 19:08:05 | P3 | SRAN | hafr | Generator_DG | 2G NSA | SMN0805 | FLM_EM | [8 empty] | API | 10/21/2025 19:18:21 | 10/22/2025 21:41:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021001099 | PCM-20251021-00002287 | TT-20251021-02324 | Reference_EM | Region_1 | HFF0008 | HFF0008 | Equipment | SW | Issue was solved after softaware configuration | Shahid Khan Dilawar Khan | 10/21/2025 19:41:05 | 10/21/2025 20:43:44 | 10/22/2025 07:41:05 | Low battery voltage at HFF0008-P2_SRAN @ Sceco | 10/21/2025 19:30:37 | Minor | 65110 | Low battery voltage | 10/21/2025 19:30:34 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0008 | FLM_EM | [8 empty] | API | 10/21/2025 19:41:05 | 10/21/2025 20:39:35 | 10/21/2025 20:42:12 | 10/21/2025 20:42:33 | 10/21/2025 20:42:55 | 10/21/2025 20:43:44 |  | Shahid Khan Dilawar Khan |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021001100 | PCM-20251021-00002286 | TT-20251021-02323 | EM | Region_1 | JBKH0570 | JBKH0570 |  |  |  | Dileesh Muringothil Devarajan | 10/21/2025 19:41:07 | 10/22/2025 07:37:29 | 10/22/2025 07:41:07 | Major Rec alarm at JBKH0570-P3_SRAN-PC @ Power Cube | 10/21/2025 19:39:02 | Minor | 65107 | Major Rec alarm | 10/21/2025 19:23:03 | P3 | SRAN | jubail | Power Cube | 2G NSA | JBKH0570 | FLM_EM | [8 empty] | API | 10/21/2025 19:41:07 | 10/22/2025 07:37:29 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251021001113 | PCM-20251021-00002315 | TT-20251021-02357 | Reference_EM | Region_2 | RYD0940 | RYD0940 | Enviroment | Genset failure_Battery charger | Change Generator battery charger | Gul Rahman Gul ZADA | 10/21/2025 20:15:18 | 10/21/2025 22:27:47 | 10/22/2025 02:15:18 | Generator failure at RYD0940-P1-HUB_SRAN @ Generator_DG | 10/21/2025 20:04:49 | Major | 65114 | Generator failure | 10/21/2025 20:04:46 | P1 | SRAN | rumah | Generator_DG | 2G NSA | RYD0940 | FLM_EM | [8 empty] | API | 10/21/2025 20:15:18 | 10/21/2025 22:27:27 | 10/21/2025 22:27:34 |  |  | 10/21/2025 22:27:47 |  | Gul Rahman Gul ZADA |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251021001120 | PCM-20251021-00002328 | TT-20251021-02375 | Reference_EM | Region_2 | MZH0490 | MZH0490 | Equipment | PMR_Power_Cable_RRU | Replace Power Cable | Ahmed Hamada Mohamed Awad Abouhatab | 10/21/2025 20:29:07 | 10/21/2025 22:35:41 | 10/22/2025 08:29:07 | Generator failure at MZH0490-P2-USF_SRAN-PC @ Power Cube | 10/21/2025 20:18:21 | Minor | 65114 | Generator failure | 10/21/2025 20:18:18 | P2 | SRAN | muzamiah | Power Cube | 2G NSA | MZH0490 | FLM_EM | [8 empty] | API | 10/21/2025 20:29:07 | 10/21/2025 22:18:36 | 10/21/2025 22:18:43 | 10/21/2025 22:18:45 | 10/21/2025 22:19:06 | 10/21/2025 22:35:41 |  | Ahmed Hamada Mohamed Awad Abouhatab |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021001126 | PCM-20251021-00002337 | TT-20251021-02383 | EM | Region_1 | HFF0008 | HFF0008 |  |  |  | Kenawy Abdalla Tawfik Abdalla | 10/21/2025 20:38:55 | 10/23/2025 11:12:37 | 10/22/2025 08:38:55 | Door opening alarm at HFF0008-P2_SRAN @ Sceco | 10/21/2025 20:38:11 | Minor | 65101 | Door opening alarm | 10/21/2025 20:38:06 | P2 | SRAN | hafouf | Sceco | 2G NSA | HFF0008 | FLM_EM | [8 empty] | API | 10/21/2025 20:38:55 | 10/23/2025 11:12:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251021001135 | PCM-20251021-00002358 | TT-20251021-02402 | EM | Region_1 | HRD9017 | HRD9017 |  |  |  | Montasir Awadalla Abdalla Bala | 10/21/2025 20:54:55 | 10/22/2025 07:35:48 | 10/22/2025 08:54:55 | NETECO: Bus Bar Undervoltage at HRD9017 @ Power Cube | 10/21/2025 20:48:30 | Minor | 8607 | Bus Bar Undervoltage | 10/21/2025 20:48:30 | P3 | Repeater | hafouf | Power Cube | 2G NSA | HRD9017 | FLM_EM | [8 empty] | API | 10/21/2025 20:54:55 | 10/22/2025 07:35:48 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251021001136 | PCM-20251021-00002359 | TT-20251021-02403 | EM | Region_1 | JBK9910 | JBK9910 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/21/2025 20:54:57 | 10/22/2025 12:44:49 | 10/22/2025 08:54:57 | NETECO: Genset Fault at JBK9910 @ Generator_SG | 10/21/2025 20:48:21 | Minor | 40564 | Genset Fault | 10/21/2025 20:48:21 | P3 | Repeater | hafr | Generator_SG | 2G NSA | JBK9910 | FLM_EM | [8 empty] | API | 10/21/2025 20:54:57 | 10/22/2025 12:43:50 | 10/22/2025 12:44:34 |  |  | 10/22/2025 12:44:49 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251021001157 | PCM-20251021-00002393 | TT-20251021-02468 | EM | Region_1 | HFR2087 | HFR2087 | Enviroment | SCECO_Failure | SCECO auto restored | Reda Mohammed Mohamed Hassanein | 10/21/2025 21:43:01 | 10/22/2025 19:27:10 | 10/22/2025 09:43:01 | Mains Failure at HFR2087-P2_SRAN @ Sceco | 10/21/2025 21:32:50 | Minor | 65109 | Mains Failure | 10/21/2025 21:32:47 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR2087 | FLM_EM | [8 empty] | API | 10/21/2025 21:43:01 | 10/21/2025 21:52:07 | 10/22/2025 19:27:04 |  |  | 10/22/2025 19:27:10 |  | Reda Mohammed Mohamed Hassanein |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251021001221 | PCM-20251021-00002506 | TT-20251021-02587 | Reference_EM | Region_2 | RIY2315 | RIY2315 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/21/2025 23:53:40 | 10/22/2025 11:15:06 | 10/22/2025 11:53:40 | Air condition 1 failure alarm at RIY2315-P2_SRAN @ Sceco | 10/21/2025 23:43:05 | Minor | 65104 | Air condition 1 failure alarm | 10/21/2025 23:43:01 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2315 | FLM_EM | [8 empty] | API | 10/21/2025 23:53:40 | 10/22/2025 11:15:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000041 | PCM-20251022-00000107 | TT-20251022-00115 | EM | Region_1 | URY9013 | URY9013 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/22/2025 01:11:11 | 10/22/2025 02:05:06 | 10/22/2025 13:11:11 | NETECO: Speed Sensor Failure at URY9013 @ Power Cube | 10/22/2025 01:04:48 | Minor | 8143 | Speed Sensor Failure | 10/22/2025 01:04:48 | P3 | Repeater | jubail | Power Cube | 2G NSA | URY9013 | FLM_EM | [8 empty] | API | 10/22/2025 01:11:11 | 10/22/2025 02:05:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000042 | PCM-20251022-00000109 | TT-20251022-00117 | Reference_EM | Region_2 | RIY0349 | RIY0349 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/22/2025 01:11:41 | 10/22/2025 17:49:50 | 10/22/2025 13:11:41 | Minor Rec alarm at RIY0349-P2_SRAN @ Sceco | 10/22/2025 01:01:16 | Minor | 65108 | Minor Rec alarm | 10/22/2025 01:01:13 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0349 | FLM_EM | [8 empty] | API | 10/22/2025 01:11:41 | 10/22/2025 17:49:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000061 | PCM-20251022-00000171 | TT-20251022-00201 | Reference_EM | Region_2 | RIY0398 | RIY0398 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/22/2025 01:54:36 | 10/22/2025 17:49:50 | 10/22/2025 13:54:36 | Air condition 2 failure alarm at RIY0398-P2_SRAN @ Sceco | 10/22/2025 01:44:07 | Minor | 65105 | Air condition 2 failure alarm | 10/22/2025 01:44:03 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0398 | FLM_EM | [8 empty] | API | 10/22/2025 01:54:36 | 10/22/2025 17:49:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000065 | PCM-20251022-00000176 | TT-20251022-00205 | Reference_EM | Region_1 | JBL2100 | JBL2100 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/22/2025 01:58:10 | 10/22/2025 02:01:08 | 10/22/2025 13:58:10 | high temprature 32 at JBL2100-P2_SRAN @ Sceco | 10/22/2025 01:47:33 | Minor | 65102 | high temprature 32 | 10/22/2025 01:47:30 | P2 | SRAN | jubail | Sceco | 2G NSA | JBL2100 | FLM_EM | [8 empty] | API | 10/22/2025 01:58:10 | 10/22/2025 02:01:08 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000071 | PCM-20251022-00000189 | TT-20251022-00218 | EM | Region_2 | RIY2856 | RIY2856 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/22/2025 02:03:29 | 10/22/2025 12:08:36 | 10/22/2025 14:03:29 | Water Alarm at RIY2856-P2_SRAN @ Sceco | 10/22/2025 01:57:25 | Minor | 25670 | Water Alarm | 10/22/2025 01:55:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2856 | FLM_EM | [8 empty] | API | 10/22/2025 02:03:29 | 10/22/2025 12:08:36 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000076 | PCM-20251022-00000196 | TT-20251022-00223 | EM | Region_2 | RIY0371 | RIY0371 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/22/2025 02:05:53 | 10/22/2025 11:15:07 | 10/22/2025 08:05:53 | Minor Rec alarm at RIY0371-P1-VIP_SRAN @ Sceco_STB | 10/22/2025 01:57:22 | Major | 65108 | Minor Rec alarm | 10/22/2025 01:55:28 | VIP | SRAN | riyadh | Sceco_STB | 2G NSA | RIY0371 | FLM_EM | [8 empty] | API | 10/22/2025 02:05:53 | 10/22/2025 11:15:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251022000077 | PCM-20251022-00000197 | TT-20251022-00224 | EM | Region_2 | RIY0362 | RIY0362 |  |  |  | Moin Uddin | 10/22/2025 02:05:55 | 10/22/2025 14:52:38 | 10/22/2025 14:05:55 | Air condition 1 failure alarm at RIY0362-P2_SRAN-FON @ Sceco | 10/22/2025 01:57:35 | Minor | 65104 | Air condition 1 failure alarm | 10/22/2025 01:55:33 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0362 | FLM_EM | [8 empty] | API | 10/22/2025 02:05:55 | 10/22/2025 10:31:08 | 10/22/2025 14:47:07 | 10/22/2025 14:47:37 | 10/22/2025 14:52:38 | [6 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251022000078 | PCM-20251022-00000200 | TT-20251022-00227 | EM | Region_2 | RIY2290 | RIY2290 | Enviroment | Air Condition | Change Fan | Moin Uddin | 10/22/2025 02:06:25 | 10/22/2025 17:51:55 | 10/22/2025 14:06:25 | Low battery voltage at RIY2290-P3_SRAN-PC @ Sceco | 10/22/2025 01:56:56 | Minor | 65110 | Low battery voltage | 10/22/2025 01:55:43 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2290 | FLM_EM | [8 empty] | API | 10/22/2025 02:06:25 | 10/22/2025 10:31:09 | 10/22/2025 16:54:23 | 10/22/2025 16:54:28 | 10/22/2025 16:54:44 | 10/22/2025 17:51:55 |  | Moin Uddin |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000080 | PCM-20251022-00000205 | TT-20251022-00232 | EM | Region_2 | RIY2724 | RIY2724 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/22/2025 02:10:06 | 10/22/2025 17:49:50 | 10/22/2025 14:10:06 | Mains Failure at RIY2724-P3_SRAN-PC @ Sceco | 10/22/2025 02:00:02 | Minor | 65109 | Mains Failure | 10/22/2025 01:59:58 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2724 | FLM_EM | [8 empty] | API | 10/22/2025 02:10:06 | 10/22/2025 17:49:50 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000082 | PCM-20251022-00000206 | TT-20251022-00233 | Reference_EM | Region_2 | RIY2444 | RIY2444 | Enviroment | Fire Alarm | Change smoke sensor | Adham Adham Hassan Farghal | 10/22/2025 02:10:36 | 10/22/2025 19:05:11 | 10/22/2025 14:10:36 | Mains Failure at RIY2444-P3_SRAN-PC @ Sceco | 10/22/2025 02:00:12 | Minor | 65109 | Mains Failure | 10/22/2025 02:00:09 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIY2444 | FLM_EM | [8 empty] | API | 10/22/2025 02:10:36 | 10/22/2025 03:00:32 | 10/22/2025 18:44:36 | 10/22/2025 18:44:38 | 10/22/2025 18:44:40 | 10/22/2025 19:05:11 |  | Adham Adham Hassan Farghal |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000085 | PCM-20251022-00000212 | TT-20251022-00239 | EM | Region_1 | DAM0313 | DAM0313 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/22/2025 02:12:05 | 10/22/2025 18:50:56 | 10/22/2025 06:12:05 | Mains Failure at DAM0313-P1-DIA-WDM_SRAN @ Sceco | 10/22/2025 02:10:12 | Critical | 65109 | Mains Failure | 10/22/2025 02:10:09 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM0313 | FLM_EM | [8 empty] | API | 10/22/2025 02:12:05 | 10/22/2025 18:50:56 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251022000100 | PCM-20251022-00000262 | TT-20251022-00292 | EM | Region_1 | JBL0448 | JBL0448 |  |  |  | Islam Elsawi Mohamed Elsawi | 10/22/2025 02:46:16 | 10/23/2025 20:52:46 | 10/22/2025 06:46:16 | Minor Rec alarm at JBL0448-P1-HUB-WDM_SRAN-FON @ Sceco | 10/22/2025 02:44:14 | Critical | 65108 | Minor Rec alarm | 10/22/2025 02:44:11 | P1 | SRAN | jubail | Sceco | 2G NSA | JBL0448 | FLM_EM | [8 empty] | API | 10/22/2025 02:46:16 | 10/23/2025 20:52:46 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251022000110 | PCM-20251022-00000288 | TT-20251022-00310 | Reference_EM | Region_1 | DMJR2264 | DMJR2264 | Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue | Emad Mahmoud Ahmed Mohamed | 10/22/2025 03:00:41 | 10/22/2025 04:40:33 | 10/22/2025 15:00:41 | Generator failure at DMJR2264-P2-USF_SRAN @ Generator_SG | 10/22/2025 02:50:10 | Minor | 65114 | Generator failure | 10/22/2025 02:50:06 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJR2264 | FLM_EM | [8 empty] | API | 10/22/2025 03:00:41 | 10/22/2025 03:01:51 | 10/22/2025 03:27:42 | 10/22/2025 03:27:44 | 10/22/2025 03:45:18 | 10/22/2025 04:40:33 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000137 | PCM-20251022-00000361 | TT-20251022-00399 | EM | Region_1 | DAM0374 | DAM0374 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/22/2025 04:01:41 | 10/22/2025 18:50:57 | 10/22/2025 16:01:41 | Door opening alarm at DAM0374-P2_SRAN @ Sceco | 10/22/2025 04:01:13 | Minor | 65101 | Door opening alarm | 10/22/2025 03:57:45 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0374 | FLM_EM | [8 empty] | API | 10/22/2025 04:01:41 | 10/22/2025 18:50:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000163 | PCM-20251022-00000415 | TT-20251022-00484 | Reference_EM | Region_1 | DAM0307 | DAM0307 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/22/2025 04:51:16 | 10/22/2025 18:50:58 | 10/22/2025 16:51:16 | Low battery voltage at DAM0307-P2_SRAN @ Sceco | 10/22/2025 04:40:48 | Minor | 65110 | Low battery voltage | 10/22/2025 04:40:43 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0307 | FLM_EM | [8 empty] | API | 10/22/2025 04:51:16 | 10/22/2025 18:50:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Departed | CM20251022000167 | PCM-20251022-00000421 | TT-20251022-00492 | Reference_EM | Region_1 | DAM0679 | DAM0679 |  |  |  | Ibrahim said mohamed Elmarhoumy | 10/22/2025 04:56:25 | 10/22/2025 07:02:06 | 10/22/2025 16:56:25 | Low battery voltage at DAM0679-P2_SRAN @ Sceco | 10/22/2025 04:46:07 | Minor | 65110 | Low battery voltage | 10/22/2025 04:46:05 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0679 | FLM_EM | [8 empty] | API | 10/22/2025 04:56:25 | 10/22/2025 05:27:36 | 10/22/2025 07:02:02 | 10/22/2025 07:02:06 | [7 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000186 | PCM-20251022-00000487 | TT-20251022-00569 | EM | Region_1 | ARM0711 | ARM0711 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Omer Elfadoul Mohamed Ibrahim | 10/22/2025 05:41:21 | 10/22/2025 17:03:15 | 10/22/2025 17:41:21 | Minor Rec alarm at ARM0711-P3_SRAN @ Generator_SG | 10/22/2025 05:34:54 | Minor | 65108 | Minor Rec alarm | 10/22/2025 05:30:48 | P3 | SRAN | dammam | Generator_SG | 2G NSA | ARM0711 | FLM_EM | [8 empty] | API | 10/22/2025 05:41:21 | 10/22/2025 06:57:37 | 10/22/2025 16:40:23 | 10/22/2025 16:40:27 | 10/22/2025 16:40:29 | 10/22/2025 17:03:15 |  | Omer Elfadoul Mohamed Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000202 | PCM-20251022-00000513 | TT-20251022-00595 | Reference_EM | Region_2 | BUR0012 | BUR0012 | Enviroment | SCECO_Failure | SCECO auto restored | Shahid Ahmed Shah Nawaz | 10/22/2025 06:01:01 | 10/23/2025 17:05:04 | 10/22/2025 18:01:01 | Fire Alarm at BUR0012-P2_SRAN @ Sceco | 10/22/2025 05:43:29 | Minor | 65119 | Fire Alarm | 10/22/2025 04:21:52 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0012 | FLM_EM | [8 empty] | API | 10/22/2025 06:01:01 | 10/23/2025 17:05:04 | [5 empty] | Shahid Ahmed Shah Nawaz | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000229 | PCM-20251022-00000558 | TT-20251022-00630 | Reference_EM | Region_1 | HRBD0622 | HRBD0622 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/22/2025 06:28:26 | 10/22/2025 12:46:33 | 10/22/2025 18:28:26 | Mains Failure at HRBD0622-P2-USF_SRAN @ Generator_SG | 10/22/2025 06:18:03 | Minor | 65109 | Mains Failure | 10/22/2025 06:17:59 | P2 | SRAN | hafr | Generator_SG | 2G NSA | HRBD0622 | FLM_EM | [8 empty] | API | 10/22/2025 06:28:26 | 10/22/2025 12:43:52 | 10/22/2025 12:46:15 |  |  | 10/22/2025 12:46:33 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000237 | PCM-20251022-00000571 | TT-20251022-00647 | EM | Region_1 | TRT0764 | TRT0764 |  |  |  | Ibrahim said mohamed Elmarhoumy | 10/22/2025 06:40:46 | 10/22/2025 06:44:45 | 10/22/2025 18:40:46 | Mains Failure at TRT0764-P3_SRAN @ Sceco | 10/22/2025 06:30:48 | Minor | 65109 | Mains Failure | 10/22/2025 06:30:43 | P3 | SRAN | hafouf | Sceco | 2G NSA | TRT0764 | FLM_EM | [8 empty] | API | 10/22/2025 06:40:46 | 10/22/2025 06:44:45 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000254 | PCM-20251022-00000640 | TT-20251022-00714 | Reference_EM | Region_2 | AFL0081 | AFL0081 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Danish Ahsan Ahsan Ullah | 10/22/2025 07:05:06 | 10/22/2025 09:04:18 | 10/22/2025 19:05:06 | Generator failure at AFL0081-P3-USF_SRAN-PC @ Power Cube | 10/22/2025 06:54:25 | Minor | 65114 | Generator failure | 10/22/2025 06:54:21 | P3 | SRAN | aflaj | Power Cube | 2G NSA | AFL0081 | FLM_EM | [8 empty] | API | 10/22/2025 07:05:06 | 10/22/2025 08:50:23 | 10/22/2025 08:50:27 | 10/22/2025 08:50:30 | 10/22/2025 08:50:33 | 10/22/2025 09:04:18 |  | Danish Ahsan Ahsan Ullah |  |  |  | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251022000255 | PCM-20251022-00000641 | TT-20251022-00721 | Reference_EM | Region_1 | YBR0669 | YBR0669 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Montasir Awadalla Abdalla Bala | 10/22/2025 07:08:41 | 10/22/2025 09:08:23 | 10/22/2025 19:08:41 | Generator failure at YBR0669-P3-USF_SRAN-PC @ Power Cube | 10/22/2025 06:58:12 | Minor | 65114 | Generator failure | 10/22/2025 06:58:09 | P3 | SRAN | hafouf | Power Cube | 2G NSA | YBR0669 | FLM_EM | [8 empty] | API | 10/22/2025 07:08:41 | 10/22/2025 07:35:48 | 10/22/2025 07:37:02 | 10/22/2025 07:37:17 | 10/22/2025 09:08:09 | 10/22/2025 09:08:23 |  | Montasir Awadalla Abdalla Bala |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000257 | PCM-20251022-00000644 | TT-20251022-00724 | Reference_EM | Region_2 | KHJ0007 | KHJ0007 | Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor | Fritz Ian Generale | 10/22/2025 07:11:16 | 10/22/2025 09:40:52 | 10/22/2025 19:11:16 | Generator failure at KHJ0007-P3-USF_SRAN-PC @ Power Cube | 10/22/2025 07:00:35 | Minor | 65114 | Generator failure | 10/22/2025 07:00:32 | P3 | SRAN | al kharj | Power Cube | 2G NSA | KHJ0007 | FLM_EM | [8 empty] | API | 10/22/2025 07:11:16 | 10/22/2025 09:15:56 | 10/22/2025 09:40:38 |  |  | 10/22/2025 09:40:52 |  | Fritz Ian Generale |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000270 | PCM-20251022-00000664 | TT-20251022-00744 | EM | Region_1 | DAM2995 | DAM2995 | Enviroment | Fire Alarm | Reset Fire Pannel | Ibrahim said mohamed Elmarhoumy | 10/22/2025 07:29:20 | 10/22/2025 08:02:21 | 10/22/2025 19:29:20 | Door opening alarm at DAM2995-P2_SRAN @ Sceco | 10/22/2025 07:28:54 | Minor | 65101 | Door opening alarm | 10/22/2025 07:28:50 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM2995 | FLM_EM | [8 empty] | API | 10/22/2025 07:29:20 | 10/22/2025 07:45:45 | 10/22/2025 07:55:04 | 10/22/2025 07:55:06 | 10/22/2025 07:55:08 | 10/22/2025 08:02:21 |  | Ibrahim said mohamed Elmarhoumy |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000272 | PCM-20251022-00000666 | TT-20251022-00747 | EM | Region_1 | JDNR2150 | JDNR2150 |  |  |  | Dileesh Muringothil Devarajan | 10/22/2025 07:30:26 | 10/22/2025 07:37:30 | 10/22/2025 19:30:26 | Mains Failure at JDNR2150-P2_SRAN @ Sceco | 10/22/2025 07:20:22 | Minor | 65109 | Mains Failure | 10/22/2025 07:20:17 | P2 | SRAN | jubail | Sceco | 2G NSA | JDNR2150 | FLM_EM | [8 empty] | API | 10/22/2025 07:30:26 | 10/22/2025 07:37:30 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251022000288 | PCM-20251022-00000696 | TT-20251022-00777 | Reference_EM | Region_1 | HRB9919 | HRB9919 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/22/2025 07:47:25 | 10/22/2025 12:46:53 | 10/22/2025 19:47:25 | Mains Failure at HRB9919-RPT @ Generator_SG | 10/22/2025 07:37:02 | Minor | 65109 | Mains Failure | 10/22/2025 07:36:57 | P3 | Repeater | hafr | Generator_SG | 3G NSA | HRB9919 | FLM_EM | [8 empty] | API | 10/22/2025 07:47:25 | 10/22/2025 12:43:53 | 10/22/2025 12:46:40 |  |  | 10/22/2025 12:46:53 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000299 | PCM-20251022-00000717 | TT-20251022-00796 | Reference_EM | Region_1 | NRY0578 | NRY0578 |  |  |  | Mohamed Ahmed Mohamed Ahmed | 10/22/2025 07:56:11 | 10/22/2025 23:10:41 | 10/22/2025 19:56:11 | Generator failure at NRY0578-P2-USF_SRAN-PC @ Power Cube | 10/22/2025 07:45:37 | Minor | 65114 | Generator failure | 10/22/2025 07:45:33 | P2 | SRAN | jubail | Power Cube | 2G NSA | NRY0578 | FLM_EM | [8 empty] | API | 10/22/2025 07:56:11 | 10/22/2025 23:10:41 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000307 | PCM-20251022-00000735 | TT-20251022-00813 | EM | Region_1 | KBR0163 | KBR0163 |  |  |  | Yasser Mohamed Abdelnabi Ibrahim | 10/22/2025 08:06:31 | 10/23/2025 02:21:38 | 10/22/2025 12:06:31 | high temprature 32 at KBR0163-P1-SHOP-HUB-WDM_SRAN @ Sceco_STB | 10/22/2025 08:04:33 | Critical | 65102 | high temprature 32 | 10/22/2025 08:04:29 | P1 | SRAN | dammam | Sceco_STB | 2G NSA | KBR0163 | FLM_EM | [8 empty] | API | 10/22/2025 08:06:31 | 10/23/2025 02:21:38 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251022000308 | PCM-20251022-00000737 | TT-20251022-00815 | Reference_EM | Region_1 | KBR2223 | KBR2223 |  |  |  | Mohamed Samir Farahat Allam | 10/22/2025 08:08:06 | 10/23/2025 13:19:31 | 10/22/2025 20:08:06 | high temprature 32 at KBR2223-P3_SRAN @ Sceco | 10/22/2025 07:57:49 | Minor | 65102 | high temprature 32 | 10/22/2025 07:57:46 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR2223 | FLM_EM | [8 empty] | API | 10/22/2025 08:08:06 | 10/23/2025 13:19:31 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000321 | PCM-20251022-00000771 | TT-20251022-00855 | Reference_EM | Region_2 | RIY0447 | RIY0447 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/22/2025 08:39:36 | 10/22/2025 17:49:51 | 10/22/2025 20:39:36 | Major Rec alarm at RIY0447-P2_SRAN @ Sceco | 10/22/2025 08:29:01 | Minor | 65107 | Major Rec alarm | 10/22/2025 08:28:57 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0447 | FLM_EM | [8 empty] | API | 10/22/2025 08:39:36 | 10/22/2025 17:49:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000327 | PCM-20251022-00000779 | TT-20251022-00861 | Reference_EM | Region_1 | KFJ2490 | KFJ2490 | Enviroment | Air Condition | Change Fan | Dileesh Muringothil Devarajan | 10/22/2025 08:49:25 | 10/23/2025 13:16:28 | 10/22/2025 20:49:25 | Air condition 1 failure alarm at KFJ2490-P2_SRAN @ Sceco | 10/22/2025 08:38:55 | Minor | 65104 | Air condition 1 failure alarm | 10/22/2025 08:38:51 | P2 | SRAN | khafji | Sceco | 2G NSA | KFJ2490 | FLM_EM | [8 empty] | API | 10/22/2025 08:49:25 | 10/22/2025 09:54:26 | 10/22/2025 16:12:00 | 10/22/2025 16:12:16 | 10/22/2025 16:12:19 | 10/23/2025 13:16:28 |  | Dileesh Muringothil Devarajan |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251022000329 | PCM-20251022-00000788 | TT-20251022-00874 | Reference_EM | Region_2 | KHJ0469 | KHJ0469 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/22/2025 08:55:06 | 10/23/2025 14:22:55 | 10/22/2025 20:55:06 | High temperature 32C alarm at KHJ2M1469-P3 @ Sceco | 10/22/2025 08:44:47 | Minor | 65102 | High temperature 32C alarm | 10/22/2025 08:44:40 | P3 | 2G | al kharj | Sceco | 2G NSA | KHJ2M1469 | FLM_EM | [8 empty] | API | 10/22/2025 08:55:06 | [7 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000335 | PCM-20251022-00000802 | TT-20251022-00883 | EM | Region_1 | HRBD0621 | HRBD0621 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Imran Qamar Ghulam Qamar | 10/22/2025 09:02:21 | 10/22/2025 12:46:05 | 10/22/2025 21:02:21 | Generator failure at HRBD0621-P2-USF_SRAN @ Generator_DG | 10/22/2025 08:54:02 | Minor | 65114 | Generator failure | 10/22/2025 08:51:38 | P2 | SRAN | hafr | Generator_DG | 2G NSA | HRBD0621 | FLM_EM | [8 empty] | API | 10/22/2025 09:02:21 | 10/22/2025 12:43:53 | 10/22/2025 12:45:43 |  |  | 10/22/2025 12:46:05 |  | Imran Qamar Ghulam Qamar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000353 | PCM-20251022-00000852 | TT-20251022-00933 | EM | Region_1 | SMRY2814 | SMRY2814 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Shaker Saied Mohamed ElShafie | 10/22/2025 09:29:10 | 10/22/2025 12:59:01 | 10/22/2025 21:29:10 | Mains Failure at SMRY2814-P2_SRAN @ Sceco | 10/22/2025 09:19:14 | Minor | 65109 | Mains Failure | 10/22/2025 09:19:10 | P2 | SRAN | hafr | Sceco | 2G NSA | SMRY2814 | FLM_EM | [8 empty] | API | 10/22/2025 09:29:10 | 10/22/2025 09:33:20 | 10/22/2025 12:02:04 | 10/22/2025 12:02:12 | 10/22/2025 12:02:21 | 10/22/2025 12:59:01 |  | Shaker Saied Mohamed ElShafie |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000356 | PCM-20251022-00000860 | TT-20251022-00939 | EM | Region_1 | JBL0968 | JBL0968 |  |  |  | Hamid Bilal Bashir Ahmed | 10/22/2025 09:32:15 | 10/23/2025 03:56:11 | 10/22/2025 15:32:15 | Door opening alarm at JBL0968-P1_SRAN @ Sceco | 10/22/2025 09:31:52 | Major | 65101 | Door opening alarm | 10/22/2025 09:31:49 | P1 | SRAN | jubail | Sceco | 2G NSA | JBL0968 | FLM_EM | [8 empty] | API | 10/22/2025 09:32:15 | 10/23/2025 03:56:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000359 | PCM-20251022-00000865 | TT-20251022-00943 | EM | Region_1 | JBKH0680 | JBKH0680 |  |  |  | Dileesh Muringothil Devarajan | 10/22/2025 09:34:20 | 10/22/2025 09:54:27 | 10/22/2025 21:34:20 | Mains Failure at JBKH0680-P2-USF_SRAN-PC @ Sceco | 10/22/2025 09:24:21 | Minor | 65109 | Mains Failure | 10/22/2025 09:24:18 | P2 | SRAN | khafji | Sceco | 2G NSA | JBKH0680 | FLM_EM | [8 empty] | API | 10/22/2025 09:34:20 | 10/22/2025 09:54:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251022000360 | PCM-20251022-00000867 | TT-20251022-00945 | Reference_EM | Region_1 | RYHF2036 | RYHF2036 |  |  |  | Abdalla Nazmy Abdelfattah Ahmed | 10/22/2025 09:34:51 | 10/22/2025 09:34:51 | 10/22/2025 21:34:51 | high temprature 32 at RYHF2036-P2_SRAN @ Generator_SG | 10/22/2025 09:24:18 | Minor | 65102 | high temprature 32 | 10/22/2025 09:24:14 | P2 | SRAN | hafouf | Generator_SG | 2G NSA | RYHF2036 | FLM_EM | [8 empty] | API | 10/22/2025 09:34:51 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000365 | PCM-20251022-00000879 | TT-20251022-00956 | EM | Region_2 | WDS9016 | WDS9016 |  |  |  | Sher Zamin Nasib Muhammad | 10/22/2025 09:41:01 | 10/23/2025 20:47:57 | 10/22/2025 21:41:01 | NETECO: Battery Undervoltage at WDS9016 @ Power Cube | 10/22/2025 09:34:12 | Minor | 8901 | Battery Undervoltage | 10/22/2025 09:34:12 | P1 | Repeater | aflaj | Power Cube | 2G NSA | WDS9016 | FLM_EM | [8 empty] | API | 10/22/2025 09:41:01 | 10/23/2025 20:47:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000368 | PCM-20251022-00000883 | TT-20251022-00960 | Reference_EM | Region_1 | JBKH2338 | JBKH2338 |  |  |  | Dileesh Muringothil Devarajan | 10/22/2025 09:45:19 | 10/22/2025 09:54:27 | 10/22/2025 15:45:19 | Door opening alarm at JBKH2338-P1-VIP_ARP_SRAN @ Sceco | 10/22/2025 09:44:44 | Major | 65101 | Door opening alarm | 10/22/2025 09:44:40 | VIP | SRAN | khafji | Sceco | 2G NSA | JBKH2338 | FLM_EM | [8 empty] | API | 10/22/2025 09:45:19 | 10/22/2025 09:54:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000385 | PCM-20251022-00000916 | TT-20251022-00986 | Reference_EM | Region_2 | RIY0253 | RIY0253 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/22/2025 10:01:11 | 10/22/2025 12:08:37 | 10/22/2025 22:01:11 | Air condition 2 failure alarm at RIY0253-P2_SRAN @ Sceco | 10/22/2025 09:54:24 | Minor | 65105 | Air condition 2 failure alarm | 10/22/2025 09:50:33 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0253 | FLM_EM | [8 empty] | API | 10/22/2025 10:01:11 | 10/22/2025 12:08:37 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000391 | PCM-20251022-00000934 | TT-20251022-01002 | Reference_EM | Region_1 | JBL0565 | JBL0565 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/22/2025 10:11:01 | 10/22/2025 11:50:16 | 10/22/2025 22:11:01 | Generator failure at JBL0565-P2-USF_SRAN-PC @ Power Cube | 10/22/2025 10:00:23 | Minor | 65114 | Generator failure | 10/22/2025 10:00:19 | P2 | SRAN | dammam | Power Cube | 2G NSA | JBL0565 | FLM_EM | [8 empty] | API | 10/22/2025 10:11:01 | 10/22/2025 10:35:54 | 10/22/2025 10:41:14 | 10/22/2025 10:41:16 | 10/22/2025 11:49:57 | 10/22/2025 11:50:16 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000395 | PCM-20251022-00000943 | TT-20251022-01014 | Reference_EM | Region_2 | RIY0232 | RIY0232 |  |  |  | Adham Adham Hassan Farghal | 10/22/2025 10:13:37 | 10/22/2025 18:44:26 | 10/22/2025 16:13:37 | high temprature 32 at RIY0232-P1_SRAN @ Sceco | 10/22/2025 09:58:36 | Major | 65102 | high temprature 32 | 10/22/2025 10:03:09 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0232 | FLM_EM | [8 empty] | API | 10/22/2025 10:13:37 | 10/22/2025 18:44:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251022000398 | PCM-20251022-00000949 | TT-20251022-01016 | Reference_EM | Region_2 | DLM0485 | DLM0485 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/22/2025 10:15:06 | 10/23/2025 14:22:56 | 10/22/2025 22:15:06 | high temprature 32 at DLM0485-P2_SRAN @ Sceco | 10/22/2025 10:04:51 | Minor | 65102 | high temprature 32 | 10/22/2025 10:04:48 | P2 | SRAN | al kharj | Sceco | 2G NSA | DLM0485 | FLM_EM | [8 empty] | API | 10/22/2025 10:15:06 | [7 empty] | EM phased out spare |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000403 | PCM-20251022-00000961 | TT-20251022-01024 | Reference_EM | Region_2 | QSHL0890 | QSHL0890 | Enviroment | SCECO_Failure | SCECO auto restored | Farman Ullah Muhammad Nazir | 10/22/2025 10:20:20 | 10/22/2025 14:44:24 | 10/22/2025 22:20:20 | Mains Failure at QSHL0890-P2_SRAN @ Sceco | 10/22/2025 10:10:13 | Minor | 65109 | Mains Failure | 10/22/2025 10:10:11 | P2 | SRAN | buraidah | Sceco | 2G NSA | QSHL0890 | FLM_EM | [8 empty] | API | 10/22/2025 10:20:20 | 10/22/2025 10:24:39 | 10/22/2025 14:44:14 |  |  | 10/22/2025 14:44:24 |  | Farman Ullah Muhammad Nazir |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000407 | PCM-20251022-00000967 | TT-20251022-01032 | Reference_EM | Region_2 | ZLHB0872 | ZLHB0872 | Enviroment | SCECO_Failure | SCECO restored after connecting PG | Mahmoud Hefny Ali Ahmed | 10/22/2025 10:24:25 | 10/22/2025 14:29:53 | 10/22/2025 22:24:25 | Mains Failure at ZLHB2M5872-P3 @ Sceco | 10/22/2025 10:14:02 | Minor | 65109 | Mains Failure | 10/22/2025 10:13:59 | P3 | 2G | majma | Sceco | 2G NSA | ZLHB2M5872 | FLM_EM | [8 empty] | API | 10/22/2025 10:24:25 | 10/22/2025 11:01:49 | 10/22/2025 11:01:53 | 10/22/2025 11:01:54 | 10/22/2025 12:07:33 | 10/22/2025 14:29:53 |  | Mahmoud Hefny Ali Ahmed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000425 | PCM-20251022-00001007 | TT-20251022-01072 | Reference_EM | Region_1 | DMJR2264 | DMJR2264 | Enviroment | Rectifier_Fault | Reset rectifier Controller | Emad Mahmoud Ahmed Mohamed | 10/22/2025 10:47:41 | 10/22/2025 18:04:53 | 10/22/2025 22:47:41 | Door opening alarm at DMJR2264-P2-USF_SRAN @ Generator_SG | 10/22/2025 10:47:05 | Minor | 65101 | Door opening alarm | 10/22/2025 10:37:35 | P2 | SRAN | hafr | Generator_SG | 2G NSA | DMJR2264 | FLM_EM | [8 empty] | API | 10/22/2025 10:47:41 | 10/22/2025 12:16:37 | 10/22/2025 18:04:35 |  |  | 10/22/2025 18:04:53 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000434 | PCM-20251022-00001025 | TT-20251022-01093 | Reference_EM | Region_1 | JBL0461 | JBL0461 |  |  |  | Ahmed Salah Abdalgadir Ahmed | 10/22/2025 11:02:41 | 10/22/2025 13:09:20 | 10/22/2025 23:02:41 | Door opening alarm at JBL0461-P2_SRAN @ Sceco | 10/22/2025 11:01:56 | Minor | 65101 | Door opening alarm | 10/22/2025 11:01:52 | P3 | SRAN | jubail | Sceco | 2G NSA | JBL0461 | FLM_EM | [8 empty] | API | 10/22/2025 11:02:41 | 10/22/2025 13:09:20 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000444 | PCM-20251022-00001040 | TT-20251022-01112 | Reference_EM | Region_2 | RIY0620 | RIY0620 | Enviroment | Air Condition | Welding condenser & adding Freon | Kadri Jalal Mohammed Asmail | 10/22/2025 11:14:31 | 10/23/2025 01:04:35 | 10/22/2025 23:14:31 | high temprature 40 at RIY0620-P2_SRAN @ Sceco | 10/22/2025 11:04:09 | Minor | 65103 | high temprature 40 | 10/22/2025 11:04:06 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0620 | FLM_EM | [8 empty] | API | 10/22/2025 11:14:31 | 10/22/2025 23:57:00 | 10/23/2025 00:13:07 | 10/23/2025 00:13:13 | 10/23/2025 00:13:17 | 10/23/2025 01:04:35 |  | Kadri Jalal Mohammed Asmail |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000460 | PCM-20251022-00001091 | TT-20251022-01157 | Reference_EM | Region_1 | SMN0850 | SMN0850 |  |  |  | Rahman Ullah Said Halim | 10/22/2025 11:39:22 | 10/23/2025 15:22:18 | 10/22/2025 23:39:22 | Generator failure at SMN0850-P2-USF_SRAN @ Generator_DG | 10/22/2025 11:31:01 | Minor | 65114 | Generator failure | 10/22/2025 11:28:49 | P2 | SRAN | hafr | Generator_DG | 2G NSA | SMN0850 | FLM_EM | [8 empty] | API | 10/22/2025 11:39:22 | 10/23/2025 15:22:18 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000477 | PCM-20251022-00001132 | TT-20251022-01192 | Reference_EM | Region_2 | HIR0543 | HIR0543 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/22/2025 12:01:01 | 10/22/2025 17:49:51 | 10/23/2025 00:01:01 | high temprature 32 at HIR0543-P2_SRAN @ Sceco | 10/22/2025 11:50:25 | Minor | 65102 | high temprature 32 | 10/22/2025 11:50:21 | P2 | SRAN | riyadh | Sceco | 2G NSA | HIR0543 | FLM_EM | [8 empty] | API | 10/22/2025 12:01:01 | 10/22/2025 17:49:51 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251022000481 | PCM-20251022-00001136 | TT-20251022-01194 | Reference_EM | Region_2 | DLM0481 | DLM0481 |  |  |  | Mohamed Talaat Mohamed Tawfik | 10/22/2025 12:03:36 | 10/22/2025 12:03:36 | 10/23/2025 00:03:36 | Air condition 1 failure alarm at DLM0481-P2_SRAN @ Sceco | 10/22/2025 11:53:07 | Minor | 65104 | Air condition 1 failure alarm | 10/22/2025 11:53:03 | P2 | SRAN | al kharj | Sceco | 2G NSA | DLM0481 | FLM_EM | [8 empty] | API | 10/22/2025 12:03:36 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000492 | PCM-20251022-00001156 | TT-20251022-01216 | Reference_EM | Region_2 | RIY0289 | RIY0289 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/22/2025 12:11:51 | 10/22/2025 12:14:13 | 10/23/2025 00:11:51 | high temprature 32 at RIY0289-P2_SRAN @ Sceco | 10/22/2025 11:22:31 | Minor | 65102 | high temprature 32 | 10/22/2025 12:01:13 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0289 | FLM_EM | [8 empty] | API | 10/22/2025 12:11:51 | 10/22/2025 12:14:13 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000494 | PCM-20251022-00001162 | TT-20251022-01222 | Reference_EM | Region_2 | RIY0928 | RIY0928 |  |  |  | Vignesh Sivakumar Sivakumar | 10/22/2025 12:14:25 | 10/22/2025 14:40:26 | 10/22/2025 18:14:25 | Mains Failure at RIY0928-FWA-P1-VIP_SRAN-FON @ Sceco | 10/22/2025 12:04:20 | Major | 65109 | Mains Failure | 10/22/2025 12:04:16 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0928 | FLM_EM | [8 empty] | API | 10/22/2025 12:14:25 | 10/22/2025 14:40:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251022000498 | PCM-20251022-00001170 | TT-20251022-01228 | Reference_EM | Region_1 | HDQ0029 | HDQ0029 | Enviroment | Rectifier Module | Change rectifer module | Emad Mahmoud Ahmed Mohamed | 10/22/2025 12:20:41 | 10/22/2025 12:42:14 | 10/23/2025 00:20:41 | Battery Faulty at HDQ2M7029-P3-PC @ Power Cube | 10/22/2025 12:10:04 | Minor | 65033 | Battery Faulty | 10/22/2025 12:10:00 | P3 | 4G | hafr | Power Cube | 2G NSA | HDQ2M7029 | FLM_EM | [8 empty] | API | 10/22/2025 12:20:41 | 10/22/2025 12:41:41 | 10/22/2025 12:42:04 |  |  | 10/22/2025 12:42:14 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000511 | PCM-20251022-00001196 | TT-20251022-01255 | EM | Region_1 | KBR0184 | KBR0184 |  |  |  | Abdul Malik Shaik | 10/22/2025 12:35:41 | 10/22/2025 21:43:57 | 10/22/2025 16:35:41 | Mains Failure at KBR0184-P1-HUB-WDM_SRAN-FON @ Sceco | 10/22/2025 12:33:37 | Critical | 65109 | Mains Failure | 10/22/2025 12:33:33 | P1 | SRAN | dammam | Sceco | 2G NSA | KBR0184 | FLM_EM | [8 empty] | API | 10/22/2025 12:35:41 | 10/22/2025 21:43:57 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251022000517 | PCM-20251022-00001207 | TT-20251022-01269 | Reference_EM | Region_2 | RIY0620 | RIY0620 |  |  |  | Pawan Virdi Santokh Singh | 10/22/2025 12:42:50 | 10/22/2025 12:48:07 | 10/23/2025 00:42:50 | Door opening alarm at RIY0620-P2_SRAN @ Sceco | 10/22/2025 12:42:19 | Minor | 65101 | Door opening alarm | 10/22/2025 12:42:14 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0620 | FLM_EM | [8 empty] | API | 10/22/2025 12:42:50 | 10/22/2025 12:48:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000519 | PCM-20251022-00001216 | TT-20251022-01283 | Reference_EM | Region_2 | RIY2327 | RIY2327 |  |  |  | Ahmed Mohamed Ibrahim Elnagar | 10/22/2025 12:49:36 | 10/22/2025 13:47:11 | 10/23/2025 00:49:36 | NETECO: AC Failure at RIY2327 @ Sceco | 10/22/2025 12:42:54 | Minor | 10202 | AC Failure | 10/22/2025 12:42:54 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2327 | FLM_EM | [8 empty] | API | 10/22/2025 12:49:36 | 10/22/2025 13:47:11 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000523 | PCM-20251022-00001225 | TT-20251022-01291 | Reference_EM | Region_2 | RIY2327 | RIY2327 | Enviroment | SCECO_Failure | SCECO auto restored | Mustansar Ali Mushtaq Ahmad | 10/22/2025 12:53:11 | 10/22/2025 14:15:19 | 10/23/2025 00:53:11 | Mains Failure at RIY2327-P2_SRAN @ Sceco | 10/22/2025 12:42:59 | Minor | 65109 | Mains Failure | 10/22/2025 12:42:55 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY2327 | FLM_EM | [8 empty] | API | 10/22/2025 12:53:11 | 10/22/2025 13:41:56 | 10/22/2025 13:42:11 | 10/22/2025 13:42:14 |  | 10/22/2025 14:15:19 |  | Mustansar Ali Mushtaq Ahmad |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000524 | PCM-20251022-00001228 | TT-20251022-01294 | Reference_EM | Region_1 | DAM2066 | DAM2066 |  |  |  | Ahmed Abdelfattah Ali Soltan | 10/22/2025 12:54:15 | 10/22/2025 13:24:32 | 10/22/2025 18:54:15 | Low battery voltage at DAM2066-P1-HUB_SRAN @ Sceco | 10/22/2025 12:43:37 | Major | 65110 | Low battery voltage | 10/22/2025 12:43:34 | P1 | SRAN | dammam | Sceco | 2G NSA | DAM2066 | FLM_EM | [8 empty] | API | 10/22/2025 12:54:15 | 10/22/2025 13:24:32 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000531 | PCM-20251022-00001236 | TT-20251022-01303 | Reference_EM | Region_1 | KBR0166 | KBR0166 |  |  |  | Abdul Malik Shaik | 10/22/2025 13:00:56 | 10/22/2025 21:43:58 | 10/23/2025 01:00:56 | high temprature 32 at KBR0166-P3_SRAN @ Sceco | 10/22/2025 12:50:31 | Minor | 65102 | high temprature 32 | 10/22/2025 12:50:27 | P3 | SRAN | dammam | Sceco | 2G NSA | KBR0166 | FLM_EM | [8 empty] | API | 10/22/2025 13:00:56 | 10/22/2025 21:43:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000533 | PCM-20251022-00001244 | TT-20251022-01320 | Reference_EM | Region_1 | SMN0804 | SMN0804 |  |  |  | Shaker Saied Mohamed ElShafie | 10/22/2025 13:10:19 | 10/22/2025 14:53:43 | 10/23/2025 01:10:19 | Mains Failure at SMN0804-P2_SRAN @ Sceco | 10/22/2025 13:00:14 | Minor | 65109 | Mains Failure | 10/22/2025 13:00:11 | P2 | SRAN | hafr | Sceco | 2G NSA | SMN0804 | FLM_EM | [8 empty] | API | 10/22/2025 13:10:19 | 10/22/2025 14:53:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251022000539 | PCM-20251022-00001262 | TT-20251022-01339 | Reference_EM | Region_1 | HFB0027 | HFB0027 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/22/2025 13:15:56 | 10/22/2025 13:15:56 | 10/23/2025 01:15:56 | Door opening alarm at HFB2M5027-P2 @ Generator_SG | 10/22/2025 13:15:18 | Minor | 65101 | Door opening alarm | 10/22/2025 13:15:15 | P2 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5027 | FLM_EM | [8 empty] | API | 10/22/2025 13:15:56 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251022000538 | PCM-20251022-00001264 | TT-20251022-01337 | Reference_EM | Region_2 | RIY2853 | RIY2853 | Enviroment | Air Condition | Change Outdoor motor | Ahmed Mohamed Ibrahim Elnagar | 10/22/2025 13:15:56 | 10/22/2025 20:54:14 | 10/22/2025 19:15:56 | high temprature 40 at RIY2853-P1-VIP_SRAN @ Generator_SG | 10/22/2025 13:05:36 | Major | 65103 | high temprature 40 | 10/22/2025 13:05:32 | VIP | SRAN | rumah | Generator_SG | 2G NSA | RIY2853 | FLM_EM | [8 empty] | API | 10/22/2025 13:15:56 | 10/22/2025 15:29:31 | 10/22/2025 15:30:28 | 10/22/2025 15:30:32 | 10/22/2025 15:30:49 | 10/22/2025 20:54:14 |  | Ahmed Mohamed Ibrahim Elnagar |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Preparation | CM20251022000546 | PCM-20251022-00001276 | TT-20251022-01342 | Telecom | Region_2 | RIY0928 | RIY0928 |  |  |  | Vignesh Sivakumar Sivakumar | 10/22/2025 13:20:40 | 10/22/2025 15:58:42 | 10/23/2025 01:20:40 | RF Unit Maintenance Link Failure at RIY0928-FWA-P1-VIP_SRAN-FON @ Sceco | 10/22/2025 13:13:09 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 13:11:26 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0928 | FLM_EM |  |  | PCM-20251022-00001267 | power issue at site // Power alarm REPORTED | power issue at site // Power alarm REPORTED |  |  |  | API | 10/22/2025 13:20:40 | 10/22/2025 14:40:26 | 10/22/2025 15:58:36 | 10/22/2025 15:58:38 | 10/22/2025 15:58:42 | [6 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251022000554 | PCM-20251022-00001304 | TT-20251022-01371 | Reference_EM | Region_1 | DAM0321 | DAM0321 |  |  |  | Gamal Hasan Farag Ali Khalifa | 10/22/2025 13:29:56 | 10/22/2025 18:50:59 | 10/23/2025 01:29:56 | Door opening alarm at DAM0321-P2_SRAN @ Sceco | 10/22/2025 13:29:28 | Minor | 65101 | Door opening alarm | 10/22/2025 13:26:51 | P2 | SRAN | dammam | Sceco | 2G NSA | DAM0321 | FLM_EM | [8 empty] | API | 10/22/2025 13:29:56 | 10/22/2025 18:50:59 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Dispatched | CM20251022000555 | PCM-20251022-00001307 | TT-20251022-01373 | Reference_EM | Region_1 | HFB0027 | HFB0027 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/22/2025 13:30:25 | 10/22/2025 13:30:25 | 10/23/2025 01:30:25 | Mains Failure at HFB2M5027-P2 @ Generator_SG | 10/22/2025 13:20:17 | Minor | 65109 | Mains Failure | 10/22/2025 13:20:13 | P2 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5027 | FLM_EM | [8 empty] | API | 10/22/2025 13:30:25 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000556 | PCM-20251022-00001309 | TT-20251022-01375 | Reference_EM | Region_2 | RIY0446 | RIY0446 |  |  |  | Tanveer Ahmad Muhammad Ishaq | 10/22/2025 13:31:25 | 10/22/2025 17:49:52 | 10/23/2025 01:31:25 | Minor Rec alarm at RIY0446-P2_SRAN @ Sceco | 10/22/2025 13:21:09 | Minor | 65108 | Minor Rec alarm | 10/22/2025 13:21:06 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0446 | FLM_EM | [8 empty] | API | 10/22/2025 13:31:25 | 10/22/2025 17:49:52 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000557 | PCM-20251022-00001310 | TT-20251022-01376 | EM | Region_2 | RIY0928 | RIY0928 |  |  |  | Vignesh Sivakumar Sivakumar | 10/22/2025 13:31:27 | 10/22/2025 14:40:27 | 10/22/2025 17:31:27 | TEMP_OVER at RIY0928-OCS1 @ Sceco | 10/22/2025 13:29:42 | Critical | 1-28 | TEMP_OVER | 10/22/2025 13:29:31 | P2 | SRAN | riyadh | Sceco | DWDM NSA | RIY0928 | FLM_EM | [5 empty] | 0-1-C-1-F1OPM8-OTHER |  |  | API | 10/22/2025 13:31:27 | 10/22/2025 14:40:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251022000565 | PCM-20251022-00001327 | TT-20251022-01396 | Reference_EM | Region_2 | JMJ0022 | JMJ0022 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Moustafa Aboelmagd Hefny | 10/22/2025 13:38:11 | 10/22/2025 18:46:51 | 10/23/2025 01:38:11 | Air-Condition #1 FA(SH2) at JMJ2M7022-P3 @ Sceco | 10/22/2025 13:32:07 | Minor | 65052 | Air-Condition #1 FA(SH2) | 10/22/2025 13:27:47 | P3 | 4G | majma | Sceco | LTE NSA | JMJ2M7022 | FLM_EM | [8 empty] | API | 10/22/2025 13:38:11 | 10/22/2025 17:11:27 | 10/22/2025 18:46:44 |  |  | 10/22/2025 18:46:51 |  | Mohamed Moustafa Aboelmagd Hefny |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000587 | PCM-20251022-00001374 | TT-20251022-01438 | Reference_EM | Region_1 | SMRY2814 | SMRY2814 |  |  |  | Shaker Saied Mohamed ElShafie | 10/22/2025 13:52:36 | 10/22/2025 14:53:43 | 10/23/2025 01:52:36 | Door opening alarm at SMRY2814-P2_SRAN @ Sceco | 10/22/2025 13:51:47 | Minor | 65101 | Door opening alarm | 10/22/2025 13:46:14 | P2 | SRAN | hafr | Sceco | 2G NSA | SMRY2814 | FLM_EM | [8 empty] | API | 10/22/2025 13:52:36 | 10/22/2025 14:53:43 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251022000592 | PCM-20251022-00001377 | TT-20251022-01442 | Reference_EM | Region_1 | HFR2197 | HFR2197 | Enviroment | Air Condition | Change Fan | Ibrahim Ù Abdulfttah Ibrahim | 10/22/2025 13:53:41 | 10/23/2025 09:36:52 | 10/23/2025 01:53:41 | Air condition 2 failure alarm at HFR2197-P2_SRAN @ Sceco | 10/22/2025 13:43:08 | Minor | 65105 | Air condition 2 failure alarm | 10/22/2025 13:43:03 | P2 | SRAN | hafr | Sceco | 2G NSA | HFR2197 | FLM_EM | [8 empty] | API | 10/22/2025 13:53:41 | 10/22/2025 21:27:03 | 10/23/2025 09:36:15 |  |  | 10/23/2025 09:36:52 |  | Ibrahim Ù Abdulfttah Ibrahim |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000594 | PCM-20251022-00001392 | TT-20251022-01454 | EM | Region_2 | RIY0928 | RIY0928 |  |  |  | Adham Adham Hassan Farghal | 10/22/2025 13:57:46 | 10/22/2025 18:44:26 | 10/22/2025 17:57:46 | RIY0928 NCE NODE ISOLATED and connected links are down | 10/22/2025 13:55:57 | Critical | 0-4 | GNE_CONNECT_FAIL | 10/22/2025 13:55:54 | P2 | SRAN | riyadh | Sceco | DWDM NSA | RIY0928 | FLM_EM | [5 empty] | Connection with gateway RIY0928-OCS1 failed |  |  | API | 10/22/2025 13:57:46 | 10/22/2025 18:44:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Request_Resolved | CM20251022000595 | PCM-20251022-00001396 | TT-20251022-01457 | Reference_EM | Region_1 | ARR0652 | ARR0652 | Enviroment | SCECO_Failure | SCECO auto restored | Mohamed Ahmed Goda | 10/22/2025 13:58:50 | 10/22/2025 16:44:55 | 10/22/2025 19:58:50 | Mains Failure at ARR0652-FWA-P1-VIP_SRAN-PC @ Sceco | 10/22/2025 13:48:40 | Major | 65109 | Mains Failure | 10/22/2025 13:48:36 | P3 | SRAN | arar | Sceco | 2G NSA | ARR0652 | FLM_EM | [8 empty] | API | 10/22/2025 13:58:50 | 10/22/2025 14:04:38 | 10/22/2025 14:04:47 | 10/22/2025 14:17:57 | 10/22/2025 14:18:00 | 10/22/2025 16:44:55 |  | Mohamed Ahmed Goda |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000597 | PCM-20251022-00001403 | TT-20251022-01463 | Reference_EM | Region_2 | RIY0303 | RIY0303 |  |  |  | RANJEET KUMAR YADAV | 10/22/2025 14:00:56 | 10/23/2025 10:34:58 | 10/23/2025 02:00:56 | Door opening alarm at RIY0303-P3_SRAN @ Generator_SG | 10/22/2025 14:00:15 | Minor | 65101 | Door opening alarm | 10/22/2025 14:00:11 | P3 | SRAN | riyadh | Generator_SG | 2G NSA | RIY0303 | FLM_EM | [8 empty] | API | 10/22/2025 14:00:56 | 10/23/2025 10:34:58 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000598 | PCM-20251022-00001404 | TT-20251022-01447 | Telecom | Region_2 | RIY0928 | RIY0928 |  |  |  | Adham Adham Hassan Farghal | 10/22/2025 14:01:00 | 10/22/2025 18:44:27 | 10/23/2025 02:01:00 | BBU DC Output Out of Range at RIY0928-FWA-P1-VIP_SRAN-FON @ Sceco | 10/22/2025 13:51:40 | Minor | 26112 | BBU DC Output Out of Range | 10/22/2025 13:50:08 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0928 | FLM_EM |  |  | PCM-20251022-00001382 | power issue at site // Power alarm REPORTED | power issue at site // Power alarm REPORTED |  |  |  | API | 10/22/2025 14:01:00 | 10/22/2025 18:44:27 | [9 empty] | EM | LATIS |  | Running |  | Inspur | High
Delivered | CM20251022000599 | PCM-20251022-00001405 | TT-20251022-01464 | Reference_EM | Region_2 | RIY0259 | RIY0259 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/22/2025 14:01:25 | 10/22/2025 20:30:25 | 10/23/2025 02:01:25 | high temprature 32 at RIY0259-P2_SRAN @ Sceco | 10/22/2025 13:51:08 | Minor | 65102 | high temprature 32 | 10/22/2025 13:51:04 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0259 | FLM_EM | [8 empty] | API | 10/22/2025 14:01:25 | 10/22/2025 20:30:25 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000607 | PCM-20251022-00001423 | TT-20251022-01480 | Reference_EM | Region_2 | RIY0624 | RIY0624 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/22/2025 14:08:36 | 10/22/2025 20:30:26 | 10/23/2025 02:08:36 | Mains Failure at RIY0624-P2_SRAN @ Sceco | 10/22/2025 13:58:21 | Minor | 65109 | Mains Failure | 10/22/2025 13:58:17 | P2 | SRAN | riyadh | Sceco | 2G NSA | RIY0624 | FLM_EM | [8 empty] | API | 10/22/2025 14:08:36 | 10/22/2025 20:30:26 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000627 | PCM-20251022-00001444 | TT-20251022-01496 | Reference_EM | Region_1 | JBL0565 | JBL0565 | Enviroment | Fire Alarm | Reset Fire Pannel | Mohamed Abdalgader farah Rahmtalla | 10/22/2025 14:17:55 | 10/23/2025 13:28:55 | 10/23/2025 02:17:55 | Door opening alarm at JBL0565-P2-USF_SRAN-PC @ Power Cube | 10/22/2025 14:17:22 | Minor | 65101 | Door opening alarm | 10/22/2025 14:17:19 | P2 | SRAN | dammam | Power Cube | 2G NSA | JBL0565 | FLM_EM | [8 empty] | API | 10/22/2025 14:17:55 | 10/22/2025 23:44:55 | 10/23/2025 11:43:10 | 10/23/2025 11:43:15 | 10/23/2025 11:43:18 | 10/23/2025 13:28:55 |  | Mohamed Abdalgader farah Rahmtalla |  |  |  | EM | LATIS |  | Running |  | Inspur | Low
Delivered | CM20251022000634 | PCM-20251022-00001461 | TT-20251022-01511 | Reference_EM | Region_2 | MZH0567 | MZH0567 |  |  |  | Ahmed Hamada Mohamed Awad Abouhatab | 10/22/2025 14:26:11 | 10/22/2025 23:09:07 | 10/23/2025 02:26:11 | Door opening alarm at MZH0567-P2-USF_SRAN-PC @ Power Cube | 10/22/2025 14:25:45 | Minor | 65101 | Door opening alarm | 10/22/2025 14:25:40 | P2 | SRAN | quweyah | Power Cube | 2G NSA | MZH0567 | FLM_EM | [8 empty] | API | 10/22/2025 14:26:11 | 10/22/2025 23:09:07 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Low
Request_Resolved | CM20251022000639 | PCM-20251022-00001470 | TT-20251022-01520 | Reference_EM | Region_2 | RIY0020 | RIY0020 | Enviroment | Air Condition | Change Fan | Ahmed Khalifa Amin Aboueltaher | 10/22/2025 14:31:21 | 10/24/2025 03:26:20 | 10/22/2025 20:31:21 | Air condition 1 failure alarm at RIY0020-P1-DIA_SRAN @ Sceco | 10/22/2025 14:20:43 | Major | 65104 | Air condition 1 failure alarm | 10/22/2025 14:20:40 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0020 | FLM_EM | [8 empty] | API | 10/22/2025 14:31:21 | 10/24/2025 03:07:04 | 10/24/2025 03:07:18 | 10/24/2025 03:07:21 | 10/24/2025 03:07:23 | 10/24/2025 03:26:20 |  | Ahmed Khalifa Amin Aboueltaher |  |  |  | EM | LATIS |  | Running |  | Inspur | Medium
Delivered | CM20251022000650 | PCM-20251022-00001494 | TT-20251022-01540 | Reference_EM | Region_2 | MUZ0144 | MUZ0144 |  |  |  | Omar Fathy Mahmoud Elsayed | 10/22/2025 14:48:56 | 10/22/2025 20:20:06 | 10/23/2025 02:48:56 | Door opening alarm at MUZ2M5144-P3 @ Generator_SG | 10/22/2025 14:48:27 | Minor | 65101 | Door opening alarm | 10/22/2025 14:48:25 | P3 | 2G | al rass | Generator_SG | 2G NSA | MUZ2M5144 | FLM_EM | [8 empty] | API | 10/22/2025 14:48:56 | 10/22/2025 20:20:06 | [9 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Dispatched | CM20251022000653 | PCM-20251022-00001500 | TT-20251022-01546 | Reference_EM | Region_1 | HFB0030 | HFB0030 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/22/2025 14:50:01 | 10/22/2025 14:50:01 | 10/23/2025 02:50:01 | Door opening alarm at HFB2M5030-P3 @ Generator_SG | 10/22/2025 14:49:15 | Minor | 65101 | Door opening alarm | 10/22/2025 14:49:13 | P3 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5030 | FLM_EM | [8 empty] | API | 10/22/2025 14:50:01 | [10 empty] | EM | LATIS |  | Running |  | Inspur | Medium
Request_Resolved | CM20251022000658 | PCM-20251022-00001508 | TT-20251022-01554 | Telecom | Region_4 | JED1MN0027 | JED0027 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Mohammed Ramadan A Abu Abid | 10/22/2025 14:53:21 | 10/23/2025 08:54:49 | 10/22/2025 20:53:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN0027-NR2.6-P3 @ Sceco | 10/22/2025 14:52:26 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:52:18 | P1 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN0027 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 14:53:21 | 10/22/2025 15:25:57 | 10/22/2025 15:44:33 | 10/22/2025 15:44:35 | 10/22/2025 15:46:06 | 10/23/2025 08:54:49 |  | Mohammed Ramadan A Abu Abid |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000659 | PCM-20251022-00001509 | TT-20251022-01555 | EM | [7 empty] | 10/22/2025 14:53:52 | 10/22/2025 14:53:52 | 10/22/2025 18:53:52 | DOOR OPEN at BISHA-SEC0012_OCS @ Sceco | 10/22/2025 14:53:30 | Critical | 1-12307 | DOOR OPEN | 10/22/2025 14:53:20 | P1 | DWDM |  | Sceco | DWDM NSA | BISHA | FLM_EM | [5 empty] | 0-TO AL-ALAYA-SEC0011(1-A)-72-E1EFI-[DOOR OPEN]:1 |  |  | API | 10/22/2025 14:53:52 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000661 | PCM-20251022-00001512 | TT-20251022-01559 | Telecom | Region_2 | RIY2208 | RIY2208 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Mubashar Farooq Abdul Majeed | 10/22/2025 14:55:25 | 10/22/2025 17:33:18 | 10/23/2025 02:55:25 | RF Unit ALD Current Out of Range at RIY2208-P1-VIP-SRAN @ Generator_SG | 10/22/2025 14:52:56 | Minor | 26530 | RF Unit ALD Current Out of Range | 10/22/2025 14:51:18 | VIP | SRAN | riyadh | Generator_SG | 2G NSA | RIY2208 | FLM_TE | [8 empty] | API | 10/22/2025 14:55:25 | 10/22/2025 15:01:18 | 10/22/2025 17:32:27 |  |  | 10/22/2025 17:33:18 |  | Mubashar Farooq Abdul Majeed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000662 | PCM-20251022-00001513 | TT-20251022-01560 | Telecom | Region_4 | HJR1M7231 | HJR0231 |  |  |  | Khizer Hayat | 10/22/2025 14:55:56 | 10/22/2025 16:24:47 | 10/23/2025 02:55:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at HJR1M7231-G9-NL8-L18-NL21-SBTS-P2-USF-WBB-G3 @ Sceco | 10/22/2025 14:54:59 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:54:54 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | HJR1M7231 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 14:55:56 | 10/22/2025 16:24:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000663 | PCM-20251022-00001514 | TT-20251022-01190 | Reference_telecom | Region_2 | BUR0038 | BUR0038 | Transsmission | MW_RSL_fading | Link Alignment Issue | Raise Ahmed Nisar Ahmed | 10/22/2025 14:56:04 | 10/23/2025 06:42:42 | 10/23/2025 02:56:04 | External Clock Reference Problem at BUR0038-P2_SRAN @ Sceco | 10/22/2025 09:02:50 | Minor | 26262 | External Clock Reference Problem | 10/22/2025 08:59:27 | P2 | SRAN | buraidah | Sceco | 2G NSA | BUR0038 | FLM_TE |  | Dear TX Team kindly check as alarm flapped active with TX alarms | PCM-20251022-00001493 | Already shared BUR0038-BUR0023 | Already shared BUR0038-BUR0023 |  |  |  | API | 10/22/2025 14:56:04 | 10/22/2025 17:10:05 | 10/23/2025 06:42:09 |  |  | 10/23/2025 06:42:42 |  | Raise Ahmed Nisar Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000664 | PCM-20251022-00001515 | TT-20251022-01561 | Telecom | Region_6 | JIZ0245 | JIZ0245 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Mohammed Sideag Mohammed Ali | 10/22/2025 14:56:28 | 10/22/2025 17:42:42 | 10/22/2025 20:56:28 | LAN_LOC at JIZ0245-OCS1 @ Sceco | 10/22/2025 14:51:05 | Major | 1-12926 | LAN_LOC | 10/22/2025 14:50:53 | P1 | 2G | jizan | Sceco | DWDM NSA | JIZ0245 | FLM_TE | [5 empty] | 0-1-C-60-Z5SCC-1(ETH1/ETH1)-COM:1 |  |  | API | 10/22/2025 14:56:28 | 10/22/2025 17:34:42 | 10/22/2025 17:42:30 |  |  | 10/22/2025 17:42:42 |  | Mohammed Sideag Mohammed Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000665 | PCM-20251022-00001520 | TT-20251022-01567 | EM | Region_4 | HJR1M7231 | HJR0231 |  |  |  | Alaa Hassan Mohammed Gad | 10/22/2025 15:00:35 | 10/22/2025 15:00:35 | 10/23/2025 03:00:35 | RECTIFIER MAINS POWER FAILURE at HJR1M7231-G9-NL8-L18-NL21-SBTS-P2-USF-WBB-G3 @ Sceco | 10/22/2025 14:52:35 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 14:52:30 | P3 | 4G | jeddah | Sceco | LTE NSA | HJR1M7231 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 15:00:35 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000668 | PCM-20251022-00001527 | TT-20251022-01574 | Telecom | Region_3 | MDN0785-CSG-01 | MDN0785 |  |  |  | Hamayo Din Jalal | 10/22/2025 15:03:41 | 10/22/2025 15:48:13 | 10/22/2025 19:03:41 | The Device is offline at MDN0785-CSG-01 @ Sceco | 10/22/2025 15:03:23 | Critical | 101-7 | The Device is offline | 10/22/2025 15:03:21 | P1 | IPRAN | madinah | Sceco | IPRAN SA | MDN0785-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 15:03:41 | 10/22/2025 15:48:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000669 | PCM-20251022-00001528 | TT-20251022-01575 | Telecom | Region_3 | MDN0706-ASG-01 | MDN0706 |  |  |  | Hamayo Din Jalal | 10/22/2025 15:03:42 | 10/22/2025 15:48:13 | 10/22/2025 19:03:42 | The Device is offline at MDN0706-ASG-01 @ Sceco | 10/22/2025 15:03:23 | Critical | 101-7 | The Device is offline | 10/22/2025 15:03:21 | P1 | IPRAN | madinah | Sceco | IPRAN SA | MDN0706-ASG-01 | FLM_TE | [8 empty] | API | 10/22/2025 15:03:42 | 10/22/2025 15:48:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000670 | PCM-20251022-00001529 | TT-20251022-01576 | Telecom | Region_3 | MDN0783-CSG-01 | MDN0783 |  |  |  | Hamayo Din Jalal | 10/22/2025 15:03:42 | 10/22/2025 15:48:14 | 10/22/2025 19:03:42 | The Device is offline at MDN0783-CSG-01 @ Sceco | 10/22/2025 15:03:23 | Critical | 101-7 | The Device is offline | 10/22/2025 15:03:21 | P1 | IPRAN | madinah | Sceco | IPRAN SA | MDN0783-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 15:03:42 | 10/22/2025 15:48:14 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000675 | PCM-20251022-00001538 | TT-20251022-01581 | EM | Region_4 | JED6020 | JED6020 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/22/2025 15:08:52 | 10/22/2025 20:21:10 | 10/23/2025 03:08:52 | AIRCON 2 FAILURE at JED6020-GSM-P3 @ Sceco | 10/22/2025 15:00:33 | Minor | 7103 | AIRCON 2 FAILURE | 10/22/2025 15:00:27 | P3 | 2G | jeddah | Sceco | 2G NSA | JED6020 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/22/2025 15:08:52 | 10/22/2025 20:21:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000676 | PCM-20251022-00001539 | TT-20250811-02077 | MW_HC | Region_2 | RIY2657 | RIY2657 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/22/2025 15:09:00 | 10/23/2025 10:39:04 | 10/23/2025 03:09:00 | Huawei MW HC_P2 Observing Errors at RIY2657-RYD2013 | 08/11/2025 15:23:29 | Minor |  | LOF | 08/11/2025 15:23:29 | P1 | SRAN | riyadh | Sceco | TX NSA | RIY2657-RYD2013 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251022-00001391 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/22/2025 15:09:00 | 10/23/2025 10:39:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000677 | PCM-20251022-00001540 | TT-20251022-01582 | Telecom | Region_6 | MKW0037 | MKW0037 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/22/2025 15:09:22 | 10/23/2025 16:21:43 | 10/23/2025 03:09:22 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKW0037-G9-L8-L18-L21-NR2.6-SBTS-P3 @ Sceco | 10/22/2025 15:08:38 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 15:08:35 | P3 | 2G | makhwa | Sceco | 5G_Cell SA | MKW0037 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 15:09:22 | 10/22/2025 16:23:21 | 10/23/2025 16:21:28 |  |  | 10/23/2025 16:21:43 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000678 | PCM-20251022-00001541 | TT-20250907-01669 | MW_HC | Region_2 | RYD0940 | RYD0940 |  |  |  | Ejaz Hussain Muhammad Sharif | 10/22/2025 15:09:45 | 10/23/2025 10:39:05 | 10/23/2025 03:09:45 | Huawei MW HC_P0 Observing Errors at RYD0940-RYD0942 | 09/07/2025 17:02:01 | Minor |  | LOF | 09/07/2025 17:02:01 | P1 | SRAN | rumah | Generator_DG | TX NSA | RYD0940-RYD0942 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251022-00001394 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/22/2025 15:09:45 | 10/23/2025 10:39:05 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000679 | PCM-20251022-00001542 | TT-20251022-01583 | EM | [7 empty] | 10/22/2025 15:09:53 | 10/22/2025 15:09:53 | 10/22/2025 19:09:53 | AIR CONDITION FAIL ALARM at BISHA-SEC0012_OCS @ Sceco | 10/22/2025 15:08:10 | Critical | 1-12307 | AIR CONDITION FAIL ALARM | 10/22/2025 15:08:00 | P1 | DWDM |  | Sceco | DWDM NSA | BISHA | FLM_EM | [5 empty] | 0-TO AL-ALAYA-SEC0011(1-A)-72-E1EFI-[AIR CONDITION FAIL ALARM]:2 |  |  | API | 10/22/2025 15:09:53 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000680 | PCM-20251022-00001544 | TT-20250922-01794 | MW_HC | Region_2 | RYQ0977 | RYQ0977 |  |  |  | Muhammad Tahir Abdulrazzaq | 10/22/2025 15:11:19 | 10/22/2025 15:11:19 | 10/23/2025 03:11:19 | Huawei MW HC_P2 Observing Errors at RYQ0977-RYQ0970 | 09/22/2025 17:07:36 | Minor |  | LOF | 09/22/2025 17:07:36 | P3 | SRAN | majma | Generator_DG | TX NSA | RYQ0977-RYQ0970 | FLM_TE |  | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | PCM-20251022-00001400 | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA | Request missing data:HC times , clearance time >= 1 hr snapshot, Actions + RCA |  |  |  | API | 10/22/2025 15:11:19 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000681 | PCM-20251022-00001548 | TT-20251022-01588 | Telecom | Region_4 | TAF2405 | TAF2405 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 15:13:00 | 10/22/2025 17:30:07 | 10/23/2025 03:13:00 | BASE STATION SERVICE PROBLEM (No connection to unit) at TAF2405-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/22/2025 15:11:53 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 15:11:43 | P2 | 2G | taif | Sceco | 5G_Cell SA | TAF2405 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 15:13:00 | 10/22/2025 17:30:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000682 | PCM-20251022-00001549 | TT-20251022-01589 | Telecom | Region_6 | ABH0171 | ABH0171 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Amir Sohail | 10/22/2025 15:14:01 | 10/22/2025 15:57:57 | 10/22/2025 21:14:01 | BASE STATION SERVICE PROBLEM (No connection to unit) at ABH0171-G9-L18-L21-NR2.6-P2 @ Generator_SG | 10/22/2025 15:13:08 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 15:13:01 | P2 | 2G | abha | Generator_SG | 5G_Cell SA | ABH0171 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 15:14:01 | 10/22/2025 15:28:09 | 10/22/2025 15:57:51 |  |  | 10/22/2025 15:57:57 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000683 | PCM-20251022-00001550 | TT-20251022-01590 | Telecom | Region_4 | JED0514 | JED0514 |  |  |  | Mohammed Altaf Naveed AbdulHakeem | 10/22/2025 15:14:32 | 10/22/2025 15:14:32 | 10/23/2025 03:14:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0514-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 @ Sceco | 10/22/2025 15:13:27 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 15:13:24 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0514 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 15:14:32 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000685 | PCM-20251022-00001553 | TT-20251022-01586 | EM | Region_6 | NMR2014 | NMR2014 |  |  |  | Mohammed Ahmed Abdulrahman M Harran | 10/22/2025 15:16:33 | 10/22/2025 15:16:33 | 10/22/2025 21:16:33 | 1(2G/LTE) sites down under NMR2014-P3/NMR2014-P3 @ Generator_SG | 10/22/2025 15:08:25 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 15:08:23 | P3 | 2G | Albaha | Generator_SG | 2G_LTE SA | NMR2014-P3 | FLM_EM | NMR2014 | Results: DOWN SITE HUB NMR2014-P3 NMR2014 Summary: Hub: NMR2014, Down Count: 1, Down Sites: NMR2014-P3 Alarm Summary: NMR2014 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 15:16:33 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000686 | PCM-20251022-00001555 | TT-20251022-01595 | Reference_EM | Region_3 | DBTB2M5270 | DBTB0270 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Walid Attia Shahata Alim | 10/22/2025 15:17:38 | 10/23/2025 17:51:22 | 10/22/2025 21:17:38 | Mains Failure at DBTB2M5270-P1-HUB @ Generator_DG | 10/22/2025 15:07:46 | Major | 65109 | Mains Failure | 10/22/2025 15:07:35 | P1 | 2G | tabouk | Generator_DG | 2G NSA | DBTB2M5270 | FLM_EM | [8 empty] | API | 10/22/2025 15:17:38 | 10/23/2025 00:00:59 | 10/23/2025 17:51:07 | 10/23/2025 17:51:09 |  | 10/23/2025 17:51:22 |  | Walid Attia Shahata Alim |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000688 | PCM-20251022-00001558 | TT-20251022-01568 | Telecom | Region_4 | JED0539 | JED0539 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 15:19:45 | 10/22/2025 15:19:45 | 10/23/2025 03:19:45 | BASE STATION ANTENNA LINE PROBLEM at JED0539-G9-L8-L18-L21-NR2.6-NR3.6-SBTS-P2 @ Sceco | 10/22/2025 14:53:47 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/22/2025 14:53:41 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0539 | FLM_TE |  |  | PCM-20251022-00001521 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/22/2025 15:19:45 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000689 | PCM-20251022-00001559 | TT-20251022-01570 | Reference_telecom | Region_6 | BHAB1M7819 | BHAB0819 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/22/2025 15:20:34 | 10/22/2025 16:12:10 | 10/23/2025 03:20:34 | BASE STATION SERVICE PROBLEM (Not able to synchronize baseband bus) at BHAB1M7819-G9-U9-L8-L18-SBTS-P3 @ Sceco | 10/22/2025 14:57:33 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 14:57:23 | P3 | 4G | makhwa | Sceco | 5G_Cell SA | BHAB1M7819 | FLM_TE |  |  | PCM-20251022-00001524 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 15:20:34 | 10/22/2025 16:11:39 | 10/22/2025 16:12:00 |  |  | 10/22/2025 16:12:10 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000691 | PCM-20251022-00001563 | TT-20251022-01591 | Telecom | Region_6 | ABH1M7361 | ABH0361 | Equipment | BTS_Cable | Replace Sync Cable | Amir Sohail | 10/22/2025 15:22:47 | 10/22/2025 17:02:02 | 10/23/2025 03:22:47 | BASE STATION ANTENNA LINE PROBLEM at ABH1M7361-CA-L800-SBTS-P3 @ Sceco | 10/22/2025 15:07:50 | Minor | 7113 | BASE STATION ANTENNA LINE PROBLEM | 10/22/2025 15:07:45 | P3 | 4G | abha | Sceco | LTE NSA | ABH1M7361 | FLM_TE |  |  | PCM-20251022-00001551 | FLM need to check ALD and VSWR issue at site. | FLM need to check ALD and VSWR issue at site. |  |  |  | API | 10/22/2025 15:22:47 | 10/22/2025 15:28:10 | 10/22/2025 17:01:27 |  |  | 10/22/2025 17:02:02 |  | Amir Sohail |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000693 | PCM-20251022-00001566 | TT-20251022-01607 | EM | Region_6 | BAH1M8159 | BAH2159 |  |  |  | Arif Ullah Shah | 10/22/2025 15:24:21 | 10/22/2025 15:24:47 | 10/23/2025 03:24:21 | SHELTER DOOR OPEN at BAH1M8159-G9-L8-L18-SBTS @ Generator_SG | 10/22/2025 15:23:44 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 15:23:40 | P3 | 4G | Baha | Generator_SG | LTE NSA | BAH1M8159 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 15:24:21 | 10/22/2025 15:24:47 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000696 | PCM-20251022-00001573 | TT-20251022-01613 | Telecom | Region_4 | JED0001 | JED0001 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 15:29:32 | 10/22/2025 17:21:34 | 10/22/2025 21:29:32 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0001-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-DIA-HUB-WDM-USF-FON @ Sceco | 10/22/2025 15:28:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 15:28:17 | P1 | 2G | jeddah | Sceco | 5G_Cell SA | JED0001 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 15:29:32 | 10/22/2025 17:21:34 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000697 | PCM-20251022-00001575 | TT-20251022-01615 | EM | Region_6 | MTB1M8377 | MTB2377 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 15:31:04 | 10/22/2025 18:29:49 | 10/23/2025 03:31:04 | RECTIFIER MAINS POWER FAILURE at MTB1M8377-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 15:22:50 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 15:22:45 | P2 | 4G | Baha | Sceco | LTE NSA | MTB1M8377 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 15:31:04 | 10/22/2025 18:29:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000698 | PCM-20251022-00001576 | TT-20251022-01616 | Telecom | Region_3 | MDN0706-ASG-01 | MDN0706 |  |  |  | Hamayo Din Jalal | 10/22/2025 15:31:05 | 10/22/2025 15:48:15 | 10/22/2025 19:31:05 | Card Invalid at MDN0706-ASG-01 @ Sceco | 10/22/2025 15:30:12 | Critical | 101-2505218 | Card Invalid | 10/22/2025 15:29:42 | P1 | IPRAN | madinah | Sceco | IPRAN SA | MDN0706-ASG-01 | FLM_TE | [8 empty] | API | 10/22/2025 15:31:05 | 10/22/2025 15:48:15 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000700 | PCM-20251022-00001580 | TT-20251022-01170 | Reference_telecom | Region_6 | AQQ0058 | AQQ0058 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/22/2025 15:32:36 | 10/23/2025 16:21:17 | 10/22/2025 21:32:36 | TRX OPERATION DEGRADED (FF FF FF FF FF FF shared:S) at AQQ0058-P2 @ Sceco | 10/22/2025 11:43:25 | Major | 7607 | TRX OPERATION DEGRADED | 10/22/2025 11:43:21 | P2 | 2G | Albaha | Sceco | 2G_TRX NSA | AQQ0058 | FLM_TE |  |  | PCM-20251022-00001112 | please check RSSI locally | please check RSSI locally |  |  |  | API | 10/22/2025 15:32:36 | 10/22/2025 16:23:22 | 10/23/2025 16:21:07 |  |  | 10/23/2025 16:21:17 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000701 | PCM-20251022-00001586 | TT-20251022-01634 | EM | Region_6 | ABBS1M8096 | ABBS2096 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 15:38:19 | 10/22/2025 18:29:50 | 10/23/2025 03:38:19 | SHELTER DOOR OPEN at ABBS1M8096-P3-L800-SBTS-WBB-G3 @ Sceco | 10/22/2025 15:37:53 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 15:37:47 | P3 | 4G | Albaha | Sceco | LTE NSA | ABBS1M8096 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 15:38:19 | 10/22/2025 18:29:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000702 | PCM-20251022-00001587 | TT-20251022-01633 | Reference_EM | Region_3 | DBTB2M5276 | DBTB0276 | Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance | Mohammad Mahmoud Abdelazim Tawfic | 10/22/2025 15:38:20 | 10/23/2025 15:22:45 | 10/23/2025 03:38:20 | Door opening alarm at DBTB2M5276-P3 @ Sceco | 10/22/2025 15:38:01 | Minor | 65101 | Door opening alarm | 10/22/2025 15:37:58 | P3 | 2G | tabouk | Sceco | 2G NSA | DBTB2M5276 | FLM_EM | [8 empty] | API | 10/22/2025 15:38:20 | 10/23/2025 12:32:08 | 10/23/2025 15:22:21 |  |  | 10/23/2025 15:22:45 |  | Mohammad Mahmoud Abdelazim Tawfic |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000704 | PCM-20251022-00001589 | TT-20251022-01639 | Reference_EM | Region_3 | AHT2153 | AHT2153 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/22/2025 15:38:49 | 10/22/2025 16:40:46 | 10/23/2025 03:38:49 | Door opening alarm at AHT2153-P3_SRAN @ Sceco | 10/22/2025 15:38:30 | Minor | 65101 | Door opening alarm | 10/22/2025 15:38:25 | P3 | SRAN | hail | Sceco | 2G NSA | AHT2153 | FLM_EM | [8 empty] | API | 10/22/2025 15:38:49 | 10/22/2025 16:40:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251022000706 | PCM-20251022-00001592 | TT-20251022-01642 | Telecom | Region_4 | JED0134 | JED0134 |  |  |  | Abdulraqib Abdo Saif Abdulaleem | 10/22/2025 15:39:51 | 10/23/2025 14:24:29 | 10/22/2025 19:39:51 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0134-G9-L8-L18-L21-NR2.6-NR3.5-P1-HUB-WDM-FON @ Sceco_STB | 10/22/2025 15:38:49 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 15:38:39 | P1 | 2G | jeddah | Sceco_STB | 5G_Cell SA | JED0134 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 15:39:51 | 10/23/2025 14:17:57 | 10/23/2025 14:24:25 | 10/23/2025 14:24:27 | 10/23/2025 14:24:29 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000707 | PCM-20251022-00001594 | TT-20251022-01626 | Telecom | Region_6 | GHM1M3452 | GHM0452 | Equipment | BSS_HW_Stuck | Reset RRU | SHAH KHALID | 10/22/2025 15:40:31 | 10/22/2025 16:50:28 | 10/22/2025 21:40:31 | 1(3G) sites down under GHM0452-P3/GHM1M3452-P3 @ Sceco | 10/22/2025 15:32:47 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 15:32:08 | P3 | 3G | Albaha | Sceco | 3G SA | GHM0452-P3 | FLM_TE |  | Results: DOWN SITE HUB GHM0452-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/22/2025 15:40:31 | 10/22/2025 16:11:40 | 10/22/2025 16:50:13 |  |  | 10/22/2025 16:50:28 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000708 | PCM-20251022-00001596 | TT-20251022-01641 | Telecom | Region_6 | KMS1M7032 | KMS0032 | Equipment | CB_BTS | Change Port on FPFH | Muhammad shafiq Muhammad Rasheed | 10/22/2025 15:45:30 | 10/22/2025 19:42:39 | 10/23/2025 03:45:30 | CELL SERVICE PROBLEM (Cell configuration data distribution failed) at KMS1M7032-G9-L8-L18-L21-SBTS-P2 @ Sceco | 10/22/2025 15:34:56 | Minor | 7114 | CELL SERVICE PROBLEM | 10/22/2025 15:34:46 | P2 | 4G | khamis mushyet | Sceco | 5G_Cell SA | KMS1M7032 | FLM_TE |  |  | PCM-20251022-00001591 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/22/2025 15:45:30 | 10/22/2025 18:43:02 | 10/22/2025 18:44:21 | 10/22/2025 18:44:25 | 10/22/2025 18:44:34 | 10/22/2025 19:42:39 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000710 | PCM-20251022-00001601 | TT-20251022-01644 | Telecom | Region_4 | RAB1MN0662 | RAB0662 |  |  |  | Khizer Hayat | 10/22/2025 15:49:32 | 10/22/2025 16:24:48 | 10/22/2025 21:49:32 | 1(5G) sites down under RAB0662-NR2.6-P3 @ Sceco | 10/22/2025 15:41:11 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 15:41:09 | P3 | 5G | jeddah | Sceco | 5G SA | RAB0662-NR2.6-P3 | FLM_TE | RAB0662 | Results: DOWN SITE HUB RAB0662-NR2.6-P3 RAB0662 Summary: Hub: RAB0662, Down Count: 1, Down Sites: RAB0662-NR2.6-P3 Alarm Summary: RAB0662 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.244.29.172:8080] [URL:http://10.244.29.172:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 15:49:32 | 10/22/2025 16:24:48 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000711 | PCM-20251022-00001607 | TT-20251022-01658 | EM | Region_6 | KHNJ1M7851 | KHNJ0851 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/22/2025 15:51:45 | 10/23/2025 18:32:00 | 10/23/2025 03:51:45 | RECTIFIER MAINS POWER FAILURE at KHNJ1M7851-L800-P2 @ Sceco | 10/22/2025 15:43:26 | Minor | 7103 | RECTIFIER MAINS POWER FAILURE | 10/22/2025 15:43:14 | P2 | 4G | najran | Sceco | LTE NSA | KHNJ1M7851 | FLM_EM | [5 empty] | RECTIFIER MAINS POWER FAILURE |  |  | API | 10/22/2025 15:51:45 | 10/22/2025 15:56:06 | 10/23/2025 18:31:49 |  |  | 10/23/2025 18:32:00 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000712 | PCM-20251022-00001609 | TT-20251022-01659 | EM | Region_6 | KHNJ1M7852 | KHNJ0852 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/22/2025 15:51:46 | 10/23/2025 18:31:41 | 10/23/2025 03:51:46 | AIRCON 2 FAILURE at KHNJ1M7852-L800-P3-SBTS @ Sceco | 10/22/2025 15:43:20 | Minor | 7103 | AIRCON 2 FAILURE | 10/22/2025 15:43:14 | P3 | 4G | najran | Sceco | LTE NSA | KHNJ1M7852 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/22/2025 15:51:46 | 10/22/2025 15:56:07 | 10/23/2025 18:31:29 |  |  | 10/23/2025 18:31:41 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000713 | PCM-20251022-00001610 | TT-20251022-01661 | EM | Region_6 | KHNJ1M7896 | KHNJ0896 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/22/2025 15:51:48 | 10/23/2025 18:31:21 | 10/23/2025 03:51:48 | AIRCON 2 FAILURE at KHNJ1M7896-L800-P3-SBTS @ Sceco | 10/22/2025 15:43:19 | Minor | 7103 | AIRCON 2 FAILURE | 10/22/2025 15:43:14 | P3 | 4G | najran | Sceco | LTE NSA | KHNJ1M7896 | FLM_EM | [5 empty] | AIRCON 2 FAILURE |  |  | API | 10/22/2025 15:51:48 | 10/22/2025 15:56:08 | 10/23/2025 18:31:09 |  |  | 10/23/2025 18:31:21 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000714 | PCM-20251022-00001613 | TT-20251022-01647 | EM | Region_6 | KHNJ0853 | KHNJ0853 | Enviroment | SCECO_Failure | SCECO auto restored | Muhammad Shafeeq Muhammad Rafeeq | 10/22/2025 15:52:22 | 10/23/2025 18:30:59 | 10/22/2025 21:52:22 | 1(2G/LTE) sites down under KHNJ0853-P2/KHNJ0853-P2 @ Generator_SG | 10/22/2025 15:43:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 15:43:51 | P2 | 2G | najran | Generator_SG | 2G_LTE SA | KHNJ0853-P2 | FLM_EM | KHNJ0853 | Results: DOWN SITE HUB KHNJ0853-P2 KHNJ0853 Summary: Hub: KHNJ0853, Down Count: 1, Down Sites: KHNJ0853-P2 Alarm Summary: KHNJ0853 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 15:52:22 | 10/22/2025 15:56:09 | 10/23/2025 18:30:46 |  |  | 10/23/2025 18:30:59 |  | Muhammad Shafeeq Muhammad Rafeeq |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000715 | PCM-20251022-00001620 | TT-20251022-01663 | EM | Region_6 | AQQ2431 | AQQ2431 |  |  |  | Sohail Nasir Mir Afzal | 10/22/2025 15:57:04 | 10/23/2025 08:05:06 | 10/22/2025 21:57:04 | 1(2G/LTE) sites down under AQQ2431-P3/AQQ2431-P3 @ Generator_SG | 10/22/2025 15:48:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 15:48:51 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | AQQ2431-P3 | FLM_EM | AQQ2431 | Results: DOWN SITE HUB AQQ2431-P3 AQQ2431 Summary: Hub: AQQ2431, Down Count: 1, Down Sites: AQQ2431-P3 Alarm Summary: AQQ2431 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 15:57:04 | 10/23/2025 08:05:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000716 | PCM-20251022-00001625 | TT-20251022-01678 | Reference_EM | Region_2 | RIY0618 | RIY0618 |  |  |  | Mustansar Ali Mushtaq Ahmad | 10/22/2025 16:01:03 | 10/22/2025 20:30:27 | 10/22/2025 22:01:03 | high temprature 32 at RIY0618-P1-SHOP_SRAN @ Sceco | 10/22/2025 15:50:30 | Major | 65102 | high temprature 32 | 10/22/2025 15:50:27 | P1 | SRAN | riyadh | Sceco | 2G NSA | RIY0618 | FLM_EM | [8 empty] | API | 10/22/2025 16:01:03 | 10/22/2025 20:30:27 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000717 | PCM-20251022-00001627 | TT-20251022-01670 | EM | Region_4 | TFSH0675 | TFSH0675 |  |  |  | Walid Magdy Tawfik Elbana | 10/22/2025 16:01:34 | 10/22/2025 16:01:34 | 10/22/2025 22:01:34 | 1(2G/3G) sites down under TFSH0675-P3/TFSH0675-P3 @ Sceco | 10/22/2025 15:53:52 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 15:53:45 | P3 | 2G | taif | Sceco | 2G_3G SA | TFSH0675-P3 | FLM_EM |  | Results: DOWN SITE HUB TFSH0675-P3 Need to check Summary: Alarm Summary: HUB site not found |  |  |  |  | sites down |  | API | 10/22/2025 16:01:34 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000718 | PCM-20251022-00001630 | TT-20251022-01682 | EM | Region_6 | AQQ1M8431 | AQQ2431 |  |  |  | Sohail Nasir Mir Afzal | 10/22/2025 16:03:37 | 10/23/2025 08:05:06 | 10/23/2025 04:03:37 | GEN NOT IN AUTO at AQQ1M8431-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/22/2025 15:55:38 | Minor | 7103 | GEN NOT IN AUTO | 10/22/2025 15:55:28 | P3 | 4G | Baha | Generator_SG | LTE NSA | AQQ1M8431 | FLM_EM | [5 empty] | GEN NOT IN AUTO |  |  | API | 10/22/2025 16:03:37 | 10/23/2025 08:05:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000719 | PCM-20251022-00001631 | TT-20251022-01675 | Telecom | Region_6 | AHM1M3195 | AHM0195 | Equipment | Jumper_Cable | Replace Outdoor Jumper Cable | Zeshan Ali Adnan | 10/22/2025 16:04:02 | 10/22/2025 22:37:06 | 10/22/2025 22:04:02 | 1(3G) sites down under AHM0195-P3/AHM1M3195-P3 @ Generator_SG | 10/22/2025 15:56:11 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 15:55:34 | P3 | 3G | jizan | Generator_SG | 3G SA | AHM0195-P3 | FLM_TE | AHM0195 | Results: DOWN SITE HUB AHM0195-P3 AHM0195 Summary: Hub: AHM0195, Down Count: 1, Down Sites: AHM0195-P3 Alarm Summary: AHM0195 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 16:04:02 | 10/22/2025 17:53:41 | 10/22/2025 22:36:33 |  |  | 10/22/2025 22:37:06 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000720 | PCM-20251022-00001632 | TT-20251022-01646 | Telecom | Region_6 | ZHR0136 | ZHR0136 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Bilal Anwar Khurshid Anwar | 10/22/2025 16:04:04 | 10/22/2025 18:14:44 | 10/22/2025 22:04:04 | 3(2G) 3(3G) 2(LTE) sites down under ZHR0136-P3,ZHR0509-P2-USF,ZHR0328-P3/ZHR0328-P3 @ Sceco | 10/22/2025 15:43:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 15:43:51 | P3 | 2G | al harja | Sceco | 2G_3G_LTE SA | ZHR0136-P3 2G_3G_LTE,ZHR0328-P3 2G_3G_LTE,ZHR0509-P2-USF 2G_3G | FLM_TE | ZHR0136 | Results: DOWN SITE HUB ZHR0136-P3 ZHR0136 ZHR0328-P3 ZHR0328 ZHR0509-P2-USF ZHR0509 Summary: Hub: ZHR0136, Down Count: 1, Down Sites: ZHR0136-P3 Hub: ZHR0328, Down Count: 1, Down Sites: ZHR0328-P3 Hub: ZHR0509, Down Count: 1, Down Sites: ZHR0509-P2-USF Alarm Summary: ZHR0136 No Active Alarm on HUB ZHR0328 Alarm Active on HUB ZHR0509 Alarm Active on HUB | PCM-20251022-00001612 | HUB: ZHR0136 We observing lan link , eth loss | HUB: ZHR0136 We observing lan link , eth loss |  | sites down |  | API | 10/22/2025 16:04:04 | 10/22/2025 16:26:19 | 10/22/2025 18:14:06 |  |  | 10/22/2025 18:14:44 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000721 | PCM-20251022-00001634 | TT-20251022-01672 | Telecom | Region_2 | RML0049 | RML0049 |  |  |  | Kazi Jalil Allimiya | 10/22/2025 16:04:41 | 10/23/2025 02:12:04 | 10/22/2025 22:04:41 | 2(2G) 1(3G) 2(LTE) sites down under RML0049-P3-USF,RML0050-P3-USF/R2_RY1_HWBSC01 @ Power Cube | 10/22/2025 15:55:54 | Major | 21825 | CSL Fault | 10/22/2025 15:55:51 | P3 | SRAN | muzamiah | Sceco | 2G_3G_LTE SA | RML0050-P3-USF 2G_3G_LTE,RML0049-P3-USF 2G_LTE | FLM_EM | RML0049 | Hub:- RML0049 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001628 | Hub:- RML0049 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RML0049 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 16:04:41 | 10/23/2025 02:12:04 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000722 | PCM-20251022-00001635 | TT-20251022-01665 | Telecom | Region_6 | AQQ2431 | AQQ2431 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/22/2025 16:05:14 | 10/22/2025 19:22:28 | 10/22/2025 22:05:14 | 4(2G) 4(LTE) sites down under AQQ2429-P3,AQQ2427-P3,AQQ2428-P3,AQQ2430-P3/AQQ2430-P3 @ Generator_SG | 10/22/2025 15:48:56 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 15:48:51 | P3 | 2G | Baha | Generator_SG | 2G_LTE SA | AQQ2429-P3 2G_LTE,AQQ2430-P3 2G_LTE,AQQ2427-P3 2G_LTE,AQQ2428-P3 2G_LTE | FLM_TE | AQQ2431 | Results: DOWN SITE HUB AQQ2429-P3 AQQ2429 AQQ2430-P3 AQQ2430 AQQ2427-P3 AQQ2427 AQQ2428-P3 AQQ2428 Summary: Hub: AQQ2429, Down Count: 1, Down Sites: AQQ2429-P3 Hub: AQQ2430, Down Count: 1, Down Sites: AQQ2430-P3 Hub: AQQ2427, Down Count: 1, Down Sites: AQQ2427-P3 Hub: AQQ2428, Down Count: 1, Down Sites: AQQ2428-P3 Alarm Summary: AQQ2429 Alarm Active on HUB AQQ2430 Alarm Active on HUB AQQ2427 Alarm Active on HUB AQQ2428 Alarm Active on HUB | PCM-20251022-00001622 | AQQ2431 | AQQ2431 |  | sites down |  | API | 10/22/2025 16:05:14 | 10/22/2025 16:23:22 | 10/22/2025 19:22:19 |  |  | 10/22/2025 19:22:28 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000723 | PCM-20251022-00001636 | TT-20251022-01596 | Telecom | Region_1 | DAM2072 | DAM2072 |  |  |  | Meraj Husain Idd Baksh | 10/22/2025 16:05:24 | 10/22/2025 16:37:25 | 10/22/2025 22:05:24 | 2(2G) 2(LTE) sites down under DAM0451-P3,DAM2072-P3/R1_DM_HWBSC01 @ Generator_SG | 10/22/2025 15:15:33 | Major | 21825 | CSL Fault | 10/22/2025 15:15:33 | P3 | SRAN | dammam | Generator_SG | 2G_LTE SA | DAM0451-P3 2G_LTE,DAM2072-P3 2G_LTE | FLM_TE | DAM2072 | Hub:- DAM2072 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001570 | telecom issue | telecom issue |  | sites down |  | API | 10/22/2025 16:05:24 | 10/22/2025 16:37:25 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000724 | PCM-20251022-00001641 | TT-20251022-01690 | Telecom | Region_3 | MDN6072 | MDN6072 | Transsmission | SFP_Transmission | Reset SFP | Ibrahim Mohammad AbdulMalik alraee | 10/22/2025 16:06:43 | 10/23/2025 12:50:56 | 10/23/2025 04:06:43 | DCU Optical Module Transmit/Receive Fault at MDN6072-Sector C-DCU @ Sceco | 10/22/2025 15:57:20 | Minor | 26232 | DCU Optical Module Transmit/Receive Fault | 10/22/2025 16:01:12 | P3 | SRAN | madinah | Sceco | 2G NSA | MDN6072 | FLM_TE | [8 empty] | API | 10/22/2025 16:06:43 | 10/22/2025 21:12:58 | 10/23/2025 12:50:35 |  |  | 10/23/2025 12:50:56 |  | Ibrahim Mohammad AbdulMalik alraee |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000725 | PCM-20251022-00001644 | TT-20251022-01692 | Telecom | Region_5 | HAJ0319 | HAJ0319 |  |  |  | Muhammad Saleem Iqbal | 10/22/2025 16:07:45 | 10/22/2025 23:33:03 | 10/23/2025 04:07:45 | RF Unit Maintenance Link Failure at HAJ0319-P3_SRAN @ Sceco | 10/22/2025 16:04:16 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 16:02:31 | P3 | SRAN | makkah | Sceco | 2G NSA | HAJ0319 | FLM_TE | [8 empty] | API | 10/22/2025 16:07:45 | 10/22/2025 23:33:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000726 | PCM-20251022-00001647 | TT-20251022-01694 | EM | Region_6 | MTB1M8377 | MTB2377 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 16:09:19 | 10/22/2025 18:29:51 | 10/23/2025 04:09:19 | SHELTER DOOR OPEN at MTB1M8377-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 16:08:52 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 16:08:44 | P2 | 4G | Baha | Sceco | LTE NSA | MTB1M8377 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 16:09:19 | 10/22/2025 18:29:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000727 | PCM-20251022-00001648 | TT-20251022-01676 | Telecom | Region_2 | QSDH0716 | QSDH0716 |  |  |  | Moustafa Elzaafarany Abdellah | 10/22/2025 16:09:37 | 10/23/2025 00:05:50 | 10/22/2025 20:09:37 | 1(2G) 2(3G) sites down under BJD0539-P2,BJD0540-P1-DIA,QSDH0716-P2/R2_BR1_HWBSC01 @ Sceco | 10/22/2025 15:57:29 | Critical | 21807 | OML Fault | 10/22/2025 15:57:20 | P3 | SRAN | dawadmi | Sceco | 2G_3G SA | BJD0539-P2 3G,BJD0540-P1-DIA 3G,QSDH0716-P2 2G | FLM_EM | QSDH0716 | Hub:- QSDH0716 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001633 | Hub:- QSDH0716 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- QSDH0716 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  | sites down |  | API | 10/22/2025 16:09:37 | 10/23/2025 00:05:50 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000728 | PCM-20251022-00001650 | TT-20251022-01697 | EM | Region_4 | FRS2420 | FRS2420 |  |  |  | Subair Mannayath Moidutty Mannayath | 10/22/2025 16:10:20 | 10/22/2025 16:37:49 | 10/23/2025 04:10:20 | SHELTER DOOR OPEN at FRS2420-G9-L8-L18-SBTS-P3 @ Sceco | 10/22/2025 16:10:01 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 16:09:57 | P3 | 2G | qunfuddah | Sceco | 2G NSA | FRS2420 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 16:10:20 | 10/22/2025 16:37:49 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000731 | PCM-20251022-00001653 | TT-20251022-01683 | EM | Region_6 | BHMF0856 | BHMF0856 | AutoRecovery | Clear_Before_Investigation | Auto Clear | SHAH KHALID | 10/22/2025 16:11:02 | 10/22/2025 17:05:01 | 10/22/2025 22:11:02 | 1(2G/LTE) sites down under BHMF0856-P3/BHMF0856-P3 @ Sceco | 10/22/2025 16:02:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 16:02:28 | P3 | 2G | makhwa | Sceco | 2G SA | BHMF0856-P3 | FLM_TE | BHMF0856 | Results: DOWN SITE HUB BHMF0856-P3 BHMF0856 Summary: Hub: BHMF0856, Down Count: 1, Down Sites: BHMF0856-P3 Alarm Summary: BHMF0856 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 16:11:02 | 10/22/2025 16:11:40 | 10/22/2025 16:12:23 |  |  | 10/22/2025 16:12:36 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000732 | PCM-20251022-00001654 | TT-20251022-01684 | Telecom | Region_5 | HAJ0319 | HAJ0319 |  |  |  | Muhammad Saleem Iqbal | 10/22/2025 16:11:06 | 10/22/2025 23:33:04 | 10/22/2025 22:11:06 | 1(5G) sites down under HAJ0319-P3_SRAN @ Sceco | 10/22/2025 16:04:08 | Major | 29840 | gNodeB Out of Service | 10/22/2025 16:02:33 | P3 | SRAN | makkah | Sceco | 5G SA | HAJ0319-P3_SRAN | FLM_TE | HAJ0319 | Results: DOWN SITE HUB HAJ0319-P3_SRAN HAJ0319 Summary: Hub: HAJ0319, Down Count: 1, Down Sites: HAJ0319-P3_SRAN Alarm Summary: HAJ0319 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 16:11:06 | 10/22/2025 23:33:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Preparation | CM20251022000733 | PCM-20251022-00001659 | TT-20251022-01704 | Reference_telecom | Region_2 | RIYA6057 | RIYA6057 |  |  |  | Muhammad Waqas Ashraf Muhammad Ashraf | 10/22/2025 16:15:31 | 10/23/2025 13:52:40 | 10/22/2025 22:15:31 | RF Unit VSWR Threshold Crossed at RIYA6057-DCU1 @ Sceco | 10/22/2025 13:09:52 | Major | 26529 | RF Unit VSWR Threshold Crossed | 10/22/2025 13:15:22 | P3 | SRAN | riyadh | Sceco | 2G NSA | RIYA6057 | FLM_TE | [8 empty] | API | 10/22/2025 16:15:31 | 10/23/2025 08:12:27 | 10/23/2025 13:39:30 | 10/23/2025 13:39:33 | 10/23/2025 13:52:40 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000735 | PCM-20251022-00001665 | TT-20251015-01271 | Reference_telecom | Region_5 | MAK0698 | MAK0698 |  |  |  | Mosab Nasr eldeen Mohamed | 10/22/2025 16:18:59 | 10/22/2025 16:18:59 | 10/23/2025 04:18:59 | FanFailure observed in MAK0698 towards 10.1.239.19 @ Sceco | 10/15/2025 00:40:13 | Minor |  | FanFailure | 10/15/2025 00:39:42 | P2 | 2G | makkah | Sceco | TX NSA | MAK0698 | FLM_TE |  |  | PCM-20251022-00001402 | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it | Dear FLM Approved for HW change based on below FLM TS & Current Alarms and update status after HW changed & tracking it |  |  |  | API | 10/22/2025 16:18:59 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000736 | PCM-20251022-00001666 | TT-20251022-01713 | Telecom | Region_6 | KMS0168 | KMS0168 |  |  |  | Amir Abbas Arif Raza | 10/22/2025 16:19:08 | 10/22/2025 20:56:13 | 10/23/2025 04:19:08 | BASE STATION SERVICE PROBLEM (No connection to unit) at KMS0168-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P3 @ Sceco | 10/22/2025 16:18:25 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 16:18:16 | P3 | 2G | khamis mushyet | Sceco | 5G_Cell SA | KMS0168 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 16:19:08 | 10/22/2025 20:56:13 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000737 | PCM-20251022-00001667 | TT-20251022-01714 | Telecom | Region_4 | MKJD1M9570 | MKJD0570 |  |  |  | Amjad Ali Muhammad Parves | 10/22/2025 16:19:38 | 10/23/2025 10:53:44 | 10/23/2025 04:19:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at MKJD1M9570-P3-L800-SBTS @ Generator_DG | 10/22/2025 16:18:41 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 16:18:30 | P2 | 4G | jeddah | Generator_DG | 5G_Cell SA | MKJD1M9570 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 16:19:38 | 10/23/2025 10:53:44 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000738 | PCM-20251022-00001670 | TT-20251022-01717 | EM | Region_3 | BDR2108 | BDR2108 |  |  |  | Muhammad Imran Muhammad Aslam | 10/22/2025 16:20:39 | 10/23/2025 19:28:12 | 10/23/2025 04:20:39 | NETECO: Communication Failure at BDR2108 @ Generator_SG | 10/22/2025 16:14:12 | Minor | 17451 | Communication Failure | 10/22/2025 16:14:12 | P3 | SRAN | yanbu | Generator_SG | 2G NSA | BDR2108 | FLM_EM | [8 empty] | API | 10/22/2025 16:20:39 | 10/23/2025 19:28:12 | [9 empty] | EM | Zain |  | Running |  | OWS
Stuck | CM20251022000739 | PCM-20251022-00001674 | TT-20251022-01619 | Telecom | [7 empty] | 10/22/2025 16:24:05 | 10/22/2025 16:24:05 | 10/23/2025 04:24:05 | HC TT For BUR2665 | 10/22/2025 15:32:03 | Minor | 676767672 | Health Check-WO to TE FME | 10/22/2025 15:32:04 | P3 | SRAN |  | Generator_SG | 2G NSA | BUR2665 | FLM_TE |  | Dear TX Team Kindly check as TX alarm reported on site and IPPM and TWAMP NOK as below | PCM-20251022-00001621 | need HC on BUR038-BUR0023 flapping AM Down shift alarm &PM error and RSL degradation observed | need HC on BUR038-BUR0023 flapping AM Down shift alarm &PM error and RSL degradation observed |  |  |  | API | 10/22/2025 16:24:05 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000740 | PCM-20251022-00001675 | TT-20251022-01721 | Reference_EM | Region_1 | HFB2M5031 | HFB0031 |  |  |  | Elarashid Eltahir Mohamed Eltahir | 10/22/2025 16:24:49 | 10/22/2025 16:24:49 | 10/22/2025 22:24:49 | Door opening alarm at HFB2M5031-P1-HUB @ Generator_SG | 10/22/2025 16:24:12 | Major | 65101 | Door opening alarm | 10/22/2025 16:24:07 | P1 | 2G | hafouf | Generator_SG | 2G NSA | HFB2M5031 | FLM_EM | [8 empty] | API | 10/22/2025 16:24:49 | [10 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000741 | PCM-20251022-00001688 | TT-20251022-01710 | Telecom | Region_6 | ABH0084 | ABH0084 |  |  |  | Khalid Frahan Almesetef | 10/22/2025 16:31:22 | 10/22/2025 16:31:22 | 10/22/2025 22:31:22 | 2(2G) 2(3G) 1(LTE) 2(5G) sites down under ABH0084-P3,ABH0172-P3/ABH0172-P3 @ Sceco | 10/22/2025 16:14:58 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 16:14:53 | P3 | 2G | abha | Sceco | 2G_3G_LTE_5G SA | ABH0172-P3 2G_3G_LTE_5G,ABH0084-P3 2G_3G_5G | FLM_EM | ABH0084 | Results: DOWN SITE HUB ABH0172-P3 ABH0172 ABH0084-P3 ABH0084 Summary: Hub: ABH0172, Down Count: 1, Down Sites: ABH0172-P3 Hub: ABH0084, Down Count: 1, Down Sites: ABH0084-P3 Alarm Summary: ABH0172 Alarm Active on HUB ABH0084 Alarm Active on HUB | PCM-20251022-00001672 | ABH0084 | ABH0084 |  | sites down |  | API | 10/22/2025 16:31:22 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000743 | PCM-20251022-00001698 | TT-20251022-01753 | Reference_EM | Region_2 | RYAB0603 | RYAB0603 |  |  |  | Fritz Ian Generale | 10/22/2025 16:40:17 | 10/23/2025 05:16:46 | 10/23/2025 04:40:17 | Door opening alarm at RYAB0603-P2_SRAN @ Sceco_STB | 10/22/2025 16:39:43 | Minor | 65101 | Door opening alarm | 10/22/2025 16:39:40 | P2 | SRAN | al kharj | Sceco_STB | 2G NSA | RYAB0603 | FLM_EM | [8 empty] | API | 10/22/2025 16:40:17 | 10/23/2025 05:16:46 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000745 | PCM-20251022-00001703 | TT-20251022-01758 | Telecom | Region_4 | HHR0815 | HHR0815 |  |  |  | Khizer Hayat | 10/22/2025 16:44:25 | 10/22/2025 17:08:47 | 10/22/2025 20:44:25 | BASE STATION SERVICE PROBLEM (No connection to unit) at HHR0815-GSM-UMTS-P1-VIP-HHR @ Generator_SG | 10/22/2025 16:43:26 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 16:43:16 | VIP | 2G | jeddah | Generator_SG | 5G_Cell SA | HHR0815 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 16:44:25 | 10/22/2025 17:08:47 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000746 | PCM-20251022-00001705 | TT-20251022-01759 | Telecom | Region_6 | DAR0950 | DAR0950 | Equipment | BSS_HW_Stuck | Reset RRU | Muhammad Ali | 10/22/2025 16:44:56 | 10/22/2025 17:34:28 | 10/22/2025 20:44:56 | BASE STATION SERVICE PROBLEM (No connection to unit) at DAR0950-GSM-UMTS-P1 @ Sceco | 10/22/2025 16:44:09 | Critical | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 16:43:56 | P1 | 2G | dair | Sceco | 5G_Cell SA | DAR0950 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 16:44:56 | 10/22/2025 17:31:23 | 10/22/2025 17:34:13 |  |  | 10/22/2025 17:34:28 |  | Muhammad Ali |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000747 | PCM-20251022-00001706 | TT-20251022-01727 | Reference_telecom | Region_6 | SUR1M3998 | SUR0998 | Transsmission | MW_Connectors | Replace Indoor MW Connector | Bilal Anwar Khurshid Anwar | 10/22/2025 16:45:28 | 10/22/2025 21:20:28 | 10/22/2025 22:45:28 | WCDMA CELL OUT OF USE (Resource status indication, cell disabled) at SUR1M3998-P2-USF @ Sceco | 10/22/2025 16:00:08 | Major | 7771 | WCDMA CELL OUT OF USE | 10/22/2025 15:57:59 | P2 | 3G | al harja | Sceco | 3G SA | SUR1M3998 | FLM_TE |  |  | PCM-20251022-00001678 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/22/2025 16:45:28 | 10/22/2025 17:02:05 | 10/22/2025 21:20:00 |  |  | 10/22/2025 21:20:28 |  | Bilal Anwar Khurshid Anwar |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000748 | PCM-20251022-00001709 | TT-20251022-01737 | Telecom | Region_4 | JED0751 | JED0751 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 16:46:09 | 10/22/2025 18:00:17 | 10/22/2025 22:46:09 | CELL SERVICE PROBLEM (Incorrect cell parameter configuration) at JED0751-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/22/2025 16:26:17 | Major | 7114 | CELL SERVICE PROBLEM | 10/22/2025 16:26:11 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0751 | FLM_TE |  |  | PCM-20251022-00001687 | please check SFP, fiber cable for RF module and BB module | please check SFP, fiber cable for RF module and BB module |  |  |  | API | 10/22/2025 16:46:09 | 10/22/2025 18:00:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000749 | PCM-20251022-00001710 | TT-20251022-01742 | Telecom | Region_4 | RYMK0528 | RYMK0528 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 16:47:20 | 10/23/2025 07:26:03 | 10/22/2025 20:47:20 | 3(2G) 3(3G) 2(LTE) sites down under RYMK0528-P1,HAW2440-P2,RYMK0665-P3/RYMK0665-P3 @ Generator_DG | 10/22/2025 16:30:17 | Critical | 7706 | BTS O&M LINK FAILURE | 10/22/2025 16:30:14 | P1 | 2G | taif | Generator_SG | 2G_3G_LTE SA | RYMK0665-P3 2G_3G_LTE,RYMK0528-P1 2G_3G,HAW2440-P2 2G_3G | FLM_TE | RYMK0528 | Results: DOWN SITE HUB RYMK0665-P3 RYMK0665 RYMK0528-P1 RYMK0528 HAW2440-P2 HAW2440 Summary: Hub: RYMK0665, Down Count: 1, Down Sites: RYMK0665-P3 Hub: RYMK0528, Down Count: 1, Down Sites: RYMK0528-P1 Hub: HAW2440, Down Count: 1, Down Sites: HAW2440-P2 Alarm Summary: RYMK0665 Alarm Active on HUB RYMK0528 Alarm Active on HUB HAW2440 Alarm Active on HUB | PCM-20251022-00001695 | RYMK0528 | RYMK0528 |  | sites down |  | API | 10/22/2025 16:47:20 | 10/23/2025 07:26:03 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000750 | PCM-20251022-00001711 | TT-20251022-01763 | Reference_EM | Region_3 | AHT2328 | AHT2328 |  |  |  | Muhammad Jamil Bhatti Nazir Ahmed | 10/22/2025 16:47:31 | 10/22/2025 16:47:31 | 10/23/2025 04:47:31 | Door opening alarm at AHT2328-P3-USF_SRAN @ Generator_SG | 10/22/2025 16:47:13 | Minor | 65101 | Door opening alarm | 10/22/2025 16:47:10 | P3 | SRAN | hail | Generator_SG | 2G NSA | AHT2328 | FLM_EM | [8 empty] | API | 10/22/2025 16:47:31 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000751 | PCM-20251022-00001717 | TT-20251022-01771 | Telecom | Region_1 | DAM2178 | DAM2178 |  |  |  | Shakeel Ahmed Hafeez Ameen | 10/22/2025 16:50:37 | 10/22/2025 17:52:18 | 10/22/2025 22:50:37 | NR Cell Unavailable at DAM2178-P2_SRAN @ Sceco | 10/22/2025 16:44:00 | Major | 29841 | NR Cell Unavailable | 10/22/2025 16:42:28 | P2 | SRAN | dammam | Sceco | 5G SA | DAM2178 | FLM_TE | [8 empty] | API | 10/22/2025 16:50:37 | 10/22/2025 17:52:18 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000752 | PCM-20251022-00001719 | TT-20251022-01773 | EM | Region_6 | BHAB1M8404 | BHAB2404 |  |  |  | Mustafa Abdalla Gubara Abdalla | 10/22/2025 16:51:09 | 10/22/2025 18:29:51 | 10/23/2025 04:51:09 | SHELTER DOOR OPEN at BHAB1M8404-G9-L8-L18-SBTS-P3 @ Generator_SG | 10/22/2025 16:50:45 | Minor | 7103 | SHELTER DOOR OPEN | 10/22/2025 16:50:41 | P3 | 4G | Albaha | Generator_SG | LTE NSA | BHAB1M8404 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 16:51:09 | 10/22/2025 18:29:51 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000753 | PCM-20251022-00001724 | TT-20251022-01779 | Telecom | Region_4 | JED1MN2299 | JED2299 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 16:54:14 | 10/23/2025 16:39:52 | 10/22/2025 22:54:14 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1MN2299-NR2.6-P3 @ Sceco | 10/22/2025 16:53:13 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 16:53:04 | P3 | 5G | jeddah | Sceco | 5G_Cell SA | JED1MN2299 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 16:54:14 | 10/23/2025 16:39:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000754 | PCM-20251022-00001725 | TT-20251022-01767 | Telecom | Region_4 | RYMK0665 | RYMK0665 |  |  |  | Ehab Ali Mohamed Abdou | 10/22/2025 16:54:28 | 10/23/2025 07:54:19 | 10/23/2025 04:54:28 | WRYMK0001 is complete down | 10/22/2025 16:44:33 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 16:44:33 | P3 | 2G | taif | Generator_DG | Wifi SA | WRYMK0001 | FLM_EM | RYMK0665 | Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | PCM-20251022-00001715 | Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. | Hub:- RYMK0665 Suspecting power issue at hub site and kindly send EM-FLM team to check and resolve issue at site. |  |  |  | API | 10/22/2025 16:54:28 | 10/23/2025 07:54:19 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000755 | PCM-20251022-00001730 | TT-20251022-01783 | Telecom | Region_6 | AHM1M7195 | AHM0195 | Equipment | Jumper_Cable | Reconnect Outdoor Jumper Cable | Zeshan Ali Adnan | 10/22/2025 16:57:52 | 10/22/2025 22:38:26 | 10/23/2025 04:57:52 | BASE STATION SERVICE PROBLEM (No connection to unit) at AHM1M7195-P3-NCA-L800-SBTS @ Generator_SG | 10/22/2025 16:57:14 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 16:57:05 | P3 | 4G | jizan | Generator_SG | 5G_Cell SA | AHM1M7195 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 16:57:52 | 10/22/2025 17:53:42 | 10/22/2025 22:37:35 |  |  | 10/22/2025 22:38:26 |  | Zeshan Ali Adnan |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000756 | PCM-20251022-00001731 | TT-20251022-01793 | Reference_EM | Region_3 | SHR0003 | SHR0003 | Enviroment | Genset failure_AVR | Change Generator AVR | Abdelwahab Mahmoud Abdelwahab Abboud | 10/22/2025 16:58:56 | 10/22/2025 18:39:25 | 10/22/2025 22:58:56 | Generator failure at SHR0003-P1-VVIP_SRAN-PC @ Power Cube | 10/22/2025 16:48:37 | Major | 65114 | Generator failure | 10/22/2025 16:48:33 | VIP | SRAN | tabouk | Power Cube | 2G NSA | SHR0003 | FLM_EM | [8 empty] | API | 10/22/2025 16:58:56 | 10/22/2025 18:28:14 | 10/22/2025 18:28:19 | 10/22/2025 18:28:22 | 10/22/2025 18:36:39 | 10/22/2025 18:39:25 |  | Abdelwahab Mahmoud Abdelwahab Abboud |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000757 | PCM-20251022-00001732 | TT-20251022-01794 | Reference_EM | Region_2 | RYD0928 | RYD0928 |  |  |  | Pawan Virdi Santokh Singh | 10/22/2025 16:59:24 | 10/23/2025 10:00:40 | 10/23/2025 04:59:24 | Mains Failure at RYD0928-P2_SRAN @ Sceco | 10/22/2025 16:49:44 | Minor | 65109 | Mains Failure | 10/22/2025 16:49:39 | P2 | SRAN | rumah | Sceco | 2G NSA | RYD0928 | FLM_EM | [8 empty] | API | 10/22/2025 16:59:24 | 10/23/2025 10:00:40 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000758 | PCM-20251022-00001734 | TT-20251022-01796 | Telecom | Region_3 | TBK2685 | TBK2685 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Tahir Abbas Fateh Khan | 10/22/2025 17:00:27 | 10/23/2025 14:32:02 | 10/23/2025 05:00:27 | RF Unit Hardware Fault at TBK2685-P2_SRAN @ Sceco | 10/22/2025 16:57:05 | Minor | 26532 | RF Unit Hardware Fault | 10/22/2025 16:55:51 | P2 | SRAN | tabouk | Sceco | 2G NSA | TBK2685 | FLM_TE | [8 empty] | API | 10/22/2025 17:00:27 | 10/22/2025 17:01:49 | 10/23/2025 14:30:18 |  |  | 10/23/2025 14:32:02 |  | Tahir Abbas Fateh Khan |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000759 | PCM-20251022-00001738 | TT-20251022-01784 | EM | Region_5 | OMQ1M3633 | OMQ0633 |  |  |  | Amjad Ali Muhammad Parves | 10/22/2025 17:03:01 | 10/23/2025 10:53:45 | 10/22/2025 23:03:01 | 1(2G/3G/LTE/5G) sites down under OMQ0633-P2-USF/OMQ1M3633-P2-USF @ Generator_SG | 10/22/2025 16:55:29 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 16:54:50 | P2 | 3G | makkah | Generator_SG | 3G SA | OMQ0633-P2-USF | FLM_TE | OMQ0633 | Results: DOWN SITE HUB OMQ0633-P2-USF OMQ0633 Summary: Hub: OMQ0633, Down Count: 1, Down Sites: OMQ0633-P2-USF Alarm Summary: OMQ0633 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 17:03:01 | 10/23/2025 10:53:45 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000761 | PCM-20251022-00001740 | TT-20251022-01806 | Reference_EM | Region_1 | ARM0714 | ARM0714 |  |  |  | Omer Elfadoul Mohamed Ibrahim | 10/22/2025 17:03:32 | 10/22/2025 17:10:06 | 10/22/2025 23:03:32 | Door opening alarm at ARM0714-P1-DIA_SRAN @ Generator_SG | 10/22/2025 17:03:01 | Major | 65101 | Door opening alarm | 10/22/2025 17:02:57 | P1 | SRAN | dammam | Generator_SG | 2G NSA | ARM0714 | FLM_EM | [8 empty] | API | 10/22/2025 17:03:32 | 10/22/2025 17:10:06 | [9 empty] | EM | Zain |  | Running |  | OWS
Preparation | CM20251022000762 | PCM-20251022-00001741 | TT-20251022-01702 | Telecom | Region_4 | JED0296 | JED0296 |  |  |  | BARKAT ALI MAIN HILAL | 10/22/2025 17:03:52 | 10/22/2025 18:04:09 | 10/22/2025 23:03:52 | 2(2G) 1(LTE) 1(5G) sites down under JED0296-P2-USF,JED6097-P3/JED61971-P3 @ Sceco | 10/22/2025 16:10:30 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 16:10:25 | P2 | 2G | jeddah | Sceco | 2G SA | JED6097-P3 2G,JED0296-P2-USF 2G | FLM_TE | JED0296 | Results: DOWN SITE HUB JED6097-P3 JED6097 JED0296-P2-USF JED0296 Summary: Hub: JED6097, Down Count: 1, Down Sites: JED6097-P3 Hub: JED0296, Down Count: 1, Down Sites: JED0296-P2-USF Alarm Summary: JED6097 No Active Alarm on HUB JED0296 Alarm Active on HUB | PCM-20251022-00001680 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 17:03:52 | 10/22/2025 17:57:02 | 10/22/2025 17:57:15 | 10/22/2025 17:57:21 | 10/22/2025 18:04:09 | [6 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000764 | PCM-20251022-00001749 | TT-20251022-01802 | Telecom | Region_6 | AQQ1M7039 | AQQ0039 | Equipment | SFP_BTS | Clean SFP | Manzoor Ahmed | 10/22/2025 17:07:32 | 10/23/2025 16:20:56 | 10/22/2025 23:07:32 | 1(LTE) sites down under AQQ0039-G9-NL8-L18-NL21-SBTS-P3 @ Sceco | 10/22/2025 16:59:19 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 16:59:15 | P3 | 4G | Albaha | Sceco | LTE SA | AQQ0039-G9-NL8-L18-NL21-SBTS-P3 | FLM_TE | AQQ0039 | Results: DOWN SITE HUB AQQ0039-G9-NL8-L18-NL21-SBTS-P3 AQQ0039 Summary: Hub: AQQ0039, Down Count: 1, Down Sites: AQQ0039-G9-NL8-L18-NL21-SBTS-P3 Alarm Summary: AQQ0039 No Active Alarm on HUB |  |  |  | Connection is closed [URL:http://10.103.247.76:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 17:07:32 | 10/22/2025 18:15:28 | 10/23/2025 16:20:43 |  |  | 10/23/2025 16:20:56 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000765 | PCM-20251022-00001751 | TT-20251022-01769 | Telecom | Region_4 | HHR0815 | HHR0815 |  |  |  | Khizer Hayat | 10/22/2025 17:08:48 | 10/22/2025 18:01:59 | 10/22/2025 21:08:48 | 1(3G) 1(LTE) sites down under JED2176-CA-L1800-L800-P3,HHR0815-P1-VIP-HHR/HHR1M3815-P1-VIP-HHR @ Generator_SG | 10/22/2025 16:47:30 | Critical | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 16:46:51 | VIP | 2G | jeddah | Generator_SG | 3G_LTE SA | JED2176-CA-L1800-L800-P3 LTE,HHR0815-P1-VIP-HHR 3G | FLM_TE | HHR0815 | Results: DOWN SITE HUB JED2176-CA-L1800-L800-P3 JED2176 HHR0815-P1-VIP-HHR HHR0815 Summary: Hub: JED2176, Down Count: 1, Down Sites: JED2176-CA-L1800-L800-P3 Hub: HHR0815, Down Count: 1, Down Sites: HHR0815-P1-VIP-HHR Alarm Summary: JED2176 No Active Alarm on HUB HHR0815 No Active Alarm on HUB | PCM-20251022-00001727 | HHR0815 | HHR0815 |  | sites down |  | API | 10/22/2025 17:08:48 | 10/22/2025 18:01:59 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000767 | PCM-20251022-00001754 | TT-20251022-01604 | Telecom | Region_4 | MLJI9425 | MLJI9425 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 17:10:02 | 10/23/2025 09:20:52 | 10/22/2025 23:10:02 | 3(3G) sites down under MLJI0373-P3,MLJI0387-P2-USF,MLJI0143-P3/MLJI1M3143-P3 @ Generator_SG | 10/22/2025 15:20:33 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 15:19:49 | P3 | Repeater | alaith | Generator_DG | 3G SA | MLJI0143-P3 3G,MLJI0373-P3 3G,MLJI0387-P2-USF 3G | FLM_TE | MLJI9425 | Results: DOWN SITE HUB MLJI0143-P3 Need to check MLJI0373-P3 Need to check MLJI0387-P2-USF Need to check Summary: Alarm Summary: HUB site not found | PCM-20251022-00001577 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 17:10:02 | 10/23/2025 09:20:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000768 | PCM-20251022-00001756 | TT-20251022-01818 | EM | Region_1 | HFR0502 | HFR0502 | Enviroment | SCECO_Failure | SCECO auto restored | Emad Mahmoud Ahmed Mohamed | 10/22/2025 17:10:46 | 10/22/2025 18:05:36 | 10/22/2025 21:10:46 | Door opening alarm at HFR0502-P1-Core-HUB-WDM_SRAN-FON @ Sceco_STB | 10/22/2025 17:10:16 | Critical | 65101 | Door opening alarm | 10/22/2025 17:10:12 | P1 | SRAN | hafr | Sceco_STB | 2G NSA | HFR0502 | FLM_EM | [8 empty] | API | 10/22/2025 17:10:46 | 10/22/2025 18:04:23 | 10/22/2025 18:05:26 |  |  | 10/22/2025 18:05:36 |  | Emad Mahmoud Ahmed Mohamed |  |  |  | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000769 | PCM-20251022-00001758 | TT-20251022-01820 | Reference_EM | Region_3 | MDTB2M5329 | MDTB0329 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/22/2025 17:11:48 | 10/22/2025 17:11:48 | 10/22/2025 23:11:48 | Door opening alarm at MDTB2M5329-P1-HUB @ Sceco_STB | 10/22/2025 17:11:18 | Major | 65101 | Door opening alarm | 10/22/2025 17:11:14 | P1 | 2G | madinah | Sceco_STB | 2G NSA | MDTB2M5329 | FLM_EM | [8 empty] | API | 10/22/2025 17:11:48 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000773 | PCM-20251022-00001764 | TT-20251022-01815 | Telecom | Region_4 | RNRY0670 | RNRY0670 |  |  |  | Ahmad Kamal Abdelmawla | 10/22/2025 17:14:02 | 10/22/2025 17:30:07 | 10/22/2025 23:14:02 | 1(5G) sites down under RNRY0670-GSM-P3 @ Sceco | 10/22/2025 17:05:51 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 17:05:48 | P3 | 2G | taif | Sceco | 5G SA | RNRY0670-GSM-P3 | FLM_TE | RNRY0670 | Results: DOWN SITE HUB RNRY0670-GSM-P3 RNRY0670 Summary: Hub: RNRY0670, Down Count: 1, Down Sites: RNRY0670-GSM-P3 Alarm Summary: RNRY0670 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.98.90.20:8080] [URL:http://10.98.90.20:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 17:14:02 | 10/22/2025 17:30:07 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000774 | PCM-20251022-00001765 | TT-20251022-01828 | Telecom | Region_6 | WDS0277 | WDS0277 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Mamdouh Helal Helal | 10/22/2025 17:14:23 | 10/23/2025 01:17:25 | 10/22/2025 23:14:23 | BASE STATION SERVICE PROBLEM (No connection to unit) at WDS0277-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP-USF @ Sceco_STB | 10/22/2025 17:13:25 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 17:13:17 | VIP | 2G | wadi dawasar | Sceco_STB | 5G_Cell SA | WDS0277 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 17:14:23 | 10/23/2025 01:16:59 | 10/23/2025 01:17:18 |  |  | 10/23/2025 01:17:25 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000775 | PCM-20251022-00001767 | TT-20251022-01817 | Reference_telecom | Region_4 | JED0252 | JED0252 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 17:17:40 | 10/22/2025 17:21:35 | 10/23/2025 05:17:40 | BASE STATION SERVICE PROBLEM (RSSI difference between main and diversity paths exceed the threshold) at JED0252-G9-L8-L18-L21-NR2.6-NR3.5-P3-SBTS @ Sceco | 10/22/2025 17:05:46 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 17:05:37 | P3 | 2G | jeddah | Sceco | 5G_Cell SA | JED0252 | FLM_TE |  |  | PCM-20251022-00001755 | FLM Need to perform extensive HC in site for impacted Antenna port. FLM can take support from BO if required while FLM available on site. Pls check all Antenna Line. Perform Cleanup at RFM and Antenna end both. Once issue resolve close the PCM with RCA. | FLM Need to perform extensive HC in site for impacted Antenna port. FLM can take support from BO if required while FLM available on site. Pls check all Antenna Line. Perform Cleanup at RFM and Antenna end both. Once issue resolve close the PCM with RCA. |  |  |  | API | 10/22/2025 17:17:40 | 10/22/2025 17:21:35 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000777 | PCM-20251022-00001770 | TT-20251022-01764 | Reference_telecom | Region_4 | TAF1M4416 | TAF2416 | Equipment | BSS_HW_Stuck | Reset System Module | Asad Ullah Rahim Said | 10/22/2025 17:19:40 | 10/22/2025 20:21:43 | 10/22/2025 23:19:40 | BASE STATION OPERATION DEGRADED (BTS internal SW management problem) at TAF1M4416-P2 @ Sceco | 10/22/2025 16:40:59 | Major | 7651 | BASE STATION OPERATION DEGRADED | 10/22/2025 16:40:40 | P2 | 3G | taif | Sceco | 3G NSA | TAF1M4416 | FLM_TE |  |  | PCM-20251022-00001712 | site is down, please check locally | site is down, please check locally |  |  |  | API | 10/22/2025 17:19:40 | 10/22/2025 20:01:24 | 10/22/2025 20:01:32 | 10/22/2025 20:01:48 | 10/22/2025 20:02:12 | 10/22/2025 20:21:43 |  | Asad Ullah Rahim Said |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000778 | PCM-20251022-00001772 | TT-20251022-01608 | Telecom | Region_1 | DRN9840 | DRN9840 |  |  |  | Imran Ali Yousaf | 10/22/2025 17:20:07 | 10/23/2025 02:43:23 | 10/23/2025 05:20:07 | BD_STATUS at DRN9840_NE_3_SDB @ Sceco | 10/22/2025 14:40:13 | Minor | 1-119 | BD_STATUS | 10/22/2025 14:39:49 |  | Repeater | dammam | Sceco | TX NSA | DRN9840 | FLM_TE |  |  | PCM-20251022-00001752 | Approved to change after TS Item=03021MXJ | Approved to change after TS Item=03021MXJ |  |  |  | API | 10/22/2025 17:20:07 | 10/23/2025 02:43:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000779 | PCM-20251022-00001773 | TT-20251022-00840 | Reference_telecom | Region_4 | JED1MN0035 | JED0035 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 17:20:08 | 10/22/2025 17:20:08 | 10/22/2025 23:20:08 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at JED1MN0035-NR2.6-P2 @ Sceco | 10/22/2025 08:02:35 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 08:02:31 | P2 | 5G | jeddah | Sceco | 5G NSA | JED1MN0035 | FLM_TE |  |  | PCM-20251022-00000764 | Alarm cleared, FLM need to check and close with RCA. | Alarm cleared, FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 17:20:08 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000781 | PCM-20251022-00001774 | TT-20251022-01752 | Reference_telecom | Region_4 | SJED1S7018 | SJED0018 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 17:20:57 | 10/23/2025 16:39:52 | 10/22/2025 21:20:57 | BASE STATION OPERATION DEGRADED (BTS reference clock missing: GPS receiver alarm: not tracking satellites) at SJED1S7018-CA-P1-ARP-HAJJ-VIP @ Sceco | 10/22/2025 16:37:44 | Critical | 7651 | BASE STATION OPERATION DEGRADED | 10/22/2025 16:27:42 | VIP | 4G | jeddah | Sceco | LTE NSA | SJED1S7018 | FLM_TE |  |  | PCM-20251022-00001697 | FLM need check GPS issue at site. | FLM need check GPS issue at site. |  |  |  | API | 10/22/2025 17:20:57 | 10/23/2025 16:39:52 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000782 | PCM-20251022-00001775 | TT-20251022-01840 | Reference_EM | Region_3 | MDTB2M5329 | MDTB0329 |  |  |  | Hafiz Muhammad Afzal Muhammad Shafqat | 10/22/2025 17:21:06 | 10/22/2025 17:21:06 | 10/22/2025 23:21:06 | Mains Failure at MDTB2M5329-P1-HUB @ Sceco_STB | 10/22/2025 17:11:35 | Major | 65109 | Mains Failure | 10/22/2025 17:11:21 | P1 | 2G | madinah | Sceco_STB | 2G NSA | MDTB2M5329 | FLM_EM | [8 empty] | API | 10/22/2025 17:21:06 | [10 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000783 | PCM-20251022-00001777 | TT-20251022-01843 | Telecom | Region_4 | JED0271 | JED0271 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 17:21:38 | 10/22/2025 18:00:17 | 10/23/2025 05:21:38 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED0271-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P2 @ Sceco | 10/22/2025 17:20:45 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 17:20:40 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | JED0271 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 17:21:38 | 10/22/2025 18:00:17 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000785 | PCM-20251022-00001779 | TT-20251022-00882 | Telecom | Region_5 | MAK0595 | MAK0595 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 17:22:33 | 10/22/2025 17:22:33 | 10/22/2025 23:22:33 | BASE STATION SERVICE PROBLEM (Pipe dangerously overheating) at MAK0595-G9-NL8-NL18-L21-NR2.6-SBTS-P1-VIP-HUB-HRM @ Sceco | 10/22/2025 08:56:27 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 08:56:19 | VIP | 2G | makkah | Sceco | 5G_Cell SA | MAK0595 | FLM_TE |  |  | PCM-20251022-00001163 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 17:22:33 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000786 | PCM-20251022-00001781 | TT-20251022-01028 | Reference_telecom | Region_6 | WDS0094 | WDS0094 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Ahmed Mamdouh Helal Helal | 10/22/2025 17:23:18 | 10/23/2025 01:17:43 | 10/23/2025 05:23:18 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at WDS0094-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/22/2025 09:52:51 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 09:52:45 | P2 | 2G | wadi dawasar | Sceco | 2G NSA | WDS0094 | FLM_TE |  |  | PCM-20251022-00000964 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 17:23:18 | 10/23/2025 01:16:59 | 10/23/2025 01:17:36 |  |  | 10/23/2025 01:17:43 |  | Ahmed Mamdouh Helal Helal |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000787 | PCM-20251022-00001785 | TT-20251022-01837 | Telecom | Region_4 | TUR1M7694 | TUR0694 |  |  |  | Rashid Shafique | 10/22/2025 17:25:02 | 10/23/2025 10:47:23 | 10/22/2025 23:25:02 | 1(LTE) sites down under TUR0694-L800-CA-P2 @ Sceco | 10/22/2025 17:16:36 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 17:16:32 | P2 | 4G | taif | Sceco | LTE SA | TUR0694-L800-CA-P2 | FLM_TE | TUR0694 | Results: DOWN SITE HUB TUR0694-L800-CA-P2 TUR0694 Summary: Hub: TUR0694, Down Count: 1, Down Sites: TUR0694-L800-CA-P2 Alarm Summary: TUR0694 Alarm Active on HUB |  |  |  | Timeout connecting to [/10.98.104.92:8080] [URL:http://10.98.104.92:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 17:25:02 | 10/23/2025 10:47:23 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000791 | PCM-20251022-00001790 | TT-20251022-01844 | Telecom | Region_4 | SJED1S7555 | SJED0555 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 17:27:02 | 10/23/2025 01:06:08 | 10/22/2025 23:27:02 | 1(LTE) sites down under SJED0555-CA-P3 @ Sceco | 10/22/2025 17:18:43 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 17:18:38 | P3 | 4G | jeddah | Sceco | LTE SA | SJED0555-CA-P3 | FLM_TE | SJED0555 | Results: DOWN SITE HUB SJED0555-CA-P3 SJED0555 Summary: Hub: SJED0555, Down Count: 1, Down Sites: SJED0555-CA-P3 Alarm Summary: SJED0555 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.99.221.28:8080] [URL:http://10.99.221.28:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 17:27:02 | 10/23/2025 01:06:08 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000792 | PCM-20251022-00001791 | TT-20251022-01765 | Reference_telecom | Region_4 | JED0885 | JED0885 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 17:27:17 | 10/23/2025 10:09:40 | 10/22/2025 23:27:17 | BASE STATION CONNECTIVITY PROBLEM (Xn SCTP endpoint broken) at JED0885-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/22/2025 16:40:59 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 16:40:49 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0885 | FLM_TE |  |  | PCM-20251022-00001713 | FLM need to check and close with RCA. | FLM need to check and close with RCA. |  |  |  | API | 10/22/2025 17:27:17 | 10/23/2025 10:09:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000794 | PCM-20251022-00001796 | TT-20251022-01164 | Reference_telecom | Region_4 | LTH0329 | LTH0329 |  |  |  | Riasat Ali Allah Baksh | 10/22/2025 17:28:13 | 10/23/2025 09:20:53 | 10/23/2025 05:28:13 | BASE STATION CONNECTIVITY PROBLEM (No X2 link available) at LTH0329-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/22/2025 11:12:55 | Minor | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 11:12:50 | P2 | 2G | qunfuddah | Sceco | 2G NSA | LTH0329 | FLM_TE |  |  | PCM-20251022-00001103 | FLM need to check Sync issue at site. | FLM need to check Sync issue at site. |  |  |  | API | 10/22/2025 17:28:13 | 10/23/2025 09:20:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000796 | PCM-20251022-00001804 | TT-20251022-01860 | Telecom | Region_4 | JED1MN0650 | JED0650 |  |  |  | Ahmed Adel Abdelaziz elkholy | 10/22/2025 17:33:02 | 10/22/2025 17:33:02 | 10/22/2025 23:33:02 | 1(5G) sites down under JED0650-NR2.6-P2 @ Sceco | 10/22/2025 17:24:55 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 17:24:53 | P2 | 5G | jeddah | Sceco | 5G SA | JED0650-NR2.6-P2 | FLM_TE | JED0650 | Results: DOWN SITE HUB JED0650-NR2.6-P2 JED0650 Summary: Hub: JED0650, Down Count: 1, Down Sites: JED0650-NR2.6-P2 Alarm Summary: JED0650 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.88.169.100:8080] [URL:http://10.88.169.100:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 17:33:02 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000797 | PCM-20251022-00001805 | TT-20251022-01846 | Telecom | Region_5 | MAK0817 | MAK0817 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 17:33:16 | 10/22/2025 17:33:16 | 10/22/2025 23:33:16 | 3(2G) 2(5G) sites down under MAK0817-P2,MAK0696-P2,MAK0040-P2/MAK0040-P2 @ Sceco | 10/22/2025 17:19:23 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 17:19:20 | P2 | 2G | makkah | Sceco | 2G_5G SA | MAK0040-P2 2G_5G,MAK0817-P2 2G_5G,MAK0696-P2 2G | FLM_TE | MAK0817 | Results: DOWN SITE HUB MAK0040-P2 MAK0817 MAK0817-P2 MAK0817 MAK0696-P2 MAK0817 Summary: Hub: MAK0817, Down Count: 3, Down Sites: MAK0040-P2, MAK0817-P2, MAK0696-P2 Alarm Summary: MAK0817 Alarm Active on HUB | PCM-20251022-00001798 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 17:33:16 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000798 | PCM-20251022-00001806 | TT-20251022-01873 | EM | Region_4 | JED0714 | JED0714 |  |  |  | Nabil Nazih Mohamoud Ahmed | 10/22/2025 17:35:04 | 10/23/2025 11:51:20 | 10/22/2025 23:35:04 | SHELTER DOOR OPEN at JED0714-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-FWA-P1-VIP @ Sceco | 10/22/2025 17:34:52 | Major | 7103 | SHELTER DOOR OPEN | 10/22/2025 17:34:47 | P3 | 2G | jeddah | Sceco | 2G NSA | JED0714 | FLM_EM | [5 empty] | SHELTER DOOR OPEN |  |  | API | 10/22/2025 17:35:04 | 10/23/2025 11:51:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000799 | PCM-20251022-00001807 | TT-20251022-01864 | Reference_telecom | Region_1 | TBJ2U6707 | TBJ6007 |  |  |  | Syed Fawad Ali | 10/22/2025 17:35:07 | 10/22/2025 17:44:54 | 10/23/2025 05:35:07 | Cell RX Channel Interference Noise Power Unbalanced at TBJ2U6707-P3 @ Sceco | 10/22/2025 14:29:46 | Minor | 29250 | Cell RX Channel Interference Noise Power Unbalanced | 10/22/2025 14:29:42 | P3 | 4G | sakaka | Sceco | 2G NSA | TBJ2U6707 | FLM_TE |  | Dears Kindly check HW | PCM-20251022-00001799 | Dears Kindly check HW | Dears Kindly check HW |  |  |  | API | 10/22/2025 17:35:07 | 10/22/2025 17:44:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000800 | PCM-20251022-00001808 | TT-20251022-01874 | Reference_EM | Region_3 | RSP0050 | RSP0050 |  |  |  | Sayed Satoor | 10/22/2025 17:35:34 | 10/22/2025 19:35:33 | 10/22/2025 23:35:34 | Door opening alarm at RSP0050-P1_SRAN @ Sceco | 10/22/2025 17:35:09 | Major | 65101 | Door opening alarm | 10/22/2025 17:35:05 | P1 | SRAN | yanbu | Sceco | 2G NSA | RSP0050 | FLM_EM | [8 empty] | API | 10/22/2025 17:35:34 | 10/22/2025 19:35:33 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000801 | PCM-20251022-00001810 | TT-20251022-01384 | Telecom | Region_5 | MAK1M9028 | MAK0028 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 17:38:38 | 10/22/2025 17:38:38 | 10/23/2025 05:38:38 | PT:: FLM need to perform HC at 33 sites on MAKKAH region /R5 (BO request) | 10/22/2025 13:34:43 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 13:34:43 | P2 | 4G | makkah | Sceco | 2G_3G_LTE_5G NSA | MAK1M9028-P2-CA-L800 MAK1M9838-L800-CA-SBTS-P3 MAK0078-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB MAK1M9093-G9-NL8-L18-L21-SBTS-P2 MAK1M7906-G9-NL8-L18-NL21-SBTS-P2-USF MAK0063-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 MAK1M9114-G9-L8-L18-L21-SBTS-P2 MAK0999-G9-L8-L18-L21-NR2.6-SBTS-P1-VIP-HRM MAK1M9122-G9-L8-L18-L21-SBTS-P2-HUB MAK0728-L8-L18-L21-NR2.6-NR3.5-SBTS-P1 MAK1M9982-P2-CA-L800 MAK0324-G9-L8-L18-L21-NR2.6-NNR3.5-SBTS-P2 MAK0238-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-VIP-HAJJ MAK1M9197-G9-L8-L18-L21-SBTS-P2 MAK1M9040-P2-L800 MAK1M9997-CA-P1-VIP-HAJJ-HRM MAK1M9984-G9-NL8-L18-NL21-SBTS-P3 MAK1M8460-SBTS-CA-L800-P3 MAK1M7784-G9-U9-NL8-NL18-L21-P1-USF MAK1M9073-G9-L8-L18-L21-SBTS-P2-HUB MAK0133-G9-L8-L18-L21-NR2.6-NR3.5-SBTS--P2-USF QUR1M7343-P3-L800 MKYL1M7910-G9-L8-L18-L21-SBTS-P1-HUB-USF ASH1M9631-P3-CA MAK0012-G9-L8-L18-L21-NR2.6-SBTS-P2 MAK0583-G9-L8-L18-L21-NR2.6-NR3.5-SBTS-P1-HUB MAK1M9190-G9-L8-L18-L21-SBTS-P2 MAK1M9678-G9-L8-L18-L21-SBTS-P3 MAK1M9082-P3-CA-L800-SBTS MAK1M9119-G9-G18-L8-L18-L21-SBTS-P1 MAK1M9237-P2-CA-L800-SBTS MAK1M9576-P2-L800 MAK0830-G9-NL8-L18-L21-NR2.6-SBTS-P3 | FLM_TE |  |  | PCM-20251022-00001450 | Mail already shared please check as per priority | Dear FLM Team, Kindly support to perform HC of the site, need to verify Clean SFPCableConnector, As the difference between ports are high. @Access Team:- Kindly assign TT to FLM for HC |  |  |  | API | 10/22/2025 17:38:38 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000802 | PCM-20251022-00001811 | TT-20251022-01877 | Telecom | Region_4 | JED1W6081 | JED6081 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 17:40:29 | 10/23/2025 01:06:09 | 10/23/2025 05:40:29 | JED1W6081 is partial down | 10/22/2025 17:36:44 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 17:36:44 | P1 | WIFI | jeddah | Sceco | Wifi SA | JED1W6081_3-6F-AP04 | FLM_TE | [8 empty] | API | 10/22/2025 17:40:29 | 10/23/2025 01:06:09 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000803 | PCM-20251022-00001813 | TT-20251022-01813 | Reference_telecom | Region_4 | JED0191 | JED0191 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 17:41:01 | 10/23/2025 10:09:40 | 10/22/2025 23:41:01 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0191-P2 @ Sceco | 10/22/2025 17:00:05 | Major | 7602 | BCF NOTIFICATION | 10/22/2025 16:59:51 | P2 | 2G | jeddah | Sceco | 2G NSA | JED0191 | FLM_TE |  |  | PCM-20251022-00001748 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/22/2025 17:41:01 | 10/23/2025 10:09:40 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000804 | PCM-20251022-00001814 | TT-20251022-01879 | Telecom | Region_3 | MDN2923 | MDN2923 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Hussain Ahmad Sultan Muhammad | 10/22/2025 17:41:46 | 10/22/2025 19:19:14 | 10/23/2025 05:41:46 | RF Unit Maintenance Link Failure at MDN2923-P3_SRAN @ Sceco | 10/22/2025 17:38:19 | Minor | 26235 | RF Unit Maintenance Link Failure | 10/22/2025 17:36:36 | P2 | SRAN | madinah | Sceco | 2G NSA | MDN2923 | FLM_TE | [8 empty] | API | 10/22/2025 17:41:46 | 10/22/2025 18:19:54 | 10/22/2025 19:05:10 | 10/22/2025 19:05:14 | 10/22/2025 19:05:19 | 10/22/2025 19:19:14 |  | Hussain Ahmad Sultan Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000805 | PCM-20251022-00001819 | TT-20251022-01882 | Telecom | Region_3 | MDN2923 | MDN2923 | Equipment | Power Cable_RRU_BTS | Replace Outdoor Power Connector | Hussain Ahmad Sultan Muhammad | 10/22/2025 17:44:52 | 10/22/2025 19:04:54 | 10/22/2025 23:44:52 | NR Cell Unavailable at MDN2923-P3_SRAN @ Sceco | 10/22/2025 17:38:14 | Major | 29841 | NR Cell Unavailable | 10/22/2025 17:36:41 | P2 | SRAN | madinah | Sceco | 5G SA | MDN2923 | FLM_TE | [8 empty] | API | 10/22/2025 17:44:52 | 10/22/2025 18:19:55 | 10/22/2025 18:20:26 | 10/22/2025 18:20:30 | 10/22/2025 18:37:39 | 10/22/2025 19:04:54 |  | Hussain Ahmad Sultan Muhammad |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000806 | PCM-20251022-00001824 | TT-20251022-01885 | EM | Region_1 | KFKM0793 | KFKM0793 | Equipment | PMR_Power_Cable_RRU | Change Port on FPFH | Mahmoud Youssef Mohamed Ahmed | 10/22/2025 17:46:24 | 10/23/2025 20:04:23 | 10/23/2025 05:46:24 | NETECO: Door Status Sensor Alarm at KFKM0793 @ Generator_SG | 10/22/2025 17:45:48 | Minor | 5152 | Door Status Sensor Alarm | 10/22/2025 17:45:48 | P3 | SRAN | hafr | Generator_SG | 2G NSA | KFKM0793 | FLM_EM | [8 empty] | API | 10/22/2025 17:46:24 | 10/22/2025 20:56:27 | 10/23/2025 20:03:17 |  |  | 10/23/2025 20:04:23 |  | Mahmoud Youssef Mohamed Ahmed |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000808 | PCM-20251022-00001827 | TT-20251022-01866 | Telecom | Region_4 | SJED0555 | SJED0555 |  |  |  | Mohamed Farag Abdelbary | 10/22/2025 17:47:23 | 10/23/2025 01:06:09 | 10/23/2025 05:47:23 | SJED1W0555 is complete down | 10/22/2025 17:21:25 | Minor | 613007 | Wi-Fi AP Out Of Service | 10/22/2025 17:21:25 | P3 | SRAN | jeddah | Sceco | Wifi SA | SJED1W0555 | FLM_EM | SJED0555 |  | PCM-20251022-00001802 | SJED0555 | SJED0555 |  |  |  | API | 10/22/2025 17:47:23 | 10/23/2025 01:06:09 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000810 | PCM-20251022-00001833 | TT-20251022-01892 | Telecom | Region_4 | JED1M8297 | JED2297 |  |  |  | MALIK ATIF ZAMAN | 10/22/2025 17:51:04 | 10/23/2025 16:39:53 | 10/22/2025 23:51:04 | BASE STATION SERVICE PROBLEM (No connection to unit) at JED1M8297-P3-CA-L800 @ Sceco | 10/22/2025 17:50:15 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 17:50:07 | P3 | 4G | jeddah | Sceco | 5G_Cell SA | JED1M8297 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 17:51:04 | 10/23/2025 16:39:53 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000813 | PCM-20251022-00001837 | TT-20251022-01774 | Telecom | Region_6 | TLT0805 | TLT0805 | AutoRecovery | Clear_Before_Investigation | Auto Clear | Muhammad Afzal Muhammad Aslam | 10/22/2025 17:54:24 | 10/22/2025 22:33:34 | 10/22/2025 23:54:24 | 3(2G) 3(3G) 3(5G) sites down under TLT0805-P3,TLT0757-P3,TLT0362-P3/TLT0362-P3 @ Generator_SG | 10/22/2025 16:49:11 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 16:49:09 | P3 | 2G | tathleeth | Sceco | 2G_3G_5G SA | TLT0362-P3 2G_3G_5G,TLT0805-P3 2G_3G_5G,TLT0757-P3 2G_3G_5G | FLM_TE | TLT0805 | Results: DOWN SITE HUB TLT0362-P3 Need to check TLT0805-P3 Need to check TLT0757-P3 Need to check Summary: Alarm Summary: HUB site not found | PCM-20251022-00001832 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 17:54:24 | 10/22/2025 17:56:04 | 10/22/2025 18:13:03 |  |  | 10/22/2025 18:13:09 |  | Muhammad Afzal Muhammad Aslam |  |  |  | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000814 | PCM-20251022-00001838 | TT-20251022-01903 | Reference_EM | Region_3 | YBDB0285 | YBDB0285 | Enviroment | Rectifier Module | Change rectifer module | Sayed Satoor | 10/22/2025 18:01:24 | 10/23/2025 18:27:32 | 10/23/2025 00:01:24 | Door opening alarm at YBDB0285-P1-HUB-SRAN @ Sceco_STB | 10/22/2025 18:01:09 | Major | 65101 | Door opening alarm | 10/22/2025 18:01:04 | P1 | SRAN | yanbu | Sceco_STB | 2G NSA | YBDB0285 | FLM_EM | [8 empty] | API | 10/22/2025 18:01:24 | 10/22/2025 19:35:34 | 10/23/2025 18:27:17 |  |  | 10/23/2025 18:27:32 |  | Sayed Satoor |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000815 | PCM-20251022-00001839 | TT-20251022-01904 | EM | Region_4 | JED1U6729 | JED6029 |  |  |  | Shaikh Iqbal Shaikh Hasan Qureshi | 10/22/2025 18:01:24 | 10/22/2025 20:21:10 | 10/23/2025 06:01:24 | Rectifier Low battery voltage at JED1U6729-G9-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 17:53:09 | Minor | 7103 | Rectifier Low battery voltage | 10/22/2025 17:52:56 | P3 | 4G | jeddah | Sceco | LTE NSA | JED1U6729 | FLM_EM | [5 empty] | Rectifier Low battery voltage |  |  | API | 10/22/2025 18:01:24 | 10/22/2025 20:21:10 | [9 empty] | EM | Zain |  | Running |  | OWS
Dispatched | CM20251022000816 | PCM-20251022-00001841 | TT-20251020-01638 | Reference_telecom | Region_5 | MAK0254 | MAK0254 |  |  |  | Aktarul Jaman Mofazzal Hoshen | 10/22/2025 18:03:15 | 10/22/2025 18:03:15 | 10/23/2025 06:03:15 | Nokia Eband Observing FanFailure-fanTray-1,ReplaceableUnitProblem-fanTra at MAK0254-10.10.141.55 | 10/19/2025 13:28:47 | Minor |  | LOF | 10/19/2025 13:28:47 | P1 | 2G | makkah | Sceco | TX NSA | MAK0254-10.10.141.55 | FLM_TE |  | Approved | PCM-20251022-00001421 | Approved | Approved |  |  |  | API | 10/22/2025 18:03:15 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000817 | PCM-20251022-00001842 | TT-20251022-01896 | Telecom | Region_6 | BHMF0859 | BHMF0859 | Equipment | BSS_HW_Stuck | Reset System Module | SHAH KHALID | 10/22/2025 18:03:32 | 10/22/2025 20:29:42 | 10/23/2025 00:03:32 | 1(5G) sites down under BHMF0859-G9-SBTS-P3 @ Sceco | 10/22/2025 17:55:28 | Major | 9047 | NE3SWS AGENT NOT RESPONDING TO REQUESTS | 10/22/2025 17:55:25 | P3 | 2G | makhwa | Sceco | 5G SA | BHMF0859-G9-SBTS-P3 | FLM_TE | BHMF0859 | Results: DOWN SITE HUB BHMF0859-G9-SBTS-P3 BHMF0859 Summary: Hub: BHMF0859, Down Count: 1, Down Sites: BHMF0859-G9-SBTS-P3 Alarm Summary: BHMF0859 No Active Alarm on HUB |  |  |  | Timeout connecting to [/10.103.201.228:8080] [URL:http://10.103.201.228:8080/NE3S/1.0/] | sites down |  | API | 10/22/2025 18:03:32 | 10/22/2025 20:23:51 | 10/22/2025 20:28:59 |  |  | 10/22/2025 20:29:42 |  | SHAH KHALID |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000818 | PCM-20251022-00001846 | TT-20251022-01918 | Telecom | Region_4 | THO0371 | THO0371 |  |  |  | Khizer Hayat | 10/22/2025 18:06:34 | 10/23/2025 00:56:50 | 10/23/2025 06:06:34 | BASE STATION SERVICE PROBLEM (No connection to unit) at THO0371-G9-L8-L18-L21-NR2.6-SBTS-P2 @ Sceco | 10/22/2025 18:05:49 | Minor | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 18:05:43 | P2 | 2G | jeddah | Sceco | 5G_Cell SA | THO0371 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 18:06:34 | 10/23/2025 00:56:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000819 | PCM-20251022-00001847 | TT-20251022-01347 | Reference_telecom | Region_6 | TNM0140 | TNM0140 |  |  |  | Fawad Khan | 10/22/2025 18:08:02 | 10/22/2025 20:36:54 | 10/23/2025 00:08:02 | P0_MW_LINK DOWN at TNM0140-LL-CSG-01 TO BHAB9036-LL-CSG-01 ¦¦ TT-20251011-02014 | 10/22/2025 13:18:12 | Major | 15269 | LOS | 10/22/2025 13:18:14 | P1 | 2G | namas | Sceco_STB | IPRAN NSA | P0_MW_LINK DOWN at TNM0140-LL-CSG-01 TO BHAB9036-LL-CSG-01 ¦¦ TT-20251011-02014 | FLM_TE |  | Thanks to confirm power stability for NMS0094 | PCM-20251022-00001617 | Thanks to confirm power stability for NMS0094 | Thanks to confirm power stability for NMS0094 |  |  |  | API | 10/22/2025 18:08:02 | 10/22/2025 20:36:54 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000820 | PCM-20251022-00001849 | TT-20251022-01909 | Telecom | Region_4 | THO1M3371 | THO0371 |  |  |  | Khizer Hayat | 10/22/2025 18:09:01 | 10/23/2025 00:56:50 | 10/23/2025 00:09:01 | 1(3G) sites down under THO0371-P2/THO1M3371-P2 @ Sceco | 10/22/2025 18:01:20 | Major | 7786 | WCDMA BASE STATION OUT OF USE | 10/22/2025 18:00:42 | P3 | 3G | jeddah | Sceco | 3G SA | THO0371-P2 | FLM_TE | THO0371 | Results: DOWN SITE HUB THO0371-P2 THO0371 Summary: Hub: THO0371, Down Count: 1, Down Sites: THO0371-P2 Alarm Summary: THO0371 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 18:09:01 | 10/23/2025 00:56:50 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000821 | PCM-20251022-00001850 | TT-20251022-01731 | Reference_telecom | Region_4 | JED2983 | JED2983 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 18:09:25 | 10/23/2025 10:09:41 | 10/23/2025 00:09:25 | BASE STATION CONNECTIVITY PROBLEM (GTP-U Path Failure) at JED2983-G9-L8-L18-L21-NR2.6-P3 @ Generator_SG | 10/22/2025 14:28:38 | Major | 7107 | BASE STATION CONNECTIVITY PROBLEM | 10/22/2025 14:28:25 | P3 | 2G | jeddah | Generator_SG | 2G NSA | JED2983 | FLM_TE |  |  | PCM-20251022-00001800 | Thanks to check JED0128-JED0006. | Thanks to check JED0128-JED0006. |  |  |  | API | 10/22/2025 18:09:25 | 10/23/2025 10:09:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Dispatched | CM20251022000822 | PCM-20251022-00001854 | TT-20251022-01924 | Reference_telecom | Region_5 | MAK1M9602 | MAK0602 |  |  |  | Atif Javed Javed Hussain | 10/22/2025 18:10:42 | 10/22/2025 18:10:42 | 10/23/2025 06:10:42 | BASE STATION INFORMATION (Unit temperature is high) at MAK1M9602-G9-L8-L18-L21-SBTS-P3 @ Sceco | 10/22/2025 17:30:38 | Minor | 7115 | BASE STATION INFORMATION | 10/22/2025 17:30:30 | VIP | 4G | makkah | Sceco | LTE NSA | MAK1M9602 | FLM_TE | [5 empty] | Unit temperature is high |  |  | API | 10/22/2025 18:10:42 | [10 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000823 | PCM-20251022-00001856 | TT-20251022-01919 | Telecom | Region_2 | SRIY0183 | SRIY0183 | Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to SCECO failure, was auto restored | Waseem Shahzad Ghulam Rasool | 10/22/2025 18:12:32 | 10/23/2025 15:37:21 | 10/22/2025 22:12:32 | 1(LTE) sites down under SRIY0183-P1-VIP_SRAN @ Sceco | 10/22/2025 18:04:26 | Critical | 301 | NE Is Disconnected | 10/22/2025 18:04:22 | VIP | SRAN | riyadh | Sceco | LTE SA | SRIY0183-P1-VIP_SRAN | FLM_TE | SRIY0183 | Results: DOWN SITE HUB SRIY0183-P1-VIP_SRAN SRIY0183 Summary: Hub: SRIY0183, Down Count: 1, Down Sites: SRIY0183-P1-VIP_SRAN Alarm Summary: SRIY0183 No Active Alarm on HUB |  |  |  |  | sites down |  | API | 10/22/2025 18:12:32 | 10/23/2025 13:18:18 | 10/23/2025 15:37:04 |  |  | 10/23/2025 15:37:21 |  | Waseem Shahzad Ghulam Rasool |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000824 | PCM-20251022-00001860 | TT-20251022-01928 | Reference_EM | Region_3 | SAR0029 | SAR0029 |  |  |  | Mohamed Hafez Fahim Abdelaziz | 10/22/2025 18:15:52 | 10/23/2025 22:43:20 | 10/23/2025 00:15:52 | Mains Failure at SAR0029-P1-HUB_SRAN @ Sceco | 10/22/2025 18:05:52 | Major | 65109 | Mains Failure | 10/22/2025 18:05:47 | P1 | SRAN | hail | Sceco | 2G NSA | SAR0029 | FLM_EM | [8 empty] | API | 10/22/2025 18:15:52 | 10/23/2025 22:43:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000825 | PCM-20251022-00001861 | TT-20251022-01931 | EM | Region_3 | DBQL0250 | DBQL0250 | Equipment | Power Cable_RRU_BTS | Reconnect Power Cable | Walid Attia Shahata Alim | 10/22/2025 18:16:55 | 10/23/2025 17:50:42 | 10/22/2025 22:16:55 | Genset running at DBQL0250-P3-WDM_SRAN @ Sceco_STB | 10/22/2025 18:14:54 | Critical | 65112 | Genset running | 10/22/2025 18:14:51 | P3 | SRAN | tabouk | Sceco_STB | 2G NSA | DBQL0250 | FLM_EM | [8 empty] | API | 10/22/2025 18:16:55 | 10/23/2025 00:01:00 | 10/23/2025 17:50:16 | 10/23/2025 17:50:18 |  | 10/23/2025 17:50:42 |  | Walid Attia Shahata Alim |  |  |  | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000826 | PCM-20251022-00001865 | TT-20251022-01926 | EM | Region_6 | TBL2328 | TBL2328 |  |  |  | Abdul Rauf Muhammad Aslam | 10/22/2025 18:19:34 | 10/23/2025 01:36:38 | 10/23/2025 00:19:34 | 1(2G/LTE) sites down under TBL2328-P3/TBL2328-P3 @ Generator_DG | 10/22/2025 18:11:18 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 18:11:12 | P3 | 2G | bisha | Generator_DG | 2G_LTE SA | TBL2328-P3 | FLM_EM | TBL2328 | Results: DOWN SITE HUB TBL2328-P3 TBL2328 Summary: Hub: TBL2328, Down Count: 1, Down Sites: TBL2328-P3 Alarm Summary: TBL2328 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 18:19:34 | 10/23/2025 01:36:38 | [9 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000828 | PCM-20251022-00001871 | TT-20251022-01939 | Telecom | Region_6 | BLJ0046-LL-CSG-01 | BLJ0046 | Transsmission | SFP_Transmission | Reset SFP | Manzoor Ahmed | 10/22/2025 18:21:33 | 10/23/2025 16:20:28 | 10/23/2025 06:21:33 | Bad Package Error Rising at BLJ0046-LL-CSG-01 @ Sceco | 10/22/2025 18:21:10 | Minor | 101-2501403 | Bad Package Error Rising | 10/22/2025 18:21:04 | P2 | IPRAN | Albaha | Sceco | IPRAN NSA | BLJ0046-LL-CSG-01 | FLM_TE | [8 empty] | API | 10/22/2025 18:21:33 | 10/22/2025 19:21:45 | 10/23/2025 16:19:54 |  |  | 10/23/2025 16:20:28 |  | Manzoor Ahmed |  |  |  | Telecom | Zain |  | Running |  | OWS
Stuck | CM20251022000829 | PCM-20251022-00001872 | TT-20251022-01932 | EM | [7 empty] | 10/22/2025 18:22:01 | 10/22/2025 18:22:01 | 10/23/2025 00:22:01 | 1(2G/LTE) sites down under HLMD2491-P3-CAP/R3_HL_HWBSC01 @ Generator_SG | 10/22/2025 18:13:46 | Major | 21825 | CSL Fault | 10/22/2025 18:13:42 | P3 | 2G |  | Generator_SG | 2G_LTE SA | HLMD2491-P3-CAP | FLM_EM | HLMD2491 | Results: DOWN SITE HUB HLMD2491-P3-CAP HLMD2491 Summary: Hub: HLMD2491, Down Count: 1, Down Sites: HLMD2491-P3-CAP Alarm Summary: HLMD2491 Alarm Active on HUB |  |  |  |  | sites down |  | API | 10/22/2025 18:22:01 | [10 empty] | EM | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000831 | PCM-20251022-00001876 | TT-20251022-01927 | Reference_telecom | Region_4 | JZMA0824 | JZMA0824 | Equipment | SFP_BTS | Replace SFP | Mudassar Bashir Bashir Ahmad | 10/22/2025 18:24:11 | 10/23/2025 18:59:51 | 10/23/2025 00:24:11 | BCF NOTIFICATION (FF FF FF FF FF FF) at JZMA0824-P3 @ Sceco | 10/22/2025 18:08:04 | Major | 7602 | BCF NOTIFICATION | 10/22/2025 18:07:50 | P3 | 2G | qunfuddah | Sceco | 2G NSA | JZMA0824 | FLM_TE |  |  | PCM-20251022-00001859 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/22/2025 18:24:11 | 10/23/2025 12:41:07 | 10/23/2025 17:56:12 | 10/23/2025 17:56:17 | 10/23/2025 17:56:20 | 10/23/2025 18:59:51 |  | Mudassar Bashir Bashir Ahmad |  |  |  | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000832 | PCM-20251022-00001877 | TT-20251022-01854 | Reference_telecom | Region_4 | JED0107 | JED0107 |  |  |  | Mohammed Ramadan A Abu Abid | 10/22/2025 18:25:53 | 10/22/2025 18:55:16 | 10/22/2025 22:25:53 | BCF NOTIFICATION (FF FF FF FF FF FF) at JED0107-P1-VIP @ Sceco | 10/22/2025 17:20:25 | Critical | 7602 | BCF NOTIFICATION | 10/22/2025 17:20:11 | VIP | 2G | jeddah | Sceco | 2G NSA | JED0107 | FLM_TE |  |  | PCM-20251022-00001792 | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement | Suspecting due to GPS issue , please proceed for below check 1- Check the GPS receiver installation. 2. Check the GPS receiver status. 3. Check the connection between the GPS receiver and the SMOD 4. if GPS faulty proceed for GPS replacement |  |  |  | API | 10/22/2025 18:25:53 | 10/22/2025 18:55:16 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000833 | PCM-20251022-00001879 | TT-20251022-01949 | Reference_telecom | Region_4 | HAW2292 | HAW2292 |  |  |  | SHEHERYAR KHAN MUNAMMAD NAWAZ | 10/22/2025 18:28:16 | 10/23/2025 07:26:04 | 10/23/2025 06:28:16 | DemFail observed in HAW2292 _01 towards 10.21.73.34 @ Generator_SG | 10/22/2025 06:30:14 | Minor |  | DemFail | 10/22/2025 06:28:09 | P3 | 2G | taif | Generator_SG | TX NSA | HAW2292 | FLM_TE | [8 empty] | API | 10/22/2025 18:28:16 | 10/23/2025 07:26:04 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Delivered | CM20251022000834 | PCM-20251022-00001880 | TT-20251022-01950 | EM | Region_3 | MDQS2437 | MDQS2437 |  |  |  | Ayman Mohamed Sayed Ahmed | 10/22/2025 18:28:16 | 10/23/2025 09:17:20 | 10/23/2025 06:28:16 | NETECO: Water Alarm at MDQS2437 @ Generator_DG | 10/22/2025 18:22:06 | Minor | 5250 | Water Alarm | 10/22/2025 18:22:06 | P3 | SRAN | madinah | Generator_DG | 2G NSA | MDQS2437 | FLM_EM | [8 empty] | API | 10/22/2025 18:28:16 | 10/23/2025 09:17:20 | [9 empty] | EM | Zain |  | Running |  | OWS
Delivered | CM20251022000836 | PCM-20251022-00001883 | TT-20251022-01951 | Telecom | Region_4 | BHR1M7309 | BHR0309 |  |  |  | Moustafa Mahmoud Ahmed Fathelbab | 10/22/2025 18:30:21 | 10/23/2025 10:09:41 | 10/23/2025 00:30:21 | BASE STATION SERVICE PROBLEM (No connection to unit) at BHR1M7309-G9-L18-SBTS-P1-HUB-USF @ Sceco_STB | 10/22/2025 18:29:45 | Major | 7116 | BASE STATION SERVICE PROBLEM | 10/22/2025 18:29:39 | P1 | 4G | jeddah | Sceco_STB | 5G_Cell SA | BHR1M7309 | FLM_TE | [5 empty] | No connection to unit |  |  | API | 10/22/2025 18:30:21 | 10/23/2025 10:09:41 | [9 empty] | Telecom | Zain |  | Running |  | OWS
Request_Resolved | CM20251022000838 | PCM-20251022-00001888 | TT-20251022-01946 | EM | Region_6 | KMS0032 | KMS0032 | Transsmission | MW_HW_fault | Replace Control Card | Muhammad shafiq Muhammad Rasheed | 10/22/2025 18:33:17 | 10/22/2025 18:43:39 | 10/23/2025 00:33:17 | 1(2G/3G/LTE/5G) sites down under KMS0032-P2/KMS0032-P2 @ Sceco | 10/22/2025 18:22:21 | Major | 7706 | BTS O&M LINK FAILURE | 10/22/2025 18:22:17 | P2 | 2G | khamis mushyet | Sceco | 2G_3G_LTE_5G SA | KMS0032-P2 | FLM_TE | KMS0032 | Results: DOWN SITE HUB KMS0032-P2 KMS0032 Summary: Hub: KMS0032, Down Count: 1, Down Sites: KMS0032-P2 Alarm Summary: KMS0032 Alarm Active on HUB | PCM-20251022-00001882 | No Power Issue | No Power Issue |  | sites down |  | API | 10/22/2025 18:33:17 | 10/22/2025 18:43:04 | 10/22/2025 18:43:09 | 10/22/2025 18:43:12 |  | 10/22/2025 18:43:39 |  | Muhammad shafiq Muhammad Rasheed |  |  |  | Telecom | Zain |  | Running |  | OWS